## BuildingSummary
Building Summary Medium Office pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Medium Office Reference Building pre-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 4982.2 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.33
| East | 0.33
| North | 0.33
| West | 0.33
| Total | 0.33
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.544
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1661
| Net Dimensions - Total Area (m2) | 1661
| Roof to Skin Ratio | 0.456
Window Dimensions (m2)
| South | 195.85
| East | 130.57
| North | 195.85
| West | 130.57
| Total Area (m2) | 652.84
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 1423.65
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9964.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.75222 | See Reference Buildings Technical Report
HVAC
| System Type | SZ-CAV | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 174.59

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Perimeter_bot_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_bot_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 10.76 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_bot_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_bot_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 10.76 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_bottom | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 10.76 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_mid_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_mid_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 10.76 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_mid_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_mid_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 10.76 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_mid | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 10.76 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_top_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_top_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 16.8993 | 10.76 |  |  | 10 |  | 70.6435 |  | 1.0346
Perimeter_top_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 16.8993 | 10.76 |  |  | 10 |  | 111.5894 |  | 0.98251
Perimeter_top_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 16.8993 | 10.76 |  |  | 10 |  | 70.6381 |  | 1.0347
Core_top | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 16.8993 | 10.76 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Firstfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.40887
Midfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.40887
Topfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 3.7565
Total Conditioned Zones |  |  | 4982.19 | 19741.41 |  | 1977.7218 | 652.8006 |  | 268.139
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ_1:1_COOLC DXCOIL | 80.3755 | 78.0958 | 70.3643 | 75.2464 | 63.2821 | 63.2449 | 52.2157 | 73.8303 | 64.7513 | 56.7588 | 72.7077 | 63.497 | 70.9433 | 59.7327 | 59.8193 | 48.1936
| PSZ_1:2_COOLC DXCOIL | 21.7171 | 24.6447 | 27.1859 | 25.7433 | 24.6266 | 25.6477 | 31.9434 | 28.2626 | 21.63 | 31.9325 | 23.0281 | 18.3142 | 24.9003 | 21.3138 | 24.5913 | 27.0183
| PSZ_1:3_COOLC DXCOIL | 25.567 | 25.2866 | 25.3833 | 24.9511 | 22.2386 | 24.2871 | 18.5664 | 23.5551 | 24.0103 | 20.7119 | 17.6794 | 16.4716 | 17.4719 | 15.8587 | 14.6963 | 17.9031
| PSZ_1:4_COOLC DXCOIL | 22.711 | 22.3234 | 21.5967 | 20.6359 | 13.7956 | 19.4706 | 10.1531 | 19.942 | 16.1502 | 13.1543 | 24.9085 | 19.2797 | 27.5269 | 22.0418 | 27.9626 | 26.784
| PSZ_1:5_COOLC DXCOIL | 30.2542 | 31.0607 | 31.7605 | 30.3292 | 27.6845 | 31.7577 | 25.0623 | 29.2619 | 31.8486 | 26.3026 | 22.2322 | 22.3436 | 21.3572 | 20.9624 | 18.8785 | 17.903
| PSZ_2:1_COOLC DXCOIL | 72.4554 | 66.796 | 68.8304 | 68.6124 | 57.9064 | 61.9616 | 51.0618 | 66.0348 | 62.5147 | 54.8297 | 64.8388 | 60.9906 | 64.6392 | 58.9062 | 55.7173 | 54.2756
| PSZ_2:2_COOLC DXCOIL | 24.16 | 27.2397 | 31.3391 | 28.5243 | 26.9154 | 29.7455 | 36.2851 | 31.0448 | 25.5978 | 36.1372 | 23.3632 | 19.1264 | 25.2587 | 22.6286 | 24.7444 | 28.3713
| PSZ_2:3_COOLC DXCOIL | 26.9812 | 26.8851 | 28.365 | 26.9086 | 23.9971 | 27.5238 | 21.3441 | 25.2768 | 26.8619 | 23.3272 | 19.6165 | 19.375 | 19.3647 | 18.8538 | 17.6694 | 18.7651
| PSZ_2:4_COOLC DXCOIL | 25.2063 | 24.9808 | 25.5971 | 23.4342 | 16.1385 | 23.6059 | 13.5629 | 22.7747 | 20.1451 | 15.8175 | 24.8317 | 19.2025 | 27.2737 | 22.3774 | 27.1062 | 28.1623
| PSZ_2:5_COOLC DXCOIL | 31.8018 | 32.7323 | 34.4475 | 32.3951 | 29.4136 | 34.8234 | 27.5189 | 31.0143 | 34.5233 | 28.8828 | 24.1679 | 25.0773 | 23.2579 | 23.7234 | 21.6278 | 19.8043
| PSZ_3:1_COOLC DXCOIL | 88.9445 | 91.1154 | 93.8136 | 87.9035 | 68.056 | 85.022 | 57.4903 | 81.4817 | 71.7149 | 61.5947 | 76.4766 | 64.2666 | 70.6354 | 58.2031 | 61.0161 | 66.1772
| PSZ_3:2_COOLC DXCOIL | 26.8711 | 30.0646 | 34.7781 | 31.1505 | 28.4063 | 32.4458 | 36.8961 | 32.6512 | 27.0542 | 37.0021 | 31.1416 | 26.1965 | 33.8871 | 30.7987 | 33.4914 | 38.628
| PSZ_3:3_COOLC DXCOIL | 26.6215 | 26.4123 | 28.1487 | 26.3142 | 22.8738 | 26.8374 | 19.7362 | 24.7283 | 24.8998 | 22.0602 | 19.1422 | 17.2315 | 19.2966 | 20.1565 | 20.0768 | 25.251
| PSZ_3:4_COOLC DXCOIL | 28.4076 | 28.5026 | 29.7715 | 26.7817 | 18.3615 | 27.233 | 14.9345 | 25.4233 | 23.3035 | 17.3159 | 32.0793 | 26.1643 | 35.6723 | 30.6116 | 35.6707 | 38.4963
| PSZ_3:5_COOLC DXCOIL | 33.952 | 35.0805 | 37.5999 | 35.0483 | 31.1231 | 37.536 | 28.5226 | 32.7155 | 36.6127 | 30.2625 | 25.4971 | 26.4841 | 24.097 | 24.498 | 22.4201 | 25.2504
Heating (kW)
| PSZ_1:1_HEATC | 95.1539 | 102.1848 | 90.1778 | 104.1033 | 92.591 | 90.9907 | 84.9112 | 106.9396 | 93.7211 | 93.7642 | 111.8577 | 98.4284 | 115.187 | 105.4605 | 109.4644 | 115.8743
| PSZ_1:2_HEATC | 24.3794 | 30.1342 | 33.3385 | 33.4769 | 36.0355 | 34.1452 | 47.3604 | 38.5096 | 28.8864 | 47.9839 | 30.5361 | 25.9629 | 34.412 | 32.7553 | 36.1606 | 47.4996
| PSZ_1:3_HEATC | 34.9703 | 35.9935 | 35.6034 | 36.1218 | 32.3114 | 33.4177 | 27.6832 | 35.1913 | 30.08 | 31.0578 | 26.6807 | 22.2686 | 27.0799 | 23.5882 | 24.482 | 31.1638
| PSZ_1:4_HEATC | 26.7031 | 28.1427 | 27.2765 | 27.4988 | 18.5649 | 26.509 | 15.818 | 27.3145 | 22.6229 | 20.4645 | 30.3214 | 25.8462 | 34.0719 | 32.4304 | 35.8092 | 47.1792
| PSZ_1:5_HEATC | 41.5829 | 43.7907 | 43.7645 | 43.5173 | 39.8486 | 43.0078 | 36.7036 | 42.8324 | 39.0393 | 38.7163 | 32.3579 | 28.9691 | 32.1951 | 29.7395 | 30.0049 | 31.1632
| PSZ_2:1_HEATC | 89.7453 | 97.4489 | 94.9941 | 100.4894 | 87.0463 | 96.2928 | 85.1279 | 105.0495 | 91.1663 | 95.1891 | 110.6446 | 95.5706 | 114.3242 | 104.4652 | 111.5379 | 124.185
| PSZ_2:2_HEATC | 28.0114 | 34.0097 | 39.3582 | 37.6628 | 39.6724 | 40.1597 | 53.3895 | 42.7948 | 33.4215 | 53.7436 | 32.3143 | 27.31 | 36.2204 | 34.3397 | 38.0127 | 49.3496
| PSZ_2:3_HEATC | 37.2578 | 38.5858 | 39.7112 | 38.9377 | 34.7452 | 37.5727 | 31.5404 | 38.143 | 33.3394 | 34.6403 | 29.9377 | 25.5815 | 30.2364 | 27.198 | 28.408 | 32.3426
| PSZ_2:4_HEATC | 30.5248 | 32.213 | 33.4175 | 31.7925 | 22.2174 | 32.6929 | 21.1522 | 31.6814 | 27.189 | 24.7991 | 32.1378 | 27.2224 | 35.9615 | 34.037 | 37.7589 | 49.0639
| PSZ_2:5_HEATC | 44.0601 | 46.4482 | 47.8284 | 46.2829 | 42.2417 | 46.9431 | 40.1151 | 45.6311 | 42.0964 | 42.2507 | 35.4002 | 32.0882 | 35.2012 | 33.0671 | 33.6352 | 33.7637
| PSZ_3:1_HEATC | 103.2362 | 114.1874 | 115.2219 | 116.2713 | 95.7803 | 112.3869 | 92.1782 | 114.1572 | 101.6757 | 101.4207 | 113.6113 | 99.3059 | 112.6003 | 103.6186 | 109.3442 | 140.4477
| PSZ_3:2_HEATC | 32.0799 | 38.1712 | 44.2307 | 41.5965 | 41.7358 | 43.9093 | 54.2379 | 45.1704 | 35.0853 | 54.9276 | 41.1499 | 35.3763 | 46.0331 | 44.1849 | 48.5024 | 63.3757
| PSZ_3:3_HEATC | 36.576 | 37.6647 | 39.4224 | 38.1411 | 33.1907 | 36.6912 | 29.3075 | 37.111 | 31.0959 | 32.9042 | 29.0418 | 23.1347 | 29.978 | 28.7668 | 31.5859 | 41.2122
| PSZ_3:4_HEATC | 35.4926 | 37.6802 | 39.5791 | 36.8819 | 25.7972 | 37.9817 | 23.4478 | 35.8188 | 30.7984 | 27.3648 | 41.0435 | 35.3396 | 45.8888 | 43.9594 | 48.3771 | 63.1956
| PSZ_3:5_HEATC | 47.4561 | 50.1853 | 52.0353 | 49.8341 | 44.6078 | 50.4248 | 41.5088 | 48.3504 | 44.4836 | 44.1401 | 37.4958 | 33.6923 | 36.5321 | 33.999 | 34.68 | 41.211
HVAC Efficiency
Air Conditioning (COP)
| PSZ_1:1_COOLC DXCOIL | 3.11 | 3.11 | 3.11 | 3.11 | 3.23 | 3.23 | 3.23 | 3.11 | 3.23 | 3.23 | 3.11 | 3.23 | 3.11 | 3.23 | 3.23 | 3.23
| PSZ_1:2_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.39 | 3.38 | 3.38 | 3.38 | 3.38
| PSZ_1:3_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.39 | 3.38 | 3.38 | 3.38 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
| PSZ_1:4_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39 | 3.39 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| PSZ_1:5_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.39 | 3.39
| PSZ_2:1_COOLC DXCOIL | 3.11 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| PSZ_2:2_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| PSZ_2:3_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.39 | 3.39 | 3.39
| PSZ_2:4_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38 | 3.39 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| PSZ_2:5_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| PSZ_3:1_COOLC DXCOIL | 3.11 | 3.11 | 3.11 | 3.11 | 3.23 | 3.11 | 3.23 | 3.11 | 3.11 | 3.23 | 3.11 | 3.23 | 3.11 | 3.23 | 3.23 | 3.23
| PSZ_3:2_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| PSZ_3:3_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.39 | 3.38 | 3.38 | 3.38 | 3.38
| PSZ_3:4_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38 | 3.39 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
| PSZ_3:5_COOLC DXCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38 | 3.38
Heating Efficiency (%)
| PSZ_1:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_1:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_1:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_1:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_2:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ_3:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ_1:1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ_1:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_1:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ_1:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_1:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_2:1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ_2:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_2:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ_2:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_2:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_3:1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ_3:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_3:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_3:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ_3:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| PSZ_1:1_FAN | 3.69 | 3.65 | 3.45 | 3.71 | 3.54 | 3.49 | 3.08 | 3.56 | 3.91 | 3.25 | 3.53 | 3.84 | 3.53 | 3.61 | 3.27 | 2.91
| PSZ_1:2_FAN | 0.96 | 1.14 | 1.38 | 1.3 | 1.47 | 1.44 | 1.93 | 1.45 | 1.31 | 1.93 | 1.05 | 1.08 | 1.2 | 1.29 | 1.29 | 1.63
| PSZ_1:3_FAN | 1.46 | 1.46 | 1.53 | 1.5 | 1.34 | 1.47 | 1.12 | 1.39 | 1.45 | 1.25 | 0.99 | 1 | 0.99 | 0.96 | 0.89 | 1.08
| PSZ_1:4_FAN | 1.07 | 1.06 | 1.1 | 1.03 | 0.7 | 1.08 | 0.56 | 0.96 | 0.98 | 0.72 | 1.04 | 1.08 | 1.18 | 1.27 | 1.27 | 1.62
| PSZ_1:5_FAN | 1.75 | 1.8 | 1.9 | 1.83 | 1.67 | 1.92 | 1.51 | 1.72 | 1.92 | 1.59 | 1.25 | 1.35 | 1.22 | 1.27 | 1.14 | 1.08
| PSZ_2:1_FAN | 3.45 | 3.44 | 3.67 | 3.55 | 3.3 | 3.74 | 3.08 | 3.48 | 3.78 | 3.31 | 3.47 | 3.68 | 3.49 | 3.56 | 3.37 | 3.28
| PSZ_2:2_FAN | 1.12 | 1.31 | 1.65 | 1.49 | 1.63 | 1.72 | 2.19 | 1.64 | 1.55 | 2.18 | 1.13 | 1.16 | 1.28 | 1.37 | 1.37 | 1.71
| PSZ_2:3_FAN | 1.56 | 1.58 | 1.71 | 1.63 | 1.45 | 1.66 | 1.29 | 1.52 | 1.62 | 1.41 | 1.14 | 1.17 | 1.14 | 1.14 | 1.07 | 1.13
| PSZ_2:4_FAN | 1.23 | 1.23 | 1.38 | 1.23 | 0.86 | 1.37 | 0.79 | 1.15 | 1.22 | 0.91 | 1.12 | 1.15 | 1.27 | 1.35 | 1.36 | 1.7
| PSZ_2:5_FAN | 1.86 | 1.92 | 2.08 | 1.96 | 1.78 | 2.1 | 1.66 | 1.85 | 2.09 | 1.74 | 1.38 | 1.51 | 1.36 | 1.43 | 1.31 | 1.2
| PSZ_3:1_FAN | 4.04 | 4.17 | 4.59 | 4.26 | 3.68 | 4.5 | 3.39 | 3.88 | 4.33 | 3.59 | 3.61 | 3.88 | 3.41 | 3.52 | 3.27 | 4
| PSZ_3:2_FAN | 1.3 | 1.49 | 1.87 | 1.67 | 1.72 | 1.9 | 2.23 | 1.74 | 1.63 | 2.24 | 1.52 | 1.58 | 1.72 | 1.86 | 1.85 | 2.33
| PSZ_3:3_FAN | 1.53 | 1.53 | 1.7 | 1.59 | 1.38 | 1.62 | 1.19 | 1.47 | 1.5 | 1.33 | 1.1 | 1.04 | 1.12 | 1.22 | 1.21 | 1.53
| PSZ_3:4_FAN | 1.45 | 1.47 | 1.66 | 1.46 | 1.02 | 1.62 | 0.89 | 1.33 | 1.41 | 1.02 | 1.52 | 1.58 | 1.71 | 1.85 | 1.85 | 2.33
| PSZ_3:5_FAN | 2 | 2.08 | 2.27 | 2.12 | 1.88 | 2.27 | 1.72 | 1.96 | 2.21 | 1.83 | 1.47 | 1.6 | 1.42 | 1.48 | 1.35 | 1.53
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.0859 | 0.11779 | 0.090226 | 0.098462 | 0.13109 | 0.099263 | 0.14863 | 0.0754 | 0.037126 | 0.075253 | 0.091257 | 0.037142 | 0.059735 | 0.076273 | 0.059058 | 0.096738
| Total Cost ($/m2) | 19.73 | 25.3 | 21.35 | 20.17 | 22.74 | 21.83 | 23.77 | 14.56 | 7.25 | 12.58 | 16.25 | 6.69 | 10.44 | 13.43 | 9.79 | 16.78
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011454 | 0.0080872 | 0.0082911 | 0.0095313 | 0.0085703 | 0.0076996 | 0.0087036 | 0.0096561 | 0.0068578 | 0.0084644 | 0.0082332 | 0.0068521 | 0.0079187 | 0.0079279 | 0.0078816 | 0.0040988
| Total Cost ($/m2) | 0.06 | 0.21 | 0.11 | 0.53 | 0.08 | 0.17 | 0.23 | 1.12 | 0.41 | 0.76 | 1.38 | 0.69 | 2.07 | 1.42 | 2.7 | 2.66
Total Utility Costs
| Cost Intensity ($/m2) | 19.79 | 25.51 | 21.46 | 20.7 | 22.82 | 22 | 24 | 15.68 | 7.65 | 13.34 | 17.64 | 7.39 | 12.51 | 14.84 | 12.49 | 19.44
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 301736.1111 | 230636.1111 | 305011.1111 | 163450 | 54647.2222 | 230033.3333 | 18325 | 122377.7778 | 108294.4444 | 20133.3333 | 70130.5556 | 61588.8889 | 59969.4444 | 36013.8889 | 26550 | 18738.8889
| Interior Lighting | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889 | 264338.8889
| Exterior Lighting | 77844.4444 | 77813.8889 | 77800 | 77786.1111 | 77727.7778 | 77708.3333 | 77750 | 77702.7778 | 77733.3333 | 77577.7778 | 77716.6667 | 77672.2222 | 77663.8889 | 77647.2222 | 77602.7778 | 77127.7778
| Interior Equipment | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 204141.6667 | 201133.3333 | 235619.4444 | 218597.2222 | 171313.8889 | 227494.4444 | 139966.6667 | 201122.2222 | 226022.2222 | 174811.1111 | 178850 | 198047.2222 | 172372.2222 | 202691.6667 | 161377.7778 | 207522.2222
| Pumps | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1144388.8889 | 1070252.7778 | 1179100 | 1020500 | 864358.3333 | 1095905.5556 | 796711.1111 | 961869.4444 | 972716.6667 | 833191.6667 | 887366.6667 | 897975 | 870675 | 877022.2222 | 826197.2222 | 864055.5556
Gas (MJ)
| Heating | 2020 | 99670 | 39100 | 245750 | 16850 | 80810 | 96970 | 543600 | 262370 | 412210 | 801410 | 468670 | 1265780 | 850570 | 1662340 | 3190850
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 22720 | 26650 | 24380 | 30450 | 29720 | 27110 | 32970 | 33440 | 32870 | 35000 | 36060 | 35920 | 38330 | 38740 | 42060 | 46580
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 24740 | 126320 | 63480 | 276200 | 46570 | 107920 | 129940 | 577040 | 295240 | 447210 | 837470 | 504590 | 1304110 | 889310 | 1704410 | 3237430
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 4144530 | 3979230 | 4308230 | 3950000 | 3158260 | 4053180 | 2998100 | 4039770 | 3797030 | 3446700 | 4031980 | 3737310 | 4438540 | 4046580 | 4678720 | 6348030
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 218.0266 | 166.6516 | 220.393 | 118.1047 | 39.4867 | 166.2161 | 13.2412 | 88.427 | 78.2507 | 14.5478 | 50.6745 | 44.5025 | 43.3323 | 26.0227 | 19.1843 | 13.5402
| Interior Lighting (elec) | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044 | 191.0044
| Exterior Lighting (elec) | 56.2484 | 56.2263 | 56.2162 | 56.2062 | 56.1641 | 56.15 | 56.1801 | 56.146 | 56.1681 | 56.0557 | 56.156 | 56.1239 | 56.1179 | 56.1058 | 56.0737 | 55.7305
| Interior Equipment (elec) | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 147.5074 | 145.3337 | 170.2524 | 157.9526 | 123.7869 | 164.3815 | 101.1362 | 145.3256 | 163.3177 | 126.3139 | 129.2323 | 143.1037 | 124.5517 | 146.4597 | 116.6074 | 149.9501
| Pumps (elec) | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 826.9054 | 773.3366 | 851.9868 | 737.3866 | 624.5627 | 791.8727 | 575.6826 | 695.0217 | 702.8596 | 602.0425 | 641.1879 | 648.8532 | 629.127 | 633.7133 | 596.9885 | 624.3439
Gas (MJ/m2)
| Heating (gas) | 0.40544 | 20.0053 | 7.848 | 49.3257 | 3.382 | 16.2198 | 19.4633 | 109.1086 | 52.6616 | 82.7367 | 160.855 | 94.0691 | 254.061 | 170.7221 | 333.6565 | 640.4513
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 4.5602 | 5.3491 | 4.8934 | 6.1118 | 5.9652 | 5.4414 | 6.6176 | 6.7119 | 6.5975 | 7.025 | 7.2378 | 7.2097 | 7.6934 | 7.7757 | 8.4421 | 9.3493
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4.9657 | 25.3543 | 12.7414 | 55.4375 | 9.3473 | 21.6612 | 26.0809 | 115.8206 | 59.2591 | 89.7617 | 168.0927 | 101.2788 | 261.7544 | 178.4978 | 342.1006 | 649.8006
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 831.8691 | 798.6909 | 864.7262 | 792.824 | 633.91 | 813.5338 | 601.7635 | 810.8422 | 762.1207 | 691.8042 | 809.2787 | 750.134 | 890.8813 | 812.2091 | 939.089 | 1274.1445
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 260.7615 | 240.1277 | 251.3512 | 221.8198 | 251.853 | 198.1528 | 185.9828 | 199.4925 | 189.8162 | 190.7334 | 190.5345 | 195.7136 | 188.464 | 202.8059 | 185.4123 | 199.064
| Feb | 267.034 | 251.9373 | 267.7415 | 221.8121 | 238.8894 | 214.5218 | 196.0904 | 193.7724 | 216.5267 | 180.4301 | 190.5345 | 186.3016 | 178.1147 | 185.1169 | 175.1021 | 199.064
| Mar | 274.472 | 246.6946 | 302.0948 | 250.9035 | 245.8905 | 255.9868 | 177.4436 | 220.4543 | 223.2715 | 191.9836 | 202.2325 | 219.9837 | 182.2218 | 200.8773 | 175.1096 | 199.064
| Apr | 279.5977 | 265.0158 | 303.5155 | 260.0343 | 249.0402 | 297.8563 | 214.4246 | 236.803 | 273.178 | 180.3851 | 203.7718 | 238.3879 | 201.3456 | 188.3414 | 178.5704 | 182.4641
| May | 290.9818 | 300.9473 | 338.8215 | 281.2925 | 238.9671 | 331.1589 | 220.2806 | 254.2419 | 290.8545 | 231.6977 | 244.8645 | 257.7 | 237.654 | 232.1799 | 212.4309 | 205.0164
| Jun | 306.8965 | 306.3522 | 403.8567 | 301.5103 | 235.7709 | 384.0179 | 226.2987 | 302.1295 | 317.1267 | 238.9762 | 277.5135 | 276.7216 | 267.2666 | 272.7495 | 232.3054 | 235.0838
| Jul | 299.6603 | 313.8636 | 377.3662 | 330.1025 | 245.5572 | 376.2593 | 242.5071 | 314.4609 | 331.0674 | 255.0109 | 282.0255 | 292.5374 | 267.0616 | 276.7622 | 248.1612 | 237.5378
| Aug | 311.4361 | 315.7736 | 385.3541 | 300.5126 | 267.1879 | 355.3093 | 229.8624 | 313.6695 | 305.9418 | 249.0286 | 277.0306 | 285.3324 | 265.003 | 267.2412 | 238.5434 | 230.0544
| Sep | 299.854 | 300.4092 | 347.4109 | 286.565 | 270.4023 | 350.5717 | 274.341 | 278.4146 | 284.8331 | 246.809 | 246.6169 | 271.2315 | 239.8087 | 250.6056 | 219.7873 | 187.1967
| Oct | 291.2703 | 278.6153 | 308.5158 | 272.5481 | 262.0056 | 305.4373 | 228.8229 | 249.5662 | 271.5029 | 205.0895 | 219.4575 | 257.8581 | 206.2755 | 223.9118 | 182.1771 | 199.064
| Nov | 271.7211 | 256.4683 | 285.9692 | 229.51 | 245.8467 | 232.1385 | 187.0042 | 230.6895 | 202.9621 | 190.7334 | 215.6158 | 205.6528 | 188.5031 | 202.8059 | 185.4123 | 199.064
| Dec | 258.2562 | 242.6673 | 243.0691 | 221.0198 | 251.6679 | 222.4383 | 186.0522 | 198.4383 | 200.2399 | 190.7334 | 190.6005 | 196.1426 | 188.464 | 202.8059 | 185.4123 | 199.064
Time of Peak Electrical Demand
| Jan | 23-JAN-16:10 | 03-JAN-13:00 | 26-JAN-15:39 | 23-JAN-16:10 | 26-JAN-13:09 | 02-JAN-16:40 | 02-JAN-16:00 | 05-JAN-16:00 | 02-JAN-08:09 | 02-JAN-16:30 | 02-JAN-16:30 | 12-JAN-16:00 | 02-JAN-16:40 | 10-JAN-08:09 | 02-JAN-16:30 | 02-JAN-08:09
| Feb | 22-FEB-13:00 | 23-FEB-13:00 | 28-FEB-16:10 | 27-FEB-16:30 | 13-FEB-11:00 | 08-FEB-13:00 | 15-FEB-16:10 | 15-FEB-16:10 | 14-FEB-16:10 | 22-FEB-08:39 | 01-FEB-16:00 | 23-FEB-08:00 | 16-FEB-08:00 | 02-FEB-08:50 | 28-FEB-08:00 | 01-FEB-08:09
| Mar | 13-MAR-15:30 | 27-MAR-15:30 | 17-MAR-15:20 | 22-MAR-15:00 | 30-MAR-12:30 | 31-MAR-15:09 | 10-MAR-08:00 | 09-MAR-16:10 | 02-MAR-14:00 | 29-MAR-15:30 | 31-MAR-15:09 | 30-MAR-15:00 | 23-MAR-15:30 | 30-MAR-15:00 | 22-MAR-07:49 | 01-MAR-08:09
| Apr | 03-APR-15:09 | 17-APR-15:39 | 26-APR-15:39 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:09 | 13-APR-15:09 | 05-APR-15:50 | 21-APR-15:39 | 26-APR-07:00 | 28-APR-15:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-15:09 | 25-APR-15:00
| May | 24-MAY-14:50 | 26-MAY-15:09 | 30-MAY-15:00 | 15-MAY-15:09 | 30-MAY-10:20 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:50 | 31-MAY-15:00 | 04-MAY-15:09 | 04-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:09
| Jun | 27-JUN-15:09 | 13-JUN-15:20 | 08-JUN-15:00 | 19-JUN-15:09 | 28-JUN-12:00 | 27-JUN-15:00 | 16-JUN-15:09 | 30-JUN-15:00 | 20-JUN-15:39 | 28-JUN-15:09 | 08-JUN-12:00 | 28-JUN-12:30 | 29-JUN-15:00 | 26-JUN-15:09 | 14-JUN-15:00 | 20-JUN-15:00
| Jul | 03-JUL-15:09 | 31-JUL-14:30 | 11-JUL-15:00 | 03-JUL-15:30 | 10-JUL-15:30 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-15:39 | 24-JUL-15:09 | 03-JUL-15:09 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-15:09 | 28-AUG-15:30 | 01-AUG-15:00 | 14-AUG-15:30 | 09-AUG-14:09 | 18-AUG-15:09 | 15-AUG-12:09 | 17-AUG-15:09 | 01-AUG-15:09 | 07-AUG-15:09 | 04-AUG-15:30 | 29-AUG-15:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 15-AUG-15:00
| Sep | 11-SEP-15:09 | 15-SEP-15:09 | 11-SEP-15:00 | 11-SEP-12:00 | 25-SEP-12:00 | 01-SEP-15:09 | 28-SEP-15:09 | 08-SEP-15:09 | 20-SEP-15:30 | 01-SEP-15:30 | 27-SEP-15:00 | 06-SEP-15:09 | 14-SEP-15:09 | 01-SEP-15:00 | 07-SEP-15:09 | 07-SEP-15:00
| Oct | 06-OCT-15:30 | 06-OCT-15:00 | 24-OCT-15:39 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:09 | 30-OCT-12:00 | 12-OCT-15:09 | 13-OCT-15:09 | 17-OCT-12:00 | 31-OCT-12:00 | 05-OCT-15:09 | 06-OCT-15:09 | 06-OCT-15:00 | 06-OCT-15:09 | 03-OCT-07:10
| Nov | 07-NOV-13:00 | 01-NOV-15:09 | 13-NOV-13:00 | 22-NOV-13:50 | 08-NOV-13:09 | 10-NOV-13:00 | 13-NOV-16:00 | 03-NOV-13:00 | 08-NOV-14:00 | 06-NOV-16:49 | 02-NOV-15:09 | 10-NOV-13:00 | 06-NOV-16:00 | 02-NOV-07:10 | 06-NOV-16:49 | 01-NOV-07:10
| Dec | 19-DEC-13:00 | 19-DEC-15:20 | 11-DEC-16:10 | 01-DEC-13:00 | 19-DEC-13:09 | 05-DEC-13:00 | 01-DEC-16:49 | 06-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 12-DEC-16:19 | 21-DEC-16:40 | 01-DEC-16:30 | 20-DEC-08:09 | 01-DEC-16:19 | 01-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 13692.38 | 14131.7 | 13495.48 | 12660.28 | 9681.53 | 14230.04 | 9018.84 | 13012.86 | 11941.32 | 5713.46 | 12242.27 | 11277.16 | 12197.13 | 11945.81 | 12083.93 | 14646.33
| Total Source Energy (MJ/m2) | 2748.27 | 2836.45 | 2708.75 | 2541.11 | 1943.23 | 2856.18 | 1810.22 | 2611.88 | 2396.8 | 1146.78 | 2457.21 | 2263.5 | 2448.15 | 2397.7 | 2425.43 | 2939.74
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
| Total Building | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
Emissions
| Carbon Equivalent (kg) | 314294.1975 | 359272.2574 | 357085.6678 | 319332.1515 | 101853.6386 | 371567.5105 | 95451.3709 | 269971.5228 | 402677.2708 | 68749.144 | 488200.0893 | 375920.6294 | 321542.6686 | 336532.9154 | 313536.8721 | 301513.7129
| CO2 (kg) | 728021.0112 | 902382.4585 | 840373.0142 | 727842.1965 | 272116.27 | 881075.4626 | 255353.0563 | 612149.1533 | 941253.8051 | 167455.0517 | 1135200 | 881018.8695 | 755011.3863 | 791765.5672 | 740769.0126 | 777725.0622
| NOX (kg) | 1282.8389 | 1183.4237 | 1417.7796 | 1390.7398 | 232.9966 | 1440.7842 | 218.8774 | 1191.1186 | 1638.4425 | 252.7735 | 2027.24 | 1523.5233 | 1315.4569 | 1365.2783 | 1270.3437 | 916.16
| SO2 (kg) | 4898.4451 | 5105.1369 | 4741.4094 | 3582.0305 | 2515.1884 | 6028.3843 | 2318.368 | 3511.3664 | 4247.7426 | 644.1101 | 5980.3579 | 3921.4178 | 2055.2827 | 2341.9895 | 1950.4165 | 4399.2532
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0223 | 0.0144 | 0.0129 | 0.0131 | 0.0011 | 0.0113 | 0.0011 | 0.0142 | 0.0166 | 0.0025 | 0.0181 | 0.0153 | 0.0151 | 0.0163 | 0.0144 | 0.0152
| Water for Electricity (m3) | 606.2487 | 1741.43 | 35024.4 | 6371.6 | 15176.2 | 30065.1 | 13988.5 | 218.3808 | 4416.92 | 8512.55 | 1376.69 | 4077.53 | 1350.8 | 55554.2 | 1281.8 | 882.7877

## Picture
DOE Commercial Building Benchmark - Medium Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1 | 54.5 | 2841.79
|  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | 10.2
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 11.3 | 60.8 | 3170.29
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 15 | 83.75 | 4366.96
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.75
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 597.6 | 3596.4 | 187526.57
|  |  | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 608.4
|  |  | WinterDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
|  |  | Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 2743.2 | 143038.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 439.2
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600