## BuildingSummary
Building Summary Retail pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Retail Reference Building pre-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Retail
Form
| Total Floor Area (m2) | 2294 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.254
| East | 0
| North | 0
| West | 0
| Total | 0.071
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Back, CoreRetail, FrontRetail, PointofSale, FrontEntry
| Floor to Ceiling Height (m) | 6.1
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1177
| Net Dimensions - Total Area (m2) | 1093.1
| Wall to Skin Ratio | 0.34
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2294
| Net Dimensions - Total Area (m2) | 2294
| Roof to Skin Ratio | 0.66
Window Dimensions (m2)
| South | 83.9
| East | 0
| North | 0
| West | 0
| Total Area (m2) | 83.9
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2294
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Internal Mass | 244.23
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 7764.95
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.27 | See Reference Buildings Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (L ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Back_Space | Yes | 1 | 379.89 | 2317.33 | 6.1 | 416.1704 | 0 | 27.8709 | 13.6303 | 12.558 | 8.0729 |  |  |  | 0.75 | 284.9175 |  | 1.4021
Core_Retail | Yes | 1 | 1600.48 | 9762.95 | 6.1 | 356.8603 | 0 | 6.1939 | 258.3982 | 36.2662 | 3.2292 |  |  |  | 1.5 | 2400.72 |  | 0.81826
Point_of_Sale | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8002 | 38.05 | 6.1939 | 24.3483 | 36.2662 | 21.5278 |  |  |  | 1.5 | 226.215 |  | 1.5111
Front_Retail | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8002 | 38.05 | 6.1939 | 24.3483 | 36.2662 | 3.2292 |  |  |  | 1.5 | 226.215 |  | 1.5111
Front_Entry | Yes | 1 | 12 | 73.2 | 6.1 | 24.38 | 7.83 | 6.1939 | 1.9374 | 36.2662 | 0 | [6 empty] | 1
Total Conditioned Zones |  |  | 2293.99 | 13993.36 |  | 1177.0111 | 83.9301 |  | 322.6626
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 50.3722 | 52.1716 | 49.0466 | 58.1154 | 28.7315 | 39.9869 | 27.0655 | 67.1974 | 46.3374 | 37.7764 | 88.6971 | 61.7167 | 99.9181 | 70.9012 | 103.5232 | 93.8768
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 222.973 | 230.3448 | 224.9198 | 226.1535 | 156.0825 | 190.1862 | 103.5335 | 201.5897 | 144.8005 | 120.2566 | 190.9514 | 134.8637 | 217.2094 | 153.6927 | 224.234 | 213.9805
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 36.7758 | 39.4503 | 39.279 | 38.1292 | 30.2889 | 34.5414 | 30.0283 | 37.9297 | 28.3021 | 30.509 | 36.0139 | 26.2502 | 40.1759 | 31.6023 | 39.7247 | 42.108
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 32.613 | 35.3921 | 35.4216 | 34.3193 | 26.6732 | 30.6258 | 25.9108 | 34.2801 | 23.4693 | 26.6177 | 38.4206 | 26.6569 | 42.5536 | 31.6064 | 42.2076 | 42.108
Heating (kW)
| FRONT_ENTRY UNIT HEATER COIL | 0.83514 | 1.8098 | 1.4048 | 2.235 | 1.0814 | 1.7791 | 1.3662 | 2.4356 | 2.1362 | 1.8943 | 2.8109 | 2.4671 | 3.138 | 3.0448 | 3.3074 | 4.3773
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 27.3226 | 55.3035 | 43.1334 | 66.3255 | 34.2046 | 53.1506 | 42.5898 | 74.2529 | 61.4876 | 57.7771 | 94.4324 | 79.3724 | 105.6153 | 99.9464 | 110.8028 | 150.0503
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 92.9463 | 160.0455 | 121.9098 | 194.5376 | 96.6681 | 153.2215 | 120.6142 | 225.3056 | 180.6699 | 172.4418 | 291.1268 | 238.6868 | 327.7199 | 306.8585 | 345.2961 | 474.1503
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 13.1104 | 27.2109 | 20.6176 | 32.9941 | 16.1553 | 25.7667 | 20.4764 | 37.3814 | 30.6667 | 28.8966 | 46.7012 | 38.8621 | 52.5577 | 49.57 | 55.2682 | 74.7357
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 13.1095 | 27.2109 | 20.6176 | 32.9953 | 16.1568 | 25.7684 | 20.4768 | 37.3833 | 30.6667 | 28.8962 | 46.7029 | 38.8584 | 52.5609 | 49.5749 | 55.2709 | 74.7357
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3 | 3.5 | 3.23 | 3.3 | 3.23 | 3.23 | 3.23 | 3.23
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.13 | 3.23
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3
Heating Efficiency (%)
| FRONT_ENTRY UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| FRONT_ENTRY UNIT HEATERFAN | 0.04 | 0.08 | 0.06 | 0.1 | 0.05 | 0.08 | 0.06 | 0.1 | 0.11 | 0.08 | 0.12 | 0.13 | 0.14 | 0.15 | 0.15 | 0.19
| PSZ-AC:1_UNITARY_PACKAGE_FAN | 2.06 | 2.16 | 2.34 | 2.57 | 1.44 | 2.16 | 1.59 | 2.76 | 2.8 | 2.17 | 3.57 | 3.61 | 4.02 | 4.28 | 4.32 | 5.67
| PSZ-AC:2_UNITARY_PACKAGE_FAN | 8.98 | 9.28 | 9.32 | 9.18 | 7.62 | 8.96 | 5.91 | 8.12 | 8.38 | 6.55 | 7.69 | 7.64 | 8.75 | 9.28 | 9.49 | 12.93
| PSZ-AC:3_UNITARY_PACKAGE_FAN | 1.58 | 1.74 | 1.96 | 1.82 | 1.7 | 1.94 | 1.81 | 1.76 | 1.71 | 1.84 | 1.58 | 1.59 | 1.79 | 1.91 | 1.93 | 2.54
| PSZ-AC:4_UNITARY_PACKAGE_FAN | 1.32 | 1.48 | 1.71 | 1.57 | 1.45 | 1.67 | 1.57 | 1.52 | 1.42 | 1.61 | 1.58 | 1.59 | 1.79 | 1.91 | 1.93 | 2.54
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.086145 | 0.12012 | 0.098032 | 0.099914 | 0.12952 | 0.099052 | 0.14802 | 0.07582 | 0.037285 | 0.074878 | 0.092663 | 0.037287 | 0.059978 | 0.074635 | 0.058722 | 0.09422
| Total Cost ($/m2) | 25.07 | 32.91 | 27.75 | 25.12 | 28.17 | 25.84 | 29.98 | 17.99 | 8.75 | 15.62 | 22 | 8.71 | 14.52 | 17.86 | 13.84 | 24.44
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011406 | 0.0080452 | 0.0081304 | 0.0094931 | 0.0086342 | 0.0076224 | 0.0085773 | 0.0096541 | 0.0068655 | 0.0084192 | 0.0082935 | 0.0068997 | 0.0078729 | 0.0080619 | 0.0078602 | 0.0041209
| Total Cost ($/m2) | 0.09 | 1.13 | 0.94 | 2.81 | 0.75 | 1.54 | 2.18 | 5.11 | 2.62 | 4 | 5.9 | 3.68 | 7.32 | 6.02 | 9.22 | 8.07
Total Utility Costs
| Cost Intensity ($/m2) | 25.16 | 34.03 | 28.69 | 27.93 | 28.92 | 27.38 | 32.16 | 23.1 | 11.38 | 19.62 | 27.9 | 12.38 | 21.84 | 23.88 | 23.06 | 32.51
Energy - End Uses
Electricity (kWh)
| Heating | 38.8889 | 525 | 438.8889 | 1083.3333 | 350 | 636.1111 | 913.8889 | 1700 | 1238.8889 | 1872.2222 | 2113.8889 | 1705.5556 | 2686.1111 | 2438.8889 | 3483.3333 | 6380.5556
| Cooling | 182338.8889 | 136897.2222 | 154055.5556 | 81391.6667 | 28055.5556 | 106783.3333 | 7338.8889 | 56886.1111 | 49461.1111 | 9336.1111 | 38666.6667 | 30219.4444 | 31350 | 16888.8889 | 9977.7778 | 3266.6667
| Interior Lighting | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444
| Exterior Lighting | 43688.8889 | 43672.2222 | 43663.8889 | 43655.5556 | 43622.2222 | 43613.8889 | 43636.1111 | 43611.1111 | 43627.7778 | 43538.8889 | 43616.6667 | 43591.6667 | 43588.8889 | 43577.7778 | 43552.7778 | 43286.1111
| Interior Equipment | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 116488.8889 | 122333.3333 | 126286.1111 | 125666.6667 | 102002.7778 | 122400 | 87775 | 117113.8889 | 119305.5556 | 98847.2222 | 135308.3333 | 135083.3333 | 152766.6667 | 160975 | 158763.8889 | 217186.1111
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 667527.7778 | 628397.2222 | 649416.6667 | 576769.4444 | 499005.5556 | 598405.5556 | 464638.8889 | 544277.7778 | 538602.7778 | 478566.6667 | 544677.7778 | 535572.2222 | 555361.1111 | 548852.7778 | 540750 | 595094.4444
Gas (MJ)
| Heating | 17880 | 321260 | 264880 | 679950 | 198340 | 463020 | 582620 | 1215270 | 876760 | 1088550 | 1632200 | 1222940 | 2132080 | 1713730 | 2689700 | 4493530
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 17880 | 321260 | 264880 | 679950 | 198340 | 463020 | 582620 | 1215270 | 876760 | 1088550 | 1632200 | 1222940 | 2132080 | 1713730 | 2689700 | 4493530
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2420980 | 2583490 | 2602780 | 2756320 | 1994760 | 2617270 | 2255320 | 3174670 | 2815730 | 2811390 | 3593030 | 3151000 | 4131380 | 3689600 | 4636400 | 6635860
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.061029 | 0.82389 | 0.68876 | 1.7001 | 0.54926 | 0.99826 | 1.4342 | 2.6678 | 1.9442 | 2.9381 | 3.3174 | 2.6766 | 4.2154 | 3.8274 | 5.4665 | 10.0131
| Cooling (elec) | 286.1477 | 214.8353 | 241.7622 | 127.7294 | 44.0281 | 167.577 | 11.5171 | 89.2724 | 77.6202 | 14.6513 | 60.6803 | 47.4239 | 49.1981 | 26.504 | 15.6583 | 5.1264
| Interior Lighting (elec) | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148
| Exterior Lighting (elec) | 68.5618 | 68.5356 | 68.5225 | 68.5095 | 68.4571 | 68.4441 | 68.4789 | 68.4397 | 68.4659 | 68.3264 | 68.4484 | 68.4092 | 68.4048 | 68.3874 | 68.3482 | 67.9297
| Interior Equipment (elec) | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 182.8081 | 191.9799 | 198.1831 | 197.211 | 160.0748 | 192.0845 | 137.7469 | 183.7889 | 187.2284 | 155.1227 | 212.3418 | 211.9887 | 239.7395 | 252.621 | 249.151 | 340.8341
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1047.5634 | 986.1551 | 1019.1413 | 905.1347 | 783.0984 | 939.0887 | 729.1662 | 854.145 | 845.2391 | 751.0233 | 854.7727 | 840.4832 | 871.5382 | 861.3246 | 848.6088 | 933.8925
Gas (MJ/m2)
| Heating (gas) | 7.7943 | 140.0442 | 115.4669 | 296.405 | 86.4607 | 201.8405 | 253.9767 | 529.7626 | 382.1987 | 474.5226 | 711.5114 | 533.1061 | 929.4199 | 747.0521 | 1172.4986 | 1958.8272
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 7.7943 | 140.0442 | 115.4669 | 296.405 | 86.4607 | 201.8405 | 253.9767 | 529.7626 | 382.1987 | 474.5226 | 711.5114 | 533.1061 | 929.4199 | 747.0521 | 1172.4986 | 1958.8272
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1055.3577 | 1126.1993 | 1134.6083 | 1201.5397 | 869.5592 | 1140.9248 | 983.1429 | 1383.9075 | 1227.4378 | 1225.5459 | 1566.2797 | 1373.5892 | 1800.9582 | 1608.3767 | 2021.1073 | 2892.7153
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 147.5748 | 139.4929 | 129.291 | 116.6083 | 125.711 | 112.2344 | 104.4239 | 110.408 | 110.2389 | 106.7391 | 113.7375 | 113.25 | 117.0786 | 118.4217 | 117.759 | 129.4597
| Feb | 157.3589 | 144.6357 | 137.4284 | 120.5491 | 120.7389 | 118.2925 | 110.5066 | 109.9585 | 113.1157 | 106.8436 | 113.2541 | 113.3444 | 116.5777 | 118.1079 | 117.699 | 129.2891
| Mar | 158.4426 | 146.2976 | 159.4741 | 131.0349 | 121.4076 | 126.0774 | 104.0233 | 122.9177 | 113.2758 | 106.5152 | 113.0249 | 119.5426 | 116.2153 | 112.1685 | 117.0534 | 126.6319
| Apr | 167.7745 | 170.7463 | 165.4993 | 149.2898 | 131.7065 | 157.2498 | 114.95 | 124.7951 | 137.5903 | 106.8415 | 114.2905 | 126.401 | 120.899 | 107.9535 | 107.5077 | 117.5717
| May | 182.6174 | 185.9709 | 195.0273 | 161.711 | 124.0439 | 174.3093 | 117 | 143.3816 | 145.3817 | 117.7953 | 143.3605 | 136.6196 | 174.1886 | 130.1187 | 125.228 | 116.3972
| Jun | 188.9977 | 188.5974 | 229.2059 | 178.6973 | 126.9574 | 206.3378 | 119.0786 | 179.5277 | 162.544 | 123.7919 | 173.3649 | 152.2041 | 172.2367 | 158.5793 | 145.3286 | 144.4986
| Jul | 182.6593 | 195.6172 | 221.1447 | 197.412 | 134.9775 | 203.3439 | 129.9708 | 187.2906 | 169.6612 | 136.7129 | 177.8086 | 161.3318 | 179.1758 | 160.6872 | 161.2097 | 151.2018
| Aug | 190.2845 | 194.3156 | 222.6851 | 183.2055 | 144.8947 | 197.736 | 125.3719 | 188.8209 | 164.4032 | 131.1219 | 173.3685 | 162.7049 | 169.9909 | 153.2741 | 160.8286 | 142.7812
| Sep | 180.6572 | 188.4633 | 204.2854 | 169.0975 | 145.6023 | 192.0707 | 145.8294 | 161.4694 | 147.3247 | 155.0143 | 149.6121 | 150.7539 | 146.8923 | 143.7516 | 134.7702 | 116.8369
| Oct | 175.317 | 166.465 | 165.6852 | 155.9946 | 135.2471 | 158.1192 | 115.4933 | 138.2641 | 131.4764 | 106.5828 | 129.1675 | 135.4366 | 132.2987 | 123.8653 | 128.7541 | 127.7435
| Nov | 160.1067 | 146.3305 | 149.9401 | 121.3251 | 126.8446 | 122.3693 | 104.4222 | 126.2791 | 113.8698 | 106.8014 | 127.3513 | 113.6908 | 116.2597 | 117.5298 | 117.4022 | 128.4049
| Dec | 149.0721 | 142.2738 | 128.1177 | 113.6189 | 127.3883 | 119.1994 | 104.3628 | 110.2958 | 110.4611 | 107.048 | 113.3093 | 113.5753 | 116.7883 | 118.4343 | 117.6228 | 129.0911
Time of Peak Electrical Demand
| Jan | 24-JAN-13:00 | 03-JAN-13:00 | 28-JAN-14:00 | 23-JAN-17:00 | 26-JAN-13:00 | 18-JAN-16:49 | 04-JAN-17:00 | 17-JAN-17:00 | 12-JAN-17:00 | 31-JAN-17:00 | 26-JAN-17:00 | 05-JAN-17:00 | 04-JAN-17:00 | 06-JAN-17:00 | 11-JAN-17:00 | 13-JAN-09:09
| Feb | 25-FEB-13:00 | 23-FEB-15:09 | 28-FEB-15:00 | 18-FEB-15:09 | 13-FEB-11:00 | 07-FEB-17:10 | 15-FEB-17:49 | 23-FEB-17:00 | 14-FEB-17:49 | 11-FEB-17:00 | 03-FEB-17:00 | 14-FEB-17:00 | 01-FEB-17:00 | 22-FEB-17:00 | 01-FEB-17:00 | 03-FEB-09:09
| Mar | 13-MAR-14:00 | 25-MAR-12:50 | 17-MAR-14:00 | 28-MAR-15:50 | 31-MAR-14:09 | 31-MAR-14:00 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-15:09 | 06-MAR-17:00 | 03-MAR-17:00 | 30-MAR-15:00 | 01-MAR-17:00 | 30-MAR-16:00 | 08-MAR-17:00 | 02-MAR-17:00
| Apr | 01-APR-15:20 | 29-APR-14:30 | 01-APR-15:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 04-APR-08:09 | 03-APR-08:09 | 10-APR-08:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-15:50 | 15-MAY-14:00 | 30-MAY-12:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 18-MAY-08:09
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-14:00 | 29-JUN-14:20 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-15:30 | 14-JUN-15:00 | 20-JUN-16:00
| Jul | 13-JUL-14:00 | 29-JUL-14:00 | 11-JUL-15:00 | 03-JUL-14:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-16:00
| Aug | 21-AUG-14:39 | 31-AUG-14:09 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-14:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:20 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-16:00
| Sep | 07-SEP-13:00 | 16-SEP-13:00 | 09-SEP-15:20 | 11-SEP-13:00 | 23-SEP-13:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 02-SEP-14:00 | 02-SEP-15:00 | 05-SEP-14:00 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 29-SEP-08:09
| Oct | 06-OCT-14:39 | 06-OCT-15:00 | 24-OCT-14:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 13-OCT-14:00 | 20-OCT-14:00 | 13-OCT-14:00 | 17-OCT-15:39 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 27-OCT-08:09
| Nov | 07-NOV-15:09 | 03-NOV-14:39 | 13-NOV-15:09 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-16:40 | 14-NOV-16:00 | 04-NOV-12:00 | 08-NOV-17:10 | 16-NOV-17:00 | 02-NOV-16:49 | 04-NOV-16:00 | 27-NOV-17:00 | 27-NOV-17:00 | 24-NOV-17:00 | 02-NOV-08:09
| Dec | 16-DEC-12:00 | 02-DEC-12:00 | 09-DEC-15:30 | 01-DEC-17:30 | 19-DEC-12:00 | 05-DEC-16:30 | 02-DEC-17:00 | 14-DEC-17:00 | 28-DEC-17:00 | 13-DEC-17:00 | 13-DEC-17:00 | 01-DEC-17:00 | 30-DEC-17:00 | 11-DEC-17:00 | 30-DEC-17:00 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 7990.6 | 8567.24 | 7684.02 | 7727.42 | 5776.5 | 8211.4 | 5813.22 | 8333.91 | 7390.93 | 4189.89 | 8735.48 | 7732.74 | 9199.83 | 8739.51 | 9627.96 | 12559.35
| Total Source Energy (MJ/m2) | 3483.27 | 3734.64 | 3349.63 | 3368.55 | 2518.1 | 3579.52 | 2534.11 | 3632.93 | 3221.86 | 1826.46 | 3807.98 | 3370.87 | 4010.4 | 3809.74 | 4197.03 | 5474.89
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 183391.5776 | 215402.0842 | 200819.2937 | 189927.6272 | 61893.2089 | 210176.5373 | 64806.579 | 168791.2876 | 235828.8671 | 54485.5155 | 319826.8231 | 240832.8272 | 228543.5428 | 231474.1888 | 233597.4558 | 248482.1391
| CO2 (kg) | 424838.0002 | 542706.4031 | 474833.7073 | 438656.7491 | 166029.004 | 502153.0815 | 175327.3223 | 392691.4757 | 558343.6763 | 139513.2155 | 755054.9214 | 573493.5641 | 549328.2831 | 555787.3761 | 566849.9037 | 653581.9823
| NOX (kg) | 748.4495 | 706.5336 | 791.7503 | 810.8011 | 142.6218 | 805.8353 | 151.622 | 716.0382 | 940.9603 | 184.5262 | 1297.2348 | 952.271 | 900.568 | 909.1449 | 905.9025 | 738.0587
| SO2 (kg) | 2857.2886 | 2997.5439 | 2611.504 | 2024.6454 | 1452.0973 | 3291.8312 | 1352.1964 | 1987.1622 | 2352.2093 | 370.1859 | 3671.1218 | 2339.0619 | 1311.3133 | 1465.9588 | 1276.9765 | 3030.4667
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.013 | 0.0085 | 0.0071 | 0.0075 | 0.0007 | 0.0062 | 0.0007 | 0.0081 | 0.0093 | 0.0016 | 0.0112 | 0.0092 | 0.0098 | 0.0103 | 0.0096 | 0.0107
| Water Environmental Factors (m3) | 353.6279 | 1022.48 | 19290.5 | 3601.12 | 8761.41 | 16416.6 | 8158 | 123.5718 | 2445.69 | 4889.43 | 845.0331 | 2431.92 | 861.6101 | 34766.5 | 838.9407 | 607.9948

## Picture
DOE Commercial Building Benchmark - Retail
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 80.65 | 4205.32
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 65.6 | 3420.57
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 43.5 | 2268.21
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 98.5 | 5136.07
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
INFIL_FRONT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 17.25 | 104.25 | 5435.89
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 18
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 12.75
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
FRONT_ENTRY_COOLING | Temperature | Through 12/31 | All | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2160 | 15120 | 788400
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 91 | 4745
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11