## Phase I
Project Home Again Phase I Addresses
[30 empty] | Outdoor Hobo H-08-032 |  |  | 385266 |  |  |  | Outside | Outside
Have Signed |  |  | Move In | [6 empty] | Floor area | Surface | Volume |  |  | Selling |  | CFM 50measured | CFM 50goal | Pass/Fail | ACH 50 | EqLA | ELA | Leak Ratio | Attic Pr. Diff. | Duct25-Total | Duct25-Out | Duct Leak | Pass/Fail |  | U10 Serial Numbers |  |  |  | HOBO | CR500s | HVAC | Air Flow | Air Pressure
Entergy Form | Name | Phone | Date | Plan | Category/Owners | Status | Lot | Address | Town/City | (ft2) | (ft2) | (ft3) | Occupied | BA Analysis | Price | HERS | CFM @ 50 Pa | CFM @ 50 Pa | 2.5 in2 | (cfm50/vol/hr) | (in2@10 Pa) | (in2@4 Pa) | (EqLA/surf/100) | Diff. @ 50 Pa | (CFM @ 25pa) | (CFM @ 25pa) | 5% goal | 5% | Test Date | TSTAT | MBR | 2nd Floor | Attic | Count |  | Installer | CFM | Pa
Yes | Yolanda Sanders | 210-887-1240 | 2009-04-11 | B4 |  |  | 1 | 1213 Mandolin St | New Orleans, 70122 | 1551 | 5078 | 21502 | yes | 2008 BAB 42% |  | 64 | 650 | 1270 | Pass | 1.8138 | 66.95 | 35.75 | 1.28 | 17 |  |  |  |  | 2009-02-12
Yes | Dwight West | 504-875-1848 | 2009-03-18 | H2 |  |  | 2 | 1207 Mandolin St | New Orleans, 70122 | 1016 | 3735 | 12526 | yes | 2008 BAB 43% |  | 67 | 852 | 934 | Pass | 4.0811 | 87.756 | 46.86 | 2.2811 | 8 |  |  |  |  | 2009-02-12
Yes | Darlene Laine | 225-329-4137 | 2009-02-13 | L2 |  | Constructed | 3 | 1201 Mandolin St. | New Orleans, 70122 | 1067 | 3844 | 12806 | yes | 2008 BAB 41% |  | 64 | 1083 | 961 | Fail | 5.0742 | 111.549 | 59.565 | 2.8174 | 14 |  |  |  |  | 2009-01-19
Yes | David Briant | 504-952-3087 | 2008-12-31 | L3 |  | Constructed | 4 | 4305 St. Bernard Ave | New Orleans, 70122 | 1377 | 4826 | 16636 | yes | 2008 BAB 41% |  | 64 | 1029 | 1207 | Pass | 3.7112 | 105.987 | 56.595 | 2.1322 | 8 |  |  |  |  | 2008-12-12
Yes but not signed | Kenneth Camp | 818-415-4852 | 2009-01-26 | B4 |  | Constructed | 5 | 4309 St. Bernard Ave | New Orleans, 70122 | 1551 | 5078 | 21502 | yes | 2008 BAB 42% |  | 64 | 1192 | 1270 | Pass | 3.3262 | 122.776 | 65.56 | 2.3474 | 15 | 192 | 80 | 10% |  | 2008-12-12
Yes | Edgar Williams | 504-256-5841 | 2008-12-23 | H2 |  | Constructed | 6 | 4313 St. Bernard Ave | New Orleans, 70122 | 1016 | 3735 | 12526 | yes | 2008 BAB 43% |  | 67 | 1049 | 934 | Fail | 5.0247 | 108.047 | 57.695 | 2.8086 | 22 |  |  |  |  | 2008-12-12
Yes | Jermaine Clark | 504-220-6394 | 2009-01-21 | B4 |  | Constructed | 7 | 4317 St. Bernard Ave | New Orleans, 70122 | 1551 | 5078 | 21502 | yes | 2008 BAB 42% |  | 64 | 1049 | 1270 | Pass | 2.9272 | 108.047 | 57.695 | 2.0658 | 14 |  |  |  |  | 2009-01-19
Yes, stopped receiving bills after Jan 2011 | Marion Brown | 504-491-7808 | 2009-03-20 | F3 |  | Constructed | 8 | 4321 St. Bernard Ave | New Orleans, 70122 | 1248 | 3791 | 20143 | yes | 2008 BAB 41% |  | 64 | 881 | 948 | Pass | 2.6242 | 90.743 | 48.455 | 2.3239 | 8 | 296 | 87 | 14.5% |  | 2009-01-19
Yes | Annie Ro-Varis | 504-390-5927 | 2009-05-28 | B4 |  | Constructed | 9 | 4325 St. Bernard Ave | New Orleans, 70122 | 1551 | 5078 | 21502 | yes | 2008 BAB 42% | 225370 | 64 | 962 | 1270 | Pass | 2.6844 | 99.086 | 52.91 | 1.8944 | 11 |  |  |  |  | 2009-01-19
Yes, stopped receiving bills after Jan 2011 | Vance Nimtz | 504-782-1046 | 2009-02-11 | L3 |  | Constructed | 10 | 4329 St. Bernard Ave | New Orleans, 70122 | 1377 | 4826 | 16636 | yes | 2008 BAB 41% | 233300 | 64 | 681 | 1207 | Pass | 2.4561 | 70.143 | 37.455 | 1.4111 | 8 |  |  |  |  | 2009-01-19
Yes, but not signed | Shannon Sheffield | 225-341-9674 | 2011-02-07 | B4 |  |  | 11 | 4333 St. Bernard Ave | New Orleans, 70122 | 1551 | 5078 | 21502 | yes | 2008 BAB 42% |  | 64 | 929 | 1270 | Pass | 2.5923 | 95.687 | 51.095 | 1.8295 | 10 |  |  |  |  | 2009-01-20
Yes, but not signed | Lynette Jordana | H:504-284-2928; W:504-592-0143 | 2009-04-07 | F3 |  |  | 12 | 4337 St. Bernard Ave | New Orleans, 70122 | 1248 | 3791 | 20143 | yes | 2008 BAB 41% |  | 64 | 1002 | 948 | Fail | 2.9847 | 103.206 | 55.11 | 2.6431 | 8 |  |  |  |  | 2009-01-20
Yes, stopped receiving bills after May 2011 | Brenda Brossett | 770-873-8573 | 2009-03-11 | H2 |  |  | 13 | 4341 St. Bernard Ave | New Orleans, 70122 | 1016 | 3735 | 12526 | yes | 2008 BAB 43% |  | 67 | 782 | 934 | Pass | 3.7458 | 80.546 | 43.01 | 2.0937 | 17 |  |  |  |  | 2009-01-20
Yes | Trevor Chase | mom Alva:817-542-2803; Dad Edgar: 504-330-2923 | 2009-08-26 | L3 |  |  | 14 | 4345 St. Bernard Ave | New Orleans, 70122 | 1377 | 4826 | 16636 | yes | 2008 BAB 41% |  | 64 | 754 | 1207 | Pass | 2.7194 | 77.662 | 41.47 | 1.5624 | 9 | 310 | 89 | 11.12% |  | 2009-01-20
Yes, but not signed | Judy Griffin | 504-975-2171 | 2009-10-14 | H2 |  |  | 15 | 1200 Owens Blvd. | New Orleans, 70122 | 1016 | 3735 | 12526 | yes | 2008 BAB 43% |  | 67 | 719 | 934 | Pass | 3.444 | 74.057 | 39.545 | 1.925 | 18 |  |  |  |  | 2009-02-11
Yes | Monchet Bridges | 504-913-8645 | 2010-06-04 | L3 |  |  | 16 | 1206 Owens Blvd. | New Orleans, 70122 | 1377 | 4826 | 16636 | yes | 2008 BAB 41% |  | 64 | 832 | 1207 | Pass | 3.0007 | 85.696 | 45.76 | 1.724 | 11 |  |  |  |  | 2009-02-11
Yes | Gaynell Baudy | 504-621-4976 | 2009-03-12 | L2 |  |  | 17 | 1212 Owens Blvd. | New Orleans, 70122 | 1067 | 3844 | 12806 | yes | 2008 BAB 41% |  | 64 | 732 | 961 | Pass | 3.4296 | 75.396 | 40.26 | 1.9043 | 11 | 253 | 66 | 11% |  | 2009-02-11
Yes | Heather Porter | 504-329-1382 | 2009-06-25 | H2 |  |  | 18 | 1218 Owens Blvd. | New Orleans, 70122 | 1016 | 3735 | 12526 | yes | 2008 BAB 43% |  | 67 | 923 | 934 | Pass | 4.4212 | 95.069 | 50.765 | 2.4712 | 16 |  |  |  |  | 2009-02-11
Yes | Jeannetta Roussell/William Broyard | 504-616-4055 | 2009-03-11 | H2 |  |  | D-1 | 4253 St. Bernard Ave | New Orleans, 70122 | 1016 | 3735 | 12526 | yes | 2008 BAB 43% |  | 67 | 749 | 934 | Pass | 3.5877 | 77.147 | 41.195 | 2.0054 | 11 | 180 | 69 | 11.5% |  | 2009-02-12
Yes | Terry Brown | 504-289-5955 | 2009-03-12 | H2 |  |  | D-2 | 4243 St. Bernard Ave | New Orleans, 70122 | 1016 | 3735 | 12526 | yes | 2008 BAB 43% |  | 67 | 720 | 934 | Pass | 3.4488 | 74.16 | 39.6 | 1.9277 | 17 |  |  |  |  | 2009-02-12
[9 empty] | highligted=received utility bills |  | green
no walk-through
Re-sent to Entergy
Multiple Disconnect Notices for:
4333 St Bernard Ave

## Phase II
Project Home Again Phase II Addresses
[26 empty] | Outdoor Hobo H-08-032 |  |  | 385266 |  |  |  | Outside | Outside
Have Signed |  |  | Move In |  |  |  | Floor area | Surface | Volume |  | HERS | Selling | CFM 50measured | CFM 50goal | Pass/Fail | ACH 50 | EqLA | ELA | Leak Ratio | Attic Pr. Diff. | Duct25-Total | Duct25-Out | Duct Leak | Pass/Fail |  | U10 Serial Numbers |  |  |  | HOBO | CR500s | HVAC | Air Flow | Air Pressure
Entergy Form | Name | Phone | Date | Plan | Address | Town/City | (ft2) | (ft2) | (ft3) | BA Analysis | Index | Price | CFM @ 50 Pa | CFM @ 50 Pa | 2.5 in2 | (cfm50/vol/hr) | (in2@10 Pa) | (in2@4 Pa) | (EqLA/surf/100) | Diff. @ 50 Pa | (CFM @ 25pa) | (CFM @ 25pa) | 5% goal | 5% | Test Date | TSTAT | MBR | 2nd Floor | Attic | Count |  | Installer | CFM | Pa
Yes, and sent March 13, 2012 | Diane Dilosa | 504-756-5852 | 2010-06-25 | Gertrude | 4310 Randolph Avenue | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 |  | 718 | 1086.75 | Pass | 2.6188 | 73.954 | 39.49 | 1.6517 | [5 empty] | 2009-02-12
Yes | Pebbles Martin | 504-473-7945 | 2010-02-18 | Gertrude | 5103 Eastern Street | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 |  |  | 1086.75 | Pass | 0 | 0 | 0 | 0 | [5 empty] | 2009-02-12
Yes | Wendell Leblanc | 504-231-9094 | 2010-06-25 | Gertrude | 5320 Wilton Drive | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 |  | 708 | 1086.75 | Pass | 2.5824 | 72.924 | 38.94 | 1.6287 |  | 199 |  |  |  | 2009-02-12
Yes, but not signed | Ruth Jackson | 504-450-0702 | 2011-02-01 | Gertrude | 4959 Miles Drive | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 |  | 748 | 1086.75 | Pass | 2.7283 | 77.044 | 41.14 | 1.7207 | [5 empty] | 2009-02-12
Yes | Linda Richardson | 504-701-0363 | 2010-01-13 | Gertrude | 4963 Painters Street | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 |  |  | 1086.75 | Pass | 0 | 0 | 0 | 0 | [5 empty] | 2009-02-12
Yes | Runda Clark | 504-344-4992 | 2009-12-09 | Gertrude | 1463 Filmore Avenue | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 |  | 710 | 1086.75 | Pass | 2.5897 | 73.13 | 39.05 | 1.6333 | [5 empty] | 2009-02-12
Yes | Emmanuel and Samantha Ilechuku | E:504-905-3630; S:504-799-5897 | 2010-07-08 | Gertrude | 4951 Piety Drive | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 |  | 713 | 1086.75 | Pass | 2.6006 | 73.439 | 39.215 | 1.6402 | [5 empty] | 2009-02-12
Yes | Prudence Grissom | 504-813-2286 | 2009-09-17 | Templeton | 5705 Wildair Drive | New Orleans, 70122 | 1213 | 5006 | 14928 | 46% | 68 |  | 751 | 1251.5 | Pass | 3.0185 | 77.353 | 41.305 | 1.5002 | [5 empty] | 2009-02-12
Yes | Chanda Hayes | 504-258-9771 | 2010-01-04 | Templeton | 5749 Wildair Drive | New Orleans, 70122 | 1213 | 5006 | 14928 | 46% | 68 |  | 710 | 1251.5 | Pass | 2.8537 | 73.13 | 39.05 | 1.4183 | [5 empty] | 2009-02-12
Yes | N'Kenge and Akbar Carriere | 504-756-2061 (N'k) | 2009-10-02 | Templeton | 4975 St. Roch Avenue | New Orleans, 70122 | 1213 | 5006 | 14928 | 46% | 68 |  | 866 | 1251.5 | Pass | 3.4807 | 89.198 | 47.63 | 1.7299
Yes | Alayna and Eric Maberry | A: 678-865-9321 E: 678-865-9318 | 2010-11-30 | Templeton | 4900 Kendall Drive | New Orleans, 70122 | 1213 | 5006 | 14928 | 46% | 68 |  | 779 | 1251.5 | Pass | 3.131 | 80.237 | 42.845 | 1.5561
Yes | Nichole Wilson | 504-473-7945 | 2009-11-16 | Camille | 5515 Wickfield Drive | New Orleans, 70122 | 1224 | 5256 | 15300 | 42% | 69 |  |  | 1314 | Pass | 0 | 0 | 0 | 0
[6 empty] | highligted=received utility bills |  | orange
Re-sent to Entergy
Multiple Disconnect Notices for:
4900 Kedall Drive
Note on B8: Philip G Kerrigan Jr: Entergy Account is in Ralph Martin's name
Note on B9: Philip G Kerrigan Jr: PHA still owns house, will be part of project

## Phase III
Project Home Again Phase III Addresses
[26 empty] | Outdoor Hobo H-08-032 |  |  | 385266 |  |  |  | Outside | Outside
Have Signed |  |  | Move In |  |  |  | Floor area | Surface | Volume |  | HERS | Selling | CFM 50measured | CFM 50goal | Pass/Fail | ACH 50 | EqLA | ELA | Leak Ratio | Attic Pr. Diff. | Duct25-Total | Duct25-Out | Duct Leak | Pass/Fail |  | U10 Serial Numbers |  |  |  | HOBO | CR500s | HVAC | Air Flow | Air Pressure
Entergy Form | Name | Phone | Date | Plan | Address | Town/City | (ft2) | (ft2) | (ft3) | BA Analysis | Index | Price | CFM @ 50 Pa | CFM @ 50 Pa | 2.5 in2 | (cfm50/vol/hr) | (in2@10 Pa) | (in2@4 Pa) | (EqLA/surf/100) | Diff. @ 50 Pa | (CFM @ 25pa) | (CFM @ 25pa) | 5% goal | 5% | Test Date | TSTAT | MBR | 2nd Floor | Attic | Count |  | Installer | CFM | Pa
Yes | Jimmie Turner Jr. | 504-451-1450 | 2011-10-21 | Templeton | 5503 Wilton Drive | New Orleans, 70122 | 1213 | 5006 | 14928 |  | 66
| PHA Office | 504-529-3522 | 2010-12-27 | Templeton | 5506 Wickfield Drive | New Orleans, 70122 | 1213 | 5006 | 14928 |  | 66
| N/A |  |  | Templeton | 5514 Wilton | New Orleans, 70122 | 1213 | 5006 | 14928 |  | 66
Yes, but not signed | Leslie Clark | 504-508-1658 | 2010-12-16 | Gertrude | 5712 Wickfield | New Orleans, 70122 | 1316 | 4347 | 16450 |  | 67
| N/A |  |  | Louise | 5716 Wickfield | New Orleans, 70122 |  |  |  |  | 68
Yes, but not signed | Justin Leggett | 504-261-9249 | 2010-12-20 | Gertrude | 5720 Wickfield | New Orleans, 70122 | 1316 | 4347 | 16450 |  | 67
Yes, but not signed | Janice Lecesne | 504-251-4371 | 2010-05-14 | Louise | 5721 Wildair | New Orleans, 70122 | 1105 | 4539 | 13798 |  | 68
Yes | Gaisha T Page | 504-994-1348 | 2010-03-30 | Louise | 5729 Wilton | New Orleans, 70122 | 1105 | 4539 | 13798 |  | 68
Yes, but not signed | Sean Fogarty | 504-252-6478 | 2010-12-20 | Louise | 5732 Wickfield | New Orleans, 70122 | 1105 | 4539 | 13798 |  | 68
Yes | Angela Isla | 504-812-7821 | 2010-10-15 | Gertrude | 5772 Wickfield | New Orleans, 70122 | 1316 | 4347 | 16450 |  | 67
Yes | Nanette James | 504-390-9921 | 2010-03-15 | Gertrude | 5773 Wildair | New Orleans, 70122 | 1316 | 4347 | 16450 |  | 67
Yes | Denise Matthews | 504-975-8891 | 2010-10-29 | Gertrude | 6056 Wickfield | New Orleans, 70122 | 1316 | 4347 | 16450 |  | 67
Yes | Tracy Brown | H:504-272-0170 (no cell, no VM) | 2010-05-17 | Camille | 5541 Pasteur | New Orleans, 70122 | 1224 | 5256 | 15300 |  | 68
[6 empty] | highligted=received utility bills |  | light blue
no walk through
re-sent to Entergy
Lousie plan not analyzed yet. Phil 7/29/2010
EGUSA File setup - PK 12/28/2011
Multiple Disconnect Notices for:

## Phase IV
| Project Home Again Phase IV Addresses |  |  |  |  | Highlighted= received utility bills
[26 empty] | Outdoor Hobo H-08-032 |  |  | 385266 |  |  |  | Outside | Outside
Have Signed |  |  | Move In |  |  |  | Floor area | Surface | Volume |  | HERS | Selling | CFM 50measured | CFM 50goal | Pass/Fail | ACH 50 | EqLA | ELA | Leak Ratio | Attic Pr. Diff. | Duct25-Total | Duct25-Out | Duct Leak | Pass/Fail |  | U10 Serial Numbers |  |  |  | HOBO | CR500s | HVAC | Air Flow | Air Pressure
Entergy Form | Name | Phone | Date | Plan | Address | Town/City | (ft2) | (ft2) | (ft3) | BA Analysis | Index | Price | CFM @ 50 Pa | CFM @ 50 Pa | 2.5 in2 | (cfm50/vol/hr) | (in2@10 Pa) | (in2@4 Pa) | (EqLA/surf/100) | Diff. @ 50 Pa | (CFM @ 25pa) | (CFM @ 25pa) | 5% goal | 5% | Test Date | TSTAT | MBR | 2nd Floor | Attic | Count |  | Installer | CFM | Pa
Yes | Alison Alonso | 985-264-7618 | 2011-10-21 | Alexander | 5750 Pasteur Bl | New Orleans, 70122 |  |  |  |  | 69
| Oliver and Mary Crumes | 504-261-1227 | 2011-07-21 | Alexander | 5752 Wildair Dr. | New Orleans, 70122 |  |  |  |  | 69
no form, PHA needs to check | Constanza Porche | 504-575-1582; 504-942-9571 | 2011-09-13 | Alexander | 5764 Wilton Dr. | New Orleans, 70122 |  |  |  |  | 69
Yes | Yolanda Stalbert | 504-222-5514 | 2011-09-16 | Alexander | 5764 Wickfield Dr. | New Orleans, 70122 |  |  |  |  | 69
Yes | Thomas and Beverly Case | T:504-931-4342 B:504-975-4342 | 2011-10-05 | Alexander | 5717 Wildair Dr. | New Orleans, 70122 |  |  |  |  | 69
| Victor and Victoria Crespo | Olga Espinal: 504-231-8598; Victor: 504-452-5858; Vicki: 504-812-5686 | 2011-04-05 | Alexander | 6050 Wildair Dr. | New Orleans, 70122 |  |  |  |  | 69
| N/A (soon!) |  |  | Alexander | 5740 Wilton Dr. | New Orleans, 70122 |  |  |  |  | 69
| John Gibson | 504-415-6674 | 2011-08-02 | Templeton | 5511 Wilton Dr. | New Orleans, 70122 |  |  |  |  | 67
| Jason Jones | 504-222-0043 | 2011-06-30 | Louise | 6000 Wickfield Dr. | New Orleans, 70122 |  |  |  |  | 67
Yes | Debra Frazier | 504-495-1656 | 2011-05-10 | Louise | 5773 Wickfield Dr. | New Orleans, 70122 |  |  |  |  | 67
| Todd Soublet | 504-704-9828 | 2011-07-21 | Templeton | 5525 Pasteur Bl | New Orleans, 70122 |  |  |  |  | 67
| Barbara Bolds | C:504-710-6648 W:504-678-0078 | 2011-01-28 | Camille | 5762 Cameron Bl | New Orleans, 70122 |  |  |  |  | 68
no form, newer mayve hasn't come throught, GCE should hae original copy | Larry and Denise Baham | L:225-268-6239 D:225-620-1286 | 2011-10-13 | Templeton | 5507 Wickfield Dr. | New Orleans, 70122 |  |  |  |  | 67
| Irvin and Alice Porter | Alice:504-400-4604, Alvin:504-388-2858 I:504-390-2989 | 2011-12-06 | Templeton | 5506 Wilton Dr. | New Orleans, 70122 |  |  |  |  | 67
| Javonka Brown | 504-274-8109 | 2012-01-27 | Camille | 5765 Wilton Dr. | New Orleans, 70122 |  |  |  |  | 68
Yes | Richard and Patricia Little | P:504-975-5652 R:504-338-7911 | 2011-07-01 | Camille | 5736 Wickfield Dr. | New Orleans, 70122 |  |  |  |  | 68
| Alice Spiller | 504-957-5522 | 2011-04-05 | Templeton | 5516 Wickfield Dr. | New Orleans, 70122 |  |  |  |  | 67
Yes | Corliss Gaines | 504-415-9852 | 2011-05-26 | Camille | 5502 Wickfield Dr. | New Orleans, 70122 |  |  |  |  | 68
| N/A |  |  | Louise | 6058 Wildair Dr. | New Orleans, 70122 |  |  |  |  | 67
no form yet | N/A (soon!) |  |  | Louise | 5761 Cameron Bl | New Orleans, 70122 |  |  |  |  | 67
Yes | Ronald Bazile | 504-982-3467 | 2011-10-21 | Templeton | 5513 Wickfield Dr. | New Orleans, 70122 |  |  |  |  | 67
Yes | Ruth Mercadel | 504-606-5125 | 2011-04-28 | Alexander | 6052 Wickfield Dr. | New Orleans, 70122 |  |  |  |  | 69
| Arthur and Denise Batiste | A:504-701-6115; D:504-296-7982 | 2011-04-05 | Camille | 6017 Wickfield Dr | New Orleans, 70122 |  |  |  |  | 68
Yes | Stephanie and Johnny Roberts | SC:504-274-9565 JC:504-274-9111 | 2011-11-16 | Louise | 5718 Pasteur Bl. | New Orleans, 70122 |  |  |  |  | 67
| N/A |  |  | Alexander | 5713 Pasteur Bl. | New Orleans, 70122 |  |  |  |  | 69
Multiple Disconnect Notices for:
6052 Wickfield Dr
Note on B13: Philip G Kerrigan Jr: Mr Gibson has declined to share utility bills

## Phase VI
Project Home Again Phase VI Addresses
[26 empty] | Outdoor Hobo H-08-032 |  |  | 385266 |  |  |  | Outside | Outside
|  | Move In |  |  |  | Floor area | Surface | Volume |  | HERS | Selling | CFM 50measured | CFM 50goal | Pass/Fail | ACH 50 | EqLA | ELA | Leak Ratio | Attic Pr. Diff. | Duct25-Total | Duct Leak | Duct25-Out | Duct Leak | Pass/Fail |  | U10 Serial Numbers |  |  |  | HOBO | CR500s | HVAC | Air Flow | Air Pressure
Name | Phone | Date | Plan | Address | Town/City | (ft2) | (ft2) | (ft3) | BA Analysis | Index | Price | CFM @ 50 Pa | CFM @ 50 Pa | 2.5 in2 | (cfm50/vol/hr) | (in2@10 Pa) | (in2@4 Pa) | (EqLA/surf/100) | Diff. @ 50 Pa | (CFM @ 25pa) | Total % | (CFM @ 25pa) | 5% goal | 5% | Test Date | TSTAT | MBR | 2nd Floor | Attic | Count |  | Installer | CFM | Pa
|  |  | Alexander | 5421 Lafaye St. | New Orleans, 70122 | 1316 | 4429 | 16492 |  | 36 |  | 660 | 1107 | Pass | 2.4012 | 67.98 | 36.3 | 1.4902 |  | 43 | 5.375% | 10 | 1.25%
|  |  | Alexander | 5428 Baccich St. | New Orleans, 70122 | 1316 | 4429 | 16492 |  | 38 |  | 748 | 1107 | Pass | 2.7213 | 77.044 | 41.14 | 1.6889 |  | 55 | 6.875% | 10 | 1.25%
|  |  | Alexander | 6322 Franklin Ave. | New Orleans, 70122 | 1316 | 4429 | 16492 |  | 35 |  | 677 | 1107 | Pass | 2.463 | 69.731 | 37.235 | 1.5286 |  | 40 | 5% | 10 | 1.25%
|  |  | Alexander | 2553 Athis St. | New Orleans, 70122 | 1316 | 4429 | 16492 |  | 66 |  | 701 | 1107 | Pass | 2.5503 | 72.203 | 38.555 | 1.5828 |  | 161 | 20.12% | 10 | 1.25%
|  |  | Alexander | 2530 Pressburg St. | New Orleans, 70122 | 1316 | 4429 | 16492 |  | 66 |  | 650 | 1107 | Pass | 2.3648 | 66.95 | 35.75 | 1.4676 |  | 103 | 12.88% | 29 | 3.625%
|  |  | Cynthia | 5439 Eads St. | New Orleans, 70122 | 1305 | 4357 | 15509 |  | 38 |  | 799 | 1089 | Pass | 3.0911 | 82.297 | 43.945 | 1.8338 |  | 178 | 22.25% | 15 | 1.875%
|  |  | Cynthia | 5500 Baccich St. | New Orleans, 70122 | 1305 | 4357 | 15509 |  | 36 |  | 668 | 1089 | Pass | 2.5843 | 68.804 | 36.74 | 1.5332 |  | 173 | 21.62% | 12 | 1.5%
|  |  | Cynthia | 5500 Eads St. | New Orleans, 70122 | 1305 | 4357 | 15509 |  | 40 |  | 703 | 1089 | Pass | 2.7197 | 72.409 | 38.665 | 1.6135 |  | 171 | 21.38% | 35 | 4.375%
|  |  | Cynthia | 2501 Pressburg St. | New Orleans, 70122 | 1305 | 4357 | 15509 |  | 66 |  | 776 | 1089 | Pass | 3.0021 | 79.928 | 42.68 | 1.781 |  | 132 | 16.5% | 11 | 1.375%
|  |  | Helen | 5607 Baccich St. | New Orleans, 70122 | 1051 | 3845 | 12687 |  | 31 |  | 594 | 961 | Pass | 2.8092 | 61.182 | 32.67 | 1.5449 |  | 197 | 24.62% | 11 | 1.375%
|  |  | Helen | 6040 Painters St. | New Orleans, 70122 | 1051 | 3845 | 12687 |  | 32 |  | 716 | 961 | Pass | 3.3861 | 73.748 | 39.38 | 1.8622 |  | 142 | 17.75% | 11 | 1.375%
|  |  | Rose | 5607 Eads St. | New Orleans, 70122 | 1316 | 4097 | 15168 |  | 66 |  | 619 | 1024 | Pass | 2.4486 | 63.757 | 34.045 | 1.5109 |  | 101 | 12.62% | 10 | 1.25%
|  |  | Rose | 2518 Pressburg St. | New Orleans, 70122 | 1316 | 4097 | 15168 |  | 67 |  | 752 | 1024 | Pass | 2.9747 | 77.456 | 41.36 | 1.8355 |  | 122 | 15.25% | 10 | 1.25%
|  |  | Rose | 2515 Mendez St. | New Orleans, 70122 | 1316 | 4097 | 15168 |  | 67 |  | 550 | 1024 | Pass | 2.1756 | 56.65 | 30.25 | 1.3424 |  | 121 | 15.12% | 10 | 1.25%
|  |  | Rose | 5916 Painters St. | New Orleans, 70122 | 1316 | 4097 | 15168 |  | 69 |  | 683 | 1024 | Pass | 2.7017 | 70.349 | 37.565 | 1.6671 |  | 189 | 23.62% | 15 | 1.875%
|  |  | Alexander | 5513 Baccich St. | New Orleans, 70122 | 1316 | 4429 | 16492 |  | 65 |  | 765 | 1107 | Pass | 2.7832 | 78.795 | 42.075 | 1.7273 |  |  | 0% | 14 | 1.75%
|  |  | Helen | 5623 Arts St. | New Orleans, 70122 | 1051 | 3845 | 12687 |  | 64 |  | 575 | 961 | Pass | 2.7193 | 59.225 | 31.625 | 1.4954 |  |  | 0% | 10 | 1.25%
|  |  | Cynthia | 5840 Eads St. | New Orleans, 70122 | 1305 | 4357 | 15509 |  | 65 |  | 610 | 1089 | Pass | 2.3599 | 62.83 | 33.55 | 1.4 |  |  | 0% | 33 | 4.125%
|  |  | Rose | 6116 Baccich St | New Orleans, 70122 | 1316 | 4097 | 15168 |  | 66 |  | 896 | 1024 | Pass | 3.5443 | 92.288 | 49.28 | 2.187 |  |  | 0% | 11 | 1.375%
|  |  | Helen | 6318 Franklin | New Orleans, 70122 | 1051 | 3845 | 12687 |  | 64 |  | 673 | 961 | Pass | 3.1828 | 69.319 | 37.015 | 1.7503 |  |  | 0% | 15 | 1.875%
|  |  |  | 6009 Wildair Drive | 101st House!!!!
|  |  |  | AVERAGES | [7 empty] | 686.4 |  |  | 2.6929 | 70.6992 | 37.752 | 1.6188 |  |  | 16.07% | 13.9333 | 1.713%
35.25%
Note on K5: Philip G Kerrigan Jr: These are the confirmed HERS Ratings from E3, the local rater.

## Phase V
Project Home Again Phase V Addresses
[27 empty] | Outdoor Hobo H-08-032 |  |  | 385266 |  |  |  | Outside | Outside
|  | Move In |  |  |  | Floor area | Surface | Volume |  | HERS | Selling |  | CFM 50measured | CFM 50goal | Pass/Fail | ACH 50 | EqLA | ELA | Leak Ratio | Attic Pr. Diff. | Duct25-Total | Duct Leak | Duct25-Out | Duct Leak | Pass/Fail |  | U10 Serial Numbers |  |  |  | HOBO | CR500s | HVAC | Air Flow | Air Pressure
Name | Phone | Date | Plan | Address | Town/City | (ft2) | (ft2) | (ft3) | BA Analysis | Index | Price |  | CFM @ 50 Pa | CFM @ 50 Pa | 2.5 in2 | (cfm50/vol/hr) | (in2@10 Pa) | (in2@4 Pa) | (EqLA/surf/100) | Diff. @ 50 Pa | (CFM @ 25pa) | Total % | (CFM @ 25pa) | 5% goal | 5% | Test Date | TSTAT | MBR | 2nd Floor | Attic | Count |  | Installer | CFM | Pa
|  |  | 3B | 2655 New York Street | New Orleans, 70122 | 1344 | 4311 | 16343 |  | 65 |  |  | 635 | 1078 | Pass | 2.3313 | 65.405 | 34.925 | 1.473 |  | 35 | 4.375% | 10 | 1.25%
|  |  | 3A | 6003 Eads Street | New Orleans, 70122 | 1248 | 4083 | 14688 |  | 34 |  | PVs | 628 | 1021 | Pass | 2.5654 | 64.684 | 34.54 | 1.5381 |  | 187 | 23.38% | 13 | 1.625%
|  |  | 3A | 6002 Baccich Street | New Orleans, 70122 | 1248 | 4083 | 14688 |  | 34 |  | PVs | 617 | 1021 | Pass | 2.5204 | 63.551 | 33.935 | 1.5111 |  | 160 | 20% | 12 | 1.5%
|  |  | 2A | 6226 Eads Street | New Orleans, 70122 | 1063 | 3563 | 12327 |  | 30 |  |  | 674 | 891 | Pass | 3.2806 | 69.422 | 37.07 | 1.8917 |  | 126 | 15.75% | 10 | 1.25%
|  |  | 3B | 2666 Robert E Lee Blvd | New Orleans, 70122 | 1344 | 4311 | 16343 |  | 65 |  |  | 555 | 1078 | Pass | 2.0376 | 57.165 | 30.525 | 1.2874 |  | 121 | 15.12% | 11 | 1.375%
|  |  | 2B | 6226 Lafaye Street | New Orleans, 70122 | 1120 | 3885 | 12718 |  | 30 |  |  | 470 | 971 | Pass | 2.2173 | 48.41 | 25.85 | 1.2098 |  | 81 | 10.12% | 10 | 1.25%
|  |  | 3B | 6103 Lafaye Street | New Orleans, 70122 | 1344 | 4311 | 16343 |  | 34 |  |  | 611 | 1078 | Pass | 2.2432 | 62.933 | 33.605 | 1.4173 |  | 51 | 6.375% | 10 | 1.25%
|  |  | 3A | 2719 Madrid Street | New Orleans, 70122 | 1248 | 4083 | 14688 |  | 65 |  |  | 690 | 1021 | Pass | 2.8186 | 71.07 | 37.95 | 1.6899 |  | 165 | 20.62% | 12 | 1.5%
|  |  | 3B | 6027-31 Eads Street | New Orleans, 70122 | 1344 | 4311 | 16343 |  | 34 |  |  | 525 | 1078 | Pass | 1.9274 | 54.075 | 28.875 | 1.2178 |  | 80 | 10% | 10 | 1.25%
|  |  | 3A | 5912-18 Eads Street | New Orleans, 70122 | 1248 | 4083 | 14688 |  | 34 |  |  | 450 | 1021 | Pass | 1.8382 | 46.35 | 24.75 | 1.1021 |  | 138 | 17.25% | 15 | 1.875%
[13 empty] | 585.5 |  |  | 2.378 | 60.3065 | 32.2025 | 1.4338 |  |  | 14.3% | 11.3 | 1.412%
42.65%
Note on K5: Philip G Kerrigan Jr: These are the confirmed HERS Ratings from E3, the local rater.

## Study Houses
Dehumidification Study Addresses
[27 empty] | Outdoor Hobo H-08-032 |  |  | 385266 |  |  |  | Outside | Outside
| Currently |  |  |  | Move In |  |  |  | Floor area | Surface | Volume |  | HERS | CFM 50measured | CFM 50goal | Pass/Fail | ACH 50 | EqLA | ELA | Leak Ratio | Attic Pr. Diff. | Duct25-Total | Duct25-Out | Duct Leak | Pass/Fail |  | U10 Serial Numbers |  |  |  | HOBO | CR500s | HVAC | Air Flow | Air Pressure
Phase | Receving Bills | Have Entergy Form? | Name | Phone | Date | Plan | Address | Town/City | (ft2) | (ft2) | (ft3) | BA Analysis | Index | CFM @ 50 Pa | CFM @ 50 Pa | 2.5 in2 | (cfm50/vol/hr) | (in2@10 Pa) | (in2@4 Pa) | (EqLA/surf/100) | Diff. @ 50 Pa | (CFM @ 25pa) | (CFM @ 25pa) | 5% goal | 5% | Test Date | TSTAT | MBR | 2nd Floor | Attic | Count |  | Installer | CFM | Pa
II | Yes | Yes | Prudence Grissom | 504-813-2286 | 2009-09-17 | Templeton | 5705 Wildair Drive | New Orleans, 70122 | 1213 | 5006 | 14928 | 46% | 68 | 751 | 1251.5 | Pass | 3.0185 | 77.353 | 41.305 | 1.5002 | [5 empty] | 2009-02-12
II | No | no copies of form | Diane Dilosa | 504-756-5852 | 2010-06-25 | Gertrude | 4310 Randolph Avenue | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 | 718 | 1086.75 | Pass | 2.6188 | 73.954 | 39.49 | 1.6517 | [5 empty] | 2009-02-12
II | No | Yes, but not signed | Ruth Jackson | 504-450-0702 | 2011-02-01 | Gertrude | 4959 Miles Drive | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 | 748 | 1086.75 | Pass | 2.7283 | 77.044 | 41.14 | 1.7207 | [5 empty] | 2009-02-12
II | No | Yes, resent to Entergy on 2/12/12 | Alayna and Eric Maberry | A: 678-865-9321 E: 678-865-9318 | 2010-11-30 | Templeton | 4900 Kendall Drive | New Orleans, 70122 | 1213 | 5006 | 14928 | 46% | 68 | 779 | 1251.5 | Pass | 3.131 | 80.237 | 42.845 | 1.5561
II | Yes | Yes | Emmanuel and Samantha Ilechuku | E:504-905-3630; S:504-799-5897 | 2010-07-08 | Gertrude | 4951 Piety Drive | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 | 713 | 1086.75 | Pass | 2.6006 | 73.439 | 39.215 | 1.6402 | [5 empty] | 2009-02-12
II | Yes | Yes | Runda Clark | 504-344-4992 | 2009-12-09 | Gertrude | 1463 Filmore Avenue | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 | 710 | 1086.75 | Pass | 2.5897 | 73.13 | 39.05 | 1.6333 | [5 empty] | 2009-02-12
II | Yes | Yes | Linda Richardson | 504-701-0363 | 2010-01-13 | Gertrude | 4963 Painters Street | New Orleans, 70122 | 1316 | 4347 | 16450 | 45% | 68 |  | 1086.75 | Pass | 0 | 0 | 0 | 0 | [5 empty] | 2009-02-12
II | Yes | Yes | Nichole Wilson | 504-473-7945 | 2009-11-16 | Camille | 5515 Wickfield Drive | New Orleans, 70122 | 1224 | 5256 | 15300 | 42% | 69 |  | 1314 | Pass | 0 | 0 | 0 | 0
II | Yes | Yes | Chanda Hayes | 504-258-9771 | 2010-01-04 | Templeton | 5749 Wildair Drive | New Orleans, 70122 | 1213 | 5006 | 14928 | 46% | 68 | 710 | 1251.5 | Pass | 2.8537 | 73.13 | 39.05 | 1.4183 | [5 empty] | 2009-02-12
IV | No | Will be getting bills | Oji Alexander |  |  | Alexander | 1401 Pressburg | New Orleans, 70122 | 1316 | 4347 | 16450
IV | Yes | Yes | Thomas and Beverly Case | T:504-931-4342 B:504-975-4342 | 2011-10-05 | Alexander | 5717 Wildair Dr. | New Orleans, 70122 | 1316 | 4347 | 16450 |  | 69
IV | No | no form, PHA needs to check | Constanza Porche | 504-575-1582; 504-942-9571 | 2011-09-13 | Alexander | 5764 Wilton Dr. | New Orleans, 70122 | 1316 | 4347 | 16450 |  | 69
IV | No | Yes, resent to Entergy on 2/12/12 | Debra Frazier | 504-495-1656 | 2011-05-10 | Louise | 5773 Wickfield Dr. | New Orleans, 70122 | 1015 | 4539 | 13798 |  | 67
IV | No | no form, newer maybe hasn't come through, GCE may have original copy | Larry and Denise Baham | L:225-268-6239 D:225-620-1286 | 2011-10-13 | Templeton | 5507 Wickfield Dr. | New Orleans, 70122 | 1213 | 5006 | 14928 |  | 67
IV | No | no form yet | N/A (soon!) |  |  | Louise | 5761 Cameron Bl | New Orleans, 70122 | 1015 | 4539 | 13798 |  | 67
IV | Yes | Yes | Stephanie and Johnny Roberts | SC:504-274-9565 JC:504-274-9111 | 2011-11-16 | Louise | 5718 Pasteur Bl. | New Orleans, 70122 | 1015 | 4539 | 13798 |  | 67
III | No | Yes, resent to Entergy on 2/12/12 | Angela Isla | 504-812-7821 | 2010-10-15 | Gertrude | 5772 Wickfield | New Orleans, 70122 | 1316 | 4347 | 16450 |  | 67
IV | Yes | Yes | Ruth Mercadel | 504-606-5125 | 2011-04-28 | Alexander | 6052 Wickfield Dr. | New Orleans, 70122 | 1316 | 4347 | 16450 |  | 69
III | Yes | Yes | Jimmie Turner Jr. | 504-451-1450 | 2011-10-21 | Templeton | 5503 Wilton Drive | New Orleans, 70122 | 1213 | 5006 | 14928 |  | 66
Note on D9: Philip G Kerrigan Jr: PHA still owns house, will be part of project
I did receive a disconnect notice for 6052 Wickfield Dr in Feb 2012

## Main Graphs
|  | 1207 Mandolin St | 4313 St. Bernard Ave | 1218 Owens Blvd | 4253 St. Bernard Ave | 4243 St. Bernard Ave | 1212 Owens Blvd | 1201 Mandolin St | 4305 St. Bernard Ave | 4329 St. Bernard Ave | 4317 St. Bernard Ave | 4345 St. Bernard Ave | not used in graph because of incomplete data
|  | Plan H2 | Plan H2 | Plan H2 | Plan H2 | Plan H2 | Plan L2 | Plan L2 | Plan L3 | Plan L3 | Plan B4 | Plan L3
|  | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual | Actual
Month on bill | Date | Actual kWh | Actual kWh | Actual kWh | Actual kWh | Actual kWh | Actual kWh | Actual kWh | Actual kWh | Actual kWh | Actual kWh | Actual kWh
2009-07-01 | 06/10 - 07/09 | 1153 | 1148 | 421 | 1436 | 1620 | 1626 | 2527 | 1646 | 1994 | 2396 | 0
2009-08-01 | 07/10 - 08/09 | 1167 | 1179 | 1426 | 933 | 1449 | 2017 | 2074 | 1812 | 1922 | 2383 | 0 |  | 0 | 25000
2009-09-01 | 08/10 - 09/09 | 1029 | 1029 | 989 | 754 | 1240 | 1674 | 1619 | 1636 | 1672 | 1989 | 229
2009-10-01 | 09/10 - 10/09 | 976 | 790 | 952 | 711 | 1470 | 1723 | 1675 | 1460 | 1410 | 1915 | 668 |  | 0 | 37500 | 150%
2009-11-01 | 10/10 - 11/09 | 828 | 538 | 706 | 825 | 1231 | 1401 | 1273 | 1267 | 1269 | 1306 | 474
2009-12-01 | 11/10 - 12/09 | 1031 | 548 | 807 | 1038 | 951 | 1365 | 1582 | 1208 | 1402 | 1382 | 562
2010-01-01 | 12/10 - 01/09 | 1210 | 897 | 1222 | 1587 | 1394 | 1880 | 2250 | 2464 | 1716 | 1807 | 1251
2010-02-01 | 01/10 - 02/09 | 985 | 608 | 869 | 1171 | 1001 | 1363 | 1511 | 1591 | 1280 | 1431 | 821
2010-03-01 | 02/10 - 03/09 | 948 | 653 | 1037 | 1078 | 1041 | 1443 | 1718 | 1533 | 1280 | 1300 | 814
2010-04-01 | 03/10 - 04/09 | 769 | 439 | 1408 | 962 | 842 | 1288 | 1088 | 1778 | 1020 | 1206 | 819
2010-05-01 | 04/10 - 05/09 | 932 | 735 | 1687 | 833 | 1035 | 1758 | 1313 | 1425 | 940 | 1730 | 1124
2010-06-01 | 05/10 - 06/09 | 1013 | 1007 | 1936 | 1347 | 1208 | 2324 | 1678 | 1619 | 1170 | 2191 | 1527
2010-07-01 | 06/10 - 07/12 | 1239 | 1153 | 2340 | 1428 | 1384 | 2520 | 1965 | 2051 | 1414 | 2558 | 1809
| Total | 12041 | 9571 | 13460 | 12675 | 14482 | 22382 | 22273 | 21490 | 18489 | 23594 | 10098
|  | Predicted (EGUSA) | Predicted (EGUSA) | Predicted (EGUSA) | Predicted (EGUSA) | Predicted (EGUSA) | Predicted (EGUSA) | Predicted (EGUSA) | Predicted (EGUSA) | Predicted (EGUSA) | Predicted (EGUSA) | Predicted (EGUSA)
Month on bill | Date | EGUSA kWh | EGUSA kWh | EGUSA kWh | EGUSA kWh | EGUSA kWh | EGUSA kWh | EGUSA kWh | EGUSA kWh | EGUSA kWh | EGUSA kWh | EGUSA kWh
2009-07-01 | 06/10 - 07/09 | 815 | 815 | 815 | 815 | 815 | 887 | 887 | 1051 | 1051 | 1174 | 1051
2009-08-01 | 07/10 - 08/09 | 880 | 880 | 880 | 880 | 880 | 950 | 950 | 1123 | 1123 | 1255 | 1123
2009-09-01 | 08/10 - 09/09 | 854 | 854 | 854 | 854 | 854 | 924 | 924 | 1095 | 1095 | 1221 | 1095
2009-10-01 | 09/10 - 10/09 | 649 | 649 | 649 | 649 | 649 | 746 | 746 | 888 | 888 | 989 | 888
2009-11-01 | 10/10 - 11/09 | 536 | 536 | 536 | 536 | 536 | 654 | 654 | 791 | 791 | 863 | 791
2009-12-01 | 11/10 - 12/09 | 526 | 526 | 526 | 526 | 526 | 659 | 659 | 783 | 783 | 859 | 783
2010-01-01 | 12/10 - 01/09 | 855 | 855 | 855 | 855 | 855 | 1002 | 1002 | 1181 | 1181 | 1250 | 1181
2010-02-01 | 01/10 - 02/09 | 827 | 827 | 827 | 827 | 827 | 962 | 962 | 1140 | 1140 | 943 | 1140
2010-03-01 | 02/10 - 03/09 | 600 | 600 | 600 | 600 | 600 | 723 | 723 | 862 | 862 | 915 | 862
2010-04-01 | 03/10 - 04/09 | 564 | 564 | 564 | 564 | 564 | 694 | 694 | 830 | 830 | 928 | 830
2010-05-01 | 04/10 - 05/09 | 593 | 593 | 593 | 593 | 593 | 698 | 698 | 831 | 831 | 1128 | 831
2010-06-01 | 05/10 - 06/09 | 752 | 752 | 752 | 752 | 752 | 853 | 853 | 1008 | 1008 | 1174 | 1008
2010-07-01 | 06/10 - 07/12 | 871 | 871 | 871 | 871 | 871 | 887 | 887 | 1051 | 1051 | 1255 | 1051
| Total | 8451 | 8451 | 8451 | 8451 | 8451 | 10639 | 10639 | 12634 | 12634 | 13954 | 12634
Month on bill | Date
2009-07-01 | 06/10 - 07/09
2009-08-01 | 07/10 - 08/09
2009-09-01 | 08/10 - 09/09
2009-10-01 | 09/10 - 10/09
2009-11-01 | 10/10 - 11/09
2009-12-01 | 11/10 - 12/09
2010-01-01 | 12/10 - 01/09
2010-02-01 | 01/10 - 02/09
2010-03-01 | 02/10 - 03/09
2010-04-01 | 03/10 - 04/09
2010-05-01 | 04/10 - 05/09
2010-06-01 | 05/10 - 06/09
2010-07-01 | 06/10 - 07/12
Total
Month on bill | Date
2009-07-01 | 06/10 - 07/09
2009-08-01 | 07/10 - 08/09
2009-09-01 | 08/10 - 09/09
2009-10-01 | 09/10 - 10/09
2009-11-01 | 10/10 - 11/09
2009-12-01 | 11/10 - 12/09
2010-01-01 | 12/10 - 01/09
2010-02-01 | 01/10 - 02/09
2010-03-01 | 02/10 - 03/09
2010-04-01 | 03/10 - 04/09
2010-05-01 | 04/10 - 05/09
2010-06-01 | 05/10 - 06/09
2010-07-01 | 06/10 - 07/12
Total
Month on bill | Date
2009-07-01 | 06/10 - 07/09
2009-08-01 | 07/10 - 08/09
2009-09-01 | 08/10 - 09/09
2009-10-01 | 09/10 - 10/09
2009-11-01 | 10/10 - 11/09
2009-12-01 | 11/10 - 12/09
2010-01-01 | 12/10 - 01/09
2010-02-01 | 01/10 - 02/09
2010-03-01 | 02/10 - 03/09
2010-04-01 | 03/10 - 04/09
2010-05-01 | 04/10 - 05/09
2010-06-01 | 05/10 - 06/09
2010-07-01 | 06/10 - 07/12
Total
Month on bill | Date
2009-07-01 | 06/10 - 07/09
2009-08-01 | 07/10 - 08/09
2009-09-01 | 08/10 - 09/09
2009-10-01 | 09/10 - 10/09
2009-11-01 | 10/10 - 11/09
2009-12-01 | 11/10 - 12/09
2010-01-01 | 12/10 - 01/09
2010-02-01 | 01/10 - 02/09
2010-03-01 | 02/10 - 03/09
2010-04-01 | 03/10 - 04/09
2010-05-01 | 04/10 - 05/09
2010-06-01 | 05/10 - 06/09
2010-07-01 | 06/10 - 07/12
Total

## Actual vs Sim
All homes for which we have at least one year of data. Data does not start at the same date for all.
|  |  | X | Y
Address | Plan | starting date | egUSA kWh | Actual kWh | BEopt kWh
1207 Mandolin St | H2 | Jan '10 | 8449 | 12016 | 9503
1201 Mandolin St | L2 | Jan '10 | 9690 | 16958 | 9126
4305 St Bernard Ave | L3 | Jan '10 | 11512 | 18415 | 10822
4313 St Bernard Ave | H2 | Jan '10 | 8450 | 9916 | 9503
4317 St Bernard Ave | B4 | Jan '10 | 12741 | 21903 | 12168
4321 St Bernard Ave | F3 | Jan '10 | 10675 | 13960 | 10692
4325 St Bernard Ave | B4 | Jan '10 | 12741 | 22104 | 12168
4329 St Bernard Ave | L3 | Jan '10 | 11512 | 14567 | 10822
4341 St Bernard Ave | H2 | Jan '10 | 8450 | 13739 | 9503
4345 St Bernard Ave | L3 | Jan '10 | 11512 | 15076 | 10822
1206 Owens Blvd | L3 |  |  |  |  | full year not available
1212 Ownens Blvd | L2 | jan '10 | 9690 | 20979 | 9126
1218 Owens Blvd | H2 | Jan '10 | 8449 | 18288 | 9503
4253 St Bernard Ave | H2 | Jan '10 | 8450 | 12884 | 9503
4243 St Bernard Ave | H2 | Jan '10 | 13795 | 14482 | 9503
1463 Filmore Ave | Gertrude | Jan '10 | 10978 | 16649 | 11094
4951 Piety Dr | Gertrude |  |  |  |  | full year not available
5705 Wildair Dr | Templeton | Jan '10 | 10397 | 16664 | 12410
5749 Wildair Dr | Templeton | Feb '10 | 10381 | 12892 | 12410
4975 St. Roach Ave | Templeton | Jan '10 | 10007 | 19712 | 12410
5515 Wickfield Dr | Camille | Jan '10 | 11108 | 15310 | 11554
5320 Wilton DR | Gertrude |  |  |  |  | full year not available
4963 Painters St | Gertrude |  |  |  |  | full year not available
5729 Wilton Dr | louise |  |  |  |  | full year not available
5773 Wildair | Gertrude |  |  |  |  | full year starting in May 10
6056 Wickfield Dr | Gertrude |  |  |  |  | full year not available
5541 Pasteur Blvd | Camille |  |  |  |  | full year starting July 10
5525 Pasteur Blvd | Templeton |  |  |  |  | full year not available
[6 empty] | B4 | 12168
[6 empty] | F3 | 10692
[6 empty] | H2 | 9503
[6 empty] | L2 | 9126
[6 empty] | L3 | 10822
[6 empty] | Gertrude | 11094
[6 empty] | Camille | 11554
[6 empty] | Templeton | 12410

## Energy per sq ft
*Source energy ratio from Deru and Torcellini reference (also used in Kohta's report page 20
|  | Site | Site | Source |  | Site energy | site energy | Source Energy*
Address | Plan | kWh/yr | MMBTU/yr | MMBtu/yr | sf | kWh/sf | kBtu/sf | kBtu/sf
1207 Mandolin St | H2 | 12016 | 41.0102 | 137.9995 | 1016 | 11.8268 | 40.3648 | 135.8275
1201 Mandolin St | L2 | 16958 | 57.8771 | 194.7566 | 1067 | 15.8932 | 54.2433 | 182.5289
4305 St Bernard Ave | L3 | 18415 | 62.8498 | 211.4897 | 1377 | 13.3733 | 45.643 | 153.5887
4313 St Bernard Ave | H2 | 9916 | 33.843 | 113.8817 | 1016 | 9.7598 | 33.3103 | 112.0893
4317 St Bernard Ave | B4 | 21903 | 74.7543 | 251.5481 | 1551 | 14.1219 | 48.1979 | 162.1859
4321 St Bernard Ave | F3 | 13960 | 47.6451 | 160.3256 | 1248 | 11.1859 | 38.1775 | 128.4672
4325 St Bernard Ave | B4 | 22104 | 75.4403 | 253.8565 | 1551 | 14.2515 | 48.6402 | 163.6743
4329 St Bernard Ave | L3 | 14567 | 49.7167 | 167.2968 | 1377 | 10.5788 | 36.1054 | 121.4948
4341 St Bernard Ave | H2 | 13739 | 46.8908 | 157.7875 | 1016 | 13.5226 | 46.1528 | 155.304
4345 St Bernard Ave | L3 | 15076 | 51.4539 | 173.1425 | 1377 | 10.9484 | 37.367 | 125.74
1212 Ownens Blvd | L2 | 20979 | 71.6007 | 240.9363 | 1067 | 19.6617 | 67.1053 | 225.8092
1218 Owens Blvd | H2 | 18288 | 62.4164 | 210.0311 | 1016 | 18 | 61.434 | 206.7254
4253 St Bernard Ave | H2 | 12884 | 43.9727 | 147.9681 | 1016 | 12.6811 | 43.2806 | 145.6392
4243 St Bernard Ave | H2 | 14482 | 49.4266 | 166.3206 | 1016 | 14.2539 | 48.6487 | 163.7028
1463 Filmore Ave | Gertrude | 16649 | 56.8225 | 191.2078 | 1316 | 12.6512 | 43.1786 | 145.296
5705 Wildair Dr | Templeton | 16664 | 56.8737 | 191.3801 | 1213 | 13.7378 | 46.8872 | 157.7756
5749 Wildair Dr | Templeton | 12892 | 44 | 148.06 | 1213 | 10.6282 | 36.274 | 122.0621
4975 St. Roach Ave | Templeton | 19712 | 67.2765 | 226.3853 | 1213 | 16.2506 | 55.4634 | 186.6342
5515 Wickfield Dr | Camille | 15310 | 52.2526 | 175.8299 | 1224 | 12.5082 | 42.6904 | 143.6531
5320 Wilton DR | Gertrude
4963 Painters St | Gertrude
5729 Wilton Dr | louise
5773 Wildair | Gertrude
6056 Wickfield Dr | Gertrude
5541 Pasteur Blvd | Camille
5525 Pasteur Blvd | Templeton
1206 Owens Blvd | L3
4951 Piety Dr | Gertrude

## Actual vs Sim EGUSA and BEopt
All homes for which we have at least one year of data. Data does not start at the same date for all. | [7 empty] | DEHUMIDIFICATION ESTIMATES
Energy Gauge
|  |  | X | Y |  | Underprediction |  | with low end of dehumid | % underprediction | high end? | %
Address | Plan | starting date | egUSA kWh | Actual kWh | BEopt kWh | EGUSA | BEopt | 791 |  | 1000
1207 Mandolin St | H2 | Jan '10 | 8449 | 12016 | 9503 | 142.2% | 126.4% | 9240 | 130% | 9449 | 127.2% | 0.10583
1201 Mandolin St | L2 | Jan '10 | 9690 | 16958 | 9126 | 175% | 185.8% | 10481 | 161.8% | 10690 | 158.6% | 0.093545
4305 St Bernard Ave | L3 | Jan '10 | 11512 | 18415 | 10822 | 160% | 170.2% | 12303 | 149.7% | 12512 | 147.2% | 0.079923
4313 St Bernard Ave | H2 | Jan '10 | 8450 | 9916 | 9503 | 117.3% | 104.3% | 9241 | 107.3% | 9450 | 104.9% | 0.10582
4317 St Bernard Ave | B4 | Jan '10 | 12741 | 21903 | 12168 | 171.9% | 180% | 13532 | 161.9% | 13741 | 159.4% | 0.072775
4321 St Bernard Ave | F3 | Jan '10 | 10675 | 13960 | 10692 | 130.8% | 130.6% | 11466 | 121.8% | 11675 | 119.6% | 0.085653
4325 St Bernard Ave | B4 | Jan '10 | 12741 | 22104 | 12168 | 173.5% | 181.7% | 13532 | 163.3% | 13741 | 160.9% | 0.072775
4329 St Bernard Ave | L3 | Jan '10 | 11512 | 14567 | 10822 | 126.5% | 134.6% | 12303 | 118.4% | 12512 | 116.4% | 0.079923
4341 St Bernard Ave | H2 | Jan '10 | 8450 | 13739 | 9503 | 162.6% | 144.6% | 9241 | 148.7% | 9450 | 145.4% | 0.10582
4345 St Bernard Ave | L3 | Jan '10 | 11512 | 15076 | 10822 | 131% | 139.3% | 12303 | 122.5% | 12512 | 120.5% | 0.079923
1212 Ownens Blvd | L2 | jan '10 | 9690 | 20979 | 9126 | 216.5% | 229.9% | 10481 | 200.2% | 10690 | 196.2% | 0.093545
1218 Owens Blvd | H2 | Jan '10 | 8449 | 18288 | 9503 | 216.5% | 192.4% | 9240 | 197.9% | 9449 | 193.5% | 0.10583
4253 St Bernard Ave | H2 | Jan '10 | 8450 | 12884 | 9503 | 152.5% | 135.6% | 9241 | 139.4% | 9450 | 136.3% | 0.10582
4243 St Bernard Ave | H2 | Jan '10 | 8450 | 14482 | 9503 | 171.4% | 152.4% | 9241 | 156.7% | 9450 | 153.2% | 0.10582
1463 Filmore Ave | Gertrude | Jan '10 | 10978 | 16649 | 11094 | 151.7% | 150.1% | 11769 | 141.5% | 11978 | 139% | 0.083486
5705 Wildair Dr | Templeton | Jan '10 | 10397 | 16664 | 10910 | 160.3% | 152.7% | 11188 | 148.9% | 11397 | 146.2% | 0.087742
5749 Wildair Dr | Templeton | Feb '10 | 10381 | 12892 | 10910 | 124.2% | 118.2% | 11172 | 115.4% | 11381 | 113.3% | 0.087866
4975 St. Roach Ave | Templeton | Jan '10 | 10007 | 19712 | 10910 | 197% | 180.7% | 10798 | 182.6% | 11007 | 179.1% | 0.090851
5515 Wickfield Dr | Camille | Jan '10 | 11108 | 15310 | 10227 | 137.8% | 149.7% | 11899 | 128.7% | 12108 | 126.4% | 0.08259
[5 empty] | MIN | 117.3% | 104.3% |  | 107.3% |  | 104.9%
[5 empty] | MAX | 216.5% | 229.9% |  | 200.2% |  | 196.2%
[5 empty] | AV | 158.9% | 155.7% |  | 147.2% |  | 144.4%
5320 Wilton DR | Gertrude | [6 empty] | full year not available
4963 Painters St | Gertrude | [6 empty] | full year not available
5729 Wilton Dr | louise | [6 empty] | full year not available
5773 Wildair | Gertrude | [6 empty] | full year starting in May 10
6056 Wickfield Dr | Gertrude | [6 empty] | full year not available
5541 Pasteur Blvd | Camille | [6 empty] | full year starting July 10
5525 Pasteur Blvd | Templeton | [6 empty] | full year not available
1206 Owens Blvd | L3 | [6 empty] | full year not available |  |  |  |  | BEopt
4951 Piety Dr | Gertrude | [6 empty] | full year not available |  |  |  | B4 | 12168
[12 empty] | F3 | 10692
[12 empty] | H2 | 9503
[12 empty] | L2 | 9126
[12 empty] | L3 | 10822
[12 empty] | Gertrude | 11094
[12 empty] | Camille | 10227
[12 empty] | Templeton | 10910
Note on I3: Rosi: Armin estimates 791 kWh per year to maintain at 55% RH
Note on K3: Rosi: High end of dehumidification energy estimated at 1000 kWh/yr?

## Actual vs Sim Base Loads
All homes for which we have at least one year of data. Data does not start at the same date for all.
[7 empty] | sorted smallest to largest |  | multiply by 12 | [5 empty] | ACTUAL | EGUSA
|  |  | X | Y |  |  | kWh |  | Actual base load/year | EGUSA base load/yr |  | % of total | % of total |  | Total-Base | total -base
Address | Plan | starting date | egUSA kWh | Actual kWh | BEopt kWh |  | Actual Base Load | EGUSA Base Load | Estimated Base Load | Estimated Base Load |  | Actual | EGUSA |  | Heating & Cooling | Heating and Cooling
4313 St Bernard Ave | H2 | Jan '10 | 8450 | 9916 | 9503 |  | 508.3333 | 537 | 6100 | 6444 |  | 61.52% | 76.26% |  | 3816 | 2006 | 1.9023
4341 St Bernard Ave | H2 | Jan '10 | 8450 | 13739 | 9503 |  | 682.6667 | 537 | 8192 | 6444 |  | 59.63% | 76.26% |  | 5547 | 2006 | 2.7652
5749 Wildair Dr | Templeton | Feb '10 | 10381 | 12892 | 10910 |  | 686 | 726.6667 | 8232 | 8720 |  | 63.85% | 84% |  | 4660 | 1661 | 2.8055
4253 St Bernard Ave | H2 | Jan '10 | 8450 | 12884 | 9503 |  | 753.6667 | 537 | 9044 | 6444 |  | 70.2% | 76.26% |  | 3840 | 2006 | 1.9143
1218 Owens Blvd | H2 | Jan '10 | 8449 | 18288 | 9503 |  | 810.6667 | 537 | 9728 | 6444 |  | 53.19% | 76.27% |  | 8560 | 2005 | 4.2693
5705 Wildair Dr | Templeton | Jan '10 | 10397 | 16664 | 10910 |  | 810.6667 | 734.6667 | 9728 | 8816 |  | 58.38% | 84.79% |  | 6936 | 1581 | 4.3871
1207 Mandolin St | H2 | Jan '10 | 8449 | 12016 | 9503 |  | 814.3333 | 537 | 9772 | 6444 |  | 81.32% | 76.27% |  | 2244 | 2005 | 1.1192
4345 St Bernard Ave | L3 | Jan '10 | 11512 | 15076 | 10822 |  | 853.3333 | 796 | 10240 | 9552 |  | 67.92% | 82.97% |  | 4836 | 1960 | 2.4673
4305 St Bernard Ave | L3 | Jan '10 | 11512 | 18415 | 10822 |  | 882 | 796 | 10584 | 9552 |  | 57.47% | 82.97% |  | 7831 | 1960 | 3.9954
4243 St Bernard Ave | H2 | Jan '10 | 8450 | 14482 | 9503 |  | 884.6667 | 537 | 10616 | 6444 |  | 73.3% | 76.26% |  | 3866 | 2006 | 1.9272
4321 St Bernard Ave | F3 | Jan '10 | 10675 | 13960 | 10692 |  | 898 | 762.3333 | 10776 | 9148 |  | 77.19% | 85.7% |  | 3184 | 1527 | 2.0851
1201 Mandolin St | L2 | Jan '10 | 9690 | 16958 | 9126 |  | 905.3333 | 666 | 10864 | 7992 |  | 64.06% | 82.48% |  | 6094 | 1698 | 3.5889
5515 Wickfield Dr | Camille | Jan '10 | 11108 | 15310 | 10227 |  | 920 | 768 | 11040 | 9216 |  | 72.11% | 82.97% |  | 4270 | 1892 | 2.2569
4329 St Bernard Ave | L3 | Jan '10 | 11512 | 14567 | 10822 |  | 969.3333 | 796 | 11632 | 9552 |  | 79.85% | 82.97% |  | 2935 | 1960 | 1.4974
4317 St Bernard Ave | B4 | Jan '10 | 12741 | 21903 | 12168 |  | 1079.3333 | 872 | 12952 | 10464 |  | 59.13% | 82.13% |  | 8951 | 2277 | 3.931
1463 Filmore Ave | Gertrude | Jan '10 | 10978 | 16649 | 11094 |  | 1088 | 742.3333 | 13056 | 8908 |  | 78.42% | 81.14% |  | 3593 | 2070 | 1.7357
4975 St. Roach Ave | Templeton | Jan '10 | 10007 | 19712 | 10910 |  | 1127 | 670 | 13524 | 8040 |  | 68.61% | 80.34% |  | 6188 | 1967 | 3.1459
1212 Ownens Blvd | L2 | jan '10 | 9690 | 20979 | 9126 |  | 1261.3333 | 661.3333 | 15136 | 7936 |  | 72.15% | 81.9% |  | 5843 | 1754 | 3.3312
4325 St Bernard Ave | B4 | Jan '10 | 12741 | 22104 | 12168 |  | 1394.6667 | 879 | 16736 | 10548 |  | 75.71% | 82.79% |  | 5368 | 2193 | 2.4478
5773 Wildair Phase III | Gertrude Phase III | aug '10 |  | 20297 |  |  | 1215.6667 |  | 14588 | [5 empty] | 5709
5541 Pasteur Phase III | Camille Phase III | aug '10 |  | 19400 |  |  | 1323.3333 |  | 15880 | [5 empty] | 3520
[6 empty] | average | 912.0702 | 689.0702 |  |  | MIN | 53.19% | 76.26%
[6 empty] | st. dev | #NAME? | #NAME? |  |  | MAX | 81.32% | 85.7%
[7 empty] | 0.56209 |  |  |  | AV | 68.11% | 80.78%
5320 Wilton DR | [7 empty] | full year not available
4963 Painters St | [7 empty] | full year not available
5729 Wilton Dr | [7 empty] | full year not available
5773 Wildair | [7 empty] | full year starting in May 10
6056 Wickfield Dr | [7 empty] | full year not available
5541 Pasteur Blvd | [7 empty] | full year starting July 10
5525 Pasteur Blvd | [7 empty] | full year not available
1206 Owens Blvd | [7 empty] | full year not available | [5 empty] | BEopt
4951 Piety Dr | [7 empty] | full year not available |  |  |  |  | B4 | 12168
[13 empty] | F3 | 10692
[13 empty] | H2 | 9503
[13 empty] | L2 | 9126
[13 empty] | L3 | 10822
[13 empty] | Gertrude | 11094
[13 empty] | Camille | 10227
[13 empty] | Templeton | 10910

## Actual vs Sim Base Loads 2
All homes for which we have at least one year of data. Data does not start at the same date for all.
[7 empty] | sorted smallest to largest |  | multiply by 12 | [5 empty] | ACTUAL | EGUSA
|  |  | X | Y |  |  | kWh |  | Actual base load/year | EGUSA base load/yr |  | % of total | % of total |  | Total-Base | total -base
Address | Plan | starting date | egUSA kWh | Actual kWh | BEopt kWh |  | Actual Base Load | EGUSA Base Load | Estimated Base Load | Estimated Base Load |  | Actual | EGUSA |  | Heating & Cooling | Heating and Cooling
4313 St Bernard Ave | H2 | Jan '10 | 8450 | 9916 | 9503 |  | 508.3333 | 537 | 6100 | 6444 |  | 61.52% | 76.26% |  | 3816 | 2006 | 1.9023
4341 St Bernard Ave | H2 | Jan '10 | 8450 | 13739 | 9503 |  | 682.6667 | 537 | 8192 | 6444 |  | 59.63% | 76.26% |  | 5547 | 2006 | 2.7652
5749 Wildair Dr | Templeton | Feb '10 | 10381 | 12892 | 10910 |  | 686 | 726.6667 | 8232 | 8720 |  | 63.85% | 84% |  | 4660 | 1661 | 2.8055
4253 St Bernard Ave | H2 | Jan '10 | 8450 | 12884 | 9503 |  | 753.6667 | 537 | 9044 | 6444 |  | 70.2% | 76.26% |  | 3840 | 2006 | 1.9143
1218 Owens Blvd | H2 | Jan '10 | 8449 | 18288 | 9503 |  | 810.6667 | 537 | 9728 | 6444 |  | 53.19% | 76.27% |  | 8560 | 2005 | 4.2693
5705 Wildair Dr | Templeton | Jan '10 | 10397 | 16664 | 10910 |  | 810.6667 | 734.6667 | 9728 | 8816 |  | 58.38% | 84.79% |  | 6936 | 1581 | 4.3871
1207 Mandolin St | H2 | Jan '10 | 8449 | 12016 | 9503 |  | 814.3333 | 537 | 9772 | 6444 |  | 81.32% | 76.27% |  | 2244 | 2005 | 1.1192
4345 St Bernard Ave | L3 | Jan '10 | 11512 | 15076 | 10822 |  | 853.3333 | 796 | 10240 | 9552 |  | 67.92% | 82.97% |  | 4836 | 1960 | 2.4673
4305 St Bernard Ave | L3 | Jan '10 | 11512 | 18415 | 10822 |  | 882 | 796 | 10584 | 9552 |  | 57.47% | 82.97% |  | 7831 | 1960 | 3.9954
4243 St Bernard Ave | H2 | Jan '10 | 8450 | 14482 | 9503 |  | 884.6667 | 537 | 10616 | 6444 |  | 73.3% | 76.26% |  | 3866 | 2006 | 1.9272
4321 St Bernard Ave | F3 | Jan '10 | 10675 | 13960 | 10692 |  | 898 | 762.3333 | 10776 | 9148 |  | 77.19% | 85.7% |  | 3184 | 1527 | 2.0851
1201 Mandolin St | L2 | Jan '10 | 9690 | 16958 | 9126 |  | 905.3333 | 666 | 10864 | 7992 |  | 64.06% | 82.48% |  | 6094 | 1698 | 3.5889
5515 Wickfield Dr | Camille | Jan '10 | 11108 | 15310 | 10227 |  | 920 | 768 | 11040 | 9216 |  | 72.11% | 82.97% |  | 4270 | 1892 | 2.2569
4329 St Bernard Ave | L3 | Jan '10 | 11512 | 14567 | 10822 |  | 969.3333 | 796 | 11632 | 9552 |  | 79.85% | 82.97% |  | 2935 | 1960 | 1.4974
4317 St Bernard Ave | B4 | Jan '10 | 12741 | 21903 | 12168 |  | 1079.3333 | 872 | 12952 | 10464 |  | 59.13% | 82.13% |  | 8951 | 2277 | 3.931
1463 Filmore Ave | Gertrude | Jan '10 | 10978 | 16649 | 11094 |  | 1088 | 742.3333 | 13056 | 8908 |  | 78.42% | 81.14% |  | 3593 | 2070 | 1.7357
4975 St. Roach Ave | Templeton | Jan '10 | 10007 | 19712 | 10910 |  | 1127 | 670 | 13524 | 8040 |  | 68.61% | 80.34% |  | 6188 | 1967 | 3.1459
5773 Wildair Phase III | Gertrude Phase III | aug '10 |  | 20297 |  |  | 1215.6667 |  | 14588 | [5 empty] | 5709
1212 Ownens Blvd | L2 | jan '10 | 9690 | 20979 | 9126 |  | 1261.3333 | 661.3333 | 15136 | 7936 |  | 72.15% | 81.9% |  | 5843 | 1754 | 3.3312
5541 Pasteur Phase III | Camille Phase III | aug '10 |  | 19400 |  |  | 1323.3333 |  | 15880 | [5 empty] | 3520
4325 St Bernard Ave | B4 | Jan '10 | 12741 | 22104 | 12168 |  | 1394.6667 | 879 | 16736 | 10548 |  | 75.71% | 82.79% |  | 5368 | 2193 | 2.4478
[6 empty] | average | 945.5439 | 686.8431 |  |  | MIN | 53.19% | 76.26%
[6 empty] | st. dev | #NAME? | #NAME? |  |  | MAX | 81.32% | 85.7%
[7 empty] | 0.363 |  |  |  | AV | 68.05% | 80.92%
Degree Days
Jan-Dec 2010 HDD | 1708
Jan-Dec 2010 CDD | 3304
% change
Aug 2010 - Jul 2011 HDD | 1311 | 0.23244
Aug 2010 - Jul 2011 CDD | 3597 | 0.081457 | [5 empty] | full year not available
full year not available
full year not available
full year starting in May 10
full year not available
full year starting July 10
full year not available
[8 empty] | full year not available | [5 empty] | BEopt
[8 empty] | full year not available |  |  |  |  | B4 | 12168
[13 empty] | F3 | 10692
[13 empty] | H2 | 9503
[13 empty] | L2 | 9126
[13 empty] | L3 | 10822
[13 empty] | Gertrude | 11094
[13 empty] | Camille | 10227
[13 empty] | Templeton | 10910

## Source per sf low to high
|  | Site | Site | Source |  |  | from B10 |  |  |  | *Source energy ratio from Deru and Torcellini reference (also used in Kohta's report page 20
Jan 2010 to Dec 2010 |  | PHA Actual | PHA Actual | PHA Actual | BEopt Model | B10 Benchmark | Reduction |  | Site energy | site energy | Source Energy* |  | MMBTU/yr
Address | Plan | kWh/yr | MMBTU/yr | MMBtu/yr | MMBtu/yr | MMBtu/yr |  | sf | kWh/sf | Site kBtu/sf | kBtu/sf | US Average | Southern Average
4313 St Bernard Ave | H2 | 9916 | 33.843 | 113.8817 | 109.1 | 153.8 | 25.95% | 1016 | 9.7598 | 33.3103 | 112.0893 | 197.9 | 220.5
4329 St Bernard Ave | L3 | 14567 | 49.7167 | 167.2968 | BEopt design | 173.4 | 3.52% | 1377 | 10.5788 | 36.1054 | 121.4948 |  | 220.5
5749 Wildair Dr | Templeton | 12892 | 44 | 148.06 | 117.4 | 163 | 9.166% | 1213 | 10.6282 | 36.274 | 122.0621 |  | 220.5
4345 St Bernard Ave | L3 | 15076 | 51.4539 | 173.1425 | MMBtu/yr | 173.4 | 0.1485% | 1377 | 10.9484 | 37.367 | 125.74 |  | 220.5
4321 St Bernard Ave | F3 | 13960 | 47.6451 | 160.3256 | 139.7 | 169 | 5.133% | 1248 | 11.1859 | 38.1775 | 128.4672 |  | 220.5
1207 Mandolin St | H2 | 12016 | 41.0102 | 137.9995 | 117.4 | 153.8 | 10.27% | 1016 | 11.8268 | 40.3648 | 135.8275 |  | 220.5
5515 Wickfield Dr | Camille | 15310 | 52.2526 | 175.8299 | 104.8 | 150 | -17.22% | 1224 | 12.5082 | 42.6904 | 143.6531 |  | 220.5
1463 Filmore Ave | Gertrude | 16649 | 56.8225 | 191.2078 | 109.1 | 153.8 | -24.32% | 1316 | 12.6512 | 43.1786 | 145.296 |  | 220.5
4253 St Bernard Ave | H2 | 12884 | 43.9727 | 147.9681 | 0 | 153.8 | 3.792% | 1016 | 12.6811 | 43.2806 | 145.6392 |  | 220.5
4305 St Bernard Ave | L3 | 18415 | 62.8498 | 211.4897 | 139.7 | 173.4 | -21.97% | 1377 | 13.3733 | 45.643 | 153.5887 |  | 220.5
4341 St Bernard Ave | H2 | 13739 | 46.8908 | 157.7875 | 0 | 153.8 | -2.593% | 1016 | 13.5226 | 46.1528 | 155.304 |  | 220.5
5705 Wildair Dr | Templeton | 16664 | 56.8737 | 191.3801 | 125.3 | 167.7 | -14.12% | 1213 | 13.7378 | 46.8872 | 157.7756 |  | 220.5
4317 St Bernard Ave | B4 | 21903 | 74.7543 | 251.5481 | 0 | 192.6 | -30.61% | 1551 | 14.1219 | 48.1979 | 162.1859 |  | 220.5
4243 St Bernard Ave | H2 | 14482 | 49.4266 | 166.3206 | 0 | 153.8 | -8.141% | 1016 | 14.2539 | 48.6487 | 163.7028 |  | 220.5
4325 St Bernard Ave | B4 | 22104 | 75.4403 | 253.8565 | 0 | 192.6 | -31.81% | 1551 | 14.2515 | 48.6402 | 163.6743 |  | 220.5
1201 Mandolin St | L2 | 16958 | 57.8771 | 194.7566 | 117.4 | 150 | -29.84% | 1067 | 15.8932 | 54.2433 | 182.5289 |  | 220.5
4975 St. Roach Ave | Templeton | 19712 | 67.2765 | 226.3853 | 0 | 0 | #DIV/0! | 1213 | 16.2506 | 55.4634 | 186.6342 |  | 220.5
1218 Owens Blvd | H2 | 18288 | 62.4164 | 210.0311 | 127.4 | 153.8 | -36.56% | 1016 | 18 | 61.434 | 206.7254 |  | 220.5
1212 Ownens Blvd | L2 | 20979 | 71.6007 | 240.9363 | 127.4 | 150 | -60.62% | 1067 | 19.6617 | 67.1053 | 225.8092 |  | 220.5
AVERAGE |  |  |  | 185.2739 | [5 empty] | 45.956
standard deviation |  |  |  | #NAME? | [5 empty] | #NAME?
|  | BEopt design | B10 benchmark
Homes types for which one year of data is available | BEopt kWh/yr | MMBtu/yr | MMBtu/yr | Modeled Reduction
B4 | 12168 | 139.7 | 192.6 | 25.96%
F3 | 10692 | 122.8 | 169 | 25.65%
H2 | 9503 | 109.1 | 153.8 | 27.1%
L2 | 9126 | 104.8 | 150 | 28.05%
L3 | 10822 | 124.3 | 173.4 | 26.61%
Gertrude | 11094 | 127.4 | 170 | 23.52%
Camille | 10227 | 117.4 | 163 | 26.19%
Templeton | 10910 | 125.3 | 167.7 | 23.71%

## Source energy low to high
|  | Site | Site | Source |  |  |  |  | from B10 |  |  |  |  | *Source energy ratio from Deru and Torcellini reference (also used in Kohta's report page 20
Jan 2010 to Dec 2010 |  | PHA Actual | PHA Actual | PHA Prototype | BEopt Prototype Model | BEopt model Adjusted | B10 Benchmark | B10 Benchmark Adjusted | Reduction | Over BEopt models |  | Site energy | site energy | Source Energy* |  | MMBTU/yr
Address | Plan | kWh/yr | MMBTU/yr | MMBtu/yr | MMBtu/yr | MMBtu/yr | MMBtu/yr |  |  |  | sf | kWh/sf | kBtu/sf | kBtu/sf | US Average | Southern Average | % below southern av
4313 St Bernard Ave | H2 | 9916 | 33.843 | 113.8817 | 109.1 | 120.2442 | 153.8 | 164.9442 | 30.96% | -5.587% | 1016 | 9.7598 | 33.3103 | 112.0893 | 197.9 | 220.5 | 48.35%
1207 Mandolin St | H2 | 12016 | 41.0102 | 137.9995 | 109.1 | 120.2442 | 153.8 | 164.9442 | 16.34% | 12.87% | 1016 | 11.8268 | 40.3648 | 135.8275 |  | 220.5 | 37.42%
4253 St Bernard Ave | H2 | 12884 | 43.9727 | 147.9681 | 109.1 | 120.2442 | 153.8 | 164.9442 | 10.29% | 18.74% | 1016 | 12.6811 | 43.2806 | 145.6392 |  | 220.5 | 32.89%
5749 Wildair Dr | Templeton | 12892 | 44 | 148.06 | 125.3 | 136.4442 | 167.7 | 178.8442 | 17.21% | 7.845% | 1213 | 10.6282 | 36.274 | 122.0621 |  | 220.5 | 32.85%
4341 St Bernard Ave | H2 | 13739 | 46.8908 | 157.7875 | 109.1 | 120.2442 | 153.8 | 164.9442 | 4.339% | 23.79% | 1016 | 13.5226 | 46.1528 | 155.304 |  | 220.5 | 28.44%
4321 St Bernard Ave | F3 | 13960 | 47.6451 | 160.3256 | 122.8 | 133.9442 | 169 | 180.1442 | 11% | 16.45% | 1248 | 11.1859 | 38.1775 | 128.4672 |  | 220.5 | 27.29%
4243 St Bernard Ave | H2 | 14482 | 49.4266 | 166.3206 | 109.1 | 120.2442 | 153.8 | 164.9442 | -0.8345% | 27.7% | 1016 | 14.2539 | 48.6487 | 163.7028 |  | 220.5 | 24.57%
4329 St Bernard Ave | L3 | 14567 | 49.7167 | 167.2968 | 124.3 | 135.4442 | 173.4 | 184.5442 | 9.346% | 19.04% | 1377 | 10.5788 | 36.1054 | 121.4948 |  | 220.5 | 24.13%
4345 St Bernard Ave | L3 | 15076 | 51.4539 | 173.1425 | 124.3 | 135.4442 | 173.4 | 184.5442 | 6.178% | 21.77% | 1377 | 10.9484 | 37.367 | 125.74 |  | 220.5 | 21.48%
5515 Wickfield Dr | Camille | 15310 | 52.2526 | 175.8299 | 117.4 | 128.5442 | 163 | 174.1442 | -0.968% | 26.89% | 1224 | 12.5082 | 42.6904 | 143.6531 |  | 220.5 | 20.26%
1463 Filmore Ave | Gertrude | 16649 | 56.8225 | 191.2078 | 127.4 | 138.5442 | 170 | 181.1442 | -5.556% | 27.54% | 1316 | 12.6512 | 43.1786 | 145.296 |  | 220.5 | 13.28%
5705 Wildair Dr | Templeton | 16664 | 56.8737 | 191.3801 | 125.3 | 136.4442 | 167.7 | 178.8442 | -7.009% | 28.71% | 1213 | 13.7378 | 46.8872 | 157.7756 |  | 220.5 | 13.21%
1201 Mandolin St | L2 | 16958 | 57.8771 | 194.7566 | 104.8 | 115.9442 | 150 | 161.1442 | -20.86% | 40.47% | 1067 | 15.8932 | 54.2433 | 182.5289 |  | 220.5 | 11.68%
4305 St Bernard Ave | L3 | 18415 | 62.8498 | 211.4897 | 124.3 | 135.4442 | 173.4 | 184.5442 | -14.6% | 35.96% | 1377 | 13.3733 | 45.643 | 153.5887 |  | 220.5 | 4.086%
1218 Owens Blvd | H2 | 18288 | 62.4164 | 210.0311 | 109.1 | 120.2442 | 153.8 | 164.9442 | -27.33% | 42.75% | 1016 | 18 | 61.434 | 206.7254 |  | 220.5 | 4.748%
4975 St. Roach Ave | Templeton | 19712 | 67.2765 | 226.3853 | 125.3 | 136.4442 | 167.7 | 178.8442 | -26.58% | 39.73% | 1213 | 16.2506 | 55.4634 | 186.6342 |  | 220.5 | -2.669%
1212 Ownens Blvd | L2 | 20979 | 71.6007 | 240.9363 | 104.8 | 115.9442 | 150 | 161.1442 | -49.52% | 51.88% | 1067 | 19.6617 | 67.1053 | 225.8092 |  | 220.5 | -9.268%
4317 St Bernard Ave | B4 | 21903 | 74.7543 | 251.5481 | 139.7 | 150.8442 | 192.6 | 203.7442 | -23.46% | 40.03% | 1551 | 14.1219 | 48.1979 | 162.1859 |  | 220.5 | -14.08%
4325 St Bernard Ave | B4 | 22104 | 75.4403 | 253.8565 | 139.7 | 150.8442 | 192.6 | 203.7442 | -24.6% | 40.58% | 1551 | 14.2515 | 48.6402 | 163.6743 |  | 220.5 | -15.13%
Mean |  |  |  | 185.2739 | 118.9474 |  | 164.9105
standard deviation |  |  |  | #NAME? | #NAME? |  | #NAME?
|  |  |  | BEopt over B10 | 27.87% |  |  | MIN | -49.52% | -5.587%
|  |  |  | Actual over BEopt | 35.8% |  |  | MAX | 30.96% | 51.88%
|  |  |  | actual over B10 | 10.99% |  |  | AV | -5.035% | 27.22%
|  | BEopt design | B10 benchmark
Homes types for which one year of data is available | BEopt kWh/yr | MMBtu/yr | MMBtu/yr | Modeled Reduction
B4 | 12168 | 139.7 | 192.6 | 25.96%
F3 | 10692 | 122.8 | 169 | 25.65%
H2 | 9503 | 109.1 | 153.8 | 27.1%
L2 | 9126 | 104.8 | 150 | 28.05%
L3 | 10822 | 124.3 | 173.4 | 26.61%
Gertrude | 11094 | 127.4 | 170 | 23.52%
Camille | 10227 | 117.4 | 163 | 26.19%
Templeton | 10910 | 125.3 | 167.7 | 23.71%
Note on G2: Rosi: Added energy used be dehumidifier
Note on I2: Rosi: Add 970 kwh to account for dehumid

## Benchmark TMY3 adjusted
Adjust actual energy use as if exposed to TMY3 weather data : reduce by 10.5%
|  | Site |  | Site | Source |  |  |  |  | from B10 |  |  |  |  | *Source energy ratio from Deru and Torcellini reference (also used in Kohta's report page 20
Jan 2010 to Dec 2010 |  | PHA Actual | PHA Actual Ajusted | PHA Actual | PHA Prototype | BEopt Prototype Model | BEopt model Adjusted | B10 Benchmark | B10 Benchmark Adjusted | Reduction | Over BEopt models |  | Site energy | site energy | Source Energy* |  | MMBTU/yr
Address | Plan | kWh/yr |  | MMBTU/yr | MMBtu/yr | MMBtu/yr | MMBtu/yr | MMBtu/yr |  |  |  | sf | kWh/sf | kBtu/sf | kBtu/sf | US Average | Southern Average | % below southern av
4313 St Bernard Ave | H2 | 9916 | 8874.82 | 30.2895 | 101.9241 | 109.1 | 120.2442 | 153.8 | 164.9442 | 38.21% | -17.97% | 1016 | 9.7598 | 33.3103 | 112.0893 | 197.9 | 220.5 | 53.78%
1207 Mandolin St | H2 | 12016 | 10754.32 | 36.7042 | 123.5095 | 109.1 | 120.2442 | 153.8 | 164.9442 | 25.12% | 2.644% | 1016 | 11.8268 | 40.3648 | 135.8275 |  | 220.5 | 43.99%
4253 St Bernard Ave | H2 | 12884 | 11531.18 | 39.3556 | 132.4315 | 109.1 | 120.2442 | 153.8 | 164.9442 | 19.71% | 9.203% | 1016 | 12.6811 | 43.2806 | 145.6392 |  | 220.5 | 39.94%
5749 Wildair Dr | Templeton | 12892 | 11538.34 | 39.38 | 132.5137 | 125.3 | 136.4442 | 167.7 | 178.8442 | 25.91% | -2.966% | 1213 | 10.6282 | 36.274 | 122.0621 |  | 220.5 | 39.9%
4341 St Bernard Ave | H2 | 13739 | 12296.405 | 41.9673 | 141.2198 | 109.1 | 120.2442 | 153.8 | 164.9442 | 14.38% | 14.85% | 1016 | 13.5226 | 46.1528 | 155.304 |  | 220.5 | 35.95%
4321 St Bernard Ave | F3 | 13960 | 12494.2 | 42.6423 | 143.4914 | 122.8 | 133.9442 | 169 | 180.1442 | 20.35% | 6.654% | 1248 | 11.1859 | 38.1775 | 128.4672 |  | 220.5 | 34.92%
4243 St Bernard Ave | H2 | 14482 | 12961.39 | 44.2368 | 148.8569 | 109.1 | 120.2442 | 153.8 | 164.9442 | 9.753% | 19.22% | 1016 | 14.2539 | 48.6487 | 163.7028 |  | 220.5 | 32.49%
4329 St Bernard Ave | L3 | 14567 | 13037.465 | 44.4965 | 149.7306 | 124.3 | 135.4442 | 173.4 | 184.5442 | 18.86% | 9.541% | 1377 | 10.5788 | 36.1054 | 121.4948 |  | 220.5 | 32.09%
4345 St Bernard Ave | L3 | 15076 | 13493.02 | 46.0513 | 154.9625 | 124.3 | 135.4442 | 173.4 | 184.5442 | 16.03% | 12.6% | 1377 | 10.9484 | 37.367 | 125.74 |  | 220.5 | 29.72%
5515 Wickfield Dr | Camille | 15310 | 13702.45 | 46.766 | 157.3677 | 117.4 | 128.5442 | 163 | 174.1442 | 9.634% | 18.32% | 1224 | 12.5082 | 42.6904 | 143.6531 |  | 220.5 | 28.63%
1463 Filmore Ave | Gertrude | 16649 | 14900.855 | 50.8562 | 171.131 | 127.4 | 138.5442 | 170 | 181.1442 | 5.528% | 19.04% | 1316 | 12.6512 | 43.1786 | 145.296 |  | 220.5 | 22.39%
5705 Wildair Dr | Templeton | 16664 | 14914.28 | 50.902 | 171.2852 | 125.3 | 136.4442 | 167.7 | 178.8442 | 4.227% | 20.34% | 1213 | 13.7378 | 46.8872 | 157.7756 |  | 220.5 | 22.32%
1201 Mandolin St | L2 | 16958 | 15177.41 | 51.8 | 174.3071 | 104.8 | 115.9442 | 150 | 161.1442 | -8.168% | 33.48% | 1067 | 15.8932 | 54.2433 | 182.5289 |  | 220.5 | 20.95%
4305 St Bernard Ave | L3 | 18415 | 16481.425 | 56.2506 | 189.2833 | 124.3 | 135.4442 | 173.4 | 184.5442 | -2.568% | 28.44% | 1377 | 13.3733 | 45.643 | 153.5887 |  | 220.5 | 14.16%
1218 Owens Blvd | H2 | 18288 | 16367.76 | 55.8627 | 187.9779 | 109.1 | 120.2442 | 153.8 | 164.9442 | -13.96% | 36.03% | 1016 | 18 | 61.434 | 206.7254 |  | 220.5 | 14.75%
4975 St. Roach Ave | Templeton | 19712 | 17642.24 | 60.2124 | 202.6148 | 125.3 | 136.4442 | 167.7 | 178.8442 | -13.29% | 32.66% | 1213 | 16.2506 | 55.4634 | 186.6342 |  | 220.5 | 8.111%
1212 Ownens Blvd | L2 | 20979 | 18776.205 | 64.0826 | 215.638 | 104.8 | 115.9442 | 150 | 161.1442 | -33.82% | 46.23% | 1067 | 19.6617 | 67.1053 | 225.8092 |  | 220.5 | 2.205%
4317 St Bernard Ave | B4 | 21903 | 19603.185 | 66.9051 | 225.1356 | 139.7 | 150.8442 | 192.6 | 203.7442 | -10.5% | 33% | 1551 | 14.1219 | 48.1979 | 162.1859 |  | 220.5 | -2.102%
4325 St Bernard Ave | B4 | 22104 | 19783.08 | 67.519 | 227.2016 | 139.7 | 150.8442 | 192.6 | 203.7442 | -11.51% | 33.61% | 1551 | 14.2515 | 48.6402 | 163.6743 |  | 220.5 | -3.039%
Mean |  |  |  |  | 165.8201 | 118.9474 |  | 164.9105
standard deviation |  |  |  |  | #NAME? | #NAME? |  | #NAME?
[5 empty] | BEopt over B10 | 27.87% |  |  | MIN | -33.82% | -17.97%
[5 empty] | Actual over BEopt | 28.27% |  |  | MAX | 38.21% | 46.23%
[5 empty] | actual over B10 | 0.5485% |  |  | AV | 5.994% | 18.68%
|  | BEopt design |  | B10 benchmark
Homes types for which one year of data is available | BEopt kWh/yr | MMBtu/yr |  | MMBtu/yr | Modeled Reduction
B4 | 12168 | 139.7 |  | 192.6 | 25.96%
F3 | 10692 | 122.8 |  | 169 | 25.65%
H2 | 9503 | 109.1 |  | 153.8 | 27.1%
L2 | 9126 | 104.8 |  | 150 | 28.05%
L3 | 10822 | 124.3 |  | 173.4 | 26.61%
Gertrude | 11094 | 127.4 |  | 170 | 23.52%
Camille | 10227 | 117.4 |  | 163 | 26.19%
Templeton | 10910 | 125.3 |  | 167.7 | 23.71%
Note on H4: Rosi: Added energy used be dehumidifier
Note on J4: Rosi: Add 970 kwh to account for dehumid

## Source energy low to high 2
|  | Site | Site | Source |  |  | from B10 |  |  |  | *Source energy ratio from Deru and Torcellini reference (also used in Kohta's report page 20
Jan 2010 to Dec 2010 |  | PHA Actual | PHA Actual | PHA Actual | BEopt Model | B10 Benchmark | Reduction |  | Site energy | site energy | Source Energy* |  | MMBTU/yr
Address | Plan | kWh/yr | MMBTU/yr | MMBtu/yr | MMBtu/yr | MMBtu/yr |  | sf | kWh/sf | kBtu/sf | kBtu/sf | US Average | Southern Average | % below southern av
4313 St Bernard Ave | H2 | 9916 | 33.843 | 113.8817 | 109.1 | 153.8 | 25.95% | 1016 | 9.7598 | 33.3103 | 112.0893 | 197.9 | 220.5 | 48.35%
1207 Mandolin St | H2 | 12016 | 41.0102 | 137.9995 | 109.1 | 153.8 | 10.27% | 1016 | 11.8268 | 40.3648 | 135.8275 |  | 220.5 | 37.42%
4253 St Bernard Ave | H2 | 12884 | 43.9727 | 147.9681 | 109.1 | 153.8 | 3.792% | 1016 | 12.6811 | 43.2806 | 145.6392 |  | 220.5 | 32.89%
5749 Wildair Dr | Templeton | 12892 | 44 | 148.06 | 125.3 | 167.7 | 11.71% | 1213 | 10.6282 | 36.274 | 122.0621 |  | 220.5 | 32.85%
4341 St Bernard Ave | H2 | 13739 | 46.8908 | 157.7875 | 109.1 | 153.8 | -2.593% | 1016 | 13.5226 | 46.1528 | 155.304 |  | 220.5 | 28.44%
4321 St Bernard Ave | F3 | 13960 | 47.6451 | 160.3256 | 122.8 | 169 | 5.133% | 1248 | 11.1859 | 38.1775 | 128.4672 |  | 220.5 | 27.29%
4243 St Bernard Ave | H2 | 14482 | 49.4266 | 166.3206 | 109.1 | 153.8 | -8.141% | 1016 | 14.2539 | 48.6487 | 163.7028 |  | 220.5 | 24.57%
4329 St Bernard Ave | L3 | 14567 | 49.7167 | 167.2968 | 124.3 | 173.4 | 3.52% | 1377 | 10.5788 | 36.1054 | 121.4948 |  | 220.5 | 24.13%
4345 St Bernard Ave | L3 | 15076 | 51.4539 | 173.1425 | 124.3 | 173.4 | 0.1485% | 1377 | 10.9484 | 37.367 | 125.74 |  | 220.5 | 21.48%
5515 Wickfield Dr | Camille | 15310 | 52.2526 | 175.8299 | 117.4 | 163 | -7.871% | 1224 | 12.5082 | 42.6904 | 143.6531 |  | 220.5 | 20.26%
1463 Filmore Ave | Gertrude | 16649 | 56.8225 | 191.2078 | 127.4 | 170 | -12.48% | 1316 | 12.6512 | 43.1786 | 145.296 |  | 220.5 | 13.28%
5705 Wildair Dr | Templeton | 16664 | 56.8737 | 191.3801 | 125.3 | 167.7 | -14.12% | 1213 | 13.7378 | 46.8872 | 157.7756 |  | 220.5 | 13.21%
1201 Mandolin St | L2 | 16958 | 57.8771 | 194.7566 | 104.8 | 150 | -29.84% | 1067 | 15.8932 | 54.2433 | 182.5289 |  | 220.5 | 11.68%
4305 St Bernard Ave | L3 | 18415 | 62.8498 | 211.4897 | 124.3 | 173.4 | -21.97% | 1377 | 13.3733 | 45.643 | 153.5887 |  | 220.5 | 4.086%
5541 Pasteur Phase III | Camille Phase III | 19400 | 66.2116 | 222.802
1218 Owens Blvd | H2 | 18288 | 62.4164 | 210.0311 | 104.8 | 153.8 | -36.56% | 1016 | 18 | 61.434 | 206.7254 |  | 220.5 | 4.748%
5773 Wildair Phase III | Gertrude Phase III | 20297 | 69.273 | 233.1038
4975 St. Roach Ave | Templeton | 19712 | 67.2765 | 226.3853 | 0 | 0 | #DIV/0! | 1213 | 16.2506 | 55.4634 | 186.6342 |  | 220.5 | -2.669%
1212 Ownens Blvd | L2 | 20979 | 71.6007 | 240.9363 | 127.4 | 150 | -60.62% | 1067 | 19.6617 | 67.1053 | 225.8092 |  | 220.5 | -9.268%
4317 St Bernard Ave | B4 | 21903 | 74.7543 | 251.5481 | 109.1 | 192.6 | -30.61% | 1551 | 14.1219 | 48.1979 | 162.1859 |  | 220.5 | -14.08%
4325 St Bernard Ave | B4 | 22104 | 75.4403 | 253.8565 | 109.1 | 192.6 | -31.81% | 1551 | 14.2515 | 48.6402 | 163.6743 |  | 220.5 | -15.13%
Mean |  |  |  | 182.6687 | 110.2118 | 151.7882
standard deviation |  |  |  | #NAME? | #NAME? | #NAME?
|  |  |  | BEopt over B10 | 27.39%
|  |  |  | Actual over BEopt | 39.67% |  | 0.25955
|  |  |  | actual over B10 | 16.91% |  | 0.10273
|  | BEopt design | B10 benchmark
Homes types for which one year of data is available | BEopt kWh/yr | MMBtu/yr | MMBtu/yr | Modeled Reduction
B4 | 12168 | 139.7 | 192.6 | 25.96%
F3 | 10692 | 122.8 | 169 | 25.65%
H2 | 9503 | 109.1 | 153.8 | 27.1%
L2 | 9126 | 104.8 | 150 | 28.05%
L3 | 10822 | 124.3 | 173.4 | 26.61%
Gertrude | 11094 | 127.4 | 170 | 23.52%
Camille | 10227 | 117.4 | 163 | 26.19%
Templeton | 10910 | 125.3 | 167.7 | 23.71%

## Actual vs Sim with Dehumid
All homes for which we have at least one year of data. Data does not start at the same date for all. | [9 empty] | DEHUMIDIFICATION ESTIMATES
|  |  | X |  | Y |  |  | Corrected w Dehumidification
Address | Plan | starting date | egUSA kWh | BEopt kWh | Actual kWh |  | real % dehumid | EGUSA kWh | Actual/EGUSA | BEopt kWh | Actual/BEopt | increase
1207 Mandolin St | H2 | Jan '10 | 8449 | 9503 | 12016 |  | 8.076% | 9419.356 | 127.6% | 10473.356 | 114.7% | 10.3%
1201 Mandolin St | L2 | Jan '10 | 9690 | 9126 | 16958 |  | 5.722% | 10660.356 | 159.1% | 10096.356 | 168% | 9.102%
4305 St Bernard Ave | L3 | Jan '10 | 11512 | 10822 | 18415 |  | 5.269% | 12482.356 | 147.5% | 11792.356 | 156.2% | 7.774%
4313 St Bernard Ave | H2 | Jan '10 | 8450 | 9503 | 9916 |  | 9.786% | 9420.356 | 105.3% | 10473.356 | 94.68% | 10.3%
4317 St Bernard Ave | B4 | Jan '10 | 12741 | 12168 | 21903 |  | 4.43% | 13711.356 | 159.7% | 13138.356 | 166.7% | 7.077%
4321 St Bernard Ave | F3 | Jan '10 | 10675 | 10692 | 13960 |  | 6.951% | 11645.356 | 119.9% | 11662.356 | 119.7% | 8.333%
4325 St Bernard Ave | B4 | Jan '10 | 12741 | 12168 | 22104 |  | 4.39% | 13711.356 | 161.2% | 13138.356 | 168.2% | 7.077%
4329 St Bernard Ave | L3 | Jan '10 | 11512 | 10822 | 14567 |  | 6.661% | 12482.356 | 116.7% | 11792.356 | 123.5% | 7.774%
4341 St Bernard Ave | H2 | Jan '10 | 8450 | 9503 | 13739 |  | 7.063% | 9420.356 | 145.8% | 10473.356 | 131.2% | 10.3%
4345 St Bernard Ave | L3 | Jan '10 | 11512 | 10822 | 15076 |  | 6.436% | 12482.356 | 120.8% | 11792.356 | 127.8% | 7.774%
1212 Ownens Blvd | L2 | jan '10 | 9690 | 9126 | 20979 |  | 4.625% | 10660.356 | 196.8% | 10096.356 | 207.8% | 9.102%
1218 Owens Blvd | H2 | Jan '10 | 8449 | 9503 | 18288 |  | 5.306% | 9419.356 | 194.2% | 10473.356 | 174.6% | 10.3%
4253 St Bernard Ave | H2 | Jan '10 | 8450 | 9503 | 12884 |  | 7.531% | 9420.356 | 136.8% | 10473.356 | 123% | 10.3%
4243 St Bernard Ave | H2 | Jan '10 | 8450 | 9503 | 14482 |  | 6.7% | 9420.356 | 153.7% | 10473.356 | 138.3% | 10.3%
1463 Filmore Ave | Gertrude | Jan '10 | 10978 | 11094 | 16649 |  | 5.828% | 11948.356 | 139.3% | 12064.356 | 138% | 8.121%
5705 Wildair Dr | Templeton | Jan '10 | 10397 | 10910 | 16664 |  | 5.823% | 11367.356 | 146.6% | 11880.356 | 140.3% | 8.536%
5749 Wildair Dr | Templeton | Feb '10 | 10381 | 10910 | 12892 |  | 7.527% | 11351.356 | 113.6% | 11880.356 | 108.5% | 8.548%
4975 St. Roach Ave | Templeton | Jan '10 | 10007 | 10910 | 19712 |  | 4.923% | 10977.356 | 179.6% | 11880.356 | 165.9% | 8.84%
5515 Wickfield Dr | Camille | Jan '10 | 11108 | 10227 | 15310 |  | 6.338% | 12078.356 | 126.8% | 11197.356 | 136.7% | 8.034%
[8 empty] | MAX | 196.8% |  | 207.8%
[8 empty] | MIN | 105.3% |  | 94.68%
[8 empty] | AV | 144.8% |  | 142.3%
Dehumidification Calc
|  |  | Estimate of run hours | 876 | 10% of 8760
|  |  | Elec draw of unit (W) | 830 | from 115V, 8 Amps, 0.9 power factor. Energy used by fan compressor etc goes to space
|  |  | Amount above in BTU/hr | 2831.96
|  |  | Heat of moisture removal added to the space (Btus/hr) | 3000 | 3.3 lbs/hr removed, derated by 20%, 1000 Btus/lb of H20) | AHAM rated capacity (association of home appliance manufactureers) 80 degrees and 60 RH = 90 pounds per day , get pounds per hour, derate by 20% |  |  |  | full year not available
|  |  | Total BTUs/hr going into the space when dehumid is running | 5831.96 | [5 empty] | full year starting in May 10
|  |  | Amount of power used by EER 12 cooling system to remove (W) | 277.7124 | EER is ratio of output cooling in Btu/hr over Watts of electrical use | need to find data at part loads because of more mild outdoor conditions (lower temp outside than peak cooling because that is when it's using |  |  |  | full year not available
|  |  | Yearly kWh used for this cooling | 243.276 | [5 empty] | full year starting July 10
|  |  | Additional kWh used by compressor, fans, etc | 727.08
|  |  | Total additional kWh in yearly energy use from dehumid system | 970.356 | [5 empty] | full year not available
full year not available
|  |  | Energy factor (liters of water removed per kWh) | 1.6988
1 pint = 1 pound =0.47 L
Note on H4: Rosi: Estimate of percentage of real energy use that is dehumidificatoin

## dehumid calc
Variable | Value | Notes
Estimate of run hours | 876 | Estimated 10% of 8760 hours per year
Elec draw of unit (W) | 830 | from 115V, 8 Amps, 0.9 power factor. Energy used by fan compressor etc goes to space
Elec draw of unit (Btu/hr). This is also equal to additional heat going into the space from the fan and compressor. | 2831.96 | Multiply by 3.412
Heat of removed moistureadded to the space (Btu/hr) | 3000 | AHAM (Association of Home Appliance Manufacturers) rated capacity (at 80 degrees F and 60% RH) is 90 lbs/day = 3.75 lbs/hr, derated by 20% because of lower temperature actual conditions = 3 lbs/hr. Multiply by 1000 Btus/lb of H20 to get the heat of space moisture removal.
Total heat going into the space when dehumid is running (Btu/hr) | 5831.96 | Add the electric draw of the unit to the heat of moisture removed from the space
Amount of power used by EER 12 cooling system to remove this heat (W) | 485.9967 | Divide Btu/hr by EER 12 to get Watts. EER is ratio of output cooling in Btu/hr over Watts of electrical use
Yearly energy used used for this cooling (kWh) | 425.7331 | Multiply by the estimated run hours
Additional kWh used by compressor, fans, etc | 727.08 | Multiply elec draw of dehumidification unit by the estimated run hours
Total additional kWh in yearly energy use from dehumidification system | 1152.8131 | Add the yearly electrical draw of the dehumidification unit to the extra electricity used by the heat pump for cooling
Energy factor (liters of water removed per kWh) | 1.6988
1 pint = 1 pound =0.47 L

## BEopt and HERS
|  | Source Energy |  | Source energy
|  | Design model |  | BA Benchmark (Adjusted)
Homes types for which one year of data is available | BEopt kWh/yr | MMBtu/yr |  | MMBtu/yr |  | Modeled Reduction
B4 | 12168 | 139.7 | 150.8442 | 192.6 | 203.7442 | 25.96% | 11.4038
F3 | 10692 | 122.8 | 133.9442 | 169 | 180.1442 | 25.65%
H2 | 9503 | 109.1 | 120.2442 | 153.8 | 164.9442 | 27.1%
L2 | 9126 | 104.8 | 115.9442 | 150 | 161.1442 | 28.05%
L3 | 10822 | 124.3 | 135.4442 | 173.4 | 184.5442 | 26.61%
Gertrude | 11094 | 127.4 | 138.5442 | 170 | 181.1442 | 23.52%
Camille | 10227 | 117.4 | 128.5442 | 163 | 174.1442 | 26.19%
Templeton | 10910 | 125.3 | 136.4442 | 167.7 | 178.8442 | 23.71%
25.85%
| HERS Index | from Phil's energy gauge models
B4 | 64
F3 | 64
L2 | 64
L3 | 64
H2 | 67
Gertrude | 68
Templeton | 68
Camille | 69
Note on D2: Rosi: adjusted to include 970 kWh for dehumid
Note on F2: Rosi: Adjusted to include 970 kWh for dehumid

## Source energy weather adjusted
ADJUST ACTUAL ENERGY USE TO TMY3 WEATHER
|  | Site |  | Site | Source |  |  |  |  | from B10 |  |  |  |  | *Source energy ratio from Deru and Torcellini reference (also used in Kohta's report page 20
Jan 2010 to Dec 2010 |  | Actual | Actual TMY3 adjust | PHA Actual | PHA Prototype | BEopt Prototype Model | BEopt model Adjusted | B10 Benchmark | B10 Benchmark Adjusted | Reduction | Over BEopt models |  | Site energy | site energy | Source Energy* |  | MMBTU/yr
Address | Plan | kWh/yr | reduce 9.5% | MMBTU/yr | MMBtu/yr | MMBtu/yr | MMBtu/yr | MMBtu/yr |  |  |  | sf | kWh/sf | kBtu/sf | kBtu/sf | US Average | Southern Average | % below southern av
4313 St Bernard Ave | H2 | 9916 | 8973.98 | 30.6279 | 103.0629 | 109.1 | 120.2442 | 153.8 | 164.9442 | 37.52% | -16.67% | 1016 | 9.7598 | 33.3103 | 112.0893 | 197.9 | 220.5 | 53.26%
1207 Mandolin St | H2 | 12016 | 10874.48 | 37.1143 | 124.8895 | 109.1 | 120.2442 | 153.8 | 164.9442 | 24.28% | 3.72% | 1016 | 11.8268 | 40.3648 | 135.8275 |  | 220.5 | 43.36%
4253 St Bernard Ave | H2 | 12884 | 11660.02 | 39.7953 | 133.9112 | 109.1 | 120.2442 | 153.8 | 164.9442 | 18.81% | 10.21% | 1016 | 12.6811 | 43.2806 | 145.6392 |  | 220.5 | 39.27%
5749 Wildair Dr | Templeton | 12892 | 11667.26 | 39.82 | 133.9943 | 125.3 | 136.4442 | 167.7 | 178.8442 | 25.08% | -1.828% | 1213 | 10.6282 | 36.274 | 122.0621 |  | 220.5 | 39.23%
4341 St Bernard Ave | H2 | 13739 | 12433.795 | 42.4362 | 142.7977 | 109.1 | 120.2442 | 153.8 | 164.9442 | 13.43% | 15.79% | 1016 | 13.5226 | 46.1528 | 155.304 |  | 220.5 | 35.24%
4321 St Bernard Ave | F3 | 13960 | 12633.8 | 43.1188 | 145.0947 | 122.8 | 133.9442 | 169 | 180.1442 | 19.46% | 7.685% | 1248 | 11.1859 | 38.1775 | 128.4672 |  | 220.5 | 34.2%
4243 St Bernard Ave | H2 | 14482 | 13106.21 | 44.7311 | 150.5201 | 109.1 | 120.2442 | 153.8 | 164.9442 | 8.745% | 20.11% | 1016 | 14.2539 | 48.6487 | 163.7028 |  | 220.5 | 31.74%
4329 St Bernard Ave | L3 | 14567 | 13183.135 | 44.9936 | 151.4036 | 124.3 | 135.4442 | 173.4 | 184.5442 | 17.96% | 10.54% | 1377 | 10.5788 | 36.1054 | 121.4948 |  | 220.5 | 31.34%
4345 St Bernard Ave | L3 | 15076 | 13643.78 | 46.5658 | 156.6939 | 124.3 | 135.4442 | 173.4 | 184.5442 | 15.09% | 13.56% | 1377 | 10.9484 | 37.367 | 125.74 |  | 220.5 | 28.94%
5515 Wickfield Dr | Camille | 15310 | 13855.55 | 47.2886 | 159.126 | 117.4 | 128.5442 | 163 | 174.1442 | 8.624% | 19.22% | 1224 | 12.5082 | 42.6904 | 143.6531 |  | 220.5 | 27.83%
1463 Filmore Ave | Gertrude | 16649 | 15067.345 | 51.4244 | 173.0431 | 127.4 | 138.5442 | 170 | 181.1442 | 4.472% | 19.94% | 1316 | 12.6512 | 43.1786 | 145.296 |  | 220.5 | 21.52%
5705 Wildair Dr | Templeton | 16664 | 15080.92 | 51.4707 | 173.199 | 125.3 | 136.4442 | 167.7 | 178.8442 | 3.157% | 21.22% | 1213 | 13.7378 | 46.8872 | 157.7756 |  | 220.5 | 21.45%
1201 Mandolin St | L2 | 16958 | 15346.99 | 52.3788 | 176.2547 | 104.8 | 115.9442 | 150 | 161.1442 | -9.377% | 34.22% | 1067 | 15.8932 | 54.2433 | 182.5289 |  | 220.5 | 20.07%
4305 St Bernard Ave | L3 | 18415 | 16665.575 | 56.8791 | 191.3982 | 124.3 | 135.4442 | 173.4 | 184.5442 | -3.714% | 29.23% | 1377 | 13.3733 | 45.643 | 153.5887 |  | 220.5 | 13.2%
1218 Owens Blvd | H2 | 18288 | 16550.64 | 56.4868 | 190.0782 | 109.1 | 120.2442 | 153.8 | 164.9442 | -15.24% | 36.74% | 1016 | 18 | 61.434 | 206.7254 |  | 220.5 | 13.8%
4975 St. Roach Ave | Templeton | 19712 | 17839.36 | 60.8852 | 204.8787 | 125.3 | 136.4442 | 167.7 | 178.8442 | -14.56% | 33.4% | 1213 | 16.2506 | 55.4634 | 186.6342 |  | 220.5 | 7.085%
1212 Ownens Blvd | L2 | 20979 | 18985.995 | 64.7986 | 218.0473 | 104.8 | 115.9442 | 150 | 161.1442 | -35.31% | 46.83% | 1067 | 19.6617 | 67.1053 | 225.8092 |  | 220.5 | 1.112%
4317 St Bernard Ave | B4 | 21903 | 19822.215 | 67.6526 | 227.651 | 139.7 | 150.8442 | 192.6 | 203.7442 | -11.73% | 33.74% | 1551 | 14.1219 | 48.1979 | 162.1859 |  | 220.5 | -3.243%
4325 St Bernard Ave | B4 | 22104 | 20004.12 | 68.2734 | 229.7401 | 139.7 | 150.8442 | 192.6 | 203.7442 | -12.76% | 34.34% | 1551 | 14.2515 | 48.6402 | 163.6743 |  | 220.5 | -4.191%
Mean |  |  |  |  | 167.6728 | 118.9474 |  | 164.9105
standard deviation |  |  |  |  | #NAME? | #NAME? |  | #NAME?
[5 empty] | BEopt over B10 | 27.87% |  |  | MIN | -35.31% | -16.67%
[5 empty] | Actual over BEopt | 29.06% |  |  | MAX | 37.52% | 46.83%
[5 empty] | actual over B10 | 1.647% |  |  | AV | 4.944% | 19.58%
|  | BEopt design |  | B10 benchmark
Homes types for which one year of data is available | BEopt kWh/yr | MMBtu/yr |  | MMBtu/yr | Modeled Reduction
B4 | 12168 | 139.7 |  | 192.6 | 25.96%
F3 | 10692 | 122.8 |  | 169 | 25.65%
H2 | 9503 | 109.1 |  | 153.8 | 27.1%
L2 | 9126 | 104.8 |  | 150 | 28.05%
L3 | 10822 | 124.3 |  | 173.4 | 26.61%
Gertrude | 11094 | 127.4 |  | 170 | 23.52%
Camille | 10227 | 117.4 |  | 163 | 26.19%
Templeton | 10910 | 125.3 |  | 167.7 | 23.71%
Note on H3: Rosi: Added energy used be dehumidifier
Note on J3: Rosi: Add 970 kwh to account for dehumid

## TMY3 HDD CDD Worksheet
|  |  |  | 484.2917 | 0
Julian Date | Hour | Dry Bulb | Avg daily Temp | CDD | HDD
157 | 1 | 78 |  |  |  |  | #days | Joule # | Row # | HDD | CDD
157 | 2 | 78 |  |  |  | Jan | 31 | 1 | 4 | 0 | 484.2917
157 | 3 | 77 | [5 empty] | 31 | 751
157 | 4 | 79 |  |  |  | Feb | 28 | 32 | 771 | 0 | 0
157 | 5 | 77 | [5 empty] | 59 | 1419
157 | 6 | 79 |  |  |  | Mar | 31 | 60 | 1443 | 0 | 0
157 | 7 | 81 | [5 empty] | 90 | 2163
157 | 8 | 84 |  |  |  | Apr | 30 | 91 | 2187 | 0 | 0
157 | 9 | 86 | [5 empty] | 120 | 2883
157 | 10 | 85 |  |  |  | May | 31 | 121 | 2931 | 0 | 0
157 | 11 | 89 | [5 empty] | 151 | 3627
157 | 12 | 91 |  |  |  | Jun | 30 | 152 | 3651 | 0 | 0
157 | 13 | 89 | [5 empty] | 181 | 4347
157 | 14 | 90 |  |  |  | Jul | 31 | 182 | 4371 | 0 | 0
157 | 15 | 89 | [5 empty] | 212 | 5091
157 | 16 | 89 |  |  |  | Aug | 31 | 213 | 5115 | 0 | 0
157 | 17 | 86 | [5 empty] | 243 | 5835
157 | 18 | 83 |  |  |  | Sep | 30 | 244 | 5859 | 0 | 0
157 | 19 | 82 | [5 empty] | 273 | 6555
157 | 20 | 81 |  |  |  | Oct | 31 | 274 | 6579 | 0 | 0
157 | 21 | 80 | [5 empty] | 304 | 7299
157 | 22 | 80 |  |  |  | Nov | 30 | 305 | 7323 | 0 | 0
157 | 23 | 79 | [5 empty] | 334 | 8019
157 | 24 | 79 | 82.9583 | 17.9583 | -17.9583 | Dec | 31 | 335 | 8043 | 0 | 0
158 | 1 | 78 |  |  |  |  | 365 | 365 | 8763
158 | 2 | 77
158 | 3 | 78 |  |  |  | Total |  |  |  | 0 | 484.2917
158 | 4 | 77
158 | 5 | 77
158 | 6 | 77
158 | 7 | 81
158 | 8 | 83
158 | 9 | 85
158 | 10 | 87
158 | 11 | 88
158 | 12 | 88
158 | 13 | 86
158 | 14 | 89
158 | 15 | 82
158 | 16 | 78
158 | 17 | 83
158 | 18 | 81
158 | 19 | 80
158 | 20 | 80
158 | 21 | 79
158 | 22 | 78
158 | 23 | 77
158 | 24 | 76 | 81.0417 | 16.0417 | -16.0417
159 | 1 | 75
159 | 2 | 74
159 | 3 | 73
159 | 4 | 72
159 | 5 | 71
159 | 6 | 74
159 | 7 | 80
159 | 8 | 83
159 | 9 | 82
159 | 10 | 85
159 | 11 | 87
159 | 12 | 87
159 | 13 | 87
159 | 14 | 85
159 | 15 | 84
159 | 16 | 87
159 | 17 | 85
159 | 18 | 83
159 | 19 | 82
159 | 20 | 80
159 | 21 | 79
159 | 22 | 78
159 | 23 | 77
159 | 24 | 77 | 80.2917 | 15.2917 | -15.2917
160 | 1 | 76
160 | 2 | 73
160 | 3 | 74
160 | 4 | 74
160 | 5 | 73
160 | 6 | 75
160 | 7 | 80
160 | 8 | 83
160 | 9 | 84
160 | 10 | 84
160 | 11 | 73
160 | 12 | 74
160 | 13 | 77
160 | 14 | 77
160 | 15 | 82
160 | 16 | 82
160 | 17 | 81
160 | 18 | 81
160 | 19 | 79
160 | 20 | 79
160 | 21 | 78
160 | 22 | 77
160 | 23 | 76
160 | 24 | 75 | 77.7917 | 12.7917 | -12.7917
161 | 1 | 76
161 | 2 | 76
161 | 3 | 75
161 | 4 | 74
161 | 5 | 74
161 | 6 | 74
161 | 7 | 78
161 | 8 | 80
161 | 9 | 82
161 | 10 | 84
161 | 11 | 86
161 | 12 | 85
161 | 13 | 84
161 | 14 | 79
161 | 15 | 75
161 | 16 | 80
161 | 17 | 82
161 | 18 | 83
161 | 19 | 81
161 | 20 | 77
161 | 21 | 78
161 | 22 | 78
161 | 23 | 76
161 | 24 | 77 | 78.9167 | 13.9167 | -13.9167
162 | 1 | 74
162 | 2 | 74
162 | 3 | 74
162 | 4 | 73
162 | 5 | 73
162 | 6 | 73
162 | 7 | 77
162 | 8 | 81
162 | 9 | 82
162 | 10 | 84
162 | 11 | 87
162 | 12 | 80
162 | 13 | 73
162 | 14 | 73
162 | 15 | 78
162 | 16 | 82
162 | 17 | 84
162 | 18 | 83
162 | 19 | 81
162 | 20 | 78
162 | 21 | 77
162 | 22 | 77
162 | 23 | 76
162 | 24 | 76 | 77.9167 | 12.9167 | -12.9167
163 | 1 | 76
163 | 2 | 75
163 | 3 | 75
163 | 4 | 74
163 | 5 | 72
163 | 6 | 76
163 | 7 | 79
163 | 8 | 80
163 | 9 | 81
163 | 10 | 80
163 | 11 | 79
163 | 12 | 83
163 | 13 | 85
163 | 14 | 87
163 | 15 | 79
163 | 16 | 80
163 | 17 | 81
163 | 18 | 80
163 | 19 | 78
163 | 20 | 76
163 | 21 | 76
163 | 22 | 77
163 | 23 | 78
163 | 24 | 78 | 78.5417 | 13.5417 | -13.5417
164 | 1 | 78
164 | 2 | 78
164 | 3 | 78
164 | 4 | 77
164 | 5 | 77
164 | 6 | 77
164 | 7 | 79
164 | 8 | 82
164 | 9 | 82
164 | 10 | 85
164 | 11 | 86
164 | 12 | 87
164 | 13 | 72
164 | 14 | 74
164 | 15 | 74
164 | 16 | 77
164 | 17 | 78
164 | 18 | 80
164 | 19 | 78
164 | 20 | 77
164 | 21 | 76
164 | 22 | 77
164 | 23 | 76
164 | 24 | 76 | 78.375 | 13.375 | -13.375
165 | 1 | 75
165 | 2 | 74
165 | 3 | 76
165 | 4 | 74
165 | 5 | 75
165 | 6 | 76
165 | 7 | 78
165 | 8 | 82
165 | 9 | 84
165 | 10 | 86
165 | 11 | 84
165 | 12 | 85
165 | 13 | 80
165 | 14 | 78
165 | 15 | 82
165 | 16 | 83
165 | 17 | 84
165 | 18 | 83
165 | 19 | 82
165 | 20 | 79
165 | 21 | 75
165 | 22 | 76
165 | 23 | 75
165 | 24 | 74 | 79.1667 | 14.1667 | -14.1667
166 | 1 | 74
166 | 2 | 74
166 | 3 | 74
166 | 4 | 73
166 | 5 | 73
166 | 6 | 74
166 | 7 | 78
166 | 8 | 81
166 | 9 | 83
166 | 10 | 84
166 | 11 | 86
166 | 12 | 77
166 | 13 | 75
166 | 14 | 78
166 | 15 | 82
166 | 16 | 81
166 | 17 | 77
166 | 18 | 76
166 | 19 | 77
166 | 20 | 75
166 | 21 | 75
166 | 22 | 74
166 | 23 | 74
166 | 24 | 73 | 77 | 12 | -12
167 | 1 | 73
167 | 2 | 73
167 | 3 | 74
167 | 4 | 73
167 | 5 | 74
167 | 6 | 74
167 | 7 | 79
167 | 8 | 81
167 | 9 | 82
167 | 10 | 83
167 | 11 | 83
167 | 12 | 84
167 | 13 | 77
167 | 14 | 80
167 | 15 | 82
167 | 16 | 82
167 | 17 | 82
167 | 18 | 82
167 | 19 | 80
167 | 20 | 79
167 | 21 | 78
167 | 22 | 78
167 | 23 | 77
167 | 24 | 76 | 78.5833 | 13.5833 | -13.5833
168 | 1 | 77
168 | 2 | 74
168 | 3 | 74
168 | 4 | 74
168 | 5 | 75
168 | 6 | 79
168 | 7 | 80
168 | 8 | 82
168 | 9 | 82
168 | 10 | 85
168 | 11 | 85
168 | 12 | 86
168 | 13 | 88
168 | 14 | 88
168 | 15 | 89
168 | 16 | 89
168 | 17 | 88
168 | 18 | 86
168 | 19 | 84
168 | 20 | 84
168 | 21 | 82
168 | 22 | 82
168 | 23 | 82
168 | 24 | 81 | 82.3333 | 17.3333 | -17.3333
169 | 1 | 80
169 | 2 | 80
169 | 3 | 77
169 | 4 | 77
169 | 5 | 78
169 | 6 | 77
169 | 7 | 78
169 | 8 | 79
169 | 9 | 80
169 | 10 | 82
169 | 11 | 83
169 | 12 | 84
169 | 13 | 84
169 | 14 | 85
169 | 15 | 86
169 | 16 | 85
169 | 17 | 86
169 | 18 | 85
169 | 19 | 83
169 | 20 | 80
169 | 21 | 79
169 | 22 | 78
169 | 23 | 76
169 | 24 | 75 | 80.7083 | 15.7083 | -15.7083
170 | 1 | 73
170 | 2 | 73
170 | 3 | 71
170 | 4 | 74
170 | 5 | 73
170 | 6 | 75
170 | 7 | 79
170 | 8 | 82
170 | 9 | 84
170 | 10 | 85
170 | 11 | 87
170 | 12 | 87
170 | 13 | 88
170 | 14 | 87
170 | 15 | 84
170 | 16 | 81
170 | 17 | 84
170 | 18 | 83
170 | 19 | 82
170 | 20 | 81
170 | 21 | 79
170 | 22 | 79
170 | 23 | 78
170 | 24 | 77 | 80.25 | 15.25 | -15.25
171 | 1 | 76
171 | 2 | 76
171 | 3 | 76
171 | 4 | 76
171 | 5 | 75
171 | 6 | 76
171 | 7 | 79
171 | 8 | 81
171 | 9 | 84
171 | 10 | 84
171 | 11 | 86
171 | 12 | 87
171 | 13 | 86
171 | 14 | 86
171 | 15 | 87
171 | 16 | 87
171 | 17 | 85
171 | 18 | 84
171 | 19 | 82
171 | 20 | 81
171 | 21 | 79
171 | 22 | 79
171 | 23 | 78
171 | 24 | 77 | 81.125 | 16.125 | -16.125
172 | 1 | 78
172 | 2 | 78
172 | 3 | 78
172 | 4 | 78
172 | 5 | 78
172 | 6 | 78
172 | 7 | 79
172 | 8 | 82
172 | 9 | 83
172 | 10 | 83
172 | 11 | 83
172 | 12 | 85
172 | 13 | 82
172 | 14 | 82
172 | 15 | 80
172 | 16 | 82
172 | 17 | 83
172 | 18 | 83
172 | 19 | 77
172 | 20 | 78
172 | 21 | 78
172 | 22 | 78
172 | 23 | 78
172 | 24 | 78 | 80.0833 | 15.0833 | -15.0833
173 | 1 | 77
173 | 2 | 77
173 | 3 | 77
173 | 4 | 76
173 | 5 | 77
173 | 6 | 78
173 | 7 | 80
173 | 8 | 83
173 | 9 | 83
173 | 10 | 84
173 | 11 | 86
173 | 12 | 86
173 | 13 | 88
173 | 14 | 86
173 | 15 | 80
173 | 16 | 82
173 | 17 | 83
173 | 18 | 83
173 | 19 | 82
173 | 20 | 80
173 | 21 | 80
173 | 22 | 80
173 | 23 | 78
173 | 24 | 78 | 81 | 16 | -16
174 | 1 | 77
174 | 2 | 76
174 | 3 | 77
174 | 4 | 77
174 | 5 | 77
174 | 6 | 78
174 | 7 | 81
174 | 8 | 83
174 | 9 | 84
174 | 10 | 87
174 | 11 | 88
174 | 12 | 90
174 | 13 | 89
174 | 14 | 88
174 | 15 | 89
174 | 16 | 89
174 | 17 | 84
174 | 18 | 81
174 | 19 | 83
174 | 20 | 82
174 | 21 | 82
174 | 22 | 80
174 | 23 | 79
174 | 24 | 79 | 82.5 | 17.5 | -17.5
175 | 1 | 79
175 | 2 | 79
175 | 3 | 78
175 | 4 | 79
175 | 5 | 77
175 | 6 | 79
175 | 7 | 82
175 | 8 | 84
175 | 9 | 85
175 | 10 | 86
175 | 11 | 87
175 | 12 | 89
175 | 13 | 90
175 | 14 | 91
175 | 15 | 88
175 | 16 | 85
175 | 17 | 86
175 | 18 | 85
175 | 19 | 84
175 | 20 | 83
175 | 21 | 83
175 | 22 | 81
175 | 23 | 80
175 | 24 | 79 | 83.2917 | 18.2917 | -18.2917
176 | 1 | 79
176 | 2 | 78
176 | 3 | 79
176 | 4 | 77
176 | 5 | 75
176 | 6 | 76
176 | 7 | 79
176 | 8 | 81
176 | 9 | 86
176 | 10 | 87
176 | 11 | 88
176 | 12 | 88
176 | 13 | 88
176 | 14 | 84
176 | 15 | 85
176 | 16 | 84
176 | 17 | 80
176 | 18 | 75
176 | 19 | 74
176 | 20 | 76
176 | 21 | 77
176 | 22 | 75
176 | 23 | 75
176 | 24 | 75 | 80.0417 | 15.0417 | -15.0417
177 | 1 | 75
177 | 2 | 75
177 | 3 | 74
177 | 4 | 74
177 | 5 | 75
177 | 6 | 78
177 | 7 | 75
177 | 8 | 77
177 | 9 | 76
177 | 10 | 77
177 | 11 | 74
177 | 12 | 75
177 | 13 | 79
177 | 14 | 79
177 | 15 | 75
177 | 16 | 75
177 | 17 | 76
177 | 18 | 78
177 | 19 | 75
177 | 20 | 75
177 | 21 | 75
177 | 22 | 75
177 | 23 | 74
177 | 24 | 75 | 75.6667 | 10.6667 | -10.6667
178 | 1 | 75
178 | 2 | 76
178 | 3 | 77
178 | 4 | 77
178 | 5 | 78
178 | 6 | 80
178 | 7 | 80
178 | 8 | 81
178 | 9 | 83
178 | 10 | 85
178 | 11 | 87
178 | 12 | 89
178 | 13 | 90
178 | 14 | 90
178 | 15 | 90
178 | 16 | 88
178 | 17 | 87
178 | 18 | 86
178 | 19 | 84
178 | 20 | 82
178 | 21 | 81
178 | 22 | 81
178 | 23 | 80
178 | 24 | 79 | 82.75 | 17.75 | -17.75
179 | 1 | 79
179 | 2 | 79
179 | 3 | 79
179 | 4 | 78
179 | 5 | 78
179 | 6 | 79
179 | 7 | 81
179 | 8 | 84
179 | 9 | 84
179 | 10 | 86
179 | 11 | 89
179 | 12 | 88
179 | 13 | 90
179 | 14 | 89
179 | 15 | 90
179 | 16 | 90
179 | 17 | 89
179 | 18 | 87
179 | 19 | 85
179 | 20 | 83
179 | 21 | 82
179 | 22 | 81
179 | 23 | 81
179 | 24 | 81 | 83.8333 | 18.8333 | -18.8333
180 | 1 | 80
180 | 2 | 80
180 | 3 | 79
180 | 4 | 78
180 | 5 | 79
180 | 6 | 80
180 | 7 | 82
180 | 8 | 84
180 | 9 | 85
180 | 10 | 87
180 | 11 | 89
180 | 12 | 91
180 | 13 | 92
180 | 14 | 90
180 | 15 | 90
180 | 16 | 89
180 | 17 | 88
180 | 18 | 86
180 | 19 | 83
180 | 20 | 82
180 | 21 | 81
180 | 22 | 80
180 | 23 | 79
180 | 24 | 78 | 83.8333 | 18.8333 | -18.8333
181 | 1 | 78
181 | 2 | 78
181 | 3 | 78
181 | 4 | 77
181 | 5 | 77
181 | 6 | 78
181 | 7 | 81
181 | 8 | 83
181 | 9 | 85
181 | 10 | 87
181 | 11 | 88
181 | 12 | 89
181 | 13 | 90
181 | 14 | 91
181 | 15 | 91
181 | 16 | 88
181 | 17 | 87
181 | 18 | 87
181 | 19 | 84
181 | 20 | 82
181 | 21 | 81
181 | 22 | 81
181 | 23 | 80
181 | 24 | 80 | 83.375 | 18.375 | -18.375
182 | 1 | 80
182 | 2 | 80
182 | 3 | 79
182 | 4 | 79
182 | 5 | 79
182 | 6 | 81
182 | 7 | 83
182 | 8 | 85
182 | 9 | 86
182 | 10 | 88
182 | 11 | 90
182 | 12 | 90
182 | 13 | 89
182 | 14 | 87
182 | 15 | 86
182 | 16 | 84
182 | 17 | 87
182 | 18 | 86
182 | 19 | 84
182 | 20 | 82
182 | 21 | 78
182 | 22 | 79
182 | 23 | 80
182 | 24 | 80 | 83.4167 | 18.4167 | -18.4167
183 | 1 | 79
183 | 2 | 79
183 | 3 | 78
183 | 4 | 78
183 | 5 | 78
183 | 6 | 78
183 | 7 | 83
183 | 8 | 85
183 | 9 | 86
183 | 10 | 85
183 | 11 | 88
183 | 12 | 89
183 | 13 | 88
183 | 14 | 87
183 | 15 | 87
183 | 16 | 82
183 | 17 | 86
183 | 18 | 87
183 | 19 | 84
183 | 20 | 83
183 | 21 | 82
183 | 22 | 82
183 | 23 | 81
183 | 24 | 80 | 83.125 | 18.125 | -18.125
184 | 1 | 79
184 | 2 | 78
184 | 3 | 78
184 | 4 | 77
184 | 5 | 76
184 | 6 | 77
184 | 7 | 83
184 | 8 | 84
184 | 9 | 75
184 | 10 | 78
184 | 11 | 83
184 | 12 | 84
184 | 13 | 81
184 | 14 | 85
184 | 15 | 79
184 | 16 | 85
184 | 17 | 85
184 | 18 | 83
184 | 19 | 83
184 | 20 | 82
184 | 21 | 81
184 | 22 | 78
184 | 23 | 77
184 | 24 | 76 | 80.2917 | 15.2917 | -15.2917
185 | 1 | 77
185 | 2 | 77
185 | 3 | 77
185 | 4 | 77
185 | 5 | 77
185 | 6 | 78
185 | 7 | 82
185 | 8 | 84
185 | 9 | 83
185 | 10 | 84
185 | 11 | 86
185 | 12 | 88
185 | 13 | 88
185 | 14 | 80
185 | 15 | 81
185 | 16 | 85
185 | 17 | 81
185 | 18 | 79
185 | 19 | 79
185 | 20 | 78
185 | 21 | 77
185 | 22 | 77
185 | 23 | 77
185 | 24 | 76 | 80.3333 | 15.3333 | -15.3333
186 | 1 | 78
186 | 2 | 80
186 | 3 | 79
186 | 4 | 79
186 | 5 | 79
186 | 6 | 79
186 | 7 | 79
186 | 8 | 79
186 | 9 | 79
186 | 10 | 80
186 | 11 | 81
186 | 12 | 83
186 | 13 | 84
186 | 14 | 84
186 | 15 | 81
186 | 16 | 81
186 | 17 | 78
186 | 18 | 78
186 | 19 | 78
186 | 20 | 78
186 | 21 | 78
186 | 22 | 77
186 | 23 | 77
186 | 24 | 76 | 79.375 | 14.375 | -14.375
187 | 1 | 78
187 | 2 | 78
187 | 3 | 78
187 | 4 | 77
187 | 5 | 77
187 | 6 | 78
187 | 7 | 80
187 | 8 | 82
187 | 9 | 84
187 | 10 | 84
187 | 11 | 86
187 | 12 | 87
187 | 13 | 84
187 | 14 | 82
187 | 15 | 84
187 | 16 | 85
187 | 17 | 86
187 | 18 | 84
187 | 19 | 82
187 | 20 | 81
187 | 21 | 80
187 | 22 | 80
187 | 23 | 78
187 | 24 | 78 | 81.375 | 16.375 | -16.375
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0!

## 1207 Mandolin St.
1207 Mandolin Street |  |  |  |  | 3/18/09 Move in Date | [12 empty] | 1 yr hdd and cdd comparison
Plan H2 | [12 empty] | Average Indoor Conditions from EGUSA |  |  |  | Actual (Jan 2010-Dec 2010) | TMY3 | % diff
Phase I | [12 empty] | Phase I |  |  | HDD | 1796 | 1304 | 27.39%
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA) | [5 empty] | 1207 Mandolin |  |  | CDD | 3166 | 2705 | 14.56%
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD |  |  |  | Avg Temp | Avg %RH | DewPt, °F()
2009-07-01 | 06/10 - 07/09 | 1153 | 630 | 0 | Quoted from utility bill |  | 815 | 472 | 0
2009-08-01 | 07/10 - 08/09 | 1167 | 585 | 0 | Quoted from utility bill |  | 880 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 1029 | 519 | 0 | Quoted from utility bill |  | 854 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 976 | 456 | 0 | Quoted from utility bill |  | 649 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 828 | 142 | 55 | Quoted from utility bill |  | 536 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 1031 | 7 | 254 | Quoted from utility bill |  | 526 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 1210 | 5 | 529 | Quoted from utility bill |  | 855 | 6 | 438 | 750.4088 | 459.5912
2010-02-01 | 01/10 - 02/09 | 985 | 5 | 429 | Quoted from utility bill |  | 827 | 13 | 386 | 755.0274 | 229.9726
2010-03-01 | 02/10 - 03/09 | 948 | 0 | 455 | Quoted from utility bill |  | 600 | 36 | 207 | 770.2028 | 177.7972 |  | 74.0524 | 48.6866 | 52.4669
2010-04-01 | 03/10 - 04/09 | 769 | 50 | 118 | Quoted from utility bill |  | 564 | 80 | 91 | 799.234 | -30.234 |  | 74.0773 | 49.0377 | 52.8077
2010-05-01 | 04/10 - 05/09 | 932 | 229 | 0 | Quoted from utility bill |  | 593 | 212 | 6 | 886.3276 | 45.6724 |  | 73.5826 | 50.0149 | 53.4237
2010-06-01 | 05/10 - 06/10 | 1013 | 491 | 0 | Quoted from utility bill |  | 752 | 376 | 0 | 994.5348 | 18.4652 |  | 71.5482 | 56.7482 | 54.7504
2010-07-01 | 06/11 - 07/12 | 1239 | 601 | 0 | Quoted from utility bill |  | 871 | 505 | 0 | 1079.649 | 159.351 |  | 68.96 | 59.3487 | 54.3988
2010-08-01 | 07/13 - 08/10 | 1161 | 598 | 0 | Quoted from utility bill |  | 827 | 503 | 0 | 1078.3294 | 82.6706
2010-09-01 | 08/11 - 09/09 | 1072 | 546 | 0 | Quoted from utility bill |  | 826 | 488 | 0 | 1068.4324 | 3.5676
2010-10-01 | 09/10 - 10/07 | 897 | 392 | 0 | Quoted from utility bill |  | 607 | 304 | 0 | 947.0292 | -50.0292
2010-11-01 | 10/08 - 11/09 | 944 | 208 | 50 | Quoted from utility bill |  | 578 | 133 | 47 | 834.2034 | 109.7966
2010-12-01 | 11/09 - 12/09 | 846 | 41 | 215 | Quoted from utility bill |  | 549 | 49 | 129 | 778.7802 | 67.2198 |  | av of three lowest months
2011-01-01 | 12/09 - 01/12 | 1174 | 6 | 475 | Quoted from utility bill |  | 958 | 6 | 519 | 10742.159 |  |  | elec base loads
2011-02-01 | 01/12 - 02/10 | 1038 | 0 | 512 | Quoted from utility bill |  | 806 | 13 | 399 | 12016 |  | Actual | 814.3333
2011-03-01 | 02/10 - 03/15 | 947 |  |  | Quoted from utility bill | [6 empty] | EGUSA | 537
2011-04-01 | 03/15 - 04/12 | 862 |  |  | Quoted from utility bill |  |  |  |  | 10.6%
2011-05-01 | 04/12 - 05/11 | 949 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/10 | 1082 |  |  | Quoted from utility bill
2011-07-01 | 06/10 - 07/11 | 1156 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 1088 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1088 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 986 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/08 | 706 |  |  | Quoted from utility bill
2011-12-01 | 11/08 - 12/08 | 883 |  |  | Quoted from utility bill
2012-01-01 | 12/08 - 01/10 | 985 |  |  | Quoted from utility bill
2012-02-01 | 01/10 - 02/09 | 883 |  |  | Quoted from utility bill
| Total | 32027 | 5511 | 3092 |  |  | 14473 | 4700 | 2398
|  |  | 14.72% | 22.45%
| TMY2 | 8268 | 2485 | 1446 |  | TMY2 | 8268 | 2485 | 1446
| % less vs. actual | 74.18% | 54.91% | 53.23% |  | % less vs. actual | 42.87% | 47.13% | 39.7%
| TMY3 | 8452 | 2729 | 1349 |  | TMY3 | 8452 | 2729 | 1349
| % less vs. actual | 73.61% | 50.48% | 56.37% |  | % less vs. actual | 41.6% | 41.94% | 43.74%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Note on K11: Rosi: Use "actual" best fit equation but put in TMY3 CDD for the value of X to get new energy use by month
Note on C33: Philip G Kerrigan Jr: Same value for Aug and Sep appears to be a coincidence

## 1201 Mandolin St.
1201 Mandolin Street |  |  |  |  | 2/13/09 move in date
Plan L2
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-07-01 | 06/10 - 07/09 | 2527 | 630 | 0 | Quoted from utility bill |  | 887 | 472 | 0
2009-08-01 | 07/10 - 08/09 | 2074 | 585 | 0 | Quoted from utility bill |  | 950 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 1619 | 519 | 0 | Quoted from utility bill |  | 924 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 1675 | 456 | 0 | Quoted from utility bill |  | 746 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 1273 | 142 | 55 | Quoted from utility bill |  | 654 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 1582 | 7 | 254 | Quoted from utility bill |  | 659 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 2250 | 5 | 529 | Quoted from utility bill |  | 1002 | 6 | 438 | 873.9102
2010-02-01 | 01/10 - 02/09 | 1511 | 5 | 429 | Quoted from utility bill |  | 962 | 13 | 386 | 888.9721
2010-03-01 | 02/10 - 03/09 | 1718 | 0 | 455 | Quoted from utility bill |  | 723 | 36 | 207 | 938.4612
2010-04-01 | 03/10 - 04/09 | 1088 | 50 | 118 | Quoted from utility bill |  | 694 | 80 | 91 | 1033.136
2010-05-01 | 04/10 - 05/09 | 1313 | 229 | 0 | Quoted from utility bill |  | 698 | 212 | 6 | 1182.7796
2010-06-01 | 05/10 - 06/10 | 1678 | 491 | 0 | Quoted from utility bill |  | 853 | 376 | 0 | 1292.3808
2010-07-01 | 06/11 - 07/12 | 1965 | 601 | 0 | Quoted from utility bill |  | 887 | 505 | 0 | 1378.5915
2010-08-01 | 07/13 - 08/10 | 1386 | 598 | 0 | Quoted from utility bill |  | 892 | 503 | 0 | 1377.2549
2010-09-01 | 08/11 - 09/09 | 984 | 546 | 0 | Quoted from utility bill |  | 894 | 488 | 0 | 1367.2304
2010-10-01 | 09/10 - 10/07 | 842 | 392 | 0 | Quoted from utility bill |  | 697 | 304 | 0 | 1244.2632
2010-11-01 | 10/08 - 11/09 | 890 | 208 | 50 | Quoted from utility bill |  | 703 | 133 | 47 | 1129.9839
2010-12-01 | 11/09 - 12/09 | 1333 | 41 | 215 | Quoted from utility bill |  | 685 | 49 | 129 | 966.4333
2011-01-01 | 12/09 - 01/12 | 2547 | 6 | 475 | Quoted from utility bill |  | 1123 | 6 | 519 | 13673.3971 |  | elec base loads
2011-02-01 | 01/12 - 02/10 | 2449 | 0 | 512 | Quoted from utility bill |  | 936.7 | 13 | 399 | 16958 | Actual | 905.3333
2011-03-01 | 02/10 - 03/15 | 1294 |  |  | Quoted from utility bill | [5 empty] | EGUSA | 666
2011-04-01 | 03/15 - 04/12 | 1008 |  |  | Quoted from utility bill |  |  |  |  | 19.37%
2011-05-01 | 04/12 - 05/11 | 1123 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/10 | 1299 |  |  | Quoted from utility bill
2011-07-01 | 06/10 - 07/11 | 1844 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 1748 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1367 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 921 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/08 | 777 |  |  | Quoted from utility bill
2011-12-01 | 11/08 - 12/08 | 1288 |  |  | Quoted from utility bill
2012-01-01 | 12/08 - 01/10 | 1818 |  |  | Quoted from utility bill
2012-02-01 | 01/10 - 02/09 | 1398 |  |  | Quoted from utility bill
| Total | 48589 | 5511 | 3092 |  |  | 16569.7 | 4700 | 2398
|  |  | 14.72% | 22.45%
| TMY2 | 9600 | 2485 | 1446 |  | TMY2 | 9600 | 2485 | 1446
| % less vs. actual | 80.24% | 54.91% | 53.23% |  | % less vs. actual | 42.06% | 47.13% | 39.7%
| TMY3 | 9752 | 2729 | 1349 |  | TMY3 | 9752 | 2729 | 1349
| % less vs. actual | 79.93% | 50.48% | 56.37% |  | % less vs. actual | 41.15% | 41.94% | 43.74%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Note on K11: Rosi: Use "actual" best fit equation but put in TMY3 CDD for the value of X to get new energy use by month

## 4305 St Bernard Ave
4305 St. Bernard Avenue |  |  |  |  | 12/31/08 move in date
Plan L3
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-07-01 | 06/10 - 07/09 | 1646 | 630 | 0 | Quoted from utility bill |  | 1051 | 472 | 0
2009-08-01 | 07/10 - 08/09 | 1812 | 585 | 0 | Quoted from utility bill |  | 1123 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 1636 | 519 | 0 | Quoted from utility bill |  | 1095 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 1460 | 456 | 0 | Quoted from utility bill |  | 888 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 1267 | 142 | 55 | Quoted from utility bill |  | 791 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 1208 | 7 | 254 | Quoted from utility bill |  | 783 | 39 | 129 |  |  | HDD | CDD
2010-01-01 | 12/10 - 01/09 | 2464 | 5 | 529 | Quoted from utility bill |  | 1181 | 6 | 438 | 917.8102 |  | 1796 | 3159
2010-02-01 | 01/10 - 02/09 | 1591 | 5 | 429 | Quoted from utility bill |  | 1140 | 13 | 386 | 926.7821
2010-03-01 | 02/10 - 03/09 | 1533 | 0 | 455 | Quoted from utility bill |  | 862 | 36 | 207 | 956.2612
2010-04-01 | 03/10 - 04/09 | 1778 | 50 | 118 | Quoted from utility bill |  | 830 | 80 | 91 | 1012.656
2010-05-01 | 04/10 - 05/09 | 1425 | 229 | 0 | Quoted from utility bill |  | 831 | 212 | 6 | 1181.8404
2010-06-01 | 05/10 - 06/10 | 1619 | 491 | 0 | Quoted from utility bill |  | 1008 | 376 | 0 | 1392.0392
2010-07-01 | 06/11 - 07/12 | 2051 | 601 | 0 | Quoted from utility bill |  | 1051 | 505 | 0 | 1557.3785
2010-08-01 | 07/13 - 08/10 | 1778 | 598 | 0 | Quoted from utility bill |  | 1056 | 503 | 0 | 1554.8151
2010-09-01 | 08/11 - 09/09 | 1324 | 546 | 0 | Quoted from utility bill |  | 1059 | 488 | 0 | 1535.5896
2010-10-01 | 09/10 - 10/08 | 976 | 392 | 0 | Quoted from utility bill |  | 864 | 318 | 0 | 1317.7006
2010-11-01 | 10/09 - 11/09 | 882 | 201 | 50 | Quoted from utility bill |  | 816 | 118 | 47 | 1061.3606
2010-12-01 | 11/09 - 12/09 | 994 | 41 | 215 | Quoted from utility bill |  | 814 | 49 | 129 | 972.9233
2011-01-01 | 12/09 - 01/12 | 1678 | 6 | 475 | Quoted from utility bill |  | 1322 | 6 | 519 | 14387.1568 |  | elec base loads
2011-02-01 | 01/12 - 02/11 | 1795 | 0 | 537 | Quoted from utility bill |  | 1146.2 | 13 | 415 | 18415 | Actual | 882
2011-03-01 | 02/11 - 03/15 | 870 |  |  | Quoted from utility bill | [5 empty] | EGUSA | 796
2011-04-01 | 03/15 - 04/12 | 894 |  |  | Quoted from utility bill |  |  |  |  | 21.87%
2011-05-01 | 04/12 - 05/11 | 1064 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/13 | 1378 |  |  | Quoted from utility bill
2011-07-01 | 06/13 - 07/11 | 1370 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/11 | 1419 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1315 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 927 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/07 | 669 |  |  | Quoted from utility bill
2011-12-01 | 11/07 - 12/07 | 979 |  |  | Quoted from utility bill
2012-01-01 | 12/07 - 01/11 | 1349 |  |  | Quoted from utility bill
2012-02-01 | 01/11 - 02/08 | 815 |  |  | Quoted from utility bill
| Total | 43966 | 5504 | 3117 |  |  | 19711.2 | 4699 | 2414
|  |  | 14.63% | 22.55%
| TMY2 | 11399 | 2485 | 1446 |  | TMY2 | 11399 | 2485 | 1446
| % less vs. actual | 74.07% | 54.85% | 53.61% |  | % less vs. actual | 42.17% | 47.12% | 40.1%
| TMY3 | 11579 | 2729 | 1349 |  | TMY3 | 11579 | 2729 | 1349
| % less vs. actual | 73.66% | 50.42% | 56.72% |  | % less vs. actual | 41.26% | 41.92% | 44.12%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Note on K11: Rosi: Use "actual" best fit equation but put in TMY3 CDD for the value of X to get new energy use by month

## 4313 St Bernard Ave
4313 St. Bernard Avenue |  |  |  |  | 12/23/08 move in date
Plan H2
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments | BEopt kWh | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-07-01 | 06/10 - 07/09 | 1148 | 630 | 0 | Quoted from utility bill | 804.3384 | 815 | 472 | 0
2009-08-01 | 07/10 - 08/09 | 1179 | 585 | 0 | Quoted from utility bill | 859.4016 | 880 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 1029 | 519 | 0 | Quoted from utility bill | 837.8496 | 854 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 790 | 456 | 0 | Quoted from utility bill | 762.516 | 649 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 538 | 142 | 55 | Quoted from utility bill | 685.404 | 536 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 548 | 7 | 254 | Quoted from utility bill | 680.748 | 526 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 897 | 5 | 529 | Quoted from utility bill | 857.0928 | 855 | 6 | 438 | 701.7616
2010-02-01 | 01/10 - 02/09 | 608 | 5 | 429 | Quoted from utility bill | 1029.9264 | 827 | 13 | 386 | 655.0552
2010-03-01 | 02/10 - 03/09 | 653 | 0 | 455 | Quoted from utility bill | 816.84 | 600 | 36 | 207 | 494.2774
2010-04-01 | 03/10 - 04/09 | 439 | 50 | 118 | Quoted from utility bill | 718.152 | 564 | 80 | 91 | 390.0862
2010-05-01 | 04/10 - 05/09 | 735 | 229 | 0 | Quoted from utility bill | 672.4104 | 593 | 212 | 6 | 682.0084
2010-06-01 | 05/10 - 06/10 | 1007 | 491 | 0 | Quoted from utility bill | 748.2744 | 752 | 376 | 0 | 884.6632
2010-07-01 | 06/11 - 07/12 | 1153 | 601 | 0 | Quoted from utility bill | 804.3384 | 871 | 505 | 0 | 1044.0685
2010-08-01 | 07/13 - 08/10 | 1149 | 598 | 0 | Quoted from utility bill | 859.4016 | 827 | 503 | 0 | 1041.5971
2010-09-01 | 08/11 - 09/09 | 1107 | 546 | 0 | Quoted from utility bill | 837.8496 | 826 | 488 | 0 | 1023.0616
2010-10-01 | 09/10 - 10/08 | 915 | 392 | 0 | Quoted from utility bill | 762.516 | 633 | 318 | 0 | 812.9926
2010-11-01 | 10/09 - 11/09 | 696 | 201 | 50 | Quoted from utility bill | 685.404 | 553 | 118 | 47 | 565.8526
2010-12-01 | 11/09 - 12/09 | 557 | 41 | 215 | Quoted from utility bill | 680.748 | 549 | 49 | 129 | 424.2178
2011-01-01 | 12/09 - 01/12 | 833 | 6 | 475 | Quoted from utility bill | 857.0928 | 958 | 6 | 519 | 8719.6422 |  | elec base loads
2011-02-01 | 01/12 - 02/11 | 896 | 0 | 537 | Quoted from utility bill | 1029.9264 | 832 | 13 | 415 | 9916 | Actual | 508.3333
2011-03-01 | 02/11 - 03/15 | 546 | 109 | 49 | Quoted from utility bill | 816.84 | 677.9 | 40 | 226 |  | EGUSA | 537
2011-04-01 | 03/15 - 04/12 | 550 | 287 | 9 | Quoted from utility bill | 718.152 | 531.3 | 105 | 86 | 12.06%
2011-05-01 | 04/12 - 05/11 | 725 | 392 | 0 | Quoted from utility bill | 672.4104 | 602.1 | 224 | 28
2011-06-01 | 05/11 - 06/13 | 1006 | 608 | 0 | Quoted from utility bill | 672.4104 | 829 | 432 | 0
2011-07-01 | 06/13 - 07/11 | 916 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 867 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 848 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 705 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/07 | 366 |  |  | Quoted from utility bill
2011-12-01 | 11/07 - 12/07 | 428 |  |  | Quoted from utility bill
2012-01-01 | 12/07 - 01/11 | 680 |  |  | Quoted from utility bill
2012-02-01 | 01/11 - 02/08 | 490 |  |  | Quoted from utility bill
| Total | 25004 | 6900 | 3175 |  |  | 17140.3 | 5500 | 2754
|  |  | 20.29% | 13.26%
| TMY2 | 8268 | 2485 | 1446 |  | TMY2 | 8268 | 2485 | 1446
| % less vs. actual | 66.93% | 63.99% | 54.46% |  | % less vs. actual | 51.76% | 54.82% | 47.49%
| TMY3 | 8452 | 2729 | 1349 |  | TMY3 | 8452 | 2729 | 1349
| % less vs. actual | 66.2% | 60.45% | 57.51% |  | % less vs. actual | 50.69% | 50.38% | 51.02%
Notes:
- Aprilaire turned off 1.5 months ago, homeowner claimed it was not working. It appeared to be working when I turned it on but I ultimately left the unit off
- Aprilaire unit was set to 3 before it was turned off.
- Summer Setpoint is 70, winter is 75
- 2 occupants, home most of the time
- HOBOs installed
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Note on K11: Rosi: Use "actual" best fit equation but put in TMY3 CDD for the value of X to get new energy use by month

## 4317 St Bernard Ave
4317 St. Bernard Avenue |  |  |  |  | 01/21/2009 move in date
Plan B4
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-07-01 | 06/10 - 07/09 | 2396 | 630 | 0 | Quoted from utility bill |  | 1174 | 472 | 0
2009-08-01 | 07/10 - 08/09 | 2383 | 585 | 0 | Quoted from utility bill |  | 1255 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 1989 | 519 | 0 | Quoted from utility bill |  | 1221 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 1915 | 456 | 0 | Quoted from utility bill |  | 989 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 1306 | 142 | 55 | Quoted from utility bill |  | 863 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 1382 | 7 | 254 | Quoted from utility bill |  | 859 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 1807 | 5 | 529 | Quoted from utility bill |  | 1250 | 6 | 438 | 1305.6834
2010-02-01 | 01/10 - 02/09 | 1431 | 5 | 429 | Quoted from utility bill |  | 943 | 13 | 386 | 1318.3807
2010-03-01 | 02/10 - 03/09 | 1300 | 0 | 455 | Quoted from utility bill |  | 915 | 36 | 207 | 1360.1004
2010-04-01 | 03/10 - 04/09 | 1206 | 50 | 118 | Quoted from utility bill |  | 928 | 80 | 91 | 1439.912
2010-05-01 | 04/10 - 05/09 | 1730 | 229 | 0 | Quoted from utility bill |  | 1128 | 212 | 6 | 1679.3468
2010-06-01 | 05/10 - 06/10 | 2191 | 491 | 0 | Quoted from utility bill |  | 1174 | 376 | 0 | 1976.8264
2010-07-01 | 06/11 - 07/12 | 2558 | 601 | 0 | Quoted from utility bill |  | 1255 | 505 | 0 | 2210.8195
2010-08-01 | 07/13 - 08/10 | 2308 | 598 | 0 | Quoted from utility bill |  | 1181 | 503 | 0 | 2207.1917
2010-09-01 | 08/11 - 09/09 | 2278 | 546 | 0 | Quoted from utility bill |  | 1183 | 488 | 0 | 2179.9832
2010-10-01 | 09/10 - 10/08 | 1881 | 392 | 0 | Quoted from utility bill |  | 961 | 318 | 0 | 1871.6202
2010-11-01 | 10/09 - 11/09 | 1570 | 201 | 50 | Quoted from utility bill |  | 894 | 118 | 47 | 1508.8402
2010-12-01 | 11/09 - 12/10 | 1643 | 41 | 215 | Quoted from utility bill |  | 929 | 49 | 129 | 1383.6811
2011-01-01 | 12/09 - 01/12 | 1567 | 6 | 475 | Quoted from utility bill |  | 984 | 6 | 519 | 20442.3856 |  | elec base loads
2011-02-01 | 01/12 - 02/11 | 1571 | 0 | 537 | Quoted from utility bill |  | 1256.9 | 13 | 415 | 21903 | Actual | 1079.3333
2011-03-01 | 02/11 - 03/15 | 1394 |  |  | Quoted from utility bill | [5 empty] | EGUSA | 872
2011-04-01 | 03/15 - 04/12 | 893 |  |  | Quoted from utility bill |  |  |  |  | 6.669%
2011-05-01 | 04/12 - 05/11 | 1139 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/13 | 1568 |  |  | Quoted from utility bill
2011-07-01 | 06/13 - 07/11 | 1540 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 1475 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1505 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 1088 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/07 | 921 |  |  | Quoted from utility bill
2011-12-01 | 11/07 - 12/07 | 1254 |  |  | Quoted from utility bill
2012-01-01 | 12/07 - 01/11 | 1485 |  |  | Quoted from utility bill
2012-02-01 | 01/11 - 02/08 | 1151 |  |  | Quoted from utility bill
| Total | 51825 | 5504 | 3117 |  |  | 21342.9 | 4699 | 2414
|  |  | 14.63% | 22.55%
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 75.69% | 54.85% | 53.61% |  | % less vs. actual | 40.96% | 47.12% | 40.1%
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 75.27% | 50.42% | 56.72% |  | % less vs. actual | 39.95% | 41.92% | 44.12%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Note on K11: Rosi: Use "actual" best fit equation but put in TMY3 CDD for the value of X to get new energy use by month

## 4321 St Bernard Ave
4321 St Bernard Avenue |  |  |  |  | 03/20/2009 move in date
Plan F3
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-08-01 | 07/10 - 08/09 | 1222 | 585 | 0 | Quoted from utility bill |  | 1026 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 989 | 519 | 0 | Quoted from utility bill |  | 1022 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 978 | 456 | 0 | Quoted from utility bill |  | 816 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 996 | 142 | 55 | Quoted from utility bill |  | 767 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 1049 | 7 | 254 | Quoted from utility bill |  | 796 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 1711 | 5 | 529 | Quoted from utility bill |  | 936 | 6 | 438 | 830.443
2010-02-01 | 01/10 - 02/09 | 1150 | 5 | 429 | guess from bar graph on utility bill |  | 968 | 13 | 386 | 836.2215
2010-03-01 | 02/10 - 03/09 | 1070 | 0 | 455 | guess from bar graph on utility bill |  | 743 | 36 | 207 | 855.208
2010-04-01 | 03/10 - 04/09 | 960 | 50 | 118 | guess from bar graph on utility bill |  | 777 | 80 | 91 | 891.53
2010-05-01 | 04/10 - 05/09 | 1060 | 229 | 0 | guess from bar graph on utility bill |  | 804 | 212 | 6 | 1000.496
2010-06-01 | 05/10 - 06/10 | 1100 | 491 | 0 | guess from bar graph on utility bill |  | 1015 | 376 | 0 | 1135.878
2010-07-01 | 06/11 - 07/12 | 1400 | 601 | 0 | guess from bar graph on utility bill |  | 1046 | 505 | 0 | 1242.3675
2010-08-01 | 07/13 - 08/10 | 1424 | 598 | 0 | Quoted from utility bill |  | 963 | 503 | 0 | 1240.7165
2010-09-01 | 08/11 - 09/09 | 1271 | 546 | 0 | Quoted from utility bill |  | 988 | 488 | 0 | 1228.334
2010-10-01 | 09/10 - 10/08 | 1098 | 392 | 0 | Quoted from utility bill |  | 790 | 318 | 0 | 1087.999
2010-11-01 | 10/09 - 11/09 | 790 | 201 | 50 | Quoted from utility bill |  | 793 | 118 | 47 | 922.899
2010-12-01 | 11/09 - 12/10 | 926 | 41 | 215 | Quoted from utility bill |  | 852 | 49 | 129 | 865.9395
2011-01-01 | 12/09 - 01/12 | 1127 | 6 | 475 | Quoted from utility bill |  | 1036 | 6 | 519 | 12138.032 |  | elec base loads
[10 empty] | 13960 | Actual | 898
| Total | 20321 | 4874 | 2580 |  |  | 16138 | 4214 | 1999 |  | EGUSA | 762.3333
|  |  | 13.54% | 22.52% | [5 empty] | 13.05%
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 38% | 49.02% | 43.95% |  | % less vs. actual | 21.92% | 41.03% | 27.66%
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 36.93% | 44.01% | 47.71% |  | % less vs. actual | 20.58% | 35.24% | 32.52%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Note on K11: Rosi: Use "actual" best fit equation but put in TMY3 CDD for the value of X to get new energy use by month

## 4325 St Bernard Ave
4325 St. Bernard Avenue |  |  |  |  | 05/08/2009 move in date
Plan B4
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-08-01 | 07/10 - 08/09 | 2012 | 585 | 0 | Quoted from utility bill |  | 1255 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 1613 | 519 | 0 | Quoted from utility bill |  | 1221 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 1477 | 456 | 0 | Quoted from utility bill |  | 989 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 1158 | 142 | 55 | Quoted from utility bill |  | 863 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 1533 | 7 | 254 | Quoted from utility bill |  | 859 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 2017 | 5 | 529 | Quoted from utility bill |  | 1250 | 6 | 438
2010-02-01 | 01/10 - 02/09 | 1463 | 5 | 429 | Quoted from utility bill |  | 943 | 13 | 386
2010-03-01 | 02/10 - 03/09 | 1362 | 0 | 455 | Quoted from utility bill |  | 915 | 36 | 207
2010-04-01 | 03/10 - 04/09 | 1283 | 50 | 118 | Quoted from utility bill |  | 928 | 80 | 91
2010-05-01 | 04/10 - 05/09 | 1345 | 229 | 0 | Quoted from utility bill |  | 1128 | 212 | 6
2010-06-01 | 05/10 - 06/10 | 1828 | 491 | 0 | Quoted from utility bill |  | 1174 | 376 | 0
2010-07-01 | 06/11 - 07/12 | 2365 | 601 | 0 | Quoted from utility bill |  | 1255 | 505 | 0
2010-08-01 | 07/13 - 08/10 | 2425 | 598 | 0 | Quoted from utility bill |  | 1181 | 503 | 0
2010-09-01 | 08/11 - 09/09 | 2313 | 546 | 0 | Quoted from utility bill |  | 1183 | 488 | 0
2010-10-01 | 09/10 - 10/08 | 2089 | 392 | 0 | Quoted from utility bill |  | 961 | 318 | 0
2010-11-01 | 10/09 - 11/09 | 1785 | 201 | 50 | Quoted from utility bill |  | 894 | 118 | 47
2010-12-01 | 11/09 - 12/10 | 1829 | 41 | 215 | Quoted from utility bill |  | 929 | 49 | 129
2011-01-01 | 12/09 - 01/12 | 1977 | 6 | 475 | Quoted from utility bill |  | 984 | 6 | 519 |  | elec base loads
2011-02-01 | 01/09 - 02/11 | 1686 | 0 | 601 | Quoted from utility bill |  | 1389 | 13 | 467 | Actual | 1394.6667
2011-03-01 | 02/11 - 03/15 | 1694 |  |  | Quoted from utility bill |  |  |  |  | EGUSA | 879
2011-04-01 | 03/11 - 04/12 | 1681 |  |  | Quoted from utility bill
2011-05-01 | 04/12 - 05/11 | 1876 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/13 | 2298 |  |  | Quoted from utility bill
2011-07-01 | 06/13 - 07/11 | 2150 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 2119 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 2299 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 2200 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/07 | 1436 |  |  | Quoted from utility bill
2011-12-01 | 11/07 - 12/07 | 1415 |  |  | Quoted from utility bill
2012-01-01 | 12/07 - 01/11 | 1430 |  |  | Quoted from utility bill
2012-02-01 | 01/11 - 02/08 | 1131 |  |  | Quoted from utility bill
| Total | 55289 | 4874 | 3181 |  |  | 20301 | 4227 | 2466
|  |  | 13.27% | 22.48%
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 77.21% | 49.02% | 54.54% |  | % less vs. actual | 37.93% | 41.21% | 41.36%
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 76.82% | 44.01% | 57.59% |  | % less vs. actual | 36.87% | 35.44% | 45.3%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 4329 St Bernard Ave
4329 St. Bernard Avenue |  |  |  |  | 2/11/09 move in date
Plan L3
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-07-01 | 06/10 - 07/09 | 1994 | 630 | 0 | Quoted from utility bill |  | 1051 | 472 | 0
2009-08-01 | 07/10 - 08/09 | 1922 | 585 | 0 | Quoted from utility bill |  | 1123 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 1672 | 519 | 0 | Quoted from utility bill |  | 1095 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 1410 | 456 | 0 | Quoted from utility bill |  | 888 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 1269 | 142 | 55 | Quoted from utility bill |  | 791 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 1402 | 7 | 254 | Quoted from utility bill |  | 783 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 1716 | 5 | 529 | Quoted from utility bill |  | 1181 | 6 | 438
2010-02-01 | 01/10 - 02/09 | 1280 | 5 | 429 | guess from bar graph on utility bill |  | 1140 | 13 | 386
2010-03-01 | 02/10 - 03/09 | 1280 | 0 | 455 | guess from bar graph on utility bill |  | 862 | 36 | 207
2010-04-01 | 03/10 - 04/09 | 1020 | 50 | 118 | guess from bar graph on utility bill |  | 830 | 80 | 91
2010-05-01 | 04/10 - 05/09 | 940 | 229 | 0 | guess from bar graph on utility bill |  | 831 | 212 | 6
2010-06-01 | 05/10 - 06/10 | 1170 | 491 | 0 | guess from bar graph on utility bill |  | 1008 | 376 | 0
2010-07-01 | 06/11 - 07/12 | 1414 | 601 | 0 | Quoted from utility bill |  | 1051 | 505 | 0
2010-08-01 | 07/13 - 08/10 | 1357 | 598 | 0 | Quoted from utility bill |  | 1056 | 503 | 0
2010-09-01 | 08/11 - 09/09 | 1221 | 546 | 0 | Quoted from utility bill |  | 1059 | 488 | 0
2010-10-01 | 09/10 - 10/08 | 992 | 392 | 0 | Quoted from utility bill |  | 864 | 318 | 0
2010-11-01 | 10/09 - 11/09 | 976 | 201 | 50 | Quoted from utility bill |  | 816 | 118 | 47
2010-12-01 | 11/09 - 12/09 | 1201 | 41 | 215 | Quoted from utility bill |  | 814 | 49 | 129
2011-01-01 | 12/09 - 01/12 | 1701 | 6 | 475 | Quoted from utility bill |  | 1322 | 6 | 519 |  | elec base loads
[10 empty] | Actual | 969.3333
| Total | 25937 | 5504 | 2580 |  |  | 18565 | 4686 | 1999 | EGUSA | 796
|  |  | 14.86% | 22.52%
| TMY2 | 11399 | 2485 | 1446 |  | TMY2 | 11399 | 2485 | 1446
| % less vs. actual | 56.05% | 54.85% | 43.95% |  | % less vs. actual | 38.6% | 46.97% | 27.66%
| TMY3 | 11579 | 2729 | 1349 |  | TMY3 | 11579 | 2729 | 1349
| % less vs. actual | 55.36% | 50.42% | 47.71% |  | % less vs. actual | 37.63% | 41.76% | 32.52%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 4341 St Bernard Ave
4341 St. Bernard Avenue |  |  |  |  | 3/11/09 move in date
Plan H2
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-08-01 | 07/10 - 08/09 | 811 | 585 | 0 | Quoted from utility bill |  | 880 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 717 | 519 | 0 | Quoted from utility bill |  | 854 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 650 | 456 | 0 | Quoted from utility bill |  | 649 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 671 | 142 | 55 | Quoted from utility bill |  | 536 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 1133 | 7 | 254 | Quoted from utility bill |  | 526 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 2233 | 5 | 529 | Quoted from utility bill |  | 855 | 6 | 438
2010-02-01 | 01/10 - 02/09 | 1562 | 5 | 429 | Quoted from utility bill |  | 827 | 13 | 386
2010-03-01 | 02/10 - 03/09 | 1608 | 0 | 455 | Quoted from utility bill |  | 600 | 36 | 207
2010-04-01 | 03/10 - 04/09 | 895 | 50 | 118 | Quoted from utility bill |  | 564 | 80 | 91
2010-05-01 | 04/10 - 05/09 | 872 | 229 | 0 | Quoted from utility bill |  | 593 | 212 | 6
2010-06-01 | 05/10 - 06/10 | 820 | 491 | 0 | guess from bar graph on utility bill |  | 752 | 376 | 0
2010-07-01 | 06/11 - 07/12 | 900 | 601 | 0 | guess from bar graph on utility bill |  | 871 | 505 | 0
2010-08-01 | 07/13 - 08/10 | 952 | 598 | 0 | Quoted from utility bill |  | 827 | 503 | 0
2010-09-01 | 08/11 - 09/09 | 980 | 546 | 0 | Quoted from utility bill |  | 826 | 488 | 0
2010-10-01 | 09/10 - 10/08 | 883 | 392 | 0 | Quoted from utility bill |  | 633 | 318 | 0
2010-11-01 | 10/09 - 11/09 | 847 | 201 | 50 | Quoted from utility bill |  | 553 | 118 | 47
2010-12-01 | 11/09 - 12/09 | 1187 | 41 | 215 | Quoted from utility bill |  | 549 | 49 | 129
2011-01-01 | 12/09 - 01/12 | 2063 | 6 | 475 | Quoted from utility bill |  | 958 | 6 | 519 |  | elec base loads
2011-02-01 | 1/12 - 02/11 | 2326 | 0 | 537 | Quoted from utility bill |  | 832.8 | 13 | 415 | Actual | 682.6667
2011-03-01 | 2/11 - 03/15 | 1053 |  |  | Quoted from utility bill |  |  |  |  | EGUSA | 537
2011-04-01 | 3/15 - 04/12 | 766 |  |  | Quoted from utility bill
2011-05-01 | 4/12 - 05/11 | 727 |  |  | Quoted from utility bill
| Total | 24656 | 4874 | 3117 |  |  | 13685.8 | 4227 | 2414
|  |  | 13.27% | 22.55%
| TMY2 | 11399 | 2485 | 1446 |  | TMY2 | 11399 | 2485 | 1446
| % less vs. actual | 53.77% | 49.02% | 53.61% |  | % less vs. actual | 16.71% | 41.21% | 40.1%
| TMY3 | 11579 | 2729 | 1349 |  | TMY3 | 11579 | 2729 | 1349
| % less vs. actual | 53.04% | 44.01% | 56.72% |  | % less vs. actual | 15.39% | 35.44% | 44.12%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 4345 St Bernard Ave
4345 St. Bernard Avenue |  |  |  |  | 8/26/09 move in date
Plan L3
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-07-01 | 06/10 - 07/09 |  | 630 | 0 | Quoted from utility bill |  | 1051 | 472 | 0
2009-08-01 | 07/10 - 08/09 |  | 585 | 0 | Quoted from utility bill |  | 1123 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 229 | 519 | 0 | Quoted from utility bill |  | 1095 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 668 | 456 | 0 | Quoted from utility bill |  | 888 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 474 | 142 | 55 | Quoted from utility bill |  | 791 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 562 | 7 | 254 | Quoted from utility bill |  | 783 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 1251 | 5 | 529 | Quoted from utility bill |  | 1181 | 6 | 438
2010-02-01 | 01/10 - 02/09 | 821 | 5 | 429 | Quoted from utility bill |  | 1140 | 13 | 386
2010-03-01 | 02/10 - 03/09 | 814 | 0 | 455 | Quoted from utility bill |  | 862 | 36 | 207
2010-04-01 | 03/10 - 04/09 | 819 | 50 | 118 | Quoted from utility bill |  | 830 | 80 | 91
2010-05-01 | 04/10 - 05/09 | 1124 | 229 | 0 | Quoted from utility bill |  | 831 | 212 | 6
2010-06-01 | 05/10 - 06/10 | 1527 | 491 | 0 | Quoted from utility bill |  | 1008 | 376 | 0
2010-07-01 | 06/11 - 07/12 | 1809 | 601 | 0 | Quoted from utility bill |  | 1051 | 505 | 0
2010-08-01 | 07/13 - 08/10 | 1900 | 598 | 0 | Quoted from utility bill |  | 1056 | 503 | 0
2010-09-01 | 08/11 - 09/09 | 1598 | 546 | 0 | Quoted from utility bill |  | 1059 | 488 | 0
2010-10-01 | 09/10 - 10/08 | 1182 | 392 | 0 | Quoted from utility bill |  | 864 | 318 | 0
2010-11-01 | 10/09 - 11/09 | 1024 | 201 | 50 | Quoted from utility bill |  | 816 | 118 | 47
2010-12-01 | 11/09 - 12/09 | 1207 | 41 | 215 | Quoted from utility bill |  | 814 | 49 | 129
2011-01-01 | 12/09 - 01/12 | 1928 | 6 | 475 | Quoted from utility bill |  | 1322 | 6 | 519 |  | elec base loads
2011-02-01 | 01/12 - 02/11 | 1848 | 0 | 537 | Quoted from utility bill |  | 1146.2 | 13 | 415 | Actual | 853.3333
2011-03-01 | 02/11 - 03/15 | 1147 |  |  | Quoted from utility bill |  |  |  |  | EGUSA | 796
2011-04-01 | 03/15 - 04/12 | 927 |  |  | Quoted from utility bill
2011-05-01 | 04/12 - 05/11 | 1220 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/13 | 1553 |  |  | Quoted from utility bill
2011-07-01 | 06/13 - 07/11 | 1541 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 1597 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1614 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 1203 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/07 | 770 |  |  | Quoted from utility bill
2011-12-01 | 11/07 - 12/07 | 1032 |  |  | Quoted from utility bill
2012-01-01 | 12/07 - 01/11 | 1417 |  |  | Quoted from utility bill
2012-02-01 | 01/11 - 02/08 | 968 |  |  | Quoted from utility bill
| Total | 35774 | 5504 | 3117 |  |  | 19711.2 | 4699 | 2414
|  |  | 14.63% | 22.55%
| TMY2 | 11399 | 2485 | 1446 | SHADED AREA NO T | TMY2 | 11399 | 2485 | 1446
| % less vs. actual | 68.14% | 54.85% | 53.61% | ACCURATE DUE TO A | % less vs. actual | 42.17% | 47.12% | 40.1%
LACK OF
| TMY3 | 11579 | 2729 | 1349 | A FULL YEAR OF | TMY3 | 11579 | 2729 | 1349
| % less vs. actual | 67.63% | 50.42% | 56.72% | UTILITLIES | % less vs. actual | 41.26% | 41.92% | 44.12%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 1206 Owens Blvd
1206 Owens Boulevard |  |  |  |  | 6/4/2010 move in date
Plan L3
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2010-06-01 | 05/11 - 06/13 | 113 |  |  | Quoted from utility bill
2010-07-01 | 06/11 - 07/12 | 716 | 601 | 0 | Quoted from utility bill |  | 1051 | 505 | 0
2010-08-01 | 07/13 - 08/10 | 1101 | 598 | 0 | Quoted from utility bill |  | 1056 | 503 | 0
2010-09-01 | 08/11 - 09/09 | 1063 | 546 | 0 | Quoted from utility bill |  | 1059 | 488 | 0
2010-10-01 | 09/10 - 10/08 | 1068 | 392 | 0 | Quoted from utility bill |  | 864 | 318 | 0
2010-11-01 | 10/09 - 11/09 | 2525 | 201 | 50 | Quoted from utility bill |  | 816 | 118 | 47
2010-12-01 | 11/09 - 12/09 | 1501 | 41 | 215 | Quoted from utility bill |  | 814 | 49 | 129
2011-01-01 | 12/09 - 01/12 | 2261 | 6 | 475 | Quoted from utility bill |  | 1322 | 6 | 519
2011-02-01 | 01/13 - 02/10 | 1930 | 0 | 537 | Quoted from utility bill |  | 1067.8 | 13 | 380
2011-03-01 | 02/10 - 03/15 | 1541 |  |  | Quoted from utility bill
2011-04-01 | 03/15 - 04/12 | 1430 |  |  | Quoted from utility bill
2011-05-01 | 04/12 - 05/11 | 1480 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/13 | 1871 |  |  | Quoted from utility bill
2011-07-01 | 06/13 - 07/11 | 1781 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 1888 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1932 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 1700 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/08 | 1342 |  |  | Quoted from utility bill
2011-12-01 | 11/08 - 12/08 | 1474 |  |  | Quoted from utility bill
2012-01-01 | 12/08 - 01/10 | 1648 |  |  | Quoted from utility bill
2012-02-01 | 01/10 - 02/09 | 1319 |  |  | Quoted from utility bill
| Total | 31684 | 2385 | 1277 |  |  | 8049.8 | 2000 | 1075
|  |  | 16.14% | 15.82%
| TMY2 | 11399 | 2485 | 1446 | SHADED AREA NO T | TMY2 | 11399 | 2485 | 1446
| % less vs. actual | 64.02% | -4.193% | -13.23% | ACCURATE DUE TO A | % less vs. actual | -41.61% | -24.25% | -34.51%
LACK OF
| TMY3 | 11579 | 2729 | 1349 | A FULL YEAR OF | TMY3 | 11579 | 2729 | 1349
| % less vs. actual | 63.45% | -14.42% | -5.638% | UTILITLIES | % less vs. actual | -43.84% | -36.45% | -25.49%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 1212 Owens Blvd
1212 Owens Boulevard |  |  |  |  | 3/12/09 move in date
Plan L2
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments | BEopt kWh | EGUSA kWh | EGUSA CDD | EGUSA HDD | Adjusted BEopt
2009-07-01 | 06/10 - 07/09 | 1626 | 630 | 0 | Quoted from utility bill | 768.2832 | 887 | 472 | 0 | 1610.1672
2009-08-01 | 07/10 - 08/09 | 2017 | 585 | 0 | Quoted from utility bill | 813.132 | 950 | 533 | 0 | 1687.8648
2009-09-01 | 08/10 - 09/09 | 1674 | 519 | 0 | Quoted from utility bill | 786.5496 | 924 | 505 | 0 | 1663.6224
2009-10-01 | 09/10 - 10/09 | 1723 | 456 | 0 | Quoted from utility bill | 728.7864 | 746 | 324 | 0 | 1558.0896
2009-11-01 | 10/10 - 11/09 | 1401 | 142 | 55 | Quoted from utility bill | 676.98 | 654 | 103 | 47 | 1556.3304
2009-12-01 | 11/10 - 12/09 | 1365 | 7 | 254 | Quoted from utility bill | 674.4984 | 659 | 39 | 129 | 1472.484
2010-01-01 | 12/10 - 01/09 | 1880 | 5 | 529 | Quoted from utility bill | 812.124 | 1002 | 6 | 438 | 1479
2010-02-01 | 01/10 - 02/09 | 1363 | 5 | 429 | Quoted from utility bill | 960.972 | 962 | 13 | 386 | 1576.5384
2010-03-01 | 02/10 - 03/09 | 1443 | 0 | 455 | Quoted from utility bill | 770.9376 | 723 | 36 | 207 | 1388.2224
2010-04-01 | 03/10 - 04/09 | 1288 | 50 | 118 | Quoted from utility bill | 703.4184 | 694 | 80 | 91 | 1532.0952
2010-05-01 | 04/10 - 05/09 | 1758 | 229 | 0 | Quoted from utility bill | 668.8392 | 698 | 212 | 6 | 1551.9552
2010-06-01 | 05/10 - 06/10 | 2324 | 491 | 0 | Quoted from utility bill | 732.2472 | 853 | 376 | 0 | 1679.4984
2010-07-01 | 06/11 - 07/12 | 2520 | 601 | 0 | Quoted from utility bill | 768.2832 | 887 | 505 | 0 | 1610.1672
2010-08-01 | 07/13 - 08/10 | 2419 | 598 | 0 | Quoted from utility bill | 813.132 | 892 | 503 | 0 | 1687.8648
2010-09-01 | 08/11 - 09/09 | 2057 | 546 | 0 | Quoted from utility bill | 786.5496 | 894 | 488 | 0 | 1663.6224
2010-10-01 | 09/10 - 10/07 | 1096 | 392 | 0 | Quoted from utility bill | 728.7864 | 697 | 304 | 0 | 1558.0896
2010-11-01 | 10/08 - 11/09 | 1421 | 208 | 50 | Quoted from utility bill | 676.98 | 703 | 133 | 47 | 1556.3304
2010-12-01 | 11/09 - 12/09 | 1410 | 41 | 215 | Quoted from utility bill | 674.4984 | 685 | 49 | 129 | 1472.484
2011-01-01 | 12/09 - 01/12 | 1706 | 6 | 475 | Quoted from utility bill | 812.124 | 1123 | 6 | 519 | 1479
2011-02-01 | 01/13 - 02/10 | 1488 | 0 | 537 | Quoted from utility bill | 960.972 | 901.8 | 13 | 380 | 1576.5384 |  | 2010-02-01 | 01/10 - 02/09 | 1576.5384
2011-03-01 | 02/10 - 03/15 | 1408 | 88 | 154 | Quoted from utility bill | 770.9376 | 812.4 | 40 | 247 | 1388.2224 |  | 2010-03-01 | 02/10 - 03/09 | 1388.2224
2011-04-01 | 03/15 - 04/12 | 1160 | 182 | 15 | Quoted from utility bill | 703.4184 | 645 | 101 | 64 | 1532.0952 |  | 2010-04-01 | 03/10 - 04/09 | 1532.0952
2011-05-01 | 04/12 - 05/11 | 1336 | 317 | 0 | Quoted from utility bill | 668.8392 | 711.2 | 220 | 6 | 1551.9552 |  | 2010-05-01 | 04/10 - 05/09 | 1551.9552
2011-06-01 | 05/11 - 06/13 | 1725 | 547 | 0 | Quoted from utility bill | 668.8392 | 935.4 | 432 | 0 | 1551.9552
2011-07-01 | 06/13 - 07/11 | 1624 |  |  | Quoted from utility bill | [6 empty] | 2010-06-01 | 05/10 - 06/10 | 1679.4984
2011-08-01 | 07/11 - 08/10 | 1591 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1498 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 1394 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/08 | 926 |  |  | Quoted from utility bill
2011-12-01 | 11/08 - 12/08 | 961 |  |  | Quoted from utility bill
2012-01-01 | 12/08 - 01/10 | 1147 |  |  | Quoted from utility bill
2012-02-01 | 01/10 - 02/09 | 921 |  |  | Quoted from utility bill
[11 empty] | elec base loads | 2010-07-01 | 06/11 - 07/12 | 1610.1672
| Total | 49670 | 6645 | 3286 |  |  | 19638.8 | 5493 | 2696 | Actual | 1261.3333 | 2010-08-01 | 07/13 - 08/10 | 1687.8648
|  |  | 17.34% | 17.95% | [5 empty] | EGUSA | 661.3333 | 2010-09-01 | 08/11 - 09/09 | 1663.6224
[12 empty] | 2010-10-01 | 09/10 - 10/08 | 1558.0896
| TMY2 | 9600 | 2485 | 1446 |  | TMY2 | 9600 | 2485 | 1446 |  |  | 2010-11-01 | 10/09 - 11/09 | 1556.3304
| % less vs. actual | 80.67% | 62.6% | 56% |  | % less vs. actual | 51.12% | 54.76% | 46.36% |  |  | 2010-12-01 | 11/09 - 12/09 | 1472.484
[12 empty] | 2011-01-01 | 12/09 - 01/12 | 1479.4896
| TMY3 | 9752 | 2729 | 1349 |  | TMY3 | 9752 | 2729 | 1349
| % less vs. actual | 80.37% | 58.93% | 58.95% |  | % less vs. actual | 50.34% | 50.32% | 49.96%
Notes:
- Aprilaire was on 4.5 dial setting until 8/31/10, then turned down to 2 by Phil
- Summer Setpoint is 70-71, winter is 73
- 3 occupants, 1 retired adult home all the time
Homeowner told me that the outside hp unit vibrate when it is running in the rain??
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Tried increasing BEopt misc loads to 4x Benchmark. Also changed temp settings to 73 winter adn 70 summer as observed.
Whole year: 20979 kWh from Dec-Jan 2010. BEopt: 9126 kWh.
Went to 9938 with new temp setpoints (8% increase)
Went to 12843 by doubling misc loads (29% increase from original)
Went to 18788 by quadrupling misc loads (51% increase from original) but the real kWh is still 10% higher.
Tried BEopt monthly graph with new temp setpoints and 4x misc loads. Appears to even out loads so that little summer/winter variation is observed. It turns out that BEopt modulates miscellaneous loads by season so they are higher in the winter and lower in the summer. With such high misc loads, this would smooth out monthly energy use. Dehumidification and resultant extra cooling still not accounted for in model.
Note on L5: Rosi: Experimented with changing BEopt model to real temp setpoints and increasing misc loads to 4 times benchmark

## 1218 Owens Blvd
1218 Owens Boulevard |  |  |  |  | 6/25/09 move in date
Plan H2
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-07-01 | 06/10 - 07/09 | 421 | 630 | 0 | Quoted from utility bill |  | 815 | 472 | 0
2009-08-01 | 07/10 - 08/09 | 1426 | 585 | 0 | Quoted from utility bill | Moved in | 880 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 989 | 519 | 0 | Quoted from utility bill |  | 854 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 952 | 456 | 0 | Quoted from utility bill |  | 649 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 706 | 142 | 55 | Quoted from utility bill |  | 536 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 807 | 7 | 254 | Quoted from utility bill |  | 526 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 1222 | 5 | 529 | Quoted from utility bill |  | 855 | 6 | 438
2010-02-01 | 01/10 - 02/09 | 869 | 5 | 429 | Quoted from utility bill |  | 827 | 13 | 386
2010-03-01 | 02/10 - 03/09 | 1037 | 0 | 455 | Quoted from utility bill |  | 600 | 36 | 207
2010-04-01 | 03/10 - 04/09 | 1408 | 50 | 118 | Quoted from utility bill |  | 564 | 80 | 91
2010-05-01 | 04/10 - 05/09 | 1687 | 229 | 0 | Quoted from utility bill |  | 593 | 212 | 6
2010-06-01 | 05/10 - 06/10 | 1936 | 491 | 0 | Quoted from utility bill |  | 752 | 376 | 0
2010-07-01 | 06/11 - 07/12 | 2340 | 601 | 0 | Quoted from utility bill |  | 871 | 505 | 0
2010-08-01 | 07/13 - 08/10 | 2116 | 598 | 0 | Quoted from utility bill |  | 827 | 503 | 0
2010-09-01 | 08/11 - 09/09 | 1956 | 546 | 0 | Quoted from utility bill |  | 826 | 488 | 0
2010-10-01 | 09/10 - 10/07 | 1543 | 392 | 0 | Quoted from utility bill |  | 607 | 304 | 0
2010-11-01 | 10/08 - 11/09 | 1317 | 208 | 50 | Quoted from utility bill |  | 578 | 133 | 47
2010-12-01 | 11/09 - 12/09 | 857 | 41 | 215 | Quoted from utility bill |  | 549 | 49 | 129
2011-01-01 | 12/09 - 01/13 | 1370 | 6 | 475 | Quoted from utility bill |  | 958 | 6 | 519 |  | elec base loads
2011-02-01 | 01/13 - 02/10 | 1184 | 0 | 537 | Quoted from utility bill |  | 775.1 | 13 | 380 | Actual | 810.6667
2011-03-01 | 02/10 - 03/15 | 1122 |  |  | Quoted from utility bill |  |  |  |  | EGUSA | 537
2011-04-01 | 03/15 - 04/12 | 902 |  |  | Quoted from utility bill
2011-05-01 | 04/12 - 05/11 | 875 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/13 | 1234 |  |  | Quoted from utility bill
2011-07-01 | 06/13 - 07/11 | 1198 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 1085 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1142 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 906 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/08 | 832 |  |  | Quoted from utility bill
2011-12-01 | 11/08 - 12/08 | 1224 |  |  | Quoted from utility bill
2012-01-01 | 12/08 - 01/10 | 1417 |  |  | Quoted from utility bill
2012-02-01 | 01/10 - 02/09 | 733 |  |  | Quoted from utility bill
| Total | 38813 | 5511 | 3117 |  |  | 14442.1 | 4700 | 2379
|  |  | 14.72% | 23.68%
| TMY2 | 8268 | 2485 | 1446 |  | TMY2 | 8268 | 2485 | 1446
| % less vs. actual | 78.7% | 54.91% | 53.61% |  | % less vs. actual | 42.75% | 47.13% | 39.22%
| TMY3 | 8452 | 2729 | 1349 |  | TMY3 | 8452 | 2729 | 1349
| % less vs. actual | 78.22% | 50.48% | 56.72% |  | % less vs. actual | 41.48% | 41.94% | 43.3%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 4253 St Bernard Ave
4253 St. Bernard Avenue |  |  |  |  | 3/11/09 move in date
Plan H2
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-07-01 | 06/10 - 07/09 | 1436 | 630 | 0 | Quoted from utility bill |  | 815 | 472 | 0
2009-08-01 | 07/10 - 08/09 | 933 | 585 | 0 | Quoted from utility bill |  | 880 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 754 | 519 | 0 | Quoted from utility bill |  | 854 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 711 | 456 | 0 | Quoted from utility bill |  | 649 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 825 | 142 | 55 | Quoted from utility bill |  | 536 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 1038 | 7 | 254 | Quoted from utility bill |  | 526 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 1587 | 5 | 529 | Quoted from utility bill |  | 855 | 6 | 438
2010-02-01 | 01/10 - 02/09 | 1171 | 5 | 429 | Quoted from utility bill |  | 827 | 13 | 386
2010-03-01 | 02/10 - 03/09 | 1078 | 0 | 455 | Quoted from utility bill |  | 600 | 36 | 207
2010-04-01 | 03/10 - 04/09 | 962 | 50 | 118 | Quoted from utility bill |  | 564 | 80 | 91
2010-05-01 | 04/10 - 05/09 | 833 | 229 | 0 | Quoted from utility bill |  | 593 | 212 | 6
2010-06-01 | 05/10 - 06/10 | 1347 | 491 | 0 | Quoted from utility bill |  | 752 | 376 | 0
2010-07-01 | 06/11 - 07/12 | 1428 | 601 | 0 | Quoted from utility bill |  | 871 | 505 | 0
2010-08-01 | 07/13 - 08/10 | 1209 | 598 | 0 | Quoted from utility bill |  | 827 | 503 | 0
2010-09-01 | 08/11 - 09/09 | 929 | 546 | 0 | Quoted from utility bill |  | 826 | 488 | 0
2010-10-01 | 09/10 - 10/08 | 798 | 392 | 0 | Quoted from utility bill |  | 633 | 318 | 0
2010-11-01 | 10/09 - 11/09 | 729 | 208 | 50 | Quoted from utility bill |  | 553 | 118 | 47
2010-12-01 | 11/09 - 12/09 | 813 | 41 | 215 | Quoted from utility bill |  | 549 | 49 | 129
2011-01-01 | 12/09 - 01/12 | 1083 | 6 | 475 | Quoted from utility bill |  | 958 | 6 | 519 |  | elec base loads
2011-02-01 | 01/12 - 02/11 | 1176 | 0 | 537 | Quoted from utility bill |  | 832.8 | 13 | 415 | Actual | 753.6667
2011-03-01 | 02/11 - 03/15 | 856 |  |  | Quoted from utility bill |  |  |  |  | EGUSA | 537
2011-04-01 | 03/15 - 04/12 | 733 |  |  | Quoted from utility bill
2011-05-01 | 04/12 - 05/11 | 817 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/13 | 1061 |  |  | Quoted from utility bill
2011-07-01 | 06/13 - 07/11 | 1051 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/11 | 996 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1054 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 999 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/07 | 734 |  |  | Quoted from utility bill
2011-12-01 | 11/07 - 12/07 | 845 |  |  | Quoted from utility bill
2012-01-01 | 12/07 - 01/11 | 1102 |  |  | Quoted from utility bill
2012-02-01 | 01/11 - 02/08 | 804 |  |  | Quoted from utility bill
| Total | 31892 | 5511 | 3117 |  |  | 14500.8 | 4699 | 2414
|  |  | 14.73% | 22.55%
| TMY2 | 8268 | 2485 | 1446 |  | TMY2 | 8268 | 2485 | 1446
| % less vs. actual | 74.08% | 54.91% | 53.61% |  | % less vs. actual | 42.98% | 47.12% | 40.1%
| TMY3 | 8452 | 2729 | 1349 |  | TMY3 | 8452 | 2729 | 1349
| % less vs. actual | 73.5% | 50.48% | 56.72% |  | % less vs. actual | 41.71% | 41.92% | 44.12%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 4243 St Bernard Ave
4243 St. Bernard Avenue |  |  |  |  | 3/12/09 move in date
Plan H2
Phase I
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-07-01 | 06/10 - 07/09 | 1620 | 630 | 0 | Quoted from utility bill |  | 815 | 472 | 0
2009-08-01 | 07/10 - 08/09 | 1449 | 585 | 0 | Quoted from utility bill |  | 880 | 533 | 0
2009-09-01 | 08/10 - 09/09 | 1240 | 519 | 0 | Quoted from utility bill |  | 854 | 505 | 0
2009-10-01 | 09/10 - 10/09 | 1470 | 456 | 0 | Quoted from utility bill |  | 649 | 324 | 0
2009-11-01 | 10/10 - 11/09 | 1231 | 142 | 55 | Quoted from utility bill |  | 536 | 103 | 47
2009-12-01 | 11/10 - 12/09 | 951 | 7 | 254 | Quoted from utility bill |  | 526 | 39 | 129
2010-01-01 | 12/10 - 01/09 | 1394 | 5 | 529 | Quoted from utility bill |  | 855 | 6 | 438 | 1125.3946 | blue is HDD equation
2010-02-01 | 01/10 - 02/09 | 1001 | 5 | 429 | Quoted from utility bill |  | 827 | 13 | 386 | 1070.7062 | red is CDD equation
2010-03-01 | 02/10 - 03/09 | 1041 | 0 | 455 | Quoted from utility bill |  | 600 | 36 | 207 | 882.4519
2010-04-01 | 03/10 - 04/09 | 842 | 50 | 118 | Quoted from utility bill |  | 564 | 80 | 91 | 760.4547
2010-05-01 | 04/10 - 05/09 | 1035 | 229 | 0 | Quoted from utility bill |  | 593 | 212 | 6 | 1000.2804
2010-06-01 | 05/10 - 06/10 | 1208 | 491 | 0 | Quoted from utility bill |  | 752 | 376 | 0 | 1170.7092
2010-07-01 | 06/10 - 07/12 | 1384 | 601 | 0 | Quoted from utility bill |  | 871 | 505 | 0 | 1304.766
2010-08-01 | 07/13 - 08/10 | 1575 | 598 | 0 | Quoted from utility bill |  | 827 | 503 | 0 | 1302.6876
2010-09-01 | 08/11 - 09/09 | 1290 | 546 | 0 | Quoted from utility bill |  | 826 | 488 | 0 | 1287.0996
2010-10-01 | 09/10 - 10/08 | 1102 | 392 | 0 | Quoted from utility bill |  | 633 | 318 | 0 | 1110.4356
2010-11-01 | 10/09 - 11/09 | 1041 | 208 | 50 | Quoted from utility bill |  | 553 | 118 | 47 | 902.5956
2010-12-01 | 11/09 - 12/09 | 882 | 41 | 215 | Quoted from utility bill |  | 549 | 49 | 129 | 800.4193
2011-01-01 | 12/09 - 01/12 | 1129 | 6 | 475 | Quoted from utility bill |  | 958 | 6 | 519 | 12718.0007 |  | elec base loads
2011-02-01 | 01/12 - 02/11 | 1367 | 0 | 537 | Quoted from utility bill |  | 832.8 | 13 | 415 | 13795 | Actual | 884.6667
2011-03-01 | 02/11 - 03/15 | 1443 |  |  | Quoted from utility bill | [5 empty] | EGUSA | 537
2011-04-01 | 03/15 - 04/12 | 1200 |  |  | Quoted from utility bill |  |  |  |  | 7.807%
2011-05-01 | 04/12 - 05/11 | 930 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/13 | 1654 |  |  | Quoted from utility bill
2011-07-01 | 06/13 - 07/11 | 1606 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 1814 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1545 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/10 | 770 |  |  | Quoted from utility bill
2011-11-01 | 10/10 - 11/07 | 498 |  |  | Quoted from utility bill
2011-12-01 | 11/07 - 12/07 | 742 |  |  | Quoted from utility bill
2012-01-01 | 12/07 - 01/11 | 908 |  |  | Quoted from utility bill
2012-02-01 | 01/11 - 02/08 | 551 |  |  | Quoted from utility bill
| Total | 37913 | 5511 | 3117 |  |  | 14500.8 | 4699 | 2414
|  |  | 14.73% | 22.55%
| TMY2 | 8268 | 2485 | 1446 |  | TMY2 | 8268 | 2485 | 1446
| % less vs. actual | 78.19% | 54.91% | 53.61% |  | % less vs. actual | 42.98% | 47.12% | 40.1%
| TMY3 | 8452 | 2729 | 1349 |  | TMY3 | 8452 | 2729 | 1349
| % less vs. actual | 77.71% | 50.48% | 56.72% |  | % less vs. actual | 41.71% | 41.92% | 44.12%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Note on K11: Rosi: Use "actual" best fit equation but put in TMY3 CDD for the value of X to get new energy use by month

## 1463 Filmore Ave
1463 Filmore Avenue |  |  |  |  | 12/09/09 move in date
Gertrude
Phase II
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | Beopt 1.2 kWh | EGUSA kWh | EGUSA CDD | EGUSA HDD
|  | 1270 |  | 193
2010-01-01 | 12/14 - 01/13 | 1510 | 5 | 555 | Quoted from utility bill |  |  | 1104 | 6 | 478
2010-02-01 | 01/14 - 02/13 | 1265 | 5 | 422 | Quoted from utility bill |  |  | 1024 | 16 | 387
2010-03-01 | 02/14 - 03/13 | 1121 | 4 | 363 | Quoted from utility bill |  |  | 773 | 37 | 180
2010-04-01 | 03/14 - 04/13 | 1081 | 58 | 108 | Quoted from utility bill |  |  | 795 | 103 | 73
2010-05-01 | 04/14 - 05/13 | 1172 | 275 | 0 | Quoted from utility bill |  |  | 856 | 243 | 6
2010-06-01 | 05/14 - 06/13 | 1504 | 517 | 0 | Quoted from utility bill |  |  | 998 | 391 | 0
2010-07-01 | 06/14- 07/13 | 1972 | 557 | 0 | Quoted from utility bill |  |  | 1037 | 479 | 0
2010-08-01 | 07/14 - 08/10 | 1731 | 578 | 0 | Quoted from utility bill |  |  | 1003 | 489 | 0
2010-09-01 | 08/11 - 09/10 | 1513 | 566 | 0 | Quoted from utility bill |  |  | 1072 | 503 | 0
2010-10-01 | 09/11 -10/10 | 1238 | 392 | 0 | Quoted from utility bill |  |  | 862 | 313 | 0
2010-11-01 | 10/11 -11/08 | 1272 | 181 | 48 | Quoted from utility bill |  |  | 708 | 99 | 47
2010-12-01 | 11/09 - 12/08 | 1270 | 41 | 193 | Quoted from utility bill |  |  | 746 | 49 | 119
2011-01-02 | 12/09 - 01/12 | 1719 | 6 | 475 | Quoted from utility bill |  |  | 1209 | 6 | 519 |  | elec base loads
2011-02-03 | 01/12 - 02/10 | 1394 | 0 | 512 | Quoted from utility bill |  |  | 1010.2 | 13 | 399 | Actual | 1088
2011-03-03 | 02/10 - 03/15 | 1190 |  |  | Quoted from utility bill | [5 empty] | EGUSA | 742.3333
2011-04-03 | 03/15 - 04/12 | 913 |  |  | Quoted from utility bill
2011-05-03 | 04/12 - 05/11 | 1028 |  |  | Quoted from utility bill
2011-06-04 | 05/11 - 06/10 | 1149 |  |  | Quoted from utility bill
2011-07-03 | 06/10 - 07/11 | 1459 |  |  | Quoted from utility bill
2011-08-04 | 07/11 - 08/10 | 1250 | . |  | Quoted from utility bill
2011-09-05 | 08/10 - 09/09 | 1336 |  |  | Quoted from utility bill
2011-10-07 | 09/09 - 10/09 | 992 |  |  | Quoted from utility bill
2011-11-08 | 10/09 - 11/07 | 756 |  |  | Quoted from utility bill |  | 728
2011-12-10 | 11/07 - 12/07 | 1067 |  |  | Quoted from utility bill |  | 796
2012-01-11 | 12/07 - 01/10 | 1187 |  |  | Quoted from utility bill |  | 1184
2012-02-12 | 01/10 - 02/08 | 817 |  |  | Quoted from utility bill
| Total | 34176 | 3185 | 2869 |  |  |  | 13197.2 | 2747 | 2208
|  |  | 13.75% | 23.04%
| TMY2 | 12600 | 2485 | 1446 | SHADED AREA NOT | TMY2 |  | 12600 | 2485 | 1446
| % less vs. actual | 63.13% | 21.98% | 49.6% | ACCURATE DUE TO A | % less vs. actual |  | 4.525% | 9.538% | 34.51%
LACK OF
| TMY3 | 12817 | 2729 | 1349 | A FULL YEAR OF | TMY3 |  | 12817 | 2729 | 1349
| % less vs. actual | 62.5% | 14.32% | 52.98% | UTILITLIES | % less vs. actual |  | 2.881% | 0.6553% | 38.9%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 4951 Piety Dr
4951 Piety Drive |  |  |  |  | 07/08/2010 move in date
Gertrude
Phase II
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2010-08-01 | 07/07 - 08/05 | 975 | 607 | 0 | Quoted from utility bill |  | 1077 | 523 | 0
2010-09-01 | 08/06 - 09/02 | 1188 | 522 | 0 | Quoted from utility bill |  | 968 | 460 | 0
2010-10-01 | 09/03 -10/01 | 1241 | 488 | 0 | Quoted from utility bill |  | 894 | 372 | 0
2010-11-01 | 10/02 -11/02 | 1056 | 227 | 3 | Quoted from utility bill |  | 787 | 120 | 47
2010-12-01 | 11/03 - 12/03 | 1122 | 47 | 164 | Quoted from utility bill |  | 774 | 89 | 81
2011-01-02 | 12/04 - 01/06 | 2206 | 6 | 439 | Quoted from utility bill |  | 1132 | 6 | 461
2011-02-03 | 01/07 - 02/04 | 1948 | 0 | 475 | Quoted from utility bill |  | 930 | 13 | 346
2011-03-03 | 02/04 - 03/08 | 1663 |  |  | Quoted from utility bill
2011-04-03 | 03/08 - 04/06 | 1110 |  |  | Quoted from utility bill
2011-05-03 | 04/06 - 05/04 | 1201 |  |  | Quoted from utility bill
2011-06-03 | 05/04 - 06/06 | 1494 |  |  | Quoted from utility bill
2011-07-03 | 06/06 - 07/06 | 1518 |  |  | Quoted from utility bill
2011-08-03 | 07/06 - 08/03 | 1359 |  |  | Quoted from utility bill
2011-09-03 | 08/03 - 09/01 | 1489 |  |  | Quoted from utility bill
2011-10-03 | 09/01 - 10/04 | 1320 |  |  | Quoted from utility bill
2011-11-03 | 10/04 - 11/01 | 1006 |  |  | Quoted from utility bill
2011-12-03 | 11/01 - 12/02 | 1322 |  |  | Quoted from utility bill
2012-01-03 | 12/02 - 01/05 | 1704 |  |  | Quoted from utility bill
2012-02-03 | 01/05 - 02/06 | 1406 |  |  | Quoted from utility bill
.
| Total | 26328 | 1897 | 1081 |  |  | 6562 | 1583 | 935
|  |  | 16.55% | 13.51%
| TMY2 | 12600 | 2485 | 1446 | SHADED AREA NOT | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 52.14% | -31% | -33.77% | ACCURATE DUE TO A | % less vs. actual | -92.01% | -56.98% | -54.65%
LACK OF
| TMY3 | 12817 | 2729 | 1349 | A FULL YEAR OF | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 51.32% | -43.86% | -24.79% | UTILITLIES | % less vs. actual | -95.32% | -72.39% | -44.28%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5705 Wildair Dr
5705 Wildair Drive |  |  |  |  | 9/17/09 move in date
Templeton Plan
Phase II
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA) |  |  | Predicted (EGUSA) with setpoints at 70 cool and 72 heat
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments | BEopt kWh | EGUSA kWh | EGUSA CDD | EGUSA HDD | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-12-01 | 11/06 - 12/05 | 762 | 14 | 215 | Quoted from utility bill | 786.4728 | 658 | 59 | 102 | 802 | 59 | 102
2010-01-01 | 12/06 - 01/05 | 1167 | 5 | 409 | Quoted from utility bill | 969.6984 | 956 | 6 | 425 | 1050 | 6 | 425
2010-02-01 | 01/06 - 02/05 | 910 | 5 | 478 | Quoted from utility bill | 1164.696 | 905 | 13 | 378 | 1036 | 13 | 378
2010-03-01 | 02/06 - 03/05 | 778 | 0 | 485 | Quoted from utility bill | 923.1912 | 797 | 26 | 290 | 870 | 26 | 290
2010-04-01 | 03/06 - 04/05 | 800 | 33 | 151 | Quoted from utility bill | 820.2072 | 701 | 82 | 100 | 850 | 82 | 100
2010-05-01 | 04/06 - 05/05 | 1076 | 201 | 0 | Quoted from utility bill | 783.5592 | 706 | 185 | 6 | 906 | 185 | 6
2010-06-01 | 05/06 - 06/05 | 1504 | 461 | 0 | Quoted from utility bill | 871.0608 | 858 | 368 | 0 | 1044 | 368 | 0
2010-07-01 | 06/06- 07/06 | 2561 | 569 | 0 | Quoted from utility bill | 932.5608 | 905 | 468 | 0 | 1069 | 468 | 0
2010-08-01 | 07/07 - 08/05 | 2690 | 621 | 0 | Quoted from utility bill | 993.2136 | 975 | 539 | 0 | 1031 | 523 | 0
2010-09-01 | 08/06 - 09/02 | 2306 | 570 | 0 | Quoted from utility bill | 963.2808 | 1012 | 504 | 0 | 931 | 460 | 0
2010-10-01 | 09/03 -10/07 | 1215 | 513 | 0 | Quoted from utility bill | 879.8832 | 1022 | 409 | 0 | 1022 | 409 | 0
2010-11-01 | 10/08 -11/07 | 880 | 208 | 38 | Quoted from utility bill | 793.6224 | 760 | 119 | 47 | 760 | 119 | 47
2010-12-01 | 11/02 - 12/03 | 777 | 53 | 164 | Quoted from utility bill | 786.4728 | 800 | 89 | 81
2011-01-02 | 12/03 - 01/06 | 923 | 6 | 447 | Quoted from utility bill | 969.6984 | 1128 | 6 | 466 |  | elec base loads
2011-02-03 | 01/06 - 02/03 | 742 | 0 | 459 | Quoted from utility bill | 1164.696 | 906 | 13 | 340 | Actual | 810.6667
2011-03-03 | 02/03 - 03/07 | 861 | 77 | 277 | Quoted from utility bill | 923.1912 | 1011 | 36 | 329 | EGUSA | 734.6667
2011-04-03 | 03/07 - 04/05 | 855 | 125 | 42 | Quoted from utility bill | 820.2072 | 764 | 77 | 100
2011-05-03 | 04/05 - 05/04 | 1008 | 299 | 9 | Quoted from utility bill | 783.5592 | 798 | 179 | 7
2011-06-03 | 05/04 - 06/06 | 1249 | 487 | 0 | Quoted from utility bill | 871.0608 | 1035 | 396 | 0
2011-07-03 | 06/06 - 07/06 | 1331 | 631 | 0 | Quoted from utility bill | 871.0608 | 1025 | 484 | 0
2011-08-03 | 07/06 - 08/04 | 1356 |  |  | Quoted from utility bill | 932.5608 | 1025 | 484 | 0
2011-09-03 | 08/04 - 09/01 | 1527 |  |  | Quoted from utility bill
2011-10-03 | 09/01 - 10/03 | 1175 |  |  | Quoted from utility bill
2011-11-03 | 10/03 - 11/01 | 853 |  |  | Quoted from utility bill
2011-12-03 | 11/01 - 12/02 | 922 |  |  | Quoted from utility bill
2012-01-03 | 12/02 - 01/04 | 1070 |  |  | Quoted from utility bill
2012-02-03 | 01/04 - 02/03 | 933 |  |  | Quoted from utility bill
.
| Total | 32231 | 4878 | 3174 |  |  | 18747 | 4542 | 2671 | 11371 | 4263.3333 | 1348
|  |  | 6.888% | 15.85%
| TMY2 | 12600 | 2485 | 1446 | SHADED AREA NOT | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 60.91% | 49.06% | 54.44% | ACCURATE DUE TO A | % less vs. actual | 32.79% | 45.29% | 45.86%
LACK OF
| TMY3 | 12817 | 2729 | 1349 | A FULL YEAR OF | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 60.23% | 44.05% | 57.5% | UTILITLIES | % less vs. actual | 31.63% | 39.92% | 49.49%
Notes:
- Aprilaire setting was saet to 5, lowered to 1 on 08/31/10
- Summer Setpoint is 70-72, setpoint sometimes can't be met.
- Measured supply temperature at kitchen register 65.2F 61.3RH
- 1-2 occupants, only 1 for the past few months, full time worker, 2 dogs, moved in September 2009
- Filters changed every month
- HOBOs and state loggers installed
-Refrigerant
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5749 Wildair Dr
5749 Wildair Drive |  |  |  |  | 1/04/2010 move in date
Templeton Plan
Phase II
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
|  | 941 | 227 | 3
|  | 641 | 47 | 164
2010-02-01 | 01/06 - 02/05 | 617 | 5 | 478 | Quoted from utility bill |  | 905 | 13 | 378
2010-03-01 | 02/06 - 03/05 | 1132 | 0 | 485 | Quoted from utility bill |  | 797 | 26 | 290
2010-04-01 | 03/06 - 04/05 | 800 | 33 | 151 | guess from bar graph on utility bill |  | 701 | 82 | 100
2010-05-01 | 04/06 - 05/05 | 870 | 201 | 0 | guess from bar graph on utility bill |  | 706 | 185 | 6
2010-06-01 | 05/06 - 06/05 | 840 | 461 | 0 | guess from bar graph on utility bill |  | 858 | 368 | 0
2010-07-01 | 06/06- 07/06 | 1550 | 569 | 0 | guess from bar graph on utility bill |  | 905 | 468 | 0
2010-08-01 | 07/07 - 08/05 | 1600 | 621 | 0 | guess from bar graph on utility bill |  | 975 | 539 | 0
2010-09-01 | 08/06 - 09/02 | 1500 | 570 | 0 | guess from bar graph on utility bill |  | 1012 | 504 | 0
2010-10-01 | 09/03 -10/01 | 1255 | 488 | 0 | Quoted from utility bill |  | 868 | 372 | 0
2010-11-01 | 10/02 -11/02 | 941 | 227 | 3 | Quoted from utility bill |  | 781 | 120 | 47
2010-12-01 | 11/03 - 12/03 | 641 | 47 | 164 | Quoted from utility bill |  | 773 | 89 | 81
2011-01-02 | 12/04 - 01/06 | 1146 | 6 | 439 | Quoted from utility bill |  | 1100 | 6 | 461 |  | elec base loads
2011-02-03 | 01/07 - 02/03 | 986 | 0 | 449 | Quoted from utility bill |  | 873 | 13 | 325 | Actual | 686
2011-03-03 | 02/03 - 03/07 | 1240 |  |  | Quoted from utility bill |  |  |  |  | EGUSA | 726.6667
received notice of last bill |  |  | .
| Total | 16700 | 3502 | 2336 |  |  | 11254 | 2785 | 1688
|  |  | 20.47% | 27.74%
| TMY2 | 12600 | 2485 | 1446 | SHADED AREA NOT | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 24.55% | 29.04% | 38.1% | ACCURATE DUE TO A | % less vs. actual | -11.96% | 10.77% | 14.34%
LACK OF
| TMY3 | 12817 | 2729 | 1349 | A FULL YEAR OF | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 23.25% | 22.07% | 42.25% | UTILITLIES | % less vs. actual | -13.89% | 2.011% | 20.08%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD. Date range for months that are guesses from the bar graph can be estimated. Date ranges for actual bills should be accurate from bill itself
Use EGUSA for predicted kWh, CDD and HDD

## 4975 St Roach Ave
4975 Saint Roach Avenue |  |  |  |  | 10/2/09 move in date
Templeton Plan
Phase II
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-11-01 | 10/08 - 11/07 | 1002 | 167 | 55 | Quoted from utility bill |  | 678 | 119 | 47
2009-12-01 | 11/08 - 12/07 | 1210 | 14 | 232 | Quoted from utility bill |  | 669 | 53 | 118
2010-01-01 | 12/08 - 01/07 | 1651 | 5 | 431 | Quoted from utility bill |  | 960 | 6 | 431 | 1591.6621
2010-02-01 | 01/08 - 02/07 | 1634 | 5 | 471 | Quoted from utility bill |  | 935 | 13 | 406 | 1552.1846
2010-03-01 | 02/08 - 03/07 | 1642 | 0 | 470 | Quoted from utility bill |  | 756 | 36 | 241 | 1291.6331
2010-04-01 | 03/08 - 04/07 | 1155 | 48 | 129 | Quoted from utility bill |  | 696 | 77 | 100 | 1068.98
2010-05-01 | 04/08 - 05/07 | 1265 | 212 | 0 | Quoted from utility bill |  | 744 | 197 | 6 | 965.2935
2010-06-01 | 05/08 - 06/07 | 1500 | 470 | 0 | guess from bar graph on utility bill |  | 871 | 386 | 0 | 1597.593
2010-07-01 | 06/08 - 07/07 | 2327 | 567 | 0 | Quoted from utility bill |  | 904 | 467 | 0 | 1868.5785
2010-08-01 | 07/08 - 08/07 | 2745 | 608 | 0 | Quoted from utility bill |  | 973 | 524 | 0 | 2059.272
2010-09-01 | 08/08 - 09/07 | 2172 | 570 | 0 | Quoted from utility bill |  | 1012 | 504 | 0 | 1992.362
2010-10-01 | 09/08 - 10/04 | 1460 | 414 | 0 | Quoted from utility bill |  | 777 | 310 | 0 | 1343.335
2010-11-01 | 10/05 - 11/03 | 1046 | 217 | 3 | Quoted from utility bill |  | 734 | 112 | 47 | 680.926
2010-12-02 | 11/11 - 12/06 | 1115 | 41 | 150 | Quoted from utility bill |  | 645 | 36 | 114 | 1091.0874
2011-01-10 | 12/06 - 01/07 | 1482 | 6 | 437 | Quoted from utility bill |  | 1075 | 6 | 446 | 17102.9072 |  | elec base loads
2011-02-11 | 01/07 - 02/07 | 1690 | 0 | 533 | Quoted from utility bill |  | 1034 | 13 | 412 | 19712 | Actual | 1127
2011-03-11 | 02/07 - 03/10 | 1436 |  |  | Quoted from utility bill | [5 empty] | EGUSA | 670
2011-04-11 | 03/10 - 04/06 | 1234 |  |  | Quoted from utility bill |  |  |  |  | 13.24%
2011-05-11 | 04/06 - 05/06 | 1111 |  |  | Quoted from utility bill
2011-06-11 | 05/06 - 06/07 | 1388 |  |  | Quoted from utility bill
2011-07-11 | 06/07 - 07/07 | 1599 |  |  | Quoted from utility bill
2011-08-11 | 07/07 - 08/04 | 1582 |  |  | Quoted from utility bill
2011-09-11 | 08/04 - 09/02 | 1804 |  |  | Quoted from utility bill
2011-10-11 | 09/02 - 10/05 | 1403 |  |  | Quoted from utility bill
2011-11-11 | 10/05 - 11/02 | 934 |  |  | Quoted from utility bill
2011-12-11 | 11/02 - 12/05 | 1039 |  |  | Quoted from utility bill
2012-01-11 | 12/05 - 01/06 | 1169 |  |  | Quoted from utility bill
2012-02-11 | 01/06 - 02/06 | 943
| Total | 40738 | 3344 | 2911 |  |  | 13463 | 2859 | 2368
|  |  | 14.5% | 18.65%
| TMY2 | 12600 | 2485 | 1446 | SHADED AREA NO T | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 69.07% | 25.69% | 50.33% | ACCURATE DUE TO A | % less vs. actual | 6.41% | 13.08% | 38.94%
LACK OF
| TMY3 | 12817 | 2729 | 1349 | A FULL YEAR OF | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 68.54% | 18.39% | 53.66% | UTILITLIES | % less vs. actual | 4.798% | 4.547% | 43.03%
Notes:
- Aprilaire dial was set to 5 until 8/31/10, then turned down to 2 by Phil
- Summer Setpoint is 77-78, winter is 78
- 5 occupants, 3 kids at home from school during summer, 2 adults
- Filters are changed almost every month
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Note on K7: Rosi: Use "actual" best fit equation but put in TMY3 CDD for the value of X to get new energy use by month

## 5515 Wickfield Dr
5515 Wickfield Drive |  |  |  |  | 11/16/09 move in date
Camille Plan
Phase II
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2009-12-01 | 11/10 - 12/09 | 396 | 7 | 236 | Quoted from utility bill |  | 754 | 39 | 218
2010-01-01 | 12/10 - 01/09 | 1916 | 5 | 495 | Quoted from utility bill |  | 1080 | 6 | 460 | 1517.838
2010-02-01 | 01/10 - 02/09 | 1210 | 5 | 429 | Quoted from utility bill |  | 1046 | 13 | 407 | 1399.7911
2010-03-01 | 02/10 - 03/09 | 1389 | 0 | 455 | Quoted from utility bill |  | 814 | 36 | 207 | 954.3311
2010-04-01 | 03/10 - 04/09 | 864 | 50 | 118 | Quoted from utility bill |  | 805 | 87 | 91 | 695.9643
2010-05-01 | 04/10 - 05/09 | 1130 | 229 | 0 | Quoted from utility bill |  | 827 | 212 | 6 | 1050.4208
2010-06-01 | 05/10 - 06/09 | 1334 | 491 | 0 | Quoted from utility bill |  | 985 | 389 | 0 | 1211.2076
2010-07-01 | 06/10 - 07/09 | 1487 | 565 | 0 | Quoted from utility bill |  | 1018 | 472 | 0 | 1286.6048
2010-08-01 | 07/10 - 08/09 | 1576 | 634 | 0 | Quoted from utility bill |  | 1083 | 533 | 0 | 1342.0172
2010-09-01 | 08/10 - 09/09 | 1321 | 566 | 0 | Quoted from utility bill |  | 1058 | 505 | 0 | 1316.582
2010-10-01 | 09/10 - 10/08 | 1187 | 392 | 0 | Quoted from utility bill |  | 842 | 343 | 0 | 1169.4212
2010-11-01 | 10/09 - 11/09 | 1000 | 201 | 50 | Quoted from utility bill |  | 796 | 118 | 47 | 965.0312
2010-12-02 | 11/10 - 12/09 | 896 | 41 | 213 | Quoted from utility bill |  | 754 | 39 | 218 | 978.8314
2011-01-10 | 12/10 - 01/13 | 1502 | 6 | 483 | Quoted from utility bill |  | 1223 | 6 | 526 | 13888.0407 |  | elec base loads
2011-02-10 | 01/13 - 02/09 | 1368 | 0 | 458 | Quoted from utility bill |  | 940.5 | 13 | 359 | 15310 | Actual | 920
2011-03-10 | 02/09 - 03/14 | 1170 |  |  | Quoted from utility bill | [5 empty] | EGUSA | 768
2011-04-10 | 03/09 - 04/13 | 1104 |  |  | Quoted from utility bill |  |  |  |  | 9.288%
2011-05-10 | 04/13 - 05/10 | 1257 |  |  | Quoted from utility bill
2011-06-10 | 05/10 - 06/10 | 1560 |  |  | Quoted from utility bill
2011-07-10 | 06/10 - 07/12 | 1589 |  |  | Quoted from utility bill
2011-08-11 | 07/12 - 08/10 | 1102 |  |  | Quoted from utility bill
2011-09-12 | 08/10 - 09/09 | 1370 |  |  | Quoted from utility bill
2011-10-14 | 09/09 - 10/10 | 1344 |  |  | Quoted from utility bill
2011-11-15 | 10/10 - 11/08 | 706 |  |  | Quoted from utility bill
2011-12-17 | 11/08 - 12/08 | 900 |  |  | Quoted from utility bill
2012-01-18 | 12/08 - 01/11 | 1018 |  |  | Quoted from utility bill
2012-02-19 | 01/11 - 02/09 | 846 |  |  | Quoted from utility bill
| Total | 32542 | 3192 | 2937 |  |  | 14025.5 | 2811 | 2539
|  |  | 11.94% | 13.55%
| TMY2 | 12600 | 2485 | 1446 | SHADED AREA NO T | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 61.28% | 22.15% | 50.77% | ACCURATE DUE TO A | % less vs. actual | 10.16% | 11.6% | 43.05%
LACK OF
| TMY3 | 12817 | 2729 | 1349 | A FULL YEAR OF | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 60.61% | 14.51% | 54.07% | UTILITLIES | % less vs. actual | 8.616% | 2.917% | 46.87%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD
Note on K7: Rosi: Use "actual" best fit equation but put in TMY3 CDD for the value of X to get new energy use by month

## 5320 Wilton Dr
5320 Wilton Dr |  |  |  |  | Aug 2010 move in date
Phase II
Gertrude
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2010-08-01 | 07/10 - 08/09 | 1163 |  |  | Quoted from utility bill
2010-09-01 | 08/10 - 09/09 | 1315 |  |  | Quoted from utility bill
2010-10-01 | 09/10 - 10/08 | 1234 |  |  | Quoted from utility bill
2010-11-01 | 10/09 - 11/09 | 864 |  |  | Quoted from utility bill
2010-12-02 | 11/10 - 12/09 | 1255 |  |  | Quoted from utility bill
2011-01-10 | 12/10 - 01/13 | 2410 |  |  | Quoted from utility bill
2011-02-10 | 01/13 - 02/09 | 1875 |  |  | guess from bar graph on utility bill
2011-03-10 | 02/09 - 03/14 | 1800 |  |  | guess from bar graph on utility bill
2011-04-10 | 03/09 - 04/13 | 940 |  |  | guess from bar graph on utility bill
2011-05-10 | 04/05 - 05/04 | 995 |  |  | Quoted from utility bill
2011-06-10 | 05/04 - 06/06 | 1243 |  |  | Quoted from utility bill
2011-07-10 | 06/06 - 07/06 | 1710 |  |  | Quoted from utility bill
2011-08-10 | 07/06 - 08/04 | 1689 |  |  | Quoted from utility bill
2011-09-10 | 08/04 - 09/01 | 2017 |  |  | Quoted from utility bill
2011-10-10 | 09/01 - 10/03 | 1699 |  |  | Quoted from utility bill
2011-11-10 | 10/03 - 11/01 | 1079 |  |  | Quoted from utility bill
2011-12-10 | 11/01 - 12/02 | 1266 |  |  | Quoted from utility bill
2012-01-10 | 12/02 - 01/04 | 1630 |  |  | Quoted from utility bill
2012-02-10 | 01/04 - 02/03 | 1356 |  |  | Quoted from utility bill
| Total | 27540 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | #DIV/0! | #DIV/0!
| TMY2 | 12600 | 2485 | 1446 | SHADED AREA NO T | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 54.25% | #DIV/0! | #DIV/0! | ACCURATE DUE TO A | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
LACK OF
| TMY3 | 12817 | 2729 | 1349 | A FULL YEAR OF | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 53.46% | #DIV/0! | #DIV/0! | UTILITLIES | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 4963 Painters St
4963 Painters St |  |  |  |  | 11/16/09 move in date
Phase II
Gertrude
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2010-05-01 | 04/10 - 05/09 | 1362 |  |  | Quoted from utility bill
2010-06-01 | 05/10 - 06/09 | 1336 |  |  | Quoted from utility bill
2010-07-01 | 06/10 - 07/09 | 1956 |  |  | Quoted from utility bill
2010-08-01 | 07/10 - 08/09 | 1594 |  |  | Quoted from utility bill
2010-09-01 | 08/10 - 09/09 | 1473 |  |  | Quoted from utility bill
2010-10-01 | 09/10 - 10/08 | 1344 |  |  | Quoted from utility bill
2010-11-01 | 10/09 - 11/09 | 1160 |  |  | Quoted from utility bill
2010-12-02 | 11/10 - 12/09 | 1324 |  |  | Quoted from utility bill
2011-01-10 | 12/10 - 01/13 | 2206 |  |  | Quoted from utility bill
2011-02-10 | 01/13 - 02/09 | 2075 |  |  | guess from bar graph on utility bill
2011-03-10 | 02/09 - 03/14 | 2000 |  |  | guess from bar graph on utility bill
2011-04-10 | 03/07 - 04/05 | 1642 |  |  | Quoted from utility bill
2011-05-10 | 04/05 - 05/05 | 1901 |  |  | Quoted from utility bill
2011-06-10 | 05/05 - 06/06 | 2072 |  |  | Quoted from utility bill
2011-07-10 | 06/06 - 07/05 | 2188 |  |  | Quoted from utility bill
2011-08-10 | 07/05 - 08/04 | 2397 |  |  | Quoted from utility bill
2011-09-10 | 08/04 - 09/01 | 2356 |  |  | Quoted from utility bill
2011-10-10 | 09/01 - 10/03 | 2183 |  |  | Quoted from utility bill
2011-11-10 | 10/03 - 11/02 | 1892 |  |  | Quoted from utility bill
2011-12-10 | 11/02 - 12/02 | 1751 |  |  | Quoted from utility bill
2012-01-10 | 12/02 - 01/04 | 2145 |  |  | Quoted from utility bill
2012-02-10 | 01/04 - 02/03 | 1600 |  |  | Quoted from utility bill
| Total | 39957 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | #DIV/0! | #DIV/0!
| TMY2 | 12600 | 2485 | 1446 | SHADED AREA NO T | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 68.47% | #DIV/0! | #DIV/0! | ACCURATE DUE TO A | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
LACK OF
| TMY3 | 12817 | 2729 | 1349 | A FULL YEAR OF | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 67.92% | #DIV/0! | #DIV/0! | UTILITLIES | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5729 Wilton Dr
5729 Wilton Drive |  |  |  |  | 03/30/2010 move in date
Louise
Phase III
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2010-05-01 | 04/02 - 05/01 | 760 | 178 | 0 | guess from bar graph on utility bill
2010-06-01 | 05/02 - 06/01 | 820 | 477 | 0 | guess from bar graph on utility bill
2010-07-01 | 06/02 - 07/01 | 1050 | 575 | 0 | guess from bar graph on utility bill
2010-08-01 | 07/02 - 08/01 | 980 | 632 | 0 | guess from bar graph on utility bill
2010-09-01 | 08/02 - 09/01 | 900 | 609 | 0 | guess from bar graph on utility bill
2010-10-01 | 09/02 - 10/01 | 960 | 505 | 0 | Quoted from utility bill
2010-11-01 | 10/01 - 11/02 | 847 | 239 | 3 | Quoted from utility bill
2010-12-01 | 11/02 - 12/03 | 928 | 53 | 164 | Quoted from utility bill
2011-01-01 | 12/04 - 01/06 | 1324 | 6 | 483 | Quoted from utility bill
| Total | 8569 | 3274 | 650 |  |  | 0 | 0 | 0
|  |  | 100% | 100%
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | -47.04% | 24.1% | -122.5% |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | -49.57% | 16.65% | -107.5% |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5773 Wildair
5773 Wildair |  |  |  |  | 03/15/2010 move in date
Gertrude
Phase III
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2010-04-01 |  | 645 |  |  | Quoted from utility bill
2010-05-01 | 04/03 - 05/02 | 956 | 174 | 0 | Quoted from utility bill |  | 797 | 165 | 11
2010-06-01 | 05/03 - 06/02 | 1240 | 463 | 0 | Quoted from utility bill |  | 954 | 318 | 0
2010-07-01 | 06/03 - 07/02 | 1624 | 559 | 0 | Quoted from utility bill |  | 1039 | 476 | 0
2010-08-01 | 07/03 - 08/02 | 1634 | 614 | 0 | Quoted from utility bill |  | 1094 | 519 | 0
2010-09-01 | 08/03 - 09/02 | 1375 | 583 | 0 | Quoted from utility bill |  | 1087 | 525 | 0
2010-10-01 | 09/03 - 10/01 | 1338 | 486 | 0 | Quoted from utility bill |  | 894 | 372 | 0
2010-11-01 | 10/02 - 11/02 | 1343 | 227 | 3 | Quoted from utility bill |  | 787 | 120 | 47
2010-12-01 | 11/03 - 12/03 | 1354 | 47 | 164 | Quoted from utility bill |  | 774 | 89 | 81
2011-01-01 | 12/04 - 01/06 | 2043 | 6 | 439 | Quoted from utility bill |  | 1132 | 6 | 461 |  | elec base loads
2011-02-01 | 01/07 - 02/03 | 1867 | 0 | 449 | Quoted from utility bill |  | 890 | 13 | 325 | Actual | 1215.6667
2011-03-01 | 02/03 - 03/07 | 1898 |  |  | Quoted from utility bill |  |  | 36 | 329 | EGUSA | 786
2011-04-01 | 03/07 - 04/05 | 1348 |  |  | Quoted from utility bill |  |  | 77 | 100
2011-05-01 | 04/05 - 05/04 | 1403 |  |  | Quoted from utility bill |  |  | 179 | 7
2011-06-01 | 05/04 - 06/06 | 1625 |  |  | Quoted from utility bill |  |  | 396 | 0
2011-07-01 | 06/06 - 07/06 | 1381 |  |  | Quoted from utility bill |  |  | 484 | 0
2011-08-01 | 07/06 - 08/04 | 1688 |  |  | Quoted from utility bill |  |  | 484 | 0
2011-09-01 | 08/04 - 09/01 | 1491 |  |  | Quoted from utility bill
2011-10-01 | 09/01 - 10/03 | 1312 |  |  | Quoted from utility bill
2011-11-01 | 10/03 - 11/01 | 1028 |  |  | Quoted from utility bill
2011-12-01 | 11/01 - 12/02 | 1165 |  |  | Quoted from utility bill
2012-01-01 | 12/02 - 01/04 | 1669 |  |  | Quoted from utility bill
2012-02-01 | 01/04 - 02/03 | 1216 |  |  | Quoted from utility bill
| Total | 32643 | 3159 | 1055 |  |  | 9448 | 4259 | 1361
one year |  |  | -34.82% | -29%
18609
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 61.4% | 21.34% | -37.06% |  | % less vs. actual | -33.36% | 41.65% | -6.245%
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 60.74% | 13.61% | -27.87% |  | % less vs. actual | -35.66% | 35.92% | 0.8817%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 6056 Wickfield Dr
6056 Wickfield Drive |  |  |  |  | 03/30/2010 move in date
Gertrude
Phase III
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2010-12-01 | 11/10 - 12/09 | 1642 | 41 | 213 | Quoted from utility bill |  | 739 | 39 | 129
2011-01-01 | 12/10 - 01/12 | 2273 | 6 | 453 | Quoted from utility bill |  | 1185 | 6 | 509
2011-02-01 | 01/12 - 02/10 | 1947 | 0 | 512 | Quoted from utility bill |  | 1010.2 | 13 | 399
2011-03-01 | 02/10 - 03/14 | 1742 |  |  | Quoted from utility bill
2011-04-01 | 03/14 - 04/12 | 1580 |  |  | Quoted from utility bill
2011-05-01 | 04/12 - 05/12 | 1805 |  |  | Quoted from utility bill
2011-06-01 | 05/11 - 06/10 | 2078 |  |  | Quoted from utility bill
2011-07-01 | 06/10 - 07/11 | 2367 |  |  | Quoted from utility bill
2011-08-01 | 07/11 - 08/10 | 2318 |  |  | Quoted from utility bill
2011-09-01 | 08/10 - 09/08 | 1868 |  |  | Quoted from utility bill
2011-10-01 | 09/08 - 10/07 | 1655 |  |  | Quoted from utility bill
2011-11-01 | 10/07 - 11/08 | 1723 |  |  | Quoted from utility bill
2011-12-01 | 11/08 - 12/08 | 1704 |  |  | Quoted from utility bill
2012-01-01 | 12/08 - 01/11 | 1941 |  |  | Quoted from utility bill
2012-02-01 | 01/11 - 02/10 | 1619 |  |  | Quoted from utility bill
| Total | 28262 | 47 | 1178 |  |  | 2934.2 | 58 | 1037
|  |  | -23.4% | 11.97%
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 55.42% | -5187% | -22.75% |  | % less vs. actual | -329.4% | -4184% | -39.44%
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 54.65% | -5706% | -14.52% |  | % less vs. actual | -336.8% | -4605% | -30.09%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5541 Pasteur Blvd
5541 Pasteur Boulevard |  |  |  |  | 03/15/2010 move in date
Camille
Phase III
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2010-07-01 | 05/31 - 06/29 | 1480 | 556 | 0 | Quoted from utility bill |  | 1010 | 459 | 0
2010-08-01 | 06/30 - 07/30 | 1628 | 589 | 0 | Quoted from utility bill |  | 1070 | 513 | 0
2010-09-01 | 07/31 - 08/30 | 1368 | 611 | 0 | Quoted from utility bill |  | 1089 | 542 | 0
2010-10-01 | 08/31 - 09/29 | 1431 | 514 | 0 | Quoted from utility bill |  | 928 | 393 | 0
2010-11-01 | 09/30 - 10/28 | 1251 | 230 | 0 | Quoted from utility bill |  | 727 | 132 | 41
2010-12-01 | 10/29 - 11/30 | 1417 | 65 | 123 | Quoted from utility bill |  | 830 | 100 | 71
2011-01-01 | 12/01 - 12/31 | 1831 | 6 | 427 | Quoted from utility bill |  | 931 | 6 | 331 |  | elec base loads
2011-02-01 | 01/01 - 01/31 | 1879 | 0 | 436 | Quoted from utility bill |  | 1102 | 1 | 471 | Actual | 1323.3333
2011-03-01 | 02/01 - 03/02 | 1774 | 63 | 302 | Quoted from utility bill |  | 1102 | 39 | 303 | EGUSA | 829.3333
2011-04-01 | 03/02 - 03/31 | 1317 | 109 | 47 | Quoted from utility bill
2011-05-01 | 03/31 - 05/02 | 1409 | 317 | 14 | Quoted from utility bill
2011-06-01 | 05/02 - 06/01 | 1363 | 403 | 0 | Quoted from utility bill |  |  |  |  | HDD | CDD
2011-07-01 | 06/01 - 06/29 | 1330 | 586 | 0 | Quoted from utility bill
2011-08-01 | 06/29 - 08/01 | 1402 |  |  | Quoted from utility bill |  |  |  |  | 1349 | 3493
2011-09-01 | 08/01 - 08/29 | 1322 |  |  | Quoted from utility bill
2011-10-01 | 08/29 - 09/28 | 1228 |  |  | Quoted from utility bill
2011-11-01 | 09/28 - 10/27 | 1056 |  |  | Quoted from utility bill
2011-12-01 | 10/27 - 11/29 | 1249 |  |  | Quoted from utility bill
2012-01-01 | 11/29 - 12/29 | 1449 |  |  | Quoted from utility bill
2012-02-01 | 12/29 - 01/31 | 1423 |  |  | Quoted from utility bill
2012-03-01 | 01/31 - 03/02 | 1200 |  |  | Quoted from utility bill
2012-04-01 | 03/02 - 04/02 | 1300 |  |  | Quoted from utility bill
on year | Total | 31107 | 4049 | 1349 |  |  | 8789 | 2185 | 1217
19400 |  |  | 46.04% | 9.785%
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | 59.49% | 38.63% | -7.191% |  | % less vs. actual | -43.36% | -13.73% | -18.82%
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | 58.8% | 32.6% | 0% |  | % less vs. actual | -45.83% | -24.9% | -10.85%
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5503 Wilton
5513 Wickfield Drive |  |  |  |  | 03/15/2010 move in date
Templeton
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2011-12-01 | 10/31 - 12/02 | 818 |  |  | guess from bar graph on utility bill
2012-01-01 | 12/02 - 01/04 | 858 |  |  | Quoted from utility bill
2012-02-01 | 01/04 02/03 | 619 |  |  | Quoted from utility bill
| Total | 2295 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | #DIV/0! | #DIV/0!
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | -449% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | -458.5% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5525 Pasteur Blvd
5525 Pasteur Boulevard |  |  |  |  | 03/15/2010 move in date
Templeton
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2011-05-01 | 04/06 - 05/02 | 570 |  |  | Quoted from utility bill
2011-06-01 | 05/02 - 06/01 | 821 |  |  | Quoted from utility bill
2011-07-01 | 06/01 - 06/29 | 989 |  |  | Quoted from utility bill
2011-08-01 | 06/29 - 08/01 | 1037 |  |  | Quoted from utility bill
2011-09-01 | 08/01 - 08/29 | 896 |  |  | Quoted from utility bill
2011-10-01 | 08/29 - 09/28 | 780 |  |  | Quoted from utility bill
2011-11-01 | 09/28 - 10/27 | 591 |  |  | Quoted from utility bill
2011-12-01 | 10/27 - 11/29 | 729 |  |  | Quoted from utility bill
2012-01-01 | 11/29 - 12/29 | 811 |  |  | Quoted from utility bill
2012-02-01 | 12/29 - 02/01 | 566 |  |  | Quoted from utility bill
| Total | 7790 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | #DIV/0! | #DIV/0!
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | -61.75% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | -64.53% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 6052 Wickfield
6052 Wickfield Drive |  |  |  |  | 03/15/2010 move in date
Alexander
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2011-05-01 |  | 475 |  |  | guess from bar graph on utility bill
2011-06-01 |  | 1550 |  |  | guess from bar graph on utility bill
2011-07-01 |  | 1920 |  |  | guess from bar graph on utility bill
2011-08-01 | 07/11 - 08/10 | 1696 |  |  | Quoted from utility bill
| Total | 5641 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | #DIV/0! | #DIV/0!
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | -123.4% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | -127.2% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5513 Wickfield
5513 Wickfield Drive |  |  |  |  | 03/15/2010 move in date
Templeton
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2011-12-01 |  | 75 |  |  | guess from bar graph on utility bill
2012-01-01 | 12/08 - 01/11 | 217 |  |  | Quoted from utility bill
2012-02-01 | 01/11 - 02/09 | 256 |  |  | Quoted from utility bill
| Total | 548 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | #DIV/0! | #DIV/0!
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | -2199% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | -2239% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5717 Wildair
5717 Wildair Drive |  |  |  |  | 03/15/2010 move in date
Alexander
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2011-12-01 | 10/31 - 12/02 | 921 |  |  | Quoted from utility bill
2012-01-01 | 12/02 - 01/04 | 1056 |  |  | Quoted from utility bill
2012-02-01 | 01/04 - 02/03 | 897 |  |  | Quoted from utility bill
| Total | 2874 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | #DIV/0! | #DIV/0!
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | -338.4% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | -346% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5718 Pasteur
5718 Pasteur Blvd |  |  |  |  | 03/15/2010 move in date
Louise
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2012-01-01 |  | 550 |  |  | guess from bar graph on utility bill
2012-02-01 | 12/29 - 01/31 | 885 |  |  | Quoted from utility bill
| Total | 1435 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | #DIV/0! | #DIV/0!
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | -778% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | -793.2% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## 5736 Wickfield
5736 Wickfield |  |  |  |  | 03/15/2010 move in date
Camille
|  | Actual | Weather Underground New Orleans INTL (KMSY) |  |  |  | Predicted (EGUSA)
Month on bill | Date | Actual kWh | Actual CDD | Actual HDD | Comments |  | EGUSA kWh | EGUSA CDD | EGUSA HDD
2011-09-01 |  | 750
2011-10-01 |  | 730
2011-11-01 |  | 730
2011-12-01 |  | 800
2012-01-01 |  | 1130 |  |  | guess from bar graph on utility bill
2012-02-01 | 01/11 - 02/09 | 966 |  |  | Quoted from utility bill
| Total | 5106 | 0 | 0 |  |  | 0 | 0 | 0
|  |  | #DIV/0! | #DIV/0!
| TMY2 | 12600 | 2485 | 1446 |  | TMY2 | 12600 | 2485 | 1446
| % less vs. actual | -146.8% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
| TMY3 | 12817 | 2729 | 1349 |  | TMY3 | 12817 | 2729 | 1349
| % less vs. actual | -151% | #DIV/0! | #DIV/0! |  | % less vs. actual | #DIV/0! | #DIV/0! | #DIV/0!
To add a new month, insert a row above the most recent month and copy that last month up 1 row. Then type in new month. this will automatically graph out the entered months.
Make sure to get actual kWh from the previous year from the Utility Bill. Change comments to reflect this.
Use weather underground (New Orleans INTL)for actual HDD and CDD.
Use EGUSA for predicted kWh, CDD and HDD

## New Orleans INTL EGUSA TMY3
|  |  |  | Annual | Annual
|  |  |  | 1348.5417 | 2728.8333
Julian Date | Hour | Dry Bulb | Avg daily Temp | HDD | CDD | [6 empty] | ANNUAL DEGREE DAYS
1 | 1 | 39 | [10 empty] | #days | Julian # | Row # | HDD | CDD
1 | 2 | 40 | [7 empty] | Julian Date |  | Jan | 31 | 1 | 4 | 470.5417 | 0.91667
1 | 3 | 40 |  |  |  | 2009-07-01 | 06/10 - 07/09 | 2010-01-01 | 2010-07-09 | 001 | 190 |  |  | 31 | 751
1 | 4 | 39 |  |  |  | 2009-08-01 | 07/10 - 08/09 | 2010-01-02 |  | 002 |  | Feb | 28 | 32 | 771 | 301.5417 | 37.3333
1 | 5 | 39 |  |  |  | 2009-09-01 | 08/10 - 09/09 | 2010-01-03 |  | 003 |  |  |  | 59 | 1419
1 | 6 | 39 |  |  |  | 2009-10-01 | 09/10 - 10/09 | 2010-01-04 |  | 004 |  | Mar | 31 | 60 | 1443 | 110.5 | 84
1 | 7 | 39 |  |  |  | 2009-11-01 | 10/10 - 11/09 | 2010-01-05 |  | 005 |  |  |  | 90 | 2163
1 | 8 | 40 |  |  |  | 2009-12-01 | 11/10 - 12/09 | 2010-01-06 |  | 006 |  | Apr | 30 | 91 | 2187 | 23.2083 | 153.75
1 | 9 | 38 |  |  |  | 2010-01-01 | 12/10 - 01/09 | [6 empty] | 120 | 2883
1 | 10 | 38 |  |  |  | 2010-02-01 | 01/10 - 02/09 |  |  |  |  | May | 31 | 121 | 2931 | 0 | 308.2917
1 | 11 | 40 |  |  |  | 2010-03-01 | 02/10 - 03/09 | 2010-02-28 |  | 059 |  |  |  | 151 | 3627
1 | 12 | 40 |  |  |  | 2010-04-01 | 03/10 - 04/09 | 2010-05-31 |  | 151 |  | Jun | 30 | 152 | 3651 | 0 | 470.875
1 | 13 | 41 |  |  |  | 2010-05-01 | 04/10 - 05/09 | [6 empty] | 181 | 4347
1 | 14 | 42 |  |  |  | 2010-06-01 | 05/10 - 06/09 |  |  |  |  | Jul | 31 | 182 | 4371 | 0 | 515
1 | 15 | 44 |  |  |  | 2010-07-01 | 06/10 - 07/12 | [6 empty] | 212 | 5091
1 | 16 | 44 | [9 empty] | Aug | 31 | 213 | 5115 | 0 | 537.2083
1 | 17 | 42 | [11 empty] | 243 | 5835
1 | 18 | 38 | [9 empty] | Sep | 30 | 244 | 5859 | 0 | 380.5
1 | 19 | 41 | [11 empty] | 273 | 6555
1 | 20 | 38 | [9 empty] | Oct | 31 | 274 | 6579 | 41.125 | 139.5
1 | 21 | 37 | [11 empty] | 304 | 7299
1 | 22 | 35 | [9 empty] | Nov | 30 | 305 | 7323 | 70.5417 | 88.9583
1 | 23 | 33 | [11 empty] | 334 | 8019
1 | 24 | 32 | 39.0833 | 25.9167 | -25.9167 | [6 empty] | Dec | 31 | 335 | 8043 | 331.0833 | 6.25
2 | 1 | 30 | [10 empty] | 365 | 365 | 8763
2 | 2 | 30
2 | 3 | 29 | [9 empty] | Total |  |  |  | 1348.5417 | 2722.5833
2 | 4 | 28
2 | 5 | 28
2 | 6 | 27
2 | 7 | 27
2 | 8 | 27
2 | 9 | 29
2 | 10 | 31
2 | 11 | 32
2 | 12 | 33
2 | 13 | 34
2 | 14 | 37
2 | 15 | 38
2 | 16 | 38
2 | 17 | 37
2 | 18 | 37
2 | 19 | 37
2 | 20 | 36
2 | 21 | 36
2 | 22 | 35
2 | 23 | 35
2 | 24 | 33 | 32.6667 | 32.3333 | -32.3333
3 | 1 | 34
3 | 2 | 33
3 | 3 | 33
3 | 4 | 32
3 | 5 | 31
3 | 6 | 31
3 | 7 | 30
3 | 8 | 31
3 | 9 | 34
3 | 10 | 35
3 | 11 | 35
3 | 12 | 37
3 | 13 | 36
3 | 14 | 37
3 | 15 | 38
3 | 16 | 38
3 | 17 | 37
3 | 18 | 35
3 | 19 | 34
3 | 20 | 32
3 | 21 | 28
3 | 22 | 29
3 | 23 | 29
3 | 24 | 26 | 33.125 | 31.875 | -31.875
4 | 1 | 29
4 | 2 | 28
4 | 3 | 28
4 | 4 | 27
4 | 5 | 27
4 | 6 | 27
4 | 7 | 26
4 | 8 | 31
4 | 9 | 37
4 | 10 | 42
4 | 11 | 45
4 | 12 | 48
4 | 13 | 51
4 | 14 | 53
4 | 15 | 53
4 | 16 | 52
4 | 17 | 49
4 | 18 | 44
4 | 19 | 42
4 | 20 | 41
4 | 21 | 39
4 | 22 | 40
4 | 23 | 39
4 | 24 | 37 | 38.9583 | 26.0417 | -26.0417
5 | 1 | 35
5 | 2 | 36
5 | 3 | 35
5 | 4 | 35
5 | 5 | 32
5 | 6 | 37
5 | 7 | 38
5 | 8 | 38
5 | 9 | 40
5 | 10 | 50
5 | 11 | 59
5 | 12 | 63
5 | 13 | 65
5 | 14 | 67
5 | 15 | 67
5 | 16 | 66
5 | 17 | 62
5 | 18 | 57
5 | 19 | 55
5 | 20 | 53
5 | 21 | 53
5 | 22 | 48
5 | 23 | 45
5 | 24 | 47 | 49.2917 | 15.7083 | -15.7083
6 | 1 | 42
6 | 2 | 42
6 | 3 | 40
6 | 4 | 38
6 | 5 | 38
6 | 6 | 38
6 | 7 | 37
6 | 8 | 41
6 | 9 | 52
6 | 10 | 57
6 | 11 | 60
6 | 12 | 63
6 | 13 | 63
6 | 14 | 65
6 | 15 | 65
6 | 16 | 64
6 | 17 | 59
6 | 18 | 54
6 | 19 | 52
6 | 20 | 51
6 | 21 | 48
6 | 22 | 48
6 | 23 | 46
6 | 24 | 47 | 50.4167 | 14.5833 | -14.5833
7 | 1 | 47
7 | 2 | 45
7 | 3 | 46
7 | 4 | 46
7 | 5 | 48
7 | 6 | 47
7 | 7 | 50
7 | 8 | 52
7 | 9 | 58
7 | 10 | 63
7 | 11 | 68
7 | 12 | 68
7 | 13 | 71
7 | 14 | 68
7 | 15 | 66
7 | 16 | 64
7 | 17 | 63
7 | 18 | 62
7 | 19 | 62
7 | 20 | 62
7 | 21 | 61
7 | 22 | 61
7 | 23 | 61
7 | 24 | 60 | 58.2917 | 6.7083 | -6.7083
8 | 1 | 53
8 | 2 | 50
8 | 3 | 48
8 | 4 | 46
8 | 5 | 45
8 | 6 | 44
8 | 7 | 43
8 | 8 | 44
8 | 9 | 44
8 | 10 | 45
8 | 11 | 48
8 | 12 | 50
8 | 13 | 51
8 | 14 | 52
8 | 15 | 53
8 | 16 | 52
8 | 17 | 50
8 | 18 | 48
8 | 19 | 48
8 | 20 | 45
8 | 21 | 43
8 | 22 | 41
8 | 23 | 38
8 | 24 | 39 | 46.6667 | 18.3333 | -18.3333
9 | 1 | 38
9 | 2 | 35
9 | 3 | 36
9 | 4 | 34
9 | 5 | 34
9 | 6 | 34
9 | 7 | 33
9 | 8 | 34
9 | 9 | 45
9 | 10 | 46
9 | 11 | 48
9 | 12 | 48
9 | 13 | 49
9 | 14 | 50
9 | 15 | 50
9 | 16 | 50
9 | 17 | 47
9 | 18 | 45
9 | 19 | 45
9 | 20 | 45
9 | 21 | 43
9 | 22 | 42
9 | 23 | 42
9 | 24 | 41 | 42.25 | 22.75 | -22.75
10 | 1 | 40
10 | 2 | 38
10 | 3 | 37
10 | 4 | 36
10 | 5 | 37
10 | 6 | 38
10 | 7 | 39
10 | 8 | 40
10 | 9 | 42
10 | 10 | 46
10 | 11 | 47
10 | 12 | 49
10 | 13 | 49
10 | 14 | 49
10 | 15 | 51
10 | 16 | 50
10 | 17 | 48
10 | 18 | 47
10 | 19 | 46
10 | 20 | 47
10 | 21 | 48
10 | 22 | 49
10 | 23 | 49
10 | 24 | 50 | 44.6667 | 20.3333 | -20.3333
11 | 1 | 50
11 | 2 | 50
11 | 3 | 51
11 | 4 | 50
11 | 5 | 51
11 | 6 | 53
11 | 7 | 56
11 | 8 | 58
11 | 9 | 59
11 | 10 | 59
11 | 11 | 62
11 | 12 | 62
11 | 13 | 66
11 | 14 | 69
11 | 15 | 67
11 | 16 | 66
11 | 17 | 62
11 | 18 | 57
11 | 19 | 51
11 | 20 | 50
11 | 21 | 50
11 | 22 | 49
11 | 23 | 49
11 | 24 | 48 | 56.0417 | 8.9583 | -8.9583
12 | 1 | 48
12 | 2 | 47
12 | 3 | 47
12 | 4 | 47
12 | 5 | 46
12 | 6 | 46
12 | 7 | 45
12 | 8 | 44
12 | 9 | 45
12 | 10 | 46
12 | 11 | 46
12 | 12 | 47
12 | 13 | 47
12 | 14 | 48
12 | 15 | 49
12 | 16 | 50
12 | 17 | 48
12 | 18 | 45
12 | 19 | 45
12 | 20 | 44
12 | 21 | 43
12 | 22 | 43
12 | 23 | 43
12 | 24 | 43 | 45.9167 | 19.0833 | -19.0833
13 | 1 | 42
13 | 2 | 42
13 | 3 | 42
13 | 4 | 42
13 | 5 | 43
13 | 6 | 43
13 | 7 | 44
13 | 8 | 44
13 | 9 | 46
13 | 10 | 49
13 | 11 | 52
13 | 12 | 52
13 | 13 | 53
13 | 14 | 53
13 | 15 | 52
13 | 16 | 50
13 | 17 | 50
13 | 18 | 49
13 | 19 | 49
13 | 20 | 50
13 | 21 | 50
13 | 22 | 50
13 | 23 | 50
13 | 24 | 51 | 47.8333 | 17.1667 | -17.1667
14 | 1 | 51
14 | 2 | 51
14 | 3 | 52
14 | 4 | 53
14 | 5 | 56
14 | 6 | 56
14 | 7 | 55
14 | 8 | 57
14 | 9 | 61
14 | 10 | 63
14 | 11 | 70
14 | 12 | 71
14 | 13 | 73
14 | 14 | 71
14 | 15 | 73
14 | 16 | 71
14 | 17 | 69
14 | 18 | 67
14 | 19 | 65
14 | 20 | 65
14 | 21 | 64
14 | 22 | 63
14 | 23 | 63
14 | 24 | 62 | 62.5833 | 2.4167 | -2.4167
15 | 1 | 62
15 | 2 | 63
15 | 3 | 63
15 | 4 | 62
15 | 5 | 62
15 | 6 | 60
15 | 7 | 54
15 | 8 | 53
15 | 9 | 54
15 | 10 | 55
15 | 11 | 55
15 | 12 | 54
15 | 13 | 54
15 | 14 | 55
15 | 15 | 55
15 | 16 | 55
15 | 17 | 54
15 | 18 | 54
15 | 19 | 54
15 | 20 | 54
15 | 21 | 54
15 | 22 | 55
15 | 23 | 54
15 | 24 | 54 | 56.2083 | 8.7917 | -8.7917
16 | 1 | 54
16 | 2 | 52
16 | 3 | 51
16 | 4 | 51
16 | 5 | 51
16 | 6 | 49
16 | 7 | 49
16 | 8 | 48
16 | 9 | 48
16 | 10 | 48
16 | 11 | 48
16 | 12 | 48
16 | 13 | 48
16 | 14 | 47
16 | 15 | 47
16 | 16 | 48
16 | 17 | 48
16 | 18 | 48
16 | 19 | 48
16 | 20 | 49
16 | 21 | 50
16 | 22 | 50
16 | 23 | 51
16 | 24 | 51 | 49.25 | 15.75 | -15.75
17 | 1 | 51
17 | 2 | 52
17 | 3 | 52
17 | 4 | 53
17 | 5 | 53
17 | 6 | 53
17 | 7 | 52
17 | 8 | 54
17 | 9 | 56
17 | 10 | 59
17 | 11 | 62
17 | 12 | 66
17 | 13 | 70
17 | 14 | 71
17 | 15 | 69
17 | 16 | 65
17 | 17 | 62
17 | 18 | 62
17 | 19 | 62
17 | 20 | 61
17 | 21 | 60
17 | 22 | 62
17 | 23 | 61
17 | 24 | 60 | 59.5 | 5.5 | -5.5
18 | 1 | 60
18 | 2 | 60
18 | 3 | 59
18 | 4 | 57
18 | 5 | 56
18 | 6 | 55
18 | 7 | 56
18 | 8 | 61
18 | 9 | 64
18 | 10 | 66
18 | 11 | 71
18 | 12 | 74
18 | 13 | 74
18 | 14 | 75
18 | 15 | 74
18 | 16 | 73
18 | 17 | 70
18 | 18 | 70
18 | 19 | 69
18 | 20 | 67
18 | 21 | 67
18 | 22 | 68
18 | 23 | 68
18 | 24 | 68 | 65.9167 | -0.91667 | 0.91667
19 | 1 | 69
19 | 2 | 68
19 | 3 | 68
19 | 4 | 68
19 | 5 | 59
19 | 6 | 51
19 | 7 | 49
19 | 8 | 48
19 | 9 | 46
19 | 10 | 46
19 | 11 | 45
19 | 12 | 45
19 | 13 | 44
19 | 14 | 44
19 | 15 | 43
19 | 16 | 43
19 | 17 | 43
19 | 18 | 43
19 | 19 | 43
19 | 20 | 43
19 | 21 | 43
19 | 22 | 43
19 | 23 | 42
19 | 24 | 40 | 49 | 16 | -16
20 | 1 | 39
20 | 2 | 38
20 | 3 | 39
20 | 4 | 38
20 | 5 | 37
20 | 6 | 34
20 | 7 | 33
20 | 8 | 36
20 | 9 | 38
20 | 10 | 39
20 | 11 | 40
20 | 12 | 41
20 | 13 | 42
20 | 14 | 43
20 | 15 | 44
20 | 16 | 44
20 | 17 | 43
20 | 18 | 40
20 | 19 | 39
20 | 20 | 37
20 | 21 | 36
20 | 22 | 36
20 | 23 | 36
20 | 24 | 36 | 38.6667 | 26.3333 | -26.3333
21 | 1 | 35
21 | 2 | 36
21 | 3 | 36
21 | 4 | 36
21 | 5 | 35
21 | 6 | 34
21 | 7 | 34
21 | 8 | 37
21 | 9 | 41
21 | 10 | 42
21 | 11 | 43
21 | 12 | 45
21 | 13 | 46
21 | 14 | 47
21 | 15 | 47
21 | 16 | 46
21 | 17 | 43
21 | 18 | 41
21 | 19 | 40
21 | 20 | 39
21 | 21 | 37
21 | 22 | 36
21 | 23 | 36
21 | 24 | 36 | 39.5 | 25.5 | -25.5
22 | 1 | 38
22 | 2 | 38
22 | 3 | 39
22 | 4 | 39
22 | 5 | 40
22 | 6 | 39
22 | 7 | 37
22 | 8 | 40
22 | 9 | 42
22 | 10 | 43
22 | 11 | 44
22 | 12 | 45
22 | 13 | 47
22 | 14 | 49
22 | 15 | 50
22 | 16 | 51
22 | 17 | 50
22 | 18 | 48
22 | 19 | 45
22 | 20 | 44
22 | 21 | 40
22 | 22 | 41
22 | 23 | 39
22 | 24 | 36 | 42.6667 | 22.3333 | -22.3333
23 | 1 | 35
23 | 2 | 35
23 | 3 | 34
23 | 4 | 33
23 | 5 | 34
23 | 6 | 32
23 | 7 | 33
23 | 8 | 42
23 | 9 | 47
23 | 10 | 50
23 | 11 | 52
23 | 12 | 51
23 | 13 | 51
23 | 14 | 51
23 | 15 | 52
23 | 16 | 52
23 | 17 | 50
23 | 18 | 49
23 | 19 | 47
23 | 20 | 45
23 | 21 | 44
23 | 22 | 42
23 | 23 | 40
23 | 24 | 38 | 43.2917 | 21.7083 | -21.7083
24 | 1 | 37
24 | 2 | 37
24 | 3 | 36
24 | 4 | 37
24 | 5 | 37
24 | 6 | 36
24 | 7 | 37
24 | 8 | 39
24 | 9 | 49
24 | 10 | 51
24 | 11 | 54
24 | 12 | 54
24 | 13 | 55
24 | 14 | 54
24 | 15 | 57
24 | 16 | 57
24 | 17 | 55
24 | 18 | 51
24 | 19 | 50
24 | 20 | 46
24 | 21 | 44
24 | 22 | 43
24 | 23 | 44
24 | 24 | 43 | 45.9583 | 19.0417 | -19.0417
25 | 1 | 42
25 | 2 | 43
25 | 3 | 41
25 | 4 | 41
25 | 5 | 42
25 | 6 | 43
25 | 7 | 43
25 | 8 | 47
25 | 9 | 50
25 | 10 | 51
25 | 11 | 52
25 | 12 | 53
25 | 13 | 54
25 | 14 | 57
25 | 15 | 59
25 | 16 | 59
25 | 17 | 58
25 | 18 | 54
25 | 19 | 52
25 | 20 | 50
25 | 21 | 48
25 | 22 | 47
25 | 23 | 46
25 | 24 | 44 | 49 | 16 | -16
26 | 1 | 43
26 | 2 | 41
26 | 3 | 41
26 | 4 | 43
26 | 5 | 45
26 | 6 | 46
26 | 7 | 48
26 | 8 | 50
26 | 9 | 53
26 | 10 | 56
26 | 11 | 59
26 | 12 | 61
26 | 13 | 64
26 | 14 | 64
26 | 15 | 66
26 | 16 | 65
26 | 17 | 64
26 | 18 | 62
26 | 19 | 62
26 | 20 | 61
26 | 21 | 60
26 | 22 | 58
26 | 23 | 55
26 | 24 | 56 | 55.125 | 9.875 | -9.875
27 | 1 | 56
27 | 2 | 56
27 | 3 | 56
27 | 4 | 56
27 | 5 | 57
27 | 6 | 57
27 | 7 | 54
27 | 8 | 58
27 | 9 | 63
27 | 10 | 63
27 | 11 | 64
27 | 12 | 67
27 | 13 | 67
27 | 14 | 68
27 | 15 | 68
27 | 16 | 68
27 | 17 | 66
27 | 18 | 66
27 | 19 | 64
27 | 20 | 63
27 | 21 | 61
27 | 22 | 57
27 | 23 | 58
27 | 24 | 57 | 61.25 | 3.75 | -3.75
28 | 1 | 56
28 | 2 | 56
28 | 3 | 55
28 | 4 | 54
28 | 5 | 55
28 | 6 | 55
28 | 7 | 55
28 | 8 | 57
28 | 9 | 61
28 | 10 | 65
28 | 11 | 69
28 | 12 | 71
28 | 13 | 72
28 | 14 | 72
28 | 15 | 69
28 | 16 | 69
28 | 17 | 69
28 | 18 | 67
28 | 19 | 66
28 | 20 | 66
28 | 21 | 66
28 | 22 | 66
28 | 23 | 65
28 | 24 | 65 | 63.375 | 1.625 | -1.625
29 | 1 | 64
29 | 2 | 65
29 | 3 | 65
29 | 4 | 65
29 | 5 | 65
29 | 6 | 66
29 | 7 | 67
29 | 8 | 69
29 | 9 | 68
29 | 10 | 71
29 | 11 | 72
29 | 12 | 72
29 | 13 | 71
29 | 14 | 54
29 | 15 | 54
29 | 16 | 54
29 | 17 | 54
29 | 18 | 54
29 | 19 | 55
29 | 20 | 55
29 | 21 | 53
29 | 22 | 53
29 | 23 | 52
29 | 24 | 51 | 61.2083 | 3.7917 | -3.7917
30 | 1 | 51
30 | 2 | 51
30 | 3 | 51
30 | 4 | 52
30 | 5 | 51
30 | 6 | 53
30 | 7 | 52
30 | 8 | 55
30 | 9 | 59
30 | 10 | 62
30 | 11 | 64
30 | 12 | 66
30 | 13 | 68
30 | 14 | 68
30 | 15 | 69
30 | 16 | 69
30 | 17 | 66
30 | 18 | 63
30 | 19 | 61
30 | 20 | 59
30 | 21 | 57
30 | 22 | 56
30 | 23 | 57
30 | 24 | 57 | 59.0417 | 5.9583 | -5.9583
31 | 1 | 55
31 | 2 | 57
31 | 3 | 55
31 | 4 | 54
31 | 5 | 55
31 | 6 | 57
31 | 7 | 57
31 | 8 | 57
31 | 9 | 58
31 | 10 | 58
31 | 11 | 59
31 | 12 | 61
31 | 13 | 61
31 | 14 | 62
31 | 15 | 63
31 | 16 | 63
31 | 17 | 62
31 | 18 | 59
31 | 19 | 58
31 | 20 | 58
31 | 21 | 57
31 | 22 | 59
31 | 23 | 60
31 | 24 | 62 | 58.625 | 6.375 | -6.375
32 | 1 | 63
32 | 2 | 65
32 | 3 | 66
32 | 4 | 68
32 | 5 | 69
32 | 6 | 69
32 | 7 | 69
32 | 8 | 69
32 | 9 | 71
32 | 10 | 75
32 | 11 | 77
32 | 12 | 79
32 | 13 | 80
32 | 14 | 79
32 | 15 | 79
32 | 16 | 78
32 | 17 | 77
32 | 18 | 74
32 | 19 | 71
32 | 20 | 71
32 | 21 | 69
32 | 22 | 69
32 | 23 | 68
32 | 24 | 68 | 71.7917 | -6.7917 | 6.7917
33 | 1 | 67
33 | 2 | 67
33 | 3 | 67
33 | 4 | 66
33 | 5 | 64
33 | 6 | 63
33 | 7 | 65
33 | 8 | 67
33 | 9 | 68
33 | 10 | 71
33 | 11 | 75
33 | 12 | 77
33 | 13 | 77
33 | 14 | 79
33 | 15 | 78
33 | 16 | 78
33 | 17 | 77
33 | 18 | 74
33 | 19 | 72
33 | 20 | 70
33 | 21 | 69
33 | 22 | 69
33 | 23 | 69
33 | 24 | 69 | 70.75 | -5.75 | 5.75
34 | 1 | 69
34 | 2 | 67
34 | 3 | 67
34 | 4 | 67
34 | 5 | 67
34 | 6 | 67
34 | 7 | 67
34 | 8 | 68
34 | 9 | 69
34 | 10 | 73
34 | 11 | 75
34 | 12 | 78
34 | 13 | 77
34 | 14 | 74
34 | 15 | 71
34 | 16 | 66
34 | 17 | 61
34 | 18 | 57
34 | 19 | 54
34 | 20 | 52
34 | 21 | 50
34 | 22 | 49
34 | 23 | 48
34 | 24 | 46 | 64.125 | 0.875 | -0.875
35 | 1 | 45
35 | 2 | 44
35 | 3 | 44
35 | 4 | 44
35 | 5 | 43
35 | 6 | 43
35 | 7 | 43
35 | 8 | 43
35 | 9 | 43
35 | 10 | 43
35 | 11 | 43
35 | 12 | 44
35 | 13 | 44
35 | 14 | 45
35 | 15 | 45
35 | 16 | 45
35 | 17 | 45
35 | 18 | 45
35 | 19 | 46
35 | 20 | 46
35 | 21 | 46
35 | 22 | 46
35 | 23 | 46
35 | 24 | 46 | 44.4583 | 20.5417 | -20.5417
36 | 1 | 45
36 | 2 | 45
36 | 3 | 45
36 | 4 | 45
36 | 5 | 45
36 | 6 | 46
36 | 7 | 46
36 | 8 | 44
36 | 9 | 44
36 | 10 | 45
36 | 11 | 47
36 | 12 | 46
36 | 13 | 45
36 | 14 | 47
36 | 15 | 49
36 | 16 | 49
36 | 17 | 49
36 | 18 | 49
36 | 19 | 49
36 | 20 | 49
36 | 21 | 49
36 | 22 | 49
36 | 23 | 49
36 | 24 | 49 | 46.875 | 18.125 | -18.125
37 | 1 | 48
37 | 2 | 48
37 | 3 | 46
37 | 4 | 44
37 | 5 | 43
37 | 6 | 42
37 | 7 | 42
37 | 8 | 42
37 | 9 | 42
37 | 10 | 43
37 | 11 | 44
37 | 12 | 44
37 | 13 | 44
37 | 14 | 45
37 | 15 | 45
37 | 16 | 44
37 | 17 | 44
37 | 18 | 44
37 | 19 | 42
37 | 20 | 40
37 | 21 | 39
37 | 22 | 38
37 | 23 | 38
37 | 24 | 37 | 42.8333 | 22.1667 | -22.1667
38 | 1 | 37
38 | 2 | 37
38 | 3 | 36
38 | 4 | 37
38 | 5 | 37
38 | 6 | 36
38 | 7 | 36
38 | 8 | 36
38 | 9 | 37
38 | 10 | 37
38 | 11 | 38
38 | 12 | 40
38 | 13 | 42
38 | 14 | 41
38 | 15 | 43
38 | 16 | 41
38 | 17 | 42
38 | 18 | 41
38 | 19 | 40
38 | 20 | 39
38 | 21 | 38
38 | 22 | 38
38 | 23 | 37
38 | 24 | 37 | 38.4583 | 26.5417 | -26.5417
39 | 1 | 37
39 | 2 | 38
39 | 3 | 38
39 | 4 | 38
39 | 5 | 38
39 | 6 | 39
39 | 7 | 38
39 | 8 | 39
39 | 9 | 41
39 | 10 | 42
39 | 11 | 44
39 | 12 | 46
39 | 13 | 49
39 | 14 | 51
39 | 15 | 52
39 | 16 | 53
39 | 17 | 51
39 | 18 | 48
39 | 19 | 47
39 | 20 | 46
39 | 21 | 44
39 | 22 | 43
39 | 23 | 42
39 | 24 | 42 | 43.5833 | 21.4167 | -21.4167
40 | 1 | 41
40 | 2 | 41
40 | 3 | 40
40 | 4 | 40
40 | 5 | 40
40 | 6 | 39
40 | 7 | 39
40 | 8 | 40
40 | 9 | 41
40 | 10 | 42
40 | 11 | 44
40 | 12 | 46
40 | 13 | 48
40 | 14 | 48
40 | 15 | 51
40 | 16 | 51
40 | 17 | 50
40 | 18 | 47
40 | 19 | 46
40 | 20 | 45
40 | 21 | 44
40 | 22 | 43
40 | 23 | 42
40 | 24 | 41 | 43.7083 | 21.2917 | -21.2917
41 | 1 | 40
41 | 2 | 39
41 | 3 | 38
41 | 4 | 36
41 | 5 | 36
41 | 6 | 36
41 | 7 | 35
41 | 8 | 38
41 | 9 | 41
41 | 10 | 43
41 | 11 | 45
41 | 12 | 47
41 | 13 | 51
41 | 14 | 52
41 | 15 | 54
41 | 16 | 55
41 | 17 | 54
41 | 18 | 49
41 | 19 | 47
41 | 20 | 46
41 | 21 | 44
41 | 22 | 43
41 | 23 | 41
41 | 24 | 40 | 43.75 | 21.25 | -21.25
42 | 1 | 38
42 | 2 | 38
42 | 3 | 37
42 | 4 | 36
42 | 5 | 35
42 | 6 | 35
42 | 7 | 35
42 | 8 | 41
42 | 9 | 52
42 | 10 | 56
42 | 11 | 58
42 | 12 | 61
42 | 13 | 61
42 | 14 | 62
42 | 15 | 62
42 | 16 | 61
42 | 17 | 60
42 | 18 | 55
42 | 19 | 54
42 | 20 | 53
42 | 21 | 52
42 | 22 | 50
42 | 23 | 49
42 | 24 | 47 | 49.5 | 15.5 | -15.5
43 | 1 | 47
43 | 2 | 47
43 | 3 | 43
43 | 4 | 45
43 | 5 | 45
43 | 6 | 46
43 | 7 | 48
43 | 8 | 52
43 | 9 | 56
43 | 10 | 60
43 | 11 | 61
43 | 12 | 63
43 | 13 | 67
43 | 14 | 69
43 | 15 | 69
43 | 16 | 68
43 | 17 | 65
43 | 18 | 62
43 | 19 | 59
43 | 20 | 55
43 | 21 | 55
43 | 22 | 55
43 | 23 | 55
43 | 24 | 54 | 56.0833 | 8.9167 | -8.9167
44 | 1 | 55
44 | 2 | 58
44 | 3 | 60
44 | 4 | 56
44 | 5 | 54
44 | 6 | 55
44 | 7 | 57
44 | 8 | 59
44 | 9 | 68
44 | 10 | 73
44 | 11 | 75
44 | 12 | 78
44 | 13 | 79
44 | 14 | 78
44 | 15 | 77
44 | 16 | 76
44 | 17 | 76
44 | 18 | 73
44 | 19 | 69
44 | 20 | 69
44 | 21 | 68
44 | 22 | 68
44 | 23 | 70
44 | 24 | 70 | 67.5417 | -2.5417 | 2.5417
45 | 1 | 69
45 | 2 | 68
45 | 3 | 68
45 | 4 | 68
45 | 5 | 67
45 | 6 | 64
45 | 7 | 62
45 | 8 | 64
45 | 9 | 65
45 | 10 | 76
45 | 11 | 78
45 | 12 | 80
45 | 13 | 81
45 | 14 | 82
45 | 15 | 81
45 | 16 | 79
45 | 17 | 77
45 | 18 | 74
45 | 19 | 73
45 | 20 | 72
45 | 21 | 72
45 | 22 | 70
45 | 23 | 70
45 | 24 | 69 | 72.0417 | -7.0417 | 7.0417
46 | 1 | 70
46 | 2 | 70
46 | 3 | 70
46 | 4 | 70
46 | 5 | 69
46 | 6 | 69
46 | 7 | 68
46 | 8 | 70
46 | 9 | 75
46 | 10 | 77
46 | 11 | 78
46 | 12 | 81
46 | 13 | 82
46 | 14 | 82
46 | 15 | 82
46 | 16 | 81
46 | 17 | 79
46 | 18 | 75
46 | 19 | 73
46 | 20 | 70
46 | 21 | 68
46 | 22 | 68
46 | 23 | 67
46 | 24 | 67 | 73.375 | -8.375 | 8.375
47 | 1 | 64
47 | 2 | 65
47 | 3 | 65
47 | 4 | 63
47 | 5 | 63
47 | 6 | 63
47 | 7 | 62
47 | 8 | 63
47 | 9 | 65
47 | 10 | 69
47 | 11 | 75
47 | 12 | 72
47 | 13 | 70
47 | 14 | 73
47 | 15 | 74
47 | 16 | 74
47 | 17 | 73
47 | 18 | 70
47 | 19 | 69
47 | 20 | 67
47 | 21 | 66
47 | 22 | 65
47 | 23 | 64
47 | 24 | 63 | 67.375 | -2.375 | 2.375
48 | 1 | 63
48 | 2 | 63
48 | 3 | 62
48 | 4 | 61
48 | 5 | 60
48 | 6 | 60
48 | 7 | 60
48 | 8 | 59
48 | 9 | 60
48 | 10 | 59
48 | 11 | 62
48 | 12 | 65
48 | 13 | 67
48 | 14 | 68
48 | 15 | 71
48 | 16 | 70
48 | 17 | 69
48 | 18 | 66
48 | 19 | 67
48 | 20 | 64
48 | 21 | 63
48 | 22 | 62
48 | 23 | 61
48 | 24 | 59 | 63.375 | 1.625 | -1.625
49 | 1 | 56
49 | 2 | 55
49 | 3 | 54
49 | 4 | 54
49 | 5 | 54
49 | 6 | 54
49 | 7 | 54
49 | 8 | 54
49 | 9 | 56
49 | 10 | 56
49 | 11 | 55
49 | 12 | 56
49 | 13 | 57
49 | 14 | 57
49 | 15 | 56
49 | 16 | 56
49 | 17 | 55
49 | 18 | 54
49 | 19 | 54
49 | 20 | 54
49 | 21 | 54
49 | 22 | 54
49 | 23 | 53
49 | 24 | 54 | 54.8333 | 10.1667 | -10.1667
50 | 1 | 53
50 | 2 | 53
50 | 3 | 52
50 | 4 | 53
50 | 5 | 52
50 | 6 | 52
50 | 7 | 52
50 | 8 | 52
50 | 9 | 53
50 | 10 | 53
50 | 11 | 55
50 | 12 | 59
50 | 13 | 57
50 | 14 | 57
50 | 15 | 59
50 | 16 | 59
50 | 17 | 59
50 | 18 | 58
50 | 19 | 59
50 | 20 | 60
50 | 21 | 60
50 | 22 | 59
50 | 23 | 59
50 | 24 | 59 | 56 | 9 | -9
51 | 1 | 58
51 | 2 | 58
51 | 3 | 58
51 | 4 | 58
51 | 5 | 58
51 | 6 | 58
51 | 7 | 58
51 | 8 | 60
51 | 9 | 67
51 | 10 | 73
51 | 11 | 76
51 | 12 | 76
51 | 13 | 78
51 | 14 | 77
51 | 15 | 78
51 | 16 | 79
51 | 17 | 76
51 | 18 | 74
51 | 19 | 73
51 | 20 | 72
51 | 21 | 72
51 | 22 | 72
51 | 23 | 72
51 | 24 | 72 | 68.875 | -3.875 | 3.875
52 | 1 | 72
52 | 2 | 71
52 | 3 | 64
52 | 4 | 63
52 | 5 | 63
52 | 6 | 62
52 | 7 | 61
52 | 8 | 60
52 | 9 | 62
52 | 10 | 62
52 | 11 | 62
52 | 12 | 64
52 | 13 | 63
52 | 14 | 62
52 | 15 | 61
52 | 16 | 60
52 | 17 | 59
52 | 18 | 57
52 | 19 | 55
52 | 20 | 54
52 | 21 | 53
52 | 22 | 52
52 | 23 | 51
52 | 24 | 50 | 60.125 | 4.875 | -4.875
53 | 1 | 50
53 | 2 | 49
53 | 3 | 48
53 | 4 | 46
53 | 5 | 46
53 | 6 | 45
53 | 7 | 44
53 | 8 | 45
53 | 9 | 46
53 | 10 | 49
53 | 11 | 48
53 | 12 | 49
53 | 13 | 52
53 | 14 | 54
53 | 15 | 53
53 | 16 | 52
53 | 17 | 51
53 | 18 | 49
53 | 19 | 47
53 | 20 | 46
53 | 21 | 45
53 | 22 | 43
53 | 23 | 42
53 | 24 | 40 | 47.4583 | 17.5417 | -17.5417
54 | 1 | 39
54 | 2 | 38
54 | 3 | 38
54 | 4 | 36
54 | 5 | 35
54 | 6 | 34
54 | 7 | 33
54 | 8 | 34
54 | 9 | 36
54 | 10 | 38
54 | 11 | 39
54 | 12 | 40
54 | 13 | 41
54 | 14 | 42
54 | 15 | 43
54 | 16 | 44
54 | 17 | 42
54 | 18 | 40
54 | 19 | 37
54 | 20 | 36
54 | 21 | 35
54 | 22 | 34
54 | 23 | 32
54 | 24 | 31 | 37.375 | 27.625 | -27.625
55 | 1 | 30
55 | 2 | 30
55 | 3 | 29
55 | 4 | 29
55 | 5 | 29
55 | 6 | 28
55 | 7 | 29
55 | 8 | 31
55 | 9 | 33
55 | 10 | 35
55 | 11 | 37
55 | 12 | 39
55 | 13 | 42
55 | 14 | 44
55 | 15 | 47
55 | 16 | 49
55 | 17 | 49
55 | 18 | 46
55 | 19 | 41
55 | 20 | 42
55 | 21 | 38
55 | 22 | 40
55 | 23 | 39
55 | 24 | 36 | 37.1667 | 27.8333 | -27.8333
56 | 1 | 34
56 | 2 | 34
56 | 3 | 33
56 | 4 | 37
56 | 5 | 39
56 | 6 | 40
56 | 7 | 41
56 | 8 | 44
56 | 9 | 46
56 | 10 | 49
56 | 11 | 51
56 | 12 | 53
56 | 13 | 55
56 | 14 | 56
56 | 15 | 57
56 | 16 | 58
56 | 17 | 58
56 | 18 | 54
56 | 19 | 51
56 | 20 | 50
56 | 21 | 50
56 | 22 | 50
56 | 23 | 52
56 | 24 | 53 | 47.7083 | 17.2917 | -17.2917
57 | 1 | 52
57 | 2 | 51
57 | 3 | 49
57 | 4 | 50
57 | 5 | 50
57 | 6 | 51
57 | 7 | 51
57 | 8 | 56
57 | 9 | 60
57 | 10 | 65
57 | 11 | 68
57 | 12 | 71
57 | 13 | 71
57 | 14 | 70
57 | 15 | 69
57 | 16 | 69
57 | 17 | 68
57 | 18 | 64
57 | 19 | 62
57 | 20 | 59
57 | 21 | 58
57 | 22 | 57
57 | 23 | 56
57 | 24 | 56 | 59.7083 | 5.2917 | -5.2917
58 | 1 | 56
58 | 2 | 54
58 | 3 | 52
58 | 4 | 53
58 | 5 | 57
58 | 6 | 59
58 | 7 | 58
58 | 8 | 61
58 | 9 | 67
58 | 10 | 71
58 | 11 | 73
58 | 12 | 72
58 | 13 | 76
58 | 14 | 74
58 | 15 | 73
58 | 16 | 73
58 | 17 | 71
58 | 18 | 70
58 | 19 | 68
58 | 20 | 67
58 | 21 | 67
58 | 22 | 67
58 | 23 | 67
58 | 24 | 68 | 65.5833 | -0.58333 | 0.58333
59 | 1 | 68
59 | 2 | 67
59 | 3 | 66
59 | 4 | 66
59 | 5 | 66
59 | 6 | 65
59 | 7 | 59
59 | 8 | 59
59 | 9 | 59
59 | 10 | 57
59 | 11 | 56
59 | 12 | 58
59 | 13 | 58
59 | 14 | 59
59 | 15 | 60
59 | 16 | 60
59 | 17 | 61
59 | 18 | 61
59 | 19 | 60
59 | 20 | 59
59 | 21 | 61
59 | 22 | 62
59 | 23 | 62
59 | 24 | 63 | 61.3333 | 3.6667 | -3.6667
60 | 1 | 64
60 | 2 | 65
60 | 3 | 65
60 | 4 | 66
60 | 5 | 67
60 | 6 | 68
60 | 7 | 69
60 | 8 | 67
60 | 9 | 69
60 | 10 | 64
60 | 11 | 64
60 | 12 | 64
60 | 13 | 63
60 | 14 | 63
60 | 15 | 62
60 | 16 | 62
60 | 17 | 61
60 | 18 | 61
60 | 19 | 61
60 | 20 | 61
60 | 21 | 61
60 | 22 | 61
60 | 23 | 62
60 | 24 | 62 | 63.8333 | 1.1667 | -1.1667
61 | 1 | 61
61 | 2 | 62
61 | 3 | 63
61 | 4 | 63
61 | 5 | 63
61 | 6 | 65
61 | 7 | 66
61 | 8 | 66
61 | 9 | 67
61 | 10 | 68
61 | 11 | 73
61 | 12 | 75
61 | 13 | 75
61 | 14 | 73
61 | 15 | 72
61 | 16 | 71
61 | 17 | 71
61 | 18 | 67
61 | 19 | 65
61 | 20 | 64
61 | 21 | 64
61 | 22 | 62
61 | 23 | 61
61 | 24 | 63 | 66.6667 | -1.6667 | 1.6667
62 | 1 | 61
62 | 2 | 61
62 | 3 | 61
62 | 4 | 59
62 | 5 | 59
62 | 6 | 59
62 | 7 | 58
62 | 8 | 59
62 | 9 | 59
62 | 10 | 57
62 | 11 | 55
62 | 12 | 54
62 | 13 | 55
62 | 14 | 53
62 | 15 | 51
62 | 16 | 50
62 | 17 | 50
62 | 18 | 49
62 | 19 | 49
62 | 20 | 48
62 | 21 | 48
62 | 22 | 48
62 | 23 | 48
62 | 24 | 47 | 54.0833 | 10.9167 | -10.9167
63 | 1 | 46
63 | 2 | 46
63 | 3 | 45
63 | 4 | 46
63 | 5 | 44
63 | 6 | 44
63 | 7 | 46
63 | 8 | 47
63 | 9 | 49
63 | 10 | 51
63 | 11 | 53
63 | 12 | 55
63 | 13 | 58
63 | 14 | 61
63 | 15 | 63
63 | 16 | 64
63 | 17 | 63
63 | 18 | 59
63 | 19 | 55
63 | 20 | 54
63 | 21 | 54
63 | 22 | 53
63 | 23 | 51
63 | 24 | 50 | 52.375 | 12.625 | -12.625
64 | 1 | 48
64 | 2 | 48
64 | 3 | 48
64 | 4 | 49
64 | 5 | 48
64 | 6 | 48
64 | 7 | 52
64 | 8 | 56
64 | 9 | 63
64 | 10 | 66
64 | 11 | 68
64 | 12 | 71
64 | 13 | 72
64 | 14 | 72
64 | 15 | 73
64 | 16 | 73
64 | 17 | 71
64 | 18 | 69
64 | 19 | 66
64 | 20 | 65
64 | 21 | 65
64 | 22 | 65
64 | 23 | 65
64 | 24 | 64 | 61.875 | 3.125 | -3.125
65 | 1 | 64
65 | 2 | 63
65 | 3 | 63
65 | 4 | 64
65 | 5 | 65
65 | 6 | 65
65 | 7 | 65
65 | 8 | 67
65 | 9 | 69
65 | 10 | 72
65 | 11 | 75
65 | 12 | 76
65 | 13 | 77
65 | 14 | 77
65 | 15 | 78
65 | 16 | 76
65 | 17 | 74
65 | 18 | 72
65 | 19 | 71
65 | 20 | 70
65 | 21 | 69
65 | 22 | 70
65 | 23 | 68
65 | 24 | 67 | 69.875 | -4.875 | 4.875
66 | 1 | 66
66 | 2 | 66
66 | 3 | 67
66 | 4 | 66
66 | 5 | 67
66 | 6 | 66
66 | 7 | 66
66 | 8 | 67
66 | 9 | 69
66 | 10 | 70
66 | 11 | 70
66 | 12 | 72
66 | 13 | 75
66 | 14 | 77
66 | 15 | 75
66 | 16 | 76
66 | 17 | 73
66 | 18 | 70
66 | 19 | 68
66 | 20 | 69
66 | 21 | 68
66 | 22 | 67
66 | 23 | 69
66 | 24 | 68 | 69.4583 | -4.4583 | 4.4583
67 | 1 | 69
67 | 2 | 69
67 | 3 | 69
67 | 4 | 68
67 | 5 | 62
67 | 6 | 60
67 | 7 | 58
67 | 8 | 57
67 | 9 | 59
67 | 10 | 60
67 | 11 | 62
67 | 12 | 62
67 | 13 | 64
67 | 14 | 65
67 | 15 | 65
67 | 16 | 66
67 | 17 | 65
67 | 18 | 62
67 | 19 | 59
67 | 20 | 61
67 | 21 | 60
67 | 22 | 59
67 | 23 | 57
67 | 24 | 58 | 62.3333 | 2.6667 | -2.6667
68 | 1 | 57
68 | 2 | 55
68 | 3 | 55
68 | 4 | 53
68 | 5 | 52
68 | 6 | 52
68 | 7 | 52
68 | 8 | 54
68 | 9 | 56
68 | 10 | 58
68 | 11 | 61
68 | 12 | 63
68 | 13 | 65
68 | 14 | 66
68 | 15 | 67
68 | 16 | 67
68 | 17 | 66
68 | 18 | 63
68 | 19 | 61
68 | 20 | 61
68 | 21 | 58
68 | 22 | 56
68 | 23 | 57
68 | 24 | 57 | 58.8333 | 6.1667 | -6.1667
69 | 1 | 55
69 | 2 | 56
69 | 3 | 55
69 | 4 | 53
69 | 5 | 52
69 | 6 | 51
69 | 7 | 50
69 | 8 | 52
69 | 9 | 54
69 | 10 | 55
69 | 11 | 57
69 | 12 | 59
69 | 13 | 61
69 | 14 | 62
69 | 15 | 65
69 | 16 | 64
69 | 17 | 63
69 | 18 | 59
69 | 19 | 56
69 | 20 | 54
69 | 21 | 50
69 | 22 | 50
69 | 23 | 49
69 | 24 | 49 | 55.4583 | 9.5417 | -9.5417
70 | 1 | 48
70 | 2 | 46
70 | 3 | 44
70 | 4 | 44
70 | 5 | 41
70 | 6 | 40
70 | 7 | 40
70 | 8 | 52
70 | 9 | 59
70 | 10 | 63
70 | 11 | 65
70 | 12 | 64
70 | 13 | 67
70 | 14 | 66
70 | 15 | 68
70 | 16 | 67
70 | 17 | 65
70 | 18 | 63
70 | 19 | 60
70 | 20 | 60
70 | 21 | 59
70 | 22 | 57
70 | 23 | 57
70 | 24 | 58 | 56.375 | 8.625 | -8.625
71 | 1 | 59
71 | 2 | 59
71 | 3 | 59
71 | 4 | 60
71 | 5 | 60
71 | 6 | 60
71 | 7 | 61
71 | 8 | 63
71 | 9 | 67
71 | 10 | 68
71 | 11 | 69
71 | 12 | 70
71 | 13 | 71
71 | 14 | 69
71 | 15 | 71
71 | 16 | 71
71 | 17 | 69
71 | 18 | 69
71 | 19 | 67
71 | 20 | 68
71 | 21 | 68
71 | 22 | 68
71 | 23 | 67
71 | 24 | 67 | 65.8333 | -0.83333 | 0.83333
72 | 1 | 67
72 | 2 | 67
72 | 3 | 67
72 | 4 | 66
72 | 5 | 63
72 | 6 | 63
72 | 7 | 62
72 | 8 | 65
72 | 9 | 67
72 | 10 | 71
72 | 11 | 73
72 | 12 | 76
72 | 13 | 78
72 | 14 | 79
72 | 15 | 78
72 | 16 | 77
72 | 17 | 74
72 | 18 | 72
72 | 19 | 67
72 | 20 | 65
72 | 21 | 63
72 | 22 | 61
72 | 23 | 59
72 | 24 | 57 | 68.2083 | -3.2083 | 3.2083
73 | 1 | 59
73 | 2 | 58
73 | 3 | 56
73 | 4 | 54
73 | 5 | 55
73 | 6 | 56
73 | 7 | 54
73 | 8 | 57
73 | 9 | 58
73 | 10 | 58
73 | 11 | 57
73 | 12 | 59
73 | 13 | 60
73 | 14 | 60
73 | 15 | 60
73 | 16 | 59
73 | 17 | 58
73 | 18 | 57
73 | 19 | 57
73 | 20 | 56
73 | 21 | 55
73 | 22 | 54
73 | 23 | 53
73 | 24 | 52 | 56.75 | 8.25 | -8.25
74 | 1 | 51
74 | 2 | 51
74 | 3 | 49
74 | 4 | 48
74 | 5 | 48
74 | 6 | 47
74 | 7 | 47
74 | 8 | 48
74 | 9 | 49
74 | 10 | 50
74 | 11 | 53
74 | 12 | 53
74 | 13 | 54
74 | 14 | 56
74 | 15 | 55
74 | 16 | 54
74 | 17 | 54
74 | 18 | 53
74 | 19 | 53
74 | 20 | 52
74 | 21 | 53
74 | 22 | 54
74 | 23 | 54
74 | 24 | 54 | 51.6667 | 13.3333 | -13.3333
75 | 1 | 54
75 | 2 | 53
75 | 3 | 53
75 | 4 | 54
75 | 5 | 55
75 | 6 | 55
75 | 7 | 56
75 | 8 | 58
75 | 9 | 57
75 | 10 | 58
75 | 11 | 59
75 | 12 | 60
75 | 13 | 60
75 | 14 | 61
75 | 15 | 61
75 | 16 | 61
75 | 17 | 60
75 | 18 | 60
75 | 19 | 61
75 | 20 | 61
75 | 21 | 61
75 | 22 | 61
75 | 23 | 61
75 | 24 | 61 | 58.375 | 6.625 | -6.625
76 | 1 | 61
76 | 2 | 60
76 | 3 | 60
76 | 4 | 59
76 | 5 | 59
76 | 6 | 59
76 | 7 | 60
76 | 8 | 61
76 | 9 | 61
76 | 10 | 61
76 | 11 | 62
76 | 12 | 63
76 | 13 | 65
76 | 14 | 66
76 | 15 | 66
76 | 16 | 67
76 | 17 | 66
76 | 18 | 66
76 | 19 | 63
76 | 20 | 62
76 | 21 | 62
76 | 22 | 62
76 | 23 | 62
76 | 24 | 62 | 62.2917 | 2.7083 | -2.7083
77 | 1 | 62
77 | 2 | 62
77 | 3 | 61
77 | 4 | 60
77 | 5 | 61
77 | 6 | 59
77 | 7 | 60
77 | 8 | 62
77 | 9 | 63
77 | 10 | 65
77 | 11 | 66
77 | 12 | 67
77 | 13 | 69
77 | 14 | 70
77 | 15 | 69
77 | 16 | 69
77 | 17 | 67
77 | 18 | 65
77 | 19 | 63
77 | 20 | 61
77 | 21 | 60
77 | 22 | 59
77 | 23 | 58
77 | 24 | 57 | 63.125 | 1.875 | -1.875
78 | 1 | 56
78 | 2 | 56
78 | 3 | 55
78 | 4 | 53
78 | 5 | 54
78 | 6 | 54
78 | 7 | 53
78 | 8 | 59
78 | 9 | 62
78 | 10 | 62
78 | 11 | 66
78 | 12 | 69
78 | 13 | 69
78 | 14 | 70
78 | 15 | 70
78 | 16 | 70
78 | 17 | 70
78 | 18 | 64
78 | 19 | 63
78 | 20 | 61
78 | 21 | 60
78 | 22 | 58
78 | 23 | 56
78 | 24 | 54 | 61 | 4 | -4
79 | 1 | 53
79 | 2 | 52
79 | 3 | 52
79 | 4 | 52
79 | 5 | 51
79 | 6 | 51
79 | 7 | 52
79 | 8 | 60
79 | 9 | 64
79 | 10 | 70
79 | 11 | 73
79 | 12 | 74
79 | 13 | 75
79 | 14 | 74
79 | 15 | 73
79 | 16 | 74
79 | 17 | 73
79 | 18 | 70
79 | 19 | 69
79 | 20 | 68
79 | 21 | 68
79 | 22 | 67
79 | 23 | 67
79 | 24 | 67 | 64.5417 | 0.45833 | -0.45833
80 | 1 | 67
80 | 2 | 67
80 | 3 | 67
80 | 4 | 68
80 | 5 | 67
80 | 6 | 68
80 | 7 | 68
80 | 8 | 70
80 | 9 | 72
80 | 10 | 76
80 | 11 | 79
80 | 12 | 79
80 | 13 | 79
80 | 14 | 78
80 | 15 | 79
80 | 16 | 76
80 | 17 | 75
80 | 18 | 73
80 | 19 | 73
80 | 20 | 73
80 | 21 | 72
80 | 22 | 73
80 | 23 | 73
80 | 24 | 73 | 72.7083 | -7.7083 | 7.7083
81 | 1 | 72
81 | 2 | 72
81 | 3 | 72
81 | 4 | 73
81 | 5 | 73
81 | 6 | 73
81 | 7 | 73
81 | 8 | 74
81 | 9 | 77
81 | 10 | 79
81 | 11 | 81
81 | 12 | 82
81 | 13 | 82
81 | 14 | 82
81 | 15 | 81
81 | 16 | 78
81 | 17 | 77
81 | 18 | 76
81 | 19 | 75
81 | 20 | 75
81 | 21 | 74
81 | 22 | 74
81 | 23 | 74
81 | 24 | 74 | 75.9583 | -10.9583 | 10.9583
82 | 1 | 73
82 | 2 | 73
82 | 3 | 73
82 | 4 | 73
82 | 5 | 72
82 | 6 | 71
82 | 7 | 73
82 | 8 | 74
82 | 9 | 78
82 | 10 | 79
82 | 11 | 77
82 | 12 | 78
82 | 13 | 76
82 | 14 | 78
82 | 15 | 78
82 | 16 | 77
82 | 17 | 75
82 | 18 | 72
82 | 19 | 72
82 | 20 | 67
82 | 21 | 67
82 | 22 | 66
82 | 23 | 64
82 | 24 | 66 | 73 | -8 | 8
83 | 1 | 64
83 | 2 | 63
83 | 3 | 64
83 | 4 | 64
83 | 5 | 62
83 | 6 | 58
83 | 7 | 60
83 | 8 | 70
83 | 9 | 71
83 | 10 | 74
83 | 11 | 76
83 | 12 | 77
83 | 13 | 79
83 | 14 | 80
83 | 15 | 81
83 | 16 | 78
83 | 17 | 78
83 | 18 | 74
83 | 19 | 72
83 | 20 | 70
83 | 21 | 69
83 | 22 | 67
83 | 23 | 64
83 | 24 | 61 | 69.8333 | -4.8333 | 4.8333
84 | 1 | 60
84 | 2 | 58
84 | 3 | 57
84 | 4 | 56
84 | 5 | 57
84 | 6 | 57
84 | 7 | 58
84 | 8 | 68
84 | 9 | 72
84 | 10 | 77
84 | 11 | 79
84 | 12 | 80
84 | 13 | 81
84 | 14 | 83
84 | 15 | 81
84 | 16 | 79
84 | 17 | 77
84 | 18 | 74
84 | 19 | 71
84 | 20 | 70
84 | 21 | 69
84 | 22 | 67
84 | 23 | 66
84 | 24 | 67 | 69.3333 | -4.3333 | 4.3333
85 | 1 | 66
85 | 2 | 66
85 | 3 | 63
85 | 4 | 67
85 | 5 | 68
85 | 6 | 69
85 | 7 | 70
85 | 8 | 74
85 | 9 | 76
85 | 10 | 77
85 | 11 | 77
85 | 12 | 80
85 | 13 | 80
85 | 14 | 81
85 | 15 | 80
85 | 16 | 80
85 | 17 | 78
85 | 18 | 75
85 | 19 | 73
85 | 20 | 72
85 | 21 | 71
85 | 22 | 71
85 | 23 | 72
85 | 24 | 73 | 73.2917 | -8.2917 | 8.2917
86 | 1 | 73
86 | 2 | 73
86 | 3 | 73
86 | 4 | 73
86 | 5 | 73
86 | 6 | 73
86 | 7 | 73
86 | 8 | 74
86 | 9 | 77
86 | 10 | 78
86 | 11 | 81
86 | 12 | 83
86 | 13 | 83
86 | 14 | 83
86 | 15 | 83
86 | 16 | 81
86 | 17 | 79
86 | 18 | 78
86 | 19 | 76
86 | 20 | 74
86 | 21 | 74
86 | 22 | 74
86 | 23 | 73
86 | 24 | 73 | 76.4583 | -11.4583 | 11.4583
87 | 1 | 71
87 | 2 | 72
87 | 3 | 71
87 | 4 | 71
87 | 5 | 71
87 | 6 | 70
87 | 7 | 71
87 | 8 | 73
87 | 9 | 76
87 | 10 | 78
87 | 11 | 79
87 | 12 | 79
87 | 13 | 79
87 | 14 | 78
87 | 15 | 79
87 | 16 | 78
87 | 17 | 77
87 | 18 | 76
87 | 19 | 75
87 | 20 | 75
87 | 21 | 74
87 | 22 | 74
87 | 23 | 74
87 | 24 | 74 | 74.7917 | -9.7917 | 9.7917
88 | 1 | 75
88 | 2 | 75
88 | 3 | 75
88 | 4 | 75
88 | 5 | 75
88 | 6 | 75
88 | 7 | 74
88 | 8 | 72
88 | 9 | 71
88 | 10 | 72
88 | 11 | 71
88 | 12 | 70
88 | 13 | 71
88 | 14 | 72
88 | 15 | 71
88 | 16 | 71
88 | 17 | 69
88 | 18 | 67
88 | 19 | 65
88 | 20 | 63
88 | 21 | 58
88 | 22 | 55
88 | 23 | 53
88 | 24 | 51 | 68.5833 | -3.5833 | 3.5833
89 | 1 | 50
89 | 2 | 50
89 | 3 | 49
89 | 4 | 49
89 | 5 | 48
89 | 6 | 48
89 | 7 | 48
89 | 8 | 49
89 | 9 | 50
89 | 10 | 52
89 | 11 | 54
89 | 12 | 57
89 | 13 | 60
89 | 14 | 62
89 | 15 | 63
89 | 16 | 64
89 | 17 | 63
89 | 18 | 61
89 | 19 | 58
89 | 20 | 58
89 | 21 | 57
89 | 22 | 56
89 | 23 | 55
89 | 24 | 52 | 54.7083 | 10.2917 | -10.2917
90 | 1 | 51
90 | 2 | 50
90 | 3 | 48
90 | 4 | 47
90 | 5 | 48
90 | 6 | 47
90 | 7 | 50
90 | 8 | 52
90 | 9 | 54
90 | 10 | 56
90 | 11 | 58
90 | 12 | 61
90 | 13 | 63
90 | 14 | 66
90 | 15 | 67
90 | 16 | 67
90 | 17 | 67
90 | 18 | 64
90 | 19 | 60
90 | 20 | 59
90 | 21 | 58
90 | 22 | 58
90 | 23 | 57
90 | 24 | 57 | 56.875 | 8.125 | -8.125
91 | 1 | 57
91 | 2 | 56
91 | 3 | 56
91 | 4 | 56
91 | 5 | 55
91 | 6 | 54
91 | 7 | 54
91 | 8 | 56
91 | 9 | 58
91 | 10 | 61
91 | 11 | 62
91 | 12 | 63
91 | 13 | 65
91 | 14 | 66
91 | 15 | 68
91 | 16 | 67
91 | 17 | 67
91 | 18 | 64
91 | 19 | 57
91 | 20 | 57
91 | 21 | 57
91 | 22 | 52
91 | 23 | 47
91 | 24 | 44 | 58.2917 | 6.7083 | -6.7083
92 | 1 | 43
92 | 2 | 43
92 | 3 | 42
92 | 4 | 43
92 | 5 | 42
92 | 6 | 41
92 | 7 | 48
92 | 8 | 59
92 | 9 | 65
92 | 10 | 69
92 | 11 | 71
92 | 12 | 72
92 | 13 | 73
92 | 14 | 75
92 | 15 | 74
92 | 16 | 74
92 | 17 | 72
92 | 18 | 68
92 | 19 | 64
92 | 20 | 63
92 | 21 | 60
92 | 22 | 58
92 | 23 | 54
92 | 24 | 49 | 59.25 | 5.75 | -5.75
93 | 1 | 47
93 | 2 | 46
93 | 3 | 44
93 | 4 | 44
93 | 5 | 43
93 | 6 | 42
93 | 7 | 52
93 | 8 | 64
93 | 9 | 69
93 | 10 | 72
93 | 11 | 74
93 | 12 | 74
93 | 13 | 75
93 | 14 | 74
93 | 15 | 73
93 | 16 | 73
93 | 17 | 71
93 | 18 | 68
93 | 19 | 65
93 | 20 | 66
93 | 21 | 66
93 | 22 | 65
93 | 23 | 64
93 | 24 | 64 | 62.2917 | 2.7083 | -2.7083
94 | 1 | 62
94 | 2 | 61
94 | 3 | 61
94 | 4 | 64
94 | 5 | 64
94 | 6 | 64
94 | 7 | 64
94 | 8 | 65
94 | 9 | 65
94 | 10 | 65
94 | 11 | 65
94 | 12 | 66
94 | 13 | 66
94 | 14 | 68
94 | 15 | 68
94 | 16 | 67
94 | 17 | 67
94 | 18 | 65
94 | 19 | 63
94 | 20 | 63
94 | 21 | 63
94 | 22 | 62
94 | 23 | 62
94 | 24 | 62 | 64.25 | 0.75 | -0.75
95 | 1 | 63
95 | 2 | 63
95 | 3 | 63
95 | 4 | 63
95 | 5 | 63
95 | 6 | 63
95 | 7 | 63
95 | 8 | 65
95 | 9 | 65
95 | 10 | 66
95 | 11 | 67
95 | 12 | 66
95 | 13 | 63
95 | 14 | 65
95 | 15 | 64
95 | 16 | 65
95 | 17 | 64
95 | 18 | 63
95 | 19 | 63
95 | 20 | 63
95 | 21 | 64
95 | 22 | 64
95 | 23 | 64
95 | 24 | 63 | 63.9583 | 1.0417 | -1.0417
96 | 1 | 63
96 | 2 | 63
96 | 3 | 63
96 | 4 | 63
96 | 5 | 61
96 | 6 | 62
96 | 7 | 63
96 | 8 | 66
96 | 9 | 67
96 | 10 | 68
96 | 11 | 72
96 | 12 | 74
96 | 13 | 76
96 | 14 | 78
96 | 15 | 75
96 | 16 | 74
96 | 17 | 73
96 | 18 | 71
96 | 19 | 66
96 | 20 | 68
96 | 21 | 67
96 | 22 | 65
96 | 23 | 64
96 | 24 | 61 | 67.625 | -2.625 | 2.625
97 | 1 | 61
97 | 2 | 58
97 | 3 | 56
97 | 4 | 54
97 | 5 | 59
97 | 6 | 60
97 | 7 | 62
97 | 8 | 67
97 | 9 | 69
97 | 10 | 72
97 | 11 | 72
97 | 12 | 74
97 | 13 | 75
97 | 14 | 76
97 | 15 | 76
97 | 16 | 73
97 | 17 | 72
97 | 18 | 69
97 | 19 | 67
97 | 20 | 66
97 | 21 | 64
97 | 22 | 63
97 | 23 | 60
97 | 24 | 58 | 65.9583 | -0.95833 | 0.95833
98 | 1 | 58
98 | 2 | 56
98 | 3 | 56
98 | 4 | 55
98 | 5 | 54
98 | 6 | 58
98 | 7 | 62
98 | 8 | 68
98 | 9 | 71
98 | 10 | 74
98 | 11 | 77
98 | 12 | 76
98 | 13 | 79
98 | 14 | 79
98 | 15 | 80
98 | 16 | 80
98 | 17 | 77
98 | 18 | 74
98 | 19 | 71
98 | 20 | 70
98 | 21 | 69
98 | 22 | 68
98 | 23 | 67
98 | 24 | 67 | 68.5833 | -3.5833 | 3.5833
99 | 1 | 66
99 | 2 | 66
99 | 3 | 58
99 | 4 | 62
99 | 5 | 64
99 | 6 | 65
99 | 7 | 68
99 | 8 | 72
99 | 9 | 74
99 | 10 | 79
99 | 11 | 80
99 | 12 | 80
99 | 13 | 80
99 | 14 | 81
99 | 15 | 81
99 | 16 | 81
99 | 17 | 78
99 | 18 | 75
99 | 19 | 72
99 | 20 | 71
99 | 21 | 69
99 | 22 | 70
99 | 23 | 70
99 | 24 | 69 | 72.125 | -7.125 | 7.125
100 | 1 | 69
100 | 2 | 69
100 | 3 | 69
100 | 4 | 69
100 | 5 | 69
100 | 6 | 69
100 | 7 | 71
100 | 8 | 75
100 | 9 | 76
100 | 10 | 78
100 | 11 | 79
100 | 12 | 81
100 | 13 | 79
100 | 14 | 78
100 | 15 | 77
100 | 16 | 75
100 | 17 | 75
100 | 18 | 74
100 | 19 | 74
100 | 20 | 70
100 | 21 | 71
100 | 22 | 70
100 | 23 | 71
100 | 24 | 71 | 73.2917 | -8.2917 | 8.2917
101 | 1 | 72
101 | 2 | 73
101 | 3 | 73
101 | 4 | 75
101 | 5 | 75
101 | 6 | 75
101 | 7 | 67
101 | 8 | 67
101 | 9 | 68
101 | 10 | 75
101 | 11 | 74
101 | 12 | 79
101 | 13 | 75
101 | 14 | 68
101 | 15 | 70
101 | 16 | 72
101 | 17 | 73
101 | 18 | 71
101 | 19 | 71
101 | 20 | 70
101 | 21 | 70
101 | 22 | 70
101 | 23 | 68
101 | 24 | 66 | 71.5417 | -6.5417 | 6.5417
102 | 1 | 65
102 | 2 | 64
102 | 3 | 62
102 | 4 | 62
102 | 5 | 62
102 | 6 | 61
102 | 7 | 64
102 | 8 | 66
102 | 9 | 70
102 | 10 | 71
102 | 11 | 73
102 | 12 | 76
102 | 13 | 77
102 | 14 | 79
102 | 15 | 78
102 | 16 | 79
102 | 17 | 79
102 | 18 | 76
102 | 19 | 70
102 | 20 | 67
102 | 21 | 61
102 | 22 | 58
102 | 23 | 59
102 | 24 | 58 | 68.2083 | -3.2083 | 3.2083
103 | 1 | 55
103 | 2 | 54
103 | 3 | 54
103 | 4 | 55
103 | 5 | 62
103 | 6 | 63
103 | 7 | 65
103 | 8 | 68
103 | 9 | 69
103 | 10 | 70
103 | 11 | 71
103 | 12 | 72
103 | 13 | 75
103 | 14 | 75
103 | 15 | 76
103 | 16 | 76
103 | 17 | 75
103 | 18 | 73
103 | 19 | 68
103 | 20 | 67
103 | 21 | 67
103 | 22 | 65
103 | 23 | 65
103 | 24 | 64 | 66.8333 | -1.8333 | 1.8333
104 | 1 | 62
104 | 2 | 60
104 | 3 | 61
104 | 4 | 61
104 | 5 | 60
104 | 6 | 58
104 | 7 | 63
104 | 8 | 66
104 | 9 | 69
104 | 10 | 72
104 | 11 | 75
104 | 12 | 77
104 | 13 | 75
104 | 14 | 76
104 | 15 | 78
104 | 16 | 77
104 | 17 | 75
104 | 18 | 72
104 | 19 | 68
104 | 20 | 65
104 | 21 | 64
104 | 22 | 56
104 | 23 | 55
104 | 24 | 53 | 66.5833 | -1.5833 | 1.5833
105 | 1 | 53
105 | 2 | 52
105 | 3 | 51
105 | 4 | 50
105 | 5 | 51
105 | 6 | 53
105 | 7 | 60
105 | 8 | 69
105 | 9 | 73
105 | 10 | 74
105 | 11 | 75
105 | 12 | 77
105 | 13 | 77
105 | 14 | 78
105 | 15 | 77
105 | 16 | 77
105 | 17 | 75
105 | 18 | 72
105 | 19 | 70
105 | 20 | 67
105 | 21 | 67
105 | 22 | 66
105 | 23 | 65
105 | 24 | 63 | 66.3333 | -1.3333 | 1.3333
106 | 1 | 61
106 | 2 | 61
106 | 3 | 58
106 | 4 | 58
106 | 5 | 59
106 | 6 | 62
106 | 7 | 66
106 | 8 | 72
106 | 9 | 77
106 | 10 | 78
106 | 11 | 81
106 | 12 | 81
106 | 13 | 82
106 | 14 | 82
106 | 15 | 80
106 | 16 | 80
106 | 17 | 79
106 | 18 | 76
106 | 19 | 74
106 | 20 | 72
106 | 21 | 71
106 | 22 | 71
106 | 23 | 70
106 | 24 | 70 | 71.7083 | -6.7083 | 6.7083
107 | 1 | 69
107 | 2 | 68
107 | 3 | 68
107 | 4 | 68
107 | 5 | 66
107 | 6 | 66
107 | 7 | 71
107 | 8 | 75
107 | 9 | 78
107 | 10 | 81
107 | 11 | 82
107 | 12 | 81
107 | 13 | 83
107 | 14 | 84
107 | 15 | 84
107 | 16 | 82
107 | 17 | 80
107 | 18 | 78
107 | 19 | 76
107 | 20 | 75
107 | 21 | 76
107 | 22 | 75
107 | 23 | 74
107 | 24 | 75 | 75.625 | -10.625 | 10.625
108 | 1 | 75
108 | 2 | 73
108 | 3 | 73
108 | 4 | 73
108 | 5 | 72
108 | 6 | 73
108 | 7 | 75
108 | 8 | 79
108 | 9 | 81
108 | 10 | 82
108 | 11 | 83
108 | 12 | 83
108 | 13 | 85
108 | 14 | 81
108 | 15 | 81
108 | 16 | 81
108 | 17 | 80
108 | 18 | 79
108 | 19 | 78
108 | 20 | 77
108 | 21 | 76
108 | 22 | 76
108 | 23 | 76
108 | 24 | 75 | 77.7917 | -12.7917 | 12.7917
109 | 1 | 76
109 | 2 | 75
109 | 3 | 75
109 | 4 | 73
109 | 5 | 72
109 | 6 | 73
109 | 7 | 75
109 | 8 | 79
109 | 9 | 80
109 | 10 | 82
109 | 11 | 83
109 | 12 | 84
109 | 13 | 84
109 | 14 | 84
109 | 15 | 81
109 | 16 | 80
109 | 17 | 81
109 | 18 | 79
109 | 19 | 77
109 | 20 | 77
109 | 21 | 77
109 | 22 | 76
109 | 23 | 76
109 | 24 | 76 | 78.125 | -13.125 | 13.125
110 | 1 | 76
110 | 2 | 77
110 | 3 | 77
110 | 4 | 77
110 | 5 | 77
110 | 6 | 76
110 | 7 | 77
110 | 8 | 79
110 | 9 | 81
110 | 10 | 81
110 | 11 | 83
110 | 12 | 83
110 | 13 | 82
110 | 14 | 82
110 | 15 | 81
110 | 16 | 82
110 | 17 | 81
110 | 18 | 80
110 | 19 | 80
110 | 20 | 80
110 | 21 | 78
110 | 22 | 77
110 | 23 | 78
110 | 24 | 79 | 79.3333 | -14.3333 | 14.3333
111 | 1 | 77
111 | 2 | 78
111 | 3 | 78
111 | 4 | 70
111 | 5 | 71
111 | 6 | 71
111 | 7 | 72
111 | 8 | 75
111 | 9 | 77
111 | 10 | 79
111 | 11 | 80
111 | 12 | 82
111 | 13 | 81
111 | 14 | 81
111 | 15 | 80
111 | 16 | 81
111 | 17 | 82
111 | 18 | 80
111 | 19 | 79
111 | 20 | 79
111 | 21 | 79
111 | 22 | 78
111 | 23 | 78
111 | 24 | 77 | 77.7083 | -12.7083 | 12.7083
112 | 1 | 77
112 | 2 | 77
112 | 3 | 77
112 | 4 | 77
112 | 5 | 77
112 | 6 | 77
112 | 7 | 78
112 | 8 | 79
112 | 9 | 80
112 | 10 | 82
112 | 11 | 83
112 | 12 | 84
112 | 13 | 83
112 | 14 | 82
112 | 15 | 83
112 | 16 | 81
112 | 17 | 80
112 | 18 | 80
112 | 19 | 78
112 | 20 | 77
112 | 21 | 77
112 | 22 | 77
112 | 23 | 76
112 | 24 | 77 | 79.125 | -14.125 | 14.125
113 | 1 | 77
113 | 2 | 77
113 | 3 | 77
113 | 4 | 77
113 | 5 | 74
113 | 6 | 69
113 | 7 | 72
113 | 8 | 74
113 | 9 | 79
113 | 10 | 80
113 | 11 | 80
113 | 12 | 82
113 | 13 | 84
113 | 14 | 78
113 | 15 | 77
113 | 16 | 73
113 | 17 | 70
113 | 18 | 68
113 | 19 | 66
113 | 20 | 65
113 | 21 | 65
113 | 22 | 64
113 | 23 | 61
113 | 24 | 60 | 72.875 | -7.875 | 7.875
114 | 1 | 58
114 | 2 | 58
114 | 3 | 57
114 | 4 | 56
114 | 5 | 56
114 | 6 | 55
114 | 7 | 55
114 | 8 | 55
114 | 9 | 58
114 | 10 | 61
114 | 11 | 63
114 | 12 | 64
114 | 13 | 66
114 | 14 | 68
114 | 15 | 67
114 | 16 | 68
114 | 17 | 67
114 | 18 | 66
114 | 19 | 62
114 | 20 | 62
114 | 21 | 62
114 | 22 | 62
114 | 23 | 61
114 | 24 | 61 | 61.1667 | 3.8333 | -3.8333
115 | 1 | 61
115 | 2 | 60
115 | 3 | 60
115 | 4 | 59
115 | 5 | 59
115 | 6 | 59
115 | 7 | 62
115 | 8 | 64
115 | 9 | 65
115 | 10 | 67
115 | 11 | 69
115 | 12 | 71
115 | 13 | 71
115 | 14 | 71
115 | 15 | 72
115 | 16 | 71
115 | 17 | 68
115 | 18 | 66
115 | 19 | 63
115 | 20 | 63
115 | 21 | 61
115 | 22 | 52
115 | 23 | 51
115 | 24 | 51 | 63.1667 | 1.8333 | -1.8333
116 | 1 | 49
116 | 2 | 49
116 | 3 | 48
116 | 4 | 47
116 | 5 | 47
116 | 6 | 48
116 | 7 | 61
116 | 8 | 68
116 | 9 | 71
116 | 10 | 72
116 | 11 | 74
116 | 12 | 75
116 | 13 | 76
116 | 14 | 76
116 | 15 | 77
116 | 16 | 76
116 | 17 | 74
116 | 18 | 72
116 | 19 | 68
116 | 20 | 64
116 | 21 | 62
116 | 22 | 65
116 | 23 | 63
116 | 24 | 64 | 64.4167 | 0.58333 | -0.58333
117 | 1 | 61
117 | 2 | 61
117 | 3 | 60
117 | 4 | 65
117 | 5 | 67
117 | 6 | 67
117 | 7 | 68
117 | 8 | 69
117 | 9 | 71
117 | 10 | 73
117 | 11 | 75
117 | 12 | 75
117 | 13 | 74
117 | 14 | 75
117 | 15 | 75
117 | 16 | 75
117 | 17 | 74
117 | 18 | 72
117 | 19 | 69
117 | 20 | 65
117 | 21 | 62
117 | 22 | 62
117 | 23 | 62
117 | 24 | 63 | 68.3333 | -3.3333 | 3.3333
118 | 1 | 62
118 | 2 | 63
118 | 3 | 66
118 | 4 | 64
118 | 5 | 65
118 | 6 | 64
118 | 7 | 67
118 | 8 | 68
118 | 9 | 73
118 | 10 | 75
118 | 11 | 77
118 | 12 | 77
118 | 13 | 80
118 | 14 | 81
118 | 15 | 81
118 | 16 | 82
118 | 17 | 80
118 | 18 | 78
118 | 19 | 70
118 | 20 | 65
118 | 21 | 64
118 | 22 | 69
118 | 23 | 69
118 | 24 | 64 | 71 | -6 | 6
119 | 1 | 62
119 | 2 | 60
119 | 3 | 58
119 | 4 | 58
119 | 5 | 58
119 | 6 | 58
119 | 7 | 66
119 | 8 | 71
119 | 9 | 75
119 | 10 | 78
119 | 11 | 78
119 | 12 | 81
119 | 13 | 82
119 | 14 | 83
119 | 15 | 80
119 | 16 | 79
119 | 17 | 78
119 | 18 | 76
119 | 19 | 74
119 | 20 | 72
119 | 21 | 71
119 | 22 | 71
119 | 23 | 70
119 | 24 | 68 | 71.125 | -6.125 | 6.125
120 | 1 | 64
120 | 2 | 63
120 | 3 | 61
120 | 4 | 60
120 | 5 | 61
120 | 6 | 61
120 | 7 | 68
120 | 8 | 74
120 | 9 | 78
120 | 10 | 80
120 | 11 | 82
120 | 12 | 84
120 | 13 | 86
120 | 14 | 86
120 | 15 | 87
120 | 16 | 84
120 | 17 | 81
120 | 18 | 79
120 | 19 | 76
120 | 20 | 73
120 | 21 | 72
120 | 22 | 72
120 | 23 | 71
120 | 24 | 71 | 73.9167 | -8.9167 | 8.9167
121 | 1 | 71
121 | 2 | 71
121 | 3 | 70
121 | 4 | 70
121 | 5 | 71
121 | 6 | 71
121 | 7 | 70
121 | 8 | 69
121 | 9 | 69
121 | 10 | 70
121 | 11 | 72
121 | 12 | 73
121 | 13 | 72
121 | 14 | 74
121 | 15 | 74
121 | 16 | 74
121 | 17 | 74
121 | 18 | 74
121 | 19 | 73
121 | 20 | 72
121 | 21 | 71
121 | 22 | 70
121 | 23 | 68
121 | 24 | 67 | 71.25 | -6.25 | 6.25
122 | 1 | 66
122 | 2 | 66
122 | 3 | 66
122 | 4 | 66
122 | 5 | 66
122 | 6 | 64
122 | 7 | 66
122 | 8 | 66
122 | 9 | 66
122 | 10 | 67
122 | 11 | 70
122 | 12 | 69
122 | 13 | 73
122 | 14 | 73
122 | 15 | 76
122 | 16 | 76
122 | 17 | 76
122 | 18 | 75
122 | 19 | 73
122 | 20 | 73
122 | 21 | 73
122 | 22 | 73
122 | 23 | 73
122 | 24 | 74 | 70.25 | -5.25 | 5.25
123 | 1 | 73
123 | 2 | 73
123 | 3 | 73
123 | 4 | 75
123 | 5 | 75
123 | 6 | 74
123 | 7 | 75
123 | 8 | 73
123 | 9 | 72
123 | 10 | 72
123 | 11 | 73
123 | 12 | 74
123 | 13 | 80
123 | 14 | 81
123 | 15 | 82
123 | 16 | 81
123 | 17 | 80
123 | 18 | 77
123 | 19 | 72
123 | 20 | 70
123 | 21 | 69
123 | 22 | 70
123 | 23 | 69
123 | 24 | 69 | 74.25 | -9.25 | 9.25
124 | 1 | 67
124 | 2 | 67
124 | 3 | 66
124 | 4 | 66
124 | 5 | 65
124 | 6 | 65
124 | 7 | 69
124 | 8 | 70
124 | 9 | 71
124 | 10 | 75
124 | 11 | 75
124 | 12 | 76
124 | 13 | 77
124 | 14 | 76
124 | 15 | 77
124 | 16 | 73
124 | 17 | 71
124 | 18 | 73
124 | 19 | 68
124 | 20 | 65
124 | 21 | 64
124 | 22 | 67
124 | 23 | 68
124 | 24 | 68 | 69.9583 | -4.9583 | 4.9583
125 | 1 | 69
125 | 2 | 67
125 | 3 | 67
125 | 4 | 66
125 | 5 | 65
125 | 6 | 66
125 | 7 | 68
125 | 8 | 70
125 | 9 | 71
125 | 10 | 73
125 | 11 | 75
125 | 12 | 76
125 | 13 | 78
125 | 14 | 79
125 | 15 | 80
125 | 16 | 82
125 | 17 | 78
125 | 18 | 76
125 | 19 | 71
125 | 20 | 65
125 | 21 | 64
125 | 22 | 63
125 | 23 | 61
125 | 24 | 60 | 70.4167 | -5.4167 | 5.4167
126 | 1 | 58
126 | 2 | 58
126 | 3 | 57
126 | 4 | 56
126 | 5 | 55
126 | 6 | 55
126 | 7 | 68
126 | 8 | 75
126 | 9 | 77
126 | 10 | 80
126 | 11 | 80
126 | 12 | 82
126 | 13 | 82
126 | 14 | 82
126 | 15 | 81
126 | 16 | 81
126 | 17 | 79
126 | 18 | 77
126 | 19 | 74
126 | 20 | 73
126 | 21 | 72
126 | 22 | 71
126 | 23 | 65
126 | 24 | 65 | 70.9583 | -5.9583 | 5.9583
127 | 1 | 62
127 | 2 | 60
127 | 3 | 64
127 | 4 | 62
127 | 5 | 61
127 | 6 | 63
127 | 7 | 72
127 | 8 | 77
127 | 9 | 80
127 | 10 | 81
127 | 11 | 83
127 | 12 | 84
127 | 13 | 85
127 | 14 | 82
127 | 15 | 82
127 | 16 | 84
127 | 17 | 82
127 | 18 | 80
127 | 19 | 78
127 | 20 | 77
127 | 21 | 76
127 | 22 | 76
127 | 23 | 71
127 | 24 | 73 | 74.7917 | -9.7917 | 9.7917
128 | 1 | 75
128 | 2 | 75
128 | 3 | 75
128 | 4 | 74
128 | 5 | 74
128 | 6 | 75
128 | 7 | 75
128 | 8 | 76
128 | 9 | 77
128 | 10 | 78
128 | 11 | 80
128 | 12 | 82
128 | 13 | 84
128 | 14 | 86
128 | 15 | 87
128 | 16 | 85
128 | 17 | 84
128 | 18 | 82
128 | 19 | 78
128 | 20 | 75
128 | 21 | 77
128 | 22 | 77
128 | 23 | 76
128 | 24 | 76 | 78.4583 | -13.4583 | 13.4583
129 | 1 | 75
129 | 2 | 74
129 | 3 | 73
129 | 4 | 73
129 | 5 | 74
129 | 6 | 75
129 | 7 | 77
129 | 8 | 79
129 | 9 | 82
129 | 10 | 84
129 | 11 | 86
129 | 12 | 87
129 | 13 | 88
129 | 14 | 84
129 | 15 | 80
129 | 16 | 80
129 | 17 | 73
129 | 18 | 73
129 | 19 | 73
129 | 20 | 72
129 | 21 | 73
129 | 22 | 71
129 | 23 | 71
129 | 24 | 72 | 77.0417 | -12.0417 | 12.0417
130 | 1 | 71
130 | 2 | 69
130 | 3 | 71
130 | 4 | 69
130 | 5 | 72
130 | 6 | 73
130 | 7 | 74
130 | 8 | 77
130 | 9 | 79
130 | 10 | 80
130 | 11 | 78
130 | 12 | 79
130 | 13 | 82
130 | 14 | 83
130 | 15 | 83
130 | 16 | 82
130 | 17 | 81
130 | 18 | 79
130 | 19 | 76
130 | 20 | 74
130 | 21 | 75
130 | 22 | 73
130 | 23 | 71
130 | 24 | 71 | 75.9167 | -10.9167 | 10.9167
131 | 1 | 70
131 | 2 | 69
131 | 3 | 70
131 | 4 | 69
131 | 5 | 68
131 | 6 | 69
131 | 7 | 75
131 | 8 | 79
131 | 9 | 82
131 | 10 | 84
131 | 11 | 86
131 | 12 | 86
131 | 13 | 88
131 | 14 | 85
131 | 15 | 84
131 | 16 | 81
131 | 17 | 80
131 | 18 | 79
131 | 19 | 78
131 | 20 | 78
131 | 21 | 76
131 | 22 | 74
131 | 23 | 75
131 | 24 | 73 | 77.4167 | -12.4167 | 12.4167
132 | 1 | 71
132 | 2 | 71
132 | 3 | 70
132 | 4 | 69
132 | 5 | 69
132 | 6 | 68
132 | 7 | 76
132 | 8 | 81
132 | 9 | 83
132 | 10 | 83
132 | 11 | 86
132 | 12 | 84
132 | 13 | 86
132 | 14 | 89
132 | 15 | 89
132 | 16 | 87
132 | 17 | 86
132 | 18 | 82
132 | 19 | 80
132 | 20 | 78
132 | 21 | 77
132 | 22 | 76
132 | 23 | 74
132 | 24 | 74 | 78.7083 | -13.7083 | 13.7083
133 | 1 | 71
133 | 2 | 70
133 | 3 | 69
133 | 4 | 68
133 | 5 | 68
133 | 6 | 71
133 | 7 | 77
133 | 8 | 81
133 | 9 | 82
133 | 10 | 85
133 | 11 | 87
133 | 12 | 88
133 | 13 | 88
133 | 14 | 90
133 | 15 | 88
133 | 16 | 86
133 | 17 | 84
133 | 18 | 83
133 | 19 | 80
133 | 20 | 79
133 | 21 | 78
133 | 22 | 78
133 | 23 | 78
133 | 24 | 77 | 79.4167 | -14.4167 | 14.4167
134 | 1 | 76
134 | 2 | 74
134 | 3 | 76
134 | 4 | 77
134 | 5 | 76
134 | 6 | 76
134 | 7 | 72
134 | 8 | 76
134 | 9 | 82
134 | 10 | 81
134 | 11 | 83
134 | 12 | 83
134 | 13 | 84
134 | 14 | 84
134 | 15 | 86
134 | 16 | 85
134 | 17 | 84
134 | 18 | 83
134 | 19 | 80
134 | 20 | 78
134 | 21 | 77
134 | 22 | 77
134 | 23 | 76
134 | 24 | 75 | 79.2083 | -14.2083 | 14.2083
135 | 1 | 74
135 | 2 | 70
135 | 3 | 70
135 | 4 | 73
135 | 5 | 70
135 | 6 | 71
135 | 7 | 78
135 | 8 | 82
135 | 9 | 84
135 | 10 | 85
135 | 11 | 85
135 | 12 | 86
135 | 13 | 89
135 | 14 | 88
135 | 15 | 88
135 | 16 | 86
135 | 17 | 86
135 | 18 | 84
135 | 19 | 81
135 | 20 | 77
135 | 21 | 77
135 | 22 | 77
135 | 23 | 78
135 | 24 | 77 | 79.8333 | -14.8333 | 14.8333
136 | 1 | 76
136 | 2 | 74
136 | 3 | 73
136 | 4 | 71
136 | 5 | 70
136 | 6 | 71
136 | 7 | 80
136 | 8 | 83
136 | 9 | 83
136 | 10 | 83
136 | 11 | 85
136 | 12 | 87
136 | 13 | 88
136 | 14 | 84
136 | 15 | 85
136 | 16 | 87
136 | 17 | 80
136 | 18 | 80
136 | 19 | 77
136 | 20 | 75
136 | 21 | 79
136 | 22 | 79
136 | 23 | 79
136 | 24 | 77 | 79.4167 | -14.4167 | 14.4167
137 | 1 | 77
137 | 2 | 77
137 | 3 | 75
137 | 4 | 76
137 | 5 | 74
137 | 6 | 73
137 | 7 | 76
137 | 8 | 79
137 | 9 | 81
137 | 10 | 83
137 | 11 | 83
137 | 12 | 82
137 | 13 | 81
137 | 14 | 80
137 | 15 | 73
137 | 16 | 74
137 | 17 | 71
137 | 18 | 72
137 | 19 | 73
137 | 20 | 74
137 | 21 | 76
137 | 22 | 75
137 | 23 | 73
137 | 24 | 71 | 76.2083 | -11.2083 | 11.2083
138 | 1 | 69
138 | 2 | 69
138 | 3 | 68
138 | 4 | 72
138 | 5 | 71
138 | 6 | 72
138 | 7 | 74
138 | 8 | 75
138 | 9 | 77
138 | 10 | 79
138 | 11 | 81
138 | 12 | 82
138 | 13 | 84
138 | 14 | 84
138 | 15 | 85
138 | 16 | 86
138 | 17 | 85
138 | 18 | 83
138 | 19 | 79
138 | 20 | 77
138 | 21 | 77
138 | 22 | 76
138 | 23 | 75
138 | 24 | 75 | 77.2917 | -12.2917 | 12.2917
139 | 1 | 74
139 | 2 | 73
139 | 3 | 72
139 | 4 | 70
139 | 5 | 69
139 | 6 | 69
139 | 7 | 70
139 | 8 | 71
139 | 9 | 73
139 | 10 | 74
139 | 11 | 76
139 | 12 | 77
139 | 13 | 78
139 | 14 | 80
139 | 15 | 82
139 | 16 | 81
139 | 17 | 81
139 | 18 | 79
139 | 19 | 76
139 | 20 | 75
139 | 21 | 74
139 | 22 | 74
139 | 23 | 73
139 | 24 | 72 | 74.7083 | -9.7083 | 9.7083
140 | 1 | 70
140 | 2 | 69
140 | 3 | 67
140 | 4 | 67
140 | 5 | 66
140 | 6 | 67
140 | 7 | 69
140 | 8 | 71
140 | 9 | 74
140 | 10 | 76
140 | 11 | 78
140 | 12 | 79
140 | 13 | 80
140 | 14 | 80
140 | 15 | 81
140 | 16 | 80
140 | 17 | 80
140 | 18 | 78
140 | 19 | 71
140 | 20 | 69
140 | 21 | 68
140 | 22 | 63
140 | 23 | 62
140 | 24 | 61 | 71.9167 | -6.9167 | 6.9167
141 | 1 | 58
141 | 2 | 58
141 | 3 | 58
141 | 4 | 60
141 | 5 | 60
141 | 6 | 63
141 | 7 | 72
141 | 8 | 76
141 | 9 | 78
141 | 10 | 80
141 | 11 | 80
141 | 12 | 80
141 | 13 | 81
141 | 14 | 82
141 | 15 | 81
141 | 16 | 83
141 | 17 | 81
141 | 18 | 80
141 | 19 | 75
141 | 20 | 68
141 | 21 | 67
141 | 22 | 68
141 | 23 | 67
141 | 24 | 61 | 71.5417 | -6.5417 | 6.5417
142 | 1 | 64
142 | 2 | 64
142 | 3 | 61
142 | 4 | 62
142 | 5 | 64
142 | 6 | 64
142 | 7 | 74
142 | 8 | 77
142 | 9 | 79
142 | 10 | 82
142 | 11 | 83
142 | 12 | 84
142 | 13 | 84
142 | 14 | 85
142 | 15 | 85
142 | 16 | 85
142 | 17 | 84
142 | 18 | 82
142 | 19 | 72
142 | 20 | 71
142 | 21 | 68
142 | 22 | 66
142 | 23 | 69
142 | 24 | 66 | 73.9583 | -8.9583 | 8.9583
143 | 1 | 64
143 | 2 | 61
143 | 3 | 60
143 | 4 | 61
143 | 5 | 63
143 | 6 | 67
143 | 7 | 72
143 | 8 | 80
143 | 9 | 82
143 | 10 | 84
143 | 11 | 85
143 | 12 | 86
143 | 13 | 88
143 | 14 | 87
143 | 15 | 87
143 | 16 | 86
143 | 17 | 85
143 | 18 | 82
143 | 19 | 79
143 | 20 | 76
143 | 21 | 73
143 | 22 | 73
143 | 23 | 71
143 | 24 | 68 | 75.8333 | -10.8333 | 10.8333
144 | 1 | 68
144 | 2 | 65
144 | 3 | 67
144 | 4 | 67
144 | 5 | 66
144 | 6 | 65
144 | 7 | 73
144 | 8 | 77
144 | 9 | 81
144 | 10 | 83
144 | 11 | 85
144 | 12 | 83
144 | 13 | 85
144 | 14 | 86
144 | 15 | 88
144 | 16 | 85
144 | 17 | 82
144 | 18 | 81
144 | 19 | 79
144 | 20 | 78
144 | 21 | 75
144 | 22 | 73
144 | 23 | 71
144 | 24 | 70 | 76.375 | -11.375 | 11.375
145 | 1 | 69
145 | 2 | 64
145 | 3 | 63
145 | 4 | 65
145 | 5 | 63
145 | 6 | 64
145 | 7 | 73
145 | 8 | 78
145 | 9 | 78
145 | 10 | 81
145 | 11 | 83
145 | 12 | 84
145 | 13 | 85
145 | 14 | 85
145 | 15 | 86
145 | 16 | 84
145 | 17 | 83
145 | 18 | 80
145 | 19 | 77
145 | 20 | 74
145 | 21 | 73
145 | 22 | 72
145 | 23 | 71
145 | 24 | 72 | 75.2917 | -10.2917 | 10.2917
146 | 1 | 71
146 | 2 | 71
146 | 3 | 71
146 | 4 | 69
146 | 5 | 70
146 | 6 | 72
146 | 7 | 77
146 | 8 | 80
146 | 9 | 80
146 | 10 | 83
146 | 11 | 85
146 | 12 | 85
146 | 13 | 87
146 | 14 | 86
146 | 15 | 88
146 | 16 | 85
146 | 17 | 85
146 | 18 | 83
146 | 19 | 80
146 | 20 | 78
146 | 21 | 76
146 | 22 | 75
146 | 23 | 75
146 | 24 | 74 | 78.5833 | -13.5833 | 13.5833
147 | 1 | 74
147 | 2 | 74
147 | 3 | 74
147 | 4 | 71
147 | 5 | 73
147 | 6 | 72
147 | 7 | 78
147 | 8 | 80
147 | 9 | 82
147 | 10 | 82
147 | 11 | 84
147 | 12 | 84
147 | 13 | 85
147 | 14 | 85
147 | 15 | 83
147 | 16 | 78
147 | 17 | 75
147 | 18 | 78
147 | 19 | 75
147 | 20 | 74
147 | 21 | 72
147 | 22 | 73
147 | 23 | 74
147 | 24 | 73 | 77.2083 | -12.2083 | 12.2083
148 | 1 | 71
148 | 2 | 71
148 | 3 | 72
148 | 4 | 71
148 | 5 | 73
148 | 6 | 73
148 | 7 | 75
148 | 8 | 75
148 | 9 | 79
148 | 10 | 82
148 | 11 | 85
148 | 12 | 82
148 | 13 | 81
148 | 14 | 79
148 | 15 | 74
148 | 16 | 73
148 | 17 | 70
148 | 18 | 71
148 | 19 | 72
148 | 20 | 70
148 | 21 | 68
148 | 22 | 68
148 | 23 | 67
148 | 24 | 67 | 73.7083 | -8.7083 | 8.7083
149 | 1 | 65
149 | 2 | 65
149 | 3 | 64
149 | 4 | 66
149 | 5 | 67
149 | 6 | 69
149 | 7 | 74
149 | 8 | 78
149 | 9 | 82
149 | 10 | 84
149 | 11 | 84
149 | 12 | 86
149 | 13 | 85
149 | 14 | 76
149 | 15 | 74
149 | 16 | 79
149 | 17 | 79
149 | 18 | 79
149 | 19 | 76
149 | 20 | 75
149 | 21 | 74
149 | 22 | 72
149 | 23 | 73
149 | 24 | 74 | 75 | -10 | 10
150 | 1 | 74
150 | 2 | 72
150 | 3 | 70
150 | 4 | 68
150 | 5 | 69
150 | 6 | 71
150 | 7 | 75
150 | 8 | 79
150 | 9 | 80
150 | 10 | 80
150 | 11 | 76
150 | 12 | 70
150 | 13 | 71
150 | 14 | 72
150 | 15 | 74
150 | 16 | 75
150 | 17 | 76
150 | 18 | 76
150 | 19 | 73
150 | 20 | 72
150 | 21 | 69
150 | 22 | 68
150 | 23 | 68
150 | 24 | 68 | 72.75 | -7.75 | 7.75
151 | 1 | 68
151 | 2 | 67
151 | 3 | 68
151 | 4 | 66
151 | 5 | 65
151 | 6 | 70
151 | 7 | 75
151 | 8 | 78
151 | 9 | 81
151 | 10 | 79
151 | 11 | 78
151 | 12 | 79
151 | 13 | 78
151 | 14 | 69
151 | 15 | 69
151 | 16 | 72
151 | 17 | 73
151 | 18 | 74
151 | 19 | 70
151 | 20 | 68
151 | 21 | 69
151 | 22 | 69
151 | 23 | 70
151 | 24 | 70 | 71.875 | -6.875 | 6.875
152 | 1 | 71
152 | 2 | 71
152 | 3 | 72
152 | 4 | 72
152 | 5 | 72
152 | 6 | 74
152 | 7 | 78
152 | 8 | 81
152 | 9 | 81
152 | 10 | 85
152 | 11 | 87
152 | 12 | 89
152 | 13 | 88
152 | 14 | 89
152 | 15 | 86
152 | 16 | 88
152 | 17 | 86
152 | 18 | 85
152 | 19 | 81
152 | 20 | 80
152 | 21 | 79
152 | 22 | 77
152 | 23 | 77
152 | 24 | 75 | 80.1667 | -15.1667 | 15.1667
153 | 1 | 76
153 | 2 | 75
153 | 3 | 74
153 | 4 | 74
153 | 5 | 74
153 | 6 | 77
153 | 7 | 80
153 | 8 | 81
153 | 9 | 85
153 | 10 | 86
153 | 11 | 87
153 | 12 | 89
153 | 13 | 85
153 | 14 | 85
153 | 15 | 89
153 | 16 | 87
153 | 17 | 87
153 | 18 | 84
153 | 19 | 82
153 | 20 | 80
153 | 21 | 79
153 | 22 | 78
153 | 23 | 78
153 | 24 | 77 | 81.2083 | -16.2083 | 16.2083
154 | 1 | 75
154 | 2 | 75
154 | 3 | 75
154 | 4 | 73
154 | 5 | 73
154 | 6 | 76
154 | 7 | 79
154 | 8 | 82
154 | 9 | 85
154 | 10 | 86
154 | 11 | 89
154 | 12 | 89
154 | 13 | 88
154 | 14 | 89
154 | 15 | 90
154 | 16 | 90
154 | 17 | 89
154 | 18 | 87
154 | 19 | 84
154 | 20 | 82
154 | 21 | 80
154 | 22 | 78
154 | 23 | 79
154 | 24 | 77 | 82.0833 | -17.0833 | 17.0833
155 | 1 | 77
155 | 2 | 76
155 | 3 | 73
155 | 4 | 75
155 | 5 | 75
155 | 6 | 76
155 | 7 | 80
155 | 8 | 82
155 | 9 | 84
155 | 10 | 85
155 | 11 | 86
155 | 12 | 88
155 | 13 | 90
155 | 14 | 91
155 | 15 | 91
155 | 16 | 91
155 | 17 | 89
155 | 18 | 87
155 | 19 | 85
155 | 20 | 82
155 | 21 | 81
155 | 22 | 80
155 | 23 | 78
155 | 24 | 79 | 82.5417 | -17.5417 | 17.5417
156 | 1 | 78
156 | 2 | 77
156 | 3 | 74
156 | 4 | 74
156 | 5 | 74
156 | 6 | 76
156 | 7 | 81
156 | 8 | 82
156 | 9 | 85
156 | 10 | 86
156 | 11 | 88
156 | 12 | 91
156 | 13 | 91
156 | 14 | 94
156 | 15 | 92
156 | 16 | 92
156 | 17 | 90
156 | 18 | 88
156 | 19 | 85
156 | 20 | 82
156 | 21 | 84
156 | 22 | 82
156 | 23 | 80
156 | 24 | 78 | 83.5 | -18.5 | 18.5
157 | 1 | 78
157 | 2 | 78
157 | 3 | 77
157 | 4 | 79
157 | 5 | 77
157 | 6 | 79
157 | 7 | 81
157 | 8 | 84
157 | 9 | 86
157 | 10 | 85
157 | 11 | 89
157 | 12 | 91
157 | 13 | 89
157 | 14 | 90
157 | 15 | 89
157 | 16 | 89
157 | 17 | 86
157 | 18 | 83
157 | 19 | 82
157 | 20 | 81
157 | 21 | 80
157 | 22 | 80
157 | 23 | 79
157 | 24 | 79 | 82.9583 | -17.9583 | 17.9583
158 | 1 | 78
158 | 2 | 77
158 | 3 | 78
158 | 4 | 77
158 | 5 | 77
158 | 6 | 77
158 | 7 | 81
158 | 8 | 83
158 | 9 | 85
158 | 10 | 87
158 | 11 | 88
158 | 12 | 88
158 | 13 | 86
158 | 14 | 89
158 | 15 | 82
158 | 16 | 78
158 | 17 | 83
158 | 18 | 81
158 | 19 | 80
158 | 20 | 80
158 | 21 | 79
158 | 22 | 78
158 | 23 | 77
158 | 24 | 76 | 81.0417 | -16.0417 | 16.0417
159 | 1 | 75
159 | 2 | 74
159 | 3 | 73
159 | 4 | 72
159 | 5 | 71
159 | 6 | 74
159 | 7 | 80
159 | 8 | 83
159 | 9 | 82
159 | 10 | 85
159 | 11 | 87
159 | 12 | 87
159 | 13 | 87
159 | 14 | 85
159 | 15 | 84
159 | 16 | 87
159 | 17 | 85
159 | 18 | 83
159 | 19 | 82
159 | 20 | 80
159 | 21 | 79
159 | 22 | 78
159 | 23 | 77
159 | 24 | 77 | 80.2917 | -15.2917 | 15.2917
160 | 1 | 76
160 | 2 | 73
160 | 3 | 74
160 | 4 | 74
160 | 5 | 73
160 | 6 | 75
160 | 7 | 80
160 | 8 | 83
160 | 9 | 84
160 | 10 | 84
160 | 11 | 73
160 | 12 | 74
160 | 13 | 77
160 | 14 | 77
160 | 15 | 82
160 | 16 | 82
160 | 17 | 81
160 | 18 | 81
160 | 19 | 79
160 | 20 | 79
160 | 21 | 78
160 | 22 | 77
160 | 23 | 76
160 | 24 | 75 | 77.7917 | -12.7917 | 12.7917
161 | 1 | 76
161 | 2 | 76
161 | 3 | 75
161 | 4 | 74
161 | 5 | 74
161 | 6 | 74
161 | 7 | 78
161 | 8 | 80
161 | 9 | 82
161 | 10 | 84
161 | 11 | 86
161 | 12 | 85
161 | 13 | 84
161 | 14 | 79
161 | 15 | 75
161 | 16 | 80
161 | 17 | 82
161 | 18 | 83
161 | 19 | 81
161 | 20 | 77
161 | 21 | 78
161 | 22 | 78
161 | 23 | 76
161 | 24 | 77 | 78.9167 | -13.9167 | 13.9167
162 | 1 | 74
162 | 2 | 74
162 | 3 | 74
162 | 4 | 73
162 | 5 | 73
162 | 6 | 73
162 | 7 | 77
162 | 8 | 81
162 | 9 | 82
162 | 10 | 84
162 | 11 | 87
162 | 12 | 80
162 | 13 | 73
162 | 14 | 73
162 | 15 | 78
162 | 16 | 82
162 | 17 | 84
162 | 18 | 83
162 | 19 | 81
162 | 20 | 78
162 | 21 | 77
162 | 22 | 77
162 | 23 | 76
162 | 24 | 76 | 77.9167 | -12.9167 | 12.9167
163 | 1 | 76
163 | 2 | 75
163 | 3 | 75
163 | 4 | 74
163 | 5 | 72
163 | 6 | 76
163 | 7 | 79
163 | 8 | 80
163 | 9 | 81
163 | 10 | 80
163 | 11 | 79
163 | 12 | 83
163 | 13 | 85
163 | 14 | 87
163 | 15 | 79
163 | 16 | 80
163 | 17 | 81
163 | 18 | 80
163 | 19 | 78
163 | 20 | 76
163 | 21 | 76
163 | 22 | 77
163 | 23 | 78
163 | 24 | 78 | 78.5417 | -13.5417 | 13.5417
164 | 1 | 78
164 | 2 | 78
164 | 3 | 78
164 | 4 | 77
164 | 5 | 77
164 | 6 | 77
164 | 7 | 79
164 | 8 | 82
164 | 9 | 82
164 | 10 | 85
164 | 11 | 86
164 | 12 | 87
164 | 13 | 72
164 | 14 | 74
164 | 15 | 74
164 | 16 | 77
164 | 17 | 78
164 | 18 | 80
164 | 19 | 78
164 | 20 | 77
164 | 21 | 76
164 | 22 | 77
164 | 23 | 76
164 | 24 | 76 | 78.375 | -13.375 | 13.375
165 | 1 | 75
165 | 2 | 74
165 | 3 | 76
165 | 4 | 74
165 | 5 | 75
165 | 6 | 76
165 | 7 | 78
165 | 8 | 82
165 | 9 | 84
165 | 10 | 86
165 | 11 | 84
165 | 12 | 85
165 | 13 | 80
165 | 14 | 78
165 | 15 | 82
165 | 16 | 83
165 | 17 | 84
165 | 18 | 83
165 | 19 | 82
165 | 20 | 79
165 | 21 | 75
165 | 22 | 76
165 | 23 | 75
165 | 24 | 74 | 79.1667 | -14.1667 | 14.1667
166 | 1 | 74
166 | 2 | 74
166 | 3 | 74
166 | 4 | 73
166 | 5 | 73
166 | 6 | 74
166 | 7 | 78
166 | 8 | 81
166 | 9 | 83
166 | 10 | 84
166 | 11 | 86
166 | 12 | 77
166 | 13 | 75
166 | 14 | 78
166 | 15 | 82
166 | 16 | 81
166 | 17 | 77
166 | 18 | 76
166 | 19 | 77
166 | 20 | 75
166 | 21 | 75
166 | 22 | 74
166 | 23 | 74
166 | 24 | 73 | 77 | -12 | 12
167 | 1 | 73
167 | 2 | 73
167 | 3 | 74
167 | 4 | 73
167 | 5 | 74
167 | 6 | 74
167 | 7 | 79
167 | 8 | 81
167 | 9 | 82
167 | 10 | 83
167 | 11 | 83
167 | 12 | 84
167 | 13 | 77
167 | 14 | 80
167 | 15 | 82
167 | 16 | 82
167 | 17 | 82
167 | 18 | 82
167 | 19 | 80
167 | 20 | 79
167 | 21 | 78
167 | 22 | 78
167 | 23 | 77
167 | 24 | 76 | 78.5833 | -13.5833 | 13.5833
168 | 1 | 77
168 | 2 | 74
168 | 3 | 74
168 | 4 | 74
168 | 5 | 75
168 | 6 | 79
168 | 7 | 80
168 | 8 | 82
168 | 9 | 82
168 | 10 | 85
168 | 11 | 85
168 | 12 | 86
168 | 13 | 88
168 | 14 | 88
168 | 15 | 89
168 | 16 | 89
168 | 17 | 88
168 | 18 | 86
168 | 19 | 84
168 | 20 | 84
168 | 21 | 82
168 | 22 | 82
168 | 23 | 82
168 | 24 | 81 | 82.3333 | -17.3333 | 17.3333
169 | 1 | 80
169 | 2 | 80
169 | 3 | 77
169 | 4 | 77
169 | 5 | 78
169 | 6 | 77
169 | 7 | 78
169 | 8 | 79
169 | 9 | 80
169 | 10 | 82
169 | 11 | 83
169 | 12 | 84
169 | 13 | 84
169 | 14 | 85
169 | 15 | 86
169 | 16 | 85
169 | 17 | 86
169 | 18 | 85
169 | 19 | 83
169 | 20 | 80
169 | 21 | 79
169 | 22 | 78
169 | 23 | 76
169 | 24 | 75 | 80.7083 | -15.7083 | 15.7083
170 | 1 | 73
170 | 2 | 73
170 | 3 | 71
170 | 4 | 74
170 | 5 | 73
170 | 6 | 75
170 | 7 | 79
170 | 8 | 82
170 | 9 | 84
170 | 10 | 85
170 | 11 | 87
170 | 12 | 87
170 | 13 | 88
170 | 14 | 87
170 | 15 | 84
170 | 16 | 81
170 | 17 | 84
170 | 18 | 83
170 | 19 | 82
170 | 20 | 81
170 | 21 | 79
170 | 22 | 79
170 | 23 | 78
170 | 24 | 77 | 80.25 | -15.25 | 15.25
171 | 1 | 76
171 | 2 | 76
171 | 3 | 76
171 | 4 | 76
171 | 5 | 75
171 | 6 | 76
171 | 7 | 79
171 | 8 | 81
171 | 9 | 84
171 | 10 | 84
171 | 11 | 86
171 | 12 | 87
171 | 13 | 86
171 | 14 | 86
171 | 15 | 87
171 | 16 | 87
171 | 17 | 85
171 | 18 | 84
171 | 19 | 82
171 | 20 | 81
171 | 21 | 79
171 | 22 | 79
171 | 23 | 78
171 | 24 | 77 | 81.125 | -16.125 | 16.125
172 | 1 | 78
172 | 2 | 78
172 | 3 | 78
172 | 4 | 78
172 | 5 | 78
172 | 6 | 78
172 | 7 | 79
172 | 8 | 82
172 | 9 | 83
172 | 10 | 83
172 | 11 | 83
172 | 12 | 85
172 | 13 | 82
172 | 14 | 82
172 | 15 | 80
172 | 16 | 82
172 | 17 | 83
172 | 18 | 83
172 | 19 | 77
172 | 20 | 78
172 | 21 | 78
172 | 22 | 78
172 | 23 | 78
172 | 24 | 78 | 80.0833 | -15.0833 | 15.0833
173 | 1 | 77
173 | 2 | 77
173 | 3 | 77
173 | 4 | 76
173 | 5 | 77
173 | 6 | 78
173 | 7 | 80
173 | 8 | 83
173 | 9 | 83
173 | 10 | 84
173 | 11 | 86
173 | 12 | 86
173 | 13 | 88
173 | 14 | 86
173 | 15 | 80
173 | 16 | 82
173 | 17 | 83
173 | 18 | 83
173 | 19 | 82
173 | 20 | 80
173 | 21 | 80
173 | 22 | 80
173 | 23 | 78
173 | 24 | 78 | 81 | -16 | 16
174 | 1 | 77
174 | 2 | 76
174 | 3 | 77
174 | 4 | 77
174 | 5 | 77
174 | 6 | 78
174 | 7 | 81
174 | 8 | 83
174 | 9 | 84
174 | 10 | 87
174 | 11 | 88
174 | 12 | 90
174 | 13 | 89
174 | 14 | 88
174 | 15 | 89
174 | 16 | 89
174 | 17 | 84
174 | 18 | 81
174 | 19 | 83
174 | 20 | 82
174 | 21 | 82
174 | 22 | 80
174 | 23 | 79
174 | 24 | 79 | 82.5 | -17.5 | 17.5
175 | 1 | 79
175 | 2 | 79
175 | 3 | 78
175 | 4 | 79
175 | 5 | 77
175 | 6 | 79
175 | 7 | 82
175 | 8 | 84
175 | 9 | 85
175 | 10 | 86
175 | 11 | 87
175 | 12 | 89
175 | 13 | 90
175 | 14 | 91
175 | 15 | 88
175 | 16 | 85
175 | 17 | 86
175 | 18 | 85
175 | 19 | 84
175 | 20 | 83
175 | 21 | 83
175 | 22 | 81
175 | 23 | 80
175 | 24 | 79 | 83.2917 | -18.2917 | 18.2917
176 | 1 | 79
176 | 2 | 78
176 | 3 | 79
176 | 4 | 77
176 | 5 | 75
176 | 6 | 76
176 | 7 | 79
176 | 8 | 81
176 | 9 | 86
176 | 10 | 87
176 | 11 | 88
176 | 12 | 88
176 | 13 | 88
176 | 14 | 84
176 | 15 | 85
176 | 16 | 84
176 | 17 | 80
176 | 18 | 75
176 | 19 | 74
176 | 20 | 76
176 | 21 | 77
176 | 22 | 75
176 | 23 | 75
176 | 24 | 75 | 80.0417 | -15.0417 | 15.0417
177 | 1 | 75
177 | 2 | 75
177 | 3 | 74
177 | 4 | 74
177 | 5 | 75
177 | 6 | 78
177 | 7 | 75
177 | 8 | 77
177 | 9 | 76
177 | 10 | 77
177 | 11 | 74
177 | 12 | 75
177 | 13 | 79
177 | 14 | 79
177 | 15 | 75
177 | 16 | 75
177 | 17 | 76
177 | 18 | 78
177 | 19 | 75
177 | 20 | 75
177 | 21 | 75
177 | 22 | 75
177 | 23 | 74
177 | 24 | 75 | 75.6667 | -10.6667 | 10.6667
178 | 1 | 75
178 | 2 | 76
178 | 3 | 77
178 | 4 | 77
178 | 5 | 78
178 | 6 | 80
178 | 7 | 80
178 | 8 | 81
178 | 9 | 83
178 | 10 | 85
178 | 11 | 87
178 | 12 | 89
178 | 13 | 90
178 | 14 | 90
178 | 15 | 90
178 | 16 | 88
178 | 17 | 87
178 | 18 | 86
178 | 19 | 84
178 | 20 | 82
178 | 21 | 81
178 | 22 | 81
178 | 23 | 80
178 | 24 | 79 | 82.75 | -17.75 | 17.75
179 | 1 | 79
179 | 2 | 79
179 | 3 | 79
179 | 4 | 78
179 | 5 | 78
179 | 6 | 79
179 | 7 | 81
179 | 8 | 84
179 | 9 | 84
179 | 10 | 86
179 | 11 | 89
179 | 12 | 88
179 | 13 | 90
179 | 14 | 89
179 | 15 | 90
179 | 16 | 90
179 | 17 | 89
179 | 18 | 87
179 | 19 | 85
179 | 20 | 83
179 | 21 | 82
179 | 22 | 81
179 | 23 | 81
179 | 24 | 81 | 83.8333 | -18.8333 | 18.8333
180 | 1 | 80
180 | 2 | 80
180 | 3 | 79
180 | 4 | 78
180 | 5 | 79
180 | 6 | 80
180 | 7 | 82
180 | 8 | 84
180 | 9 | 85
180 | 10 | 87
180 | 11 | 89
180 | 12 | 91
180 | 13 | 92
180 | 14 | 90
180 | 15 | 90
180 | 16 | 89
180 | 17 | 88
180 | 18 | 86
180 | 19 | 83
180 | 20 | 82
180 | 21 | 81
180 | 22 | 80
180 | 23 | 79
180 | 24 | 78 | 83.8333 | -18.8333 | 18.8333
181 | 1 | 78
181 | 2 | 78
181 | 3 | 78
181 | 4 | 77
181 | 5 | 77
181 | 6 | 78
181 | 7 | 81
181 | 8 | 83
181 | 9 | 85
181 | 10 | 87
181 | 11 | 88
181 | 12 | 89
181 | 13 | 90
181 | 14 | 91
181 | 15 | 91
181 | 16 | 88
181 | 17 | 87
181 | 18 | 87
181 | 19 | 84
181 | 20 | 82
181 | 21 | 81
181 | 22 | 81
181 | 23 | 80
181 | 24 | 80 | 83.375 | -18.375 | 18.375
182 | 1 | 80
182 | 2 | 80
182 | 3 | 79
182 | 4 | 79
182 | 5 | 79
182 | 6 | 81
182 | 7 | 83
182 | 8 | 85
182 | 9 | 86
182 | 10 | 88
182 | 11 | 90
182 | 12 | 90
182 | 13 | 89
182 | 14 | 87
182 | 15 | 86
182 | 16 | 84
182 | 17 | 87
182 | 18 | 86
182 | 19 | 84
182 | 20 | 82
182 | 21 | 78
182 | 22 | 79
182 | 23 | 80
182 | 24 | 80 | 83.4167 | -18.4167 | 18.4167
183 | 1 | 79
183 | 2 | 79
183 | 3 | 78
183 | 4 | 78
183 | 5 | 78
183 | 6 | 78
183 | 7 | 83
183 | 8 | 85
183 | 9 | 86
183 | 10 | 85
183 | 11 | 88
183 | 12 | 89
183 | 13 | 88
183 | 14 | 87
183 | 15 | 87
183 | 16 | 82
183 | 17 | 86
183 | 18 | 87
183 | 19 | 84
183 | 20 | 83
183 | 21 | 82
183 | 22 | 82
183 | 23 | 81
183 | 24 | 80 | 83.125 | -18.125 | 18.125
184 | 1 | 79
184 | 2 | 78
184 | 3 | 78
184 | 4 | 77
184 | 5 | 76
184 | 6 | 77
184 | 7 | 83
184 | 8 | 84
184 | 9 | 75
184 | 10 | 78
184 | 11 | 83
184 | 12 | 84
184 | 13 | 81
184 | 14 | 85
184 | 15 | 79
184 | 16 | 85
184 | 17 | 85
184 | 18 | 83
184 | 19 | 83
184 | 20 | 82
184 | 21 | 81
184 | 22 | 78
184 | 23 | 77
184 | 24 | 76 | 80.2917 | -15.2917 | 15.2917
185 | 1 | 77
185 | 2 | 77
185 | 3 | 77
185 | 4 | 77
185 | 5 | 77
185 | 6 | 78
185 | 7 | 82
185 | 8 | 84
185 | 9 | 83
185 | 10 | 84
185 | 11 | 86
185 | 12 | 88
185 | 13 | 88
185 | 14 | 80
185 | 15 | 81
185 | 16 | 85
185 | 17 | 81
185 | 18 | 79
185 | 19 | 79
185 | 20 | 78
185 | 21 | 77
185 | 22 | 77
185 | 23 | 77
185 | 24 | 76 | 80.3333 | -15.3333 | 15.3333
186 | 1 | 78
186 | 2 | 80
186 | 3 | 79
186 | 4 | 79
186 | 5 | 79
186 | 6 | 79
186 | 7 | 79
186 | 8 | 79
186 | 9 | 79
186 | 10 | 80
186 | 11 | 81
186 | 12 | 83
186 | 13 | 84
186 | 14 | 84
186 | 15 | 81
186 | 16 | 81
186 | 17 | 78
186 | 18 | 78
186 | 19 | 78
186 | 20 | 78
186 | 21 | 78
186 | 22 | 77
186 | 23 | 77
186 | 24 | 76 | 79.375 | -14.375 | 14.375
187 | 1 | 78
187 | 2 | 78
187 | 3 | 78
187 | 4 | 77
187 | 5 | 77
187 | 6 | 78
187 | 7 | 80
187 | 8 | 82
187 | 9 | 84
187 | 10 | 84
187 | 11 | 86
187 | 12 | 87
187 | 13 | 84
187 | 14 | 82
187 | 15 | 84
187 | 16 | 85
187 | 17 | 86
187 | 18 | 84
187 | 19 | 82
187 | 20 | 81
187 | 21 | 80
187 | 22 | 80
187 | 23 | 78
187 | 24 | 78 | 81.375 | -16.375 | 16.375
188 | 1 | 76
188 | 2 | 76
188 | 3 | 75
188 | 4 | 74
188 | 5 | 75
188 | 6 | 75
188 | 7 | 81
188 | 8 | 83
188 | 9 | 83
188 | 10 | 84
188 | 11 | 84
188 | 12 | 87
188 | 13 | 86
188 | 14 | 89
188 | 15 | 89
188 | 16 | 88
188 | 17 | 87
188 | 18 | 82
188 | 19 | 78
188 | 20 | 80
188 | 21 | 81
188 | 22 | 80
188 | 23 | 79
188 | 24 | 80 | 81.3333 | -16.3333 | 16.3333
189 | 1 | 78
189 | 2 | 77
189 | 3 | 76
189 | 4 | 76
189 | 5 | 76
189 | 6 | 78
189 | 7 | 81
189 | 8 | 83
189 | 9 | 83
189 | 10 | 84
189 | 11 | 85
189 | 12 | 86
189 | 13 | 86
189 | 14 | 88
189 | 15 | 85
189 | 16 | 87
189 | 17 | 86
189 | 18 | 85
189 | 19 | 83
189 | 20 | 80
189 | 21 | 79
189 | 22 | 79
189 | 23 | 80
189 | 24 | 79 | 81.6667 | -16.6667 | 16.6667
190 | 1 | 78
190 | 2 | 78
190 | 3 | 75
190 | 4 | 78
190 | 5 | 76
190 | 6 | 78
190 | 7 | 82
190 | 8 | 84
190 | 9 | 86
190 | 10 | 85
190 | 11 | 84
190 | 12 | 85
190 | 13 | 87
190 | 14 | 88
190 | 15 | 88
190 | 16 | 82
190 | 17 | 81
190 | 18 | 83
190 | 19 | 80
190 | 20 | 80
190 | 21 | 80
190 | 22 | 79
190 | 23 | 79
190 | 24 | 79 | 81.4583 | -16.4583 | 16.4583
191 | 1 | 78
191 | 2 | 78
191 | 3 | 77
191 | 4 | 78
191 | 5 | 77
191 | 6 | 78
191 | 7 | 82
191 | 8 | 83
191 | 9 | 78
191 | 10 | 79
191 | 11 | 82
191 | 12 | 84
191 | 13 | 79
191 | 14 | 79
191 | 15 | 83
191 | 16 | 85
191 | 17 | 86
191 | 18 | 85
191 | 19 | 81
191 | 20 | 79
191 | 21 | 79
191 | 22 | 79
191 | 23 | 78
191 | 24 | 78 | 80.2083 | -15.2083 | 15.2083
192 | 1 | 77
192 | 2 | 77
192 | 3 | 77
192 | 4 | 77
192 | 5 | 77
192 | 6 | 79
192 | 7 | 81
192 | 8 | 84
192 | 9 | 82
192 | 10 | 84
192 | 11 | 87
192 | 12 | 89
192 | 13 | 90
192 | 14 | 89
192 | 15 | 87
192 | 16 | 89
192 | 17 | 89
192 | 18 | 86
192 | 19 | 85
192 | 20 | 84
192 | 21 | 82
192 | 22 | 81
192 | 23 | 83
192 | 24 | 83 | 83.2917 | -18.2917 | 18.2917
193 | 1 | 82
193 | 2 | 82
193 | 3 | 80
193 | 4 | 80
193 | 5 | 80
193 | 6 | 79
193 | 7 | 80
193 | 8 | 82
193 | 9 | 83
193 | 10 | 86
193 | 11 | 87
193 | 12 | 87
193 | 13 | 82
193 | 14 | 73
193 | 15 | 75
193 | 16 | 76
193 | 17 | 77
193 | 18 | 77
193 | 19 | 76
193 | 20 | 76
193 | 21 | 76
193 | 22 | 75
193 | 23 | 75
193 | 24 | 74 | 79.1667 | -14.1667 | 14.1667
194 | 1 | 74
194 | 2 | 74
194 | 3 | 74
194 | 4 | 74
194 | 5 | 74
194 | 6 | 74
194 | 7 | 74
194 | 8 | 77
194 | 9 | 79
194 | 10 | 80
194 | 11 | 81
194 | 12 | 83
194 | 13 | 82
194 | 14 | 85
194 | 15 | 85
194 | 16 | 85
194 | 17 | 83
194 | 18 | 81
194 | 19 | 79
194 | 20 | 78
194 | 21 | 76
194 | 22 | 76
194 | 23 | 75
194 | 24 | 76 | 78.2917 | -13.2917 | 13.2917
195 | 1 | 73
195 | 2 | 73
195 | 3 | 74
195 | 4 | 73
195 | 5 | 74
195 | 6 | 74
195 | 7 | 78
195 | 8 | 82
195 | 9 | 83
195 | 10 | 85
195 | 11 | 85
195 | 12 | 86
195 | 13 | 85
195 | 14 | 87
195 | 15 | 80
195 | 16 | 86
195 | 17 | 87
195 | 18 | 86
195 | 19 | 83
195 | 20 | 80
195 | 21 | 79
195 | 22 | 78
195 | 23 | 77
195 | 24 | 77 | 80.2083 | -15.2083 | 15.2083
196 | 1 | 75
196 | 2 | 76
196 | 3 | 75
196 | 4 | 75
196 | 5 | 74
196 | 6 | 75
196 | 7 | 81
196 | 8 | 83
196 | 9 | 84
196 | 10 | 83
196 | 11 | 85
196 | 12 | 88
196 | 13 | 87
196 | 14 | 89
196 | 15 | 88
196 | 16 | 86
196 | 17 | 87
196 | 18 | 85
196 | 19 | 83
196 | 20 | 81
196 | 21 | 81
196 | 22 | 80
196 | 23 | 78
196 | 24 | 79 | 81.5833 | -16.5833 | 16.5833
197 | 1 | 78
197 | 2 | 77
197 | 3 | 75
197 | 4 | 75
197 | 5 | 73
197 | 6 | 78
197 | 7 | 82
197 | 8 | 82
197 | 9 | 84
197 | 10 | 86
197 | 11 | 87
197 | 12 | 89
197 | 13 | 75
197 | 14 | 78
197 | 15 | 80
197 | 16 | 83
197 | 17 | 81
197 | 18 | 81
197 | 19 | 81
197 | 20 | 81
197 | 21 | 80
197 | 22 | 80
197 | 23 | 77
197 | 24 | 77 | 80 | -15 | 15
198 | 1 | 78
198 | 2 | 77
198 | 3 | 77
198 | 4 | 76
198 | 5 | 77
198 | 6 | 76
198 | 7 | 82
198 | 8 | 84
198 | 9 | 85
198 | 10 | 86
198 | 11 | 83
198 | 12 | 78
198 | 13 | 79
198 | 14 | 80
198 | 15 | 82
198 | 16 | 84
198 | 17 | 81
198 | 18 | 81
198 | 19 | 80
198 | 20 | 78
198 | 21 | 78
198 | 22 | 78
198 | 23 | 76
198 | 24 | 77 | 79.7083 | -14.7083 | 14.7083
199 | 1 | 75
199 | 2 | 75
199 | 3 | 77
199 | 4 | 74
199 | 5 | 75
199 | 6 | 78
199 | 7 | 81
199 | 8 | 83
199 | 9 | 84
199 | 10 | 82
199 | 11 | 78
199 | 12 | 84
199 | 13 | 84
199 | 14 | 85
199 | 15 | 83
199 | 16 | 84
199 | 17 | 84
199 | 18 | 83
199 | 19 | 81
199 | 20 | 81
199 | 21 | 80
199 | 22 | 79
199 | 23 | 77
199 | 24 | 76 | 80.125 | -15.125 | 15.125
200 | 1 | 75
200 | 2 | 75
200 | 3 | 76
200 | 4 | 76
200 | 5 | 77
200 | 6 | 78
200 | 7 | 81
200 | 8 | 83
200 | 9 | 82
200 | 10 | 80
200 | 11 | 85
200 | 12 | 81
200 | 13 | 76
200 | 14 | 78
200 | 15 | 85
200 | 16 | 83
200 | 17 | 83
200 | 18 | 82
200 | 19 | 81
200 | 20 | 80
200 | 21 | 80
200 | 22 | 78
200 | 23 | 78
200 | 24 | 78 | 79.625 | -14.625 | 14.625
201 | 1 | 77
201 | 2 | 77
201 | 3 | 76
201 | 4 | 76
201 | 5 | 76
201 | 6 | 76
201 | 7 | 78
201 | 8 | 80
201 | 9 | 80
201 | 10 | 80
201 | 11 | 80
201 | 12 | 83
201 | 13 | 84
201 | 14 | 84
201 | 15 | 77
201 | 16 | 82
201 | 17 | 80
201 | 18 | 79
201 | 19 | 78
201 | 20 | 77
201 | 21 | 76
201 | 22 | 76
201 | 23 | 77
201 | 24 | 75 | 78.5 | -13.5 | 13.5
202 | 1 | 74
202 | 2 | 73
202 | 3 | 74
202 | 4 | 74
202 | 5 | 73
202 | 6 | 76
202 | 7 | 81
202 | 8 | 84
202 | 9 | 84
202 | 10 | 85
202 | 11 | 87
202 | 12 | 88
202 | 13 | 89
202 | 14 | 89
202 | 15 | 90
202 | 16 | 86
202 | 17 | 86
202 | 18 | 85
202 | 19 | 83
202 | 20 | 82
202 | 21 | 81
202 | 22 | 80
202 | 23 | 79
202 | 24 | 78 | 81.7083 | -16.7083 | 16.7083
203 | 1 | 77
203 | 2 | 77
203 | 3 | 78
203 | 4 | 76
203 | 5 | 76
203 | 6 | 77
203 | 7 | 81
203 | 8 | 83
203 | 9 | 85
203 | 10 | 86
203 | 11 | 87
203 | 12 | 88
203 | 13 | 90
203 | 14 | 90
203 | 15 | 91
203 | 16 | 92
203 | 17 | 91
203 | 18 | 90
203 | 19 | 87
203 | 20 | 85
203 | 21 | 85
203 | 22 | 83
203 | 23 | 81
203 | 24 | 80 | 84 | -19 | 19
204 | 1 | 78
204 | 2 | 78
204 | 3 | 77
204 | 4 | 76
204 | 5 | 76
204 | 6 | 79
204 | 7 | 82
204 | 8 | 85
204 | 9 | 87
204 | 10 | 90
204 | 11 | 91
204 | 12 | 91
204 | 13 | 93
204 | 14 | 93
204 | 15 | 92
204 | 16 | 93
204 | 17 | 92
204 | 18 | 90
204 | 19 | 87
204 | 20 | 87
204 | 21 | 86
204 | 22 | 85
204 | 23 | 84
204 | 24 | 83 | 85.625 | -20.625 | 20.625
205 | 1 | 83
205 | 2 | 82
205 | 3 | 81
205 | 4 | 80
205 | 5 | 80
205 | 6 | 80
205 | 7 | 85
205 | 8 | 87
205 | 9 | 88
205 | 10 | 87
205 | 11 | 89
205 | 12 | 91
205 | 13 | 79
205 | 14 | 77
205 | 15 | 78
205 | 16 | 77
205 | 17 | 80
205 | 18 | 78
205 | 19 | 78
205 | 20 | 77
205 | 21 | 76
205 | 22 | 77
205 | 23 | 77
205 | 24 | 76 | 80.9583 | -15.9583 | 15.9583
206 | 1 | 77
206 | 2 | 77
206 | 3 | 75
206 | 4 | 76
206 | 5 | 78
206 | 6 | 78
206 | 7 | 79
206 | 8 | 83
206 | 9 | 85
206 | 10 | 87
206 | 11 | 88
206 | 12 | 89
206 | 13 | 89
206 | 14 | 91
206 | 15 | 91
206 | 16 | 90
206 | 17 | 89
206 | 18 | 88
206 | 19 | 85
206 | 20 | 84
206 | 21 | 83
206 | 22 | 82
206 | 23 | 82
206 | 24 | 81 | 83.625 | -18.625 | 18.625
207 | 1 | 80
207 | 2 | 79
207 | 3 | 79
207 | 4 | 78
207 | 5 | 77
207 | 6 | 78
207 | 7 | 80
207 | 8 | 82
207 | 9 | 84
207 | 10 | 85
207 | 11 | 88
207 | 12 | 89
207 | 13 | 89
207 | 14 | 90
207 | 15 | 89
207 | 16 | 89
207 | 17 | 79
207 | 18 | 82
207 | 19 | 84
207 | 20 | 83
207 | 21 | 79
207 | 22 | 76
207 | 23 | 76
207 | 24 | 75 | 82.0833 | -17.0833 | 17.0833
208 | 1 | 75
208 | 2 | 75
208 | 3 | 76
208 | 4 | 75
208 | 5 | 76
208 | 6 | 77
208 | 7 | 80
208 | 8 | 83
208 | 9 | 85
208 | 10 | 88
208 | 11 | 90
208 | 12 | 91
208 | 13 | 92
208 | 14 | 91
208 | 15 | 87
208 | 16 | 86
208 | 17 | 78
208 | 18 | 79
208 | 19 | 77
208 | 20 | 76
208 | 21 | 75
208 | 22 | 75
208 | 23 | 74
208 | 24 | 76 | 80.7083 | -15.7083 | 15.7083
209 | 1 | 74
209 | 2 | 74
209 | 3 | 74
209 | 4 | 74
209 | 5 | 74
209 | 6 | 75
209 | 7 | 79
209 | 8 | 82
209 | 9 | 85
209 | 10 | 88
209 | 11 | 90
209 | 12 | 90
209 | 13 | 93
209 | 14 | 93
209 | 15 | 94
209 | 16 | 94
209 | 17 | 89
209 | 18 | 85
209 | 19 | 84
209 | 20 | 82
209 | 21 | 81
209 | 22 | 80
209 | 23 | 79
209 | 24 | 78 | 82.9583 | -17.9583 | 17.9583
210 | 1 | 77
210 | 2 | 77
210 | 3 | 77
210 | 4 | 77
210 | 5 | 77
210 | 6 | 78
210 | 7 | 81
210 | 8 | 84
210 | 9 | 87
210 | 10 | 89
210 | 11 | 91
210 | 12 | 92
210 | 13 | 91
210 | 14 | 93
210 | 15 | 93
210 | 16 | 92
210 | 17 | 91
210 | 18 | 90
210 | 19 | 87
210 | 20 | 86
210 | 21 | 85
210 | 22 | 83
210 | 23 | 82
210 | 24 | 82 | 85.0833 | -20.0833 | 20.0833
211 | 1 | 82
211 | 2 | 81
211 | 3 | 81
211 | 4 | 80
211 | 5 | 80
211 | 6 | 80
211 | 7 | 81
211 | 8 | 83
211 | 9 | 84
211 | 10 | 87
211 | 11 | 88
211 | 12 | 88
211 | 13 | 89
211 | 14 | 89
211 | 15 | 90
211 | 16 | 90
211 | 17 | 91
211 | 18 | 88
211 | 19 | 86
211 | 20 | 85
211 | 21 | 84
211 | 22 | 82
211 | 23 | 83
211 | 24 | 81 | 84.7083 | -19.7083 | 19.7083
212 | 1 | 80
212 | 2 | 80
212 | 3 | 80
212 | 4 | 79
212 | 5 | 79
212 | 6 | 79
212 | 7 | 82
212 | 8 | 85
212 | 9 | 87
212 | 10 | 89
212 | 11 | 91
212 | 12 | 91
212 | 13 | 91
212 | 14 | 93
212 | 15 | 91
212 | 16 | 89
212 | 17 | 89
212 | 18 | 90
212 | 19 | 87
212 | 20 | 85
212 | 21 | 85
212 | 22 | 84
212 | 23 | 83
212 | 24 | 82 | 85.4583 | -20.4583 | 20.4583
213 | 1 | 80
213 | 2 | 79
213 | 3 | 78
213 | 4 | 77
213 | 5 | 77
213 | 6 | 77
213 | 7 | 79
213 | 8 | 82
213 | 9 | 84
213 | 10 | 87
213 | 11 | 90
213 | 12 | 93
213 | 13 | 94
213 | 14 | 94
213 | 15 | 95
213 | 16 | 93
213 | 17 | 91
213 | 18 | 89
213 | 19 | 87
213 | 20 | 85
213 | 21 | 83
213 | 22 | 82
213 | 23 | 82
213 | 24 | 81 | 84.9583 | -19.9583 | 19.9583
214 | 1 | 80
214 | 2 | 79
214 | 3 | 78
214 | 4 | 78
214 | 5 | 77
214 | 6 | 77
214 | 7 | 80
214 | 8 | 83
214 | 9 | 86
214 | 10 | 89
214 | 11 | 91
214 | 12 | 94
214 | 13 | 95
214 | 14 | 95
214 | 15 | 96
214 | 16 | 94
214 | 17 | 92
214 | 18 | 90
214 | 19 | 88
214 | 20 | 86
214 | 21 | 84
214 | 22 | 83
214 | 23 | 82
214 | 24 | 81 | 85.75 | -20.75 | 20.75
215 | 1 | 80
215 | 2 | 80
215 | 3 | 79
215 | 4 | 78
215 | 5 | 78
215 | 6 | 77
215 | 7 | 80
215 | 8 | 84
215 | 9 | 87
215 | 10 | 89
215 | 11 | 91
215 | 12 | 93
215 | 13 | 94
215 | 14 | 96
215 | 15 | 97
215 | 16 | 96
215 | 17 | 96
215 | 18 | 95
215 | 19 | 92
215 | 20 | 89
215 | 21 | 86
215 | 22 | 85
215 | 23 | 83
215 | 24 | 82 | 86.9583 | -21.9583 | 21.9583
216 | 1 | 82
216 | 2 | 82
216 | 3 | 82
216 | 4 | 82
216 | 5 | 81
216 | 6 | 81
216 | 7 | 83
216 | 8 | 86
216 | 9 | 88
216 | 10 | 90
216 | 11 | 92
216 | 12 | 94
216 | 13 | 95
216 | 14 | 95
216 | 15 | 96
216 | 16 | 94
216 | 17 | 93
216 | 18 | 91
216 | 19 | 89
216 | 20 | 87
216 | 21 | 85
216 | 22 | 84
216 | 23 | 82
216 | 24 | 81 | 87.2917 | -22.2917 | 22.2917
217 | 1 | 80
217 | 2 | 80
217 | 3 | 79
217 | 4 | 79
217 | 5 | 79
217 | 6 | 79
217 | 7 | 82
217 | 8 | 85
217 | 9 | 88
217 | 10 | 89
217 | 11 | 90
217 | 12 | 91
217 | 13 | 91
217 | 14 | 92
217 | 15 | 92
217 | 16 | 92
217 | 17 | 91
217 | 18 | 91
217 | 19 | 89
217 | 20 | 86
217 | 21 | 84
217 | 22 | 83
217 | 23 | 83
217 | 24 | 82 | 85.7083 | -20.7083 | 20.7083
218 | 1 | 81
218 | 2 | 81
218 | 3 | 80
218 | 4 | 79
218 | 5 | 79
218 | 6 | 78
218 | 7 | 81
218 | 8 | 84
218 | 9 | 87
218 | 10 | 88
218 | 11 | 90
218 | 12 | 91
218 | 13 | 89
218 | 14 | 87
218 | 15 | 85
218 | 16 | 84
218 | 17 | 83
218 | 18 | 82
218 | 19 | 81
218 | 20 | 81
218 | 21 | 80
218 | 22 | 80
218 | 23 | 79
218 | 24 | 79 | 82.875 | -17.875 | 17.875
219 | 1 | 79
219 | 2 | 79
219 | 3 | 79
219 | 4 | 79
219 | 5 | 79
219 | 6 | 79
219 | 7 | 81
219 | 8 | 83
219 | 9 | 85
219 | 10 | 87
219 | 11 | 88
219 | 12 | 90
219 | 13 | 87
219 | 14 | 84
219 | 15 | 81
219 | 16 | 79
219 | 17 | 78
219 | 18 | 76
219 | 19 | 76
219 | 20 | 76
219 | 21 | 76
219 | 22 | 77
219 | 23 | 77
219 | 24 | 78 | 80.5417 | -15.5417 | 15.5417
220 | 1 | 78
220 | 2 | 78
220 | 3 | 78
220 | 4 | 78
220 | 5 | 77
220 | 6 | 77
220 | 7 | 76
220 | 8 | 76
220 | 9 | 75
220 | 10 | 76
220 | 11 | 76
220 | 12 | 77
220 | 13 | 78
220 | 14 | 78
220 | 15 | 79
220 | 16 | 79
220 | 17 | 78
220 | 18 | 78
220 | 19 | 78
220 | 20 | 78
220 | 21 | 78
220 | 22 | 77
220 | 23 | 77
220 | 24 | 76 | 77.3333 | -12.3333 | 12.3333
221 | 1 | 76
221 | 2 | 75
221 | 3 | 75
221 | 4 | 75
221 | 5 | 75
221 | 6 | 75
221 | 7 | 76
221 | 8 | 76
221 | 9 | 77
221 | 10 | 79
221 | 11 | 80
221 | 12 | 82
221 | 13 | 83
221 | 14 | 84
221 | 15 | 85
221 | 16 | 84
221 | 17 | 84
221 | 18 | 83
221 | 19 | 81
221 | 20 | 80
221 | 21 | 78
221 | 22 | 78
221 | 23 | 77
221 | 24 | 77 | 78.9583 | -13.9583 | 13.9583
222 | 1 | 77
222 | 2 | 78
222 | 3 | 78
222 | 4 | 78
222 | 5 | 77
222 | 6 | 77
222 | 7 | 79
222 | 8 | 82
222 | 9 | 84
222 | 10 | 85
222 | 11 | 86
222 | 12 | 87
222 | 13 | 88
222 | 14 | 89
222 | 15 | 90
222 | 16 | 88
222 | 17 | 87
222 | 18 | 85
222 | 19 | 83
222 | 20 | 82
222 | 21 | 80
222 | 22 | 80
222 | 23 | 79
222 | 24 | 79 | 82.4167 | -17.4167 | 17.4167
223 | 1 | 79
223 | 2 | 78
223 | 3 | 78
223 | 4 | 78
223 | 5 | 77
223 | 6 | 77
223 | 7 | 80
223 | 8 | 84
223 | 9 | 87
223 | 10 | 88
223 | 11 | 90
223 | 12 | 91
223 | 13 | 90
223 | 14 | 88
223 | 15 | 87
223 | 16 | 87
223 | 17 | 87
223 | 18 | 87
223 | 19 | 85
223 | 20 | 82
223 | 21 | 80
223 | 22 | 79
223 | 23 | 78
223 | 24 | 77 | 83.0833 | -18.0833 | 18.0833
224 | 1 | 77
224 | 2 | 78
224 | 3 | 78
224 | 4 | 78
224 | 5 | 79
224 | 6 | 79
224 | 7 | 81
224 | 8 | 82
224 | 9 | 84
224 | 10 | 84
224 | 11 | 84
224 | 12 | 84
224 | 13 | 86
224 | 14 | 87
224 | 15 | 89
224 | 16 | 88
224 | 17 | 86
224 | 18 | 85
224 | 19 | 84
224 | 20 | 82
224 | 21 | 81
224 | 22 | 80
224 | 23 | 80
224 | 24 | 79 | 82.2917 | -17.2917 | 17.2917
225 | 1 | 79
225 | 2 | 78
225 | 3 | 78
225 | 4 | 78
225 | 5 | 79
225 | 6 | 79
225 | 7 | 81
225 | 8 | 84
225 | 9 | 86
225 | 10 | 88
225 | 11 | 89
225 | 12 | 91
225 | 13 | 87
225 | 14 | 83
225 | 15 | 79
225 | 16 | 79
225 | 17 | 79
225 | 18 | 79
225 | 19 | 79
225 | 20 | 78
225 | 21 | 78
225 | 22 | 76
225 | 23 | 75
225 | 24 | 73 | 80.625 | -15.625 | 15.625
226 | 1 | 73
226 | 2 | 73
226 | 3 | 73
226 | 4 | 73
226 | 5 | 72
226 | 6 | 72
226 | 7 | 77
226 | 8 | 81
226 | 9 | 86
226 | 10 | 83
226 | 11 | 79
226 | 12 | 76
226 | 13 | 79
226 | 14 | 82
226 | 15 | 85
226 | 16 | 84
226 | 17 | 82
226 | 18 | 81
226 | 19 | 80
226 | 20 | 78
226 | 21 | 77
226 | 22 | 76
226 | 23 | 74
226 | 24 | 73 | 77.875 | -12.875 | 12.875
227 | 1 | 72
227 | 2 | 72
227 | 3 | 71
227 | 4 | 71
227 | 5 | 71
227 | 6 | 71
227 | 7 | 75
227 | 8 | 80
227 | 9 | 84
227 | 10 | 86
227 | 11 | 88
227 | 12 | 90
227 | 13 | 90
227 | 14 | 91
227 | 15 | 91
227 | 16 | 90
227 | 17 | 89
227 | 18 | 88
227 | 19 | 86
227 | 20 | 85
227 | 21 | 83
227 | 22 | 82
227 | 23 | 82
227 | 24 | 81 | 82.0417 | -17.0417 | 17.0417
228 | 1 | 80
228 | 2 | 80
228 | 3 | 79
228 | 4 | 78
228 | 5 | 77
228 | 6 | 76
228 | 7 | 79
228 | 8 | 83
228 | 9 | 86
228 | 10 | 88
228 | 11 | 89
228 | 12 | 91
228 | 13 | 91
228 | 14 | 92
228 | 15 | 92
228 | 16 | 89
228 | 17 | 85
228 | 18 | 82
228 | 19 | 81
228 | 20 | 81
228 | 21 | 80
228 | 22 | 80
228 | 23 | 80
228 | 24 | 80 | 83.2917 | -18.2917 | 18.2917
229 | 1 | 79
229 | 2 | 78
229 | 3 | 77
229 | 4 | 77
229 | 5 | 76
229 | 6 | 76
229 | 7 | 80
229 | 8 | 83
229 | 9 | 87
229 | 10 | 88
229 | 11 | 90
229 | 12 | 91
229 | 13 | 91
229 | 14 | 91
229 | 15 | 91
229 | 16 | 87
229 | 17 | 84
229 | 18 | 80
229 | 19 | 79
229 | 20 | 78
229 | 21 | 77
229 | 22 | 77
229 | 23 | 78
229 | 24 | 78 | 82.2083 | -17.2083 | 17.2083
230 | 1 | 77
230 | 2 | 76
230 | 3 | 75
230 | 4 | 75
230 | 5 | 76
230 | 6 | 76
230 | 7 | 80
230 | 8 | 83
230 | 9 | 87
230 | 10 | 88
230 | 11 | 90
230 | 12 | 91
230 | 13 | 91
230 | 14 | 92
230 | 15 | 92
230 | 16 | 91
230 | 17 | 89
230 | 18 | 88
230 | 19 | 86
230 | 20 | 85
230 | 21 | 83
230 | 22 | 83
230 | 23 | 82
230 | 24 | 82 | 84.0833 | -19.0833 | 19.0833
231 | 1 | 80
231 | 2 | 78
231 | 3 | 76
231 | 4 | 76
231 | 5 | 77
231 | 6 | 77
231 | 7 | 80
231 | 8 | 84
231 | 9 | 87
231 | 10 | 88
231 | 11 | 90
231 | 12 | 91
231 | 13 | 92
231 | 14 | 92
231 | 15 | 93
231 | 16 | 91
231 | 17 | 88
231 | 18 | 86
231 | 19 | 84
231 | 20 | 81
231 | 21 | 79
231 | 22 | 80
231 | 23 | 80
231 | 24 | 81 | 83.7917 | -18.7917 | 18.7917
232 | 1 | 79
232 | 2 | 78
232 | 3 | 76
232 | 4 | 76
232 | 5 | 77
232 | 6 | 77
232 | 7 | 79
232 | 8 | 82
232 | 9 | 84
232 | 10 | 86
232 | 11 | 89
232 | 12 | 91
232 | 13 | 92
232 | 14 | 93
232 | 15 | 94
232 | 16 | 89
232 | 17 | 83
232 | 18 | 78
232 | 19 | 78
232 | 20 | 77
232 | 21 | 77
232 | 22 | 76
232 | 23 | 76
232 | 24 | 75 | 81.75 | -16.75 | 16.75
233 | 1 | 75
233 | 2 | 75
233 | 3 | 75
233 | 4 | 75
233 | 5 | 74
233 | 6 | 74
233 | 7 | 77
233 | 8 | 81
233 | 9 | 84
233 | 10 | 86
233 | 11 | 87
233 | 12 | 89
233 | 13 | 90
233 | 14 | 92
233 | 15 | 93
233 | 16 | 92
233 | 17 | 90
233 | 18 | 89
233 | 19 | 87
233 | 20 | 84
233 | 21 | 82
233 | 22 | 81
233 | 23 | 80
233 | 24 | 79 | 82.9583 | -17.9583 | 17.9583
234 | 1 | 79
234 | 2 | 78
234 | 3 | 78
234 | 4 | 78
234 | 5 | 79
234 | 6 | 79
234 | 7 | 82
234 | 8 | 85
234 | 9 | 88
234 | 10 | 88
234 | 11 | 89
234 | 12 | 89
234 | 13 | 90
234 | 14 | 91
234 | 15 | 92
234 | 16 | 87
234 | 17 | 81
234 | 18 | 76
234 | 19 | 77
234 | 20 | 77
234 | 21 | 78
234 | 22 | 77
234 | 23 | 77
234 | 24 | 76 | 82.125 | -17.125 | 17.125
235 | 1 | 75
235 | 2 | 75
235 | 3 | 74
235 | 4 | 74
235 | 5 | 74
235 | 6 | 74
235 | 7 | 78
235 | 8 | 81
235 | 9 | 85
235 | 10 | 86
235 | 11 | 87
235 | 12 | 88
235 | 13 | 89
235 | 14 | 90
235 | 15 | 91
235 | 16 | 90
235 | 17 | 90
235 | 18 | 89
235 | 19 | 87
235 | 20 | 84
235 | 21 | 82
235 | 22 | 81
235 | 23 | 79
235 | 24 | 78 | 82.5417 | -17.5417 | 17.5417
236 | 1 | 78
236 | 2 | 77
236 | 3 | 77
236 | 4 | 78
236 | 5 | 78
236 | 6 | 79
236 | 7 | 81
236 | 8 | 83
236 | 9 | 85
236 | 10 | 86
236 | 11 | 88
236 | 12 | 89
236 | 13 | 90
236 | 14 | 91
236 | 15 | 92
236 | 16 | 90
236 | 17 | 89
236 | 18 | 87
236 | 19 | 84
236 | 20 | 80
236 | 21 | 77
236 | 22 | 77
236 | 23 | 77
236 | 24 | 77 | 82.9167 | -17.9167 | 17.9167
237 | 1 | 76
237 | 2 | 76
237 | 3 | 75
237 | 4 | 74
237 | 5 | 74
237 | 6 | 73
237 | 7 | 78
237 | 8 | 83
237 | 9 | 88
237 | 10 | 89
237 | 11 | 90
237 | 12 | 91
237 | 13 | 91
237 | 14 | 92
237 | 15 | 92
237 | 16 | 91
237 | 17 | 89
237 | 18 | 88
237 | 19 | 86
237 | 20 | 83
237 | 21 | 81
237 | 22 | 78
237 | 23 | 76
237 | 24 | 73 | 82.7917 | -17.7917 | 17.7917
238 | 1 | 73
238 | 2 | 72
238 | 3 | 72
238 | 4 | 72
238 | 5 | 72
238 | 6 | 72
238 | 7 | 77
238 | 8 | 82
238 | 9 | 87
238 | 10 | 88
238 | 11 | 88
238 | 12 | 89
238 | 13 | 90
238 | 14 | 90
238 | 15 | 91
238 | 16 | 90
238 | 17 | 88
238 | 18 | 87
238 | 19 | 85
238 | 20 | 83
238 | 21 | 81
238 | 22 | 81
238 | 23 | 80
238 | 24 | 80 | 82.0833 | -17.0833 | 17.0833
239 | 1 | 80
239 | 2 | 80
239 | 3 | 80
239 | 4 | 79
239 | 5 | 79
239 | 6 | 78
239 | 7 | 81
239 | 8 | 84
239 | 9 | 87
239 | 10 | 88
239 | 11 | 88
239 | 12 | 89
239 | 13 | 87
239 | 14 | 84
239 | 15 | 82
239 | 16 | 81
239 | 17 | 81
239 | 18 | 80
239 | 19 | 80
239 | 20 | 79
239 | 21 | 79
239 | 22 | 79
239 | 23 | 78
239 | 24 | 78 | 81.7083 | -16.7083 | 16.7083
240 | 1 | 79
240 | 2 | 79
240 | 3 | 80
240 | 4 | 80
240 | 5 | 80
240 | 6 | 80
240 | 7 | 81
240 | 8 | 83
240 | 9 | 84
240 | 10 | 85
240 | 11 | 85
240 | 12 | 86
240 | 13 | 83
240 | 14 | 79
240 | 15 | 76
240 | 16 | 76
240 | 17 | 77
240 | 18 | 77
240 | 19 | 77
240 | 20 | 77
240 | 21 | 77
240 | 22 | 78
240 | 23 | 79
240 | 24 | 80 | 79.9167 | -14.9167 | 14.9167
241 | 1 | 80
241 | 2 | 81
241 | 3 | 81
241 | 4 | 81
241 | 5 | 82
241 | 6 | 82
241 | 7 | 83
241 | 8 | 83
241 | 9 | 84
241 | 10 | 81
241 | 11 | 78
241 | 12 | 75
241 | 13 | 76
241 | 14 | 76
241 | 15 | 77
241 | 16 | 78
241 | 17 | 79
241 | 18 | 80
241 | 19 | 80
241 | 20 | 79
241 | 21 | 79
241 | 22 | 79
241 | 23 | 78
241 | 24 | 78 | 79.5833 | -14.5833 | 14.5833
242 | 1 | 78
242 | 2 | 78
242 | 3 | 78
242 | 4 | 77
242 | 5 | 76
242 | 6 | 75
242 | 7 | 78
242 | 8 | 81
242 | 9 | 84
242 | 10 | 85
242 | 11 | 87
242 | 12 | 88
242 | 13 | 87
242 | 14 | 87
242 | 15 | 86
242 | 16 | 84
242 | 17 | 81
242 | 18 | 79
242 | 19 | 79
242 | 20 | 78
242 | 21 | 78
242 | 22 | 77
242 | 23 | 77
242 | 24 | 76 | 80.5833 | -15.5833 | 15.5833
243 | 1 | 76
243 | 2 | 77
243 | 3 | 77
243 | 4 | 77
243 | 5 | 76
243 | 6 | 76
243 | 7 | 78
243 | 8 | 80
243 | 9 | 82
243 | 10 | 83
243 | 11 | 85
243 | 12 | 86
243 | 13 | 87
243 | 14 | 87
243 | 15 | 88
243 | 16 | 87
243 | 17 | 86
243 | 18 | 85
243 | 19 | 83
243 | 20 | 80
243 | 21 | 78
243 | 22 | 78
243 | 23 | 78
243 | 24 | 78 | 81.1667 | -16.1667 | 16.1667
244 | 1 | 79
244 | 2 | 79
244 | 3 | 79
244 | 4 | 79
244 | 5 | 80
244 | 6 | 79
244 | 7 | 82
244 | 8 | 85
244 | 9 | 87
244 | 10 | 89
244 | 11 | 89
244 | 12 | 86
244 | 13 | 86
244 | 14 | 88
244 | 15 | 87
244 | 16 | 87
244 | 17 | 77
244 | 18 | 78
244 | 19 | 78
244 | 20 | 78
244 | 21 | 79
244 | 22 | 79
244 | 23 | 79
244 | 24 | 79 | 82 | -17 | 17
245 | 1 | 79
245 | 2 | 79
245 | 3 | 78
245 | 4 | 77
245 | 5 | 77
245 | 6 | 76
245 | 7 | 75
245 | 8 | 76
245 | 9 | 75
245 | 10 | 76
245 | 11 | 75
245 | 12 | 75
245 | 13 | 76
245 | 14 | 75
245 | 15 | 76
245 | 16 | 77
245 | 17 | 77
245 | 18 | 77
245 | 19 | 76
245 | 20 | 75
245 | 21 | 75
245 | 22 | 75
245 | 23 | 75
245 | 24 | 75 | 76.125 | -11.125 | 11.125
246 | 1 | 76
246 | 2 | 76
246 | 3 | 75
246 | 4 | 75
246 | 5 | 75
246 | 6 | 75
246 | 7 | 76
246 | 8 | 79
246 | 9 | 82
246 | 10 | 84
246 | 11 | 86
246 | 12 | 86
246 | 13 | 87
246 | 14 | 86
246 | 15 | 73
246 | 16 | 76
246 | 17 | 78
246 | 18 | 78
246 | 19 | 77
246 | 20 | 77
246 | 21 | 76
246 | 22 | 76
246 | 23 | 76
246 | 24 | 76 | 78.375 | -13.375 | 13.375
247 | 1 | 75
247 | 2 | 74
247 | 3 | 74
247 | 4 | 74
247 | 5 | 74
247 | 6 | 74
247 | 7 | 78
247 | 8 | 83
247 | 9 | 85
247 | 10 | 87
247 | 11 | 87
247 | 12 | 90
247 | 13 | 89
247 | 14 | 89
247 | 15 | 88
247 | 16 | 88
247 | 17 | 86
247 | 18 | 84
247 | 19 | 83
247 | 20 | 82
247 | 21 | 80
247 | 22 | 80
247 | 23 | 78
247 | 24 | 78 | 81.6667 | -16.6667 | 16.6667
248 | 1 | 78
248 | 2 | 77
248 | 3 | 76
248 | 4 | 76
248 | 5 | 77
248 | 6 | 76
248 | 7 | 79
248 | 8 | 82
248 | 9 | 85
248 | 10 | 87
248 | 11 | 88
248 | 12 | 90
248 | 13 | 90
248 | 14 | 89
248 | 15 | 87
248 | 16 | 87
248 | 17 | 87
248 | 18 | 85
248 | 19 | 83
248 | 20 | 82
248 | 21 | 81
248 | 22 | 80
248 | 23 | 80
248 | 24 | 79 | 82.5417 | -17.5417 | 17.5417
249 | 1 | 79
249 | 2 | 78
249 | 3 | 78
249 | 4 | 77
249 | 5 | 77
249 | 6 | 77
249 | 7 | 80
249 | 8 | 83
249 | 9 | 86
249 | 10 | 88
249 | 11 | 89
249 | 12 | 89
249 | 13 | 91
249 | 14 | 90
249 | 15 | 92
249 | 16 | 92
249 | 17 | 81
249 | 18 | 78
249 | 19 | 77
249 | 20 | 77
249 | 21 | 76
249 | 22 | 77
249 | 23 | 77
249 | 24 | 77 | 81.9167 | -16.9167 | 16.9167
250 | 1 | 76
250 | 2 | 74
250 | 3 | 74
250 | 4 | 74
250 | 5 | 74
250 | 6 | 74
250 | 7 | 77
250 | 8 | 80
250 | 9 | 83
250 | 10 | 85
250 | 11 | 88
250 | 12 | 89
250 | 13 | 88
250 | 14 | 82
250 | 15 | 78
250 | 16 | 79
250 | 17 | 75
250 | 18 | 76
250 | 19 | 76
250 | 20 | 75
250 | 21 | 76
250 | 22 | 74
250 | 23 | 75
250 | 24 | 75 | 78.2083 | -13.2083 | 13.2083
251 | 1 | 75
251 | 2 | 75
251 | 3 | 74
251 | 4 | 74
251 | 5 | 73
251 | 6 | 74
251 | 7 | 78
251 | 8 | 80
251 | 9 | 83
251 | 10 | 84
251 | 11 | 86
251 | 12 | 87
251 | 13 | 89
251 | 14 | 84
251 | 15 | 81
251 | 16 | 73
251 | 17 | 74
251 | 18 | 75
251 | 19 | 75
251 | 20 | 74
251 | 21 | 75
251 | 22 | 75
251 | 23 | 74
251 | 24 | 74 | 77.75 | -12.75 | 12.75
252 | 1 | 73
252 | 2 | 73
252 | 3 | 75
252 | 4 | 75
252 | 5 | 74
252 | 6 | 73
252 | 7 | 75
252 | 8 | 77
252 | 9 | 79
252 | 10 | 80
252 | 11 | 80
252 | 12 | 83
252 | 13 | 84
252 | 14 | 86
252 | 15 | 86
252 | 16 | 86
252 | 17 | 85
252 | 18 | 84
252 | 19 | 83
252 | 20 | 82
252 | 21 | 81
252 | 22 | 82
252 | 23 | 81
252 | 24 | 80 | 79.875 | -14.875 | 14.875
253 | 1 | 79
253 | 2 | 78
253 | 3 | 77
253 | 4 | 77
253 | 5 | 76
253 | 6 | 74
253 | 7 | 78
253 | 8 | 80
253 | 9 | 81
253 | 10 | 82
253 | 11 | 83
253 | 12 | 84
253 | 13 | 86
253 | 14 | 88
253 | 15 | 89
253 | 16 | 87
253 | 17 | 87
253 | 18 | 83
253 | 19 | 80
253 | 20 | 79
253 | 21 | 76
253 | 22 | 76
253 | 23 | 74
253 | 24 | 72 | 80.25 | -15.25 | 15.25
254 | 1 | 69
254 | 2 | 69
254 | 3 | 67
254 | 4 | 66
254 | 5 | 65
254 | 6 | 66
254 | 7 | 71
254 | 8 | 79
254 | 9 | 82
254 | 10 | 86
254 | 11 | 87
254 | 12 | 88
254 | 13 | 88
254 | 14 | 88
254 | 15 | 88
254 | 16 | 88
254 | 17 | 87
254 | 18 | 85
254 | 19 | 82
254 | 20 | 78
254 | 21 | 76
254 | 22 | 74
254 | 23 | 74
254 | 24 | 74 | 78.2083 | -13.2083 | 13.2083
255 | 1 | 72
255 | 2 | 72
255 | 3 | 74
255 | 4 | 75
255 | 5 | 77
255 | 6 | 78
255 | 7 | 79
255 | 8 | 81
255 | 9 | 84
255 | 10 | 85
255 | 11 | 86
255 | 12 | 87
255 | 13 | 81
255 | 14 | 85
255 | 15 | 75
255 | 16 | 75
255 | 17 | 83
255 | 18 | 82
255 | 19 | 80
255 | 20 | 80
255 | 21 | 79
255 | 22 | 80
255 | 23 | 79
255 | 24 | 79 | 79.5 | -14.5 | 14.5
256 | 1 | 76
256 | 2 | 74
256 | 3 | 75
256 | 4 | 73
256 | 5 | 73
256 | 6 | 73
256 | 7 | 80
256 | 8 | 81
256 | 9 | 83
256 | 10 | 84
256 | 11 | 85
256 | 12 | 87
256 | 13 | 88
256 | 14 | 89
256 | 15 | 89
256 | 16 | 89
256 | 17 | 88
256 | 18 | 85
256 | 19 | 82
256 | 20 | 80
256 | 21 | 80
256 | 22 | 77
256 | 23 | 77
256 | 24 | 77 | 81.0417 | -16.0417 | 16.0417
257 | 1 | 78
257 | 2 | 77
257 | 3 | 77
257 | 4 | 77
257 | 5 | 76
257 | 6 | 76
257 | 7 | 77
257 | 8 | 78
257 | 9 | 79
257 | 10 | 81
257 | 11 | 82
257 | 12 | 84
257 | 13 | 86
257 | 14 | 87
257 | 15 | 87
257 | 16 | 87
257 | 17 | 86
257 | 18 | 85
257 | 19 | 84
257 | 20 | 83
257 | 21 | 82
257 | 22 | 82
257 | 23 | 81
257 | 24 | 80 | 81.3333 | -16.3333 | 16.3333
258 | 1 | 79
258 | 2 | 79
258 | 3 | 78
258 | 4 | 77
258 | 5 | 76
258 | 6 | 74
258 | 7 | 75
258 | 8 | 76
258 | 9 | 78
258 | 10 | 80
258 | 11 | 81
258 | 12 | 84
258 | 13 | 86
258 | 14 | 87
258 | 15 | 88
258 | 16 | 88
258 | 17 | 87
258 | 18 | 83
258 | 19 | 80
258 | 20 | 80
258 | 21 | 78
258 | 22 | 79
258 | 23 | 78
258 | 24 | 77 | 80.3333 | -15.3333 | 15.3333
259 | 1 | 77
259 | 2 | 76
259 | 3 | 74
259 | 4 | 75
259 | 5 | 74
259 | 6 | 74
259 | 7 | 75
259 | 8 | 77
259 | 9 | 78
259 | 10 | 80
259 | 11 | 81
259 | 12 | 83
259 | 13 | 85
259 | 14 | 87
259 | 15 | 87
259 | 16 | 87
259 | 17 | 85
259 | 18 | 80
259 | 19 | 78
259 | 20 | 80
259 | 21 | 80
259 | 22 | 79
259 | 23 | 77
259 | 24 | 77 | 79.4167 | -14.4167 | 14.4167
260 | 1 | 75
260 | 2 | 73
260 | 3 | 73
260 | 4 | 72
260 | 5 | 71
260 | 6 | 70
260 | 7 | 72
260 | 8 | 73
260 | 9 | 76
260 | 10 | 77
260 | 11 | 80
260 | 12 | 82
260 | 13 | 83
260 | 14 | 84
260 | 15 | 85
260 | 16 | 85
260 | 17 | 83
260 | 18 | 78
260 | 19 | 75
260 | 20 | 72
260 | 21 | 72
260 | 22 | 68
260 | 23 | 65
260 | 24 | 64 | 75.3333 | -10.3333 | 10.3333
261 | 1 | 65
261 | 2 | 64
261 | 3 | 63
261 | 4 | 65
261 | 5 | 62
261 | 6 | 60
261 | 7 | 71
261 | 8 | 76
261 | 9 | 79
261 | 10 | 81
261 | 11 | 82
261 | 12 | 84
261 | 13 | 85
261 | 14 | 86
261 | 15 | 87
261 | 16 | 87
261 | 17 | 85
261 | 18 | 83
261 | 19 | 80
261 | 20 | 79
261 | 21 | 76
261 | 22 | 75
261 | 23 | 76
261 | 24 | 77 | 76.1667 | -11.1667 | 11.1667
262 | 1 | 76
262 | 2 | 76
262 | 3 | 75
262 | 4 | 76
262 | 5 | 76
262 | 6 | 75
262 | 7 | 77
262 | 8 | 79
262 | 9 | 81
262 | 10 | 82
262 | 11 | 85
262 | 12 | 86
262 | 13 | 88
262 | 14 | 89
262 | 15 | 88
262 | 16 | 88
262 | 17 | 86
262 | 18 | 84
262 | 19 | 82
262 | 20 | 81
262 | 21 | 80
262 | 22 | 80
262 | 23 | 79
262 | 24 | 79 | 81.1667 | -16.1667 | 16.1667
263 | 1 | 79
263 | 2 | 79
263 | 3 | 77
263 | 4 | 77
263 | 5 | 77
263 | 6 | 77
263 | 7 | 77
263 | 8 | 77
263 | 9 | 78
263 | 10 | 79
263 | 11 | 79
263 | 12 | 81
263 | 13 | 84
263 | 14 | 85
263 | 15 | 87
263 | 16 | 88
263 | 17 | 86
263 | 18 | 85
263 | 19 | 83
263 | 20 | 81
263 | 21 | 80
263 | 22 | 80
263 | 23 | 78
263 | 24 | 76 | 80.4167 | -15.4167 | 15.4167
264 | 1 | 75
264 | 2 | 75
264 | 3 | 74
264 | 4 | 73
264 | 5 | 73
264 | 6 | 74
264 | 7 | 77
264 | 8 | 80
264 | 9 | 81
264 | 10 | 82
264 | 11 | 85
264 | 12 | 85
264 | 13 | 86
264 | 14 | 84
264 | 15 | 83
264 | 16 | 83
264 | 17 | 80
264 | 18 | 77
264 | 19 | 75
264 | 20 | 74
264 | 21 | 72
264 | 22 | 71
264 | 23 | 70
264 | 24 | 69 | 77.4167 | -12.4167 | 12.4167
265 | 1 | 67
265 | 2 | 67
265 | 3 | 66
265 | 4 | 65
265 | 5 | 65
265 | 6 | 63
265 | 7 | 65
265 | 8 | 67
265 | 9 | 69
265 | 10 | 70
265 | 11 | 72
265 | 12 | 73
265 | 13 | 74
265 | 14 | 76
265 | 15 | 76
265 | 16 | 77
265 | 17 | 76
265 | 18 | 73
265 | 19 | 73
265 | 20 | 72
265 | 21 | 72
265 | 22 | 70
265 | 23 | 70
265 | 24 | 70 | 70.3333 | -5.3333 | 5.3333
266 | 1 | 67
266 | 2 | 67
266 | 3 | 65
266 | 4 | 66
266 | 5 | 64
266 | 6 | 64
266 | 7 | 67
266 | 8 | 70
266 | 9 | 73
266 | 10 | 75
266 | 11 | 76
266 | 12 | 77
266 | 13 | 77
266 | 14 | 79
266 | 15 | 79
266 | 16 | 79
266 | 17 | 77
266 | 18 | 73
266 | 19 | 69
266 | 20 | 69
266 | 21 | 66
266 | 22 | 63
266 | 23 | 64
266 | 24 | 60 | 70.25 | -5.25 | 5.25
267 | 1 | 60
267 | 2 | 57
267 | 3 | 59
267 | 4 | 55
267 | 5 | 57
267 | 6 | 58
267 | 7 | 64
267 | 8 | 67
267 | 9 | 75
267 | 10 | 76
267 | 11 | 76
267 | 12 | 78
267 | 13 | 79
267 | 14 | 81
267 | 15 | 80
267 | 16 | 79
267 | 17 | 78
267 | 18 | 75
267 | 19 | 74
267 | 20 | 71
267 | 21 | 71
267 | 22 | 69
267 | 23 | 69
267 | 24 | 67 | 69.7917 | -4.7917 | 4.7917
268 | 1 | 67
268 | 2 | 68
268 | 3 | 68
268 | 4 | 68
268 | 5 | 68
268 | 6 | 68
268 | 7 | 72
268 | 8 | 76
268 | 9 | 79
268 | 10 | 81
268 | 11 | 82
268 | 12 | 78
268 | 13 | 78
268 | 14 | 78
268 | 15 | 76
268 | 16 | 75
268 | 17 | 74
268 | 18 | 75
268 | 19 | 75
268 | 20 | 75
268 | 21 | 76
268 | 22 | 76
268 | 23 | 75
268 | 24 | 75 | 74.2917 | -9.2917 | 9.2917
269 | 1 | 73
269 | 2 | 73
269 | 3 | 73
269 | 4 | 72
269 | 5 | 72
269 | 6 | 73
269 | 7 | 73
269 | 8 | 74
269 | 9 | 75
269 | 10 | 80
269 | 11 | 81
269 | 12 | 81
269 | 13 | 83
269 | 14 | 82
269 | 15 | 82
269 | 16 | 83
269 | 17 | 81
269 | 18 | 80
269 | 19 | 79
269 | 20 | 78
269 | 21 | 77
269 | 22 | 77
269 | 23 | 76
269 | 24 | 76 | 77.25 | -12.25 | 12.25
270 | 1 | 76
270 | 2 | 76
270 | 3 | 74
270 | 4 | 71
270 | 5 | 70
270 | 6 | 74
270 | 7 | 75
270 | 8 | 77
270 | 9 | 81
270 | 10 | 82
270 | 11 | 83
270 | 12 | 86
270 | 13 | 87
270 | 14 | 86
270 | 15 | 86
270 | 16 | 85
270 | 17 | 84
270 | 18 | 82
270 | 19 | 80
270 | 20 | 79
270 | 21 | 79
270 | 22 | 78
270 | 23 | 78
270 | 24 | 77 | 79.4167 | -14.4167 | 14.4167
271 | 1 | 77
271 | 2 | 78
271 | 3 | 77
271 | 4 | 77
271 | 5 | 76
271 | 6 | 76
271 | 7 | 77
271 | 8 | 77
271 | 9 | 79
271 | 10 | 80
271 | 11 | 81
271 | 12 | 82
271 | 13 | 82
271 | 14 | 82
271 | 15 | 83
271 | 16 | 80
271 | 17 | 79
271 | 18 | 78
271 | 19 | 77
271 | 20 | 76
271 | 21 | 75
271 | 22 | 75
271 | 23 | 74
271 | 24 | 74 | 78 | -13 | 13
272 | 1 | 76
272 | 2 | 76
272 | 3 | 76
272 | 4 | 75
272 | 5 | 75
272 | 6 | 74
272 | 7 | 76
272 | 8 | 80
272 | 9 | 82
272 | 10 | 84
272 | 11 | 74
272 | 12 | 77
272 | 13 | 80
272 | 14 | 79
272 | 15 | 78
272 | 16 | 77
272 | 17 | 70
272 | 18 | 67
272 | 19 | 67
272 | 20 | 66
272 | 21 | 66
272 | 22 | 66
272 | 23 | 65
272 | 24 | 65 | 73.7917 | -8.7917 | 8.7917
273 | 1 | 65
273 | 2 | 64
273 | 3 | 64
273 | 4 | 63
273 | 5 | 63
273 | 6 | 63
273 | 7 | 63
273 | 8 | 66
273 | 9 | 67
273 | 10 | 68
273 | 11 | 69
273 | 12 | 70
273 | 13 | 72
273 | 14 | 74
273 | 15 | 72
273 | 16 | 72
273 | 17 | 72
273 | 18 | 68
273 | 19 | 69
273 | 20 | 69
273 | 21 | 69
273 | 22 | 71
273 | 23 | 73
273 | 24 | 74 | 68.3333 | -3.3333 | 3.3333
274 | 1 | 76
274 | 2 | 78
274 | 3 | 79
274 | 4 | 81
274 | 5 | 81
274 | 6 | 81
274 | 7 | 83
274 | 8 | 85
274 | 9 | 87
274 | 10 | 89
274 | 11 | 90
274 | 12 | 92
274 | 13 | 92
274 | 14 | 91
274 | 15 | 91
274 | 16 | 89
274 | 17 | 88
274 | 18 | 86
274 | 19 | 85
274 | 20 | 83
274 | 21 | 82
274 | 22 | 82
274 | 23 | 81
274 | 24 | 81 | 84.7083 | -19.7083 | 19.7083
275 | 1 | 80
275 | 2 | 80
275 | 3 | 79
275 | 4 | 79
275 | 5 | 78
275 | 6 | 78
275 | 7 | 81
275 | 8 | 84
275 | 9 | 87
275 | 10 | 84
275 | 11 | 80
275 | 12 | 77
275 | 13 | 77
275 | 14 | 78
275 | 15 | 78
275 | 16 | 78
275 | 17 | 78
275 | 18 | 78
275 | 19 | 76
275 | 20 | 75
275 | 21 | 73
275 | 22 | 72
275 | 23 | 71
275 | 24 | 70 | 77.9583 | -12.9583 | 12.9583
276 | 1 | 69
276 | 2 | 67
276 | 3 | 66
276 | 4 | 65
276 | 5 | 64
276 | 6 | 63
276 | 7 | 64
276 | 8 | 65
276 | 9 | 66
276 | 10 | 67
276 | 11 | 69
276 | 12 | 70
276 | 13 | 71
276 | 14 | 72
276 | 15 | 73
276 | 16 | 72
276 | 17 | 70
276 | 18 | 69
276 | 19 | 68
276 | 20 | 68
276 | 21 | 67
276 | 22 | 66
276 | 23 | 66
276 | 24 | 65 | 67.5833 | -2.5833 | 2.5833
277 | 1 | 65
277 | 2 | 64
277 | 3 | 64
277 | 4 | 63
277 | 5 | 62
277 | 6 | 61
277 | 7 | 63
277 | 8 | 65
277 | 9 | 67
277 | 10 | 69
277 | 11 | 70
277 | 12 | 72
277 | 13 | 73
277 | 14 | 73
277 | 15 | 74
277 | 16 | 70
277 | 17 | 67
277 | 18 | 63
277 | 19 | 61
277 | 20 | 59
277 | 21 | 57
277 | 22 | 56
277 | 23 | 56
277 | 24 | 55 | 64.5417 | 0.45833 | -0.45833
278 | 1 | 55
278 | 2 | 56
278 | 3 | 56
278 | 4 | 57
278 | 5 | 57
278 | 6 | 58
278 | 7 | 63
278 | 8 | 67
278 | 9 | 72
278 | 10 | 74
278 | 11 | 76
278 | 12 | 78
278 | 13 | 78
278 | 14 | 79
278 | 15 | 79
278 | 16 | 77
278 | 17 | 75
278 | 18 | 73
278 | 19 | 72
278 | 20 | 72
278 | 21 | 71
278 | 22 | 71
278 | 23 | 71
278 | 24 | 71 | 69.0833 | -4.0833 | 4.0833
279 | 1 | 71
279 | 2 | 71
279 | 3 | 71
279 | 4 | 71
279 | 5 | 71
279 | 6 | 71
279 | 7 | 73
279 | 8 | 76
279 | 9 | 78
279 | 10 | 79
279 | 11 | 80
279 | 12 | 81
279 | 13 | 81
279 | 14 | 82
279 | 15 | 82
279 | 16 | 79
279 | 17 | 75
279 | 18 | 72
279 | 19 | 70
279 | 20 | 68
279 | 21 | 66
279 | 22 | 66
279 | 23 | 66
279 | 24 | 66 | 73.5833 | -8.5833 | 8.5833
280 | 1 | 65
280 | 2 | 63
280 | 3 | 62
280 | 4 | 63
280 | 5 | 63
280 | 6 | 64
280 | 7 | 68
280 | 8 | 71
280 | 9 | 75
280 | 10 | 77
280 | 11 | 79
280 | 12 | 81
280 | 13 | 81
280 | 14 | 82
280 | 15 | 82
280 | 16 | 81
280 | 17 | 79
280 | 18 | 78
280 | 19 | 77
280 | 20 | 76
280 | 21 | 75
280 | 22 | 75
280 | 23 | 75
280 | 24 | 75 | 73.625 | -8.625 | 8.625
281 | 1 | 74
281 | 2 | 74
281 | 3 | 73
281 | 4 | 74
281 | 5 | 74
281 | 6 | 75
281 | 7 | 77
281 | 8 | 79
281 | 9 | 81
281 | 10 | 83
281 | 11 | 85
281 | 12 | 87
281 | 13 | 86
281 | 14 | 85
281 | 15 | 84
281 | 16 | 83
281 | 17 | 82
281 | 18 | 81
281 | 19 | 80
281 | 20 | 79
281 | 21 | 78
281 | 22 | 78
281 | 23 | 79
281 | 24 | 79 | 79.5833 | -14.5833 | 14.5833
282 | 1 | 77
282 | 2 | 74
282 | 3 | 72
282 | 4 | 72
282 | 5 | 72
282 | 6 | 72
282 | 7 | 70
282 | 8 | 68
282 | 9 | 66
282 | 10 | 68
282 | 11 | 71
282 | 12 | 73
282 | 13 | 74
282 | 14 | 75
282 | 15 | 76
282 | 16 | 74
282 | 17 | 72
282 | 18 | 70
282 | 19 | 69
282 | 20 | 67
282 | 21 | 66
282 | 22 | 66
282 | 23 | 65
282 | 24 | 65 | 70.5833 | -5.5833 | 5.5833
283 | 1 | 64
283 | 2 | 62
283 | 3 | 61
283 | 4 | 60
283 | 5 | 60
283 | 6 | 59
283 | 7 | 63
283 | 8 | 67
283 | 9 | 71
283 | 10 | 73
283 | 11 | 76
283 | 12 | 78
283 | 13 | 78
283 | 14 | 77
283 | 15 | 77
283 | 16 | 75
283 | 17 | 72
283 | 18 | 70
283 | 19 | 70
283 | 20 | 70
283 | 21 | 70
283 | 22 | 70
283 | 23 | 69
283 | 24 | 69 | 69.2083 | -4.2083 | 4.2083
284 | 1 | 69
284 | 2 | 70
284 | 3 | 70
284 | 4 | 70
284 | 5 | 71
284 | 6 | 71
284 | 7 | 71
284 | 8 | 72
284 | 9 | 72
284 | 10 | 72
284 | 11 | 72
284 | 12 | 72
284 | 13 | 72
284 | 14 | 71
284 | 15 | 71
284 | 16 | 70
284 | 17 | 68
284 | 18 | 67
284 | 19 | 66
284 | 20 | 66
284 | 21 | 65
284 | 22 | 64
284 | 23 | 62
284 | 24 | 61 | 68.9583 | -3.9583 | 3.9583
285 | 1 | 60
285 | 2 | 59
285 | 3 | 58
285 | 4 | 58
285 | 5 | 58
285 | 6 | 58
285 | 7 | 59
285 | 8 | 59
285 | 9 | 60
285 | 10 | 62
285 | 11 | 64
285 | 12 | 66
285 | 13 | 66
285 | 14 | 66
285 | 15 | 66
285 | 16 | 64
285 | 17 | 61
285 | 18 | 59
285 | 19 | 58
285 | 20 | 58
285 | 21 | 57
285 | 22 | 57
285 | 23 | 56
285 | 24 | 56 | 60.2083 | 4.7917 | -4.7917
286 | 1 | 56
286 | 2 | 55
286 | 3 | 55
286 | 4 | 54
286 | 5 | 54
286 | 6 | 53
286 | 7 | 55
286 | 8 | 56
286 | 9 | 58
286 | 10 | 59
286 | 11 | 61
286 | 12 | 62
286 | 13 | 63
286 | 14 | 64
286 | 15 | 65
286 | 16 | 63
286 | 17 | 60
286 | 18 | 58
286 | 19 | 56
286 | 20 | 54
286 | 21 | 52
286 | 22 | 52
286 | 23 | 51
286 | 24 | 51 | 56.9583 | 8.0417 | -8.0417
287 | 1 | 49
287 | 2 | 46
287 | 3 | 44
287 | 4 | 44
287 | 5 | 44
287 | 6 | 44
287 | 7 | 50
287 | 8 | 56
287 | 9 | 62
287 | 10 | 63
287 | 11 | 65
287 | 12 | 66
287 | 13 | 67
287 | 14 | 68
287 | 15 | 69
287 | 16 | 65
287 | 17 | 61
287 | 18 | 57
287 | 19 | 55
287 | 20 | 54
287 | 21 | 52
287 | 22 | 53
287 | 23 | 53
287 | 24 | 54 | 55.875 | 9.125 | -9.125
288 | 1 | 53
288 | 2 | 51
288 | 3 | 50
288 | 4 | 49
288 | 5 | 47
288 | 6 | 46
288 | 7 | 52
288 | 8 | 59
288 | 9 | 65
288 | 10 | 68
288 | 11 | 71
288 | 12 | 74
288 | 13 | 75
288 | 14 | 76
288 | 15 | 77
288 | 16 | 74
288 | 17 | 71
288 | 18 | 68
288 | 19 | 66
288 | 20 | 65
288 | 21 | 63
288 | 22 | 63
288 | 23 | 62
288 | 24 | 62 | 62.7917 | 2.2083 | -2.2083
289 | 1 | 62
289 | 2 | 61
289 | 3 | 61
289 | 4 | 60
289 | 5 | 58
289 | 6 | 57
289 | 7 | 59
289 | 8 | 60
289 | 9 | 62
289 | 10 | 64
289 | 11 | 65
289 | 12 | 67
289 | 13 | 68
289 | 14 | 69
289 | 15 | 70
289 | 16 | 67
289 | 17 | 65
289 | 18 | 62
289 | 19 | 59
289 | 20 | 55
289 | 21 | 52
289 | 22 | 51
289 | 23 | 51
289 | 24 | 50 | 60.625 | 4.375 | -4.375
290 | 1 | 49
290 | 2 | 48
290 | 3 | 47
290 | 4 | 46
290 | 5 | 45
290 | 6 | 44
290 | 7 | 50
290 | 8 | 57
290 | 9 | 63
290 | 10 | 65
290 | 11 | 67
290 | 12 | 69
290 | 13 | 69
290 | 14 | 69
290 | 15 | 69
290 | 16 | 64
290 | 17 | 60
290 | 18 | 55
290 | 19 | 53
290 | 20 | 51
290 | 21 | 49
290 | 22 | 49
290 | 23 | 48
290 | 24 | 48 | 55.5833 | 9.4167 | -9.4167
291 | 1 | 47
291 | 2 | 47
291 | 3 | 46
291 | 4 | 46
291 | 5 | 45
291 | 6 | 45
291 | 7 | 53
291 | 8 | 60
291 | 9 | 68
291 | 10 | 71
291 | 11 | 73
291 | 12 | 76
291 | 13 | 77
291 | 14 | 77
291 | 15 | 78
291 | 16 | 74
291 | 17 | 71
291 | 18 | 67
291 | 19 | 66
291 | 20 | 64
291 | 21 | 63
291 | 22 | 62
291 | 23 | 60
291 | 24 | 59 | 62.2917 | 2.7083 | -2.7083
292 | 1 | 59
292 | 2 | 60
292 | 3 | 60
292 | 4 | 59
292 | 5 | 59
292 | 6 | 58
292 | 7 | 63
292 | 8 | 67
292 | 9 | 72
292 | 10 | 75
292 | 11 | 78
292 | 12 | 81
292 | 13 | 81
292 | 14 | 82
292 | 15 | 82
292 | 16 | 78
292 | 17 | 74
292 | 18 | 70
292 | 19 | 69
292 | 20 | 69
292 | 21 | 68
292 | 22 | 67
292 | 23 | 67
292 | 24 | 66 | 69.3333 | -4.3333 | 4.3333
293 | 1 | 65
293 | 2 | 65
293 | 3 | 64
293 | 4 | 64
293 | 5 | 65
293 | 6 | 65
293 | 7 | 66
293 | 8 | 68
293 | 9 | 69
293 | 10 | 71
293 | 11 | 74
293 | 12 | 76
293 | 13 | 76
293 | 14 | 77
293 | 15 | 77
293 | 16 | 75
293 | 17 | 73
293 | 18 | 71
293 | 19 | 69
293 | 20 | 68
293 | 21 | 66
293 | 22 | 66
293 | 23 | 65
293 | 24 | 65 | 69.1667 | -4.1667 | 4.1667
294 | 1 | 64
294 | 2 | 64
294 | 3 | 63
294 | 4 | 63
294 | 5 | 62
294 | 6 | 62
294 | 7 | 66
294 | 8 | 69
294 | 9 | 73
294 | 10 | 75
294 | 11 | 76
294 | 12 | 78
294 | 13 | 78
294 | 14 | 79
294 | 15 | 79
294 | 16 | 76
294 | 17 | 72
294 | 18 | 69
294 | 19 | 66
294 | 20 | 64
294 | 21 | 61
294 | 22 | 62
294 | 23 | 63
294 | 24 | 64 | 68.6667 | -3.6667 | 3.6667
295 | 1 | 64
295 | 2 | 63
295 | 3 | 63
295 | 4 | 63
295 | 5 | 64
295 | 6 | 64
295 | 7 | 67
295 | 8 | 70
295 | 9 | 73
295 | 10 | 75
295 | 11 | 77
295 | 12 | 79
295 | 13 | 79
295 | 14 | 78
295 | 15 | 78
295 | 16 | 76
295 | 17 | 75
295 | 18 | 73
295 | 19 | 73
295 | 20 | 72
295 | 21 | 72
295 | 22 | 72
295 | 23 | 72
295 | 24 | 72 | 71.4167 | -6.4167 | 6.4167
296 | 1 | 72
296 | 2 | 72
296 | 3 | 72
296 | 4 | 71
296 | 5 | 71
296 | 6 | 70
296 | 7 | 71
296 | 8 | 73
296 | 9 | 74
296 | 10 | 74
296 | 11 | 75
296 | 12 | 75
296 | 13 | 76
296 | 14 | 76
296 | 15 | 77
296 | 16 | 76
296 | 17 | 74
296 | 18 | 73
296 | 19 | 72
296 | 20 | 72
296 | 21 | 71
296 | 22 | 71
296 | 23 | 70
296 | 24 | 70 | 72.8333 | -7.8333 | 7.8333
297 | 1 | 69
297 | 2 | 69
297 | 3 | 68
297 | 4 | 68
297 | 5 | 69
297 | 6 | 69
297 | 7 | 70
297 | 8 | 70
297 | 9 | 71
297 | 10 | 71
297 | 11 | 70
297 | 12 | 70
297 | 13 | 70
297 | 14 | 71
297 | 15 | 71
297 | 16 | 72
297 | 17 | 72
297 | 18 | 73
297 | 19 | 73
297 | 20 | 73
297 | 21 | 73
297 | 22 | 73
297 | 23 | 73
297 | 24 | 73 | 70.875 | -5.875 | 5.875
298 | 1 | 73
298 | 2 | 73
298 | 3 | 73
298 | 4 | 73
298 | 5 | 72
298 | 6 | 72
298 | 7 | 72
298 | 8 | 71
298 | 9 | 71
298 | 10 | 72
298 | 11 | 72
298 | 12 | 73
298 | 13 | 74
298 | 14 | 74
298 | 15 | 75
298 | 16 | 74
298 | 17 | 72
298 | 18 | 71
298 | 19 | 70
298 | 20 | 70
298 | 21 | 69
298 | 22 | 68
298 | 23 | 68
298 | 24 | 67 | 71.625 | -6.625 | 6.625
299 | 1 | 66
299 | 2 | 65
299 | 3 | 64
299 | 4 | 63
299 | 5 | 62
299 | 6 | 61
299 | 7 | 64
299 | 8 | 66
299 | 9 | 69
299 | 10 | 72
299 | 11 | 74
299 | 12 | 77
299 | 13 | 77
299 | 14 | 78
299 | 15 | 78
299 | 16 | 76
299 | 17 | 74
299 | 18 | 72
299 | 19 | 71
299 | 20 | 69
299 | 21 | 68
299 | 22 | 67
299 | 23 | 65
299 | 24 | 64 | 69.25 | -4.25 | 4.25
300 | 1 | 63
300 | 2 | 63
300 | 3 | 62
300 | 4 | 60
300 | 5 | 59
300 | 6 | 57
300 | 7 | 60
300 | 8 | 62
300 | 9 | 65
300 | 10 | 67
300 | 11 | 69
300 | 12 | 71
300 | 13 | 72
300 | 14 | 74
300 | 15 | 75
300 | 16 | 71
300 | 17 | 68
300 | 18 | 64
300 | 19 | 63
300 | 20 | 63
300 | 21 | 62
300 | 22 | 63
300 | 23 | 63
300 | 24 | 64 | 65 | 0 | 0
301 | 1 | 63
301 | 2 | 62
301 | 3 | 61
301 | 4 | 61
301 | 5 | 60
301 | 6 | 60
301 | 7 | 62
301 | 8 | 65
301 | 9 | 67
301 | 10 | 69
301 | 11 | 71
301 | 12 | 73
301 | 13 | 73
301 | 14 | 74
301 | 15 | 74
301 | 16 | 71
301 | 17 | 69
301 | 18 | 66
301 | 19 | 64
301 | 20 | 63
301 | 21 | 61
301 | 22 | 61
301 | 23 | 62
301 | 24 | 62 | 65.5833 | -0.58333 | 0.58333
302 | 1 | 61
302 | 2 | 59
302 | 3 | 58
302 | 4 | 58
302 | 5 | 57
302 | 6 | 57
302 | 7 | 61
302 | 8 | 66
302 | 9 | 70
302 | 10 | 72
302 | 11 | 73
302 | 12 | 75
302 | 13 | 76
302 | 14 | 76
302 | 15 | 77
302 | 16 | 74
302 | 17 | 71
302 | 18 | 68
302 | 19 | 66
302 | 20 | 65
302 | 21 | 63
302 | 22 | 63
302 | 23 | 62
302 | 24 | 62 | 66.25 | -1.25 | 1.25
303 | 1 | 61
303 | 2 | 59
303 | 3 | 58
303 | 4 | 58
303 | 5 | 57
303 | 6 | 57
303 | 7 | 61
303 | 8 | 65
303 | 9 | 69
303 | 10 | 72
303 | 11 | 74
303 | 12 | 77
303 | 13 | 77
303 | 14 | 77
303 | 15 | 77
303 | 16 | 75
303 | 17 | 74
303 | 18 | 72
303 | 19 | 71
303 | 20 | 70
303 | 21 | 69
303 | 22 | 68
303 | 23 | 68
303 | 24 | 67 | 68.0417 | -3.0417 | 3.0417
304 | 1 | 66
304 | 2 | 65
304 | 3 | 64
304 | 4 | 63
304 | 5 | 63
304 | 6 | 62
304 | 7 | 65
304 | 8 | 68
304 | 9 | 71
304 | 10 | 74
304 | 11 | 76
304 | 12 | 79
304 | 13 | 80
304 | 14 | 80
304 | 15 | 81
304 | 16 | 79
304 | 17 | 76
304 | 18 | 74
304 | 19 | 74
304 | 20 | 73
304 | 21 | 73
304 | 22 | 72
304 | 23 | 71
304 | 24 | 69 | 71.5833 | -6.5833 | 6.5833
305 | 1 | 68
305 | 2 | 67
305 | 3 | 65
305 | 4 | 64
305 | 5 | 61
305 | 6 | 56
305 | 7 | 56
305 | 8 | 57
305 | 9 | 59
305 | 10 | 60
305 | 11 | 62
305 | 12 | 63
305 | 13 | 65
305 | 14 | 67
305 | 15 | 68
305 | 16 | 67
305 | 17 | 63
305 | 18 | 53
305 | 19 | 50
305 | 20 | 50
305 | 21 | 48
305 | 22 | 48
305 | 23 | 50
305 | 24 | 46 | 58.875 | 6.125 | -6.125
306 | 1 | 46
306 | 2 | 45
306 | 3 | 45
306 | 4 | 45
306 | 5 | 45
306 | 6 | 46
306 | 7 | 49
306 | 8 | 63
306 | 9 | 72
306 | 10 | 74
306 | 11 | 76
306 | 12 | 79
306 | 13 | 79
306 | 14 | 77
306 | 15 | 79
306 | 16 | 78
306 | 17 | 74
306 | 18 | 71
306 | 19 | 70
306 | 20 | 68
306 | 21 | 69
306 | 22 | 69
306 | 23 | 68
306 | 24 | 68 | 64.7917 | 0.20833 | -0.20833
307 | 1 | 70
307 | 2 | 70
307 | 3 | 70
307 | 4 | 71
307 | 5 | 71
307 | 6 | 71
307 | 7 | 71
307 | 8 | 72
307 | 9 | 75
307 | 10 | 75
307 | 11 | 78
307 | 12 | 81
307 | 13 | 80
307 | 14 | 80
307 | 15 | 80
307 | 16 | 79
307 | 17 | 76
307 | 18 | 73
307 | 19 | 71
307 | 20 | 69
307 | 21 | 67
307 | 22 | 65
307 | 23 | 64
307 | 24 | 65 | 72.6667 | -7.6667 | 7.6667
308 | 1 | 65
308 | 2 | 62
308 | 3 | 63
308 | 4 | 65
308 | 5 | 60
308 | 6 | 60
308 | 7 | 62
308 | 8 | 71
308 | 9 | 76
308 | 10 | 79
308 | 11 | 81
308 | 12 | 84
308 | 13 | 82
308 | 14 | 82
308 | 15 | 81
308 | 16 | 79
308 | 17 | 77
308 | 18 | 75
308 | 19 | 74
308 | 20 | 75
308 | 21 | 75
308 | 22 | 76
308 | 23 | 76
308 | 24 | 76 | 73.1667 | -8.1667 | 8.1667
309 | 1 | 77
309 | 2 | 77
309 | 3 | 77
309 | 4 | 77
309 | 5 | 77
309 | 6 | 77
309 | 7 | 77
309 | 8 | 77
309 | 9 | 78
309 | 10 | 82
309 | 11 | 83
309 | 12 | 85
309 | 13 | 86
309 | 14 | 86
309 | 15 | 82
309 | 16 | 81
309 | 17 | 80
309 | 18 | 78
309 | 19 | 78
309 | 20 | 77
309 | 21 | 77
309 | 22 | 77
309 | 23 | 77
309 | 24 | 75 | 79.0833 | -14.0833 | 14.0833
310 | 1 | 71
310 | 2 | 71
310 | 3 | 70
310 | 4 | 69
310 | 5 | 68
310 | 6 | 68
310 | 7 | 67
310 | 8 | 68
310 | 9 | 69
310 | 10 | 70
310 | 11 | 71
310 | 12 | 75
310 | 13 | 75
310 | 14 | 76
310 | 15 | 77
310 | 16 | 77
310 | 17 | 73
310 | 18 | 62
310 | 19 | 66
310 | 20 | 70
310 | 21 | 69
310 | 22 | 68
310 | 23 | 67
310 | 24 | 66 | 70.125 | -5.125 | 5.125
311 | 1 | 65
311 | 2 | 64
311 | 3 | 63
311 | 4 | 62
311 | 5 | 61
311 | 6 | 61
311 | 7 | 61
311 | 8 | 63
311 | 9 | 66
311 | 10 | 68
311 | 11 | 72
311 | 12 | 75
311 | 13 | 77
311 | 14 | 75
311 | 15 | 75
311 | 16 | 74
311 | 17 | 71
311 | 18 | 66
311 | 19 | 65
311 | 20 | 62
311 | 21 | 62
311 | 22 | 60
311 | 23 | 58
311 | 24 | 57 | 65.9583 | -0.95833 | 0.95833
312 | 1 | 55
312 | 2 | 52
312 | 3 | 54
312 | 4 | 56
312 | 5 | 58
312 | 6 | 59
312 | 7 | 59
312 | 8 | 67
312 | 9 | 69
312 | 10 | 75
312 | 11 | 78
312 | 12 | 78
312 | 13 | 78
312 | 14 | 78
312 | 15 | 79
312 | 16 | 77
312 | 17 | 75
312 | 18 | 75
312 | 19 | 73
312 | 20 | 73
312 | 21 | 72
312 | 22 | 72
312 | 23 | 71
312 | 24 | 71 | 68.9167 | -3.9167 | 3.9167
313 | 1 | 71
313 | 2 | 71
313 | 3 | 71
313 | 4 | 71
313 | 5 | 70
313 | 6 | 70
313 | 7 | 70
313 | 8 | 69
313 | 9 | 74
313 | 10 | 78
313 | 11 | 82
313 | 12 | 82
313 | 13 | 83
313 | 14 | 84
313 | 15 | 82
313 | 16 | 81
313 | 17 | 78
313 | 18 | 76
313 | 19 | 75
313 | 20 | 74
313 | 21 | 73
313 | 22 | 72
313 | 23 | 73
313 | 24 | 72 | 75.0833 | -10.0833 | 10.0833
314 | 1 | 71
314 | 2 | 72
314 | 3 | 73
314 | 4 | 73
314 | 5 | 68
314 | 6 | 68
314 | 7 | 67
314 | 8 | 69
314 | 9 | 71
314 | 10 | 71
314 | 11 | 73
314 | 12 | 73
314 | 13 | 74
314 | 14 | 72
314 | 15 | 71
314 | 16 | 69
314 | 17 | 66
314 | 18 | 65
314 | 19 | 64
314 | 20 | 63
314 | 21 | 62
314 | 22 | 63
314 | 23 | 62
314 | 24 | 62 | 68.4167 | -3.4167 | 3.4167
315 | 1 | 62
315 | 2 | 62
315 | 3 | 62
315 | 4 | 62
315 | 5 | 62
315 | 6 | 62
315 | 7 | 62
315 | 8 | 62
315 | 9 | 62
315 | 10 | 63
315 | 11 | 62
315 | 12 | 63
315 | 13 | 64
315 | 14 | 64
315 | 15 | 64
315 | 16 | 63
315 | 17 | 63
315 | 18 | 63
315 | 19 | 62
315 | 20 | 63
315 | 21 | 63
315 | 22 | 64
315 | 23 | 64
315 | 24 | 64 | 62.7917 | 2.2083 | -2.2083
316 | 1 | 64
316 | 2 | 64
316 | 3 | 63
316 | 4 | 63
316 | 5 | 62
316 | 6 | 62
316 | 7 | 62
316 | 8 | 62
316 | 9 | 62
316 | 10 | 64
316 | 11 | 66
316 | 12 | 69
316 | 13 | 67
316 | 14 | 68
316 | 15 | 68
316 | 16 | 68
316 | 17 | 66
316 | 18 | 66
316 | 19 | 66
316 | 20 | 63
316 | 21 | 66
316 | 22 | 65
316 | 23 | 64
316 | 24 | 65 | 64.7917 | 0.20833 | -0.20833
317 | 1 | 65
317 | 2 | 65
317 | 3 | 65
317 | 4 | 65
317 | 5 | 63
317 | 6 | 63
317 | 7 | 65
317 | 8 | 67
317 | 9 | 69
317 | 10 | 69
317 | 11 | 72
317 | 12 | 74
317 | 13 | 74
317 | 14 | 73
317 | 15 | 72
317 | 16 | 71
317 | 17 | 70
317 | 18 | 69
317 | 19 | 69
317 | 20 | 69
317 | 21 | 70
317 | 22 | 69
317 | 23 | 67
317 | 24 | 66 | 68.375 | -3.375 | 3.375
318 | 1 | 67
318 | 2 | 67
318 | 3 | 68
318 | 4 | 67
318 | 5 | 66
318 | 6 | 65
318 | 7 | 66
318 | 8 | 71
318 | 9 | 74
318 | 10 | 77
318 | 11 | 78
318 | 12 | 80
318 | 13 | 80
318 | 14 | 79
318 | 15 | 78
318 | 16 | 76
318 | 17 | 72
318 | 18 | 68
318 | 19 | 66
318 | 20 | 62
318 | 21 | 59
318 | 22 | 58
318 | 23 | 57
318 | 24 | 59 | 69.1667 | -4.1667 | 4.1667
319 | 1 | 64
319 | 2 | 65
319 | 3 | 64
319 | 4 | 63
319 | 5 | 63
319 | 6 | 61
319 | 7 | 58
319 | 8 | 68
319 | 9 | 71
319 | 10 | 73
319 | 11 | 75
319 | 12 | 77
319 | 13 | 78
319 | 14 | 78
319 | 15 | 79
319 | 16 | 78
319 | 17 | 74
319 | 18 | 73
319 | 19 | 71
319 | 20 | 71
319 | 21 | 69
319 | 22 | 66
319 | 23 | 65
319 | 24 | 65 | 69.5417 | -4.5417 | 4.5417
320 | 1 | 66
320 | 2 | 61
320 | 3 | 63
320 | 4 | 62
320 | 5 | 62
320 | 6 | 63
320 | 7 | 64
320 | 8 | 66
320 | 9 | 63
320 | 10 | 65
320 | 11 | 68
320 | 12 | 70
320 | 13 | 72
320 | 14 | 71
320 | 15 | 72
320 | 16 | 72
320 | 17 | 70
320 | 18 | 68
320 | 19 | 66
320 | 20 | 63
320 | 21 | 62
320 | 22 | 61
320 | 23 | 61
320 | 24 | 60 | 65.4583 | -0.45833 | 0.45833
321 | 1 | 60
321 | 2 | 60
321 | 3 | 60
321 | 4 | 60
321 | 5 | 60
321 | 6 | 60
321 | 7 | 60
321 | 8 | 61
321 | 9 | 62
321 | 10 | 63
321 | 11 | 65
321 | 12 | 65
321 | 13 | 66
321 | 14 | 67
321 | 15 | 67
321 | 16 | 65
321 | 17 | 61
321 | 18 | 54
321 | 19 | 52
321 | 20 | 50
321 | 21 | 53
321 | 22 | 51
321 | 23 | 48
321 | 24 | 46 | 59 | 6 | -6
322 | 1 | 50
322 | 2 | 52
322 | 3 | 56
322 | 4 | 54
322 | 5 | 57
322 | 6 | 57
322 | 7 | 61
322 | 8 | 63
322 | 9 | 64
322 | 10 | 66
322 | 11 | 68
322 | 12 | 69
322 | 13 | 68
322 | 14 | 70
322 | 15 | 70
322 | 16 | 69
322 | 17 | 66
322 | 18 | 65
322 | 19 | 65
322 | 20 | 64
322 | 21 | 63
322 | 22 | 63
322 | 23 | 62
322 | 24 | 61 | 62.625 | 2.375 | -2.375
323 | 1 | 60
323 | 2 | 59
323 | 3 | 58
323 | 4 | 58
323 | 5 | 59
323 | 6 | 58
323 | 7 | 58
323 | 8 | 60
323 | 9 | 61
323 | 10 | 63
323 | 11 | 67
323 | 12 | 70
323 | 13 | 69
323 | 14 | 69
323 | 15 | 68
323 | 16 | 66
323 | 17 | 63
323 | 18 | 57
323 | 19 | 55
323 | 20 | 56
323 | 21 | 57
323 | 22 | 58
323 | 23 | 56
323 | 24 | 57 | 60.9167 | 4.0833 | -4.0833
324 | 1 | 55
324 | 2 | 55
324 | 3 | 57
324 | 4 | 56
324 | 5 | 61
324 | 6 | 62
324 | 7 | 62
324 | 8 | 68
324 | 9 | 71
324 | 10 | 75
324 | 11 | 77
324 | 12 | 78
324 | 13 | 78
324 | 14 | 77
324 | 15 | 76
324 | 16 | 76
324 | 17 | 73
324 | 18 | 72
324 | 19 | 71
324 | 20 | 70
324 | 21 | 71
324 | 22 | 70
324 | 23 | 70
324 | 24 | 69 | 68.75 | -3.75 | 3.75
325 | 1 | 67
325 | 2 | 69
325 | 3 | 67
325 | 4 | 65
325 | 5 | 64
325 | 6 | 66
325 | 7 | 65
325 | 8 | 70
325 | 9 | 72
325 | 10 | 77
325 | 11 | 78
325 | 12 | 78
325 | 13 | 79
325 | 14 | 80
325 | 15 | 80
325 | 16 | 78
325 | 17 | 68
325 | 18 | 59
325 | 19 | 58
325 | 20 | 55
325 | 21 | 58
325 | 22 | 53
325 | 23 | 51
325 | 24 | 59 | 67.3333 | -2.3333 | 2.3333
326 | 1 | 60
326 | 2 | 60
326 | 3 | 60
326 | 4 | 58
326 | 5 | 58
326 | 6 | 58
326 | 7 | 57
326 | 8 | 60
326 | 9 | 62
326 | 10 | 64
326 | 11 | 67
326 | 12 | 71
326 | 13 | 71
326 | 14 | 71
326 | 15 | 71
326 | 16 | 71
326 | 17 | 66
326 | 18 | 56
326 | 19 | 54
326 | 20 | 63
326 | 21 | 64
326 | 22 | 62
326 | 23 | 62
326 | 24 | 61 | 62.7917 | 2.2083 | -2.2083
327 | 1 | 59
327 | 2 | 57
327 | 3 | 56
327 | 4 | 55
327 | 5 | 54
327 | 6 | 52
327 | 7 | 52
327 | 8 | 53
327 | 9 | 53
327 | 10 | 56
327 | 11 | 57
327 | 12 | 60
327 | 13 | 62
327 | 14 | 63
327 | 15 | 63
327 | 16 | 62
327 | 17 | 60
327 | 18 | 58
327 | 19 | 58
327 | 20 | 57
327 | 21 | 56
327 | 22 | 56
327 | 23 | 54
327 | 24 | 53 | 56.9167 | 8.0833 | -8.0833
328 | 1 | 52
328 | 2 | 52
328 | 3 | 52
328 | 4 | 52
328 | 5 | 51
328 | 6 | 50
328 | 7 | 50
328 | 8 | 50
328 | 9 | 50
328 | 10 | 52
328 | 11 | 52
328 | 12 | 53
328 | 13 | 53
328 | 14 | 54
328 | 15 | 54
328 | 16 | 54
328 | 17 | 52
328 | 18 | 51
328 | 19 | 52
328 | 20 | 53
328 | 21 | 52
328 | 22 | 50
328 | 23 | 48
328 | 24 | 49 | 51.5833 | 13.4167 | -13.4167
329 | 1 | 45
329 | 2 | 47
329 | 3 | 50
329 | 4 | 50
329 | 5 | 51
329 | 6 | 50
329 | 7 | 52
329 | 8 | 56
329 | 9 | 62
329 | 10 | 63
329 | 11 | 67
329 | 12 | 69
329 | 13 | 72
329 | 14 | 72
329 | 15 | 71
329 | 16 | 69
329 | 17 | 68
329 | 18 | 66
329 | 19 | 65
329 | 20 | 65
329 | 21 | 63
329 | 22 | 63
329 | 23 | 64
329 | 24 | 64 | 61 | 4 | -4
330 | 1 | 64
330 | 2 | 63
330 | 3 | 65
330 | 4 | 65
330 | 5 | 67
330 | 6 | 67
330 | 7 | 67
330 | 8 | 70
330 | 9 | 73
330 | 10 | 77
330 | 11 | 80
330 | 12 | 80
330 | 13 | 80
330 | 14 | 79
330 | 15 | 79
330 | 16 | 78
330 | 17 | 75
330 | 18 | 73
330 | 19 | 71
330 | 20 | 70
330 | 21 | 70
330 | 22 | 70
330 | 23 | 70
330 | 24 | 71 | 71.8333 | -6.8333 | 6.8333
331 | 1 | 72
331 | 2 | 72
331 | 3 | 72
331 | 4 | 72
331 | 5 | 72
331 | 6 | 71
331 | 7 | 71
331 | 8 | 72
331 | 9 | 76
331 | 10 | 78
331 | 11 | 79
331 | 12 | 79
331 | 13 | 80
331 | 14 | 80
331 | 15 | 80
331 | 16 | 79
331 | 17 | 76
331 | 18 | 75
331 | 19 | 75
331 | 20 | 74
331 | 21 | 74
331 | 22 | 74
331 | 23 | 74
331 | 24 | 75 | 75.0833 | -10.0833 | 10.0833
332 | 1 | 76
332 | 2 | 59
332 | 3 | 58
332 | 4 | 59
332 | 5 | 60
332 | 6 | 59
332 | 7 | 59
332 | 8 | 59
332 | 9 | 60
332 | 10 | 62
332 | 11 | 61
332 | 12 | 61
332 | 13 | 62
332 | 14 | 62
332 | 15 | 64
332 | 16 | 63
332 | 17 | 63
332 | 18 | 62
332 | 19 | 61
332 | 20 | 59
332 | 21 | 61
332 | 22 | 61
332 | 23 | 62
332 | 24 | 62 | 61.4583 | 3.5417 | -3.5417
333 | 1 | 62
333 | 2 | 57
333 | 3 | 58
333 | 4 | 57
333 | 5 | 55
333 | 6 | 55
333 | 7 | 54
333 | 8 | 54
333 | 9 | 54
333 | 10 | 54
333 | 11 | 54
333 | 12 | 55
333 | 13 | 56
333 | 14 | 56
333 | 15 | 57
333 | 16 | 57
333 | 17 | 55
333 | 18 | 56
333 | 19 | 55
333 | 20 | 54
333 | 21 | 55
333 | 22 | 54
333 | 23 | 54
333 | 24 | 54 | 55.5 | 9.5 | -9.5
334 | 1 | 55
334 | 2 | 54
334 | 3 | 54
334 | 4 | 55
334 | 5 | 55
334 | 6 | 54
334 | 7 | 54
334 | 8 | 53
334 | 9 | 54
334 | 10 | 57
334 | 11 | 59
334 | 12 | 60
334 | 13 | 61
334 | 14 | 62
334 | 15 | 60
334 | 16 | 60
334 | 17 | 58
334 | 18 | 58
334 | 19 | 57
334 | 20 | 56
334 | 21 | 53
334 | 22 | 54
334 | 23 | 55
334 | 24 | 56 | 56.4167 | 8.5833 | -8.5833
335 | 1 | 57
335 | 2 | 58
335 | 3 | 59
335 | 4 | 60
335 | 5 | 60
335 | 6 | 57
335 | 7 | 53
335 | 8 | 60
335 | 9 | 66
335 | 10 | 71
335 | 11 | 74
335 | 12 | 77
335 | 13 | 75
335 | 14 | 77
335 | 15 | 77
335 | 16 | 73
335 | 17 | 69
335 | 18 | 66
335 | 19 | 66
335 | 20 | 59
335 | 21 | 60
335 | 22 | 58
335 | 23 | 56
335 | 24 | 55 | 64.2917 | 0.70833 | -0.70833
336 | 1 | 54
336 | 2 | 54
336 | 3 | 54
336 | 4 | 54
336 | 5 | 53
336 | 6 | 51
336 | 7 | 50
336 | 8 | 51
336 | 9 | 57
336 | 10 | 59
336 | 11 | 60
336 | 12 | 62
336 | 13 | 63
336 | 14 | 64
336 | 15 | 64
336 | 16 | 63
336 | 17 | 58
336 | 18 | 55
336 | 19 | 50
336 | 20 | 47
336 | 21 | 47
336 | 22 | 44
336 | 23 | 44
336 | 24 | 45 | 54.2917 | 10.7083 | -10.7083
337 | 1 | 46
337 | 2 | 43
337 | 3 | 44
337 | 4 | 48
337 | 5 | 48
337 | 6 | 45
337 | 7 | 44
337 | 8 | 54
337 | 9 | 64
337 | 10 | 68
337 | 11 | 71
337 | 12 | 73
337 | 13 | 75
337 | 14 | 74
337 | 15 | 74
337 | 16 | 71
337 | 17 | 67
337 | 18 | 63
337 | 19 | 61
337 | 20 | 60
337 | 21 | 60
337 | 22 | 60
337 | 23 | 59
337 | 24 | 59 | 59.625 | 5.375 | -5.375
338 | 1 | 58
338 | 2 | 60
338 | 3 | 60
338 | 4 | 60
338 | 5 | 59
338 | 6 | 56
338 | 7 | 55
338 | 8 | 56
338 | 9 | 58
338 | 10 | 59
338 | 11 | 60
338 | 12 | 62
338 | 13 | 63
338 | 14 | 64
338 | 15 | 64
338 | 16 | 63
338 | 17 | 59
338 | 18 | 58
338 | 19 | 56
338 | 20 | 55
338 | 21 | 54
338 | 22 | 52
338 | 23 | 51
338 | 24 | 51 | 58.0417 | 6.9583 | -6.9583
339 | 1 | 50
339 | 2 | 50
339 | 3 | 49
339 | 4 | 49
339 | 5 | 48
339 | 6 | 49
339 | 7 | 49
339 | 8 | 50
339 | 9 | 53
339 | 10 | 55
339 | 11 | 56
339 | 12 | 56
339 | 13 | 56
339 | 14 | 57
339 | 15 | 59
339 | 16 | 58
339 | 17 | 54
339 | 18 | 48
339 | 19 | 44
339 | 20 | 44
339 | 21 | 45
339 | 22 | 46
339 | 23 | 47
339 | 24 | 44 | 50.6667 | 14.3333 | -14.3333
340 | 1 | 43
340 | 2 | 45
340 | 3 | 47
340 | 4 | 44
340 | 5 | 42
340 | 6 | 46
340 | 7 | 48
340 | 8 | 50
340 | 9 | 52
340 | 10 | 55
340 | 11 | 59
340 | 12 | 60
340 | 13 | 60
340 | 14 | 60
340 | 15 | 61
340 | 16 | 60
340 | 17 | 57
340 | 18 | 56
340 | 19 | 56
340 | 20 | 56
340 | 21 | 56
340 | 22 | 56
340 | 23 | 56
340 | 24 | 53 | 53.25 | 11.75 | -11.75
341 | 1 | 51
341 | 2 | 46
341 | 3 | 47
341 | 4 | 45
341 | 5 | 50
341 | 6 | 51
341 | 7 | 54
341 | 8 | 58
341 | 9 | 64
341 | 10 | 69
341 | 11 | 71
341 | 12 | 74
341 | 13 | 73
341 | 14 | 75
341 | 15 | 74
341 | 16 | 72
341 | 17 | 69
341 | 18 | 67
341 | 19 | 65
341 | 20 | 63
341 | 21 | 62
341 | 22 | 60
341 | 23 | 59
341 | 24 | 56 | 61.4583 | 3.5417 | -3.5417
342 | 1 | 54
342 | 2 | 57
342 | 3 | 56
342 | 4 | 56
342 | 5 | 57
342 | 6 | 56
342 | 7 | 55
342 | 8 | 60
342 | 9 | 64
342 | 10 | 67
342 | 11 | 73
342 | 12 | 73
342 | 13 | 75
342 | 14 | 76
342 | 15 | 77
342 | 16 | 75
342 | 17 | 68
342 | 18 | 61
342 | 19 | 60
342 | 20 | 64
342 | 21 | 62
342 | 22 | 62
342 | 23 | 62
342 | 24 | 60 | 63.75 | 1.25 | -1.25
343 | 1 | 59
343 | 2 | 57
343 | 3 | 56
343 | 4 | 55
343 | 5 | 54
343 | 6 | 53
343 | 7 | 51
343 | 8 | 53
343 | 9 | 56
343 | 10 | 58
343 | 11 | 59
343 | 12 | 60
343 | 13 | 61
343 | 14 | 63
343 | 15 | 65
343 | 16 | 64
343 | 17 | 57
343 | 18 | 51
343 | 19 | 46
343 | 20 | 45
343 | 21 | 44
343 | 22 | 42
343 | 23 | 50
343 | 24 | 52 | 54.625 | 10.375 | -10.375
344 | 1 | 51
344 | 2 | 52
344 | 3 | 51
344 | 4 | 50
344 | 5 | 49
344 | 6 | 48
344 | 7 | 48
344 | 8 | 50
344 | 9 | 51
344 | 10 | 53
344 | 11 | 54
344 | 12 | 54
344 | 13 | 55
344 | 14 | 58
344 | 15 | 58
344 | 16 | 58
344 | 17 | 54
344 | 18 | 46
344 | 19 | 47
344 | 20 | 48
344 | 21 | 45
344 | 22 | 43
344 | 23 | 45
344 | 24 | 44 | 50.5 | 14.5 | -14.5
345 | 1 | 42
345 | 2 | 42
345 | 3 | 40
345 | 4 | 43
345 | 5 | 45
345 | 6 | 48
345 | 7 | 49
345 | 8 | 50
345 | 9 | 56
345 | 10 | 58
345 | 11 | 60
345 | 12 | 63
345 | 13 | 63
345 | 14 | 63
345 | 15 | 63
345 | 16 | 62
345 | 17 | 61
345 | 18 | 59
345 | 19 | 60
345 | 20 | 60
345 | 21 | 61
345 | 22 | 60
345 | 23 | 60
345 | 24 | 61 | 55.375 | 9.625 | -9.625
346 | 1 | 62
346 | 2 | 62
346 | 3 | 62
346 | 4 | 62
346 | 5 | 63
346 | 6 | 63
346 | 7 | 63
346 | 8 | 57
346 | 9 | 54
346 | 10 | 53
346 | 11 | 51
346 | 12 | 50
346 | 13 | 49
346 | 14 | 50
346 | 15 | 50
346 | 16 | 50
346 | 17 | 50
346 | 18 | 50
346 | 19 | 50
346 | 20 | 50
346 | 21 | 49
346 | 22 | 49
346 | 23 | 49
346 | 24 | 49 | 54.0417 | 10.9583 | -10.9583
347 | 1 | 49
347 | 2 | 49
347 | 3 | 49
347 | 4 | 49
347 | 5 | 49
347 | 6 | 49
347 | 7 | 49
347 | 8 | 49
347 | 9 | 50
347 | 10 | 50
347 | 11 | 51
347 | 12 | 51
347 | 13 | 54
347 | 14 | 54
347 | 15 | 56
347 | 16 | 57
347 | 17 | 55
347 | 18 | 54
347 | 19 | 54
347 | 20 | 55
347 | 21 | 55
347 | 22 | 56
347 | 23 | 57
347 | 24 | 57 | 52.4167 | 12.5833 | -12.5833
348 | 1 | 58
348 | 2 | 60
348 | 3 | 61
348 | 4 | 61
348 | 5 | 60
348 | 6 | 63
348 | 7 | 56
348 | 8 | 56
348 | 9 | 57
348 | 10 | 58
348 | 11 | 59
348 | 12 | 57
348 | 13 | 54
348 | 14 | 52
348 | 15 | 51
348 | 16 | 50
348 | 17 | 50
348 | 18 | 50
348 | 19 | 51
348 | 20 | 50
348 | 21 | 49
348 | 22 | 49
348 | 23 | 47
348 | 24 | 47 | 54.4167 | 10.5833 | -10.5833
349 | 1 | 47
349 | 2 | 46
349 | 3 | 45
349 | 4 | 45
349 | 5 | 45
349 | 6 | 45
349 | 7 | 44
349 | 8 | 44
349 | 9 | 46
349 | 10 | 48
349 | 11 | 49
349 | 12 | 51
349 | 13 | 54
349 | 14 | 56
349 | 15 | 56
349 | 16 | 56
349 | 17 | 52
349 | 18 | 51
349 | 19 | 45
349 | 20 | 40
349 | 21 | 41
349 | 22 | 41
349 | 23 | 38
349 | 24 | 45 | 47.0833 | 17.9167 | -17.9167
350 | 1 | 39
350 | 2 | 38
350 | 3 | 38
350 | 4 | 39
350 | 5 | 39
350 | 6 | 40
350 | 7 | 40
350 | 8 | 47
350 | 9 | 54
350 | 10 | 58
350 | 11 | 62
350 | 12 | 64
350 | 13 | 64
350 | 14 | 65
350 | 15 | 65
350 | 16 | 65
350 | 17 | 62
350 | 18 | 58
350 | 19 | 56
350 | 20 | 55
350 | 21 | 53
350 | 22 | 53
350 | 23 | 54
350 | 24 | 54 | 52.5833 | 12.4167 | -12.4167
351 | 1 | 53
351 | 2 | 54
351 | 3 | 57
351 | 4 | 59
351 | 5 | 61
351 | 6 | 60
351 | 7 | 60
351 | 8 | 63
351 | 9 | 67
351 | 10 | 71
351 | 11 | 73
351 | 12 | 75
351 | 13 | 60
351 | 14 | 58
351 | 15 | 57
351 | 16 | 53
351 | 17 | 50
351 | 18 | 50
351 | 19 | 49
351 | 20 | 48
351 | 21 | 47
351 | 22 | 45
351 | 23 | 44
351 | 24 | 43 | 56.5417 | 8.4583 | -8.4583
352 | 1 | 42
352 | 2 | 42
352 | 3 | 41
352 | 4 | 40
352 | 5 | 39
352 | 6 | 38
352 | 7 | 37
352 | 8 | 38
352 | 9 | 38
352 | 10 | 39
352 | 11 | 41
352 | 12 | 43
352 | 13 | 44
352 | 14 | 45
352 | 15 | 46
352 | 16 | 45
352 | 17 | 42
352 | 18 | 40
352 | 19 | 38
352 | 20 | 37
352 | 21 | 36
352 | 22 | 35
352 | 23 | 33
352 | 24 | 32 | 39.625 | 25.375 | -25.375
353 | 1 | 31
353 | 2 | 30
353 | 3 | 30
353 | 4 | 29
353 | 5 | 28
353 | 6 | 28
353 | 7 | 27
353 | 8 | 29
353 | 9 | 31
353 | 10 | 32
353 | 11 | 34
353 | 12 | 36
353 | 13 | 35
353 | 14 | 38
353 | 15 | 38
353 | 16 | 38
353 | 17 | 35
353 | 18 | 33
353 | 19 | 33
353 | 20 | 37
353 | 21 | 38
353 | 22 | 38
353 | 23 | 37
353 | 24 | 33 | 33.25 | 31.75 | -31.75
354 | 1 | 33
354 | 2 | 31
354 | 3 | 35
354 | 4 | 36
354 | 5 | 36
354 | 6 | 36
354 | 7 | 36
354 | 8 | 37
354 | 9 | 38
354 | 10 | 40
354 | 11 | 46
354 | 12 | 45
354 | 13 | 46
354 | 14 | 47
354 | 15 | 48
354 | 16 | 48
354 | 17 | 46
354 | 18 | 46
354 | 19 | 46
354 | 20 | 46
354 | 21 | 49
354 | 22 | 51
354 | 23 | 52
354 | 24 | 51 | 42.7083 | 22.2917 | -22.2917
355 | 1 | 53
355 | 2 | 53
355 | 3 | 52
355 | 4 | 53
355 | 5 | 54
355 | 6 | 55
355 | 7 | 56
355 | 8 | 60
355 | 9 | 63
355 | 10 | 65
355 | 11 | 67
355 | 12 | 69
355 | 13 | 72
355 | 14 | 72
355 | 15 | 71
355 | 16 | 70
355 | 17 | 69
355 | 18 | 66
355 | 19 | 64
355 | 20 | 63
355 | 21 | 63
355 | 22 | 63
355 | 23 | 63
355 | 24 | 64 | 62.5 | 2.5 | -2.5
356 | 1 | 64
356 | 2 | 64
356 | 3 | 63
356 | 4 | 63
356 | 5 | 64
356 | 6 | 65
356 | 7 | 67
356 | 8 | 68
356 | 9 | 68
356 | 10 | 71
356 | 11 | 72
356 | 12 | 73
356 | 13 | 73
356 | 14 | 75
356 | 15 | 74
356 | 16 | 73
356 | 17 | 72
356 | 18 | 70
356 | 19 | 69
356 | 20 | 69
356 | 21 | 68
356 | 22 | 67
356 | 23 | 67
356 | 24 | 68 | 68.625 | -3.625 | 3.625
357 | 1 | 68
357 | 2 | 67
357 | 3 | 58
357 | 4 | 56
357 | 5 | 55
357 | 6 | 55
357 | 7 | 54
357 | 8 | 53
357 | 9 | 54
357 | 10 | 55
357 | 11 | 55
357 | 12 | 58
357 | 13 | 58
357 | 14 | 59
357 | 15 | 60
357 | 16 | 57
357 | 17 | 56
357 | 18 | 54
357 | 19 | 52
357 | 20 | 50
357 | 21 | 49
357 | 22 | 48
357 | 23 | 47
357 | 24 | 47 | 55.2083 | 9.7917 | -9.7917
358 | 1 | 47
358 | 2 | 46
358 | 3 | 46
358 | 4 | 46
358 | 5 | 46
358 | 6 | 46
358 | 7 | 45
358 | 8 | 45
358 | 9 | 46
358 | 10 | 46
358 | 11 | 47
358 | 12 | 47
358 | 13 | 46
358 | 14 | 47
358 | 15 | 47
358 | 16 | 46
358 | 17 | 45
358 | 18 | 46
358 | 19 | 46
358 | 20 | 45
358 | 21 | 45
358 | 22 | 45
358 | 23 | 45
358 | 24 | 45 | 45.875 | 19.125 | -19.125
359 | 1 | 45
359 | 2 | 45
359 | 3 | 45
359 | 4 | 46
359 | 5 | 46
359 | 6 | 46
359 | 7 | 46
359 | 8 | 46
359 | 9 | 47
359 | 10 | 48
359 | 11 | 49
359 | 12 | 49
359 | 13 | 51
359 | 14 | 52
359 | 15 | 51
359 | 16 | 51
359 | 17 | 49
359 | 18 | 48
359 | 19 | 46
359 | 20 | 44
359 | 21 | 44
359 | 22 | 44
359 | 23 | 47
359 | 24 | 48 | 47.2083 | 17.7917 | -17.7917
360 | 1 | 48
360 | 2 | 49
360 | 3 | 49
360 | 4 | 49
360 | 5 | 49
360 | 6 | 44
360 | 7 | 43
360 | 8 | 44
360 | 9 | 53
360 | 10 | 59
360 | 11 | 61
360 | 12 | 63
360 | 13 | 62
360 | 14 | 63
360 | 15 | 67
360 | 16 | 66
360 | 17 | 64
360 | 18 | 63
360 | 19 | 63
360 | 20 | 62
360 | 21 | 62
360 | 22 | 62
360 | 23 | 62
360 | 24 | 63 | 57.0833 | 7.9167 | -7.9167
361 | 1 | 62
361 | 2 | 58
361 | 3 | 58
361 | 4 | 56
361 | 5 | 52
361 | 6 | 49
361 | 7 | 41
361 | 8 | 47
361 | 9 | 54
361 | 10 | 58
361 | 11 | 59
361 | 12 | 62
361 | 13 | 64
361 | 14 | 64
361 | 15 | 66
361 | 16 | 65
361 | 17 | 63
361 | 18 | 60
361 | 19 | 57
361 | 20 | 59
361 | 21 | 57
361 | 22 | 58
361 | 23 | 60
361 | 24 | 61 | 57.9167 | 7.0833 | -7.0833
362 | 1 | 62
362 | 2 | 63
362 | 3 | 66
362 | 4 | 65
362 | 5 | 65
362 | 6 | 66
362 | 7 | 66
362 | 8 | 66
362 | 9 | 69
362 | 10 | 71
362 | 11 | 73
362 | 12 | 75
362 | 13 | 80
362 | 14 | 81
362 | 15 | 70
362 | 16 | 69
362 | 17 | 67
362 | 18 | 66
362 | 19 | 66
362 | 20 | 65
362 | 21 | 64
362 | 22 | 64
362 | 23 | 63
362 | 24 | 61 | 67.625 | -2.625 | 2.625
363 | 1 | 60
363 | 2 | 58
363 | 3 | 57
363 | 4 | 56
363 | 5 | 55
363 | 6 | 55
363 | 7 | 53
363 | 8 | 51
363 | 9 | 51
363 | 10 | 51
363 | 11 | 52
363 | 12 | 52
363 | 13 | 52
363 | 14 | 51
363 | 15 | 52
363 | 16 | 52
363 | 17 | 52
363 | 18 | 52
363 | 19 | 53
363 | 20 | 53
363 | 21 | 54
363 | 22 | 53
363 | 23 | 53
363 | 24 | 53 | 53.375 | 11.625 | -11.625
364 | 1 | 52
364 | 2 | 50
364 | 3 | 50
364 | 4 | 49
364 | 5 | 49
364 | 6 | 49
364 | 7 | 50
364 | 8 | 49
364 | 9 | 50
364 | 10 | 50
364 | 11 | 51
364 | 12 | 53
364 | 13 | 53
364 | 14 | 53
364 | 15 | 54
364 | 16 | 55
364 | 17 | 54
364 | 18 | 53
364 | 19 | 54
364 | 20 | 54
364 | 21 | 55
364 | 22 | 55
364 | 23 | 55
364 | 24 | 56 | 52.2083 | 12.7917 | -12.7917
365 | 1 | 58
365 | 2 | 60
365 | 3 | 61
365 | 4 | 61
365 | 5 | 64
365 | 6 | 57
365 | 7 | 54
365 | 8 | 55
365 | 9 | 60
365 | 10 | 65
365 | 11 | 67
365 | 12 | 72
365 | 13 | 73
365 | 14 | 75
365 | 15 | 76
365 | 16 | 73
365 | 17 | 69
365 | 18 | 67
365 | 19 | 64
365 | 20 | 63
365 | 21 | 62
365 | 22 | 61
365 | 23 | 61
365 | 24 | 58 | 64 | 1 | -1

## New Orleans EGUSA TMY2
|  |  |  | Annual | Annual
|  |  |  | 1446 | 2484.875
Julian Date | Hour | Dry Bulb | Avg daily Temp | HDD | CDD
1 | 1 | 39 |  |  |  |  | #days | Joule # | Row # | HDD | CDD
1 | 2 | 38 |  |  |  | Jan | 31 | 1 | 4 | 362.7917 | 20.0833
1 | 3 | 38 | [5 empty] | 31 | 751
1 | 4 | 36 |  |  |  | Feb | 28 | 32 | 771 | 350.7917 | 3.2083
1 | 5 | 35 | [5 empty] | 59 | 1419
1 | 6 | 33 |  |  |  | Mar | 31 | 60 | 1443 | 188.9583 | 31.7917
1 | 7 | 33 | [5 empty] | 90 | 2163
1 | 8 | 35 |  |  |  | Apr | 30 | 91 | 2187 | 21.0833 | 131.4167
1 | 9 | 38 | [5 empty] | 120 | 2883
1 | 10 | 40 |  |  |  | May | 31 | 121 | 2931 | 0 | 300.625
1 | 11 | 41 | [5 empty] | 151 | 3627
1 | 12 | 42 |  |  |  | Jun | 30 | 152 | 3651 | 0 | 451.2083
1 | 13 | 45 | [5 empty] | 181 | 4347
1 | 14 | 45 |  |  |  | Jul | 31 | 182 | 4371 | 0 | 514.9167
1 | 15 | 46 | [5 empty] | 212 | 5091
1 | 16 | 46 |  |  |  | Aug | 31 | 213 | 5115 | 0 | 464.2917
1 | 17 | 43 | [5 empty] | 243 | 5835
1 | 18 | 43 |  |  |  | Sep | 30 | 244 | 5859 | 0 | 363.5417
1 | 19 | 46 | [5 empty] | 273 | 6555
1 | 20 | 44 |  |  |  | Oct | 31 | 274 | 6579 | 41.125 | 137.8333
1 | 21 | 45 | [5 empty] | 304 | 7299
1 | 22 | 45 |  |  |  | Nov | 30 | 305 | 7323 | 150.4583 | 47.9583
1 | 23 | 45 | [5 empty] | 334 | 8019
1 | 24 | 45 | 41.0833 | 23.9167 | -23.9167 | Dec | 31 | 335 | 8043 | 330.7917 | 6.25
2 | 1 | 45 |  |  |  |  | 365 | 365 | 8763
2 | 2 | 44
2 | 3 | 43 |  |  |  | Total |  |  |  | 1446 | 2473.125
2 | 4 | 43
2 | 5 | 42
2 | 6 | 43
2 | 7 | 43
2 | 8 | 45
2 | 9 | 47
2 | 10 | 48
2 | 11 | 50
2 | 12 | 52
2 | 13 | 52
2 | 14 | 51
2 | 15 | 49
2 | 16 | 48
2 | 17 | 48
2 | 18 | 47
2 | 19 | 47
2 | 20 | 47
2 | 21 | 46
2 | 22 | 46
2 | 23 | 47
2 | 24 | 47 | 46.6667 | 18.3333 | -18.3333
3 | 1 | 48
3 | 2 | 49
3 | 3 | 50
3 | 4 | 50
3 | 5 | 50
3 | 6 | 50
3 | 7 | 51
3 | 8 | 51
3 | 9 | 53
3 | 10 | 54
3 | 11 | 56
3 | 12 | 57
3 | 13 | 57
3 | 14 | 58
3 | 15 | 59
3 | 16 | 58
3 | 17 | 57
3 | 18 | 56
3 | 19 | 56
3 | 20 | 51
3 | 21 | 49
3 | 22 | 48
3 | 23 | 47
3 | 24 | 47 | 52.5833 | 12.4167 | -12.4167
4 | 1 | 46
4 | 2 | 45
4 | 3 | 43
4 | 4 | 42
4 | 5 | 41
4 | 6 | 40
4 | 7 | 38
4 | 8 | 36
4 | 9 | 37
4 | 10 | 38
4 | 11 | 38
4 | 12 | 38
4 | 13 | 41
4 | 14 | 40
4 | 15 | 42
4 | 16 | 40
4 | 17 | 39
4 | 18 | 37
4 | 19 | 37
4 | 20 | 36
4 | 21 | 35
4 | 22 | 33
4 | 23 | 33
4 | 24 | 32 | 38.625 | 26.375 | -26.375
5 | 1 | 31
5 | 2 | 30
5 | 3 | 29
5 | 4 | 28
5 | 5 | 28
5 | 6 | 27
5 | 7 | 27
5 | 8 | 28
5 | 9 | 32
5 | 10 | 35
5 | 11 | 37
5 | 12 | 40
5 | 13 | 44
5 | 14 | 44
5 | 15 | 44
5 | 16 | 45
5 | 17 | 41
5 | 18 | 38
5 | 19 | 34
5 | 20 | 29
5 | 21 | 32
5 | 22 | 34
5 | 23 | 33
5 | 24 | 33 | 34.2917 | 30.7083 | -30.7083
6 | 1 | 26
6 | 2 | 28
6 | 3 | 26
6 | 4 | 25
6 | 5 | 24
6 | 6 | 25
6 | 7 | 30
6 | 8 | 36
6 | 9 | 44
6 | 10 | 49
6 | 11 | 53
6 | 12 | 57
6 | 13 | 62
6 | 14 | 63
6 | 15 | 64
6 | 16 | 63
6 | 17 | 60
6 | 18 | 56
6 | 19 | 49
6 | 20 | 50
6 | 21 | 48
6 | 22 | 48
6 | 23 | 46
6 | 24 | 44 | 44.8333 | 20.1667 | -20.1667
7 | 1 | 45
7 | 2 | 45
7 | 3 | 46
7 | 4 | 47
7 | 5 | 41
7 | 6 | 37
7 | 7 | 37
7 | 8 | 39
7 | 9 | 51
7 | 10 | 55
7 | 11 | 57
7 | 12 | 62
7 | 13 | 63
7 | 14 | 61
7 | 15 | 62
7 | 16 | 61
7 | 17 | 56
7 | 18 | 53
7 | 19 | 54
7 | 20 | 55
7 | 21 | 54
7 | 22 | 55
7 | 23 | 54
7 | 24 | 53 | 51.7917 | 13.2083 | -13.2083
8 | 1 | 55
8 | 2 | 56
8 | 3 | 58
8 | 4 | 57
8 | 5 | 57
8 | 6 | 57
8 | 7 | 58
8 | 8 | 61
8 | 9 | 63
8 | 10 | 65
8 | 11 | 68
8 | 12 | 70
8 | 13 | 72
8 | 14 | 72
8 | 15 | 72
8 | 16 | 70
8 | 17 | 67
8 | 18 | 65
8 | 19 | 62
8 | 20 | 61
8 | 21 | 60
8 | 22 | 60
8 | 23 | 61
8 | 24 | 62 | 62.875 | 2.125 | -2.125
9 | 1 | 63
9 | 2 | 62
9 | 3 | 62
9 | 4 | 62
9 | 5 | 62
9 | 6 | 60
9 | 7 | 61
9 | 8 | 62
9 | 9 | 66
9 | 10 | 73
9 | 11 | 74
9 | 12 | 77
9 | 13 | 62
9 | 14 | 55
9 | 15 | 53
9 | 16 | 53
9 | 17 | 50
9 | 18 | 50
9 | 19 | 48
9 | 20 | 47
9 | 21 | 47
9 | 22 | 45
9 | 23 | 43
9 | 24 | 42 | 57.4583 | 7.5417 | -7.5417
10 | 1 | 41
10 | 2 | 39
10 | 3 | 39
10 | 4 | 36
10 | 5 | 36
10 | 6 | 34
10 | 7 | 33
10 | 8 | 34
10 | 9 | 36
10 | 10 | 39
10 | 11 | 42
10 | 12 | 43
10 | 13 | 46
10 | 14 | 46
10 | 15 | 46
10 | 16 | 47
10 | 17 | 43
10 | 18 | 42
10 | 19 | 42
10 | 20 | 42
10 | 21 | 42
10 | 22 | 41
10 | 23 | 39
10 | 24 | 38 | 40.25 | 24.75 | -24.75
11 | 1 | 38
11 | 2 | 38
11 | 3 | 38
11 | 4 | 38
11 | 5 | 38
11 | 6 | 38
11 | 7 | 37
11 | 8 | 37
11 | 9 | 37
11 | 10 | 38
11 | 11 | 40
11 | 12 | 43
11 | 13 | 43
11 | 14 | 46
11 | 15 | 48
11 | 16 | 46
11 | 17 | 45
11 | 18 | 41
11 | 19 | 40
11 | 20 | 39
11 | 21 | 41
11 | 22 | 42
11 | 23 | 41
11 | 24 | 41 | 40.5417 | 24.4583 | -24.4583
12 | 1 | 40
12 | 2 | 39
12 | 3 | 38
12 | 4 | 37
12 | 5 | 37
12 | 6 | 35
12 | 7 | 35
12 | 8 | 39
12 | 9 | 40
12 | 10 | 42
12 | 11 | 45
12 | 12 | 47
12 | 13 | 49
12 | 14 | 50
12 | 15 | 50
12 | 16 | 48
12 | 17 | 46
12 | 18 | 43
12 | 19 | 32
12 | 20 | 32
12 | 21 | 30
12 | 22 | 32
12 | 23 | 27
12 | 24 | 30 | 39.2917 | 25.7083 | -25.7083
13 | 1 | 28
13 | 2 | 28
13 | 3 | 30
13 | 4 | 33
13 | 5 | 35
13 | 6 | 33
13 | 7 | 36
13 | 8 | 36
13 | 9 | 47
13 | 10 | 50
13 | 11 | 54
13 | 12 | 56
13 | 13 | 58
13 | 14 | 60
13 | 15 | 60
13 | 16 | 59
13 | 17 | 53
13 | 18 | 48
13 | 19 | 46
13 | 20 | 46
13 | 21 | 45
13 | 22 | 41
13 | 23 | 37
13 | 24 | 35 | 43.9167 | 21.0833 | -21.0833
14 | 1 | 35
14 | 2 | 35
14 | 3 | 35
14 | 4 | 35
14 | 5 | 32
14 | 6 | 37
14 | 7 | 37
14 | 8 | 39
14 | 9 | 48
14 | 10 | 56
14 | 11 | 59
14 | 12 | 59
14 | 13 | 61
14 | 14 | 61
14 | 15 | 61
14 | 16 | 60
14 | 17 | 56
14 | 18 | 52
14 | 19 | 46
14 | 20 | 44
14 | 21 | 43
14 | 22 | 44
14 | 23 | 43
14 | 24 | 44 | 46.75 | 18.25 | -18.25
15 | 1 | 45
15 | 2 | 46
15 | 3 | 46
15 | 4 | 46
15 | 5 | 44
15 | 6 | 43
15 | 7 | 42
15 | 8 | 45
15 | 9 | 53
15 | 10 | 59
15 | 11 | 64
15 | 12 | 64
15 | 13 | 65
15 | 14 | 65
15 | 15 | 65
15 | 16 | 65
15 | 17 | 60
15 | 18 | 57
15 | 19 | 54
15 | 20 | 54
15 | 21 | 54
15 | 22 | 54
15 | 23 | 53
15 | 24 | 53 | 54 | 11 | -11
16 | 1 | 51
16 | 2 | 50
16 | 3 | 51
16 | 4 | 54
16 | 5 | 54
16 | 6 | 53
16 | 7 | 54
16 | 8 | 58
16 | 9 | 60
16 | 10 | 66
16 | 11 | 69
16 | 12 | 68
16 | 13 | 68
16 | 14 | 63
16 | 15 | 60
16 | 16 | 62
16 | 17 | 63
16 | 18 | 63
16 | 19 | 64
16 | 20 | 65
16 | 21 | 64
16 | 22 | 64
16 | 23 | 64
16 | 24 | 63 | 60.4583 | 4.5417 | -4.5417
17 | 1 | 63
17 | 2 | 63
17 | 3 | 62
17 | 4 | 63
17 | 5 | 64
17 | 6 | 63
17 | 7 | 63
17 | 8 | 63
17 | 9 | 64
17 | 10 | 64
17 | 11 | 65
17 | 12 | 65
17 | 13 | 64
17 | 14 | 65
17 | 15 | 65
17 | 16 | 65
17 | 17 | 64
17 | 18 | 63
17 | 19 | 63
17 | 20 | 63
17 | 21 | 62
17 | 22 | 62
17 | 23 | 61
17 | 24 | 61 | 63.3333 | 1.6667 | -1.6667
18 | 1 | 60
18 | 2 | 60
18 | 3 | 60
18 | 4 | 60
18 | 5 | 60
18 | 6 | 60
18 | 7 | 58
18 | 8 | 57
18 | 9 | 59
18 | 10 | 60
18 | 11 | 59
18 | 12 | 60
18 | 13 | 62
18 | 14 | 61
18 | 15 | 61
18 | 16 | 62
18 | 17 | 61
18 | 18 | 61
18 | 19 | 60
18 | 20 | 60
18 | 21 | 60
18 | 22 | 60
18 | 23 | 61
18 | 24 | 60 | 60.0833 | 4.9167 | -4.9167
19 | 1 | 59
19 | 2 | 60
19 | 3 | 60
19 | 4 | 60
19 | 5 | 59
19 | 6 | 58
19 | 7 | 57
19 | 8 | 59
19 | 9 | 61
19 | 10 | 62
19 | 11 | 63
19 | 12 | 65
19 | 13 | 66
19 | 14 | 65
19 | 15 | 65
19 | 16 | 63
19 | 17 | 61
19 | 18 | 59
19 | 19 | 58
19 | 20 | 57
19 | 21 | 56
19 | 22 | 54
19 | 23 | 53
19 | 24 | 52 | 59.6667 | 5.3333 | -5.3333
20 | 1 | 51
20 | 2 | 50
20 | 3 | 50
20 | 4 | 50
20 | 5 | 50
20 | 6 | 50
20 | 7 | 50
20 | 8 | 50
20 | 9 | 50
20 | 10 | 50
20 | 11 | 51
20 | 12 | 51
20 | 13 | 53
20 | 14 | 53
20 | 15 | 54
20 | 16 | 53
20 | 17 | 53
20 | 18 | 52
20 | 19 | 49
20 | 20 | 49
20 | 21 | 49
20 | 22 | 49
20 | 23 | 48
20 | 24 | 45 | 50.4167 | 14.5833 | -14.5833
21 | 1 | 47
21 | 2 | 50
21 | 3 | 50
21 | 4 | 50
21 | 5 | 50
21 | 6 | 50
21 | 7 | 50
21 | 8 | 51
21 | 9 | 52
21 | 10 | 53
21 | 11 | 54
21 | 12 | 59
21 | 13 | 61
21 | 14 | 64
21 | 15 | 64
21 | 16 | 64
21 | 17 | 62
21 | 18 | 60
21 | 19 | 59
21 | 20 | 57
21 | 21 | 57
21 | 22 | 57
21 | 23 | 58
21 | 24 | 58 | 55.7083 | 9.2917 | -9.2917
22 | 1 | 57
22 | 2 | 55
22 | 3 | 56
22 | 4 | 57
22 | 5 | 57
22 | 6 | 57
22 | 7 | 57
22 | 8 | 58
22 | 9 | 58
22 | 10 | 60
22 | 11 | 63
22 | 12 | 66
22 | 13 | 69
22 | 14 | 71
22 | 15 | 72
22 | 16 | 73
22 | 17 | 70
22 | 18 | 67
22 | 19 | 66
22 | 20 | 65
22 | 21 | 65
22 | 22 | 64
22 | 23 | 64
22 | 24 | 64 | 62.9583 | 2.0417 | -2.0417
23 | 1 | 64
23 | 2 | 64
23 | 3 | 65
23 | 4 | 65
23 | 5 | 65
23 | 6 | 66
23 | 7 | 66
23 | 8 | 67
23 | 9 | 70
23 | 10 | 73
23 | 11 | 75
23 | 12 | 75
23 | 13 | 76
23 | 14 | 78
23 | 15 | 77
23 | 16 | 76
23 | 17 | 72
23 | 18 | 68
23 | 19 | 66
23 | 20 | 65
23 | 21 | 64
23 | 22 | 65
23 | 23 | 65
23 | 24 | 63 | 68.75 | -3.75 | 3.75
24 | 1 | 61
24 | 2 | 63
24 | 3 | 62
24 | 4 | 62
24 | 5 | 62
24 | 6 | 63
24 | 7 | 63
24 | 8 | 61
24 | 9 | 60
24 | 10 | 58
24 | 11 | 58
24 | 12 | 55
24 | 13 | 59
24 | 14 | 57
24 | 15 | 57
24 | 16 | 58
24 | 17 | 57
24 | 18 | 53
24 | 19 | 53
24 | 20 | 52
24 | 21 | 51
24 | 22 | 49
24 | 23 | 47
24 | 24 | 46 | 56.9583 | 8.0417 | -8.0417
25 | 1 | 46
25 | 2 | 46
25 | 3 | 45
25 | 4 | 45
25 | 5 | 45
25 | 6 | 45
25 | 7 | 43
25 | 8 | 44
25 | 9 | 46
25 | 10 | 50
25 | 11 | 51
25 | 12 | 52
25 | 13 | 54
25 | 14 | 57
25 | 15 | 57
25 | 16 | 58
25 | 17 | 56
25 | 18 | 51
25 | 19 | 52
25 | 20 | 50
25 | 21 | 49
25 | 22 | 47
25 | 23 | 47
25 | 24 | 47 | 49.2917 | 15.7083 | -15.7083
26 | 1 | 46
26 | 2 | 45
26 | 3 | 46
26 | 4 | 45
26 | 5 | 44
26 | 6 | 44
26 | 7 | 43
26 | 8 | 44
26 | 9 | 47
26 | 10 | 48
26 | 11 | 52
26 | 12 | 52
26 | 13 | 56
26 | 14 | 60
26 | 15 | 59
26 | 16 | 56
26 | 17 | 54
26 | 18 | 52
26 | 19 | 52
26 | 20 | 53
26 | 21 | 53
26 | 22 | 54
26 | 23 | 54
26 | 24 | 54 | 50.5417 | 14.4583 | -14.4583
27 | 1 | 55
27 | 2 | 55
27 | 3 | 55
27 | 4 | 53
27 | 5 | 52
27 | 6 | 52
27 | 7 | 52
27 | 8 | 56
27 | 9 | 64
27 | 10 | 68
27 | 11 | 72
27 | 12 | 74
27 | 13 | 74
27 | 14 | 75
27 | 15 | 74
27 | 16 | 72
27 | 17 | 70
27 | 18 | 66
27 | 19 | 61
27 | 20 | 61
27 | 21 | 61
27 | 22 | 62
27 | 23 | 62
27 | 24 | 62 | 62.8333 | 2.1667 | -2.1667
28 | 1 | 63
28 | 2 | 63
28 | 3 | 63
28 | 4 | 64
28 | 5 | 64
28 | 6 | 64
28 | 7 | 64
28 | 8 | 65
28 | 9 | 67
28 | 10 | 74
28 | 11 | 72
28 | 12 | 75
28 | 13 | 77
28 | 14 | 76
28 | 15 | 76
28 | 16 | 75
28 | 17 | 72
28 | 18 | 71
28 | 19 | 69
28 | 20 | 69
28 | 21 | 69
28 | 22 | 68
28 | 23 | 68
28 | 24 | 68 | 69 | -4 | 4
29 | 1 | 69
29 | 2 | 68
29 | 3 | 67
29 | 4 | 66
29 | 5 | 65
29 | 6 | 65
29 | 7 | 65
29 | 8 | 66
29 | 9 | 68
29 | 10 | 70
29 | 11 | 73
29 | 12 | 74
29 | 13 | 75
29 | 14 | 78
29 | 15 | 77
29 | 16 | 75
29 | 17 | 73
29 | 18 | 70
29 | 19 | 67
29 | 20 | 67
29 | 21 | 66
29 | 22 | 67
29 | 23 | 67
29 | 24 | 66 | 69.3333 | -4.3333 | 4.3333
30 | 1 | 67
30 | 2 | 67
30 | 3 | 67
30 | 4 | 67
30 | 5 | 68
30 | 6 | 68
30 | 7 | 67
30 | 8 | 67
30 | 9 | 68
30 | 10 | 70
30 | 11 | 74
30 | 12 | 77
30 | 13 | 77
30 | 14 | 78
30 | 15 | 77
30 | 16 | 78
30 | 17 | 75
30 | 18 | 72
30 | 19 | 70
30 | 20 | 68
30 | 21 | 68
30 | 22 | 67
30 | 23 | 63
30 | 24 | 62 | 70.0833 | -5.0833 | 5.0833
31 | 1 | 62
31 | 2 | 61
31 | 3 | 61
31 | 4 | 61
31 | 5 | 61
31 | 6 | 63
31 | 7 | 62
31 | 8 | 64
31 | 9 | 67
31 | 10 | 72
31 | 11 | 74
31 | 12 | 76
31 | 13 | 75
31 | 14 | 77
31 | 15 | 75
31 | 16 | 74
31 | 17 | 72
31 | 18 | 70
31 | 19 | 69
31 | 20 | 67
31 | 21 | 67
31 | 22 | 67
31 | 23 | 67
31 | 24 | 66 | 67.9167 | -2.9167 | 2.9167
32 | 1 | 66
32 | 2 | 66
32 | 3 | 66
32 | 4 | 66
32 | 5 | 66
32 | 6 | 66
32 | 7 | 67
32 | 8 | 67
32 | 9 | 68
32 | 10 | 69
32 | 11 | 71
32 | 12 | 72
32 | 13 | 71
32 | 14 | 71
32 | 15 | 70
32 | 16 | 68
32 | 17 | 67
32 | 18 | 65
32 | 19 | 64
32 | 20 | 64
32 | 21 | 63
32 | 22 | 62
32 | 23 | 61
32 | 24 | 60 | 66.5 | -1.5 | 1.5
33 | 1 | 58
33 | 2 | 57
33 | 3 | 55
33 | 4 | 53
33 | 5 | 52
33 | 6 | 50
33 | 7 | 51
33 | 8 | 52
33 | 9 | 53
33 | 10 | 56
33 | 11 | 59
33 | 12 | 62
33 | 13 | 62
33 | 14 | 63
33 | 15 | 63
33 | 16 | 61
33 | 17 | 59
33 | 18 | 57
33 | 19 | 54
33 | 20 | 51
33 | 21 | 48
33 | 22 | 47
33 | 23 | 47
33 | 24 | 46 | 54.8333 | 10.1667 | -10.1667
34 | 1 | 46
34 | 2 | 47
34 | 3 | 47
34 | 4 | 47
34 | 5 | 46
34 | 6 | 46
34 | 7 | 48
34 | 8 | 50
34 | 9 | 52
34 | 10 | 54
34 | 11 | 56
34 | 12 | 58
34 | 13 | 60
34 | 14 | 62
34 | 15 | 64
34 | 16 | 62
34 | 17 | 61
34 | 18 | 59
34 | 19 | 54
34 | 20 | 50
34 | 21 | 45
34 | 22 | 44
34 | 23 | 43
34 | 24 | 42 | 51.7917 | 13.2083 | -13.2083
35 | 1 | 41
35 | 2 | 39
35 | 3 | 38
35 | 4 | 40
35 | 5 | 41
35 | 6 | 43
35 | 7 | 46
35 | 8 | 49
35 | 9 | 52
35 | 10 | 56
35 | 11 | 61
35 | 12 | 65
35 | 13 | 66
35 | 14 | 67
35 | 15 | 68
35 | 16 | 65
35 | 17 | 62
35 | 18 | 59
35 | 19 | 57
35 | 20 | 54
35 | 21 | 52
35 | 22 | 52
35 | 23 | 51
35 | 24 | 51 | 53.125 | 11.875 | -11.875
36 | 1 | 50
36 | 2 | 50
36 | 3 | 49
36 | 4 | 49
36 | 5 | 48
36 | 6 | 48
36 | 7 | 52
36 | 8 | 56
36 | 9 | 60
36 | 10 | 64
36 | 11 | 67
36 | 12 | 71
36 | 13 | 72
36 | 14 | 74
36 | 15 | 75
36 | 16 | 72
36 | 17 | 68
36 | 18 | 65
36 | 19 | 64
36 | 20 | 62
36 | 21 | 61
36 | 22 | 60
36 | 23 | 60
36 | 24 | 59 | 60.6667 | 4.3333 | -4.3333
37 | 1 | 59
37 | 2 | 59
37 | 3 | 59
37 | 4 | 59
37 | 5 | 59
37 | 6 | 59
37 | 7 | 60
37 | 8 | 61
37 | 9 | 62
37 | 10 | 66
37 | 11 | 71
37 | 12 | 75
37 | 13 | 75
37 | 14 | 76
37 | 15 | 76
37 | 16 | 73
37 | 17 | 71
37 | 18 | 68
37 | 19 | 67
37 | 20 | 65
37 | 21 | 64
37 | 22 | 64
37 | 23 | 63
37 | 24 | 63 | 65.5833 | -0.58333 | 0.58333
38 | 1 | 62
38 | 2 | 61
38 | 3 | 60
38 | 4 | 59
38 | 5 | 58
38 | 6 | 57
38 | 7 | 59
38 | 8 | 62
38 | 9 | 64
38 | 10 | 68
38 | 11 | 71
38 | 12 | 75
38 | 13 | 74
38 | 14 | 74
38 | 15 | 73
38 | 16 | 72
38 | 17 | 70
38 | 18 | 69
38 | 19 | 68
38 | 20 | 67
38 | 21 | 66
38 | 22 | 66
38 | 23 | 66
38 | 24 | 66 | 66.125 | -1.125 | 1.125
39 | 1 | 66
39 | 2 | 67
39 | 3 | 67
39 | 4 | 67
39 | 5 | 68
39 | 6 | 68
39 | 7 | 69
39 | 8 | 69
39 | 9 | 70
39 | 10 | 64
39 | 11 | 58
39 | 12 | 52
39 | 13 | 50
39 | 14 | 47
39 | 15 | 45
39 | 16 | 44
39 | 17 | 43
39 | 18 | 42
39 | 19 | 41
39 | 20 | 41
39 | 21 | 40
39 | 22 | 40
39 | 23 | 39
39 | 24 | 39 | 54 | 11 | -11
40 | 1 | 38
40 | 2 | 37
40 | 3 | 36
40 | 4 | 36
40 | 5 | 36
40 | 6 | 36
40 | 7 | 36
40 | 8 | 35
40 | 9 | 35
40 | 10 | 34
40 | 11 | 34
40 | 12 | 33
40 | 13 | 33
40 | 14 | 32
40 | 15 | 32
40 | 16 | 32
40 | 17 | 31
40 | 18 | 31
40 | 19 | 31
40 | 20 | 31
40 | 21 | 31
40 | 22 | 31
40 | 23 | 31
40 | 24 | 31 | 33.4583 | 31.5417 | -31.5417
41 | 1 | 30
41 | 2 | 30
41 | 3 | 29
41 | 4 | 28
41 | 5 | 28
41 | 6 | 27
41 | 7 | 28
41 | 8 | 29
41 | 9 | 30
41 | 10 | 32
41 | 11 | 35
41 | 12 | 37
41 | 13 | 39
41 | 14 | 42
41 | 15 | 44
41 | 16 | 43
41 | 17 | 41
41 | 18 | 40
41 | 19 | 39
41 | 20 | 39
41 | 21 | 38
41 | 22 | 37
41 | 23 | 37
41 | 24 | 36 | 34.9167 | 30.0833 | -30.0833
42 | 1 | 35
42 | 2 | 35
42 | 3 | 34
42 | 4 | 32
42 | 5 | 29
42 | 6 | 27
42 | 7 | 31
42 | 8 | 35
42 | 9 | 39
42 | 10 | 42
42 | 11 | 45
42 | 12 | 48
42 | 13 | 49
42 | 14 | 49
42 | 15 | 50
42 | 16 | 47
42 | 17 | 44
42 | 18 | 41
42 | 19 | 41
42 | 20 | 41
42 | 21 | 41
42 | 22 | 40
42 | 23 | 39
42 | 24 | 38 | 39.6667 | 25.3333 | -25.3333
43 | 1 | 37
43 | 2 | 36
43 | 3 | 35
43 | 4 | 37
43 | 5 | 40
43 | 6 | 42
43 | 7 | 45
43 | 8 | 48
43 | 9 | 51
43 | 10 | 53
43 | 11 | 55
43 | 12 | 57
43 | 13 | 57
43 | 14 | 58
43 | 15 | 58
43 | 16 | 58
43 | 17 | 59
43 | 18 | 59
43 | 19 | 59
43 | 20 | 58
43 | 21 | 58
43 | 22 | 58
43 | 23 | 59
43 | 24 | 59 | 51.5 | 13.5 | -13.5
44 | 1 | 59
44 | 2 | 59
44 | 3 | 59
44 | 4 | 59
44 | 5 | 60
44 | 6 | 60
44 | 7 | 61
44 | 8 | 62
44 | 9 | 63
44 | 10 | 66
44 | 11 | 69
44 | 12 | 72
44 | 13 | 71
44 | 14 | 70
44 | 15 | 69
44 | 16 | 68
44 | 17 | 67
44 | 18 | 66
44 | 19 | 66
44 | 20 | 65
44 | 21 | 65
44 | 22 | 63
44 | 23 | 61
44 | 24 | 59 | 64.125 | 0.875 | -0.875
45 | 1 | 59
45 | 2 | 58
45 | 3 | 58
45 | 4 | 57
45 | 5 | 56
45 | 6 | 55
45 | 7 | 56
45 | 8 | 56
45 | 9 | 57
45 | 10 | 58
45 | 11 | 58
45 | 12 | 59
45 | 13 | 61
45 | 14 | 62
45 | 15 | 64
45 | 16 | 62
45 | 17 | 60
45 | 18 | 58
45 | 19 | 56
45 | 20 | 54
45 | 21 | 52
45 | 22 | 51
45 | 23 | 50
45 | 24 | 49 | 56.9167 | 8.0833 | -8.0833
46 | 1 | 48
46 | 2 | 47
46 | 3 | 46
46 | 4 | 45
46 | 5 | 44
46 | 6 | 43
46 | 7 | 43
46 | 8 | 44
46 | 9 | 44
46 | 10 | 46
46 | 11 | 48
46 | 12 | 50
46 | 13 | 52
46 | 14 | 54
46 | 15 | 56
46 | 16 | 55
46 | 17 | 54
46 | 18 | 53
46 | 19 | 52
46 | 20 | 50
46 | 21 | 49
46 | 22 | 47
46 | 23 | 46
46 | 24 | 44 | 48.3333 | 16.6667 | -16.6667
47 | 1 | 43
47 | 2 | 41
47 | 3 | 40
47 | 4 | 39
47 | 5 | 39
47 | 6 | 38
47 | 7 | 39
47 | 8 | 40
47 | 9 | 41
47 | 10 | 43
47 | 11 | 44
47 | 12 | 46
47 | 13 | 48
47 | 14 | 50
47 | 15 | 52
47 | 16 | 51
47 | 17 | 50
47 | 18 | 49
47 | 19 | 48
47 | 20 | 46
47 | 21 | 45
47 | 22 | 44
47 | 23 | 42
47 | 24 | 41 | 44.125 | 20.875 | -20.875
48 | 1 | 41
48 | 2 | 40
48 | 3 | 40
48 | 4 | 39
48 | 5 | 38
48 | 6 | 37
48 | 7 | 37
48 | 8 | 36
48 | 9 | 36
48 | 10 | 37
48 | 11 | 37
48 | 12 | 38
48 | 13 | 38
48 | 14 | 39
48 | 15 | 39
48 | 16 | 39
48 | 17 | 39
48 | 18 | 39
48 | 19 | 39
48 | 20 | 40
48 | 21 | 40
48 | 22 | 40
48 | 23 | 39
48 | 24 | 39 | 38.5833 | 26.4167 | -26.4167
49 | 1 | 39
49 | 2 | 40
49 | 3 | 40
49 | 4 | 40
49 | 5 | 40
49 | 6 | 40
49 | 7 | 41
49 | 8 | 41
49 | 9 | 42
49 | 10 | 45
49 | 11 | 49
49 | 12 | 52
49 | 13 | 53
49 | 14 | 55
49 | 15 | 56
49 | 16 | 55
49 | 17 | 53
49 | 18 | 52
49 | 19 | 51
49 | 20 | 50
49 | 21 | 49
49 | 22 | 49
49 | 23 | 49
49 | 24 | 49 | 47.0833 | 17.9167 | -17.9167
50 | 1 | 49
50 | 2 | 50
50 | 3 | 50
50 | 4 | 50
50 | 5 | 49
50 | 6 | 49
50 | 7 | 50
50 | 8 | 50
50 | 9 | 51
50 | 10 | 54
50 | 11 | 56
50 | 12 | 59
50 | 13 | 60
50 | 14 | 60
50 | 15 | 61
50 | 16 | 59
50 | 17 | 57
50 | 18 | 55
50 | 19 | 55
50 | 20 | 54
50 | 21 | 54
50 | 22 | 53
50 | 23 | 52
50 | 24 | 51 | 53.6667 | 11.3333 | -11.3333
51 | 1 | 50
51 | 2 | 49
51 | 3 | 48
51 | 4 | 46
51 | 5 | 45
51 | 6 | 43
51 | 7 | 48
51 | 8 | 54
51 | 9 | 59
51 | 10 | 62
51 | 11 | 66
51 | 12 | 69
51 | 13 | 69
51 | 14 | 68
51 | 15 | 68
51 | 16 | 66
51 | 17 | 63
51 | 18 | 61
51 | 19 | 59
51 | 20 | 57
51 | 21 | 55
51 | 22 | 53
51 | 23 | 52
51 | 24 | 50 | 56.6667 | 8.3333 | -8.3333
52 | 1 | 49
52 | 2 | 48
52 | 3 | 47
52 | 4 | 47
52 | 5 | 46
52 | 6 | 46
52 | 7 | 47
52 | 8 | 48
52 | 9 | 49
52 | 10 | 50
52 | 11 | 52
52 | 12 | 53
52 | 13 | 54
52 | 14 | 55
52 | 15 | 56
52 | 16 | 56
52 | 17 | 55
52 | 18 | 55
52 | 19 | 53
52 | 20 | 52
52 | 21 | 50
52 | 22 | 50
52 | 23 | 49
52 | 24 | 49 | 50.6667 | 14.3333 | -14.3333
53 | 1 | 48
53 | 2 | 48
53 | 3 | 47
53 | 4 | 46
53 | 5 | 46
53 | 6 | 45
53 | 7 | 47
53 | 8 | 48
53 | 9 | 50
53 | 10 | 52
53 | 11 | 55
53 | 12 | 57
53 | 13 | 56
53 | 14 | 56
53 | 15 | 55
53 | 16 | 54
53 | 17 | 53
53 | 18 | 52
53 | 19 | 50
53 | 20 | 49
53 | 21 | 47
53 | 22 | 47
53 | 23 | 48
53 | 24 | 48 | 50.1667 | 14.8333 | -14.8333
54 | 1 | 48
54 | 2 | 49
54 | 3 | 49
54 | 4 | 49
54 | 5 | 49
54 | 6 | 49
54 | 7 | 49
54 | 8 | 50
54 | 9 | 50
54 | 10 | 52
54 | 11 | 53
54 | 12 | 55
54 | 13 | 56
54 | 14 | 57
54 | 15 | 58
54 | 16 | 58
54 | 17 | 57
54 | 18 | 57
54 | 19 | 53
54 | 20 | 48
54 | 21 | 44
54 | 22 | 43
54 | 23 | 43
54 | 24 | 42 | 50.75 | 14.25 | -14.25
55 | 1 | 43
55 | 2 | 45
55 | 3 | 46
55 | 4 | 46
55 | 5 | 47
55 | 6 | 47
55 | 7 | 49
55 | 8 | 51
55 | 9 | 53
55 | 10 | 54
55 | 11 | 56
55 | 12 | 57
55 | 13 | 56
55 | 14 | 55
55 | 15 | 54
55 | 16 | 54
55 | 17 | 55
55 | 18 | 55
55 | 19 | 54
55 | 20 | 54
55 | 21 | 53
55 | 22 | 53
55 | 23 | 53
55 | 24 | 53 | 51.7917 | 13.2083 | -13.2083
56 | 1 | 53
56 | 2 | 53
56 | 3 | 53
56 | 4 | 53
56 | 5 | 53
56 | 6 | 53
56 | 7 | 53
56 | 8 | 54
56 | 9 | 54
56 | 10 | 57
56 | 11 | 60
56 | 12 | 63
56 | 13 | 64
56 | 14 | 66
56 | 15 | 67
56 | 16 | 65
56 | 17 | 63
56 | 18 | 61
56 | 19 | 57
56 | 20 | 54
56 | 21 | 50
56 | 22 | 49
56 | 23 | 48
56 | 24 | 47 | 56.25 | 8.75 | -8.75
57 | 1 | 47
57 | 2 | 47
57 | 3 | 47
57 | 4 | 46
57 | 5 | 45
57 | 6 | 44
57 | 7 | 49
57 | 8 | 54
57 | 9 | 59
57 | 10 | 62
57 | 11 | 66
57 | 12 | 69
57 | 13 | 70
57 | 14 | 72
57 | 15 | 73
57 | 16 | 71
57 | 17 | 70
57 | 18 | 68
57 | 19 | 67
57 | 20 | 67
57 | 21 | 66
57 | 22 | 63
57 | 23 | 60
57 | 24 | 57 | 59.9583 | 5.0417 | -5.0417
58 | 1 | 56
58 | 2 | 55
58 | 3 | 54
58 | 4 | 54
58 | 5 | 54
58 | 6 | 54
58 | 7 | 55
58 | 8 | 55
58 | 9 | 56
58 | 10 | 57
58 | 11 | 59
58 | 12 | 60
58 | 13 | 62
58 | 14 | 64
58 | 15 | 66
58 | 16 | 64
58 | 17 | 63
58 | 18 | 61
58 | 19 | 60
58 | 20 | 58
58 | 21 | 57
58 | 22 | 55
58 | 23 | 54
58 | 24 | 52 | 57.7083 | 7.2917 | -7.2917
59 | 1 | 51
59 | 2 | 50
59 | 3 | 49
59 | 4 | 48
59 | 5 | 47
59 | 6 | 46
59 | 7 | 47
59 | 8 | 48
59 | 9 | 49
59 | 10 | 52
59 | 11 | 54
59 | 12 | 57
59 | 13 | 59
59 | 14 | 61
59 | 15 | 63
59 | 16 | 61
59 | 17 | 59
59 | 18 | 57
59 | 19 | 55
59 | 20 | 54
59 | 21 | 53
59 | 22 | 54
59 | 23 | 54
59 | 24 | 55 | 53.4583 | 11.5417 | -11.5417
60 | 1 | 56
60 | 2 | 56
60 | 3 | 57
60 | 4 | 57
60 | 5 | 56
60 | 6 | 56
60 | 7 | 56
60 | 8 | 55
60 | 9 | 55
60 | 10 | 55
60 | 11 | 56
60 | 12 | 56
60 | 13 | 57
60 | 14 | 59
60 | 15 | 60
60 | 16 | 60
60 | 17 | 59
60 | 18 | 59
60 | 19 | 58
60 | 20 | 57
60 | 21 | 56
60 | 22 | 55
60 | 23 | 55
60 | 24 | 54 | 56.6667 | 8.3333 | -8.3333
61 | 1 | 54
61 | 2 | 54
61 | 3 | 54
61 | 4 | 54
61 | 5 | 55
61 | 6 | 55
61 | 7 | 57
61 | 8 | 59
61 | 9 | 61
61 | 10 | 62
61 | 11 | 64
61 | 12 | 65
61 | 13 | 64
61 | 14 | 64
61 | 15 | 63
61 | 16 | 62
61 | 17 | 62
61 | 18 | 61
61 | 19 | 61
61 | 20 | 62
61 | 21 | 62
61 | 22 | 61
61 | 23 | 59
61 | 24 | 58 | 59.7083 | 5.2917 | -5.2917
62 | 1 | 58
62 | 2 | 57
62 | 3 | 57
62 | 4 | 56
62 | 5 | 56
62 | 6 | 55
62 | 7 | 55
62 | 8 | 55
62 | 9 | 55
62 | 10 | 54
62 | 11 | 52
62 | 12 | 51
62 | 13 | 51
62 | 14 | 50
62 | 15 | 50
62 | 16 | 48
62 | 17 | 46
62 | 18 | 44
62 | 19 | 43
62 | 20 | 43
62 | 21 | 42
62 | 22 | 41
62 | 23 | 40
62 | 24 | 39 | 49.9167 | 15.0833 | -15.0833
63 | 1 | 39
63 | 2 | 39
63 | 3 | 39
63 | 4 | 39
63 | 5 | 38
63 | 6 | 38
63 | 7 | 38
63 | 8 | 39
63 | 9 | 39
63 | 10 | 40
63 | 11 | 41
63 | 12 | 42
63 | 13 | 43
63 | 14 | 44
63 | 15 | 45
63 | 16 | 45
63 | 17 | 44
63 | 18 | 44
63 | 19 | 43
63 | 20 | 42
63 | 21 | 41
63 | 22 | 40
63 | 23 | 39
63 | 24 | 38 | 40.7917 | 24.2083 | -24.2083
64 | 1 | 37
64 | 2 | 36
64 | 3 | 35
64 | 4 | 35
64 | 5 | 34
64 | 6 | 34
64 | 7 | 34
64 | 8 | 34
64 | 9 | 34
64 | 10 | 40
64 | 11 | 45
64 | 12 | 51
64 | 13 | 52
64 | 14 | 54
64 | 15 | 55
64 | 16 | 54
64 | 17 | 53
64 | 18 | 52
64 | 19 | 50
64 | 20 | 49
64 | 21 | 47
64 | 22 | 47
64 | 23 | 46
64 | 24 | 46 | 43.9167 | 21.0833 | -21.0833
65 | 1 | 45
65 | 2 | 43
65 | 3 | 42
65 | 4 | 44
65 | 5 | 47
65 | 6 | 49
65 | 7 | 52
65 | 8 | 55
65 | 9 | 58
65 | 10 | 60
65 | 11 | 63
65 | 12 | 65
65 | 13 | 66
65 | 14 | 66
65 | 15 | 67
65 | 16 | 65
65 | 17 | 63
65 | 18 | 61
65 | 19 | 60
65 | 20 | 59
65 | 21 | 58
65 | 22 | 59
65 | 23 | 59
65 | 24 | 60 | 56.9167 | 8.0833 | -8.0833
66 | 1 | 60
66 | 2 | 61
66 | 3 | 61
66 | 4 | 61
66 | 5 | 62
66 | 6 | 62
66 | 7 | 62
66 | 8 | 63
66 | 9 | 63
66 | 10 | 63
66 | 11 | 63
66 | 12 | 63
66 | 13 | 63
66 | 14 | 62
66 | 15 | 62
66 | 16 | 62
66 | 17 | 63
66 | 18 | 63
66 | 19 | 62
66 | 20 | 62
66 | 21 | 61
66 | 22 | 61
66 | 23 | 60
66 | 24 | 60 | 61.875 | 3.125 | -3.125
67 | 1 | 60
67 | 2 | 59
67 | 3 | 59
67 | 4 | 58
67 | 5 | 58
67 | 6 | 57
67 | 7 | 58
67 | 8 | 58
67 | 9 | 59
67 | 10 | 59
67 | 11 | 58
67 | 12 | 58
67 | 13 | 58
67 | 14 | 58
67 | 15 | 58
67 | 16 | 57
67 | 17 | 55
67 | 18 | 54
67 | 19 | 53
67 | 20 | 53
67 | 21 | 52
67 | 22 | 51
67 | 23 | 51
67 | 24 | 50 | 56.2917 | 8.7083 | -8.7083
68 | 1 | 48
68 | 2 | 47
68 | 3 | 45
68 | 4 | 45
68 | 5 | 46
68 | 6 | 46
68 | 7 | 46
68 | 8 | 46
68 | 9 | 46
68 | 10 | 46
68 | 11 | 47
68 | 12 | 47
68 | 13 | 47
68 | 14 | 47
68 | 15 | 47
68 | 16 | 47
68 | 17 | 47
68 | 18 | 47
68 | 19 | 46
68 | 20 | 46
68 | 21 | 45
68 | 22 | 45
68 | 23 | 44
68 | 24 | 44 | 46.125 | 18.875 | -18.875
69 | 1 | 44
69 | 2 | 43
69 | 3 | 43
69 | 4 | 43
69 | 5 | 43
69 | 6 | 43
69 | 7 | 45
69 | 8 | 47
69 | 9 | 49
69 | 10 | 52
69 | 11 | 55
69 | 12 | 58
69 | 13 | 59
69 | 14 | 61
69 | 15 | 62
69 | 16 | 61
69 | 17 | 59
69 | 18 | 58
69 | 19 | 56
69 | 20 | 54
69 | 21 | 52
69 | 22 | 50
69 | 23 | 49
69 | 24 | 47 | 51.375 | 13.625 | -13.625
70 | 1 | 47
70 | 2 | 48
70 | 3 | 48
70 | 4 | 46
70 | 5 | 45
70 | 6 | 43
70 | 7 | 48
70 | 8 | 54
70 | 9 | 59
70 | 10 | 62
70 | 11 | 64
70 | 12 | 67
70 | 13 | 68
70 | 14 | 70
70 | 15 | 71
70 | 16 | 69
70 | 17 | 68
70 | 18 | 66
70 | 19 | 66
70 | 20 | 65
70 | 21 | 65
70 | 22 | 65
70 | 23 | 64
70 | 24 | 64 | 59.6667 | 5.3333 | -5.3333
71 | 1 | 64
71 | 2 | 65
71 | 3 | 65
71 | 4 | 64
71 | 5 | 64
71 | 6 | 63
71 | 7 | 63
71 | 8 | 62
71 | 9 | 62
71 | 10 | 64
71 | 11 | 65
71 | 12 | 67
71 | 13 | 68
71 | 14 | 69
71 | 15 | 70
71 | 16 | 68
71 | 17 | 66
71 | 18 | 64
71 | 19 | 64
71 | 20 | 63
71 | 21 | 63
71 | 22 | 63
71 | 23 | 63
71 | 24 | 63 | 64.6667 | 0.33333 | -0.33333
72 | 1 | 64
72 | 2 | 64
72 | 3 | 65
72 | 4 | 65
72 | 5 | 65
72 | 6 | 65
72 | 7 | 67
72 | 8 | 70
72 | 9 | 72
72 | 10 | 73
72 | 11 | 74
72 | 12 | 75
72 | 13 | 74
72 | 14 | 74
72 | 15 | 73
72 | 16 | 73
72 | 17 | 72
72 | 18 | 72
72 | 19 | 72
72 | 20 | 71
72 | 21 | 71
72 | 22 | 71
72 | 23 | 72
72 | 24 | 72 | 70.25 | -5.25 | 5.25
73 | 1 | 72
73 | 2 | 71
73 | 3 | 71
73 | 4 | 69
73 | 5 | 67
73 | 6 | 65
73 | 7 | 67
73 | 8 | 69
73 | 9 | 71
73 | 10 | 74
73 | 11 | 78
73 | 12 | 81
73 | 13 | 81
73 | 14 | 82
73 | 15 | 82
73 | 16 | 80
73 | 17 | 79
73 | 18 | 77
73 | 19 | 74
73 | 20 | 70
73 | 21 | 67
73 | 22 | 66
73 | 23 | 65
73 | 24 | 64 | 72.5833 | -7.5833 | 7.5833
74 | 1 | 62
74 | 2 | 60
74 | 3 | 58
74 | 4 | 58
74 | 5 | 58
74 | 6 | 58
74 | 7 | 61
74 | 8 | 64
74 | 9 | 67
74 | 10 | 71
74 | 11 | 75
74 | 12 | 79
74 | 13 | 80
74 | 14 | 80
74 | 15 | 81
74 | 16 | 80
74 | 17 | 78
74 | 18 | 77
74 | 19 | 74
74 | 20 | 71
74 | 21 | 68
74 | 22 | 67
74 | 23 | 67
74 | 24 | 66 | 69.1667 | -4.1667 | 4.1667
75 | 1 | 65
75 | 2 | 65
75 | 3 | 64
75 | 4 | 60
75 | 5 | 57
75 | 6 | 53
75 | 7 | 53
75 | 8 | 53
75 | 9 | 53
75 | 10 | 54
75 | 11 | 55
75 | 12 | 56
75 | 13 | 58
75 | 14 | 61
75 | 15 | 63
75 | 16 | 61
75 | 17 | 60
75 | 18 | 58
75 | 19 | 57
75 | 20 | 55
75 | 21 | 54
75 | 22 | 51
75 | 23 | 49
75 | 24 | 46 | 56.7083 | 8.2917 | -8.2917
76 | 1 | 45
76 | 2 | 44
76 | 3 | 43
76 | 4 | 43
76 | 5 | 44
76 | 6 | 44
76 | 7 | 48
76 | 8 | 51
76 | 9 | 55
76 | 10 | 57
76 | 11 | 60
76 | 12 | 62
76 | 13 | 63
76 | 14 | 65
76 | 15 | 66
76 | 16 | 65
76 | 17 | 63
76 | 18 | 62
76 | 19 | 59
76 | 20 | 55
76 | 21 | 52
76 | 22 | 52
76 | 23 | 51
76 | 24 | 51 | 54.1667 | 10.8333 | -10.8333
77 | 1 | 50
77 | 2 | 49
77 | 3 | 48
77 | 4 | 48
77 | 5 | 47
77 | 6 | 47
77 | 7 | 51
77 | 8 | 56
77 | 9 | 60
77 | 10 | 63
77 | 11 | 66
77 | 12 | 69
77 | 13 | 70
77 | 14 | 71
77 | 15 | 72
77 | 16 | 70
77 | 17 | 68
77 | 18 | 66
77 | 19 | 63
77 | 20 | 59
77 | 21 | 56
77 | 22 | 54
77 | 23 | 53
77 | 24 | 51 | 58.625 | 6.375 | -6.375
78 | 1 | 52
78 | 2 | 52
78 | 3 | 53
78 | 4 | 52
78 | 5 | 50
78 | 6 | 49
78 | 7 | 55
78 | 8 | 60
78 | 9 | 66
78 | 10 | 68
78 | 11 | 70
78 | 12 | 72
78 | 13 | 72
78 | 14 | 73
78 | 15 | 73
78 | 16 | 71
78 | 17 | 68
78 | 18 | 66
78 | 19 | 64
78 | 20 | 62
78 | 21 | 60
78 | 22 | 59
78 | 23 | 58
78 | 24 | 57 | 61.75 | 3.25 | -3.25
79 | 1 | 56
79 | 2 | 54
79 | 3 | 53
79 | 4 | 54
79 | 5 | 55
79 | 6 | 56
79 | 7 | 60
79 | 8 | 63
79 | 9 | 67
79 | 10 | 68
79 | 11 | 69
79 | 12 | 70
79 | 13 | 71
79 | 14 | 72
79 | 15 | 73
79 | 16 | 71
79 | 17 | 69
79 | 18 | 67
79 | 19 | 67
79 | 20 | 66
79 | 21 | 66
79 | 22 | 65
79 | 23 | 65
79 | 24 | 64 | 64.2083 | 0.79167 | -0.79167
80 | 1 | 64
80 | 2 | 63
80 | 3 | 63
80 | 4 | 63
80 | 5 | 64
80 | 6 | 64
80 | 7 | 66
80 | 8 | 67
80 | 9 | 69
80 | 10 | 71
80 | 11 | 74
80 | 12 | 76
80 | 13 | 74
80 | 14 | 71
80 | 15 | 69
80 | 16 | 69
80 | 17 | 70
80 | 18 | 70
80 | 19 | 67
80 | 20 | 63
80 | 21 | 60
80 | 22 | 60
80 | 23 | 60
80 | 24 | 60 | 66.5417 | -1.5417 | 1.5417
81 | 1 | 58
81 | 2 | 55
81 | 3 | 53
81 | 4 | 54
81 | 5 | 55
81 | 6 | 56
81 | 7 | 60
81 | 8 | 63
81 | 9 | 67
81 | 10 | 69
81 | 11 | 71
81 | 12 | 73
81 | 13 | 74
81 | 14 | 76
81 | 15 | 77
81 | 16 | 75
81 | 17 | 74
81 | 18 | 72
81 | 19 | 70
81 | 20 | 68
81 | 21 | 66
81 | 22 | 65
81 | 23 | 65
81 | 24 | 64 | 65.8333 | -0.83333 | 0.83333
82 | 1 | 64
82 | 2 | 64
82 | 3 | 64
82 | 4 | 64
82 | 5 | 64
82 | 6 | 64
82 | 7 | 65
82 | 8 | 65
82 | 9 | 66
82 | 10 | 68
82 | 11 | 70
82 | 12 | 72
82 | 13 | 74
82 | 14 | 75
82 | 15 | 77
82 | 16 | 76
82 | 17 | 74
82 | 18 | 73
82 | 19 | 71
82 | 20 | 68
82 | 21 | 66
82 | 22 | 66
82 | 23 | 65
82 | 24 | 65 | 68.3333 | -3.3333 | 3.3333
83 | 1 | 65
83 | 2 | 65
83 | 3 | 65
83 | 4 | 65
83 | 5 | 65
83 | 6 | 65
83 | 7 | 66
83 | 8 | 66
83 | 9 | 67
83 | 10 | 67
83 | 11 | 67
83 | 12 | 67
83 | 13 | 70
83 | 14 | 72
83 | 15 | 75
83 | 16 | 74
83 | 17 | 73
83 | 18 | 72
83 | 19 | 70
83 | 20 | 68
83 | 21 | 66
83 | 22 | 65
83 | 23 | 63
83 | 24 | 62 | 67.5 | -2.5 | 2.5
84 | 1 | 62
84 | 2 | 63
84 | 3 | 63
84 | 4 | 62
84 | 5 | 60
84 | 6 | 59
84 | 7 | 59
84 | 8 | 59
84 | 9 | 59
84 | 10 | 60
84 | 11 | 60
84 | 12 | 61
84 | 13 | 62
84 | 14 | 64
84 | 15 | 65
84 | 16 | 64
84 | 17 | 64
84 | 18 | 63
84 | 19 | 62
84 | 20 | 60
84 | 21 | 59
84 | 22 | 59
84 | 23 | 59
84 | 24 | 59 | 61.125 | 3.875 | -3.875
85 | 1 | 58
85 | 2 | 57
85 | 3 | 56
85 | 4 | 53
85 | 5 | 50
85 | 6 | 47
85 | 7 | 49
85 | 8 | 51
85 | 9 | 53
85 | 10 | 55
85 | 11 | 58
85 | 12 | 60
85 | 13 | 62
85 | 14 | 63
85 | 15 | 65
85 | 16 | 64
85 | 17 | 63
85 | 18 | 62
85 | 19 | 60
85 | 20 | 57
85 | 21 | 55
85 | 22 | 54
85 | 23 | 52
85 | 24 | 51 | 56.4583 | 8.5417 | -8.5417
86 | 1 | 50
86 | 2 | 48
86 | 3 | 47
86 | 4 | 45
86 | 5 | 43
86 | 6 | 41
86 | 7 | 46
86 | 8 | 50
86 | 9 | 55
86 | 10 | 57
86 | 11 | 58
86 | 12 | 60
86 | 13 | 62
86 | 14 | 64
86 | 15 | 66
86 | 16 | 65
86 | 17 | 65
86 | 18 | 64
86 | 19 | 60
86 | 20 | 57
86 | 21 | 53
86 | 22 | 54
86 | 23 | 55
86 | 24 | 56 | 55.0417 | 9.9583 | -9.9583
87 | 1 | 55
87 | 2 | 55
87 | 3 | 54
87 | 4 | 52
87 | 5 | 51
87 | 6 | 49
87 | 7 | 53
87 | 8 | 57
87 | 9 | 61
87 | 10 | 63
87 | 11 | 64
87 | 12 | 66
87 | 13 | 67
87 | 14 | 69
87 | 15 | 70
87 | 16 | 69
87 | 17 | 69
87 | 18 | 68
87 | 19 | 65
87 | 20 | 63
87 | 21 | 60
87 | 22 | 59
87 | 23 | 57
87 | 24 | 56 | 60.5 | 4.5 | -4.5
88 | 1 | 55
88 | 2 | 54
88 | 3 | 53
88 | 4 | 53
88 | 5 | 52
88 | 6 | 52
88 | 7 | 57
88 | 8 | 61
88 | 9 | 66
88 | 10 | 68
88 | 11 | 71
88 | 12 | 73
88 | 13 | 74
88 | 14 | 75
88 | 15 | 76
88 | 16 | 75
88 | 17 | 73
88 | 18 | 72
88 | 19 | 70
88 | 20 | 67
88 | 21 | 65
88 | 22 | 64
88 | 23 | 62
88 | 24 | 61 | 64.5417 | 0.45833 | -0.45833
89 | 1 | 61
89 | 2 | 60
89 | 3 | 60
89 | 4 | 58
89 | 5 | 57
89 | 6 | 55
89 | 7 | 59
89 | 8 | 63
89 | 9 | 67
89 | 10 | 70
89 | 11 | 73
89 | 12 | 76
89 | 13 | 78
89 | 14 | 79
89 | 15 | 81
89 | 16 | 80
89 | 17 | 79
89 | 18 | 78
89 | 19 | 72
89 | 20 | 66
89 | 21 | 60
89 | 22 | 61
89 | 23 | 62
89 | 24 | 63 | 67.4167 | -2.4167 | 2.4167
90 | 1 | 62
90 | 2 | 60
90 | 3 | 59
90 | 4 | 57
90 | 5 | 55
90 | 6 | 53
90 | 7 | 60
90 | 8 | 67
90 | 9 | 74
90 | 10 | 77
90 | 11 | 80
90 | 12 | 83
90 | 13 | 83
90 | 14 | 84
90 | 15 | 84
90 | 16 | 82
90 | 17 | 79
90 | 18 | 77
90 | 19 | 71
90 | 20 | 66
90 | 21 | 63
90 | 22 | 62
90 | 23 | 61
90 | 24 | 61 | 69.1667 | -4.1667 | 4.1667
91 | 1 | 62
91 | 2 | 62
91 | 3 | 63
91 | 4 | 62
91 | 5 | 60
91 | 6 | 60
91 | 7 | 65
91 | 8 | 70
91 | 9 | 74
91 | 10 | 77
91 | 11 | 78
91 | 12 | 78
91 | 13 | 80
91 | 14 | 80
91 | 15 | 78
91 | 16 | 77
91 | 17 | 77
91 | 18 | 74
91 | 19 | 73
91 | 20 | 66
91 | 21 | 68
91 | 22 | 67
91 | 23 | 67
91 | 24 | 68 | 70.25 | -5.25 | 5.25
92 | 1 | 68
92 | 2 | 69
92 | 3 | 70
92 | 4 | 71
92 | 5 | 72
92 | 6 | 66
92 | 7 | 65
92 | 8 | 66
92 | 9 | 66
92 | 10 | 68
92 | 11 | 70
92 | 12 | 70
92 | 13 | 71
92 | 14 | 70
92 | 15 | 68
92 | 16 | 67
92 | 17 | 68
92 | 18 | 68
92 | 19 | 68
92 | 20 | 68
92 | 21 | 68
92 | 22 | 67
92 | 23 | 67
92 | 24 | 67 | 68.25 | -3.25 | 3.25
93 | 1 | 65
93 | 2 | 66
93 | 3 | 67
93 | 4 | 67
93 | 5 | 68
93 | 6 | 67
93 | 7 | 68
93 | 8 | 67
93 | 9 | 67
93 | 10 | 67
93 | 11 | 68
93 | 12 | 69
93 | 13 | 70
93 | 14 | 70
93 | 15 | 71
93 | 16 | 71
93 | 17 | 72
93 | 18 | 71
93 | 19 | 69
93 | 20 | 67
93 | 21 | 67
93 | 22 | 63
93 | 23 | 62
93 | 24 | 60 | 67.4583 | -2.4583 | 2.4583
94 | 1 | 60
94 | 2 | 59
94 | 3 | 57
94 | 4 | 56
94 | 5 | 56
94 | 6 | 56
94 | 7 | 60
94 | 8 | 69
94 | 9 | 71
94 | 10 | 74
94 | 11 | 76
94 | 12 | 77
94 | 13 | 79
94 | 14 | 80
94 | 15 | 80
94 | 16 | 80
94 | 17 | 79
94 | 18 | 77
94 | 19 | 73
94 | 20 | 70
94 | 21 | 69
94 | 22 | 68
94 | 23 | 66
94 | 24 | 66 | 69.0833 | -4.0833 | 4.0833
95 | 1 | 65
95 | 2 | 65
95 | 3 | 64
95 | 4 | 64
95 | 5 | 64
95 | 6 | 64
95 | 7 | 69
95 | 8 | 73
95 | 9 | 77
95 | 10 | 76
95 | 11 | 80
95 | 12 | 82
95 | 13 | 81
95 | 14 | 80
95 | 15 | 79
95 | 16 | 80
95 | 17 | 80
95 | 18 | 77
95 | 19 | 76
95 | 20 | 75
95 | 21 | 74
95 | 22 | 74
95 | 23 | 73
95 | 24 | 73 | 73.5417 | -8.5417 | 8.5417
96 | 1 | 73
96 | 2 | 73
96 | 3 | 72
96 | 4 | 73
96 | 5 | 73
96 | 6 | 68
96 | 7 | 67
96 | 8 | 66
96 | 9 | 65
96 | 10 | 68
96 | 11 | 69
96 | 12 | 69
96 | 13 | 71
96 | 14 | 72
96 | 15 | 73
96 | 16 | 73
96 | 17 | 72
96 | 18 | 68
96 | 19 | 67
96 | 20 | 66
96 | 21 | 64
96 | 22 | 62
96 | 23 | 61
96 | 24 | 60 | 68.5417 | -3.5417 | 3.5417
97 | 1 | 56
97 | 2 | 54
97 | 3 | 54
97 | 4 | 56
97 | 5 | 54
97 | 6 | 57
97 | 7 | 61
97 | 8 | 64
97 | 9 | 66
97 | 10 | 67
97 | 11 | 68
97 | 12 | 69
97 | 13 | 70
97 | 14 | 72
97 | 15 | 73
97 | 16 | 75
97 | 17 | 73
97 | 18 | 72
97 | 19 | 69
97 | 20 | 65
97 | 21 | 64
97 | 22 | 63
97 | 23 | 64
97 | 24 | 62 | 64.5 | 0.5 | -0.5
98 | 1 | 64
98 | 2 | 63
98 | 3 | 62
98 | 4 | 62
98 | 5 | 60
98 | 6 | 59
98 | 7 | 63
98 | 8 | 65
98 | 9 | 66
98 | 10 | 67
98 | 11 | 68
98 | 12 | 71
98 | 13 | 73
98 | 14 | 74
98 | 15 | 77
98 | 16 | 78
98 | 17 | 78
98 | 18 | 72
98 | 19 | 63
98 | 20 | 61
98 | 21 | 61
98 | 22 | 61
98 | 23 | 60
98 | 24 | 59 | 66.125 | -1.125 | 1.125
99 | 1 | 58
99 | 2 | 58
99 | 3 | 57
99 | 4 | 58
99 | 5 | 59
99 | 6 | 58
99 | 7 | 64
99 | 8 | 69
99 | 9 | 70
99 | 10 | 71
99 | 11 | 71
99 | 12 | 74
99 | 13 | 75
99 | 14 | 77
99 | 15 | 76
99 | 16 | 74
99 | 17 | 72
99 | 18 | 70
99 | 19 | 66
99 | 20 | 63
99 | 21 | 62
99 | 22 | 62
99 | 23 | 62
99 | 24 | 61 | 66.125 | -1.125 | 1.125
100 | 1 | 62
100 | 2 | 61
100 | 3 | 60
100 | 4 | 61
100 | 5 | 59
100 | 6 | 59
100 | 7 | 66
100 | 8 | 70
100 | 9 | 72
100 | 10 | 75
100 | 11 | 77
100 | 12 | 77
100 | 13 | 75
100 | 14 | 77
100 | 15 | 78
100 | 16 | 78
100 | 17 | 76
100 | 18 | 72
100 | 19 | 68
100 | 20 | 65
100 | 21 | 64
100 | 22 | 60
100 | 23 | 60
100 | 24 | 59 | 67.9583 | -2.9583 | 2.9583
101 | 1 | 58
101 | 2 | 53
101 | 3 | 51
101 | 4 | 49
101 | 5 | 48
101 | 6 | 48
101 | 7 | 47
101 | 8 | 50
101 | 9 | 52
101 | 10 | 55
101 | 11 | 57
101 | 12 | 57
101 | 13 | 54
101 | 14 | 57
101 | 15 | 55
101 | 16 | 56
101 | 17 | 54
101 | 18 | 52
101 | 19 | 51
101 | 20 | 51
101 | 21 | 49
101 | 22 | 49
101 | 23 | 49
101 | 24 | 49 | 52.125 | 12.875 | -12.875
102 | 1 | 49
102 | 2 | 50
102 | 3 | 51
102 | 4 | 51
102 | 5 | 53
102 | 6 | 53
102 | 7 | 54
102 | 8 | 58
102 | 9 | 61
102 | 10 | 63
102 | 11 | 66
102 | 12 | 68
102 | 13 | 70
102 | 14 | 72
102 | 15 | 72
102 | 16 | 72
102 | 17 | 72
102 | 18 | 69
102 | 19 | 62
102 | 20 | 61
102 | 21 | 58
102 | 22 | 55
102 | 23 | 53
102 | 24 | 53 | 60.25 | 4.75 | -4.75
103 | 1 | 51
103 | 2 | 51
103 | 3 | 50
103 | 4 | 50
103 | 5 | 49
103 | 6 | 48
103 | 7 | 58
103 | 8 | 64
103 | 9 | 67
103 | 10 | 70
103 | 11 | 72
103 | 12 | 74
103 | 13 | 76
103 | 14 | 76
103 | 15 | 79
103 | 16 | 78
103 | 17 | 77
103 | 18 | 74
103 | 19 | 71
103 | 20 | 67
103 | 21 | 66
103 | 22 | 63
103 | 23 | 62
103 | 24 | 60 | 64.7083 | 0.29167 | -0.29167
104 | 1 | 60
104 | 2 | 53
104 | 3 | 53
104 | 4 | 52
104 | 5 | 53
104 | 6 | 52
104 | 7 | 59
104 | 8 | 68
104 | 9 | 72
104 | 10 | 76
104 | 11 | 78
104 | 12 | 79
104 | 13 | 80
104 | 14 | 79
104 | 15 | 80
104 | 16 | 78
104 | 17 | 76
104 | 18 | 73
104 | 19 | 69
104 | 20 | 66
104 | 21 | 65
104 | 22 | 63
104 | 23 | 61
104 | 24 | 60 | 66.875 | -1.875 | 1.875
105 | 1 | 57
105 | 2 | 57
105 | 3 | 52
105 | 4 | 52
105 | 5 | 51
105 | 6 | 51
105 | 7 | 58
105 | 8 | 67
105 | 9 | 70
105 | 10 | 72
105 | 11 | 74
105 | 12 | 76
105 | 13 | 78
105 | 14 | 79
105 | 15 | 77
105 | 16 | 76
105 | 17 | 77
105 | 18 | 73
105 | 19 | 70
105 | 20 | 67
105 | 21 | 65
105 | 22 | 64
105 | 23 | 61
105 | 24 | 62 | 66.0833 | -1.0833 | 1.0833
106 | 1 | 61
106 | 2 | 56
106 | 3 | 55
106 | 4 | 53
106 | 5 | 54
106 | 6 | 52
106 | 7 | 60
106 | 8 | 66
106 | 9 | 68
106 | 10 | 70
106 | 11 | 73
106 | 12 | 73
106 | 13 | 74
106 | 14 | 76
106 | 15 | 76
106 | 16 | 73
106 | 17 | 72
106 | 18 | 72
106 | 19 | 68
106 | 20 | 69
106 | 21 | 67
106 | 22 | 67
106 | 23 | 67
106 | 24 | 67 | 66.2083 | -1.2083 | 1.2083
107 | 1 | 67
107 | 2 | 67
107 | 3 | 67
107 | 4 | 67
107 | 5 | 67
107 | 6 | 68
107 | 7 | 68
107 | 8 | 70
107 | 9 | 73
107 | 10 | 77
107 | 11 | 77
107 | 12 | 79
107 | 13 | 79
107 | 14 | 80
107 | 15 | 77
107 | 16 | 77
107 | 17 | 76
107 | 18 | 74
107 | 19 | 72
107 | 20 | 71
107 | 21 | 71
107 | 22 | 71
107 | 23 | 72
107 | 24 | 72 | 72.4583 | -7.4583 | 7.4583
108 | 1 | 72
108 | 2 | 73
108 | 3 | 73
108 | 4 | 69
108 | 5 | 70
108 | 6 | 70
108 | 7 | 71
108 | 8 | 72
108 | 9 | 73
108 | 10 | 77
108 | 11 | 79
108 | 12 | 81
108 | 13 | 77
108 | 14 | 79
108 | 15 | 79
108 | 16 | 78
108 | 17 | 77
108 | 18 | 75
108 | 19 | 73
108 | 20 | 73
108 | 21 | 71
108 | 22 | 70
108 | 23 | 70
108 | 24 | 70 | 73.8333 | -8.8333 | 8.8333
109 | 1 | 68
109 | 2 | 65
109 | 3 | 63
109 | 4 | 61
109 | 5 | 60
109 | 6 | 59
109 | 7 | 60
109 | 8 | 61
109 | 9 | 62
109 | 10 | 65
109 | 11 | 68
109 | 12 | 69
109 | 13 | 69
109 | 14 | 71
109 | 15 | 73
109 | 16 | 73
109 | 17 | 73
109 | 18 | 69
109 | 19 | 66
109 | 20 | 64
109 | 21 | 64
109 | 22 | 63
109 | 23 | 62
109 | 24 | 60 | 65.3333 | -0.33333 | 0.33333
110 | 1 | 58
110 | 2 | 56
110 | 3 | 52
110 | 4 | 51
110 | 5 | 50
110 | 6 | 51
110 | 7 | 61
110 | 8 | 65
110 | 9 | 69
110 | 10 | 71
110 | 11 | 73
110 | 12 | 74
110 | 13 | 76
110 | 14 | 76
110 | 15 | 76
110 | 16 | 76
110 | 17 | 75
110 | 18 | 71
110 | 19 | 71
110 | 20 | 69
110 | 21 | 68
110 | 22 | 66
110 | 23 | 65
110 | 24 | 65 | 66.0417 | -1.0417 | 1.0417
111 | 1 | 64
111 | 2 | 62
111 | 3 | 63
111 | 4 | 62
111 | 5 | 62
111 | 6 | 62
111 | 7 | 65
111 | 8 | 69
111 | 9 | 72
111 | 10 | 76
111 | 11 | 79
111 | 12 | 81
111 | 13 | 83
111 | 14 | 82
111 | 15 | 83
111 | 16 | 82
111 | 17 | 78
111 | 18 | 75
111 | 19 | 72
111 | 20 | 70
111 | 21 | 69
111 | 22 | 69
111 | 23 | 68
111 | 24 | 71 | 71.625 | -6.625 | 6.625
112 | 1 | 71
112 | 2 | 72
112 | 3 | 72
112 | 4 | 73
112 | 5 | 72
112 | 6 | 73
112 | 7 | 74
112 | 8 | 75
112 | 9 | 78
112 | 10 | 78
112 | 11 | 82
112 | 12 | 82
112 | 13 | 81
112 | 14 | 81
112 | 15 | 81
112 | 16 | 81
112 | 17 | 79
112 | 18 | 77
112 | 19 | 76
112 | 20 | 76
112 | 21 | 75
112 | 22 | 75
112 | 23 | 75
112 | 24 | 75 | 76.4167 | -11.4167 | 11.4167
113 | 1 | 75
113 | 2 | 75
113 | 3 | 74
113 | 4 | 74
113 | 5 | 73
113 | 6 | 73
113 | 7 | 73
113 | 8 | 75
113 | 9 | 76
113 | 10 | 79
113 | 11 | 78
113 | 12 | 81
113 | 13 | 84
113 | 14 | 83
113 | 15 | 81
113 | 16 | 82
113 | 17 | 80
113 | 18 | 78
113 | 19 | 77
113 | 20 | 77
113 | 21 | 76
113 | 22 | 75
113 | 23 | 74
113 | 24 | 74 | 76.9583 | -11.9583 | 11.9583
114 | 1 | 74
114 | 2 | 74
114 | 3 | 73
114 | 4 | 73
114 | 5 | 72
114 | 6 | 71
114 | 7 | 73
114 | 8 | 76
114 | 9 | 78
114 | 10 | 81
114 | 11 | 83
114 | 12 | 87
114 | 13 | 88
114 | 14 | 88
114 | 15 | 87
114 | 16 | 88
114 | 17 | 85
114 | 18 | 82
114 | 19 | 79
114 | 20 | 78
114 | 21 | 76
114 | 22 | 76
114 | 23 | 74
114 | 24 | 75 | 78.7917 | -13.7917 | 13.7917
115 | 1 | 74
115 | 2 | 75
115 | 3 | 75
115 | 4 | 74
115 | 5 | 74
115 | 6 | 74
115 | 7 | 75
115 | 8 | 76
115 | 9 | 77
115 | 10 | 81
115 | 11 | 82
115 | 12 | 82
115 | 13 | 83
115 | 14 | 84
115 | 15 | 83
115 | 16 | 82
115 | 17 | 81
115 | 18 | 80
115 | 19 | 76
115 | 20 | 75
115 | 21 | 73
115 | 22 | 72
115 | 23 | 72
115 | 24 | 71 | 77.125 | -12.125 | 12.125
116 | 1 | 71
116 | 2 | 69
116 | 3 | 67
116 | 4 | 65
116 | 5 | 63
116 | 6 | 64
116 | 7 | 69
116 | 8 | 72
116 | 9 | 75
116 | 10 | 76
116 | 11 | 79
116 | 12 | 81
116 | 13 | 81
116 | 14 | 83
116 | 15 | 84
116 | 16 | 85
116 | 17 | 85
116 | 18 | 81
116 | 19 | 72
116 | 20 | 70
116 | 21 | 67
116 | 22 | 67
116 | 23 | 65
116 | 24 | 64 | 73.125 | -8.125 | 8.125
117 | 1 | 63
117 | 2 | 61
117 | 3 | 60
117 | 4 | 62
117 | 5 | 58
117 | 6 | 61
117 | 7 | 69
117 | 8 | 77
117 | 9 | 82
117 | 10 | 78
117 | 11 | 77
117 | 12 | 79
117 | 13 | 80
117 | 14 | 81
117 | 15 | 81
117 | 16 | 81
117 | 17 | 80
117 | 18 | 78
117 | 19 | 75
117 | 20 | 75
117 | 21 | 74
117 | 22 | 73
117 | 23 | 70
117 | 24 | 68 | 72.625 | -7.625 | 7.625
118 | 1 | 68
118 | 2 | 67
118 | 3 | 66
118 | 4 | 65
118 | 5 | 64
118 | 6 | 64
118 | 7 | 65
118 | 8 | 67
118 | 9 | 69
118 | 10 | 72
118 | 11 | 74
118 | 12 | 75
118 | 13 | 76
118 | 14 | 78
118 | 15 | 78
118 | 16 | 79
118 | 17 | 77
118 | 18 | 74
118 | 19 | 72
118 | 20 | 69
118 | 21 | 68
118 | 22 | 67
118 | 23 | 64
118 | 24 | 61 | 69.9583 | -4.9583 | 4.9583
119 | 1 | 58
119 | 2 | 59
119 | 3 | 58
119 | 4 | 59
119 | 5 | 63
119 | 6 | 64
119 | 7 | 68
119 | 8 | 71
119 | 9 | 74
119 | 10 | 74
119 | 11 | 74
119 | 12 | 75
119 | 13 | 73
119 | 14 | 71
119 | 15 | 70
119 | 16 | 69
119 | 17 | 67
119 | 18 | 63
119 | 19 | 63
119 | 20 | 62
119 | 21 | 62
119 | 22 | 60
119 | 23 | 59
119 | 24 | 59 | 65.625 | -0.625 | 0.625
120 | 1 | 60
120 | 2 | 60
120 | 3 | 60
120 | 4 | 61
120 | 5 | 62
120 | 6 | 63
120 | 7 | 62
120 | 8 | 61
120 | 9 | 60
120 | 10 | 60
120 | 11 | 60
120 | 12 | 61
120 | 13 | 62
120 | 14 | 62
120 | 15 | 64
120 | 16 | 63
120 | 17 | 62
120 | 18 | 62
120 | 19 | 63
120 | 20 | 64
120 | 21 | 65
120 | 22 | 66
120 | 23 | 66
120 | 24 | 67 | 62.3333 | 2.6667 | -2.6667
121 | 1 | 69
121 | 2 | 69
121 | 3 | 70
121 | 4 | 70
121 | 5 | 70
121 | 6 | 71
121 | 7 | 75
121 | 8 | 77
121 | 9 | 79
121 | 10 | 82
121 | 11 | 82
121 | 12 | 83
121 | 13 | 85
121 | 14 | 84
121 | 15 | 84
121 | 16 | 84
121 | 17 | 83
121 | 18 | 80
121 | 19 | 78
121 | 20 | 77
121 | 21 | 73
121 | 22 | 73
121 | 23 | 72
121 | 24 | 72 | 76.75 | -11.75 | 11.75
122 | 1 | 72
122 | 2 | 72
122 | 3 | 71
122 | 4 | 72
122 | 5 | 70
122 | 6 | 70
122 | 7 | 72
122 | 8 | 74
122 | 9 | 76
122 | 10 | 78
122 | 11 | 79
122 | 12 | 80
122 | 13 | 82
122 | 14 | 81
122 | 15 | 80
122 | 16 | 78
122 | 17 | 77
122 | 18 | 75
122 | 19 | 73
122 | 20 | 72
122 | 21 | 70
122 | 22 | 69
122 | 23 | 68
122 | 24 | 67 | 74.0833 | -9.0833 | 9.0833
123 | 1 | 66
123 | 2 | 65
123 | 3 | 64
123 | 4 | 65
123 | 5 | 65
123 | 6 | 65
123 | 7 | 65
123 | 8 | 65
123 | 9 | 65
123 | 10 | 67
123 | 11 | 69
123 | 12 | 70
123 | 13 | 71
123 | 14 | 72
123 | 15 | 70
123 | 16 | 68
123 | 17 | 68
123 | 18 | 68
123 | 19 | 67
123 | 20 | 66
123 | 21 | 66
123 | 22 | 62
123 | 23 | 60
123 | 24 | 59 | 66.1667 | -1.1667 | 1.1667
124 | 1 | 58
124 | 2 | 58
124 | 3 | 58
124 | 4 | 57
124 | 5 | 60
124 | 6 | 63
124 | 7 | 66
124 | 8 | 69
124 | 9 | 71
124 | 10 | 73
124 | 11 | 74
124 | 12 | 76
124 | 13 | 78
124 | 14 | 78
124 | 15 | 78
124 | 16 | 78
124 | 17 | 77
124 | 18 | 76
124 | 19 | 74
124 | 20 | 72
124 | 21 | 72
124 | 22 | 71
124 | 23 | 69
124 | 24 | 68 | 69.75 | -4.75 | 4.75
125 | 1 | 69
125 | 2 | 69
125 | 3 | 69
125 | 4 | 68
125 | 5 | 67
125 | 6 | 69
125 | 7 | 73
125 | 8 | 76
125 | 9 | 78
125 | 10 | 79
125 | 11 | 80
125 | 12 | 81
125 | 13 | 81
125 | 14 | 79
125 | 15 | 78
125 | 16 | 74
125 | 17 | 73
125 | 18 | 71
125 | 19 | 71
125 | 20 | 72
125 | 21 | 72
125 | 22 | 71
125 | 23 | 71
125 | 24 | 71 | 73.4167 | -8.4167 | 8.4167
126 | 1 | 71
126 | 2 | 71
126 | 3 | 72
126 | 4 | 72
126 | 5 | 72
126 | 6 | 71
126 | 7 | 74
126 | 8 | 78
126 | 9 | 80
126 | 10 | 81
126 | 11 | 83
126 | 12 | 84
126 | 13 | 84
126 | 14 | 84
126 | 15 | 84
126 | 16 | 83
126 | 17 | 82
126 | 18 | 80
126 | 19 | 77
126 | 20 | 76
126 | 21 | 75
126 | 22 | 75
126 | 23 | 74
126 | 24 | 74 | 77.375 | -12.375 | 12.375
127 | 1 | 74
127 | 2 | 73
127 | 3 | 72
127 | 4 | 73
127 | 5 | 70
127 | 6 | 71
127 | 7 | 71
127 | 8 | 73
127 | 9 | 76
127 | 10 | 75
127 | 11 | 77
127 | 12 | 82
127 | 13 | 81
127 | 14 | 80
127 | 15 | 79
127 | 16 | 75
127 | 17 | 79
127 | 18 | 78
127 | 19 | 77
127 | 20 | 76
127 | 21 | 73
127 | 22 | 73
127 | 23 | 72
127 | 24 | 72 | 75.0833 | -10.0833 | 10.0833
128 | 1 | 72
128 | 2 | 71
128 | 3 | 71
128 | 4 | 70
128 | 5 | 71
128 | 6 | 71
128 | 7 | 74
128 | 8 | 76
128 | 9 | 80
128 | 10 | 81
128 | 11 | 81
128 | 12 | 83
128 | 13 | 81
128 | 14 | 78
128 | 15 | 79
128 | 16 | 78
128 | 17 | 77
128 | 18 | 76
128 | 19 | 74
128 | 20 | 72
128 | 21 | 70
128 | 22 | 69
128 | 23 | 65
128 | 24 | 67 | 74.4583 | -9.4583 | 9.4583
129 | 1 | 67
129 | 2 | 66
129 | 3 | 65
129 | 4 | 65
129 | 5 | 65
129 | 6 | 65
129 | 7 | 70
129 | 8 | 73
129 | 9 | 75
129 | 10 | 76
129 | 11 | 77
129 | 12 | 79
129 | 13 | 81
129 | 14 | 82
129 | 15 | 80
129 | 16 | 82
129 | 17 | 82
129 | 18 | 79
129 | 19 | 75
129 | 20 | 76
129 | 21 | 74
129 | 22 | 72
129 | 23 | 71
129 | 24 | 70 | 73.625 | -8.625 | 8.625
130 | 1 | 69
130 | 2 | 68
130 | 3 | 67
130 | 4 | 66
130 | 5 | 65
130 | 6 | 67
130 | 7 | 71
130 | 8 | 75
130 | 9 | 78
130 | 10 | 80
130 | 11 | 80
130 | 12 | 82
130 | 13 | 83
130 | 14 | 83
130 | 15 | 83
130 | 16 | 80
130 | 17 | 82
130 | 18 | 80
130 | 19 | 75
130 | 20 | 73
130 | 21 | 73
130 | 22 | 73
130 | 23 | 72
130 | 24 | 71 | 74.8333 | -9.8333 | 9.8333
131 | 1 | 71
131 | 2 | 68
131 | 3 | 69
131 | 4 | 68
131 | 5 | 68
131 | 6 | 67
131 | 7 | 75
131 | 8 | 78
131 | 9 | 79
131 | 10 | 82
131 | 11 | 83
131 | 12 | 85
131 | 13 | 84
131 | 14 | 86
131 | 15 | 85
131 | 16 | 84
131 | 17 | 83
131 | 18 | 81
131 | 19 | 78
131 | 20 | 77
131 | 21 | 76
131 | 22 | 75
131 | 23 | 74
131 | 24 | 74 | 77.0833 | -12.0833 | 12.0833
132 | 1 | 74
132 | 2 | 73
132 | 3 | 71
132 | 4 | 69
132 | 5 | 73
132 | 6 | 75
132 | 7 | 76
132 | 8 | 78
132 | 9 | 80
132 | 10 | 83
132 | 11 | 83
132 | 12 | 85
132 | 13 | 86
132 | 14 | 87
132 | 15 | 86
132 | 16 | 85
132 | 17 | 84
132 | 18 | 82
132 | 19 | 78
132 | 20 | 77
132 | 21 | 76
132 | 22 | 75
132 | 23 | 74
132 | 24 | 73 | 78.4583 | -13.4583 | 13.4583
133 | 1 | 72
133 | 2 | 74
133 | 3 | 74
133 | 4 | 73
133 | 5 | 73
133 | 6 | 72
133 | 7 | 73
133 | 8 | 75
133 | 9 | 77
133 | 10 | 79
133 | 11 | 81
133 | 12 | 80
133 | 13 | 81
133 | 14 | 82
133 | 15 | 82
133 | 16 | 82
133 | 17 | 82
133 | 18 | 81
133 | 19 | 79
133 | 20 | 79
133 | 21 | 78
133 | 22 | 78
133 | 23 | 77
133 | 24 | 75 | 77.4583 | -12.4583 | 12.4583
134 | 1 | 74
134 | 2 | 74
134 | 3 | 74
134 | 4 | 75
134 | 5 | 75
134 | 6 | 75
134 | 7 | 77
134 | 8 | 80
134 | 9 | 82
134 | 10 | 84
134 | 11 | 85
134 | 12 | 86
134 | 13 | 87
134 | 14 | 87
134 | 15 | 84
134 | 16 | 85
134 | 17 | 82
134 | 18 | 82
134 | 19 | 77
134 | 20 | 74
134 | 21 | 76
134 | 22 | 75
134 | 23 | 74
134 | 24 | 73 | 79.0417 | -14.0417 | 14.0417
135 | 1 | 73
135 | 2 | 72
135 | 3 | 71
135 | 4 | 69
135 | 5 | 72
135 | 6 | 74
135 | 7 | 74
135 | 8 | 73
135 | 9 | 75
135 | 10 | 77
135 | 11 | 79
135 | 12 | 80
135 | 13 | 81
135 | 14 | 82
135 | 15 | 80
135 | 16 | 83
135 | 17 | 83
135 | 18 | 80
135 | 19 | 76
135 | 20 | 75
135 | 21 | 73
135 | 22 | 70
135 | 23 | 72
135 | 24 | 72 | 75.6667 | -10.6667 | 10.6667
136 | 1 | 70
136 | 2 | 70
136 | 3 | 65
136 | 4 | 60
136 | 5 | 59
136 | 6 | 61
136 | 7 | 75
136 | 8 | 77
136 | 9 | 79
136 | 10 | 81
136 | 11 | 82
136 | 12 | 84
136 | 13 | 84
136 | 14 | 86
136 | 15 | 87
136 | 16 | 87
136 | 17 | 85
136 | 18 | 83
136 | 19 | 78
136 | 20 | 75
136 | 21 | 74
136 | 22 | 73
136 | 23 | 72
136 | 24 | 72 | 75.7917 | -10.7917 | 10.7917
137 | 1 | 73
137 | 2 | 73
137 | 3 | 72
137 | 4 | 72
137 | 5 | 71
137 | 6 | 72
137 | 7 | 74
137 | 8 | 75
137 | 9 | 76
137 | 10 | 77
137 | 11 | 78
137 | 12 | 79
137 | 13 | 81
137 | 14 | 83
137 | 15 | 83
137 | 16 | 82
137 | 17 | 81
137 | 18 | 80
137 | 19 | 77
137 | 20 | 74
137 | 21 | 73
137 | 22 | 72
137 | 23 | 70
137 | 24 | 71 | 75.7917 | -10.7917 | 10.7917
138 | 1 | 72
138 | 2 | 69
138 | 3 | 68
138 | 4 | 67
138 | 5 | 66
138 | 6 | 66
138 | 7 | 69
138 | 8 | 70
138 | 9 | 71
138 | 10 | 72
138 | 11 | 73
138 | 12 | 74
138 | 13 | 75
138 | 14 | 75
138 | 15 | 74
138 | 16 | 77
138 | 17 | 74
138 | 18 | 73
138 | 19 | 69
138 | 20 | 67
138 | 21 | 67
138 | 22 | 69
138 | 23 | 66
138 | 24 | 66 | 70.375 | -5.375 | 5.375
139 | 1 | 67
139 | 2 | 64
139 | 3 | 63
139 | 4 | 61
139 | 5 | 59
139 | 6 | 59
139 | 7 | 70
139 | 8 | 74
139 | 9 | 77
139 | 10 | 79
139 | 11 | 81
139 | 12 | 82
139 | 13 | 83
139 | 14 | 84
139 | 15 | 82
139 | 16 | 83
139 | 17 | 80
139 | 18 | 78
139 | 19 | 76
139 | 20 | 74
139 | 21 | 73
139 | 22 | 72
139 | 23 | 71
139 | 24 | 69 | 73.375 | -8.375 | 8.375
140 | 1 | 67
140 | 2 | 67
140 | 3 | 66
140 | 4 | 65
140 | 5 | 65
140 | 6 | 66
140 | 7 | 75
140 | 8 | 77
140 | 9 | 79
140 | 10 | 78
140 | 11 | 81
140 | 12 | 84
140 | 13 | 85
140 | 14 | 85
140 | 15 | 86
140 | 16 | 86
140 | 17 | 86
140 | 18 | 85
140 | 19 | 82
140 | 20 | 79
140 | 21 | 78
140 | 22 | 76
140 | 23 | 75
140 | 24 | 71 | 76.8333 | -11.8333 | 11.8333
141 | 1 | 69
141 | 2 | 69
141 | 3 | 69
141 | 4 | 71
141 | 5 | 69
141 | 6 | 71
141 | 7 | 77
141 | 8 | 80
141 | 9 | 81
141 | 10 | 83
141 | 11 | 83
141 | 12 | 81
141 | 13 | 68
141 | 14 | 67
141 | 15 | 69
141 | 16 | 70
141 | 17 | 74
141 | 18 | 73
141 | 19 | 72
141 | 20 | 70
141 | 21 | 71
141 | 22 | 72
141 | 23 | 71
141 | 24 | 71 | 72.9583 | -7.9583 | 7.9583
142 | 1 | 71
142 | 2 | 70
142 | 3 | 69
142 | 4 | 68
142 | 5 | 69
142 | 6 | 69
142 | 7 | 73
142 | 8 | 74
142 | 9 | 77
142 | 10 | 82
142 | 11 | 85
142 | 12 | 85
142 | 13 | 87
142 | 14 | 88
142 | 15 | 87
142 | 16 | 87
142 | 17 | 86
142 | 18 | 83
142 | 19 | 81
142 | 20 | 79
142 | 21 | 77
142 | 22 | 76
142 | 23 | 75
142 | 24 | 75 | 78.0417 | -13.0417 | 13.0417
143 | 1 | 74
143 | 2 | 74
143 | 3 | 74
143 | 4 | 73
143 | 5 | 72
143 | 6 | 73
143 | 7 | 75
143 | 8 | 77
143 | 9 | 75
143 | 10 | 71
143 | 11 | 68
143 | 12 | 70
143 | 13 | 72
143 | 14 | 70
143 | 15 | 70
143 | 16 | 72
143 | 17 | 74
143 | 18 | 73
143 | 19 | 69
143 | 20 | 68
143 | 21 | 66
143 | 22 | 67
143 | 23 | 67
143 | 24 | 67 | 71.2917 | -6.2917 | 6.2917
144 | 1 | 68
144 | 2 | 68
144 | 3 | 67
144 | 4 | 67
144 | 5 | 66
144 | 6 | 68
144 | 7 | 73
144 | 8 | 76
144 | 9 | 77
144 | 10 | 78
144 | 11 | 78
144 | 12 | 80
144 | 13 | 81
144 | 14 | 82
144 | 15 | 83
144 | 16 | 82
144 | 17 | 82
144 | 18 | 80
144 | 19 | 76
144 | 20 | 73
144 | 21 | 74
144 | 22 | 73
144 | 23 | 73
144 | 24 | 71 | 74.8333 | -9.8333 | 9.8333
145 | 1 | 70
145 | 2 | 68
145 | 3 | 62
145 | 4 | 60
145 | 5 | 59
145 | 6 | 61
145 | 7 | 73
145 | 8 | 76
145 | 9 | 78
145 | 10 | 79
145 | 11 | 80
145 | 12 | 80
145 | 13 | 81
145 | 14 | 82
145 | 15 | 82
145 | 16 | 82
145 | 17 | 83
145 | 18 | 80
145 | 19 | 75
145 | 20 | 70
145 | 21 | 68
145 | 22 | 67
145 | 23 | 65
145 | 24 | 63 | 72.6667 | -7.6667 | 7.6667
146 | 1 | 64
146 | 2 | 61
146 | 3 | 60
146 | 4 | 60
146 | 5 | 61
146 | 6 | 63
146 | 7 | 74
146 | 8 | 78
146 | 9 | 80
146 | 10 | 82
146 | 11 | 83
146 | 12 | 84
146 | 13 | 85
146 | 14 | 86
146 | 15 | 85
146 | 16 | 85
146 | 17 | 85
146 | 18 | 83
146 | 19 | 80
146 | 20 | 76
146 | 21 | 74
146 | 22 | 72
146 | 23 | 71
146 | 24 | 69 | 75.0417 | -10.0417 | 10.0417
147 | 1 | 69
147 | 2 | 64
147 | 3 | 64
147 | 4 | 62
147 | 5 | 63
147 | 6 | 65
147 | 7 | 73
147 | 8 | 78
147 | 9 | 80
147 | 10 | 82
147 | 11 | 83
147 | 12 | 83
147 | 13 | 84
147 | 14 | 83
147 | 15 | 83
147 | 16 | 83
147 | 17 | 82
147 | 18 | 80
147 | 19 | 77
147 | 20 | 75
147 | 21 | 73
147 | 22 | 71
147 | 23 | 71
147 | 24 | 67 | 74.7917 | -9.7917 | 9.7917
148 | 1 | 65
148 | 2 | 64
148 | 3 | 65
148 | 4 | 65
148 | 5 | 64
148 | 6 | 64
148 | 7 | 75
148 | 8 | 78
148 | 9 | 79
148 | 10 | 81
148 | 11 | 82
148 | 12 | 83
148 | 13 | 84
148 | 14 | 85
148 | 15 | 85
148 | 16 | 85
148 | 17 | 84
148 | 18 | 82
148 | 19 | 78
148 | 20 | 76
148 | 21 | 73
148 | 22 | 71
148 | 23 | 71
148 | 24 | 70 | 75.375 | -10.375 | 10.375
149 | 1 | 69
149 | 2 | 66
149 | 3 | 65
149 | 4 | 66
149 | 5 | 66
149 | 6 | 67
149 | 7 | 75
149 | 8 | 78
149 | 9 | 81
149 | 10 | 83
149 | 11 | 85
149 | 12 | 87
149 | 13 | 87
149 | 14 | 87
149 | 15 | 86
149 | 16 | 86
149 | 17 | 84
149 | 18 | 83
149 | 19 | 80
149 | 20 | 76
149 | 21 | 76
149 | 22 | 75
149 | 23 | 73
149 | 24 | 72 | 77.2083 | -12.2083 | 12.2083
150 | 1 | 71
150 | 2 | 72
150 | 3 | 71
150 | 4 | 71
150 | 5 | 72
150 | 6 | 73
150 | 7 | 77
150 | 8 | 80
150 | 9 | 81
150 | 10 | 83
150 | 11 | 86
150 | 12 | 87
150 | 13 | 89
150 | 14 | 88
150 | 15 | 88
150 | 16 | 88
150 | 17 | 86
150 | 18 | 84
150 | 19 | 81
150 | 20 | 78
150 | 21 | 76
150 | 22 | 75
150 | 23 | 74
150 | 24 | 73 | 79.3333 | -14.3333 | 14.3333
151 | 1 | 74
151 | 2 | 74
151 | 3 | 73
151 | 4 | 74
151 | 5 | 73
151 | 6 | 74
151 | 7 | 77
151 | 8 | 80
151 | 9 | 82
151 | 10 | 85
151 | 11 | 87
151 | 12 | 88
151 | 13 | 89
151 | 14 | 91
151 | 15 | 91
151 | 16 | 90
151 | 17 | 88
151 | 18 | 86
151 | 19 | 81
151 | 20 | 77
151 | 21 | 75
151 | 22 | 74
151 | 23 | 74
151 | 24 | 73 | 80.4167 | -15.4167 | 15.4167
152 | 1 | 73
152 | 2 | 73
152 | 3 | 69
152 | 4 | 69
152 | 5 | 67
152 | 6 | 67
152 | 7 | 77
152 | 8 | 80
152 | 9 | 82
152 | 10 | 83
152 | 11 | 85
152 | 12 | 86
152 | 13 | 87
152 | 14 | 84
152 | 15 | 84
152 | 16 | 81
152 | 17 | 76
152 | 18 | 79
152 | 19 | 78
152 | 20 | 76
152 | 21 | 76
152 | 22 | 75
152 | 23 | 73
152 | 24 | 73 | 77.2083 | -12.2083 | 12.2083
153 | 1 | 73
153 | 2 | 70
153 | 3 | 64
153 | 4 | 64
153 | 5 | 63
153 | 6 | 64
153 | 7 | 75
153 | 8 | 79
153 | 9 | 80
153 | 10 | 83
153 | 11 | 85
153 | 12 | 85
153 | 13 | 85
153 | 14 | 87
153 | 15 | 87
153 | 16 | 87
153 | 17 | 84
153 | 18 | 83
153 | 19 | 81
153 | 20 | 77
153 | 21 | 75
153 | 22 | 72
153 | 23 | 70
153 | 24 | 70 | 76.7917 | -11.7917 | 11.7917
154 | 1 | 68
154 | 2 | 68
154 | 3 | 67
154 | 4 | 67
154 | 5 | 68
154 | 6 | 67
154 | 7 | 79
154 | 8 | 82
154 | 9 | 83
154 | 10 | 85
154 | 11 | 87
154 | 12 | 88
154 | 13 | 89
154 | 14 | 91
154 | 15 | 90
154 | 16 | 90
154 | 17 | 87
154 | 18 | 85
154 | 19 | 80
154 | 20 | 77
154 | 21 | 75
154 | 22 | 74
154 | 23 | 73
154 | 24 | 75 | 78.9583 | -13.9583 | 13.9583
155 | 1 | 74
155 | 2 | 71
155 | 3 | 75
155 | 4 | 73
155 | 5 | 75
155 | 6 | 77
155 | 7 | 81
155 | 8 | 83
155 | 9 | 85
155 | 10 | 87
155 | 11 | 88
155 | 12 | 89
155 | 13 | 93
155 | 14 | 93
155 | 15 | 94
155 | 16 | 93
155 | 17 | 89
155 | 18 | 83
155 | 19 | 79
155 | 20 | 75
155 | 21 | 74
155 | 22 | 75
155 | 23 | 75
155 | 24 | 76 | 81.5417 | -16.5417 | 16.5417
156 | 1 | 76
156 | 2 | 75
156 | 3 | 75
156 | 4 | 74
156 | 5 | 75
156 | 6 | 75
156 | 7 | 81
156 | 8 | 84
156 | 9 | 85
156 | 10 | 87
156 | 11 | 88
156 | 12 | 87
156 | 13 | 76
156 | 14 | 76
156 | 15 | 77
156 | 16 | 78
156 | 17 | 80
156 | 18 | 78
156 | 19 | 75
156 | 20 | 74
156 | 21 | 71
156 | 22 | 70
156 | 23 | 72
156 | 24 | 70 | 77.4583 | -12.4583 | 12.4583
157 | 1 | 70
157 | 2 | 71
157 | 3 | 70
157 | 4 | 71
157 | 5 | 70
157 | 6 | 72
157 | 7 | 80
157 | 8 | 82
157 | 9 | 84
157 | 10 | 85
157 | 11 | 87
157 | 12 | 87
157 | 13 | 88
157 | 14 | 82
157 | 15 | 85
157 | 16 | 85
157 | 17 | 84
157 | 18 | 82
157 | 19 | 80
157 | 20 | 78
157 | 21 | 78
157 | 22 | 77
157 | 23 | 77
157 | 24 | 75 | 79.1667 | -14.1667 | 14.1667
158 | 1 | 74
158 | 2 | 75
158 | 3 | 74
158 | 4 | 73
158 | 5 | 72
158 | 6 | 74
158 | 7 | 79
158 | 8 | 82
158 | 9 | 86
158 | 10 | 86
158 | 11 | 88
158 | 12 | 87
158 | 13 | 84
158 | 14 | 87
158 | 15 | 89
158 | 16 | 83
158 | 17 | 85
158 | 18 | 84
158 | 19 | 80
158 | 20 | 77
158 | 21 | 75
158 | 22 | 76
158 | 23 | 75
158 | 24 | 73 | 79.9167 | -14.9167 | 14.9167
159 | 1 | 73
159 | 2 | 73
159 | 3 | 73
159 | 4 | 71
159 | 5 | 70
159 | 6 | 71
159 | 7 | 79
159 | 8 | 82
159 | 9 | 85
159 | 10 | 86
159 | 11 | 87
159 | 12 | 87
159 | 13 | 90
159 | 14 | 88
159 | 15 | 87
159 | 16 | 82
159 | 17 | 78
159 | 18 | 78
159 | 19 | 73
159 | 20 | 74
159 | 21 | 74
159 | 22 | 74
159 | 23 | 72
159 | 24 | 73 | 78.3333 | -13.3333 | 13.3333
160 | 1 | 73
160 | 2 | 73
160 | 3 | 72
160 | 4 | 71
160 | 5 | 71
160 | 6 | 73
160 | 7 | 80
160 | 8 | 83
160 | 9 | 84
160 | 10 | 86
160 | 11 | 87
160 | 12 | 88
160 | 13 | 89
160 | 14 | 88
160 | 15 | 88
160 | 16 | 89
160 | 17 | 87
160 | 18 | 85
160 | 19 | 82
160 | 20 | 80
160 | 21 | 80
160 | 22 | 79
160 | 23 | 78
160 | 24 | 78 | 81 | -16 | 16
161 | 1 | 77
161 | 2 | 77
161 | 3 | 77
161 | 4 | 74
161 | 5 | 73
161 | 6 | 75
161 | 7 | 82
161 | 8 | 84
161 | 9 | 87
161 | 10 | 86
161 | 11 | 88
161 | 12 | 89
161 | 13 | 92
161 | 14 | 89
161 | 15 | 90
161 | 16 | 89
161 | 17 | 88
161 | 18 | 85
161 | 19 | 82
161 | 20 | 81
161 | 21 | 81
161 | 22 | 80
161 | 23 | 78
161 | 24 | 77 | 82.5417 | -17.5417 | 17.5417
162 | 1 | 77
162 | 2 | 76
162 | 3 | 76
162 | 4 | 75
162 | 5 | 75
162 | 6 | 77
162 | 7 | 81
162 | 8 | 84
162 | 9 | 86
162 | 10 | 89
162 | 11 | 90
162 | 12 | 89
162 | 13 | 91
162 | 14 | 89
162 | 15 | 92
162 | 16 | 91
162 | 17 | 91
162 | 18 | 88
162 | 19 | 85
162 | 20 | 83
162 | 21 | 82
162 | 22 | 79
162 | 23 | 76
162 | 24 | 79 | 83.375 | -18.375 | 18.375
163 | 1 | 78
163 | 2 | 74
163 | 3 | 75
163 | 4 | 74
163 | 5 | 76
163 | 6 | 79
163 | 7 | 82
163 | 8 | 86
163 | 9 | 89
163 | 10 | 89
163 | 11 | 89
163 | 12 | 90
163 | 13 | 90
163 | 14 | 90
163 | 15 | 87
163 | 16 | 84
163 | 17 | 83
163 | 18 | 72
163 | 19 | 72
163 | 20 | 73
163 | 21 | 71
163 | 22 | 71
163 | 23 | 72
163 | 24 | 71 | 79.875 | -14.875 | 14.875
164 | 1 | 70
164 | 2 | 70
164 | 3 | 70
164 | 4 | 71
164 | 5 | 70
164 | 6 | 72
164 | 7 | 75
164 | 8 | 81
164 | 9 | 82
164 | 10 | 84
164 | 11 | 85
164 | 12 | 88
164 | 13 | 88
164 | 14 | 91
164 | 15 | 91
164 | 16 | 92
164 | 17 | 91
164 | 18 | 88
164 | 19 | 81
164 | 20 | 76
164 | 21 | 75
164 | 22 | 75
164 | 23 | 76
164 | 24 | 73 | 79.7917 | -14.7917 | 14.7917
165 | 1 | 72
165 | 2 | 70
165 | 3 | 70
165 | 4 | 67
165 | 5 | 68
165 | 6 | 73
165 | 7 | 82
165 | 8 | 85
165 | 9 | 87
165 | 10 | 88
165 | 11 | 90
165 | 12 | 91
165 | 13 | 92
165 | 14 | 92
165 | 15 | 92
165 | 16 | 92
165 | 17 | 90
165 | 18 | 88
165 | 19 | 85
165 | 20 | 82
165 | 21 | 81
165 | 22 | 80
165 | 23 | 80
165 | 24 | 78 | 82.2917 | -17.2917 | 17.2917
166 | 1 | 77
166 | 2 | 74
166 | 3 | 71
166 | 4 | 71
166 | 5 | 71
166 | 6 | 74
166 | 7 | 82
166 | 8 | 86
166 | 9 | 86
166 | 10 | 86
166 | 11 | 88
166 | 12 | 89
166 | 13 | 86
166 | 14 | 81
166 | 15 | 84
166 | 16 | 87
166 | 17 | 86
166 | 18 | 85
166 | 19 | 82
166 | 20 | 80
166 | 21 | 79
166 | 22 | 78
166 | 23 | 78
166 | 24 | 75 | 80.6667 | -15.6667 | 15.6667
167 | 1 | 72
167 | 2 | 72
167 | 3 | 72
167 | 4 | 71
167 | 5 | 71
167 | 6 | 74
167 | 7 | 82
167 | 8 | 85
167 | 9 | 84
167 | 10 | 86
167 | 11 | 88
167 | 12 | 87
167 | 13 | 80
167 | 14 | 76
167 | 15 | 76
167 | 16 | 79
167 | 17 | 81
167 | 18 | 80
167 | 19 | 78
167 | 20 | 77
167 | 21 | 77
167 | 22 | 76
167 | 23 | 76
167 | 24 | 75 | 78.125 | -13.125 | 13.125
168 | 1 | 74
168 | 2 | 72
168 | 3 | 71
168 | 4 | 70
168 | 5 | 71
168 | 6 | 73
168 | 7 | 82
168 | 8 | 84
168 | 9 | 86
168 | 10 | 82
168 | 11 | 87
168 | 12 | 87
168 | 13 | 88
168 | 14 | 71
168 | 15 | 72
168 | 16 | 73
168 | 17 | 75
168 | 18 | 76
168 | 19 | 75
168 | 20 | 73
168 | 21 | 73
168 | 22 | 74
168 | 23 | 73
168 | 24 | 74 | 76.5 | -11.5 | 11.5
169 | 1 | 73
169 | 2 | 72
169 | 3 | 71
169 | 4 | 70
169 | 5 | 72
169 | 6 | 74
169 | 7 | 81
169 | 8 | 81
169 | 9 | 85
169 | 10 | 85
169 | 11 | 85
169 | 12 | 87
169 | 13 | 85
169 | 14 | 79
169 | 15 | 82
169 | 16 | 80
169 | 17 | 81
169 | 18 | 82
169 | 19 | 78
169 | 20 | 76
169 | 21 | 74
169 | 22 | 74
169 | 23 | 73
169 | 24 | 73 | 78.0417 | -13.0417 | 13.0417
170 | 1 | 72
170 | 2 | 72
170 | 3 | 71
170 | 4 | 71
170 | 5 | 72
170 | 6 | 73
170 | 7 | 81
170 | 8 | 84
170 | 9 | 84
170 | 10 | 86
170 | 11 | 83
170 | 12 | 74
170 | 13 | 86
170 | 14 | 87
170 | 15 | 87
170 | 16 | 87
170 | 17 | 86
170 | 18 | 84
170 | 19 | 80
170 | 20 | 78
170 | 21 | 77
170 | 22 | 80
170 | 23 | 79
170 | 24 | 77 | 79.625 | -14.625 | 14.625
171 | 1 | 75
171 | 2 | 74
171 | 3 | 73
171 | 4 | 73
171 | 5 | 73
171 | 6 | 74
171 | 7 | 79
171 | 8 | 79
171 | 9 | 79
171 | 10 | 81
171 | 11 | 84
171 | 12 | 84
171 | 13 | 83
171 | 14 | 84
171 | 15 | 85
171 | 16 | 83
171 | 17 | 82
171 | 18 | 81
171 | 19 | 79
171 | 20 | 78
171 | 21 | 77
171 | 22 | 77
171 | 23 | 76
171 | 24 | 76 | 78.7083 | -13.7083 | 13.7083
172 | 1 | 76
172 | 2 | 76
172 | 3 | 75
172 | 4 | 74
172 | 5 | 75
172 | 6 | 75
172 | 7 | 81
172 | 8 | 83
172 | 9 | 82
172 | 10 | 82
172 | 11 | 84
172 | 12 | 85
172 | 13 | 85
172 | 14 | 78
172 | 15 | 76
172 | 16 | 77
172 | 17 | 78
172 | 18 | 78
172 | 19 | 76
172 | 20 | 76
172 | 21 | 74
172 | 22 | 74
172 | 23 | 73
172 | 24 | 74 | 77.7917 | -12.7917 | 12.7917
173 | 1 | 75
173 | 2 | 75
173 | 3 | 76
173 | 4 | 76
173 | 5 | 73
173 | 6 | 75
173 | 7 | 79
173 | 8 | 80
173 | 9 | 83
173 | 10 | 84
173 | 11 | 80
173 | 12 | 79
173 | 13 | 83
173 | 14 | 85
173 | 15 | 87
173 | 16 | 84
173 | 17 | 84
173 | 18 | 78
173 | 19 | 77
173 | 20 | 76
173 | 21 | 77
173 | 22 | 76
173 | 23 | 76
173 | 24 | 74 | 78.8333 | -13.8333 | 13.8333
174 | 1 | 74
174 | 2 | 73
174 | 3 | 74
174 | 4 | 75
174 | 5 | 73
174 | 6 | 76
174 | 7 | 82
174 | 8 | 85
174 | 9 | 86
174 | 10 | 88
174 | 11 | 86
174 | 12 | 90
174 | 13 | 91
174 | 14 | 90
174 | 15 | 88
174 | 16 | 89
174 | 17 | 87
174 | 18 | 86
174 | 19 | 84
174 | 20 | 82
174 | 21 | 81
174 | 22 | 81
174 | 23 | 81
174 | 24 | 81 | 82.625 | -17.625 | 17.625
175 | 1 | 80
175 | 2 | 80
175 | 3 | 80
175 | 4 | 79
175 | 5 | 79
175 | 6 | 79
175 | 7 | 82
175 | 8 | 86
175 | 9 | 86
175 | 10 | 88
175 | 11 | 90
175 | 12 | 91
175 | 13 | 90
175 | 14 | 90
175 | 15 | 90
175 | 16 | 88
175 | 17 | 88
175 | 18 | 87
175 | 19 | 84
175 | 20 | 82
175 | 21 | 81
175 | 22 | 81
175 | 23 | 82
175 | 24 | 81 | 84.3333 | -19.3333 | 19.3333
176 | 1 | 81
176 | 2 | 81
176 | 3 | 81
176 | 4 | 81
176 | 5 | 81
176 | 6 | 82
176 | 7 | 84
176 | 8 | 86
176 | 9 | 87
176 | 10 | 89
176 | 11 | 89
176 | 12 | 91
176 | 13 | 91
176 | 14 | 90
176 | 15 | 90
176 | 16 | 91
176 | 17 | 89
176 | 18 | 87
176 | 19 | 84
176 | 20 | 83
176 | 21 | 82
176 | 22 | 81
176 | 23 | 81
176 | 24 | 81 | 85.125 | -20.125 | 20.125
177 | 1 | 79
177 | 2 | 79
177 | 3 | 79
177 | 4 | 78
177 | 5 | 78
177 | 6 | 79
177 | 7 | 82
177 | 8 | 85
177 | 9 | 86
177 | 10 | 88
177 | 11 | 79
177 | 12 | 85
177 | 13 | 87
177 | 14 | 89
177 | 15 | 88
177 | 16 | 90
177 | 17 | 89
177 | 18 | 87
177 | 19 | 83
177 | 20 | 82
177 | 21 | 80
177 | 22 | 77
177 | 23 | 76
177 | 24 | 76 | 82.5417 | -17.5417 | 17.5417
178 | 1 | 76
178 | 2 | 76
178 | 3 | 76
178 | 4 | 75
178 | 5 | 74
178 | 6 | 74
178 | 7 | 75
178 | 8 | 77
178 | 9 | 79
178 | 10 | 81
178 | 11 | 82
178 | 12 | 84
178 | 13 | 86
178 | 14 | 87
178 | 15 | 87
178 | 16 | 87
178 | 17 | 86
178 | 18 | 85
178 | 19 | 80
178 | 20 | 73
178 | 21 | 71
178 | 22 | 68
178 | 23 | 66
178 | 24 | 65 | 77.9167 | -12.9167 | 12.9167
179 | 1 | 64
179 | 2 | 65
179 | 3 | 64
179 | 4 | 64
179 | 5 | 63
179 | 6 | 67
179 | 7 | 77
179 | 8 | 81
179 | 9 | 84
179 | 10 | 84
179 | 11 | 88
179 | 12 | 87
179 | 13 | 88
179 | 14 | 89
179 | 15 | 90
179 | 16 | 90
179 | 17 | 89
179 | 18 | 88
179 | 19 | 83
179 | 20 | 81
179 | 21 | 81
179 | 22 | 80
179 | 23 | 79
179 | 24 | 79 | 79.375 | -14.375 | 14.375
180 | 1 | 76
180 | 2 | 74
180 | 3 | 75
180 | 4 | 73
180 | 5 | 72
180 | 6 | 75
180 | 7 | 82
180 | 8 | 85
180 | 9 | 87
180 | 10 | 90
180 | 11 | 90
180 | 12 | 91
180 | 13 | 91
180 | 14 | 90
180 | 15 | 91
180 | 16 | 80
180 | 17 | 79
180 | 18 | 80
180 | 19 | 80
180 | 20 | 81
180 | 21 | 81
180 | 22 | 81
180 | 23 | 79
180 | 24 | 79 | 81.75 | -16.75 | 16.75
181 | 1 | 77
181 | 2 | 74
181 | 3 | 74
181 | 4 | 74
181 | 5 | 73
181 | 6 | 75
181 | 7 | 83
181 | 8 | 85
181 | 9 | 86
181 | 10 | 89
181 | 11 | 89
181 | 12 | 89
181 | 13 | 88
181 | 14 | 87
181 | 15 | 92
181 | 16 | 81
181 | 17 | 81
181 | 18 | 83
181 | 19 | 82
181 | 20 | 78
181 | 21 | 78
181 | 22 | 76
181 | 23 | 75
181 | 24 | 75 | 81 | -16 | 16
182 | 1 | 74
182 | 2 | 73
182 | 3 | 73
182 | 4 | 72
182 | 5 | 71
182 | 6 | 71
182 | 7 | 75
182 | 8 | 79
182 | 9 | 84
182 | 10 | 85
182 | 11 | 86
182 | 12 | 87
182 | 13 | 87
182 | 14 | 88
182 | 15 | 88
182 | 16 | 87
182 | 17 | 86
182 | 18 | 85
182 | 19 | 82
182 | 20 | 80
182 | 21 | 77
182 | 22 | 75
182 | 23 | 73
182 | 24 | 71 | 79.5417 | -14.5417 | 14.5417
183 | 1 | 71
183 | 2 | 72
183 | 3 | 72
183 | 4 | 71
183 | 5 | 71
183 | 6 | 70
183 | 7 | 75
183 | 8 | 79
183 | 9 | 84
183 | 10 | 86
183 | 11 | 87
183 | 12 | 89
183 | 13 | 85
183 | 14 | 81
183 | 15 | 77
183 | 16 | 78
183 | 17 | 79
183 | 18 | 80
183 | 19 | 77
183 | 20 | 74
183 | 21 | 71
183 | 22 | 71
183 | 23 | 72
183 | 24 | 72 | 76.8333 | -11.8333 | 11.8333
184 | 1 | 71
184 | 2 | 71
184 | 3 | 70
184 | 4 | 70
184 | 5 | 70
184 | 6 | 70
184 | 7 | 75
184 | 8 | 79
184 | 9 | 84
184 | 10 | 84
184 | 11 | 84
184 | 12 | 84
184 | 13 | 85
184 | 14 | 86
184 | 15 | 87
184 | 16 | 84
184 | 17 | 81
184 | 18 | 78
184 | 19 | 77
184 | 20 | 77
184 | 21 | 76
184 | 22 | 75
184 | 23 | 74
184 | 24 | 73 | 77.7083 | -12.7083 | 12.7083
185 | 1 | 73
185 | 2 | 72
185 | 3 | 72
185 | 4 | 72
185 | 5 | 72
185 | 6 | 72
185 | 7 | 77
185 | 8 | 81
185 | 9 | 86
185 | 10 | 87
185 | 11 | 87
185 | 12 | 88
185 | 13 | 84
185 | 14 | 80
185 | 15 | 76
185 | 16 | 77
185 | 17 | 77
185 | 18 | 78
185 | 19 | 76
185 | 20 | 75
185 | 21 | 73
185 | 22 | 73
185 | 23 | 72
185 | 24 | 72 | 77.1667 | -12.1667 | 12.1667
186 | 1 | 72
186 | 2 | 73
186 | 3 | 73
186 | 4 | 73
186 | 5 | 73
186 | 6 | 73
186 | 7 | 77
186 | 8 | 81
186 | 9 | 85
186 | 10 | 81
186 | 11 | 76
186 | 12 | 72
186 | 13 | 75
186 | 14 | 79
186 | 15 | 82
186 | 16 | 81
186 | 17 | 81
186 | 18 | 80
186 | 19 | 79
186 | 20 | 79
186 | 21 | 78
186 | 22 | 77
186 | 23 | 77
186 | 24 | 76 | 77.2083 | -12.2083 | 12.2083
187 | 1 | 76
187 | 2 | 76
187 | 3 | 76
187 | 4 | 76
187 | 5 | 75
187 | 6 | 75
187 | 7 | 77
187 | 8 | 80
187 | 9 | 82
187 | 10 | 83
187 | 11 | 85
187 | 12 | 86
187 | 13 | 87
187 | 14 | 87
187 | 15 | 88
187 | 16 | 87
187 | 17 | 86
187 | 18 | 85
187 | 19 | 82
187 | 20 | 80
187 | 21 | 77
187 | 22 | 78
187 | 23 | 78
187 | 24 | 79 | 80.875 | -15.875 | 15.875
188 | 1 | 78
188 | 2 | 78
188 | 3 | 77
188 | 4 | 77
188 | 5 | 77
188 | 6 | 77
188 | 7 | 80
188 | 8 | 83
188 | 9 | 86
188 | 10 | 87
188 | 11 | 88
188 | 12 | 89
188 | 13 | 90
188 | 14 | 90
188 | 15 | 91
188 | 16 | 91
188 | 17 | 90
188 | 18 | 90
188 | 19 | 87
188 | 20 | 83
188 | 21 | 80
188 | 22 | 78
188 | 23 | 77
188 | 24 | 75 | 83.2917 | -18.2917 | 18.2917
189 | 1 | 75
189 | 2 | 76
189 | 3 | 76
189 | 4 | 76
189 | 5 | 76
189 | 6 | 76
189 | 7 | 79
189 | 8 | 83
189 | 9 | 86
189 | 10 | 88
189 | 11 | 89
189 | 12 | 91
189 | 13 | 92
189 | 14 | 92
189 | 15 | 93
189 | 16 | 93
189 | 17 | 92
189 | 18 | 92
189 | 19 | 88
189 | 20 | 85
189 | 21 | 81
189 | 22 | 80
189 | 23 | 80
189 | 24 | 79 | 84.0833 | -19.0833 | 19.0833
190 | 1 | 78
190 | 2 | 78
190 | 3 | 77
190 | 4 | 77
190 | 5 | 77
190 | 6 | 77
190 | 7 | 81
190 | 8 | 85
190 | 9 | 89
190 | 10 | 90
190 | 11 | 91
190 | 12 | 92
190 | 13 | 91
190 | 14 | 89
190 | 15 | 88
190 | 16 | 88
190 | 17 | 89
190 | 18 | 89
190 | 19 | 87
190 | 20 | 84
190 | 21 | 82
190 | 22 | 81
190 | 23 | 81
190 | 24 | 80 | 84.2083 | -19.2083 | 19.2083
191 | 1 | 79
191 | 2 | 77
191 | 3 | 76
191 | 4 | 76
191 | 5 | 75
191 | 6 | 75
191 | 7 | 79
191 | 8 | 84
191 | 9 | 88
191 | 10 | 89
191 | 11 | 91
191 | 12 | 92
191 | 13 | 93
191 | 14 | 93
191 | 15 | 94
191 | 16 | 92
191 | 17 | 91
191 | 18 | 89
191 | 19 | 86
191 | 20 | 84
191 | 21 | 81
191 | 22 | 80
191 | 23 | 79
191 | 24 | 78 | 84.2083 | -19.2083 | 19.2083
192 | 1 | 77
192 | 2 | 75
192 | 3 | 74
192 | 4 | 74
192 | 5 | 74
192 | 6 | 74
192 | 7 | 78
192 | 8 | 82
192 | 9 | 86
192 | 10 | 88
192 | 11 | 90
192 | 12 | 92
192 | 13 | 93
192 | 14 | 93
192 | 15 | 94
192 | 16 | 92
192 | 17 | 91
192 | 18 | 89
192 | 19 | 86
192 | 20 | 83
192 | 21 | 80
192 | 22 | 77
192 | 23 | 73
192 | 24 | 70 | 82.7083 | -17.7083 | 17.7083
193 | 1 | 70
193 | 2 | 70
193 | 3 | 70
193 | 4 | 70
193 | 5 | 71
193 | 6 | 71
193 | 7 | 76
193 | 8 | 82
193 | 9 | 87
193 | 10 | 88
193 | 11 | 90
193 | 12 | 91
193 | 13 | 91
193 | 14 | 92
193 | 15 | 92
193 | 16 | 91
193 | 17 | 90
193 | 18 | 89
193 | 19 | 87
193 | 20 | 84
193 | 21 | 82
193 | 22 | 81
193 | 23 | 80
193 | 24 | 79 | 82.25 | -17.25 | 17.25
194 | 1 | 78
194 | 2 | 78
194 | 3 | 77
194 | 4 | 76
194 | 5 | 74
194 | 6 | 73
194 | 7 | 78
194 | 8 | 82
194 | 9 | 87
194 | 10 | 88
194 | 11 | 90
194 | 12 | 91
194 | 13 | 89
194 | 14 | 86
194 | 15 | 84
194 | 16 | 84
194 | 17 | 84
194 | 18 | 84
194 | 19 | 83
194 | 20 | 83
194 | 21 | 82
194 | 22 | 80
194 | 23 | 79
194 | 24 | 77 | 81.9583 | -16.9583 | 16.9583
195 | 1 | 75
195 | 2 | 74
195 | 3 | 72
195 | 4 | 72
195 | 5 | 73
195 | 6 | 73
195 | 7 | 77
195 | 8 | 82
195 | 9 | 86
195 | 10 | 88
195 | 11 | 89
195 | 12 | 91
195 | 13 | 92
195 | 14 | 92
195 | 15 | 93
195 | 16 | 93
195 | 17 | 92
195 | 18 | 92
195 | 19 | 88
195 | 20 | 83
195 | 21 | 79
195 | 22 | 79
195 | 23 | 80
195 | 24 | 80 | 83.125 | -18.125 | 18.125
196 | 1 | 80
196 | 2 | 79
196 | 3 | 79
196 | 4 | 79
196 | 5 | 79
196 | 6 | 79
196 | 7 | 77
196 | 8 | 75
196 | 9 | 73
196 | 10 | 74
196 | 11 | 74
196 | 12 | 75
196 | 13 | 79
196 | 14 | 84
196 | 15 | 88
196 | 16 | 88
196 | 17 | 87
196 | 18 | 87
196 | 19 | 85
196 | 20 | 82
196 | 21 | 80
196 | 22 | 80
196 | 23 | 80
196 | 24 | 80 | 80.125 | -15.125 | 15.125
197 | 1 | 79
197 | 2 | 78
197 | 3 | 77
197 | 4 | 76
197 | 5 | 76
197 | 6 | 75
197 | 7 | 79
197 | 8 | 82
197 | 9 | 86
197 | 10 | 86
197 | 11 | 87
197 | 12 | 87
197 | 13 | 88
197 | 14 | 90
197 | 15 | 91
197 | 16 | 89
197 | 17 | 86
197 | 18 | 84
197 | 19 | 83
197 | 20 | 83
197 | 21 | 82
197 | 22 | 81
197 | 23 | 81
197 | 24 | 80 | 82.75 | -17.75 | 17.75
198 | 1 | 79
198 | 2 | 77
198 | 3 | 76
198 | 4 | 76
198 | 5 | 76
198 | 6 | 76
198 | 7 | 80
198 | 8 | 83
198 | 9 | 87
198 | 10 | 88
198 | 11 | 90
198 | 12 | 91
198 | 13 | 91
198 | 14 | 92
198 | 15 | 92
198 | 16 | 90
198 | 17 | 87
198 | 18 | 85
198 | 19 | 82
198 | 20 | 80
198 | 21 | 77
198 | 22 | 77
198 | 23 | 76
198 | 24 | 76 | 82.6667 | -17.6667 | 17.6667
199 | 1 | 76
199 | 2 | 76
199 | 3 | 76
199 | 4 | 76
199 | 5 | 76
199 | 6 | 76
199 | 7 | 79
199 | 8 | 83
199 | 9 | 86
199 | 10 | 87
199 | 11 | 87
199 | 12 | 88
199 | 13 | 88
199 | 14 | 88
199 | 15 | 88
199 | 16 | 85
199 | 17 | 83
199 | 18 | 80
199 | 19 | 79
199 | 20 | 79
199 | 21 | 78
199 | 22 | 77
199 | 23 | 76
199 | 24 | 75 | 80.9167 | -15.9167 | 15.9167
200 | 1 | 75
200 | 2 | 75
200 | 3 | 75
200 | 4 | 75
200 | 5 | 74
200 | 6 | 74
200 | 7 | 78
200 | 8 | 82
200 | 9 | 86
200 | 10 | 88
200 | 11 | 89
200 | 12 | 91
200 | 13 | 92
200 | 14 | 92
200 | 15 | 93
200 | 16 | 92
200 | 17 | 92
200 | 18 | 91
200 | 19 | 88
200 | 20 | 85
200 | 21 | 82
200 | 22 | 81
200 | 23 | 81
200 | 24 | 80 | 83.7917 | -18.7917 | 18.7917
201 | 1 | 79
201 | 2 | 79
201 | 3 | 78
201 | 4 | 78
201 | 5 | 77
201 | 6 | 77
201 | 7 | 80
201 | 8 | 84
201 | 9 | 87
201 | 10 | 89
201 | 11 | 90
201 | 12 | 92
201 | 13 | 93
201 | 14 | 94
201 | 15 | 95
201 | 16 | 90
201 | 17 | 86
201 | 18 | 81
201 | 19 | 81
201 | 20 | 81
201 | 21 | 81
201 | 22 | 80
201 | 23 | 80
201 | 24 | 79 | 83.7917 | -18.7917 | 18.7917
202 | 1 | 78
202 | 2 | 77
202 | 3 | 76
202 | 4 | 76
202 | 5 | 77
202 | 6 | 77
202 | 7 | 80
202 | 8 | 84
202 | 9 | 87
202 | 10 | 88
202 | 11 | 88
202 | 12 | 89
202 | 13 | 86
202 | 14 | 84
202 | 15 | 81
202 | 16 | 81
202 | 17 | 80
202 | 18 | 80
202 | 19 | 79
202 | 20 | 78
202 | 21 | 77
202 | 22 | 76
202 | 23 | 75
202 | 24 | 74 | 80.3333 | -15.3333 | 15.3333
203 | 1 | 74
203 | 2 | 74
203 | 3 | 74
203 | 4 | 75
203 | 5 | 76
203 | 6 | 77
203 | 7 | 79
203 | 8 | 82
203 | 9 | 84
203 | 10 | 85
203 | 11 | 87
203 | 12 | 88
203 | 13 | 88
203 | 14 | 88
203 | 15 | 88
203 | 16 | 88
203 | 17 | 87
203 | 18 | 87
203 | 19 | 85
203 | 20 | 83
203 | 21 | 81
203 | 22 | 80
203 | 23 | 79
203 | 24 | 78 | 81.9583 | -16.9583 | 16.9583
204 | 1 | 77
204 | 2 | 75
204 | 3 | 74
204 | 4 | 74
204 | 5 | 75
204 | 6 | 75
204 | 7 | 79
204 | 8 | 83
204 | 9 | 87
204 | 10 | 85
204 | 11 | 84
204 | 12 | 82
204 | 13 | 82
204 | 14 | 82
204 | 15 | 82
204 | 16 | 82
204 | 17 | 83
204 | 18 | 83
204 | 19 | 82
204 | 20 | 81
204 | 21 | 80
204 | 22 | 79
204 | 23 | 79
204 | 24 | 78 | 80.125 | -15.125 | 15.125
205 | 1 | 76
205 | 2 | 74
205 | 3 | 72
205 | 4 | 72
205 | 5 | 71
205 | 6 | 71
205 | 7 | 76
205 | 8 | 80
205 | 9 | 85
205 | 10 | 86
205 | 11 | 88
205 | 12 | 89
205 | 13 | 89
205 | 14 | 89
205 | 15 | 89
205 | 16 | 88
205 | 17 | 88
205 | 18 | 87
205 | 19 | 83
205 | 20 | 79
205 | 21 | 75
205 | 22 | 74
205 | 23 | 73
205 | 24 | 72 | 80.25 | -15.25 | 15.25
206 | 1 | 74
206 | 2 | 76
206 | 3 | 78
206 | 4 | 78
206 | 5 | 78
206 | 6 | 78
206 | 7 | 81
206 | 8 | 83
206 | 9 | 86
206 | 10 | 87
206 | 11 | 87
206 | 12 | 88
206 | 13 | 89
206 | 14 | 91
206 | 15 | 92
206 | 16 | 91
206 | 17 | 90
206 | 18 | 89
206 | 19 | 86
206 | 20 | 84
206 | 21 | 81
206 | 22 | 81
206 | 23 | 81
206 | 24 | 81 | 83.75 | -18.75 | 18.75
207 | 1 | 81
207 | 2 | 80
207 | 3 | 80
207 | 4 | 80
207 | 5 | 81
207 | 6 | 81
207 | 7 | 83
207 | 8 | 84
207 | 9 | 86
207 | 10 | 85
207 | 11 | 83
207 | 12 | 82
207 | 13 | 84
207 | 14 | 85
207 | 15 | 87
207 | 16 | 85
207 | 17 | 84
207 | 18 | 82
207 | 19 | 82
207 | 20 | 81
207 | 21 | 81
207 | 22 | 80
207 | 23 | 80
207 | 24 | 79 | 82.3333 | -17.3333 | 17.3333
208 | 1 | 79
208 | 2 | 79
208 | 3 | 79
208 | 4 | 79
208 | 5 | 78
208 | 6 | 78
208 | 7 | 79
208 | 8 | 81
208 | 9 | 82
208 | 10 | 83
208 | 11 | 83
208 | 12 | 84
208 | 13 | 86
208 | 14 | 87
208 | 15 | 89
208 | 16 | 88
208 | 17 | 88
208 | 18 | 87
208 | 19 | 85
208 | 20 | 83
208 | 21 | 81
208 | 22 | 80
208 | 23 | 80
208 | 24 | 79 | 82.375 | -17.375 | 17.375
209 | 1 | 78
209 | 2 | 76
209 | 3 | 75
209 | 4 | 75
209 | 5 | 74
209 | 6 | 74
209 | 7 | 78
209 | 8 | 83
209 | 9 | 87
209 | 10 | 88
209 | 11 | 88
209 | 12 | 89
209 | 13 | 89
209 | 14 | 89
209 | 15 | 89
209 | 16 | 88
209 | 17 | 87
209 | 18 | 86
209 | 19 | 85
209 | 20 | 83
209 | 21 | 82
209 | 22 | 81
209 | 23 | 80
209 | 24 | 79 | 82.625 | -17.625 | 17.625
210 | 1 | 78
210 | 2 | 77
210 | 3 | 76
210 | 4 | 76
210 | 5 | 76
210 | 6 | 76
210 | 7 | 80
210 | 8 | 83
210 | 9 | 87
210 | 10 | 89
210 | 11 | 91
210 | 12 | 93
210 | 13 | 93
210 | 14 | 94
210 | 15 | 94
210 | 16 | 93
210 | 17 | 91
210 | 18 | 90
210 | 19 | 88
210 | 20 | 85
210 | 21 | 83
210 | 22 | 82
210 | 23 | 81
210 | 24 | 80 | 84.8333 | -19.8333 | 19.8333
211 | 1 | 80
211 | 2 | 79
211 | 3 | 79
211 | 4 | 79
211 | 5 | 79
211 | 6 | 79
211 | 7 | 82
211 | 8 | 86
211 | 9 | 89
211 | 10 | 90
211 | 11 | 92
211 | 12 | 93
211 | 13 | 93
211 | 14 | 92
211 | 15 | 92
211 | 16 | 88
211 | 17 | 85
211 | 18 | 81
211 | 19 | 80
211 | 20 | 79
211 | 21 | 78
211 | 22 | 78
211 | 23 | 77
211 | 24 | 77 | 83.625 | -18.625 | 18.625
212 | 1 | 76
212 | 2 | 76
212 | 3 | 75
212 | 4 | 76
212 | 5 | 78
212 | 6 | 79
212 | 7 | 77
212 | 8 | 76
212 | 9 | 74
212 | 10 | 75
212 | 11 | 76
212 | 12 | 77
212 | 13 | 80
212 | 14 | 82
212 | 15 | 85
212 | 16 | 85
212 | 17 | 84
212 | 18 | 84
212 | 19 | 81
212 | 20 | 78
212 | 21 | 76
212 | 22 | 78
212 | 23 | 78
212 | 24 | 78 | 78.5 | -13.5 | 13.5
213 | 1 | 78
213 | 2 | 78
213 | 3 | 77
213 | 4 | 76
213 | 5 | 75
213 | 6 | 74
213 | 7 | 77
213 | 8 | 80
213 | 9 | 84
213 | 10 | 85
213 | 11 | 86
213 | 12 | 87
213 | 13 | 88
213 | 14 | 90
213 | 15 | 91
213 | 16 | 89
213 | 17 | 86
213 | 18 | 84
213 | 19 | 84
213 | 20 | 83
213 | 21 | 83
213 | 22 | 80
213 | 23 | 78
213 | 24 | 75 | 82 | -17 | 17
214 | 1 | 74
214 | 2 | 73
214 | 3 | 72
214 | 4 | 73
214 | 5 | 73
214 | 6 | 74
214 | 7 | 77
214 | 8 | 80
214 | 9 | 83
214 | 10 | 85
214 | 11 | 86
214 | 12 | 88
214 | 13 | 88
214 | 14 | 89
214 | 15 | 89
214 | 16 | 88
214 | 17 | 88
214 | 18 | 87
214 | 19 | 85
214 | 20 | 84
214 | 21 | 82
214 | 22 | 82
214 | 23 | 81
214 | 24 | 81 | 81.75 | -16.75 | 16.75
215 | 1 | 81
215 | 2 | 80
215 | 3 | 80
215 | 4 | 80
215 | 5 | 80
215 | 6 | 80
215 | 7 | 82
215 | 8 | 84
215 | 9 | 86
215 | 10 | 87
215 | 11 | 87
215 | 12 | 88
215 | 13 | 87
215 | 14 | 85
215 | 15 | 84
215 | 16 | 84
215 | 17 | 83
215 | 18 | 83
215 | 19 | 82
215 | 20 | 80
215 | 21 | 79
215 | 22 | 79
215 | 23 | 78
215 | 24 | 78 | 82.375 | -17.375 | 17.375
216 | 1 | 77
216 | 2 | 77
216 | 3 | 76
216 | 4 | 76
216 | 5 | 77
216 | 6 | 77
216 | 7 | 77
216 | 8 | 78
216 | 9 | 78
216 | 10 | 79
216 | 11 | 80
216 | 12 | 81
216 | 13 | 81
216 | 14 | 81
216 | 15 | 81
216 | 16 | 79
216 | 17 | 77
216 | 18 | 75
216 | 19 | 75
216 | 20 | 75
216 | 21 | 75
216 | 22 | 75
216 | 23 | 76
216 | 24 | 76 | 77.4583 | -12.4583 | 12.4583
217 | 1 | 76
217 | 2 | 76
217 | 3 | 76
217 | 4 | 76
217 | 5 | 75
217 | 6 | 75
217 | 7 | 77
217 | 8 | 80
217 | 9 | 82
217 | 10 | 80
217 | 11 | 78
217 | 12 | 76
217 | 13 | 78
217 | 14 | 79
217 | 15 | 81
217 | 16 | 81
217 | 17 | 82
217 | 18 | 82
217 | 19 | 80
217 | 20 | 77
217 | 21 | 75
217 | 22 | 75
217 | 23 | 74
217 | 24 | 74 | 77.7083 | -12.7083 | 12.7083
218 | 1 | 74
218 | 2 | 74
218 | 3 | 74
218 | 4 | 74
218 | 5 | 74
218 | 6 | 74
218 | 7 | 75
218 | 8 | 77
218 | 9 | 78
218 | 10 | 80
218 | 11 | 81
218 | 12 | 83
218 | 13 | 83
218 | 14 | 82
218 | 15 | 82
218 | 16 | 82
218 | 17 | 83
218 | 18 | 83
218 | 19 | 81
218 | 20 | 80
218 | 21 | 78
218 | 22 | 77
218 | 23 | 76
218 | 24 | 75 | 78.3333 | -13.3333 | 13.3333
219 | 1 | 75
219 | 2 | 74
219 | 3 | 74
219 | 4 | 73
219 | 5 | 73
219 | 6 | 72
219 | 7 | 76
219 | 8 | 79
219 | 9 | 83
219 | 10 | 84
219 | 11 | 85
219 | 12 | 86
219 | 13 | 87
219 | 14 | 89
219 | 15 | 90
219 | 16 | 88
219 | 17 | 86
219 | 18 | 84
219 | 19 | 82
219 | 20 | 81
219 | 21 | 79
219 | 22 | 79
219 | 23 | 78
219 | 24 | 78 | 80.625 | -15.625 | 15.625
220 | 1 | 77
220 | 2 | 77
220 | 3 | 76
220 | 4 | 74
220 | 5 | 73
220 | 6 | 71
220 | 7 | 75
220 | 8 | 80
220 | 9 | 84
220 | 10 | 86
220 | 11 | 87
220 | 12 | 89
220 | 13 | 90
220 | 14 | 90
220 | 15 | 91
220 | 16 | 89
220 | 17 | 87
220 | 18 | 85
220 | 19 | 83
220 | 20 | 81
220 | 21 | 79
220 | 22 | 78
220 | 23 | 78
220 | 24 | 77 | 81.5417 | -16.5417 | 16.5417
221 | 1 | 77
221 | 2 | 77
221 | 3 | 77
221 | 4 | 77
221 | 5 | 77
221 | 6 | 77
221 | 7 | 79
221 | 8 | 82
221 | 9 | 84
221 | 10 | 85
221 | 11 | 85
221 | 12 | 86
221 | 13 | 86
221 | 14 | 86
221 | 15 | 86
221 | 16 | 85
221 | 17 | 84
221 | 18 | 83
221 | 19 | 82
221 | 20 | 81
221 | 21 | 80
221 | 22 | 80
221 | 23 | 79
221 | 24 | 79 | 81.4167 | -16.4167 | 16.4167
222 | 1 | 79
222 | 2 | 79
222 | 3 | 79
222 | 4 | 78
222 | 5 | 77
222 | 6 | 76
222 | 7 | 78
222 | 8 | 80
222 | 9 | 82
222 | 10 | 82
222 | 11 | 83
222 | 12 | 83
222 | 13 | 82
222 | 14 | 82
222 | 15 | 81
222 | 16 | 80
222 | 17 | 79
222 | 18 | 78
222 | 19 | 77
222 | 20 | 76
222 | 21 | 75
222 | 22 | 75
222 | 23 | 75
222 | 24 | 75 | 78.7917 | -13.7917 | 13.7917
223 | 1 | 75
223 | 2 | 75
223 | 3 | 75
223 | 4 | 75
223 | 5 | 76
223 | 6 | 76
223 | 7 | 79
223 | 8 | 82
223 | 9 | 85
223 | 10 | 87
223 | 11 | 88
223 | 12 | 90
223 | 13 | 89
223 | 14 | 88
223 | 15 | 87
223 | 16 | 86
223 | 17 | 85
223 | 18 | 84
223 | 19 | 83
223 | 20 | 81
223 | 21 | 80
223 | 22 | 80
223 | 23 | 80
223 | 24 | 80 | 81.9167 | -16.9167 | 16.9167
224 | 1 | 80
224 | 2 | 79
224 | 3 | 79
224 | 4 | 79
224 | 5 | 79
224 | 6 | 79
224 | 7 | 82
224 | 8 | 85
224 | 9 | 88
224 | 10 | 89
224 | 11 | 91
224 | 12 | 92
224 | 13 | 92
224 | 14 | 91
224 | 15 | 91
224 | 16 | 90
224 | 17 | 88
224 | 18 | 87
224 | 19 | 85
224 | 20 | 84
224 | 21 | 82
224 | 22 | 81
224 | 23 | 81
224 | 24 | 80 | 84.75 | -19.75 | 19.75
225 | 1 | 79
225 | 2 | 78
225 | 3 | 77
225 | 4 | 76
225 | 5 | 74
225 | 6 | 73
225 | 7 | 78
225 | 8 | 82
225 | 9 | 87
225 | 10 | 88
225 | 11 | 89
225 | 12 | 90
225 | 13 | 91
225 | 14 | 91
225 | 15 | 92
225 | 16 | 89
225 | 17 | 87
225 | 18 | 84
225 | 19 | 82
225 | 20 | 79
225 | 21 | 77
225 | 22 | 78
225 | 23 | 78
225 | 24 | 79 | 82.4167 | -17.4167 | 17.4167
226 | 1 | 79
226 | 2 | 80
226 | 3 | 80
226 | 4 | 78
226 | 5 | 75
226 | 6 | 73
226 | 7 | 78
226 | 8 | 82
226 | 9 | 87
226 | 10 | 88
226 | 11 | 89
226 | 12 | 90
226 | 13 | 86
226 | 14 | 83
226 | 15 | 79
226 | 16 | 82
226 | 17 | 84
226 | 18 | 87
226 | 19 | 84
226 | 20 | 81
226 | 21 | 78
226 | 22 | 77
226 | 23 | 76
226 | 24 | 75 | 81.2917 | -16.2917 | 16.2917
227 | 1 | 75
227 | 2 | 74
227 | 3 | 74
227 | 4 | 73
227 | 5 | 73
227 | 6 | 72
227 | 7 | 77
227 | 8 | 81
227 | 9 | 86
227 | 10 | 87
227 | 11 | 88
227 | 12 | 89
227 | 13 | 89
227 | 14 | 88
227 | 15 | 88
227 | 16 | 87
227 | 17 | 85
227 | 18 | 84
227 | 19 | 83
227 | 20 | 82
227 | 21 | 81
227 | 22 | 79
227 | 23 | 77
227 | 24 | 75 | 81.125 | -16.125 | 16.125
228 | 1 | 75
228 | 2 | 76
228 | 3 | 76
228 | 4 | 76
228 | 5 | 75
228 | 6 | 75
228 | 7 | 79
228 | 8 | 82
228 | 9 | 86
228 | 10 | 88
228 | 11 | 89
228 | 12 | 91
228 | 13 | 92
228 | 14 | 93
228 | 15 | 94
228 | 16 | 93
228 | 17 | 92
228 | 18 | 91
228 | 19 | 86
228 | 20 | 80
228 | 21 | 75
228 | 22 | 75
228 | 23 | 76
228 | 24 | 76 | 82.9583 | -17.9583 | 17.9583
229 | 1 | 76
229 | 2 | 75
229 | 3 | 75
229 | 4 | 74
229 | 5 | 74
229 | 6 | 73
229 | 7 | 77
229 | 8 | 81
229 | 9 | 85
229 | 10 | 85
229 | 11 | 86
229 | 12 | 86
229 | 13 | 87
229 | 14 | 89
229 | 15 | 90
229 | 16 | 87
229 | 17 | 83
229 | 18 | 80
229 | 19 | 80
229 | 20 | 79
229 | 21 | 79
229 | 22 | 78
229 | 23 | 77
229 | 24 | 76 | 80.5 | -15.5 | 15.5
230 | 1 | 75
230 | 2 | 75
230 | 3 | 74
230 | 4 | 74
230 | 5 | 74
230 | 6 | 74
230 | 7 | 77
230 | 8 | 79
230 | 9 | 82
230 | 10 | 83
230 | 11 | 85
230 | 12 | 86
230 | 13 | 87
230 | 14 | 87
230 | 15 | 88
230 | 16 | 87
230 | 17 | 86
230 | 18 | 85
230 | 19 | 82
230 | 20 | 80
230 | 21 | 77
230 | 22 | 76
230 | 23 | 76
230 | 24 | 75 | 80.1667 | -15.1667 | 15.1667
231 | 1 | 76
231 | 2 | 76
231 | 3 | 77
231 | 4 | 77
231 | 5 | 76
231 | 6 | 76
231 | 7 | 80
231 | 8 | 83
231 | 9 | 87
231 | 10 | 88
231 | 11 | 89
231 | 12 | 90
231 | 13 | 88
231 | 14 | 87
231 | 15 | 85
231 | 16 | 84
231 | 17 | 84
231 | 18 | 83
231 | 19 | 80
231 | 20 | 78
231 | 21 | 75
231 | 22 | 75
231 | 23 | 76
231 | 24 | 76 | 81.0833 | -16.0833 | 16.0833
232 | 1 | 75
232 | 2 | 74
232 | 3 | 73
232 | 4 | 74
232 | 5 | 74
232 | 6 | 75
232 | 7 | 78
232 | 8 | 82
232 | 9 | 85
232 | 10 | 87
232 | 11 | 90
232 | 12 | 92
232 | 13 | 89
232 | 14 | 87
232 | 15 | 84
232 | 16 | 82
232 | 17 | 80
232 | 18 | 78
232 | 19 | 78
232 | 20 | 78
232 | 21 | 78
232 | 22 | 78
232 | 23 | 77
232 | 24 | 77 | 80.2083 | -15.2083 | 15.2083
233 | 1 | 75
233 | 2 | 74
233 | 3 | 72
233 | 4 | 72
233 | 5 | 71
233 | 6 | 71
233 | 7 | 76
233 | 8 | 81
233 | 9 | 86
233 | 10 | 88
233 | 11 | 89
233 | 12 | 91
233 | 13 | 90
233 | 14 | 90
233 | 15 | 89
233 | 16 | 88
233 | 17 | 87
233 | 18 | 86
233 | 19 | 83
233 | 20 | 81
233 | 21 | 78
233 | 22 | 78
233 | 23 | 77
233 | 24 | 77 | 81.25 | -16.25 | 16.25
234 | 1 | 75
234 | 2 | 73
234 | 3 | 71
234 | 4 | 71
234 | 5 | 71
234 | 6 | 71
234 | 7 | 75
234 | 8 | 80
234 | 9 | 84
234 | 10 | 85
234 | 11 | 87
234 | 12 | 88
234 | 13 | 89
234 | 14 | 90
234 | 15 | 91
234 | 16 | 90
234 | 17 | 89
234 | 18 | 88
234 | 19 | 85
234 | 20 | 83
234 | 21 | 80
234 | 22 | 79
234 | 23 | 78
234 | 24 | 77 | 81.25 | -16.25 | 16.25
235 | 1 | 77
235 | 2 | 76
235 | 3 | 76
235 | 4 | 76
235 | 5 | 75
235 | 6 | 75
235 | 7 | 79
235 | 8 | 82
235 | 9 | 86
235 | 10 | 87
235 | 11 | 89
235 | 12 | 90
235 | 13 | 91
235 | 14 | 91
235 | 15 | 92
235 | 16 | 90
235 | 17 | 89
235 | 18 | 87
235 | 19 | 85
235 | 20 | 83
235 | 21 | 81
235 | 22 | 80
235 | 23 | 80
235 | 24 | 79 | 83.1667 | -18.1667 | 18.1667
236 | 1 | 78
236 | 2 | 76
236 | 3 | 75
236 | 4 | 74
236 | 5 | 74
236 | 6 | 73
236 | 7 | 75
236 | 8 | 76
236 | 9 | 78
236 | 10 | 79
236 | 11 | 81
236 | 12 | 82
236 | 13 | 83
236 | 14 | 85
236 | 15 | 86
236 | 16 | 85
236 | 17 | 83
236 | 18 | 82
236 | 19 | 81
236 | 20 | 79
236 | 21 | 78
236 | 22 | 77
236 | 23 | 76
236 | 24 | 75 | 78.7917 | -13.7917 | 13.7917
237 | 1 | 74
237 | 2 | 73
237 | 3 | 72
237 | 4 | 72
237 | 5 | 71
237 | 6 | 71
237 | 7 | 73
237 | 8 | 76
237 | 9 | 78
237 | 10 | 79
237 | 11 | 81
237 | 12 | 82
237 | 13 | 82
237 | 14 | 81
237 | 15 | 81
237 | 16 | 79
237 | 17 | 78
237 | 18 | 76
237 | 19 | 73
237 | 20 | 71
237 | 21 | 68
237 | 22 | 67
237 | 23 | 67
237 | 24 | 66 | 74.625 | -9.625 | 9.625
238 | 1 | 66
238 | 2 | 65
238 | 3 | 65
238 | 4 | 65
238 | 5 | 65
238 | 6 | 65
238 | 7 | 70
238 | 8 | 75
238 | 9 | 80
238 | 10 | 82
238 | 11 | 83
238 | 12 | 85
238 | 13 | 85
238 | 14 | 86
238 | 15 | 86
238 | 16 | 84
238 | 17 | 81
238 | 18 | 79
238 | 19 | 77
238 | 20 | 74
238 | 21 | 72
238 | 22 | 71
238 | 23 | 69
238 | 24 | 68 | 74.9167 | -9.9167 | 9.9167
239 | 1 | 67
239 | 2 | 66
239 | 3 | 65
239 | 4 | 65
239 | 5 | 66
239 | 6 | 66
239 | 7 | 71
239 | 8 | 76
239 | 9 | 81
239 | 10 | 81
239 | 11 | 82
239 | 12 | 82
239 | 13 | 82
239 | 14 | 82
239 | 15 | 82
239 | 16 | 80
239 | 17 | 79
239 | 18 | 77
239 | 19 | 76
239 | 20 | 75
239 | 21 | 74
239 | 22 | 75
239 | 23 | 75
239 | 24 | 76 | 75.0417 | -10.0417 | 10.0417
240 | 1 | 76
240 | 2 | 77
240 | 3 | 77
240 | 4 | 76
240 | 5 | 76
240 | 6 | 75
240 | 7 | 74
240 | 8 | 74
240 | 9 | 73
240 | 10 | 73
240 | 11 | 73
240 | 12 | 73
240 | 13 | 74
240 | 14 | 76
240 | 15 | 77
240 | 16 | 77
240 | 17 | 77
240 | 18 | 77
240 | 19 | 77
240 | 20 | 77
240 | 21 | 77
240 | 22 | 77
240 | 23 | 76
240 | 24 | 76 | 75.625 | -10.625 | 10.625
241 | 1 | 75
241 | 2 | 75
241 | 3 | 74
241 | 4 | 74
241 | 5 | 75
241 | 6 | 75
241 | 7 | 77
241 | 8 | 80
241 | 9 | 82
241 | 10 | 83
241 | 11 | 84
241 | 12 | 85
241 | 13 | 86
241 | 14 | 86
241 | 15 | 87
241 | 16 | 86
241 | 17 | 84
241 | 18 | 83
241 | 19 | 82
241 | 20 | 81
241 | 21 | 80
241 | 22 | 79
241 | 23 | 77
241 | 24 | 76 | 80.25 | -15.25 | 15.25
242 | 1 | 74
242 | 2 | 72
242 | 3 | 70
242 | 4 | 70
242 | 5 | 70
242 | 6 | 70
242 | 7 | 75
242 | 8 | 80
242 | 9 | 85
242 | 10 | 85
242 | 11 | 85
242 | 12 | 85
242 | 13 | 83
242 | 14 | 82
242 | 15 | 80
242 | 16 | 81
242 | 17 | 81
242 | 18 | 82
242 | 19 | 80
242 | 20 | 77
242 | 21 | 75
242 | 22 | 73
242 | 23 | 72
242 | 24 | 70 | 77.375 | -12.375 | 12.375
243 | 1 | 70
243 | 2 | 69
243 | 3 | 69
243 | 4 | 69
243 | 5 | 68
243 | 6 | 68
243 | 7 | 73
243 | 8 | 78
243 | 9 | 83
243 | 10 | 85
243 | 11 | 86
243 | 12 | 88
243 | 13 | 88
243 | 14 | 88
243 | 15 | 88
243 | 16 | 86
243 | 17 | 84
243 | 18 | 82
243 | 19 | 80
243 | 20 | 78
243 | 21 | 76
243 | 22 | 76
243 | 23 | 77
243 | 24 | 77 | 78.5833 | -13.5833 | 13.5833
244 | 1 | 79
244 | 2 | 79
244 | 3 | 79
244 | 4 | 79
244 | 5 | 78
244 | 6 | 78
244 | 7 | 80
244 | 8 | 82
244 | 9 | 85
244 | 10 | 87
244 | 11 | 90
244 | 12 | 91
244 | 13 | 91
244 | 14 | 91
244 | 15 | 92
244 | 16 | 87
244 | 17 | 86
244 | 18 | 85
244 | 19 | 82
244 | 20 | 83
244 | 21 | 81
244 | 22 | 82
244 | 23 | 81
244 | 24 | 80 | 83.6667 | -18.6667 | 18.6667
245 | 1 | 80
245 | 2 | 76
245 | 3 | 75
245 | 4 | 75
245 | 5 | 74
245 | 6 | 73
245 | 7 | 80
245 | 8 | 86
245 | 9 | 86
245 | 10 | 88
245 | 11 | 89
245 | 12 | 90
245 | 13 | 83
245 | 14 | 88
245 | 15 | 90
245 | 16 | 90
245 | 17 | 83
245 | 18 | 80
245 | 19 | 78
245 | 20 | 80
245 | 21 | 81
245 | 22 | 77
245 | 23 | 78
245 | 24 | 81 | 81.7083 | -16.7083 | 16.7083
246 | 1 | 80
246 | 2 | 77
246 | 3 | 75
246 | 4 | 75
246 | 5 | 74
246 | 6 | 74
246 | 7 | 81
246 | 8 | 86
246 | 9 | 86
246 | 10 | 87
246 | 11 | 90
246 | 12 | 88
246 | 13 | 81
246 | 14 | 83
246 | 15 | 86
246 | 16 | 87
246 | 17 | 80
246 | 18 | 80
246 | 19 | 79
246 | 20 | 78
246 | 21 | 76
246 | 22 | 76
246 | 23 | 74
246 | 24 | 73 | 80.25 | -15.25 | 15.25
247 | 1 | 73
247 | 2 | 72
247 | 3 | 72
247 | 4 | 72
247 | 5 | 70
247 | 6 | 70
247 | 7 | 75
247 | 8 | 84
247 | 9 | 86
247 | 10 | 88
247 | 11 | 86
247 | 12 | 89
247 | 13 | 90
247 | 14 | 91
247 | 15 | 87
247 | 16 | 85
247 | 17 | 82
247 | 18 | 81
247 | 19 | 78
247 | 20 | 76
247 | 21 | 77
247 | 22 | 78
247 | 23 | 76
247 | 24 | 76 | 79.75 | -14.75 | 14.75
248 | 1 | 74
248 | 2 | 74
248 | 3 | 74
248 | 4 | 74
248 | 5 | 74
248 | 6 | 73
248 | 7 | 77
248 | 8 | 84
248 | 9 | 86
248 | 10 | 89
248 | 11 | 89
248 | 12 | 91
248 | 13 | 92
248 | 14 | 93
248 | 15 | 90
248 | 16 | 90
248 | 17 | 87
248 | 18 | 85
248 | 19 | 82
248 | 20 | 79
248 | 21 | 79
248 | 22 | 77
248 | 23 | 76
248 | 24 | 74 | 81.7917 | -16.7917 | 16.7917
249 | 1 | 73
249 | 2 | 73
249 | 3 | 74
249 | 4 | 75
249 | 5 | 76
249 | 6 | 77
249 | 7 | 79
249 | 8 | 81
249 | 9 | 83
249 | 10 | 86
249 | 11 | 88
249 | 12 | 89
249 | 13 | 90
249 | 14 | 92
249 | 15 | 91
249 | 16 | 84
249 | 17 | 84
249 | 18 | 84
249 | 19 | 79
249 | 20 | 79
249 | 21 | 76
249 | 22 | 75
249 | 23 | 74
249 | 24 | 76 | 80.75 | -15.75 | 15.75
250 | 1 | 75
250 | 2 | 73
250 | 3 | 73
250 | 4 | 73
250 | 5 | 72
250 | 6 | 71
250 | 7 | 75
250 | 8 | 83
250 | 9 | 87
250 | 10 | 89
250 | 11 | 90
250 | 12 | 92
250 | 13 | 92
250 | 14 | 94
250 | 15 | 93
250 | 16 | 92
250 | 17 | 90
250 | 18 | 87
250 | 19 | 84
250 | 20 | 83
250 | 21 | 82
250 | 22 | 76
250 | 23 | 76
250 | 24 | 75 | 82.375 | -17.375 | 17.375
251 | 1 | 76
251 | 2 | 76
251 | 3 | 75
251 | 4 | 75
251 | 5 | 75
251 | 6 | 74
251 | 7 | 77
251 | 8 | 81
251 | 9 | 85
251 | 10 | 87
251 | 11 | 88
251 | 12 | 89
251 | 13 | 90
251 | 14 | 91
251 | 15 | 89
251 | 16 | 90
251 | 17 | 87
251 | 18 | 85
251 | 19 | 81
251 | 20 | 80
251 | 21 | 80
251 | 22 | 77
251 | 23 | 75
251 | 24 | 75 | 81.5833 | -16.5833 | 16.5833
252 | 1 | 74
252 | 2 | 73
252 | 3 | 72
252 | 4 | 72
252 | 5 | 70
252 | 6 | 71
252 | 7 | 75
252 | 8 | 85
252 | 9 | 87
252 | 10 | 89
252 | 11 | 90
252 | 12 | 91
252 | 13 | 92
252 | 14 | 92
252 | 15 | 92
252 | 16 | 91
252 | 17 | 90
252 | 18 | 88
252 | 19 | 79
252 | 20 | 83
252 | 21 | 78
252 | 22 | 78
252 | 23 | 76
252 | 24 | 75 | 81.7917 | -16.7917 | 16.7917
253 | 1 | 74
253 | 2 | 74
253 | 3 | 74
253 | 4 | 73
253 | 5 | 72
253 | 6 | 73
253 | 7 | 78
253 | 8 | 83
253 | 9 | 87
253 | 10 | 89
253 | 11 | 90
253 | 12 | 92
253 | 13 | 92
253 | 14 | 92
253 | 15 | 93
253 | 16 | 92
253 | 17 | 90
253 | 18 | 87
253 | 19 | 83
253 | 20 | 80
253 | 21 | 80
253 | 22 | 79
253 | 23 | 78
253 | 24 | 77 | 82.5833 | -17.5833 | 17.5833
254 | 1 | 77
254 | 2 | 75
254 | 3 | 75
254 | 4 | 74
254 | 5 | 74
254 | 6 | 72
254 | 7 | 76
254 | 8 | 83
254 | 9 | 87
254 | 10 | 87
254 | 11 | 87
254 | 12 | 91
254 | 13 | 91
254 | 14 | 93
254 | 15 | 88
254 | 16 | 86
254 | 17 | 85
254 | 18 | 82
254 | 19 | 81
254 | 20 | 81
254 | 21 | 80
254 | 22 | 79
254 | 23 | 78
254 | 24 | 78 | 81.6667 | -16.6667 | 16.6667
255 | 1 | 78
255 | 2 | 74
255 | 3 | 73
255 | 4 | 73
255 | 5 | 73
255 | 6 | 74
255 | 7 | 78
255 | 8 | 83
255 | 9 | 86
255 | 10 | 87
255 | 11 | 90
255 | 12 | 90
255 | 13 | 92
255 | 14 | 91
255 | 15 | 90
255 | 16 | 86
255 | 17 | 84
255 | 18 | 83
255 | 19 | 78
255 | 20 | 77
255 | 21 | 81
255 | 22 | 76
255 | 23 | 75
255 | 24 | 76 | 81.1667 | -16.1667 | 16.1667
256 | 1 | 76
256 | 2 | 74
256 | 3 | 72
256 | 4 | 71
256 | 5 | 72
256 | 6 | 74
256 | 7 | 77
256 | 8 | 81
256 | 9 | 85
256 | 10 | 86
256 | 11 | 87
256 | 12 | 87
256 | 13 | 90
256 | 14 | 90
256 | 15 | 90
256 | 16 | 89
256 | 17 | 86
256 | 18 | 74
256 | 19 | 73
256 | 20 | 74
256 | 21 | 74
256 | 22 | 74
256 | 23 | 73
256 | 24 | 72 | 79.2083 | -14.2083 | 14.2083
257 | 1 | 71
257 | 2 | 70
257 | 3 | 70
257 | 4 | 70
257 | 5 | 70
257 | 6 | 70
257 | 7 | 73
257 | 8 | 77
257 | 9 | 80
257 | 10 | 80
257 | 11 | 84
257 | 12 | 83
257 | 13 | 83
257 | 14 | 85
257 | 15 | 85
257 | 16 | 84
257 | 17 | 84
257 | 18 | 79
257 | 19 | 77
257 | 20 | 75
257 | 21 | 73
257 | 22 | 75
257 | 23 | 73
257 | 24 | 74 | 76.875 | -11.875 | 11.875
258 | 1 | 73
258 | 2 | 73
258 | 3 | 74
258 | 4 | 77
258 | 5 | 77
258 | 6 | 75
258 | 7 | 76
258 | 8 | 79
258 | 9 | 82
258 | 10 | 84
258 | 11 | 75
258 | 12 | 78
258 | 13 | 83
258 | 14 | 83
258 | 15 | 84
258 | 16 | 82
258 | 17 | 80
258 | 18 | 75
258 | 19 | 75
258 | 20 | 75
258 | 21 | 75
258 | 22 | 76
258 | 23 | 76
258 | 24 | 76 | 77.625 | -12.625 | 12.625
259 | 1 | 76
259 | 2 | 76
259 | 3 | 75
259 | 4 | 76
259 | 5 | 75
259 | 6 | 76
259 | 7 | 76
259 | 8 | 75
259 | 9 | 73
259 | 10 | 75
259 | 11 | 75
259 | 12 | 74
259 | 13 | 75
259 | 14 | 76
259 | 15 | 77
259 | 16 | 76
259 | 17 | 76
259 | 18 | 76
259 | 19 | 76
259 | 20 | 76
259 | 21 | 76
259 | 22 | 76
259 | 23 | 76
259 | 24 | 75 | 75.5417 | -10.5417 | 10.5417
260 | 1 | 76
260 | 2 | 76
260 | 3 | 75
260 | 4 | 75
260 | 5 | 76
260 | 6 | 76
260 | 7 | 75
260 | 8 | 77
260 | 9 | 79
260 | 10 | 78
260 | 11 | 80
260 | 12 | 82
260 | 13 | 83
260 | 14 | 83
260 | 15 | 83
260 | 16 | 80
260 | 17 | 79
260 | 18 | 79
260 | 19 | 79
260 | 20 | 77
260 | 21 | 78
260 | 22 | 77
260 | 23 | 77
260 | 24 | 76 | 78.1667 | -13.1667 | 13.1667
261 | 1 | 76
261 | 2 | 76
261 | 3 | 76
261 | 4 | 75
261 | 5 | 75
261 | 6 | 75
261 | 7 | 75
261 | 8 | 75
261 | 9 | 77
261 | 10 | 79
261 | 11 | 80
261 | 12 | 83
261 | 13 | 82
261 | 14 | 77
261 | 15 | 79
261 | 16 | 78
261 | 17 | 78
261 | 18 | 76
261 | 19 | 76
261 | 20 | 76
261 | 21 | 75
261 | 22 | 75
261 | 23 | 75
261 | 24 | 75 | 76.8333 | -11.8333 | 11.8333
262 | 1 | 75
262 | 2 | 75
262 | 3 | 74
262 | 4 | 74
262 | 5 | 74
262 | 6 | 73
262 | 7 | 75
262 | 8 | 76
262 | 9 | 78
262 | 10 | 80
262 | 11 | 83
262 | 12 | 84
262 | 13 | 85
262 | 14 | 85
262 | 15 | 85
262 | 16 | 84
262 | 17 | 83
262 | 18 | 79
262 | 19 | 72
262 | 20 | 71
262 | 21 | 70
262 | 22 | 69
262 | 23 | 67
262 | 24 | 66 | 76.5417 | -11.5417 | 11.5417
263 | 1 | 65
263 | 2 | 65
263 | 3 | 66
263 | 4 | 66
263 | 5 | 66
263 | 6 | 67
263 | 7 | 73
263 | 8 | 76
263 | 9 | 80
263 | 10 | 83
263 | 11 | 84
263 | 12 | 85
263 | 13 | 86
263 | 14 | 86
263 | 15 | 87
263 | 16 | 86
263 | 17 | 84
263 | 18 | 76
263 | 19 | 72
263 | 20 | 70
263 | 21 | 70
263 | 22 | 70
263 | 23 | 70
263 | 24 | 70 | 75.125 | -10.125 | 10.125
264 | 1 | 70
264 | 2 | 70
264 | 3 | 68
264 | 4 | 67
264 | 5 | 68
264 | 6 | 66
264 | 7 | 72
264 | 8 | 74
264 | 9 | 78
264 | 10 | 81
264 | 11 | 84
264 | 12 | 84
264 | 13 | 84
264 | 14 | 87
264 | 15 | 82
264 | 16 | 83
264 | 17 | 80
264 | 18 | 75
264 | 19 | 72
264 | 20 | 69
264 | 21 | 71
264 | 22 | 71
264 | 23 | 70
264 | 24 | 70 | 74.8333 | -9.8333 | 9.8333
265 | 1 | 68
265 | 2 | 70
265 | 3 | 72
265 | 4 | 73
265 | 5 | 75
265 | 6 | 72
265 | 7 | 71
265 | 8 | 75
265 | 9 | 73
265 | 10 | 74
265 | 11 | 74
265 | 12 | 76
265 | 13 | 80
265 | 14 | 83
265 | 15 | 84
265 | 16 | 85
265 | 17 | 84
265 | 18 | 77
265 | 19 | 74
265 | 20 | 72
265 | 21 | 72
265 | 22 | 72
265 | 23 | 72
265 | 24 | 77 | 75.2083 | -10.2083 | 10.2083
266 | 1 | 76
266 | 2 | 74
266 | 3 | 73
266 | 4 | 73
266 | 5 | 72
266 | 6 | 72
266 | 7 | 75
266 | 8 | 80
266 | 9 | 81
266 | 10 | 81
266 | 11 | 79
266 | 12 | 78
266 | 13 | 79
266 | 14 | 78
266 | 15 | 79
266 | 16 | 78
266 | 17 | 77
266 | 18 | 77
266 | 19 | 75
266 | 20 | 74
266 | 21 | 73
266 | 22 | 72
266 | 23 | 71
266 | 24 | 70 | 75.7083 | -10.7083 | 10.7083
267 | 1 | 69
267 | 2 | 67
267 | 3 | 67
267 | 4 | 66
267 | 5 | 65
267 | 6 | 64
267 | 7 | 65
267 | 8 | 68
267 | 9 | 71
267 | 10 | 74
267 | 11 | 73
267 | 12 | 74
267 | 13 | 75
267 | 14 | 72
267 | 15 | 73
267 | 16 | 73
267 | 17 | 74
267 | 18 | 73
267 | 19 | 70
267 | 20 | 68
267 | 21 | 64
267 | 22 | 67
267 | 23 | 70
267 | 24 | 71 | 69.7083 | -4.7083 | 4.7083
268 | 1 | 70
268 | 2 | 70
268 | 3 | 68
268 | 4 | 67
268 | 5 | 66
268 | 6 | 66
268 | 7 | 67
268 | 8 | 69
268 | 9 | 71
268 | 10 | 72
268 | 11 | 74
268 | 12 | 75
268 | 13 | 77
268 | 14 | 78
268 | 15 | 80
268 | 16 | 80
268 | 17 | 78
268 | 18 | 71
268 | 19 | 68
268 | 20 | 66
268 | 21 | 65
268 | 22 | 64
268 | 23 | 68
268 | 24 | 70 | 70.8333 | -5.8333 | 5.8333
269 | 1 | 71
269 | 2 | 71
269 | 3 | 70
269 | 4 | 69
269 | 5 | 69
269 | 6 | 69
269 | 7 | 72
269 | 8 | 71
269 | 9 | 72
269 | 10 | 76
269 | 11 | 75
269 | 12 | 75
269 | 13 | 77
269 | 14 | 76
269 | 15 | 76
269 | 16 | 75
269 | 17 | 74
269 | 18 | 74
269 | 19 | 74
269 | 20 | 74
269 | 21 | 74
269 | 22 | 74
269 | 23 | 74
269 | 24 | 74 | 73.1667 | -8.1667 | 8.1667
270 | 1 | 73
270 | 2 | 73
270 | 3 | 73
270 | 4 | 72
270 | 5 | 73
270 | 6 | 72
270 | 7 | 72
270 | 8 | 72
270 | 9 | 73
270 | 10 | 73
270 | 11 | 73
270 | 12 | 73
270 | 13 | 71
270 | 14 | 71
270 | 15 | 70
270 | 16 | 70
270 | 17 | 70
270 | 18 | 70
270 | 19 | 70
270 | 20 | 69
270 | 21 | 68
270 | 22 | 68
270 | 23 | 68
270 | 24 | 67 | 71 | -6 | 6
271 | 1 | 67
271 | 2 | 67
271 | 3 | 66
271 | 4 | 66
271 | 5 | 66
271 | 6 | 66
271 | 7 | 67
271 | 8 | 66
271 | 9 | 67
271 | 10 | 68
271 | 11 | 68
271 | 12 | 70
271 | 13 | 73
271 | 14 | 74
271 | 15 | 74
271 | 16 | 76
271 | 17 | 73
271 | 18 | 72
271 | 19 | 72
271 | 20 | 68
271 | 21 | 67
271 | 22 | 65
271 | 23 | 64
271 | 24 | 67 | 68.7083 | -3.7083 | 3.7083
272 | 1 | 67
272 | 2 | 67
272 | 3 | 66
272 | 4 | 64
272 | 5 | 63
272 | 6 | 62
272 | 7 | 65
272 | 8 | 69
272 | 9 | 74
272 | 10 | 77
272 | 11 | 80
272 | 12 | 82
272 | 13 | 83
272 | 14 | 84
272 | 15 | 84
272 | 16 | 84
272 | 17 | 83
272 | 18 | 77
272 | 19 | 76
272 | 20 | 72
272 | 21 | 69
272 | 22 | 67
272 | 23 | 65
272 | 24 | 64 | 72.6667 | -7.6667 | 7.6667
273 | 1 | 63
273 | 2 | 62
273 | 3 | 61
273 | 4 | 61
273 | 5 | 61
273 | 6 | 60
273 | 7 | 62
273 | 8 | 64
273 | 9 | 65
273 | 10 | 67
273 | 11 | 68
273 | 12 | 71
273 | 13 | 73
273 | 14 | 74
273 | 15 | 74
273 | 16 | 75
273 | 17 | 73
273 | 18 | 66
273 | 19 | 61
273 | 20 | 65
273 | 21 | 65
273 | 22 | 68
273 | 23 | 71
273 | 24 | 71 | 66.7083 | -1.7083 | 1.7083
274 | 1 | 74
274 | 2 | 75
274 | 3 | 76
274 | 4 | 77
274 | 5 | 78
274 | 6 | 80
274 | 7 | 83
274 | 8 | 85
274 | 9 | 87
274 | 10 | 89
274 | 11 | 90
274 | 12 | 92
274 | 13 | 92
274 | 14 | 91
274 | 15 | 91
274 | 16 | 89
274 | 17 | 88
274 | 18 | 86
274 | 19 | 85
274 | 20 | 83
274 | 21 | 82
274 | 22 | 82
274 | 23 | 81
274 | 24 | 81 | 84.0417 | -19.0417 | 19.0417
275 | 1 | 80
275 | 2 | 80
275 | 3 | 79
275 | 4 | 79
275 | 5 | 78
275 | 6 | 78
275 | 7 | 81
275 | 8 | 84
275 | 9 | 87
275 | 10 | 84
275 | 11 | 80
275 | 12 | 77
275 | 13 | 77
275 | 14 | 78
275 | 15 | 78
275 | 16 | 78
275 | 17 | 78
275 | 18 | 78
275 | 19 | 76
275 | 20 | 75
275 | 21 | 73
275 | 22 | 72
275 | 23 | 71
275 | 24 | 70 | 77.9583 | -12.9583 | 12.9583
276 | 1 | 69
276 | 2 | 67
276 | 3 | 66
276 | 4 | 65
276 | 5 | 64
276 | 6 | 63
276 | 7 | 64
276 | 8 | 65
276 | 9 | 66
276 | 10 | 67
276 | 11 | 69
276 | 12 | 70
276 | 13 | 71
276 | 14 | 72
276 | 15 | 73
276 | 16 | 72
276 | 17 | 70
276 | 18 | 69
276 | 19 | 68
276 | 20 | 68
276 | 21 | 67
276 | 22 | 66
276 | 23 | 66
276 | 24 | 65 | 67.5833 | -2.5833 | 2.5833
277 | 1 | 65
277 | 2 | 64
277 | 3 | 64
277 | 4 | 63
277 | 5 | 62
277 | 6 | 61
277 | 7 | 63
277 | 8 | 65
277 | 9 | 67
277 | 10 | 69
277 | 11 | 70
277 | 12 | 72
277 | 13 | 73
277 | 14 | 73
277 | 15 | 74
277 | 16 | 70
277 | 17 | 67
277 | 18 | 63
277 | 19 | 61
277 | 20 | 59
277 | 21 | 57
277 | 22 | 56
277 | 23 | 56
277 | 24 | 55 | 64.5417 | 0.45833 | -0.45833
278 | 1 | 55
278 | 2 | 56
278 | 3 | 56
278 | 4 | 57
278 | 5 | 57
278 | 6 | 58
278 | 7 | 63
278 | 8 | 67
278 | 9 | 72
278 | 10 | 74
278 | 11 | 76
278 | 12 | 78
278 | 13 | 78
278 | 14 | 79
278 | 15 | 79
278 | 16 | 77
278 | 17 | 75
278 | 18 | 73
278 | 19 | 72
278 | 20 | 72
278 | 21 | 71
278 | 22 | 71
278 | 23 | 71
278 | 24 | 71 | 69.0833 | -4.0833 | 4.0833
279 | 1 | 71
279 | 2 | 71
279 | 3 | 71
279 | 4 | 71
279 | 5 | 71
279 | 6 | 71
279 | 7 | 73
279 | 8 | 76
279 | 9 | 78
279 | 10 | 79
279 | 11 | 80
279 | 12 | 81
279 | 13 | 81
279 | 14 | 82
279 | 15 | 82
279 | 16 | 79
279 | 17 | 75
279 | 18 | 72
279 | 19 | 70
279 | 20 | 68
279 | 21 | 66
279 | 22 | 66
279 | 23 | 66
279 | 24 | 66 | 73.5833 | -8.5833 | 8.5833
280 | 1 | 65
280 | 2 | 63
280 | 3 | 62
280 | 4 | 63
280 | 5 | 63
280 | 6 | 64
280 | 7 | 68
280 | 8 | 71
280 | 9 | 75
280 | 10 | 77
280 | 11 | 79
280 | 12 | 81
280 | 13 | 81
280 | 14 | 82
280 | 15 | 82
280 | 16 | 81
280 | 17 | 79
280 | 18 | 78
280 | 19 | 77
280 | 20 | 76
280 | 21 | 75
280 | 22 | 75
280 | 23 | 75
280 | 24 | 75 | 73.625 | -8.625 | 8.625
281 | 1 | 74
281 | 2 | 74
281 | 3 | 73
281 | 4 | 74
281 | 5 | 74
281 | 6 | 75
281 | 7 | 77
281 | 8 | 79
281 | 9 | 81
281 | 10 | 83
281 | 11 | 85
281 | 12 | 87
281 | 13 | 86
281 | 14 | 85
281 | 15 | 84
281 | 16 | 83
281 | 17 | 82
281 | 18 | 81
281 | 19 | 80
281 | 20 | 79
281 | 21 | 78
281 | 22 | 78
281 | 23 | 79
281 | 24 | 79 | 79.5833 | -14.5833 | 14.5833
282 | 1 | 77
282 | 2 | 74
282 | 3 | 72
282 | 4 | 72
282 | 5 | 72
282 | 6 | 72
282 | 7 | 70
282 | 8 | 68
282 | 9 | 66
282 | 10 | 68
282 | 11 | 71
282 | 12 | 73
282 | 13 | 74
282 | 14 | 75
282 | 15 | 76
282 | 16 | 74
282 | 17 | 72
282 | 18 | 70
282 | 19 | 69
282 | 20 | 67
282 | 21 | 66
282 | 22 | 66
282 | 23 | 65
282 | 24 | 65 | 70.5833 | -5.5833 | 5.5833
283 | 1 | 64
283 | 2 | 62
283 | 3 | 61
283 | 4 | 60
283 | 5 | 60
283 | 6 | 59
283 | 7 | 63
283 | 8 | 67
283 | 9 | 71
283 | 10 | 73
283 | 11 | 76
283 | 12 | 78
283 | 13 | 78
283 | 14 | 77
283 | 15 | 77
283 | 16 | 75
283 | 17 | 72
283 | 18 | 70
283 | 19 | 70
283 | 20 | 70
283 | 21 | 70
283 | 22 | 70
283 | 23 | 69
283 | 24 | 69 | 69.2083 | -4.2083 | 4.2083
284 | 1 | 69
284 | 2 | 70
284 | 3 | 70
284 | 4 | 70
284 | 5 | 71
284 | 6 | 71
284 | 7 | 71
284 | 8 | 72
284 | 9 | 72
284 | 10 | 72
284 | 11 | 72
284 | 12 | 72
284 | 13 | 72
284 | 14 | 71
284 | 15 | 71
284 | 16 | 70
284 | 17 | 68
284 | 18 | 67
284 | 19 | 66
284 | 20 | 66
284 | 21 | 65
284 | 22 | 64
284 | 23 | 62
284 | 24 | 61 | 68.9583 | -3.9583 | 3.9583
285 | 1 | 60
285 | 2 | 59
285 | 3 | 58
285 | 4 | 58
285 | 5 | 58
285 | 6 | 58
285 | 7 | 59
285 | 8 | 59
285 | 9 | 60
285 | 10 | 62
285 | 11 | 64
285 | 12 | 66
285 | 13 | 66
285 | 14 | 66
285 | 15 | 66
285 | 16 | 64
285 | 17 | 61
285 | 18 | 59
285 | 19 | 58
285 | 20 | 58
285 | 21 | 57
285 | 22 | 57
285 | 23 | 56
285 | 24 | 56 | 60.2083 | 4.7917 | -4.7917
286 | 1 | 56
286 | 2 | 55
286 | 3 | 55
286 | 4 | 54
286 | 5 | 54
286 | 6 | 53
286 | 7 | 55
286 | 8 | 56
286 | 9 | 58
286 | 10 | 59
286 | 11 | 61
286 | 12 | 62
286 | 13 | 63
286 | 14 | 64
286 | 15 | 65
286 | 16 | 63
286 | 17 | 60
286 | 18 | 58
286 | 19 | 56
286 | 20 | 54
286 | 21 | 52
286 | 22 | 52
286 | 23 | 51
286 | 24 | 51 | 56.9583 | 8.0417 | -8.0417
287 | 1 | 49
287 | 2 | 46
287 | 3 | 44
287 | 4 | 44
287 | 5 | 44
287 | 6 | 44
287 | 7 | 50
287 | 8 | 56
287 | 9 | 62
287 | 10 | 63
287 | 11 | 65
287 | 12 | 66
287 | 13 | 67
287 | 14 | 68
287 | 15 | 69
287 | 16 | 65
287 | 17 | 61
287 | 18 | 57
287 | 19 | 55
287 | 20 | 54
287 | 21 | 52
287 | 22 | 53
287 | 23 | 53
287 | 24 | 54 | 55.875 | 9.125 | -9.125
288 | 1 | 53
288 | 2 | 51
288 | 3 | 50
288 | 4 | 49
288 | 5 | 47
288 | 6 | 46
288 | 7 | 52
288 | 8 | 59
288 | 9 | 65
288 | 10 | 68
288 | 11 | 71
288 | 12 | 74
288 | 13 | 75
288 | 14 | 76
288 | 15 | 77
288 | 16 | 74
288 | 17 | 71
288 | 18 | 68
288 | 19 | 66
288 | 20 | 65
288 | 21 | 63
288 | 22 | 63
288 | 23 | 62
288 | 24 | 62 | 62.7917 | 2.2083 | -2.2083
289 | 1 | 62
289 | 2 | 61
289 | 3 | 61
289 | 4 | 60
289 | 5 | 58
289 | 6 | 57
289 | 7 | 59
289 | 8 | 60
289 | 9 | 62
289 | 10 | 64
289 | 11 | 65
289 | 12 | 67
289 | 13 | 68
289 | 14 | 69
289 | 15 | 70
289 | 16 | 67
289 | 17 | 65
289 | 18 | 62
289 | 19 | 59
289 | 20 | 55
289 | 21 | 52
289 | 22 | 51
289 | 23 | 51
289 | 24 | 50 | 60.625 | 4.375 | -4.375
290 | 1 | 49
290 | 2 | 48
290 | 3 | 47
290 | 4 | 46
290 | 5 | 45
290 | 6 | 44
290 | 7 | 50
290 | 8 | 57
290 | 9 | 63
290 | 10 | 65
290 | 11 | 67
290 | 12 | 69
290 | 13 | 69
290 | 14 | 69
290 | 15 | 69
290 | 16 | 64
290 | 17 | 60
290 | 18 | 55
290 | 19 | 53
290 | 20 | 51
290 | 21 | 49
290 | 22 | 49
290 | 23 | 48
290 | 24 | 48 | 55.5833 | 9.4167 | -9.4167
291 | 1 | 47
291 | 2 | 47
291 | 3 | 46
291 | 4 | 46
291 | 5 | 45
291 | 6 | 45
291 | 7 | 53
291 | 8 | 60
291 | 9 | 68
291 | 10 | 71
291 | 11 | 73
291 | 12 | 76
291 | 13 | 77
291 | 14 | 77
291 | 15 | 78
291 | 16 | 74
291 | 17 | 71
291 | 18 | 67
291 | 19 | 66
291 | 20 | 64
291 | 21 | 63
291 | 22 | 62
291 | 23 | 60
291 | 24 | 59 | 62.2917 | 2.7083 | -2.7083
292 | 1 | 59
292 | 2 | 60
292 | 3 | 60
292 | 4 | 59
292 | 5 | 59
292 | 6 | 58
292 | 7 | 63
292 | 8 | 67
292 | 9 | 72
292 | 10 | 75
292 | 11 | 78
292 | 12 | 81
292 | 13 | 81
292 | 14 | 82
292 | 15 | 82
292 | 16 | 78
292 | 17 | 74
292 | 18 | 70
292 | 19 | 69
292 | 20 | 69
292 | 21 | 68
292 | 22 | 67
292 | 23 | 67
292 | 24 | 66 | 69.3333 | -4.3333 | 4.3333
293 | 1 | 65
293 | 2 | 65
293 | 3 | 64
293 | 4 | 64
293 | 5 | 65
293 | 6 | 65
293 | 7 | 66
293 | 8 | 68
293 | 9 | 69
293 | 10 | 71
293 | 11 | 74
293 | 12 | 76
293 | 13 | 76
293 | 14 | 77
293 | 15 | 77
293 | 16 | 75
293 | 17 | 73
293 | 18 | 71
293 | 19 | 69
293 | 20 | 68
293 | 21 | 66
293 | 22 | 66
293 | 23 | 65
293 | 24 | 65 | 69.1667 | -4.1667 | 4.1667
294 | 1 | 64
294 | 2 | 64
294 | 3 | 63
294 | 4 | 63
294 | 5 | 62
294 | 6 | 62
294 | 7 | 66
294 | 8 | 69
294 | 9 | 73
294 | 10 | 75
294 | 11 | 76
294 | 12 | 78
294 | 13 | 78
294 | 14 | 79
294 | 15 | 79
294 | 16 | 76
294 | 17 | 72
294 | 18 | 69
294 | 19 | 66
294 | 20 | 64
294 | 21 | 61
294 | 22 | 62
294 | 23 | 63
294 | 24 | 64 | 68.6667 | -3.6667 | 3.6667
295 | 1 | 64
295 | 2 | 63
295 | 3 | 63
295 | 4 | 63
295 | 5 | 64
295 | 6 | 64
295 | 7 | 67
295 | 8 | 70
295 | 9 | 73
295 | 10 | 75
295 | 11 | 77
295 | 12 | 79
295 | 13 | 79
295 | 14 | 78
295 | 15 | 78
295 | 16 | 76
295 | 17 | 75
295 | 18 | 73
295 | 19 | 73
295 | 20 | 72
295 | 21 | 72
295 | 22 | 72
295 | 23 | 72
295 | 24 | 72 | 71.4167 | -6.4167 | 6.4167
296 | 1 | 72
296 | 2 | 72
296 | 3 | 72
296 | 4 | 71
296 | 5 | 71
296 | 6 | 70
296 | 7 | 71
296 | 8 | 73
296 | 9 | 74
296 | 10 | 74
296 | 11 | 75
296 | 12 | 75
296 | 13 | 76
296 | 14 | 76
296 | 15 | 77
296 | 16 | 76
296 | 17 | 74
296 | 18 | 73
296 | 19 | 72
296 | 20 | 72
296 | 21 | 71
296 | 22 | 71
296 | 23 | 70
296 | 24 | 70 | 72.8333 | -7.8333 | 7.8333
297 | 1 | 69
297 | 2 | 69
297 | 3 | 68
297 | 4 | 68
297 | 5 | 69
297 | 6 | 69
297 | 7 | 70
297 | 8 | 70
297 | 9 | 71
297 | 10 | 71
297 | 11 | 70
297 | 12 | 70
297 | 13 | 70
297 | 14 | 71
297 | 15 | 71
297 | 16 | 72
297 | 17 | 72
297 | 18 | 73
297 | 19 | 73
297 | 20 | 73
297 | 21 | 73
297 | 22 | 73
297 | 23 | 73
297 | 24 | 73 | 70.875 | -5.875 | 5.875
298 | 1 | 73
298 | 2 | 73
298 | 3 | 73
298 | 4 | 73
298 | 5 | 72
298 | 6 | 72
298 | 7 | 72
298 | 8 | 71
298 | 9 | 71
298 | 10 | 72
298 | 11 | 72
298 | 12 | 73
298 | 13 | 74
298 | 14 | 74
298 | 15 | 75
298 | 16 | 74
298 | 17 | 72
298 | 18 | 71
298 | 19 | 70
298 | 20 | 70
298 | 21 | 69
298 | 22 | 68
298 | 23 | 68
298 | 24 | 67 | 71.625 | -6.625 | 6.625
299 | 1 | 66
299 | 2 | 65
299 | 3 | 64
299 | 4 | 63
299 | 5 | 62
299 | 6 | 61
299 | 7 | 64
299 | 8 | 66
299 | 9 | 69
299 | 10 | 72
299 | 11 | 74
299 | 12 | 77
299 | 13 | 77
299 | 14 | 78
299 | 15 | 78
299 | 16 | 76
299 | 17 | 74
299 | 18 | 72
299 | 19 | 71
299 | 20 | 69
299 | 21 | 68
299 | 22 | 67
299 | 23 | 65
299 | 24 | 64 | 69.25 | -4.25 | 4.25
300 | 1 | 63
300 | 2 | 63
300 | 3 | 62
300 | 4 | 60
300 | 5 | 59
300 | 6 | 57
300 | 7 | 60
300 | 8 | 62
300 | 9 | 65
300 | 10 | 67
300 | 11 | 69
300 | 12 | 71
300 | 13 | 72
300 | 14 | 74
300 | 15 | 75
300 | 16 | 71
300 | 17 | 68
300 | 18 | 64
300 | 19 | 63
300 | 20 | 63
300 | 21 | 62
300 | 22 | 63
300 | 23 | 63
300 | 24 | 64 | 65 | 0 | 0
301 | 1 | 63
301 | 2 | 62
301 | 3 | 61
301 | 4 | 61
301 | 5 | 60
301 | 6 | 60
301 | 7 | 62
301 | 8 | 65
301 | 9 | 67
301 | 10 | 69
301 | 11 | 71
301 | 12 | 73
301 | 13 | 73
301 | 14 | 74
301 | 15 | 74
301 | 16 | 71
301 | 17 | 69
301 | 18 | 66
301 | 19 | 64
301 | 20 | 63
301 | 21 | 61
301 | 22 | 61
301 | 23 | 62
301 | 24 | 62 | 65.5833 | -0.58333 | 0.58333
302 | 1 | 61
302 | 2 | 59
302 | 3 | 58
302 | 4 | 58
302 | 5 | 57
302 | 6 | 57
302 | 7 | 61
302 | 8 | 66
302 | 9 | 70
302 | 10 | 72
302 | 11 | 73
302 | 12 | 75
302 | 13 | 76
302 | 14 | 76
302 | 15 | 77
302 | 16 | 74
302 | 17 | 71
302 | 18 | 68
302 | 19 | 66
302 | 20 | 65
302 | 21 | 63
302 | 22 | 63
302 | 23 | 62
302 | 24 | 62 | 66.25 | -1.25 | 1.25
303 | 1 | 61
303 | 2 | 59
303 | 3 | 58
303 | 4 | 58
303 | 5 | 57
303 | 6 | 57
303 | 7 | 61
303 | 8 | 65
303 | 9 | 69
303 | 10 | 72
303 | 11 | 74
303 | 12 | 77
303 | 13 | 77
303 | 14 | 77
303 | 15 | 77
303 | 16 | 75
303 | 17 | 74
303 | 18 | 72
303 | 19 | 71
303 | 20 | 70
303 | 21 | 69
303 | 22 | 68
303 | 23 | 68
303 | 24 | 67 | 68.0417 | -3.0417 | 3.0417
304 | 1 | 66
304 | 2 | 65
304 | 3 | 64
304 | 4 | 63
304 | 5 | 63
304 | 6 | 62
304 | 7 | 65
304 | 8 | 68
304 | 9 | 71
304 | 10 | 74
304 | 11 | 76
304 | 12 | 79
304 | 13 | 80
304 | 14 | 80
304 | 15 | 81
304 | 16 | 79
304 | 17 | 76
304 | 18 | 74
304 | 19 | 72
304 | 20 | 71
304 | 21 | 69
304 | 22 | 67
304 | 23 | 65
304 | 24 | 64 | 70.5833 | -5.5833 | 5.5833
305 | 1 | 62
305 | 2 | 60
305 | 3 | 59
305 | 4 | 56
305 | 5 | 54
305 | 6 | 55
305 | 7 | 58
305 | 8 | 64
305 | 9 | 68
305 | 10 | 72
305 | 11 | 73
305 | 12 | 76
305 | 13 | 78
305 | 14 | 79
305 | 15 | 79
305 | 16 | 78
305 | 17 | 74
305 | 18 | 65
305 | 19 | 61
305 | 20 | 59
305 | 21 | 56
305 | 22 | 57
305 | 23 | 56
305 | 24 | 56 | 64.7917 | 0.20833 | -0.20833
306 | 1 | 58
306 | 2 | 58
306 | 3 | 57
306 | 4 | 56
306 | 5 | 55
306 | 6 | 60
306 | 7 | 61
306 | 8 | 67
306 | 9 | 70
306 | 10 | 73
306 | 11 | 77
306 | 12 | 79
306 | 13 | 80
306 | 14 | 79
306 | 15 | 78
306 | 16 | 79
306 | 17 | 74
306 | 18 | 70
306 | 19 | 66
306 | 20 | 63
306 | 21 | 62
306 | 22 | 63
306 | 23 | 61
306 | 24 | 60 | 66.9167 | -1.9167 | 1.9167
307 | 1 | 64
307 | 2 | 65
307 | 3 | 63
307 | 4 | 63
307 | 5 | 63
307 | 6 | 62
307 | 7 | 65
307 | 8 | 68
307 | 9 | 70
307 | 10 | 73
307 | 11 | 72
307 | 12 | 72
307 | 13 | 70
307 | 14 | 70
307 | 15 | 73
307 | 16 | 73
307 | 17 | 71
307 | 18 | 72
307 | 19 | 70
307 | 20 | 69
307 | 21 | 69
307 | 22 | 68
307 | 23 | 68
307 | 24 | 67 | 68.3333 | -3.3333 | 3.3333
308 | 1 | 67
308 | 2 | 67
308 | 3 | 68
308 | 4 | 69
308 | 5 | 66
308 | 6 | 66
308 | 7 | 67
308 | 8 | 67
308 | 9 | 66
308 | 10 | 68
308 | 11 | 68
308 | 12 | 71
308 | 13 | 71
308 | 14 | 71
308 | 15 | 73
308 | 16 | 72
308 | 17 | 70
308 | 18 | 67
308 | 19 | 68
308 | 20 | 68
308 | 21 | 66
308 | 22 | 66
308 | 23 | 66
308 | 24 | 64 | 68 | -3 | 3
309 | 1 | 61
309 | 2 | 62
309 | 3 | 61
309 | 4 | 63
309 | 5 | 62
309 | 6 | 61
309 | 7 | 62
309 | 8 | 68
309 | 9 | 70
309 | 10 | 73
309 | 11 | 75
309 | 12 | 78
309 | 13 | 79
309 | 14 | 80
309 | 15 | 80
309 | 16 | 79
309 | 17 | 75
309 | 18 | 71
309 | 19 | 71
309 | 20 | 69
309 | 21 | 67
309 | 22 | 64
309 | 23 | 63
309 | 24 | 62 | 69 | -4 | 4
310 | 1 | 60
310 | 2 | 58
310 | 3 | 57
310 | 4 | 56
310 | 5 | 55
310 | 6 | 53
310 | 7 | 53
310 | 8 | 56
310 | 9 | 57
310 | 10 | 58
310 | 11 | 61
310 | 12 | 63
310 | 13 | 66
310 | 14 | 67
310 | 15 | 68
310 | 16 | 68
310 | 17 | 62
310 | 18 | 54
310 | 19 | 50
310 | 20 | 49
310 | 21 | 46
310 | 22 | 47
310 | 23 | 46
310 | 24 | 46 | 56.5 | 8.5 | -8.5
311 | 1 | 46
311 | 2 | 46
311 | 3 | 50
311 | 4 | 50
311 | 5 | 50
311 | 6 | 49
311 | 7 | 53
311 | 8 | 61
311 | 9 | 69
311 | 10 | 73
311 | 11 | 74
311 | 12 | 73
311 | 13 | 74
311 | 14 | 74
311 | 15 | 73
311 | 16 | 71
311 | 17 | 71
311 | 18 | 70
311 | 19 | 67
311 | 20 | 67
311 | 21 | 67
311 | 22 | 66
311 | 23 | 66
311 | 24 | 65 | 63.5417 | 1.4583 | -1.4583
312 | 1 | 64
312 | 2 | 64
312 | 3 | 64
312 | 4 | 65
312 | 5 | 64
312 | 6 | 66
312 | 7 | 67
312 | 8 | 71
312 | 9 | 73
312 | 10 | 76
312 | 11 | 78
312 | 12 | 79
312 | 13 | 79
312 | 14 | 77
312 | 15 | 77
312 | 16 | 75
312 | 17 | 73
312 | 18 | 72
312 | 19 | 71
312 | 20 | 71
312 | 21 | 71
312 | 22 | 69
312 | 23 | 70
312 | 24 | 69 | 71.0417 | -6.0417 | 6.0417
313 | 1 | 68
313 | 2 | 68
313 | 3 | 69
313 | 4 | 69
313 | 5 | 68
313 | 6 | 68
313 | 7 | 69
313 | 8 | 70
313 | 9 | 72
313 | 10 | 73
313 | 11 | 76
313 | 12 | 74
313 | 13 | 74
313 | 14 | 75
313 | 15 | 75
313 | 16 | 76
313 | 17 | 74
313 | 18 | 71
313 | 19 | 68
313 | 20 | 66
313 | 21 | 66
313 | 22 | 66
313 | 23 | 65
313 | 24 | 64 | 70.1667 | -5.1667 | 5.1667
314 | 1 | 62
314 | 2 | 61
314 | 3 | 61
314 | 4 | 60
314 | 5 | 60
314 | 6 | 59
314 | 7 | 59
314 | 8 | 60
314 | 9 | 59
314 | 10 | 57
314 | 11 | 56
314 | 12 | 52
314 | 13 | 50
314 | 14 | 50
314 | 15 | 51
314 | 16 | 50
314 | 17 | 50
314 | 18 | 49
314 | 19 | 49
314 | 20 | 49
314 | 21 | 48
314 | 22 | 48
314 | 23 | 48
314 | 24 | 48 | 54 | 11 | -11
315 | 1 | 47
315 | 2 | 46
315 | 3 | 43
315 | 4 | 43
315 | 5 | 42
315 | 6 | 41
315 | 7 | 42
315 | 8 | 44
315 | 9 | 47
315 | 10 | 48
315 | 11 | 50
315 | 12 | 53
315 | 13 | 55
315 | 14 | 57
315 | 15 | 58
315 | 16 | 56
315 | 17 | 54
315 | 18 | 53
315 | 19 | 53
315 | 20 | 52
315 | 21 | 52
315 | 22 | 51
315 | 23 | 50
315 | 24 | 48 | 49.375 | 15.625 | -15.625
316 | 1 | 47
316 | 2 | 45
316 | 3 | 44
316 | 4 | 41
316 | 5 | 39
316 | 6 | 41
316 | 7 | 42
316 | 8 | 48
316 | 9 | 52
316 | 10 | 54
316 | 11 | 56
316 | 12 | 58
316 | 13 | 58
316 | 14 | 58
316 | 15 | 60
316 | 16 | 60
316 | 17 | 53
316 | 18 | 49
316 | 19 | 45
316 | 20 | 42
316 | 21 | 43
316 | 22 | 45
316 | 23 | 44
316 | 24 | 40 | 48.5 | 16.5 | -16.5
317 | 1 | 42
317 | 2 | 44
317 | 3 | 42
317 | 4 | 41
317 | 5 | 43
317 | 6 | 42
317 | 7 | 43
317 | 8 | 47
317 | 9 | 55
317 | 10 | 59
317 | 11 | 58
317 | 12 | 59
317 | 13 | 60
317 | 14 | 62
317 | 15 | 62
317 | 16 | 62
317 | 17 | 58
317 | 18 | 53
317 | 19 | 53
317 | 20 | 51
317 | 21 | 49
317 | 22 | 50
317 | 23 | 53
317 | 24 | 52 | 51.6667 | 13.3333 | -13.3333
318 | 1 | 52
318 | 2 | 54
318 | 3 | 54
318 | 4 | 55
318 | 5 | 56
318 | 6 | 57
318 | 7 | 58
318 | 8 | 61
318 | 9 | 64
318 | 10 | 68
318 | 11 | 69
318 | 12 | 70
318 | 13 | 73
318 | 14 | 73
318 | 15 | 73
318 | 16 | 70
318 | 17 | 67
318 | 18 | 64
318 | 19 | 66
318 | 20 | 66
318 | 21 | 66
318 | 22 | 66
318 | 23 | 66
318 | 24 | 66 | 63.9167 | 1.0833 | -1.0833
319 | 1 | 66
319 | 2 | 64
319 | 3 | 65
319 | 4 | 61
319 | 5 | 60
319 | 6 | 61
319 | 7 | 63
319 | 8 | 67
319 | 9 | 71
319 | 10 | 75
319 | 11 | 77
319 | 12 | 76
319 | 13 | 76
319 | 14 | 78
319 | 15 | 76
319 | 16 | 74
319 | 17 | 72
319 | 18 | 72
319 | 19 | 71
319 | 20 | 71
319 | 21 | 71
319 | 22 | 72
319 | 23 | 72
319 | 24 | 72 | 70.125 | -5.125 | 5.125
320 | 1 | 72
320 | 2 | 73
320 | 3 | 73
320 | 4 | 73
320 | 5 | 73
320 | 6 | 73
320 | 7 | 73
320 | 8 | 74
320 | 9 | 76
320 | 10 | 78
320 | 11 | 79
320 | 12 | 79
320 | 13 | 79
320 | 14 | 79
320 | 15 | 77
320 | 16 | 76
320 | 17 | 75
320 | 18 | 64
320 | 19 | 63
320 | 20 | 63
320 | 21 | 63
320 | 22 | 63
320 | 23 | 64
320 | 24 | 63 | 71.875 | -6.875 | 6.875
321 | 1 | 62
321 | 2 | 61
321 | 3 | 59
321 | 4 | 58
321 | 5 | 57
321 | 6 | 56
321 | 7 | 57
321 | 8 | 59
321 | 9 | 61
321 | 10 | 64
321 | 11 | 66
321 | 12 | 68
321 | 13 | 69
321 | 14 | 71
321 | 15 | 71
321 | 16 | 69
321 | 17 | 65
321 | 18 | 57
321 | 19 | 56
321 | 20 | 58
321 | 21 | 51
321 | 22 | 50
321 | 23 | 50
321 | 24 | 56 | 60.4583 | 4.5417 | -4.5417
322 | 1 | 56
322 | 2 | 55
322 | 3 | 52
322 | 4 | 54
322 | 5 | 55
322 | 6 | 55
322 | 7 | 55
322 | 8 | 57
322 | 9 | 59
322 | 10 | 59
322 | 11 | 62
322 | 12 | 64
322 | 13 | 65
322 | 14 | 64
322 | 15 | 66
322 | 16 | 65
322 | 17 | 62
322 | 18 | 58
322 | 19 | 57
322 | 20 | 58
322 | 21 | 60
322 | 22 | 60
322 | 23 | 61
322 | 24 | 60 | 59.125 | 5.875 | -5.875
323 | 1 | 59
323 | 2 | 59
323 | 3 | 57
323 | 4 | 57
323 | 5 | 57
323 | 6 | 56
323 | 7 | 56
323 | 8 | 58
323 | 9 | 60
323 | 10 | 59
323 | 11 | 61
323 | 12 | 64
323 | 13 | 67
323 | 14 | 67
323 | 15 | 68
323 | 16 | 66
323 | 17 | 63
323 | 18 | 60
323 | 19 | 59
323 | 20 | 59
323 | 21 | 57
323 | 22 | 55
323 | 23 | 54
323 | 24 | 52 | 59.5833 | 5.4167 | -5.4167
324 | 1 | 51
324 | 2 | 51
324 | 3 | 50
324 | 4 | 50
324 | 5 | 50
324 | 6 | 50
324 | 7 | 50
324 | 8 | 52
324 | 9 | 53
324 | 10 | 55
324 | 11 | 57
324 | 12 | 59
324 | 13 | 62
324 | 14 | 63
324 | 15 | 65
324 | 16 | 64
324 | 17 | 61
324 | 18 | 57
324 | 19 | 56
324 | 20 | 56
324 | 21 | 56
324 | 22 | 54
324 | 23 | 53
324 | 24 | 51 | 55.25 | 9.75 | -9.75
325 | 1 | 50
325 | 2 | 48
325 | 3 | 45
325 | 4 | 44
325 | 5 | 45
325 | 6 | 44
325 | 7 | 45
325 | 8 | 48
325 | 9 | 50
325 | 10 | 52
325 | 11 | 54
325 | 12 | 55
325 | 13 | 57
325 | 14 | 58
325 | 15 | 59
325 | 16 | 59
325 | 17 | 53
325 | 18 | 46
325 | 19 | 50
325 | 20 | 47
325 | 21 | 43
325 | 22 | 45
325 | 23 | 40
325 | 24 | 40 | 49.0417 | 15.9583 | -15.9583
326 | 1 | 37
326 | 2 | 39
326 | 3 | 39
326 | 4 | 39
326 | 5 | 40
326 | 6 | 43
326 | 7 | 43
326 | 8 | 52
326 | 9 | 60
326 | 10 | 66
326 | 11 | 69
326 | 12 | 70
326 | 13 | 71
326 | 14 | 71
326 | 15 | 70
326 | 16 | 69
326 | 17 | 65
326 | 18 | 61
326 | 19 | 59
326 | 20 | 58
326 | 21 | 58
326 | 22 | 57
326 | 23 | 57
326 | 24 | 54 | 56.125 | 8.875 | -8.875
327 | 1 | 54
327 | 2 | 52
327 | 3 | 49
327 | 4 | 50
327 | 5 | 49
327 | 6 | 51
327 | 7 | 52
327 | 8 | 62
327 | 9 | 69
327 | 10 | 73
327 | 11 | 75
327 | 12 | 78
327 | 13 | 78
327 | 14 | 77
327 | 15 | 77
327 | 16 | 74
327 | 17 | 71
327 | 18 | 68
327 | 19 | 64
327 | 20 | 64
327 | 21 | 65
327 | 22 | 64
327 | 23 | 64
327 | 24 | 65 | 64.375 | 0.625 | -0.625
328 | 1 | 64
328 | 2 | 62
328 | 3 | 63
328 | 4 | 63
328 | 5 | 64
328 | 6 | 62
328 | 7 | 64
328 | 8 | 67
328 | 9 | 71
328 | 10 | 73
328 | 11 | 76
328 | 12 | 78
328 | 13 | 77
328 | 14 | 75
328 | 15 | 76
328 | 16 | 72
328 | 17 | 70
328 | 18 | 67
328 | 19 | 67
328 | 20 | 67
328 | 21 | 66
328 | 22 | 65
328 | 23 | 65
328 | 24 | 64 | 68.25 | -3.25 | 3.25
329 | 1 | 65
329 | 2 | 66
329 | 3 | 66
329 | 4 | 64
329 | 5 | 63
329 | 6 | 62
329 | 7 | 61
329 | 8 | 66
329 | 9 | 67
329 | 10 | 73
329 | 11 | 75
329 | 12 | 77
329 | 13 | 77
329 | 14 | 77
329 | 15 | 77
329 | 16 | 75
329 | 17 | 72
329 | 18 | 71
329 | 19 | 69
329 | 20 | 68
329 | 21 | 68
329 | 22 | 68
329 | 23 | 67
329 | 24 | 67 | 69.2083 | -4.2083 | 4.2083
330 | 1 | 65
330 | 2 | 65
330 | 3 | 66
330 | 4 | 64
330 | 5 | 63
330 | 6 | 65
330 | 7 | 65
330 | 8 | 66
330 | 9 | 67
330 | 10 | 72
330 | 11 | 75
330 | 12 | 75
330 | 13 | 76
330 | 14 | 75
330 | 15 | 71
330 | 16 | 71
330 | 17 | 69
330 | 18 | 67
330 | 19 | 68
330 | 20 | 64
330 | 21 | 66
330 | 22 | 67
330 | 23 | 63
330 | 24 | 65 | 67.9167 | -2.9167 | 2.9167
331 | 1 | 66
331 | 2 | 64
331 | 3 | 63
331 | 4 | 65
331 | 5 | 65
331 | 6 | 64
331 | 7 | 63
331 | 8 | 64
331 | 9 | 65
331 | 10 | 66
331 | 11 | 69
331 | 12 | 72
331 | 13 | 74
331 | 14 | 72
331 | 15 | 75
331 | 16 | 73
331 | 17 | 71
331 | 18 | 67
331 | 19 | 68
331 | 20 | 68
331 | 21 | 68
331 | 22 | 68
331 | 23 | 63
331 | 24 | 58 | 67.125 | -2.125 | 2.125
332 | 1 | 57
332 | 2 | 56
332 | 3 | 55
332 | 4 | 55
332 | 5 | 54
332 | 6 | 54
332 | 7 | 51
332 | 8 | 51
332 | 9 | 52
332 | 10 | 54
332 | 11 | 56
332 | 12 | 56
332 | 13 | 58
332 | 14 | 60
332 | 15 | 60
332 | 16 | 60
332 | 17 | 55
332 | 18 | 51
332 | 19 | 51
332 | 20 | 52
332 | 21 | 51
332 | 22 | 51
332 | 23 | 49
332 | 24 | 48 | 54.0417 | 10.9583 | -10.9583
333 | 1 | 47
333 | 2 | 46
333 | 3 | 46
333 | 4 | 45
333 | 5 | 46
333 | 6 | 47
333 | 7 | 46
333 | 8 | 51
333 | 9 | 53
333 | 10 | 55
333 | 11 | 57
333 | 12 | 56
333 | 13 | 58
333 | 14 | 58
333 | 15 | 59
333 | 16 | 57
333 | 17 | 55
333 | 18 | 54
333 | 19 | 54
333 | 20 | 53
333 | 21 | 53
333 | 22 | 53
333 | 23 | 53
333 | 24 | 53 | 52.2917 | 12.7083 | -12.7083
334 | 1 | 51
334 | 2 | 52
334 | 3 | 52
334 | 4 | 52
334 | 5 | 52
334 | 6 | 52
334 | 7 | 52
334 | 8 | 53
334 | 9 | 56
334 | 10 | 59
334 | 11 | 61
334 | 12 | 63
334 | 13 | 65
334 | 14 | 64
334 | 15 | 65
334 | 16 | 64
334 | 17 | 60
334 | 18 | 57
334 | 19 | 56
334 | 20 | 55
334 | 21 | 56
334 | 22 | 56
334 | 23 | 56
334 | 24 | 58 | 56.9583 | 8.0417 | -8.0417
335 | 1 | 60
335 | 2 | 61
335 | 3 | 60
335 | 4 | 60
335 | 5 | 60
335 | 6 | 57
335 | 7 | 53
335 | 8 | 60
335 | 9 | 66
335 | 10 | 71
335 | 11 | 74
335 | 12 | 77
335 | 13 | 75
335 | 14 | 77
335 | 15 | 77
335 | 16 | 73
335 | 17 | 69
335 | 18 | 66
335 | 19 | 66
335 | 20 | 59
335 | 21 | 60
335 | 22 | 58
335 | 23 | 56
335 | 24 | 55 | 64.5833 | 0.41667 | -0.41667
336 | 1 | 54
336 | 2 | 54
336 | 3 | 54
336 | 4 | 54
336 | 5 | 53
336 | 6 | 51
336 | 7 | 50
336 | 8 | 51
336 | 9 | 57
336 | 10 | 59
336 | 11 | 60
336 | 12 | 62
336 | 13 | 63
336 | 14 | 64
336 | 15 | 64
336 | 16 | 63
336 | 17 | 58
336 | 18 | 55
336 | 19 | 50
336 | 20 | 47
336 | 21 | 47
336 | 22 | 44
336 | 23 | 44
336 | 24 | 45 | 54.2917 | 10.7083 | -10.7083
337 | 1 | 46
337 | 2 | 43
337 | 3 | 44
337 | 4 | 48
337 | 5 | 48
337 | 6 | 45
337 | 7 | 44
337 | 8 | 54
337 | 9 | 64
337 | 10 | 68
337 | 11 | 71
337 | 12 | 73
337 | 13 | 75
337 | 14 | 74
337 | 15 | 74
337 | 16 | 71
337 | 17 | 67
337 | 18 | 63
337 | 19 | 61
337 | 20 | 60
337 | 21 | 60
337 | 22 | 60
337 | 23 | 59
337 | 24 | 59 | 59.625 | 5.375 | -5.375
338 | 1 | 58
338 | 2 | 60
338 | 3 | 60
338 | 4 | 60
338 | 5 | 59
338 | 6 | 56
338 | 7 | 55
338 | 8 | 56
338 | 9 | 58
338 | 10 | 59
338 | 11 | 60
338 | 12 | 62
338 | 13 | 63
338 | 14 | 64
338 | 15 | 64
338 | 16 | 63
338 | 17 | 59
338 | 18 | 58
338 | 19 | 56
338 | 20 | 55
338 | 21 | 54
338 | 22 | 52
338 | 23 | 51
338 | 24 | 51 | 58.0417 | 6.9583 | -6.9583
339 | 1 | 50
339 | 2 | 50
339 | 3 | 49
339 | 4 | 49
339 | 5 | 48
339 | 6 | 49
339 | 7 | 49
339 | 8 | 50
339 | 9 | 53
339 | 10 | 55
339 | 11 | 56
339 | 12 | 56
339 | 13 | 56
339 | 14 | 57
339 | 15 | 59
339 | 16 | 58
339 | 17 | 54
339 | 18 | 48
339 | 19 | 44
339 | 20 | 44
339 | 21 | 45
339 | 22 | 46
339 | 23 | 47
339 | 24 | 44 | 50.6667 | 14.3333 | -14.3333
340 | 1 | 43
340 | 2 | 45
340 | 3 | 47
340 | 4 | 44
340 | 5 | 42
340 | 6 | 46
340 | 7 | 48
340 | 8 | 50
340 | 9 | 52
340 | 10 | 55
340 | 11 | 59
340 | 12 | 60
340 | 13 | 60
340 | 14 | 60
340 | 15 | 61
340 | 16 | 60
340 | 17 | 57
340 | 18 | 56
340 | 19 | 56
340 | 20 | 56
340 | 21 | 56
340 | 22 | 56
340 | 23 | 56
340 | 24 | 53 | 53.25 | 11.75 | -11.75
341 | 1 | 51
341 | 2 | 46
341 | 3 | 47
341 | 4 | 45
341 | 5 | 50
341 | 6 | 51
341 | 7 | 54
341 | 8 | 58
341 | 9 | 64
341 | 10 | 69
341 | 11 | 71
341 | 12 | 74
341 | 13 | 73
341 | 14 | 75
341 | 15 | 74
341 | 16 | 72
341 | 17 | 69
341 | 18 | 67
341 | 19 | 65
341 | 20 | 63
341 | 21 | 62
341 | 22 | 60
341 | 23 | 59
341 | 24 | 56 | 61.4583 | 3.5417 | -3.5417
342 | 1 | 54
342 | 2 | 57
342 | 3 | 56
342 | 4 | 56
342 | 5 | 57
342 | 6 | 56
342 | 7 | 55
342 | 8 | 60
342 | 9 | 64
342 | 10 | 67
342 | 11 | 73
342 | 12 | 73
342 | 13 | 75
342 | 14 | 76
342 | 15 | 77
342 | 16 | 75
342 | 17 | 68
342 | 18 | 61
342 | 19 | 60
342 | 20 | 64
342 | 21 | 62
342 | 22 | 62
342 | 23 | 62
342 | 24 | 60 | 63.75 | 1.25 | -1.25
343 | 1 | 59
343 | 2 | 57
343 | 3 | 56
343 | 4 | 55
343 | 5 | 54
343 | 6 | 53
343 | 7 | 51
343 | 8 | 53
343 | 9 | 56
343 | 10 | 58
343 | 11 | 59
343 | 12 | 60
343 | 13 | 61
343 | 14 | 63
343 | 15 | 65
343 | 16 | 64
343 | 17 | 57
343 | 18 | 51
343 | 19 | 46
343 | 20 | 45
343 | 21 | 44
343 | 22 | 42
343 | 23 | 50
343 | 24 | 52 | 54.625 | 10.375 | -10.375
344 | 1 | 51
344 | 2 | 52
344 | 3 | 51
344 | 4 | 50
344 | 5 | 49
344 | 6 | 48
344 | 7 | 48
344 | 8 | 50
344 | 9 | 51
344 | 10 | 53
344 | 11 | 54
344 | 12 | 54
344 | 13 | 55
344 | 14 | 58
344 | 15 | 58
344 | 16 | 58
344 | 17 | 54
344 | 18 | 46
344 | 19 | 47
344 | 20 | 48
344 | 21 | 45
344 | 22 | 43
344 | 23 | 45
344 | 24 | 44 | 50.5 | 14.5 | -14.5
345 | 1 | 42
345 | 2 | 42
345 | 3 | 40
345 | 4 | 43
345 | 5 | 45
345 | 6 | 48
345 | 7 | 49
345 | 8 | 50
345 | 9 | 56
345 | 10 | 58
345 | 11 | 60
345 | 12 | 63
345 | 13 | 63
345 | 14 | 63
345 | 15 | 63
345 | 16 | 62
345 | 17 | 61
345 | 18 | 59
345 | 19 | 60
345 | 20 | 60
345 | 21 | 61
345 | 22 | 60
345 | 23 | 60
345 | 24 | 61 | 55.375 | 9.625 | -9.625
346 | 1 | 62
346 | 2 | 62
346 | 3 | 62
346 | 4 | 62
346 | 5 | 63
346 | 6 | 63
346 | 7 | 63
346 | 8 | 57
346 | 9 | 54
346 | 10 | 53
346 | 11 | 51
346 | 12 | 50
346 | 13 | 49
346 | 14 | 50
346 | 15 | 50
346 | 16 | 50
346 | 17 | 50
346 | 18 | 50
346 | 19 | 50
346 | 20 | 50
346 | 21 | 49
346 | 22 | 49
346 | 23 | 49
346 | 24 | 49 | 54.0417 | 10.9583 | -10.9583
347 | 1 | 49
347 | 2 | 49
347 | 3 | 49
347 | 4 | 49
347 | 5 | 49
347 | 6 | 49
347 | 7 | 49
347 | 8 | 49
347 | 9 | 50
347 | 10 | 50
347 | 11 | 51
347 | 12 | 51
347 | 13 | 54
347 | 14 | 54
347 | 15 | 56
347 | 16 | 57
347 | 17 | 55
347 | 18 | 54
347 | 19 | 54
347 | 20 | 55
347 | 21 | 55
347 | 22 | 56
347 | 23 | 57
347 | 24 | 57 | 52.4167 | 12.5833 | -12.5833
348 | 1 | 58
348 | 2 | 60
348 | 3 | 61
348 | 4 | 61
348 | 5 | 60
348 | 6 | 63
348 | 7 | 56
348 | 8 | 56
348 | 9 | 57
348 | 10 | 58
348 | 11 | 59
348 | 12 | 57
348 | 13 | 54
348 | 14 | 52
348 | 15 | 51
348 | 16 | 50
348 | 17 | 50
348 | 18 | 50
348 | 19 | 51
348 | 20 | 50
348 | 21 | 49
348 | 22 | 49
348 | 23 | 47
348 | 24 | 47 | 54.4167 | 10.5833 | -10.5833
349 | 1 | 47
349 | 2 | 46
349 | 3 | 45
349 | 4 | 45
349 | 5 | 45
349 | 6 | 45
349 | 7 | 44
349 | 8 | 44
349 | 9 | 46
349 | 10 | 48
349 | 11 | 49
349 | 12 | 51
349 | 13 | 54
349 | 14 | 56
349 | 15 | 56
349 | 16 | 56
349 | 17 | 52
349 | 18 | 51
349 | 19 | 45
349 | 20 | 40
349 | 21 | 41
349 | 22 | 41
349 | 23 | 38
349 | 24 | 45 | 47.0833 | 17.9167 | -17.9167
350 | 1 | 39
350 | 2 | 38
350 | 3 | 38
350 | 4 | 39
350 | 5 | 39
350 | 6 | 40
350 | 7 | 40
350 | 8 | 47
350 | 9 | 54
350 | 10 | 58
350 | 11 | 62
350 | 12 | 64
350 | 13 | 64
350 | 14 | 65
350 | 15 | 65
350 | 16 | 65
350 | 17 | 62
350 | 18 | 58
350 | 19 | 56
350 | 20 | 55
350 | 21 | 53
350 | 22 | 53
350 | 23 | 54
350 | 24 | 54 | 52.5833 | 12.4167 | -12.4167
351 | 1 | 53
351 | 2 | 54
351 | 3 | 57
351 | 4 | 59
351 | 5 | 61
351 | 6 | 60
351 | 7 | 60
351 | 8 | 63
351 | 9 | 67
351 | 10 | 71
351 | 11 | 73
351 | 12 | 75
351 | 13 | 60
351 | 14 | 58
351 | 15 | 57
351 | 16 | 53
351 | 17 | 50
351 | 18 | 50
351 | 19 | 49
351 | 20 | 48
351 | 21 | 47
351 | 22 | 45
351 | 23 | 44
351 | 24 | 43 | 56.5417 | 8.4583 | -8.4583
352 | 1 | 42
352 | 2 | 42
352 | 3 | 41
352 | 4 | 40
352 | 5 | 39
352 | 6 | 38
352 | 7 | 37
352 | 8 | 38
352 | 9 | 38
352 | 10 | 39
352 | 11 | 41
352 | 12 | 43
352 | 13 | 44
352 | 14 | 45
352 | 15 | 46
352 | 16 | 45
352 | 17 | 42
352 | 18 | 40
352 | 19 | 38
352 | 20 | 37
352 | 21 | 36
352 | 22 | 35
352 | 23 | 33
352 | 24 | 32 | 39.625 | 25.375 | -25.375
353 | 1 | 31
353 | 2 | 30
353 | 3 | 30
353 | 4 | 29
353 | 5 | 28
353 | 6 | 28
353 | 7 | 27
353 | 8 | 29
353 | 9 | 31
353 | 10 | 32
353 | 11 | 34
353 | 12 | 36
353 | 13 | 35
353 | 14 | 38
353 | 15 | 38
353 | 16 | 38
353 | 17 | 35
353 | 18 | 33
353 | 19 | 33
353 | 20 | 37
353 | 21 | 38
353 | 22 | 38
353 | 23 | 37
353 | 24 | 33 | 33.25 | 31.75 | -31.75
354 | 1 | 33
354 | 2 | 31
354 | 3 | 35
354 | 4 | 36
354 | 5 | 36
354 | 6 | 36
354 | 7 | 36
354 | 8 | 37
354 | 9 | 38
354 | 10 | 40
354 | 11 | 46
354 | 12 | 45
354 | 13 | 46
354 | 14 | 47
354 | 15 | 48
354 | 16 | 48
354 | 17 | 46
354 | 18 | 46
354 | 19 | 46
354 | 20 | 46
354 | 21 | 49
354 | 22 | 51
354 | 23 | 52
354 | 24 | 51 | 42.7083 | 22.2917 | -22.2917
355 | 1 | 53
355 | 2 | 53
355 | 3 | 52
355 | 4 | 53
355 | 5 | 54
355 | 6 | 55
355 | 7 | 56
355 | 8 | 60
355 | 9 | 63
355 | 10 | 65
355 | 11 | 67
355 | 12 | 69
355 | 13 | 72
355 | 14 | 72
355 | 15 | 71
355 | 16 | 70
355 | 17 | 69
355 | 18 | 66
355 | 19 | 64
355 | 20 | 63
355 | 21 | 63
355 | 22 | 63
355 | 23 | 63
355 | 24 | 64 | 62.5 | 2.5 | -2.5
356 | 1 | 64
356 | 2 | 64
356 | 3 | 63
356 | 4 | 63
356 | 5 | 64
356 | 6 | 65
356 | 7 | 67
356 | 8 | 68
356 | 9 | 68
356 | 10 | 71
356 | 11 | 72
356 | 12 | 73
356 | 13 | 73
356 | 14 | 75
356 | 15 | 74
356 | 16 | 73
356 | 17 | 72
356 | 18 | 70
356 | 19 | 69
356 | 20 | 69
356 | 21 | 68
356 | 22 | 67
356 | 23 | 67
356 | 24 | 68 | 68.625 | -3.625 | 3.625
357 | 1 | 68
357 | 2 | 67
357 | 3 | 58
357 | 4 | 56
357 | 5 | 55
357 | 6 | 55
357 | 7 | 54
357 | 8 | 53
357 | 9 | 54
357 | 10 | 55
357 | 11 | 55
357 | 12 | 58
357 | 13 | 58
357 | 14 | 59
357 | 15 | 60
357 | 16 | 57
357 | 17 | 56
357 | 18 | 54
357 | 19 | 52
357 | 20 | 50
357 | 21 | 49
357 | 22 | 48
357 | 23 | 47
357 | 24 | 47 | 55.2083 | 9.7917 | -9.7917
358 | 1 | 47
358 | 2 | 46
358 | 3 | 46
358 | 4 | 46
358 | 5 | 46
358 | 6 | 46
358 | 7 | 45
358 | 8 | 45
358 | 9 | 46
358 | 10 | 46
358 | 11 | 47
358 | 12 | 47
358 | 13 | 46
358 | 14 | 47
358 | 15 | 47
358 | 16 | 46
358 | 17 | 45
358 | 18 | 46
358 | 19 | 46
358 | 20 | 45
358 | 21 | 45
358 | 22 | 45
358 | 23 | 45
358 | 24 | 45 | 45.875 | 19.125 | -19.125
359 | 1 | 45
359 | 2 | 45
359 | 3 | 45
359 | 4 | 46
359 | 5 | 46
359 | 6 | 46
359 | 7 | 46
359 | 8 | 46
359 | 9 | 47
359 | 10 | 48
359 | 11 | 49
359 | 12 | 49
359 | 13 | 51
359 | 14 | 52
359 | 15 | 51
359 | 16 | 51
359 | 17 | 49
359 | 18 | 48
359 | 19 | 46
359 | 20 | 44
359 | 21 | 44
359 | 22 | 44
359 | 23 | 47
359 | 24 | 48 | 47.2083 | 17.7917 | -17.7917
360 | 1 | 48
360 | 2 | 49
360 | 3 | 49
360 | 4 | 49
360 | 5 | 49
360 | 6 | 44
360 | 7 | 43
360 | 8 | 44
360 | 9 | 53
360 | 10 | 59
360 | 11 | 61
360 | 12 | 63
360 | 13 | 62
360 | 14 | 63
360 | 15 | 67
360 | 16 | 66
360 | 17 | 64
360 | 18 | 63
360 | 19 | 63
360 | 20 | 62
360 | 21 | 62
360 | 22 | 62
360 | 23 | 62
360 | 24 | 63 | 57.0833 | 7.9167 | -7.9167
361 | 1 | 62
361 | 2 | 58
361 | 3 | 58
361 | 4 | 56
361 | 5 | 52
361 | 6 | 49
361 | 7 | 41
361 | 8 | 47
361 | 9 | 54
361 | 10 | 58
361 | 11 | 59
361 | 12 | 62
361 | 13 | 64
361 | 14 | 64
361 | 15 | 66
361 | 16 | 65
361 | 17 | 63
361 | 18 | 60
361 | 19 | 57
361 | 20 | 59
361 | 21 | 57
361 | 22 | 58
361 | 23 | 60
361 | 24 | 61 | 57.9167 | 7.0833 | -7.0833
362 | 1 | 62
362 | 2 | 63
362 | 3 | 66
362 | 4 | 65
362 | 5 | 65
362 | 6 | 66
362 | 7 | 66
362 | 8 | 66
362 | 9 | 69
362 | 10 | 71
362 | 11 | 73
362 | 12 | 75
362 | 13 | 80
362 | 14 | 81
362 | 15 | 70
362 | 16 | 69
362 | 17 | 67
362 | 18 | 66
362 | 19 | 66
362 | 20 | 65
362 | 21 | 64
362 | 22 | 64
362 | 23 | 63
362 | 24 | 61 | 67.625 | -2.625 | 2.625
363 | 1 | 60
363 | 2 | 58
363 | 3 | 57
363 | 4 | 56
363 | 5 | 55
363 | 6 | 55
363 | 7 | 53
363 | 8 | 51
363 | 9 | 51
363 | 10 | 51
363 | 11 | 52
363 | 12 | 52
363 | 13 | 52
363 | 14 | 51
363 | 15 | 52
363 | 16 | 52
363 | 17 | 52
363 | 18 | 52
363 | 19 | 53
363 | 20 | 53
363 | 21 | 54
363 | 22 | 53
363 | 23 | 53
363 | 24 | 53 | 53.375 | 11.625 | -11.625
364 | 1 | 52
364 | 2 | 50
364 | 3 | 50
364 | 4 | 49
364 | 5 | 49
364 | 6 | 49
364 | 7 | 50
364 | 8 | 49
364 | 9 | 50
364 | 10 | 50
364 | 11 | 51
364 | 12 | 53
364 | 13 | 53
364 | 14 | 53
364 | 15 | 54
364 | 16 | 55
364 | 17 | 54
364 | 18 | 53
364 | 19 | 54
364 | 20 | 54
364 | 21 | 55
364 | 22 | 55
364 | 23 | 55
364 | 24 | 56 | 52.2083 | 12.7917 | -12.7917
365 | 1 | 58
365 | 2 | 60
365 | 3 | 61
365 | 4 | 61
365 | 5 | 64
365 | 6 | 57
365 | 7 | 54
365 | 8 | 55
365 | 9 | 60
365 | 10 | 65
365 | 11 | 67
365 | 12 | 72
365 | 13 | 73
365 | 14 | 75
365 | 15 | 76
365 | 16 | 73
365 | 17 | 69
365 | 18 | 67
365 | 19 | 64
365 | 20 | 63
365 | 21 | 62
365 | 22 | 61
365 | 23 | 61
365 | 24 | 58 | 64 | 1 | -1