## 0 - Overview
Title: | intercomparison_of_hybrid_CSP_PV_systems_fixed_HCF_design_results
Description | This excel workbook contains the results of a verification study done between the 4 models. The first verification was taken by fixing the design that was found by the HOPP model at 30%, 50%, 70%, and 90% hybrid capacity factor (HCF). The remaining three models were run with fixed designs. A second verification was performed the same way with the results for the AESOPT model.
Sheet | Description
1.1 - HOPP 30% | This sheet contains the results of all models running a fixed design obtained from the optimization performed by HOPP for a hybrid capacity value of 30%.
1.2 - HOPP 50% | This sheet contains the results of all models running a fixed design obtained from the optimization performed by HOPP for a hybrid capacity value of 50%.
1.3 - HOPP 70% | This sheet contains the results of all models running a fixed design obtained from the optimization performed by HOPP for a hybrid capacity value of 70%.
1.4 - HOPP 90% | This sheet contains the results of all models running a fixed design obtained from the optimization performed by HOPP for a hybrid capacity value of 90%.
2.1 - AESOPT 30% | This sheet contains the results of all models running a fixed design obtained from the optimization performed by AESOPT for a hybrid capacity value of 30%.
1.2 - AESOPT 50% | This sheet contains the results of all models running a fixed design obtained from the optimization performed by AESOPT for a hybrid capacity value of 50%.
1.3 - AESOPT 70% | This sheet contains the results of all models running a fixed design obtained from the optimization performed by AESOPT for a hybrid capacity value of 70%.
1.4- AESOPT 90% | This sheet contains the results of all models running a fixed design obtained from the optimization performed by AESOPT for a hybrid capacity value of 90%.
2.1 - Paper Figures HOPP | This sheet contains all the paper figures associated with running a fixed design obtained from the optimization performed by HOPP.
2.2 - Paper Figures AESOPT | This sheet contains all the paper figures associated with running a fixed design obtained from the optimization performed by AESOPT.

## 1.1 - HOPP - 30%
Type | Symbol | Description | Unit | Partners
|  |  |  | MoSES | YACOP | AESOPT | HOPP
Key Performance Indicators (KPIs) | AEY | Annual Energy Yield | GWh | 124.6609 | 113.2941 | 121.8703 | 123.5104
|  | Annual HTF energy into from field (CSP-only) | GWht | 0 |  | 0 | 0
| HCF | Hybrid Capacity Factor | % | 35.88% | 32.59% | 35.08% | 35.55%
| NPV | Net Present Value | MEUR | 30.1389 | 21.4665 | 28.1959 | 29.2594
| PPA | Power Purchase Agreement | EUR/MWh | 0 |  | 0 | 0
|  | LCOE | EUR/MWh | 32.9511 | 36.2549 | 33.6231 | 33.2425
| CAPEX | Capital Expenditure | MEUR | 50.0583 | 50.0396 | 49.913 | 50.035
| OPEX | Operational Expenditure | kEUR/year | 769.86 | 770.8608 | 769.4996 | 769.4996
|  | Revenues | kEUR/year | 6117.3529 | 5538.8379 | 5977.738 | 6056.7909
| AF | Availability Factor | % |  |  | 0%
| EH_UF | Electric Heater Utilization Factor | % |  |  | 0%
| TES_PV_fraction | Fraction of TES charged by PV+EH | % |  |  | 0%
| c_block | Specifc cost of the power block | EUR/kW |  | 0 | 0
| eta_blk_des | Design Efficiency of the PB (NET) | % |  |  | 0%
| f_AEY_CSP | Share of AEY - CSP | % | 0% | 0% | 0%
| f_AEY_PV | Share of AEY - PV | % | 100% | 100% | 100% | 100%
| f_AEY_BESS | Share of AEY - BESS | % | 0% | 0% | 0%
|  | AEY - CSP | GWh | 0 | 0 | 0
|  | AEY - PV | GWh | 124.6609 | 113.2941 | 121.8703 | 123.5104
|  | AEY - BESS (Discharge) | GWh | 0 | 0 | 0
| EW_PV | Electricity Curtailed PV and Wasted | GWh | 35.6207 | 31.9613 | 28.4142 | 31.2962
| EEH_PV | Electricity from PV to EH | GWh | 0 |  | 0
| EBESS_PV | Electricity from PV to BESS | GWh | 0 | 0 | 0
| CF_tot | Total Capacity Factor | % | 20.19% | 18.31% | 19.74% | 19.29%
| CF_CSP | CSP production over CSP installed capacity | % | 0% | 0% | 0%
| CF_PV | PV production over PV installed capacity | % | 20.19% | 18% | 24.35% | 15.39%
| CF_BESS | BESS production over BESS installed capacity | % | 0% | 0% | 0%
Costs | CAPEX_CSP | Capital Expenditure - CSP | MEUR |  | 0 | 0
| CAPEX_PV | Capital Expenditure - PV | MEUR | 50.0583 | 50.0396 | 49.913 | 50.035
| CAPEX_BESS | Capital Expenditure - BESS | MEUR |  | 0 | 0
| C_tower | Tower Cost | MEUR |  |  | 0
| C_receiver | Receiver Cost | MEUR |  |  | 0
| C_field | Field Cost | MEUR |  |  | 0
| C_site_CSP | Site Improvement Cost - CSP | MEUR |  |  | 0
| C_storage | Storage Cost | MEUR |  |  | 0
| C_block | Block Cost | MEUR |  |  | 0
| C_bop | Bop Cost | MEUR |  |  | 0
| C_heater | Heater Cost | MEUR |  |  | 0
| C_land_CSP | Land Cost - CSP | MEUR |  |  | 0
| C_year_CSP | Annual fixed operating Cost - CSP | kEUR/year |  |  | 0
| C_OM_CSP | Annual variable operating Cost - CSP | kEUR/year |  |  | 0
| C_cap_CSP | Total capital cost - CSP | MEUR |  | 0 | 0
| C_modules_PV | Modules Cost - PV | MEUR | 21.5561 | 21.6016 | 21.546 | 21.546
| C_BoS_PV | Bos Cost - PV | MEUR | 16.1671 | 16.2012 | 16.1595 | 16.1595
| C_site_PV | Site Improvement Cost - PV | MEUR | 0 | 0 | 0 | 0
| C_inverter_PV | Inverter Cost - PV | MEUR | 2.961 | 2.9648 | 2.9596 | 2.9596
| C_land_PV | Land Cost - PV | MEUR | 3.9632 | 3.9722 | 3.9614 | 3.9614
| C_year_PV | Annual fixed operating Cost - PV | kEUR/year | 769.86 | 770.8608 | 769.4996 | 769.4996
| C_cap_PV | Total capital cost - PV | MEUR | 40.6841 | 40.7676 | 40.6651 | 40.6651
| C_BoS_BESS | Bos Cost - BESS | MEUR | 0 |  | 0
| C_PCS_BESS | Power Convertion System - BESS | MEUR | 0 |  | 0
| C_ES_BESS | Energy Storage Cost - BESS | MEUR | 0 |  | 0
| C_replacement_BESS | Replacement Cost - BESS | MEUR | 0 | 0 | 0
| C_year_BESS | Annual fixed operating Cost - BESS | kEUR/year | 0 |  | 0
| c_OM_BESS | Annual variable operating Cost - BESS | kEUR/year | 0 |  | 0
| C_Cap_BESS | Total capital cost - BESS | MEUR | 0 | 0 | 0
| C_year | Total Annual cost | MEUR/year |  | 4.1075 | 4.0977 | 4.1058
Design | Q_field_des | Design Solar Field Power | MW |  |  | 0
| A_SF | Area of the SF | m2 |  |  | 0
| A_land_CSP_tot | Total Land Area CSP | m2 |  |  | 0
| eff_SF_des | Design Solar Field Efficiency | % |  |  | 0
| n_heliostat | Number of Heliostat | -
| SM | Solar Multiple | - |  |  | 0
| H_tower | Tower height | m |  |  | 0
| Q_rec_des | Design Receiver Output | MW |  |  | 0
| H_rec | Height of the Receiver | m
| D_rec | Diameter of the Receiver | m
| rec_eff_design | Total Receiver Efficiency | % |  |  | 0
| rec_eff_th_design | Receiver Thermal Efficiency | %
| A_receiver | Area of the receiver | m2 |  |  | 0
| m_flow_rec | Design mass flow rate receiver | kg/s |  | 0
| T_hot_set_REC/EH | Design hot temperature REC/EH | C
| T_cold_set_REC/EH | T_cold_set_REC/EH | C
| Q_name_EH | Design thermal power EH | MW |  |  | 0
| EH_eff_design | Design EH efficiency | % |  |  | 0.95
| m_flow_EH_des | Design EH mass flow rate | kg/s |  | 0
| P_name_EH | Design electrical power EH | MW |  | 0 | 0
| EH_W_min | Mimum power to run EH | MW |  | 0
| t_storage | TES hours | h |  |  | 0
| H_storage | Height of the TES tank | m
| D_storage | Diameter of the TES tank | m
| A_surf_TES | Surface losses area TES | m2
| E_max | Maximum Energy that can be stored in the TES | MWh |  |  | 0
| Q_flow_des | Design thermal power to PB | MW |  |  | 0
| eta_blk_des | Design NET Efficiency of the PB | % |  |  | 0
| TIT | Turbine Inlet Temperature | C
| T_hot_MS | Molten Salt Hot Temperature - PB | C |  |  | 550
| T_return_MS | Molten Salt Cold Temperature - PB | C |  |  | 290
| T_amb_PB | Design ambient temperature - PB | C |  |  | 30
| P_gross | Design gross electrical power - PB | MW |  |  | 0
| P_net | Design net electrical power - PB | MW | 0 | 0 | 0
| PV_P_AC | Design AC Power - PV | MW | 70.467 | 70.5917 | 70.467 | 70.467
| PV_P_DC | Design DC Power - PV | MW | 91.65 | 91.8435 | 91.6071 | 91.6071
| PV_r_DCAC | DC-to-AC ratio | - | 1.3 | 1.3011 | 1.3 | 1.3
| A_PV_field | Area of the PV field | m2 | 509166.6667 | 510241.4 | 508928.3 | 508928.3333
| A_land_PV_tot | Total land occupied by the PV plant | m2 | 1909376.25 | 1913405.25 | 1908481 | 1908481.25
| PV_GCR | GCR | - | 0.4 | 0.4 | 0.4 | 0.4
| PV_tilt | Design tilt PV | deg | 37 | 37 | 37 | 37
| PV_azimuth | Design azimuth PV | deg | 0 | 0 | 0 | 0
| eta_inv | Inverter design efficiency | % | 0.95 | 0.95 | 95 | 0.95
| P_max | Maximum power injectable to the grid | MW | 50 | 50 | 50 | 50
| BESS_h | BESS hours of storage | h | 0 |  | 0
| P_BESS | Design power BESS | MW | 0 | 0 | 0 | 0
| E_BESS | Energy storage Capacity - BESS | MWh | 0 |  | 0 | 0
|  | Annual BESS cycles |  | 0 | 0 | 0
| N_cycle_max | Maximum cycle per BESS | - | 0 | 0 | 0
| N_replacement | Number of replacements BESS | - | 0 | 0 | 0
|  | EUR Conversion Factor |  |  |  |  | 0.84

## 1.2 - HOPP - 50%
Type | Symbol | Description | Unit | Partners
|  |  |  | MoSES | YACOP | AESOPT | HOPP
Key Performance Indicators (KPIs) | AEY | Annual Energy Yield | GWh | 172.4321 | 169.6 | 178.2734 | 183.9878
|  | Annual HTF energy into from field (CSP-only) | GWht | 0 | 0 | 0 | 0
| HCF | Hybrid Capacity Factor | % | 0.49636 | 0.49 | 0.51317 | 0.52962
| NPV | Net Present Value | MEUR | -54.8471 | -68.66 | -74.8027 | -57.7244
| PPA | Power Purchase Agreement | EUR/MWh | 0 | 0 | 0 | 0
|  | LCOE | EUR/MWh | 71.8498 | 76.72 | 78.2626 | 71.169
| CAPEX | Capital Expenditure | MEUR | 162.564 | 215.92 | 185.6906 | 217.069
| OPEX | Operational Expenditure | kEUR/year | 1549.5711 | 1557.46 | 1570.433 | 1571.9982
|  | Revenues | kEUR/year | 8732.0539 | 8432.9 | 8964.351 | 9245.2444
| AF | Availability Factor | % | 0 |  | 0 | 0
| EH_UF | Electric Heater Utilization Factor | % | 0 |  | 0 | 0
| TES_PV_fraction | Fraction of TES charged by PV+EH | % | 0 |  | 0 | 0
| c_block | Specifc cost of the power block | EUR/kW | 0 | 0 | 0 | 0
| eta_blk_des | Design Efficiency of the PB (NET) | % | 0 |  | 0 | 0
| f_AEY_CSP | Share of AEY - CSP | % | 0 | 0 | 0 | 0
| f_AEY_PV | Share of AEY - PV | % | 0.82928 | 0.77 | 0.79022 | 0.77022
| f_AEY_BESS | Share of AEY - BESS | % | 0.17072 | 0.23 | 0.20978 | 0.22978
|  | AEY - CSP | GWh | 0 | 0 | 0 | 0
|  | AEY - PV | GWh | 142.9952 | 129.83 | 140.8752 | 141.7105
|  | AEY - BESS (Discharge) | GWh | 29.4369 | 39.77 | 37.3982 | 42.2773
| EW_PV | Electricity Curtailed PV and Wasted | GWh | 100.8112 | 76.88 | 77.9548 | 87.7918
| EEH_PV | Electricity from PV to EH | GWh | 0 |  | 0 | 0
| EBESS_PV | Electricity from PV to BESS | GWh | 38.3109 | 46.71 | 45.8075 | 43.0958
| CF_tot | Total Capacity Factor | % | 0.13238 | 0.13 | 0.1369 | 0.16691
| CF_CSP | CSP production over CSP installed capacity | % | 0 | 0 | 0 | 0
| CF_PV | PV production over PV installed capacity | % | 0.13155 | 0.12 | 0.24346 | 0.10028
| CF_BESS | BESS production over BESS installed capacity | % | 0.1366 | 0.18 | 0.17376 | 0.19643
Costs | CAPEX_CSP | Capital Expenditure - CSP | MEUR | 0 | 0 | 0 | 0
| CAPEX_PV | Capital Expenditure - PV | MEUR | 88.1097 | 87.3 | 87.8922 | 88.107
| CAPEX_BESS | Capital Expenditure - BESS | MEUR | 74.4543 | 128.62 | 97.7984 | 128.962
| C_tower | Tower Cost | MEUR | 0 |  | 0 | 0
| C_receiver | Receiver Cost | MEUR | 0 |  | 0 | 0
| C_field | Field Cost | MEUR | 0 |  | 0 | 0
| C_site_CSP | Site Improvement Cost - CSP | MEUR | 0 |  | 0 | 0
| C_storage | Storage Cost | MEUR | 0 |  | 0 | 0
| C_block | Block Cost | MEUR | 0 |  | 0 | 0
| C_bop | Bop Cost | MEUR | 0 |  | 0 | 0
| C_heater | Heater Cost | MEUR | 0 |  | 0 | 0
| C_land_CSP | Land Cost - CSP | MEUR | 0 |  | 0 | 0
| C_year_CSP | Annual fixed operating Cost - CSP | kEUR/year | 0 |  | 0 | 0
| C_OM_CSP | Annual variable operating Cost - CSP | kEUR/year | 0 |  | 0 | 0
| C_cap_CSP | Total capital cost - CSP | MEUR | 0 | 0 | 0 | 0
| C_modules_PV | Modules Cost - PV | MEUR | 37.9418 | 37.69 | 37.9405 | 37.9405
| C_BoS_PV | Bos Cost - PV | MEUR | 28.4563 | 28.27 | 28.4554 | 28.4554
| C_site_PV | Site Improvement Cost - PV | MEUR | 0 | 0 | 0 | 0
| C_inverter_PV | Inverter Cost - PV | MEUR | 5.2118 | 5.17 | 5.2116 | 5.2116
| C_land_PV | Land Cost - PV | MEUR | 6.9758 | 6.93 | 6.9757 | 6.9757
| C_year_PV | Annual fixed operating Cost - PV | kEUR/year | 1355.0628 | 1344.91 | 1355.019 | 1355.0191
| C_cap_PV | Total capital cost - PV | MEUR | 71.6099 | 71.13 | 71.6076 | 71.6075
| C_BoS_BESS | Bos Cost - BESS | MEUR | 0 |  | 0 | 0
| C_PCS_BESS | Power Convertion System - BESS | MEUR | 4.6494 | 4.64 | 4.6435 | 4.6435
| C_ES_BESS | Energy Storage Cost - BESS | MEUR | 30.5324 | 27.3 | 27.3012 | 27.295
| C_replacement_BESS | Replacement Cost - BESS | MEUR | 30.5324 | 81.89 | 54.6025 | 81.8849
| C_year_BESS | Annual fixed operating Cost - BESS | kEUR/year | 142.5816 | 142.4 | 142.4019 | 142.402
| c_OM_BESS | Annual variable operating Cost - BESS | kEUR/year | 51.9267 | 70.15 | 73.0116 | 74.5771
| C_Cap_BESS | Total capital cost - BESS | MEUR | 65.7143 | 113.82 | 86.5472 | 113.8235
| C_year | Total Annual cost | MEUR/year |  | 13.01 | 13.9521 | 13.0942
Design | Q_field_des | Design Solar Field Power | MW | 0 |  | 0 | 0
| A_SF | Area of the SF | m2 | 0 |  | 0 | 0
| A_land_CSP_tot | Total Land Area CSP | m2 | 0 |  | 0 | 0
| eff_SF_des | Design Solar Field Efficiency | % | 0 |  | 0 | 0
| n_heliostat | Number of Heliostat | - | 0 |  |  | 0
| SM | Solar Multiple | - | 0 |  | 0 | 0
| H_tower | Tower height | m | 0 |  | 0 | 0
| Q_rec_des | Design Receiver Output | MW | 0 |  | 0 | 0
| H_rec | Height of the Receiver | m | 0 |  |  | 0
| D_rec | Diameter of the Receiver | m | 0 |  |  | 0
| rec_eff_design | Total Receiver Efficiency | % | 0 |  | 0 | 0
| rec_eff_th_design | Receiver Thermal Efficiency | % | 0 |  |  | 0
| A_receiver | Area of the receiver | m2 | 0 |  | 0 | 0
| m_flow_rec | Design mass flow rate receiver | kg/s | 0 | 0 |  | 0
| T_hot_set_REC/EH | Design hot temperature REC/EH | C | 0 |  |  | 0
| T_cold_set_REC/EH | T_cold_set_REC/EH | C | 0 |  |  | 0
| Q_name_EH | Design thermal power EH | MW | 0 |  | 0 | 0
| EH_eff_design | Design EH efficiency | % | 0.95 |  | 0.95 | 0.95
| m_flow_EH_des | Design EH mass flow rate | kg/s | 0 | 0 |  | 0
| P_name_EH | Design electrical power EH | MW | 0 | 0 | 0 | 0
| EH_W_min | Mimum power to run EH | MW | 0 | 0 |  | 0
| t_storage | TES hours | h | 0 |  | 0 | 0
| H_storage | Height of the TES tank | m | 0 |  |  | 0
| D_storage | Diameter of the TES tank | m | 0 |  |  | 0
| A_surf_TES | Surface losses area TES | m2 | 0 |  |  | 0
| E_max | Maximum Energy that can be stored in the TES | MWh | 0 |  | 0 | 0
| Q_flow_des | Design thermal power to PB | MW | 0 |  | 0 | 0
| eta_blk_des | Design NET Efficiency of the PB | % | 0 |  | 0 | 0
| TIT | Turbine Inlet Temperature | C | 0 |  |  | 0
| T_hot_MS | Molten Salt Hot Temperature - PB | C | 550 |  | 550 | 550
| T_return_MS | Molten Salt Cold Temperature - PB | C | 290 |  | 290 | 290
| T_amb_PB | Design ambient temperature - PB | C | 30 |  | 30 | 30
| P_gross | Design gross electrical power - PB | MW | 0 |  | 0 | 0
| P_net | Design net electrical power - PB | MW | 0 | 0 | 0 | 0
| PV_P_AC | Design AC Power - PV | MW | 124.09 | 123.16 | 124.086 | 124.086
| PV_P_DC | Design DC Power - PV | MW | 161.317 | 160.24 | 161.3118 | 161.3118
| PV_r_DCAC | DC-to-AC ratio | - | 1.3 | 1.3 | 1.3 | 1.3
| A_PV_field | Area of the PV field | m2 | 896205.5556 | 890208.4 | 896176.7 | 896176.6667
| A_land_PV_tot | Total land occupied by the PV plant | m2 | 3360772.5 | 3338281.5 | 3360663 | 3360662.5
| PV_GCR | GCR | - | 0.4 | 0.4 | 0.4 | 0.4
| PV_tilt | Design tilt PV | deg | 37 | 37 | 37 | 37
| PV_azimuth | Design azimuth PV | deg | 0 | 0 | 0 | 0
| eta_inv | Inverter design efficiency | % | 0.95 | 0.95 | 95 | 0.95
| P_max | Maximum power injectable to the grid | MW | 50 | 50 | 50 | 50
| BESS_h | BESS hours of storage | h | 6 |  | 6.3281 | 5.0624
| P_BESS | Design power BESS | MW | 24.6 | 24.57 | 24.569 | 24.569
| E_BESS | Energy storage Capacity - BESS | MWh | 155.5 | 155.47 | 155.474 | 155.4738
|  | Annual BESS cycles |  | 199.2535 | 255.17 | 240.5429
| N_cycle_max | Maximum cycle per BESS | - | - | 2000 | 2000 | 2000
| N_replacement | Number of replacements BESS | - | 1 | 3 | 2 | 3
|  | EUR Conversion Factor |  |  |  | 227 | 0.84
6.3281

## 1.3 - HOPP - 70%
Type | Symbol | Description | Unit | Partners
|  |  |  | MoSES | YACOP | AESOPT | HOPP
Key Performance Indicators (KPIs) | AEY | Annual Energy Yield | GWh | 265.7898 | 249.74 | 266.5311 | 256.5451
|  | Annual HTF energy into from field (CSP-only) | GWht |  |  | 346.8373 | 451.3963
| HCF | Hybrid Capacity Factor | % | 76.51% | 72% | 76.72% | 73.85%
| NPV | Net Present Value | MEUR | -138.5871 | -149.19 | -130.866 | -145.2668
| PPA | Power Purchase Agreement | EUR/MWh | 0 |  | 0 | 0
|  | LCOE | EUR/MWh | 83.9345 | 88.55 | 81.9462 | 86.926
| CAPEX | Capital Expenditure | MEUR | 300.9772 | 297.08 | 294.0631 | 299.7847
| OPEX | Operational Expenditure | kEUR/year | 2240.0064 | 2305.87 | 2233.311 | 2311.131
|  | Revenues | kEUR/year | 13068.0579 | 12167.07 | 13115.17 | 12614.2668
| AF | Availability Factor | % | 0 |  | 0 | 0
| EH_UF | Electric Heater Utilization Factor | % | 0 |  | 0 | 0
| TES_PV_fraction | Fraction of TES charged by PV+EH | % | 0 |  | 0 | 0
| c_block | Specifc cost of the power block | EUR/kW | 2221.3205 | 2153.33 | 2104.078 | 2153
| eta_blk_des | Design Efficiency of the PB (NET) | % | 38.37% | 38% | 38.91% | 38.37%
| f_AEY_CSP | Share of AEY - CSP | % | 51.92% | 56.2% | 51.65% | 62.99%
| f_AEY_PV | Share of AEY - PV | % | 48.08% | 43.8% | 48.35% | 37.01%
| f_AEY_BESS | Share of AEY - BESS | % | 0% | 0% | 0% | 0%
|  | AEY - CSP | GWh | 137.9926 | 140.43 | 137.6597 | 161.59
|  | AEY - PV | GWh | 127.7972 | 109.31 | 128.8714 | 94.952
|  | AEY - BESS (Discharge) | GWh | 0 | 0 | 0 | 0
| EW_PV | Electricity Curtailed PV and Wasted | GWh | 65.2225 | 66.85 | 52.0877 | 91.45
| EEH_PV | Electricity from PV to EH | GWh | 0 |  | 0 | 0
| EBESS_PV | Electricity from PV to BESS | GWh | 0 | 0 | 0 | 0
| CF_tot | Total Capacity Factor | % | 0.27127 | 0.25 | 0.272 | 0.28647
| CF_CSP | CSP production over CSP installed capacity | % | 0.58343 | 0.59 | 0.58181 | 0.65017
| CF_PV | PV production over PV installed capacity | % | 0.17194 | 0.15 | 0.24346 | 0.09826
| CF_BESS | BESS production over BESS installed capacity | % | 0 | 0 | 0
Costs | CAPEX_CSP | Capital Expenditure - CSP | MEUR | 240.6942 | 236.3891 | 233.9624 | 239.537
| CAPEX_PV | Capital Expenditure - PV | MEUR | 60.283 | 60.6864 | 60.1007 | 60.247
| CAPEX_BESS | Capital Expenditure - BESS | MEUR | 0 | 0 | 0
| C_tower | Tower Cost | MEUR | 15.1642 | 14.9109 | 14.8848 | 14.85
| C_receiver | Receiver Cost | MEUR | 42.7497 | 41.7874 | 41.5555 | 42.382
| C_field | Field Cost | MEUR | 49.2679 | 47.9168 | 47.5936 | 48.478
| C_site_CSP | Site Improvement Cost - CSP | MEUR | 4.1385 | 3.9931 | 3.9661 | 4.0398
| C_storage | Storage Cost | MEUR | 23.1082 | 22.7988 | 22.7989 | 24.217
| C_block | Block Cost | MEUR | 59.9757 | 61.0712 | 59.6966 | 61.085
| C_bop | Bop Cost | MEUR | 0 |  | 0
| C_heater | Heater Cost | MEUR | 0 |  | 0
| C_land_CSP | Land Cost - CSP | MEUR | 5.6402 | 5.4154 | 5.3678 | 5.4722
| C_year_CSP | Annual fixed operating Cost - CSP | kEUR/year | 907.2 | 907.2 | 907.536 | 907.536
| C_OM_CSP | Annual variable operating Cost - CSP | kEUR/year | 405.6984 | 463.7917 | 399.2131 | 477.03
| C_cap_CSP | Total capital cost - CSP | MEUR | 194.4041 | 192.4781 | 190.4955 | 195.054
| C_modules_PV | Modules Cost - PV | MEUR | 25.959 | 26.1977 | 25.9437 | 25.943
| C_BoS_PV | Bos Cost - PV | MEUR | 19.4693 | 19.6482 | 19.4578 | 19.457
| C_site_PV | Site Improvement Cost - PV | MEUR | 0 | 0 | 0
| C_inverter_PV | Inverter Cost - PV | MEUR | 3.5658 | 3.5957 | 3.5637 | 3.5637
| C_land_PV | Land Cost - PV | MEUR | 4.7727 | 4.8174 | 4.77 | 4.7699
| C_year_PV | Annual fixed operating Cost - PV | kEUR/year | 927.108 | 934.8738 | 926.562 | 926.562
| C_cap_PV | Total capital cost - PV | MEUR | 48.9941 | 49.4416 | 48.9652 | 48.965
| C_BoS_BESS | Bos Cost - BESS | MEUR | 0 |  | 0
| C_PCS_BESS | Power Convertion System - BESS | MEUR | 0 |  | 0
| C_ES_BESS | Energy Storage Cost - BESS | MEUR | 0 |  | 0
| C_replacement_BESS | Replacement Cost - BESS | MEUR | 0 | 0 | 0
| C_year_BESS | Annual fixed operating Cost - BESS | kEUR/year | 0 |  | 0
| c_OM_BESS | Annual variable operating Cost - BESS | kEUR/year | 0 |  | 0
| C_Cap_BESS | Total capital cost - BESS | MEUR | 0 | 0 | 0
| C_year | Total Annual cost | MEUR/year |  | 22.1146 | 21.8412 | 22.3005
Design | Q_field_des | Design Solar Field Power | MW | 286.4059 | 284.4641 | 282.5534 | 286.1726
| A_SF | Area of the SF | m2 | 492678.6085 | 475365.1137 | 472159.2 | 480938.184
| A_land_CSP_tot | Total Land Area CSP | m2 | 2714730.5012 | 2608553.589 | 2586049 | 2636360.747
| eff_SF_des | Design Solar Field Efficiency | % | 0.66256 | 0.6649 | 0.6653
| n_heliostat | Number of Heliostat | - | 3311 | 3194 |  | 3232
| SM | Solar Multiple | - | 3.5514 |  | 3.5514 | 3.5514
| H_tower | Tower height | m | 158.8212 | 157.3302 | 157.1523 | 156.9703
| Q_rec_des | Design Receiver Output | MW | 249.8918 | 248.2112 | 246.547 | 249.9811
| H_rec | Height of the Receiver | m | - |  | - | 13.4319
| D_rec | Diameter of the Receiver | m | - |  | - | 13.4319
| rec_eff_design | Total Receiver Efficiency | % | 0.87251 | 0.87256 | 0.87256 | 0.87353
| rec_eff_th_design | Receiver Thermal Efficiency | % | - |  | - | -
| A_receiver | Area of the receiver | m2 | 573.8132 | 555.4508 | 551.5937 | 566.506
| m_flow_rec | Design mass flow rate receiver | kg/s | 634.3037 | 630.0379 |  | 638.867
| T_hot_set_REC/EH | Design hot temperature REC/EH | C | 550 | 550 |  | 550
| T_cold_set_REC/EH | T_cold_set_REC/EH | C | 290 | 290 |  | 290
| Q_name_EH | Design thermal power EH | MW | 0 |  | 0
| EH_eff_design | Design EH efficiency | % | 0.95 |  | 0.95
| m_flow_EH_des | Design EH mass flow rate | kg/s | 0 | 0
| P_name_EH | Design electrical power EH | MW | 0 | 0 | 0
| EH_W_min | Mimum power to run EH | MW | 0 | 0
| t_storage | TES hours | h | 18.6 |  | 18.617 | 18.617
| H_storage | Height of the TES tank | m
| D_storage | Diameter of the TES tank | m
| A_surf_TES | Surface losses area TES | m2
| E_max | Maximum Energy that can be stored in the TES | MWh | 1308.7891 | 1292.45 | 1292.454 | 1310.45
| Q_flow_des | Design thermal power to PB | MW | 70.365 | 70.1516 | 69.4232 | 70.3901
| eta_blk_des | Design NET Efficiency of the PB | % | 0.38371 | 0.38488 | 0.38906 | 0.3837
| TIT | Turbine Inlet Temperature | C | 540
| T_hot_MS | Molten Salt Hot Temperature - PB | C | 550 | 550 | 550 | 550
| T_return_MS | Molten Salt Cold Temperature - PB | C | 290 | 290.1764 | 290 | 290
| T_amb_PB | Design ambient temperature - PB | C | 30 | 30 | 30 | 30
| P_gross | Design gross electrical power - PB | MW | 28.3613 | 28.3613 | 28.3718 | 28.37
| P_net | Design net electrical power - PB | MW | 27 | 27 | 27.01 | 27.0098
| PV_P_AC | Design AC Power - PV | MW | 84.85 | 85.6111 | 84.85 | 84.8504
| PV_P_DC | Design DC Power - PV | MW | 110.305 | 111.3846 | 110.305 | 110.305
| PV_r_DCAC | DC-to-AC ratio | - | 1.3 | 1.3011 | 1.3 | 1.3
| A_PV_field | Area of the PV field | m2 | 613166.6667 | 618803.4 | 612805.6 | 612805.555
| A_land_PV_tot | Total land occupied by the PV plant | m2 | 2299373.25 | 2320512.75 | 2298021 | 2298020.83
| PV_GCR | GCR | - | 0.4 | 0.4 | 0.4 | 0.4
| PV_tilt | Design tilt PV | deg | 37 | 37 | 37 | 37
| PV_azimuth | Design azimuth PV | deg | 0 | 0 | 0 | 0
| eta_inv | Inverter design efficiency | % | 95 | 0.95 | 95 | 95
| P_max | Maximum power injectable to the grid | MW | 50 | 50 | 50 | 50
| BESS_h | BESS hours of storage | h | 0 |  | 0 | 0
| P_BESS | Design power BESS | MW | 0 | 0 | 0 | 0
| E_BESS | Energy storage Capacity - BESS | MWh | 0 |  | 0 | 0
|  | Annual BESS cycles |  | 0 | 0 | 0 | 0
| N_cycle_max | Maximum cycle per BESS | - | 0 | 0 | 0 | 0
| N_replacement | Number of replacements BESS | - | 0 | 0 | 0 | 0
|  | EUR Conversion Factor |  |  |  |  | 0.84

## 1.4 - HOPP - 90%
Type | Symbol | Description | Unit | Partners
|  |  |  | MoSES | YACOP | AESOPT | HOPP
Key Performance Indicators (KPIs) | AEY | Annual Energy Yield | GWh | 330.6163 | 319.28 | 326.848 | 315.4624
|  | Annual HTF energy into from field (CSP-only) | GWht |  |  | 529.1759 | 836.5789
| HCF | Hybrid Capacity Factor | % | 95.17% | 91.84% | 94.09% | 90.81%
| NPV | Net Present Value | MEUR | -319.7322 | -323.6614 | -313.153 | -326.73
| PPA | Power Purchase Agreement | EUR/MWh | 0 |  | 0
|  | LCOE | EUR/MWh | 113.5918 | 116.5634 | 113.171 | 118.26
| CAPEX | Capital Expenditure | MEUR | 513.2526 | 505.9126 | 505.5754 | 509.0418
| OPEX | Operational Expenditure | kEUR/year | 3332.0199 | 3482.495 | 3278.316 | 3364.2531
|  | Revenues | kEUR/year | 16078.2729 | 15634.8682 | 16108.91 | 15520.627
| AF | Availability Factor | % |  |  | 69.61%
| EH_UF | Electric Heater Utilization Factor | % | 0% |  | 0%
| TES_PV_fraction | Fraction of TES charged by PV+EH | % | 0% |  | 0%
| c_block | Specifc cost of the power block | EUR/kW | 1707.1104 | 1654.8999 | 1635.472 | 1654.88
| eta_blk_des | Design Efficiency of the PB (NET) | % | 39.34% | 39.24% | 39.44% | 39.34%
| f_AEY_CSP | Share of AEY - CSP | % | 66.66% | 71.34% | 62.71% | 88.31%
| f_AEY_PV | Share of AEY - PV | % | 33.34% | 28.66% | 37.29% | 11.69%
| f_AEY_BESS | Share of AEY - BESS | % | 0% | 0% | 0%
|  | AEY - CSP | GWh | 220.3887 | 227.7638 | 204.9559 | 278.588
|  | AEY - PV | GWh | 110.2276 | 91.5161 | 121.8921 | 36.8741
|  | AEY - BESS (Discharge) | GWh | 0 | 0 | 0
| EW_PV | Electricity Curtailed PV and Wasted | GWh | 62.301 | 66.1015 | 39.9517 | 129.839
| EEH_PV | Electricity from PV to EH | GWh | 0 |  | 0
| EBESS_PV | Electricity from PV to BESS | GWh | 0 | 0 | 0
| CF_tot | Total Capacity Factor | % | 28.78% | 27.63% | 28.46% | 33.29%
| CF_CSP | CSP production over CSP installed capacity | % | 45.56% | 47.06% | 42.37% | 54.83%
| CF_PV | PV production over PV installed capacity | % | 16.58% | 13.63% | 24.35% | 4.267%
| CF_BESS | BESS production over BESS installed capacity | % | 0% | 0% | 0%
Costs | CAPEX_CSP | Capital Expenditure - CSP | MEUR | 459.3693 | 451.6143 | 451.8234 | 455.1583
| CAPEX_PV | Capital Expenditure - PV | MEUR | 53.8833 | 54.2983 | 53.752 | 53.883
| CAPEX_BESS | Capital Expenditure - BESS | MEUR | 0 | 0 | 0
| C_tower | Tower Cost | MEUR | 20.1829 | 19.858 | 19.9098 | 19.8555
| C_receiver | Receiver Cost | MEUR | 77.1744 | 75.5507 | 76.3579 | 76.001
| C_field | Field Cost | MEUR | 116.0035 | 113.3599 | 114.0545 | 113.728
| C_site_CSP | Site Improvement Cost - CSP | MEUR | 9.7443 | 9.4467 | 9.5045 | 9.4773
| C_storage | Storage Cost | MEUR | 49.6169 | 49.5144 | 49.5144 | 51.872
| C_block | Block Cost | MEUR | 94.2666 | 95.9842 | 94.8574 | 95.983
| C_bop | Bop Cost | MEUR | 0 |  | 0
| C_heater | Heater Cost | MEUR | 0 |  | 0
| C_land_CSP | Land Cost - CSP | MEUR | 15.6434 | 15.1576 | 14.7852 | 14.8562
| C_year_CSP | Annual fixed operating Cost - CSP | kEUR/year | 1855.392 | 1855.2576 | 1855.258 | 1680
| C_OM_CSP | Annual variable operating Cost - CSP | kEUR/year | 647.9428 | 790.7714 | 594.3721 | 855.5671
| C_cap_CSP | Total capital cost - CSP | MEUR | 366.9886 | 363.7138 | 364.1984 | 366.918
| C_modules_PV | Modules Cost - PV | MEUR | 23.2032 | 23.44 | 23.2032 | 23.203
| C_BoS_PV | Bos Cost - PV | MEUR | 17.4024 | 17.58 | 17.4024 | 17.4024
| C_site_PV | Site Improvement Cost - PV | MEUR | 0 | 0 | 0
| C_inverter_PV | Inverter Cost - PV | MEUR | 3.1873 | 3.2172 | 3.1873 | 3.1872
| C_land_PV | Land Cost - PV | MEUR | 4.266 | 4.3103 | 4.2661 | 4.2661
| C_year_PV | Annual fixed operating Cost - PV | kEUR/year | 828.6851 | 836.466 | 828.686 | 828.686
| C_cap_PV | Total capital cost - PV | MEUR | 43.7928 | 44.2372 | 43.7929 | 43.7928
| C_BoS_BESS | Bos Cost - BESS | MEUR | 0 |  | 0
| C_PCS_BESS | Power Convertion System - BESS | MEUR | 0 |  | 0
| C_ES_BESS | Energy Storage Cost - BESS | MEUR |  |  | 0
| C_replacement_BESS | Replacement Cost - BESS | MEUR |  | 0 | 0
| C_year_BESS | Annual fixed operating Cost - BESS | kEUR/year |  |  | 0
| c_OM_BESS | Annual variable operating Cost - BESS | kEUR/year |  |  | 0
| C_Cap_BESS | Total capital cost - BESS | MEUR |  | 0 | 0
| C_year | Total Annual cost | MEUR/year |  | 37.2164 | 36.9897 | 37.3067
Design | Q_field_des | Design Solar Field Power | MW | 619.837 | 616.646 | 619.0498 | 610.1418
| A_SF | Area of the SF | m2 | 1160035.4311 | 1124602.4 | 1131493 | 1128254.677
| A_land_CSP_tot | Total Land Area CSP | m2 | 7531751.3849 | 7301366.571 | 7123062 | 7157279.9894
| eff_SF_des | Design Solar Field Efficiency | % | 0.60709 | 0.60925 | 0.60834
| n_heliostat | Number of Heliostat | - | 7794 | 7556 |  | 7581
| SM | Solar Multiple | - | 3.83 |  | 3.8316 | 3.8316
| H_tower | Tower height | m | 184.1217 | 182.6855 | 182.8666 | 182.6746
| Q_rec_des | Design Receiver Output | MW | 537.5664 | 534.9377 | 536.458 | 537.7535
| H_rec | Height of the Receiver | m |  |  |  | 20.3847
| D_rec | Diameter of the Receiver | m
| rec_eff_design | Total Receiver Efficiency | % | 0.86827 | 0.8675 | 0.86662 | 88.1358
| rec_eff_th_design | Receiver Thermal Efficiency | %
| A_receiver | Area of the receiver | m2 | 1334.3108 | 1294.3886 | 1315.283 | 1304.782
| m_flow_rec | Design mass flow rate receiver | kg/s | 1364.512 | 1357.8395 |  | 1374.3159
| T_hot_set_REC/EH | Design hot temperature REC/EH | C | 550 | 550 |  | 550
| T_cold_set_REC/EH | T_cold_set_REC/EH | C | 290 | 290 |  | 290
| Q_name_EH | Design thermal power EH | MW | 0 |  | 0
| EH_eff_design | Design EH efficiency | % | 0.95 |  | 0.95
| m_flow_EH_des | Design EH mass flow rate | kg/s | 0 | 0
| P_name_EH | Design electrical power EH | MW | 0 | 0 | 0
| EH_W_min | Mimum power to run EH | MW | 0 | 0
| t_storage | TES hours | h | 20.04 |  | 20.0483 | 20
| H_storage | Height of the TES tank | m |  |  |  | 12
| D_storage | Diameter of the TES tank | m
| A_surf_TES | Surface losses area TES | m2
| E_max | Maximum Energy that can be stored in the TES | MWh | 2812.7497 | 2806.94 | 2806.937 | 2806.9374
| Q_flow_des | Design thermal power to PB | MW | 140.3568 | 140.729 | 140.0088 | 140.3469
| eta_blk_des | Design NET Efficiency of the PB | % | 0.39231 | 0.39236 | 0.39437 | 0.3934
| TIT | Turbine Inlet Temperature | C | 540
| T_hot_MS | Molten Salt Hot Temperature - PB | C | 550 | 550 | 550 | 550
| T_return_MS | Molten Salt Cold Temperature - PB | C | 290 | 290.1764 | 290 | 290
| T_amb_PB | Design ambient temperature - PB | C | 30 | 30 | 30 | 30
| P_gross | Design gross electrical power - PB | MW | 58 | 58 | 58 | 58
| P_net | Design net electrical power - PB | MW | 55.22 | 55.216 | 55.216 | 55.216
| PV_P_AC | Design AC Power - PV | MW | 75.9 | 76.5995 | 75.887 | 75.8869
| PV_P_DC | Design DC Power - PV | MW | 98.67 | 99.6599 | 98.6531 | 98.6531
| PV_r_DCAC | DC-to-AC ratio | - | 1.3 | 1.3011 | 1.3 | 1.3
| A_PV_field | Area of the PV field | m2 | 548166.6667 | 553666.2 | 548072.8 | 548072.77
| A_land_PV_tot | Total land occupied by the PV plant | m2 | 2055618.75 | 2076248.25 | 2055273 | 2055272.916
| PV_GCR | GCR | - | 0.4 | 0.4 | 0.4 | 0.4
| PV_tilt | Design tilt PV | deg | 37 | 37 | 37 | 37
| PV_azimuth | Design azimuth PV | deg | 0 | 0 | 0 | 0
| eta_inv | Inverter design efficiency | % | 0.95 | 0.95 | 95 | 95
| P_max | Maximum power injectable to the grid | MW | 50 | 50 | 50 | 50
| BESS_h | BESS hours of storage | h |  |  | 0
| P_BESS | Design power BESS | MW | 0 | 0 | 0 | 0
| E_BESS | Energy storage Capacity - BESS | MWh |  |  | 0 | 0
|  | Annual BESS cycles |  | 0 | 0 | 0
| N_cycle_max | Maximum cycle per BESS | - | 0 | 0 | 0
| N_replacement | Number of replacements BESS | - | 0 | 0 | 0
|  | EUR Conversion Factor |  |  |  |  | 0.84

## 2.1 - AESOPT - 30%
Type | Symbol | Description | Unit | Partners
|  |  |  | MoSES | YACOP | AESOPT | HOPP
Key Performance Indicators (KPIs) | AEY | Annual Energy Yield | GWh | 110.8351 | 101.337 | 106.5002 | 108.6383
|  | Annual HTF energy into from field (CSP-only) | GWht |  |  | 0
| HCF | Hybrid Capacity Factor | % | 31.9% | 29.15% | 30.66% | 31.27%
| NPV | Net Present Value | MEUR | 34.7936 | 26.8051 | 31.6456 | 33.1531
| PPA | Power Purchase Agreement | EUR/MWh |  |  | 0
|  | LCOE | EUR/MWh | 27.9144 | 31.0464 | 28.9737 | 28.4599
| CAPEX | Capital Expenditure | MEUR | 37.7035 | 38.3282 | 37.5866 | 37.6784
| OPEX | Operational Expenditure | kEUR/year | 579.852 | 590.4466 | 579.4657 | 579.4657
|  | Revenues | kEUR/year | 5413.9045 | 4933.4882 | 5195.8141 | 5302.4619
| AF | Availability Factor | % | 0% |  | 0%
| EH_UF | Electric Heater Utilization Factor | % | 0% |  | 0% | 0%
| TES_PV_fraction | Fraction of TES charged by PV+EH | % | 0% |  | 0% | 0%
| c_block | Specifc cost of the power block | EUR/kW | 0 | 0 | 0
| eta_blk_des | Design Efficiency of the PB (NET) | % | 0% |  | 0%
| f_AEY_CSP | Share of AEY - CSP | % | 0% | 0% | 0%
| f_AEY_PV | Share of AEY - PV | % | 100% | 100% | 100% | 100%
| f_AEY_BESS | Share of AEY - BESS | % | 0% | 0% | 0%
|  | AEY - CSP | GWh | 0 | 0 | 0
|  | AEY - PV | GWh | 110.8351 | 101.337 | 106.5002 | 108.6383
|  | AEY - BESS (Discharge) | GWh | 0 | 0 | 0
| EW_PV | Electricity Curtailed PV and Wasted | GWh | 9.8879 | 9.9225 | 6.6704 | 7.9381
| EEH_PV | Electricity from PV to EH | GWh | 0 |  | 0
| EBESS_PV | Electricity from PV to BESS | GWh | 0 | 0 | 0
| CF_tot | Total Capacity Factor | % | 23.84% | 21.38% | 22.91% | 19.29%
| CF_CSP | CSP production over CSP installed capacity | % | 0% | 0% | 0%
| CF_PV | PV production over PV installed capacity | % | 25.34% | 21.38% | 24.35% | 17.98%
| CF_BESS | BESS production over BESS installed capacity | % | 0% | 0% | 0%
Costs | CAPEX_CSP | Capital Expenditure - CSP | MEUR | 0 | 0 | 0
| CAPEX_PV | Capital Expenditure - PV | MEUR | 37.7035 | 38.3282 | 37.5866 | 37.6784
| CAPEX_BESS | Capital Expenditure - BESS | MEUR | 0 | 0 | 0
| C_tower | Tower Cost | MEUR |  |  | 0
| C_receiver | Receiver Cost | MEUR |  |  | 0
| C_field | Field Cost | MEUR |  |  | 0
| C_site_CSP | Site Improvement Cost - CSP | MEUR |  |  | 0
| C_storage | Storage Cost | MEUR |  |  | 0
| C_block | Block Cost | MEUR |  |  | 0
| C_bop | Bop Cost | MEUR |  |  | 0
| C_heater | Heater Cost | MEUR |  |  | 0
| C_land_CSP | Land Cost - CSP | MEUR |  |  | 0
| C_year_CSP | Annual fixed operating Cost - CSP | kEUR/year |  |  | 0
| C_OM_CSP | Annual variable operating Cost - CSP | kEUR/year |  |  | 0
| C_cap_CSP | Total capital cost - CSP | MEUR |  | 0 | 0
| C_modules_PV | Modules Cost - PV | MEUR | 16.2359 | 16.5459 | 16.225 | 16.225
| C_BoS_PV | Bos Cost - PV | MEUR | 12.1769 | 12.4094 | 12.1688 | 12.1688
| C_site_PV | Site Improvement Cost - PV | MEUR | 0 | 0 | 0 | 0
| C_inverter_PV | Inverter Cost - PV | MEUR | 2.2302 | 2.2709 | 2.2287 | 2.2287
| C_land_PV | Land Cost - PV | MEUR | 2.985 | 3.0426 | 2.9831 | 2.9831
| C_year_PV | Annual fixed operating Cost - PV | kEUR/year | 579.852 | 590.4466 | 579.4657 | 579.4657
| C_cap_PV | Total capital cost - PV | MEUR | 30.6429 | 31.2263 | 30.6225 | 30.6225
| C_BoS_BESS | Bos Cost - BESS | MEUR |  |  | 0
| C_PCS_BESS | Power Convertion System - BESS | MEUR |  |  | 0
| C_ES_BESS | Energy Storage Cost - BESS | MEUR |  |  | 0
| C_replacement_BESS | Replacement Cost - BESS | MEUR |  | 0 | 0
| C_year_BESS | Annual fixed operating Cost - BESS | kEUR/year |  |  | 0
| c_OM_BESS | Annual variable operating Cost - BESS | kEUR/year |  |  | 0
| C_Cap_BESS | Total capital cost - BESS | MEUR |  | 0 | 0
| C_year | Total Annual cost | MEUR/year |  | 3.1461 | 3.0857 | 3.0918
Design | Q_field_des | Design Solar Field Power | MW |  |  | 0
| A_SF | Area of the SF | m2 |  |  | 0
| A_land_CSP_tot | Total Land Area CSP | m2 |  |  | 0
| eff_SF_des | Design Solar Field Efficiency | % |  |  | 0
| n_heliostat | Number of Heliostat | -
| SM | Solar Multiple | - |  |  | 0
| H_tower | Tower height | m |  |  | 0
| Q_rec_des | Design Receiver Output | MW |  |  | 0
| H_rec | Height of the Receiver | m
| D_rec | Diameter of the Receiver | m
| rec_eff_design | Total Receiver Efficiency | % |  |  | 0
| rec_eff_th_design | Receiver Thermal Efficiency | %
| A_receiver | Area of the receiver | m2 |  |  | 0
| m_flow_rec | Design mass flow rate receiver | kg/s |  | 0
| T_hot_set_REC/EH | Design hot temperature REC/EH | C
| T_cold_set_REC/EH | T_cold_set_REC/EH | C
| Q_name_EH | Design thermal power EH | MW |  |  | 0
| EH_eff_design | Design EH efficiency | % |  |  | 0.95
| m_flow_EH_des | Design EH mass flow rate | kg/s |  | 0
| P_name_EH | Design electrical power EH | MW |  | 0 | 0
| EH_W_min | Mimum power to run EH | MW |  | 0
| t_storage | TES hours | h |  |  | 0
| H_storage | Height of the TES tank | m
| D_storage | Diameter of the TES tank | m
| A_surf_TES | Surface losses area TES | m2
| E_max | Maximum Energy that can be stored in the TES | MWh |  |  | 0
| Q_flow_des | Design thermal power to PB | MW |  |  | 0
| eta_blk_des | Design NET Efficiency of the PB | % |  |  | 0
| TIT | Turbine Inlet Temperature | C
| T_hot_MS | Molten Salt Hot Temperature - PB | C |  |  | 550
| T_return_MS | Molten Salt Cold Temperature - PB | C |  |  | 290
| T_amb_PB | Design ambient temperature - PB | C |  |  | 30
| P_gross | Design gross electrical power - PB | MW |  |  | 0
| P_net | Design net electrical power - PB | MW |  | 0 | 0
| PV_P_AC | Design AC Power - PV | MW | 53.1 | 54.0702 | 53.0646 | 53.0646
| PV_P_DC | Design DC Power - PV | MW | 69.03 | 70.3482 | 68.984 | 68.984
| PV_r_DCAC | DC-to-AC ratio | - | 1.3 | 1.3011 | 1.3 | 1.3
| A_PV_field | Area of the PV field | m2 | 383500 | 390823.2 | 383244.5031 | 383244.5
| A_land_PV_tot | Total land occupied by the PV plant | m2 | 1438123.5 | 1465587 | 1437166.8865 | 1437166.875
| PV_GCR | GCR | - | 0.4 | 0.4 | 0.4 | 0.4
| PV_tilt | Design tilt PV | deg | 37 | 37 | 37 | 37
| PV_azimuth | Design azimuth PV | deg | 0 | 0 | 0 | 0
| eta_inv | Inverter design efficiency | % | 95 | 0.95 | 95 | 0.95
| P_max | Maximum power injectable to the grid | MW | 50 | 50 | 50 | 50
| BESS_h | BESS hours of storage | h | 0 |  | 0
| P_BESS | Design power BESS | MW | 0 | 0 | 0
| E_BESS | Energy storage Capacity - BESS | MWh | 0 |  | 0
|  | Annual BESS cycles |  | 0 | 0 | 0
| N_cycle_max | Maximum cycle per BESS | - | 0 | 0 | 0
| N_replacement | Number of replacements BESS | - | 0 | 0 | 0
|  | EUR Conversion Factor |  |  |  |  | 0.84

## 2.2 - AESOPT - 50%
Type | Symbol | Description | Unit | Partners
|  |  |  | MoSES | YACOP | AESOPT | HOPP
Key Performance Indicators (KPIs) | AEY | Annual Energy Yield | GWh | 158.724 | 162.3651 | 170.0924 | 175.5054
|  | Annual HTF energy into from field (CSP-only) | GWht |  |  | 0
| HCF | Hybrid Capacity Factor | % | 45.69% | 46.71% | 48.96% | 50.52%
| NPV | Net Present Value | MEUR | -44.5053 | -52.5483 | -58.0768 | -41.9807
| PPA | Power Purchase Agreement | EUR/MWh |  |  | 0
|  | LCOE | EUR/MWh | 69.2589 | 71.4687 | 73.113 | 66.282
| CAPEX | Capital Expenditure | MEUR | 144.7307 | 194.7609 | 165.9122 | 195.2467
| OPEX | Operational Expenditure | kEUR/year | 1342.5239 | 1370.6867 | 1373.0612 | 1375.2374
|  | Revenues | kEUR/year | 8025.4746 | 8100.1499 | 8563.4437 | 8833.6954
| AF | Availability Factor | % | 0% |  | 0%
| EH_UF | Electric Heater Utilization Factor | % | 0% |  | 0% | 0%
| TES_PV_fraction | Fraction of TES charged by PV+EH | % | 0% |  | 0% | 0%
| c_block | Specifc cost of the power block | EUR/kW | 0 | 0 | 0
| eta_blk_des | Design Efficiency of the PB (NET) | % | 0% |  | 0%
| f_AEY_CSP | Share of AEY - CSP | % | 0% | -1.31e-14% | 0%
| f_AEY_PV | Share of AEY - PV | % | 86.61% | 77% | 79.47% | 77.28%
| f_AEY_BESS | Share of AEY - BESS | % | 13.39% | 23% | 20.53% | 22.72%
|  | AEY - CSP | GWh | 0 | -2.13e-14 | 0
|  | AEY - PV | GWh | 137.4769 | 125.0242 | 135.1733 | 135.6257
|  | AEY - BESS (Discharge) | GWh | 21.2471 | 37.341 | 34.9191 | 39.8798
| EW_PV | Electricity Curtailed PV and Wasted | GWh | 67.1232 | 41.2705 | 39.9176 | 47.9271
| EEH_PV | Electricity from PV to EH | GWh | 0 |  | 0
| EBESS_PV | Electricity from PV to BESS | GWh | 27.6448 | 43.8621 | 42.771 | 40.8633
| CF_tot | Total Capacity Factor | % | 13.44% | 13.74% | 14.4% | 15.41%
| CF_CSP | CSP production over CSP installed capacity | % | 0% | 0% | 0%
| CF_PV | PV production over PV installed capacity | % | 24.76% | 13.96% | 24.35% | 11.66%
| CF_BESS | BESS production over BESS installed capacity | % | 7.423% | 13.03% | 12.2% | 13.93%
Costs | CAPEX_CSP | Capital Expenditure - CSP | MEUR | 0 | 0 | 0
| CAPEX_PV | Capital Expenditure - PV | MEUR | 72.5337 | 72.3978 | 72.3569 | 72.5338
| CAPEX_BESS | Capital Expenditure - BESS | MEUR | 72.197 | 122.3632 | 93.5552 | 122.7129
| C_tower | Tower Cost | MEUR |  |  | 0
| C_receiver | Receiver Cost | MEUR |  |  | 0
| C_field | Field Cost | MEUR |  |  | 0
| C_site_CSP | Site Improvement Cost - CSP | MEUR |  |  | 0
| C_storage | Storage Cost | MEUR |  |  | 0
| C_block | Block Cost | MEUR |  |  | 0
| C_bop | Bop Cost | MEUR |  |  | 0
| C_heater | Heater Cost | MEUR |  |  | 0
| C_land_CSP | Land Cost - CSP | MEUR |  |  | 0
| C_year_CSP | Annual fixed operating Cost - CSP | kEUR/year |  |  | 0
| C_OM_CSP | Annual variable operating Cost - CSP | kEUR/year |  |  | 0
| C_cap_CSP | Total capital cost - CSP | MEUR |  | 0 | 0
| C_modules_PV | Modules Cost - PV | MEUR | 31.2344 | 31.2533 | 31.2344 | 31.2344
| C_BoS_PV | Bos Cost - PV | MEUR | 23.4258 | 23.44 | 23.4258 | 23.4258
| C_site_PV | Site Improvement Cost - PV | MEUR | 0 | 0 | 0 | 0
| C_inverter_PV | Inverter Cost - PV | MEUR | 4.2904 | 4.2896 | 4.2904 | 4.2904
| C_land_PV | Land Cost - PV | MEUR | 5.7426 | 5.7471 | 5.7427 | 5.7427
| C_year_PV | Annual fixed operating Cost - PV | kEUR/year | 1115.5148 | 1115.288 | 1115.5148 | 1115.5148
| C_cap_PV | Total capital cost - PV | MEUR | 58.9507 | 58.9829 | 58.9507 | 58.9507
| C_BoS_BESS | Bos Cost - BESS | MEUR | 0 | 0 | 0 | 0
| C_PCS_BESS | Power Convertion System - BESS | MEUR | 6.1803 | 6.1803 | 6.1753 | 6.1753
| C_ES_BESS | Energy Storage Cost - BESS | MEUR | 28.7708 | 25.5264 | 25.539 | 25.5332
| C_replacement_BESS | Replacement Cost - BESS | MEUR | 28.7708 | 76.5793 | 51.078 | 76.5995
| C_year_BESS | Annual fixed operating Cost - BESS | kEUR/year | 189.5292 | 189.5292 | 189.3747 | 189.3747
| c_OM_BESS | Annual variable operating Cost - BESS | kEUR/year | 37.4799 | 65.8695 | 68.1718 | 70.3479
| C_Cap_BESS | Total capital cost - BESS | MEUR | 63.722 | 108.286 | 82.7922 | 108.308
| C_year | Total Annual cost | MEUR/year |  | 11.604 | 12.436 | 11.632
Design | Q_field_des | Design Solar Field Power | MW |  |  | 0
| A_SF | Area of the SF | m2 |  |  | 0
| A_land_CSP_tot | Total Land Area CSP | m2 |  |  | 0
| eff_SF_des | Design Solar Field Efficiency | % |  |  | 0
| n_heliostat | Number of Heliostat | -
| SM | Solar Multiple | - |  |  | 0
| H_tower | Tower height | m |  |  | 0
| Q_rec_des | Design Receiver Output | MW |  |  | 0
| H_rec | Height of the Receiver | m
| D_rec | Diameter of the Receiver | m
| rec_eff_design | Total Receiver Efficiency | % |  |  | 0
| rec_eff_th_design | Receiver Thermal Efficiency | %
| A_receiver | Area of the receiver | m2 |  |  | 0
| m_flow_rec | Design mass flow rate receiver | kg/s |  | 0
| T_hot_set_REC/EH | Design hot temperature REC/EH | C
| T_cold_set_REC/EH | T_cold_set_REC/EH | C
| Q_name_EH | Design thermal power EH | MW |  |  | 0
| EH_eff_design | Design EH efficiency | % |  |  | 0.95
| m_flow_EH_des | Design EH mass flow rate | kg/s |  | 0
| P_name_EH | Design electrical power EH | MW |  | 0 | 0
| EH_W_min | Mimum power to run EH | MW |  | 0
| t_storage | TES hours | h |  |  | 0
| H_storage | Height of the TES tank | m
| D_storage | Diameter of the TES tank | m
| A_surf_TES | Surface losses area TES | m2
| E_max | Maximum Energy that can be stored in the TES | MWh |  |  | 0
| Q_flow_des | Design thermal power to PB | MW |  |  | 0
| eta_blk_des | Design NET Efficiency of the PB | % |  |  | 0
| TIT | Turbine Inlet Temperature | C
| T_hot_MS | Molten Salt Hot Temperature - PB | C | 550 |  | 550
| T_return_MS | Molten Salt Cold Temperature - PB | C | 290 |  | 290
| T_amb_PB | Design ambient temperature - PB | C | 30 |  | 30
| P_gross | Design gross electrical power - PB | MW | 0 |  | 0
| P_net | Design net electrical power - PB | MW | 0 | 0 | 0
| PV_P_AC | Design AC Power - PV | MW | 102.1534 | 102.1326 | 102.1534 | 102.1534
| PV_P_DC | Design DC Power - PV | MW | 132.7994 | 132.8799 | 132.7994 | 132.7994
| PV_r_DCAC | DC-to-AC ratio | - | 1.3 | 1.3011 | 1.3 | 1.3
| A_PV_field | Area of the PV field | m2 | 737774.3193 | 738221.6 | 737774.3193 | 737774.3193
| A_land_PV_tot | Total land occupied by the PV plant | m2 | 2766653.6973 | 2768331 | 2766653.6973 | 2766653.697
| PV_GCR | GCR | - | 0.4 | 0.4 | 0.4 | 0.4
| PV_tilt | Design tilt PV | deg | 37 | 37 | 37 | 37
| PV_azimuth | Design azimuth PV | deg | 0 | 0 | 0 | 0
| eta_inv | Inverter design efficiency | % | 95 | 0.95 | 95 | 0.95
| P_max | Maximum power injectable to the grid | MW | 50 | 50 | 50 | 50
| BESS_h | BESS hours of storage | h | 4.2569 |  | 4.4513 | 3.561
| P_BESS | Design power BESS | MW | 32.6733 | 32.7 | 32.6733 | 32.6733
| E_BESS | Energy storage Capacity - BESS | MWh | 146.52 | 145.4 | 145.4385 | 145.4385
|  | Annual BESS cycles |  | 153 | 256.1753 | 240.0955
| N_cycle_max | Maximum cycle per BESS | - |  | 2000 | 2000 | 2000
| N_replacement | Number of replacements BESS | - | 1 | 3 | 2 | 3
|  | EUR Conversion Factor |  |  |  |  | 0.84

## 2.3 - AESOPT - 70%
Type | Symbol | Description | Unit | Partners
|  |  |  | MoSES | YACOP | AESOPT | HOPP
Key Performance Indicators (KPIs) | AEY | Annual Energy Yield | GWh | 244.3977 | 222.206 | 241.274 | 228.1172
|  | Annual HTF energy into from field (CSP-only) | GWht |  |  | 311.9473 | 335.1875
| HCF | Hybrid Capacity Factor | % | 70.35% | 63.92% | 69.45% | 65.67%
| NPV | Net Present Value | MEUR | -92.3501 | -109.4353 | -90.9611 | -103.7579
| PPA | Power Purchase Agreement | EUR/MWh |  |  | 0
|  | LCOE | EUR/MWh | 74.992 | 81.6037 | 74.7471 | 80.0567
| CAPEX | Capital Expenditure | MEUR | 244.4285 | 241.3216 | 240.1795 | 243.8224
| OPEX | Operational Expenditure | kEUR/year | 2029.5576 | 2041.692 | 2019.5525 | 2004.4313
|  | Revenues | kEUR/year | 12170.0309 | 10835.7669 | 11969.3232 | 11343.8285
| AF | Availability Factor | % |  |  | 0%
| EH_UF | Electric Heater Utilization Factor | % |  |  | 0% | 0%
| TES_PV_fraction | Fraction of TES charged by PV+EH | % |  |  | 0% | 0%
| c_block | Specifc cost of the power block | EUR/kW | 2171.9636 | 2105.4799 | 2049.2513 | 2104.7385
| eta_blk_des | Design Efficiency of the PB (NET) | % | 38.46% | 38.61% | 38.97% | 38.46%
| f_AEY_CSP | Share of AEY - CSP | % | 51.75% | 53.16% | 51.52% | 50.9%
| f_AEY_PV | Share of AEY - PV | % | 48.25% | 46.84% | 48.48% | 49.1%
| f_AEY_BESS | Share of AEY - BESS | % | 0% | 0% | 0%
|  | AEY - CSP | GWh | 126.4686 | 118.1346 | 124.3002 | 116.1131
|  | AEY - PV | GWh | 117.9291 | 104.0714 | 116.9738 | 112.0042
|  | AEY - BESS (Discharge) | GWh | 0 | 0 | 0
| EW_PV | Electricity Curtailed PV and Wasted | GWh | 26.4381 | 25.7313 | 18.5376 | 27.585
| EEH_PV | Electricity from PV to EH | GWh | 0 |  | 0
| EBESS_PV | Electricity from PV to BESS | GWh | 0 | 0 | 0
| CF_tot | Total Capacity Factor | % | 30.24% | 27.62% | 29.85% | 2589%
| CF_CSP | CSP production over CSP installed capacity | % | 50.26% | 46.96% | 49.39% | 4393%
| CF_PV | PV production over PV installed capacity | % | 24.54% | 18.82% | 24.35% | 1548%
| CF_BESS | BESS production over BESS installed capacity | % | 0% | 0% | 0%
Costs | CAPEX_CSP | Capital Expenditure - CSP | MEUR | 199.3405 | 196.6053 | 195.173 | 198.7059
| CAPEX_PV | Capital Expenditure - PV | MEUR | 45.088 | 44.7163 | 45.0065 | 45.1165
| CAPEX_BESS | Capital Expenditure - BESS | MEUR | 0 | 0 | 0
| C_tower | Tower Cost | MEUR | 13.4813 | 13.3632 | 13.4162 | 13.6566
| C_receiver | Receiver Cost | MEUR | 31.8696 | 31.2142 | 31.1946 | 30.7976
| C_field | Field Cost | MEUR | 31.3058 | 30.4456 | 30.7904 | 30.8946
| C_site_CSP | Site Improvement Cost - CSP | MEUR | 2.6297 | 2.5371 | 2.5659 | 2.5745
| C_storage | Storage Cost | MEUR | 20.5376 | 20.2631 | 20.2624 | 21.5094
| C_block | Block Cost | MEUR | 62.3354 | 63.474 | 61.8369 | 63.5112
| C_bop | Bop Cost | MEUR | 0 |  | 0 | 0
| C_heater | Heater Cost | MEUR | 0 |  | 0 | 0
| C_land_CSP | Land Cost - CSP | MEUR | 3.2738 | 3.0486 | 3.0935 | 3.1732
| C_year_CSP | Annual fixed operating Cost - CSP | kEUR/year | 964.32 | 964.32 | 965.2248 | 965.2248
| C_OM_CSP | Annual variable operating Cost - CSP | kEUR/year | 366.247 | 388.5177 | 360.4706 | 345.3494
| C_cap_CSP | Total capital cost - CSP | MEUR | 162.1592 | 161.2973 | 160.0663 | 162.9439
| C_modules_PV | Modules Cost - PV | MEUR | 19.4158 | 19.3035 | 19.428 | 19.428
| C_BoS_PV | Bos Cost - PV | MEUR | 14.5618 | 14.4777 | 14.571 | 14.571
| C_site_PV | Site Improvement Cost - PV | MEUR | 0 | 0 | 0 | 0
| C_inverter_PV | Inverter Cost - PV | MEUR | 2.667 | 2.6494 | 2.6687 | 2.6687
| C_land_PV | Land Cost - PV | MEUR | 3.5697 | 3.5497 | 3.572 | 3.572
| C_year_PV | Annual fixed operating Cost - PV | kEUR/year | 693.42 | 688.8543 | 693.8572 | 693.8572
| C_cap_PV | Total capital cost - PV | MEUR | 36.6446 | 36.4306 | 36.6677 | 36.6677
| C_BoS_BESS | Bos Cost - BESS | MEUR | 0 |  | 0
| C_PCS_BESS | Power Convertion System - BESS | MEUR | 0 |  | 0
| C_ES_BESS | Energy Storage Cost - BESS | MEUR | 0 |  | 0
| C_replacement_BESS | Replacement Cost - BESS | MEUR | 0 | 0 | 0
| C_year_BESS | Annual fixed operating Cost - BESS | kEUR/year | 0 |  | 0
| c_OM_BESS | Annual variable operating Cost - BESS | kEUR/year | 0 |  | 0
| C_Cap_BESS | Total capital cost - BESS | MEUR | 0 | 0 | 0
| C_year | Total Annual cost | MEUR/year |  | 18.1328 | 18.0345 | 18.2623
Design | Q_field_des | Design Solar Field Power | MW | 189.9698 | 187.038 | 187.9726 | 190.2195
| A_SF | Area of the SF | m2 | 313057.5975 | 302039.6941 | 305460.3795 | 306493.8097
| A_land_CSP_tot | Total Land Area CSP | m2 | 1574708.3527 | 1468487.833 | 1490357.6143 | 1528773.589
| eff_SF_des | Design Solar Field Efficiency | % | 0.68658 | 0.68806 | 0.68756
| n_heliostat | Number of Heliostat | - | 2104 | 2030 |  | 2060
| SM | Solar Multiple | - | 2.22 |  | 2.2239 | 2.2239
| H_tower | Tower height | m | 148.411 | 147.6324 | 147.8242 | 149.5541
| Q_rec_des | Design Receiver Output | MW | 165.6832 | 163.1755 | 163.9472 | 166.1261
| H_rec | Height of the Receiver | m |  |  |  | 10.6926
| D_rec | Diameter of the Receiver | m |  |  |  | 10.6926
| rec_eff_design | Total Receiver Efficiency | % | 0.87216 | 0.87242 | 0.87212 | 87.3339
| rec_eff_th_design | Receiver Thermal Efficiency | %
| A_receiver | Area of the receiver | m2 | 377.7017 | 366.148 | 369.5394 | 359.0046
| m_flow_rec | Design mass flow rate receiver | kg/s | 420.5559 | 414.1905 |  | 424.5622
| T_hot_set_REC/EH | Design hot temperature REC/EH | C | 550 | 550 |  | 550
| T_cold_set_REC/EH | T_cold_set_REC/EH | C | 290 | 290 |  | 290
| Q_name_EH | Design thermal power EH | MW |  |  | 0
| EH_eff_design | Design EH efficiency | % |  |  | 0.95
| m_flow_EH_des | Design EH mass flow rate | kg/s |  | 0
| P_name_EH | Design electrical power EH | MW |  | 0 | 0
| EH_W_min | Mimum power to run EH | MW |  | 0
| t_storage | TES hours | h | 15.6 |  | 15.5814 | 15.5814
| H_storage | Height of the TES tank | m |  |  |  | 12
| D_storage | Diameter of the TES tank | m
| A_surf_TES | Surface losses area TES | m2
| E_max | Maximum Energy that can be stored in the TES | MWh | 1164.2603 | 1148.7 | 1148.6598 | 1163.926
| Q_flow_des | Design thermal power to PB | MW | 74.6321 | 74.336 | 73.7198 | 74.6996
| eta_blk_des | Design NET Efficiency of the PB | % | 0.38455 | 0.38608 | 0.38968 | 0.38457
| TIT | Turbine Inlet Temperature | C
| T_hot_MS | Molten Salt Hot Temperature - PB | C | 550 | 550 | 550 | 550
| T_return_MS | Molten Salt Cold Temperature - PB | C | 290 | 290.1764 | 290 | 290
| T_amb_PB | Design ambient temperature - PB | C | 30 | 30 | 30 | 30
| P_gross | Design gross electrical power - PB | MW | 30.1471 | 30.1471 | 30.1753 | 30.1753
| P_net | Design net electrical power - PB | MW | 28.7 | 28.7 | 28.7269 | 28.7269
| PV_P_AC | Design AC Power - PV | MW | 63.5 | 63.0819 | 63.54 | 63.54
| PV_P_DC | Design DC Power - PV | MW | 82.55 | 82.0729 | 82.602 | 82.602
| PV_r_DCAC | DC-to-AC ratio | - | 1.3 | 1.3011 | 1.3 | 1.3
| A_PV_field | Area of the PV field | m2 | 458611.1111 | 455960.4 | 458900.2449 | 458900.2449
| A_land_PV_tot | Total land occupied by the PV plant | m2 | 1719796.5 | 1709851.5 | 1720875.9183 | 1720875.918
| PV_GCR | GCR | - | 0.4 | 0.4 | 0.4 | 0.4
| PV_tilt | Design tilt PV | deg | 37 | 37 | 37 | 37
| PV_azimuth | Design azimuth PV | deg | 0 | 0 | 0 | 0
| eta_inv | Inverter design efficiency | % |  | 0.95 | 95 | 0.95
| P_max | Maximum power injectable to the grid | MW |  | 50 | 50 | 50
| BESS_h | BESS hours of storage | h |  |  | 0
| P_BESS | Design power BESS | MW |  | 0 | 0
| E_BESS | Energy storage Capacity - BESS | MWh |  |  | 0
|  | Annual BESS cycles |  |  | 0 | 0
| N_cycle_max | Maximum cycle per BESS | - |  | 0 | 0
| N_replacement | Number of replacements BESS | - |  | 0 | 0
|  | EUR Conversion Factor |  |  |  |  | 0.84

## 2.4 - AESOPT - 90%
Type | Symbol | Description | Unit | Partners
|  |  |  | MoSES | YACOP | AESOPT | HOPP
Key Performance Indicators (KPIs) | AEY | Annual Energy Yield | GWh | 304.0089 | 292.8817 | 309.9734 | 299.8998
|  | Annual HTF energy into from field (CSP-only) | GWht |  |  | 448.4409 | 620.4995
| HCF | Hybrid Capacity Factor | % | 87.51% | 84.25% | 89.23% | 86.33%
| NPV | Net Present Value | MEUR | -193.6455 | -205.6579 | -191.2601 | -208.4301
| PPA | Power Purchase Agreement | EUR/MWh |  |  | 0
|  | LCOE | EUR/MWh | 91.6421 | 95.6764 | 90.5262 | 95.5822
| CAPEX | Capital Expenditure | MEUR | 315.1723 | 386.9031 | 381.4068 | 395.994
| OPEX | Operational Expenditure | kEUR/year | 2680.4568 | 2715.7063 | 2628.7841 | 2768.2957
|  | Revenues | kEUR/year | 14947.879 | 14308.7612 | 15307.6288 | 14767.1229
| AF | Availability Factor | % |  |  | 62.49%
| EH_UF | Electric Heater Utilization Factor | % |  |  | 0%
| TES_PV_fraction | Fraction of TES charged by PV+EH | % |  |  | 0%
| c_block | Specifc cost of the power block | EUR/kW | 2000.4458 | 1938.9959 | 1877.1239 | 1939.1985
| eta_blk_des | Design Efficiency of the PB (NET) | % | 38.77% | 38.87% | 39.16% | 38.77%
| f_AEY_CSP | Share of AEY - CSP | % | 65.55% | 63.32% | 56.91% | 73.31%
| f_AEY_PV | Share of AEY - PV | % | 34.45% | 34.2% | 40.36% | 24.2%
| f_AEY_BESS | Share of AEY - BESS | % | 0% | 2.48% | 2.734% | 2.488%
|  | AEY - CSP | GWh | 199.2819 | 185.4533 | 176.3932 | 219.8499
|  | AEY - PV | GWh | 104.727 | 100.166 | 125.1044 | 72.5873
|  | AEY - BESS (Discharge) | GWh | 0 | 7.2624 | 8.4758 | 7.4626
| EW_PV | Electricity Curtailed PV and Wasted | GWh | 70.7614 | 48.9201 | 31.2607 | 89.3003
| EEH_PV | Electricity from PV to EH | GWh | 0 |  | 0
| EBESS_PV | Electricity from PV to BESS | GWh | 11.4857 | 8.5315 | 8.2557 | 7.6863
| CF_tot | Total Capacity Factor | % | 28.69% | 27.75% | 29.25% | 3077%
| CF_CSP | CSP production over CSP installed capacity | % | 63.39% | 58.93% | 56.11% | 6657%
| CF_PV | PV production over PV installed capacity | % | 15.49% | 14.92% | 24.35% | 825.8%
| CF_BESS | BESS production over BESS installed capacity | % | 0% | 10.49% | 12.26% | 1079%
Costs | CAPEX_CSP | Capital Expenditure - CSP | MEUR | 315.1723 | 309.7303 | 309.1249 | 318.2151
| CAPEX_PV | Capital Expenditure - PV | MEUR | 54.8079 | 54.2983 | 54.6744 | 54.808
| CAPEX_BESS | Capital Expenditure - BESS | MEUR | 7.6418 | 22.8745 | 17.6076 | 22.9709
| C_tower | Tower Cost | MEUR | 17.2097 | 16.963 | 17.0832 | 16.4875
| C_receiver | Receiver Cost | MEUR | 54.0647 | 52.912 | 53.3998 | 55.318
| C_field | Field Cost | MEUR | 70.2178 | 68.4743 | 69.5169 | 71.1809
| C_site_CSP | Site Improvement Cost - CSP | MEUR | 5.8983 | 5.7062 | 5.7931 | 5.9317
| C_storage | Storage Cost | MEUR | 34.4409 | 34.0999 | 34.1001 | 36.0809
| C_block | Block Cost | MEUR | 71.7942 | 73.1197 | 70.765 | 73.1052
| C_bop | Bop Cost | MEUR | 0 |  | 0
| C_heater | Heater Cost | MEUR | 0 |  | 0
| C_land_CSP | Land Cost - CSP | MEUR | 9.1004 | 8.2002 | 8.3351 | 8.4901
| C_year_CSP | Annual fixed operating Cost - CSP | kEUR/year | 1205.8743 | 1206.24 | 1205.8743 | 1205.8743
| C_OM_CSP | Annual variable operating Cost - CSP | kEUR/year | 585.8888 | 614.401 | 517.7056 | 660.6004
| C_cap_CSP | Total capital cost - CSP | MEUR | 253.6256 | 251.2751 | 250.6581 | 258.1042
| C_modules_PV | Modules Cost - PV | MEUR | 23.6014 | 23.44 | 23.6014 | 23.6014
| C_BoS_PV | Bos Cost - PV | MEUR | 17.701 | 17.58 | 17.701 | 17.701
| C_site_PV | Site Improvement Cost - PV | MEUR | 0 | 0 | 0
| C_inverter_PV | Inverter Cost - PV | MEUR | 3.2419 | 3.2172 | 3.2419 | 3.2419
| C_land_PV | Land Cost - PV | MEUR | 4.3392 | 4.3103 | 4.3393 | 4.3393
| C_year_PV | Annual fixed operating Cost - PV | kEUR/year | 842.9054 | 836.466 | 842.9054 | 842.9054
| C_cap_PV | Total capital cost - PV | MEUR | 44.5443 | 44.2372 | 44.5443 | 44.5443
| C_BoS_BESS | Bos Cost - BESS | MEUR | 0 |  | 0
| C_PCS_BESS | Power Convertion System - BESS | MEUR | 1.4931 | 1.4931 | 1.4919 | 1.4919
| C_ES_BESS | Energy Storage Cost - BESS | MEUR | 5.2517 | 4.6875 | 4.6967 | 4.6956
| C_replacement_BESS | Replacement Cost - BESS | MEUR | 0 | 14.0624 | 9.3934 | 14.0868
| C_year_BESS | Annual fixed operating Cost - BESS | kEUR/year | 45.7884 | 45.7884 | 45.7517 | 45.7517
| c_OM_BESS | Annual variable operating Cost - BESS | kEUR/year | 0 | 12.8109 | 16.5471 | 13.164
| C_Cap_BESS | Total capital cost - BESS | MEUR | 6.7448 | 20.2429 | 15.582 | 20.2744
| C_year | Total Annual cost | MEUR/year |  | 28.0219 | 28.0607 | 28.665
Design | Q_field_des | Design Solar Field Power | MW | 398.5774 | 389.85 | 394.6074 | 395.6877
| A_SF | Area of the SF | m2 | 702178.0599 | 679308.2118 | 689651.8725 | 706160.0895
| A_land_CSP_tot | Total Land Area CSP | m2 | 4380775.5823 | 3950010.272 | 4015603.1355 | 4090246.949
| eff_SF_des | Design Solar Field Efficiency | % | 0.63457 | 0.63766 | 0.63626
| n_heliostat | Number of Heliostat | - | 4718 | 4565 |  | 4745
| SM | Solar Multiple | - | 3.7515 |  | 3.7515 | 3.7515
| H_tower | Tower height | m | 170.0188 | 168.7411 | 169.3227 | 166.2249
| Q_rec_des | Design Receiver Output | MW | 347.2391 | 339.7039 | 343.8035 | 347.2391
| H_rec | Height of the Receiver | m |  |  |  | 16.2466
| D_rec | Diameter of the Receiver | m |  |  |  | 16.2466
| rec_eff_design | Total Receiver Efficiency | % | 0.87085 | 0.87137 | 0.87127 | 87.7558
| rec_eff_th_design | Receiver Thermal Efficiency | %
| A_receiver | Area of the receiver | m2 | 849.5821 | 778.1937 | 789.1208 | 828.8121
| m_flow_rec | Design mass flow rate receiver | kg/s | 881.4015 | 862.2749 |  | 887.4255
| T_hot_set_REC/EH | Design hot temperature REC/EH | C | 550 | 550 |  | 550
| T_cold_set_REC/EH | T_cold_set_REC/EH | C | 290 | 290 |  | 290
| Q_name_EH | Design thermal power EH | MW |  |  | 0
| EH_eff_design | Design EH efficiency | % |  |  | 0.95
| m_flow_EH_des | Design EH mass flow rate | kg/s |  | 0
| P_name_EH | Design electrical power EH | MW |  | 0 | 0
| EH_W_min | Mimum power to run EH | MW |  | 0
| t_storage | TES hours | h | 21.1 |  | 21.0939 | 21.0939
| H_storage | Height of the TES tank | m |  |  |  | 12
| D_storage | Diameter of the TES tank | m
| A_surf_TES | Surface losses area TES | m2
| E_max | Maximum Energy that can be stored in the TES | MWh | 1952.9937 | 1933.1 | 1933.1134 | 1952.4303
| Q_flow_des | Design thermal power to PB | MW | 92.5589 | 92.3664 | 91.6432 | 92.5589
| eta_blk_des | Design NET Efficiency of the PB | % | 38.85% | 38.87% | 39.16% | 38.77%
| TIT | Turbine Inlet Temperature | C | 540
| T_hot_MS | Molten Salt Hot Temperature - PB | C | 550 | 550 | 550 | 550
| T_return_MS | Molten Salt Cold Temperature - PB | C | 290 | 290.1764 | 290 | 290
| T_amb_PB | Design ambient temperature - PB | C | 30 | 30 | 30 | 30
| P_gross | Design gross electrical power - PB | MW | 37.6987 | 37.7101 | 37.6987 | 37.6987
| P_net | Design net electrical power - PB | MW | 35.8891 | 35.9 | 35.8891 | 35.8891
| PV_P_AC | Design AC Power - PV | MW | 77.1891 | 76.5995 | 77.1891 | 77.1891
| PV_P_DC | Design DC Power - PV | MW | 100.3459 | 99.6599 | 100.3459 | 100.3459
| PV_r_DCAC | DC-to-AC ratio | - | 1.3 | 1.3011 | 1.3 | 1.3
| A_PV_field | Area of the PV field | m2 | 557477.0909 | 553666.2 | 557477.0909 | 557477.089
| A_land_PV_tot | Total land occupied by the PV plant | m2 | 2090539.0908 | 2076248.25 | 2090539.0908 | 2090539.08
| PV_GCR | GCR | - | 0.4 | 0.4 | 0.4 | 0.4
| PV_tilt | Design tilt PV | deg | 37 | 37 | 37 | 37
| PV_azimuth | Design azimuth PV | deg | 0 | 0 | 0 | 0
| eta_inv | Inverter design efficiency | % | 0.95 | 0.95 | 0.95 | 0.95
| P_max | Maximum power injectable to the grid | MW | 50 | 50 | 50 | 50
| BESS_h | BESS hours of storage | h | 3.2163 |  | 3.3883 | 2.7107
| P_BESS | Design power BESS | MW | 7.8937 | 7.9 | 7.8937 | 7.8937
| E_BESS | Energy storage Capacity - BESS | MWh | 26.7465 | 26.7 | 26.7465 | 26.7465
|  | Annual BESS cycles |  |  | 272.1863 | 316.8944
| N_cycle_max | Maximum cycle per BESS | - |  | 2000 | 2000 | 2000
| N_replacement | Number of replacements BESS | - | 0 | 3 | 2 | 3

## 3.1 - Paper Figures - HOPP
Appendix C - Results of fixed design comparison
HOPP-30% | MoSES | YACOP | AESOPT | HOPP
AEY | 0.93152 | -8.2716 | -1.3279 | 0
HCF | 0.93152 | -8.3351 | -1.3281 | 0
NPV | 3.0059 | -26.6339 | -3.635 | 0
LCOE | -0.87665 | 9.0619 | 1.1449 | 0
CAPEX | 0.04667 | 0.0093461 | -0.24382 | 0
OPEX | 0.04683 | 0.17689 | -5.1982e-06 | 0
REV | 0.9999 | -8.5516 | -1.3052 | 0
30% HCF solution
HOPP-50% | MoSES | YACOP | AESOPT | HOPP
AEY | -6.2807 | -7.82 | -3.1059 | 0
HCF | -6.2807 | -7.4813 | -3.1062 | 0
NPV | 4.9846 | -18.9445 | -29.5859 | 0
LCOE | 0.95662 | 7.7997 | 9.9673 | 0
CAPEX | -25.1095 | -0.52932 | -14.4555 | 0
OPEX | -1.4267 | -0.92482 | -0.099569 | 0
REV | -5.5509 | -8.7866 | -3.0382 | 0
50% HCF solution
HOPP-70% | MoSES | YACOP | AESOPT | HOPP
AEY | 3.6035 | -2.6526 | 3.8925 | 0
HCF | 3.6035 | -2.503 | 3.8922 | 0
NPV | 4.5983 | -2.7007 | 9.9133 | 0
LCOE | -3.4414 | 1.8683 | -5.7288 | 0
CAPEX | 0.39779 | -0.9022 | -1.9086 | 0
OPEX | -3.0775 | -0.22764 | -3.3672 | 0
REV | 3.5974 | -3.5452 | 3.9709 | 0
0
70% HCF solution
HOPP-90% | MoSES | YACOP | AESOPT | HOPP
AEY | 4.8037 | 1.2101 | 3.6092 | 0
HCF | 4.8038 | 1.1406 | 3.6089 | 0
NPV | 2.1418 | 0.93919 | 4.1554 | 0
LCOE | -3.9474 | -1.4346 | -4.3032 | 0
CAPEX | 0.8272 | -0.61473 | -0.68097 | 0
OPEX | -0.95811 | 3.5147 | -2.5544 | 0
REV | 3.5929 | 0.73606 | 3.7903 | 0
| 3.8925 | -2.6526
| 4.8037 | 1.2101
90% HCF solution
Figure 35: KPIs of the hybrid CSP system evaluated with different modeling tools using the optimal design of HOPP solutions for different values of the HCF.

## 3.2 - Paper Figures - AESOPT
Appendix C - Results of fixed design comparison
AESOPT-30% | MoSES | YACOP | AESOPT | HOPP
AEY | 4.0703 | -4.8481 | 0 | 2.0076
HCF | 4.0707 | -4.9132 | 0 | 2.0079
NPV | 9.9477 | -15.2959 | 0 | 4.7638
LCOE | -3.6563 | 7.1534 | 0 | -1.7735
CAPEX | 0.31107 | 1.9732 | 0 | 0.24442
OPEX | 0.066667 | 1.895 | 0 | -8.004e-07
REV | 4.1974 | -5.0488 | 0 | 2.0526
30% HCF solution
AESOPT-50% | MoSES | YACOP | AESOPT | HOPP
AEY | -6.6837 | -4.543 | 0 | 3.1824
HCF | -6.6834 | -4.6083 | 0 | 3.1828
NPV | -23.3682 | -9.5192 | 0 | -27.7152
LCOE | -5.2713 | -2.2489 | 0 | -9.343
CAPEX | -12.7667 | 17.388 | 0 | 17.6808
OPEX | -2.224 | -0.17294 | 0 | 0.15849
REV | -6.2822 | -5.4101 | 0 | 3.1559
50% HCF solution
AESOPT-70% | MoSES | YACOP | AESOPT | HOPP
AEY | 1.2947 | -7.903 | 0 | -5.4531
HCF | 1.295 | -7.9661 | 0 | -5.4527
NPV | 1.527 | 20.31 | 0 | 14.0684
LCOE | 0.32757 | 9.173 | 0 | 7.1034
CAPEX | 1.7691 | 0.4755 | 0 | 1.5167
OPEX | 0.49541 | 1.0963 | 0 | -0.74874
REV | 1.6769 | -9.4705 | 0 | -5.2258
70% HCF solution
AESOPT-90% | MoSES | YACOP | AESOPT | HOPP
AEY | -1.9242 | -5.5139 | 0 | -3.2498
HCF | 1.295 | -7.9661 | 0 | -5.4527
NPV | 1.2472 | 7.5279 | 0 | 8.9773
LCOE | 1.2327 | 5.6892 | 0 | 5.5852
CAPEX | -17.3658 | 1.441 | 0 | 3.8246
OPEX | 1.9657 | 3.3066 | 0 | 5.3071
REV | -2.3501 | -6.5253 | 0 | -3.531
| 17.6808 | -12.7667
| 0 | -27.7152
90% HCF solution
Figure 36: KPIs of the hybrid CSP system evaluated with different modeling tools using the optimal design of AESOPT solutions for different values of the HCF.