## 0 - Overview
Title: | intercomparison_of_hybrid_CSP_PV_systems_fixed_design_outputs
Description | This excel workbook contains that results of running the fixed design case. All models ran the same design values and reported the resulting design outputs and operational decisions.
Sheet | Description
1 - Fixed Design Outputs | This sheet contains all design values for running a fixed variable design for all models.
2.1 - Output Operation - MoSES | This sheet contains the output operation for the fixed design when running the MoSES model.
2.2 - Output Operation - AESOPT | This sheet contains the output operation for the fixed design when running the AESOPT model.
2.3 - Output Operation - YACOP | This sheet contains the output operation for the fixed design when running the YACOP model.
2.4 - Output Operation - HOPP | This sheet contains the output operation for the fixed design when running the HOPP model.
3 - Paper Figures | This sheet contains the figures found in the corresponding paper.

## 1 - Fixed Design Outputs
Type | Symbol | Description | Unit | Partners
|  |  |  | MoSES | YACOP | AESOPT | HOPP
Key Performance Indicators (KPIs) | AEY | Annual Energy Yield | GWh | 284.694 | 272.864 | 289.2231 | 271.62
|  | Annual HTF energy into from field (CSP-only) | GWht | 428.7725 | - | 384.8882 | 533.688
| HCF | Hybrid Capacity Factor | % | 81.95 | 79.27 | 83.2548 | 78.189
| NPV | Net Present Value | MEUR | -208.61 | -212.43 | -211.4251 | -212.1
|  | LCOE | EUR/MWh | 97.1043 | 100.35 | 98.5349 | 101.8363
| CAPEX | Capital Expenditure | MEUR | 370.5972 | 382.4 | 380.5811 | 384.5025
| OPEX | Operational Expenditure | kEUR/year | 3071.6549 | 3325 | 3121.7129 | 3209.75
|  | Revenues | kEUR/year | 13872.8119 | 13488 | 14400.9095 | 13518.75
| EH_UF | Electric Heater Utilization Factor | % | 0 | 0 | 0 | 0
| TES_PV_fraction | Fraction of TES charged by PV+EH | % | 0 | 0 | 0 | 0
| c_block | Specifc cost of the power block | EUR/kW | 1770.6476 | 1716 | 1679.9376 | 1716.4361
| eta_blk_des | Design Efficiency of the PB (NET) | % | 39.2308 | 39.2 | 39.3865 | 39.2308
| f_AEY_CSP | Share of AEY - CSP | % | 47.6 | 57.278 | 51.7116 | 50.114
| f_AEY_PV | Share of AEY - PV | % | 46.6 | 36.6849 | 42.7735 | 45.5
| f_AEY_BESS | Share of AEY - BESS | % | 5.8 | 6.036 | 5.5149 | 4.37
|  | AEY - CSP | GWh | 135.54 | 156.291 | 149.562 | 181.44
|  | AEY - PV | GWh | 132.55 | 100.1 | 123.7108 | 164.7648
|  | PV- AC Generation (before curtailment) | GWh | 189.37 |  | 0 | 164.7648
|  | AEY - BESS (Discharge) | GWh | 16.6 | 16.47 | 15.9503 | 15.84
| EW_PV | Electricity Curtailed PV and Wasted | GWh | 20.98 | 35 | 18.4115 | 74.093
| EEH_PV | Electricity from PV to EH | GWh | 0 | 0 | 0 | 0
| EBESS_PV | Electricity from PV to BESS | GWh | 21.6 | 19.34 | 17.8297 | NA
| CF_tot | Total Capacity Factor | % | 21.6 | 21 | 21.976 | 22.54
| CF_CSP | CSP production over CSP installed capacity | % | 30.94 | 36.27 | 33.9849 | 39.43
| CF_PV | PV production over PV installed capacity | % | 20.1763 | 15.2 | 24.3458 | 19.29
| CF_BESS | BESS production over BESS installed capacity | % | 7.5 | 7.5 | 7.2832 | 7.2355
Costs | CAPEX_CSP | Capital Expenditure - CSP | MEUR | 276.8642 | 274.22 | 272.5111 | 276.1681
| CAPEX_PV | Capital Expenditure - PV | MEUR | 53.2535 | 53.23 | 53.1238 | 53.2536
| CAPEX_BESS | Capital Expenditure - BESS | MEUR | 40.479 | 54.9 | 54.9462 | 55.0808
| C_tower | Tower Cost | MEUR | 15.2691 | 15.1 | 15.0644 | 14.9352
| C_receiver | Receiver Cost | MEUR | 43.3614 | 42.63 | 42.6095 | 43.0755
| C_field | Field Cost | MEUR | 50.3317 | 49.4 | 49.4613 | 49.6145
| C_site_CSP | Site Improvement Cost - CSP | MEUR | 4.2279 | 4.11 | 4.1218 | 4.1345
| C_storage | Storage Cost | MEUR | 22.4824 | 22.5 | 22.5 | 23.5529
| C_block | Block Cost | MEUR | 88.5324 | 90.15 | 88.6518 | 90.1489
| C_bop | Bop Cost | MEUR | 0 | 0 | 0 | 0
| C_heater | Heater Cost | MEUR | 0 | 0 | 0 | 0
| C_land_CSP | Land Cost - CSP | MEUR | 5.7781 | 5.62 | 5.6206 | 5.6207
| C_year_CSP | Annual fixed operating Cost - CSP | kEUR/year | 1680 | 1680 | 1687.993 | 1679.9997
| C_OM_CSP | Annual variable operating Cost - CSP | kEUR/year | 398.4693 | 531 | 438.6806 | 531.9138
| C_cap_CSP | Total capital cost - CSP | MEUR | 224.2049 | 223.89 | 222.4088 | 225.4562
| C_modules_PV | Modules Cost - PV | MEUR | 22.932 | 22.98 | 22.932 | 22.932
| C_BoS_PV | Bos Cost - PV | MEUR | 17.199 | 17.24 | 17.199 | 17.199
| C_site_PV | Site Improvement Cost - PV | MEUR | 0 | 0 | 0 | 0
| C_inverter_PV | Inverter Cost - PV | MEUR | 3.15 | 3.15 | 3.15 | 3.15
| C_land_PV | Land Cost - PV | MEUR | 4.2162 | 4.23 | 4.2162 | 4.2
| C_year_PV | Annual fixed operating Cost - PV | kEUR/year | 819 | 820 | 819 | 819
| C_cap_PV | Total capital cost - PV | MEUR | 43.281 | 43.37 | 43.281 | 43.28
| C_BoS_BESS | Bos Cost - BESS | MEUR | 0 | 0 | 0 | 0
| C_PCS_BESS | Power Convertion System - BESS | MEUR | 4.725 | 4.725 | 4.725 | 4.725
| C_ES_BESS | Energy Storage Cost - BESS | MEUR | 10.334 | 10.97 | 10.975 | 10.9725
| C_replacement_BESS | Replacement Cost - BESS | MEUR | 20.668 | 32.9 | 32.925 | 32.9175
| C_year_BESS | Annual fixed operating Cost - BESS | kEUR/year | 144.9 | 144.9 | 144.9 | 144.9
| c_OM_BESS | Annual variable operating Cost - BESS | kEUR/year | 29.3 | 29 | 31.1393 | 27.4623
| C_Cap_BESS | Total capital cost - BESS | MEUR | 35.7276 | 48.6 | 48.625 | 48.57
| C_year | Total Annual cost | MEUR/year | 3.07 | 27.65 | 28.4986 | 27.6615
Design | Q_field_des | Design Solar Field Power | MW | 292.1709 | 292.4 | 292.4044 | 292.5065
| A_SF | Area of the SF | m2 | 503317.3878 | 490 045 | 490687.174 | 492207
| A_land_CSP_tot | Total Land Area CSP | m2 | 2780226.267 | 2705111 | 2707831.5606 | 2707875.605
| eff_SF_des | Design Solar Field Efficiency | % | 66.11 | 66.29 | 66.2826
| n_heliostat | Number of Heliostat | - | 3382 | 3293 |  | 3307
| SM | Solar Multiple | - | 2 | 2 | 2.0001 | 2
| H_tower | Tower height | m | 159.431 | 158.15 | 158.1891 | 157.459
| Q_rec_des | Design Receiver Output | MW | 255 | 255.1 | 255.115 | 254.9
| H_rec | Height of the Receiver | m | - |  |  | 13.58
| D_rec | Diameter of the Receiver | m | -
| rec_eff_design | Total Receiver Efficiency | % | 87.2442 | 87.25 | 87.2504 | 87.58
| rec_eff_th_design | Receiver Thermal Efficiency | % | -
| A_receiver | Area of the receiver | m2 | 585.5803 | 571.48 | 571.8284 | 579.7783
| m_flow_rec | Design mass flow rate receiver | kg/s | 647.0214 | 647.5 |  | 651.4434
| T_hot_set_REC/EH | Design hot temperature REC/EH | C | 550 | 550 |  | 550
| T_cold_set_REC/EH | T_cold_set_REC/EH | C | 290 | 290 |  | 290
| Q_name_EH | Design thermal power EH | MW | 0 | 0 | 0 | NA
| EH_eff_design | Design EH efficiency | % | 95 | 95 | 95 | NA
| m_flow_EH_des | Design EH mass flow rate | kg/s | 0 | 0 |  | NA
| P_name_EH | Design electrical power EH | MW | 0 | 0 | 0 | NA
| EH_W_min | Mimum power to run EH | MW | 0 | 0 |  | NA
| t_storage | TES hours | h | 10 | 10 | 10 | 10
| H_storage | Height of the TES tank | m | 9 |  |  | 12
| D_storage | Diameter of the TES tank | m | 29
| A_surf_TES | Surface losses area TES | m2 | 1508
| E_max | Maximum Energy that can be stored in the TES | MWh | 1274.5 | 1275.5 | 1275.5102 | 1274.5102
| Q_flow_des | Design thermal power to PB | MW | 127.45 | 127.56 | 127.551 | 127.45
| eta_blk_des | Design NET Efficiency of the PB | % | 39.2 | 39.2 | 39.3865 | 39.2307
| TIT | Turbine Inlet Temperature | C | 540
| T_hot_MS | Molten Salt Hot Temperature - PB | C | 550 | 550 | 550 | 550
| T_return_MS | Molten Salt Cold Temperature - PB | C | 290 | 290 | 290 | 290
| T_amb_PB | Design ambient temperature - PB | C | 30 | 30 | 30 | 30
| P_gross | Design gross electrical power - PB | MW | 52.52 | 52.52 | 52.7709 | 52.521
| P_net | Design net electrical power - PB | MW | 50 | 50 | 50.2379 | 50
| PV_P_AC | Design AC Power - PV | MW | 75 | 75.09 | 75 | 75
| PV_P_DC | Design DC Power - PV | MW | 97.5 | 97.7 | 97.5 | 97.5
| PV_r_DCAC | DC-to-AC ratio | - | 1.3 | 1.301 | 1.3 | 1.3
| A_PV_field | Area of the PV field | m2 | 541666.6667 | 542810 | 541666.6667 | 541666
| A_land_PV_tot | Total land occupied by the PV plant | m2 | 2031253.5 | 2035538 | 2031250 | 2031250
| PV_GCR | GCR | - | 0.4 | 0.4 | 0.4 | 0.4
| PV_tilt | Design tilt PV | deg | 37 | 37 | 37 | 37
| PV_azimuth | Design azimuth PV | deg | 180 | 0 | 0 | 180
| eta_inv | Inverter design efficiency | % | 98 | 95 | 95 | 95
| P_max | Maximum power injectable to the grid | MW | 50 | 50 | 50 | 50
| BESS_h | BESS hours of storage | h | 2 | 2 | 2 | 2
| P_BESS | Design power BESS | MW | 25 | 25 | 25 | 25
| E_BESS | Energy storage Capacity - BESS | MWh | 50 | 62.5 | 62.5 | 62.5
|  | Annual BESS cycles |  | 332 | 263 | 255.2041
| N_cycle_max | Maximum cycle per BESS | - | 2000 | 2000 | 2000
| N_replacement | Number of replacements BESS | - | 2 | 3 | 3 | 3
Note on G55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 3 times energy storage costs (3 replacements) times 1.13 for contingency and EPC indirect costs
Note on H14: Lorenzo Pilotti: difference due to the linear approximation of the cost function
Note on H15: Lorenzo Pilotti: difference due to the linearization of the size effect on efficiency
Note on H38: Lorenzo Pilotti: difference due to the linearization of PB investment cost function
Note on H42: Lorenzo Pilotti: Different because the PB size is not exactly 50 MW (see comment below)
Note on H55: Lorenzo Pilotti: replacement cost computed considering 3 replacements and the total BESS capacity (62.5 MWh)
Note on H72: Lorenzo Pilotti: Small difference due to the linear approximation of the SF model (see page "5 - Solar Field Design")
Note on H93: Lorenzo Pilotti: PB size is not exactly 50 MW as I've fixed the SM and hence the PB input size (127.55 MW). According to our model such input size corresponds to a nominal output of 50.24 MW, because the linearization of the correlation between PB size and its nominal efficiency
Note on J59: Lorenzo Pilotti: TAC check with formula

## 2.1 - Output Operation - MoSES
Hours | DNI | GHI | DHI | Wspd | T_amb | Q_in_SF | Q_out_SF | Q_def_SF | Q_out_rec | PV_AC_tot | PV_AC_waste | PV_AC_toBESS | PV_AC_togrid | PV_AC_toEH | P_in_EH | Q_out_EH | Q_in_PB | P_net_PB | TES_ch | TES_disch | TES_SOC | TES_SOC_normalized | BESS_ch | BESS_disch | BESS_SOC | BESS_SOC_normalized | P_injected_to_grid | Legend
h | W/m2 | W/m2 | W/m2 | m/s | C | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MWh | % | MW | MW | MWh | % | MW | Symbol | Description | Unit
0 | 0 | 0 | 0 | 2.0149 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.2552 | 50% | 0 | 0 | 25 | 50% | 0 | DNI | Direct Normal Irradiance | W/m2
1 | 0 | 0 | 0 | 1.0074 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.2552 | 50% | 0 | 25 | 0 | 0% | 25 | GHI | Global Horizontal Irradiance | W/m2
2 | 0 | 0 | 0 | 1.8134 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.0989 | 27.1 | 0 | 69.0989 | 573.8458 | 45.02% | 0 | 0 | 0 | 0% | 27.1 | DHI | Diffuse Horizontal Irradiance | W/m2
3 | 0 | 0 | 0 | 1.4104 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1902 | 26.7 | 0 | 68.1902 | 511.2935 | 40.12% | 0 | 0 | 0 | 0% | 26.7 | Wspd | Wind Speed | m/s
4 | 0 | 0 | 0 | 2.4178 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.6515 | 26.9 | 0 | 68.6515 | 448.2882 | 35.17% | 0 | 0 | 0 | 0% | 26.9 | T_amb | Ambient Temperature | C
5 | 0 | 0 | 0 | 3.6268 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2383 | 27.6 | 0 | 70.2383 | 383.6446 | 30.1% | 0 | 0 | 0 | 0% | 27.6 | defocus | Boolean - 1 if defocus SF | -
6 | 0 | 0 | 0 | 3.0223 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.0071 | 27.5 | 0 | 70.0071 | 319.2287 | 25.05% | 0 | 0 | 0 | 0% | 27.5 | eta_opt_SF | Solar Field Efficiency | %
7 | 0 | 0 | 0 | 1.6119 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.012 | 28.4 | 0 | 72.012 | 252.6028 | 19.82% | 0 | 0 | 0 | 0% | 28.4 | Q_in_SF | Power Input Solar Field | MW
8 | 154 | 18 | 8 | 1.4104 | 4.6 | 77.5109 | 0 | 0 | 0 | 1.8686 | 0 | 0 | 1.8686 | 0 | 0 | 0 | 72.9742 | 28.8314 | 0 | 72.9742 | 184.9018 | 14.51% | 0 | 0 | 0 | 0% | 30.7 | Q_out_SF | Power Output Solar Field | MW
9 | 699 | 158 | 31 | 0.60446 | 9.5 | 351.8189 | 172.9143 | 0 | 144.3449 | 37.0262 | 2.2631 | 0 | 34.7631 | 0 | 0 | 0 | 0 | 0 | 144.3449 | 0 | 324.2306 | 25.44% | 0 | 0 | 0 | 0% | 32.5 | eta_rec | Receiver Efficiency | %
10 | 873 | 324 | 42 | 0.40297 | 14.6 | 439.3961 | 248.0842 | 0 | 214.5911 | 90.794 | 3.797 | 25 | 61.997 | 0 | 0 | 0 | 0 | 0 | 214.5911 | 0 | 531.3645 | 41.69% | 19.175 | 0 | 19.1794 | 38.36% | 33.2 | eta_th_rec | Thermal Receiver Efficiency | %
11 | 945 | 454 | 47 | 1.6119 | 16.7 | 475.6349 | 285.4391 | 0 | 249.1504 | 116.1 | 16.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 249.1504 | 0 | 771.8567 | 60.56% | 19.175 | 0 | 38.3589 | 76.72% | 33.9 | SF_on | Boolean - 1 if SF is on | -
12 | 974 | 529 | 49 | 5.0372 | 17.5 | 490.2311 | 299.6219 | 0 | 261.2222 | 116.2 | 26.026 | 15.174 | 75 | 0 | 0 | 0 | 0 | 0 | 261.2222 | 0 | 1024.0012 | 80.34% | 11.6384 | 0 | 50 | 100% | 33.8 | Wspd_Ht | Wind Speed at the tower height | m/s
13 | 979 | 543 | 49 | 6.4476 | 18.5 | 492.7477 | 297.6439 | 0 | 258.5385 | 118 | 43 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 258.5385 | 0 | 1273.5553 | 99.93% | 0 | 0 | 50 | 100% | 32 | Q_rec | Receiver Output Power | MW
14 | 959 | 494 | 48 | 6.2461 | 19.2 | 482.6814 | 0 | 278.8161 | 0 | 118.7 | 43.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.5553 | 99.93% | 0 | 0 | 50 | 100% | 31.3 | T_REC_hot | Hot temperature Receiver | C
15 | 907 | 387 | 44 | 8.0595 | 18.9 | 456.5089 | 0 | 232.5018 | 0 | 111.6161 | 39.8581 | 0 | 71.7581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.5553 | 99.93% | 0 | 0 | 50 | 100% | 31.9 | T_REC_cold | Cold temperature Receiver | C
16 | 788 | 235 | 36 | 7.6565 | 18.3 | 396.6141 | 0 | 156.0915 | 0 | 66.0594 | 15.2297 | 0 | 50.8297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.5553 | 99.93% | 0 | 0 | 50 | 100% | 35.6 | m_flow_rec | Mass flow rate Receiver | kg/s
17 | 440 | 68 | 18 | 6.0446 | 16.1 | 221.4597 | 0 | 0 | 0 | 10.3223 | 0 | 0 | 10.3223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.5553 | 99.93% | 0 | 25 | 24.998 | 50% | 35.3223 | waste_extra_PV | Power extra PV - wasted | MW
18 | 1 | 0 | 0 | 2.6193 | 12.1 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.5553 | 99.93% | 0 | 24.9961 | 0 | 0% | 24.9961 | W_heater | Power to EH | MW
19 | 0 | 0 | 0 | 0.40297 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.954 | 39.7 | 0 | 98.954 | 1175.5288 | 92.23% | 0 | 0 | 0 | 0% | 39.7 | Q_out_heater | Electric Heater Output Power | MW
20 | 0 | 0 | 0 | 1.4104 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9975 | 38.5 | 0 | 95.9975 | 1080.9431 | 84.81% | 0 | 0 | 0 | 0% | 38.5 | eta_heater | Efficiency of the Electric Heater | %
21 | 0 | 0 | 0 | 2.2164 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2872 | 35.7 | 0 | 89.2872 | 994.2614 | 78.01% | 0 | 0 | 0 | 0% | 35.7 | Q_loss_heater | Losses Heater | MW
22 | 0 | 0 | 0 | 2.8208 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1532 | 32.3 | 0 | 81.1532 | 917.2675 | 71.97% | 0 | 0 | 0 | 0% | 32.3 | EH_on | Boolean - 1 if EH is on | -
23 | 0 | 0 | 0 | 3.4253 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.977 | 29.7 | 0 | 74.977 | 847.4191 | 66.49% | 0 | 0 | 0 | 0% | 29.7 | m_flow_heater | Mass flow rate EH | kg/s
24 | 0 | 0 | 0 | 4.2312 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.1989 | 28 | 0 | 71.1989 | 781.7149 | 61.33% | 0 | 0 | 0 | 0% | 28 | T_EH_hot | Hot temperature EH | C
25 | 0 | 0 | 0 | 2.4178 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8242 | 27.4 | 0 | 69.8242 | 717.4627 | 56.29% | 0 | 0 | 0 | 0% | 27.4 | T_EH_cold | Cold temperature EH | C
26 | 0 | 0 | 0 | 2.2164 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.3586 | 27.2 | 0 | 69.3586 | 653.6638 | 51.29% | 0 | 0 | 0 | 0% | 27.2 | m_flow_toTES_hot | Mass flow rate to the hot TES | kg/s
27 | 0 | 0 | 0 | 4.8357 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.086 | 28.4 | 0 | 72.086 | 586.9519 | 46.05% | 0 | 0 | 0 | 0% | 28.4 | T_toTES_hot | Temperature to the hot TES | C
28 | 0 | 0 | 0 | 4.4327 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1532 | 32.3 | 0 | 81.1532 | 509.8842 | 40.01% | 0 | 0 | 0 | 0% | 32.3 | T_TES_hot | Average temperature of the hot TES | C
29 | 0 | 0 | 0 | 3.6268 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.057 | 37.7 | 0 | 94.057 | 417.4342 | 32.75% | 0 | 0 | 0 | 0% | 37.7 | m_flow_TES_hot | Mass flow rate from the hot TES | kg/s
30 | 0 | 0 | 0 | 5.8431 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.1076 | 42.3 | 0 | 105.1076 | 311.8572 | 24.47% | 0 | 0 | 0 | 0% | 42.3 | m_flow_toTES_cold | Mass flow rate to the cold TES | kg/s
31 | 0 | 0 | 0 | 5.0372 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.2579 | 46.1 | 0 | 114.2579 | 195.3401 | 15.33% | 0 | 0 | 0 | 0% | 46.1 | T_toTES_cold | Temperature to the cold TES | C
32 | 154 | 18 | 8 | 5.8431 | 7.7 | 77.5109 | 0 | 0 | 0 | 1.8273 | 0 | 0 | 1.8273 | 0 | 0 | 0 | 71.7663 | 28.2504 | 0 | 71.7663 | 128.9074 | 10.11% | 0 | 0 | 0 | 0% | 30.0777 | T_TES_cold | Average temperature of the cold TES | C
33 | 705 | 159 | 31 | 1.6119 | 10.9 | 354.8388 | 174.7914 | 0 | 145.7555 | 35.037 | 0 | 0 | 35.037 | 0 | 0 | 0 | 0 | 0 | 145.7555 | 0 | 266.8653 | 20.94% | 0 | 0 | 0 | 0% | 35.037 | m_flow_TES_cold | Mass flow rate from the cold TES | kg/s
34 | 879 | 327 | 42 | 2.0149 | 14.6 | 442.416 | 250.2622 | 0 | 216.0178 | 79.13 | 0 | 15.665 | 63.465 | 0 | 0 | 0 | 0 | 0 | 216.0178 | 0 | 471.3264 | 36.98% | 12.015 | 0 | 12.0195 | 24.04% | 47.8 | L_HT | State of Charge TES - Level HT | %
35 | 952 | 458 | 48 | 1.8134 | 17.2 | 479.1582 | 287.7843 | 0 | 251.3013 | 102.4 | 2.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 251.3013 | 0 | 709.1834 | 55.64% | 19.175 | 0 | 31.2017 | 62.4% | 47.6 | L_CT | Level Cold Tank | %
36 | 980 | 534 | 51 | 2.8208 | 18.4 | 493.251 | 301.6552 | 0 | 263.9147 | 103.5 | 4.0003 | 24.4997 | 75 | 0 | 0 | 0 | 0 | 0 | 263.9147 | 0 | 958.9792 | 75.24% | 18.7913 | 0 | 50 | 100% | 46.5 | Q_losses_HT | Losses Hot Tank | MW
37 | 976 | 546 | 53 | 5.2387 | 18.2 | 491.2378 | 296.8478 | 0 | 258.5389 | 104.9 | 29.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 258.5389 | 0 | 1203.6866 | 94.44% | 0 | 0 | 50 | 100% | 45.1 | Q_losses_CT | Losses Cold Tank | MW
38 | 947 | 495 | 53 | 5.0372 | 18.6 | 476.6416 | 160.4826 | 114.9542 | 138.9543 | 105.7 | 30.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 138.9543 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.3 | Q_flow_PB | Thermal Power to the PB | MW
39 | 854 | 377 | 50 | 5.2387 | 18.6 | 429.833 | 0 | 218.9013 | 0 | 91.6904 | 23.4952 | 0 | 68.1952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.7 | m_flow_PB | Molten salt Mass flow rate to the PB | kg/s
40 | 729 | 229 | 44 | 4.8357 | 17.6 | 366.9184 | 0 | 144.2963 | 0 | 49.9042 | 1.2021 | 0 | 48.7021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.5 | T_toTES_MH_cold | Return temperature Molten Salt - PB | C
41 | 376 | 67 | 23 | 3.4253 | 15.7 | 189.2473 | 0 | 0 | 0 | 10.1658 | 0 | 0 | 10.1658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9945 | 49.99% | 35.1658 | PB_on | Boolean - 1 if PB is on | -
42 | 1 | 1 | 0 | 5.2387 | 11.6 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.4117 | 24.011 | 0 | 62.4117 | 1217.443 | 95.52% | 0 | 24.989 | 0 | 0% | 49 | PV_share | PV share of the total production | %
43 | 0 | 0 | 0 | 4.2312 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1807 | 48.5 | 0 | 120.1807 | 1094.2123 | 85.85% | 0 | 0 | 0 | 0% | 48.5 | BESS_share | BESS share of the total production | %
44 | 0 | 0 | 0 | 5.0372 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.9038 | 45.5 | 0 | 112.9038 | 979.617 | 76.86% | 0 | 0 | 0 | 0% | 45.5 | F_prod | PB share of the total production | %
45 | 0 | 0 | 0 | 6.0446 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.044 | 41.4 | 0 | 103.044 | 876.7325 | 68.79% | 0 | 0 | 0 | 0% | 41.4 | W_net_CSP | Net CSP electrical power production | MW
46 | 0 | 0 | 0 | 6.0446 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1293 | 37.7 | 0 | 94.1293 | 784.3743 | 61.54% | 0 | 0 | 0 | 0% | 37.7 | W_net_PV | Net PV electrical power production | MW
47 | 0 | 0 | 0 | 6.0446 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1697 | 34.4 | 0 | 86.1697 | 701.3379 | 55.03% | 0 | 0 | 0 | 0% | 34.4 | W_BESS | Net BESS electrical power production | MW
48 | 0 | 0 | 0 | 5.4401 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8533 | 32.6 | 0 | 81.8533 | 623.4448 | 48.92% | 0 | 0 | 0 | 0% | 32.6 | W_net_tot | Net total electrical power production | MW
49 | 0 | 0 | 0 | 6.2461 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7 | 31.7 | 0 | 79.7 | 548.0831 | 43% | 0 | 0 | 0 | 0% | 31.7 | eff_PB | Power block efficiency | %
50 | 0 | 0 | 0 | 5.2387 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4181 | 31.6 | 0 | 79.4181 | 472.9882 | 37.11% | 0 | 0 | 0 | 0% | 31.6 | W_PV_to_BESS | PV to BESS | MW
51 | 0 | 0 | 0 | 4.8357 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3389 | 32.4 | 0 | 81.3389 | 395.618 | 31.04% | 0 | 0 | 0 | 0% | 32.4 | W_grid_to_BESS | Grid to BESS | MW
52 | 0 | 0 | 0 | 5.8431 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.242 | 35.7 | 0 | 89.242 | 308.7849 | 24.23% | 0 | 0 | 0 | 0% | 35.7 | BESS_SOC | BESS state of charge | %
53 | 0 | 0 | 0 | 5.6416 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4991 | 40.8 | 0 | 101.4991 | 207.4278 | 16.28% | 0 | 0 | 0 | 0% | 40.8 | BESS_DOD | BESS DOD | %
54 | 0 | 0 | 0 | 5.6416 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7885 | 45.5 | 0 | 112.7885 | 92.5831 | 7.264% | 0 | 0 | 0 | 0% | 45.5 | BESS_N_cycles | Number of cycle - BESS | -
55 | 0 | 0 | 0 | 5.0372 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5831 | 7.264% | 0 | 0 | 0 | 0% | 0 | V_BESS | BESS output Voltage | V
56 | 8 | 9 | 8 | 5.2387 | 4.3 | 4.0265 | 0 | 0 | 0 | 0.11432 | 0 | 0 | 0.11432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5831 | 7.264% | 0 | 0 | 0 | 0% | 0.11432 | I_BESS | BESS output Current | A
57 | 599 | 148 | 38 | 2.8208 | 7.1 | 301.4871 | 148.8577 | 0 | 121.016 | 32.1781 | 0 | 0 | 32.1781 | 0 | 0 | 0 | 0 | 0 | 121.016 | 0 | 208.4348 | 16.35% | 0 | 0 | 0 | 0% | 32.1781 | E_BESS | Energy stored in the BESS | MWh
58 | 788 | 314 | 58 | 8.261 | 10.3 | 396.6141 | 224.798 | 0 | 189.1186 | 75.9254 | 0 | 13.2127 | 62.7127 | 0 | 0 | 0 | 0 | 0 | 189.1186 | 0 | 389.4829 | 30.56% | 10.1341 | 0 | 10.1393 | 20.28% | 49.5 | eta_BESS_RT | Round trip BESS Efficiency | %
59 | 835 | 439 | 76 | 10.4773 | 11.7 | 420.27 | 252.631 | 0 | 213.6264 | 101 | 1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 213.6264 | 0 | 593.9929 | 46.61% | 19.175 | 0 | 29.3242 | 58.65% | 49
60 | 417 | 400 | 191 | 7.858 | 12.5 | 209.8834 | 128.4441 | 0 | 99.2551 | 71.4341 | 0 | 11.867 | 59.567 | 0 | 0 | 0 | 0 | 0 | 99.2551 | 0 | 689.0124 | 54.06% | 9.102 | 0 | 38.4309 | 76.86% | 47.7
61 | 540 | 454 | 178 | 9.6714 | 12.6 | 271.7914 | 164.3127 | 0 | 131.7031 | 93.2122 | 8.3303 | 15.0758 | 69.8061 | 0 | 0 | 0 | 0 | 0 | 131.7031 | 0 | 815.0952 | 63.95% | 11.5631 | 0 | 50 | 100% | 46.4
62 | 525 | 425 | 172 | 7.455 | 13.1 | 264.2416 | 152.7741 | 0 | 122.3527 | 84.0606 | 19.0303 | 0 | 65.0303 | 0 | 0 | 0 | 0 | 0 | 122.3527 | 0 | 932.2266 | 73.14% | 0 | 0 | 50 | 100% | 46
63 | 464 | 297 | 119 | 5.8431 | 12.9 | 233.5393 | 118.9394 | 0 | 91.8053 | 52.4675 | 2.9337 | 0 | 49.5337 | 0 | 0 | 0 | 0 | 0 | 91.8053 | 0 | 1020.1141 | 80.04% | 0 | 0 | 50 | 100% | 46.6
64 | 514 | 206 | 80 | 5.8431 | 12.8 | 258.7051 | 101.6829 | 0 | 75.361 | 41.178 | 0 | 0 | 41.178 | 0 | 0 | 0 | 0 | 0 | 75.361 | 0 | 1092.2591 | 85.7% | 0 | 7.822 | 42.1752 | 84.35% | 49
65 | 140 | 63 | 42 | 8.0595 | 11.6 | 70.4644 | 0 | 0 | 0 | 7.8158 | 0 | 0 | 7.8158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092.2591 | 85.7% | 0 | 25 | 17.1657 | 34.33% | 32.8158
66 | 0 | 1 | 0 | 6.0446 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5567 | 32.8403 | 0 | 82.5567 | 1013.7277 | 79.54% | 0 | 17.1597 | 0 | 0% | 50
67 | 0 | 0 | 0 | 5.0372 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1191 | 49.7 | 0 | 123.1191 | 886.9416 | 69.59% | 0 | 0 | 0 | 0% | 49.7
68 | 0 | 0 | 0 | 5.4401 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.5787 | 46.6 | 0 | 115.5787 | 769.1534 | 60.35% | 0 | 0 | 0 | 0% | 46.6
69 | 0 | 0 | 0 | 4.2312 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.4186 | 42.4 | 0 | 105.4186 | 663.3979 | 52.05% | 0 | 0 | 0 | 0% | 42.4
70 | 0 | 0 | 0 | 4.4327 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2388 | 38.6 | 0 | 96.2388 | 568.4426 | 44.6% | 0 | 0 | 0 | 0% | 38.6
71 | 0 | 0 | 0 | 4.4327 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2767 | 35.3 | 0 | 88.2767 | 482.7793 | 37.88% | 0 | 0 | 0 | 0% | 35.3
72 | 0 | 0 | 0 | 2.6193 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2168 | 33.6 | 0 | 84.2168 | 401.9936 | 31.54% | 0 | 0 | 0 | 0% | 33.6
73 | 0 | 0 | 0 | 2.0149 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0618 | 32.7 | 0 | 82.0618 | 323.7649 | 25.4% | 0 | 0 | 0 | 0% | 32.7
74 | 0 | 0 | 0 | 2.4178 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8184 | 32.6 | 0 | 81.8184 | 245.7991 | 19.29% | 0 | 0 | 0 | 0% | 32.6
75 | 0 | 0 | 0 | 2.2164 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4947 | 33.3 | 0 | 83.4947 | 165.8056 | 13.01% | 0 | 0 | 0 | 0% | 33.3
76 | 0 | 0 | 0 | 2.6193 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9906 | 23.1094 | 0 | 59.9906 | 110.9148 | 8.703% | 0 | 0 | 0 | 0% | 23.1094
77 | 0 | 0 | 0 | 4.2312 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.9148 | 8.703% | 0 | 0 | 0 | 0% | 0
78 | 0 | 0 | 0 | 5.0372 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.9148 | 8.703% | 0 | 0 | 0 | 0% | 0
79 | 0 | 0 | 0 | 4.4327 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.9148 | 8.703% | 0 | 0 | 0 | 0% | 0
80 | 97 | 16 | 10 | 4.8357 | 4.4 | 48.8218 | 0 | 0 | 0 | 0.86171 | 0 | 0 | 0.86171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.9148 | 8.703% | 0 | 0 | 0 | 0% | 0.86171
81 | 580 | 156 | 47 | 3.2238 | 6.5 | 291.9241 | 144.4846 | 0 | 116.7619 | 32.7606 | 0 | 0 | 32.7606 | 0 | 0 | 0 | 0 | 0 | 116.7619 | 0 | 222.6251 | 17.47% | 0 | 0 | 0 | 0% | 32.7606
82 | 806 | 330 | 65 | 1.8134 | 9 | 405.6738 | 230.4086 | 0 | 197.6438 | 75.8126 | 0 | 12.9563 | 62.8563 | 0 | 0 | 0 | 0 | 0 | 197.6438 | 0 | 411.7181 | 32.3% | 9.9375 | 0 | 9.944 | 19.89% | 49.9
83 | 898 | 456 | 62 | 2.0149 | 11.5 | 451.979 | 271.9369 | 0 | 236.2464 | 100.7 | 0.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 236.2464 | 0 | 637.7435 | 50.04% | 19.175 | 0 | 29.1316 | 58.26% | 49.3
84 | 944 | 535 | 61 | 2.8208 | 12.5 | 475.1316 | 290.9824 | 0 | 253.9417 | 102.5 | 2.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 253.9417 | 0 | 880.6988 | 69.1% | 19.175 | 0 | 48.3192 | 96.64% | 47.5
85 | 944 | 547 | 61 | 3.6268 | 13.3 | 475.1316 | 287.3865 | 0 | 250.2374 | 103.9 | 28.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 250.2374 | 0 | 1120.11 | 87.89% | 0 | 0 | 48.3192 | 96.64% | 46.1
86 | 927 | 501 | 60 | 3.8283 | 14 | 466.5752 | 253.7357 | 16.1841 | 219.6793 | 104.5 | 29.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 219.6793 | 0 | 1274.5104 | 100% | 0 | 0 | 48.3192 | 96.64% | 45.5
87 | 883 | 397 | 53 | 4.0297 | 14.7 | 444.4293 | 0 | 226.3767 | 0 | 96.4885 | 25.2942 | 0 | 71.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.3192 | 96.64% | 45.9
88 | 761 | 243 | 44 | 5.6416 | 14.3 | 383.0245 | 0 | 150.4905 | 0 | 54.3903 | 2.8951 | 0 | 51.4951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.3192 | 96.64% | 48.6
89 | 407 | 72 | 23 | 5.8431 | 12.2 | 204.8502 | 0 | 0 | 0 | 11.6228 | 0 | 0 | 11.6228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.3066 | 46.61% | 36.6228
90 | 0 | 1 | 1 | 5.0372 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.4622 | 26.3052 | 0 | 67.4622 | 1212.5653 | 95.14% | 0 | 23.2948 | 0 | 0% | 49.6
91 | 0 | 0 | 0 | 0.40297 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.0683 | 48.9 | 0 | 121.0683 | 1088.1456 | 85.38% | 0 | 0 | 0 | 0% | 48.9
92 | 0 | 0 | 0 | 1.8134 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.7181 | 46.3 | 0 | 114.7181 | 971.2275 | 76.2% | 0 | 0 | 0 | 0% | 46.3
93 | 0 | 0 | 0 | 2.2164 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.5486 | 42.9 | 0 | 106.5486 | 864.0423 | 67.79% | 0 | 0 | 0 | 0% | 42.9
94 | 0 | 0 | 0 | 4.2312 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8442 | 39.7 | 0 | 98.8442 | 765.9144 | 60.09% | 0 | 0 | 0 | 0% | 39.7
95 | 0 | 0 | 0 | 3.2238 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.898 | 36.4 | 0 | 90.898 | 677.1754 | 53.13% | 0 | 0 | 0 | 0% | 36.4
96 | 0 | 0 | 0 | 3.2238 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1544 | 34 | 0 | 85.1544 | 595.2409 | 46.7% | 0 | 0 | 0 | 0% | 34
97 | 0 | 0 | 0 | 1.6119 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2417 | 32.8 | 0 | 82.2417 | 516.7362 | 40.54% | 0 | 0 | 0 | 0% | 32.8
98 | 0 | 0 | 0 | 0.60446 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0192 | 32.3 | 0 | 81.0192 | 439.6434 | 34.5% | 0 | 0 | 0 | 0% | 32.3
99 | 0 | 0 | 0 | 1.8134 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.784 | 32.2 | 0 | 80.784 | 362.8104 | 28.47% | 0 | 0 | 0 | 0% | 32.2
100 | 0 | 0 | 0 | 3.6268 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7018 | 33 | 0 | 82.7018 | 283.6806 | 22.26% | 0 | 0 | 0 | 0% | 33
101 | 0 | 0 | 0 | 2.8208 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7077 | 35.1 | 0 | 87.7077 | 198.459 | 15.57% | 0 | 0 | 0 | 0% | 35.1
102 | 0 | 0 | 0 | 1.6119 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0045 | 37.3 | 0 | 93.0045 | 107.0252 | 8.397% | 0 | 0 | 0 | 0% | 37.3
103 | 0 | 0 | 0 | 2.4178 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.0252 | 8.397% | 0 | 0 | 0 | 0% | 0
104 | 156 | 18 | 8 | 3.0223 | 2 | 78.5175 | 0 | 0 | 0 | 1.175 | 0 | 0 | 1.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.0252 | 8.397% | 0 | 0 | 0 | 0% | 1.175
105 | 694 | 159 | 32 | 0.80595 | 5.8 | 349.3023 | 173.3153 | 0 | 144.6453 | 35.1439 | 0 | 0 | 35.1439 | 0 | 0 | 0 | 0 | 0 | 144.6453 | 0 | 245.2699 | 19.24% | 0 | 0 | 0 | 0% | 35.1439
106 | 871 | 329 | 43 | 1.4104 | 10.8 | 438.3894 | 249.5261 | 0 | 215.5467 | 82.8118 | 0 | 19.4559 | 63.3559 | 0 | 0 | 0 | 0 | 0 | 215.5467 | 0 | 451.2785 | 35.41% | 14.9227 | 0 | 14.9345 | 29.87% | 43.9
107 | 941 | 461 | 48 | 1.4104 | 13.6 | 473.6217 | 285.2295 | 0 | 249.0157 | 106.5 | 6.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 249.0157 | 0 | 689.2752 | 54.08% | 19.175 | 0 | 34.1247 | 68.25% | 43.5
108 | 968 | 537 | 52 | 3.6268 | 13.8 | 487.2112 | 298.6136 | 0 | 260.7638 | 107.2 | 11.5185 | 20.6815 | 75 | 0 | 0 | 0 | 0 | 0 | 260.7638 | 0 | 938.5001 | 73.64% | 15.8627 | 0 | 50 | 100% | 42.8
109 | 977 | 553 | 52 | 4.0297 | 14.4 | 491.7411 | 297.5975 | 0 | 259.6808 | 108.7 | 33.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 259.6808 | 0 | 1186.6899 | 93.11% | 0 | 0 | 50 | 100% | 41.3
110 | 957 | 505 | 51 | 5.0372 | 15.3 | 481.6747 | 141.4789 | 137.3753 | 122.6091 | 109.8 | 34.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 122.6091 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.2
111 | 910 | 400 | 47 | 6.8506 | 15.4 | 458.0188 | 0 | 233.3576 | 0 | 106.5796 | 33.2398 | 0 | 73.3398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.1
112 | 798 | 248 | 39 | 5.2387 | 15.2 | 401.6473 | 0 | 157.7793 | 0 | 62.4883 | 9.9941 | 0 | 52.4941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
113 | 463 | 77 | 21 | 5.8431 | 13.1 | 233.036 | 0 | 0 | 0 | 12.9302 | 0 | 0 | 12.9302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.984 | 49.97% | 37.9302
114 | 1 | 1 | 1 | 3.0223 | 9.2 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.968 | 0 | 0% | 24.968
115 | 0 | 0 | 0 | 1.4104 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.9426 | 44.3 | 0 | 109.9426 | 1163.3506 | 91.28% | 0 | 0 | 0 | 0% | 44.3
116 | 0 | 0 | 0 | 1.8134 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7887 | 43 | 0 | 106.7887 | 1055.9074 | 82.85% | 0 | 0 | 0 | 0% | 43
117 | 0 | 0 | 0 | 1.8134 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4742 | 40.8 | 0 | 101.4742 | 954.6911 | 74.91% | 0 | 0 | 0 | 0% | 40.8
118 | 0 | 0 | 0 | 1.8134 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2335 | 37.8 | 0 | 94.2335 | 862.0208 | 67.64% | 0 | 0 | 0 | 0% | 37.8
119 | 0 | 0 | 0 | 2.2164 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5992 | 34.6 | 0 | 86.5992 | 778.3715 | 61.07% | 0 | 0 | 0 | 0% | 34.6
120 | 0 | 0 | 0 | 3.6268 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.099 | 32.3 | 0 | 81.099 | 701.3131 | 55.03% | 0 | 0 | 0 | 0% | 32.3
121 | 0 | 0 | 0 | 5.0372 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9871 | 31 | 0 | 77.9871 | 627.8979 | 49.27% | 0 | 0 | 0 | 0% | 31
122 | 0 | 0 | 0 | 4.8357 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2949 | 30.3 | 0 | 76.2949 | 556.4162 | 43.66% | 0 | 0 | 0 | 0% | 30.3
123 | 0 | 0 | 0 | 4.0297 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.8126 | 30.1 | 0 | 75.8126 | 485.4745 | 38.09% | 0 | 0 | 0 | 0% | 30.1
124 | 0 | 0 | 0 | 5.0372 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0112 | 30.6 | 0 | 77.0112 | 413.1321 | 32.41% | 0 | 0 | 0 | 0% | 30.6
125 | 0 | 0 | 0 | 4.8357 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6585 | 31.7 | 0 | 79.6585 | 337.6946 | 26.5% | 0 | 0 | 0 | 0% | 31.7
126 | 0 | 0 | 0 | 2.6193 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2977 | 32.8 | 0 | 82.2977 | 259.118 | 20.33% | 0 | 0 | 0 | 0% | 32.8
127 | 0 | 0 | 0 | 2.4178 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9749 | 35.6 | 0 | 88.9749 | 172.4791 | 13.53% | 0 | 0 | 0 | 0% | 35.6
128 | 164 | 18 | 8 | 3.0223 | 5.4 | 82.5441 | 0 | 0 | 0 | 1.2084 | 0 | 0 | 1.2084 | 0 | 0 | 0 | 75.1482 | 29.8112 | 0 | 75.1482 | 102.1722 | 8.017% | 0 | 0 | 0 | 0% | 31.0195
129 | 717 | 161 | 31 | 1.6119 | 8.9 | 360.8786 | 179.5206 | 0 | 150.1376 | 35.8349 | 0 | 0 | 35.8349 | 0 | 0 | 0 | 0 | 0 | 150.1376 | 0 | 244.2187 | 19.16% | 0 | 0 | 0 | 0% | 35.8349
130 | 888 | 331 | 42 | 1.4104 | 13.3 | 446.9458 | 254.9653 | 0 | 220.609 | 88.3696 | 0 | 24.6848 | 63.6848 | 0 | 0 | 0 | 0 | 0 | 220.609 | 0 | 452.9387 | 35.54% | 18.9332 | 0 | 18.9509 | 37.9% | 39
131 | 958 | 465 | 48 | 1.8134 | 16.1 | 482.1781 | 290.6727 | 0 | 254.0365 | 111.5 | 11.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 254.0365 | 0 | 693.2848 | 54.4% | 19.175 | 0 | 38.1438 | 76.29% | 38.5
132 | 989 | 544 | 51 | 3.0223 | 17.1 | 497.7809 | 305.3463 | 0 | 267.2604 | 112.4 | 21.9566 | 15.4434 | 75 | 0 | 0 | 0 | 0 | 0 | 267.2604 | 0 | 946.1422 | 74.24% | 11.8451 | 0 | 50 | 100% | 37.6
133 | 991 | 560 | 52 | 1.4104 | 19 | 498.7875 | 302.0452 | 0 | 264.7779 | 114.2 | 39.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 264.7779 | 0 | 1196.6509 | 93.89% | 0 | 0 | 50 | 100% | 35.8
134 | 957 | 508 | 53 | 4.0297 | 19.1 | 481.6747 | 135.5419 | 143.5409 | 117.6768 | 114.9 | 39.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 117.6768 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.1
135 | 897 | 400 | 50 | 6.6491 | 18.6 | 451.4757 | 0 | 230.1062 | 0 | 108.625 | 36.5625 | 0 | 72.0625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.5
136 | 771 | 246 | 42 | 6.6491 | 17.6 | 388.0577 | 0 | 152.4432 | 0 | 63.4196 | 12.1598 | 0 | 51.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.1
137 | 432 | 76 | 23 | 3.0223 | 15.1 | 217.4331 | 0 | 0 | 0 | 12.6797 | 0 | 0 | 12.6797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9805 | 49.96% | 37.6797
138 | 1 | 1 | 1 | 5.8431 | 11.3 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.961 | 2.7756e-15 | 5.551e-15% | 24.961
139 | 0 | 0 | 0 | 2.0149 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0746 | 43.5 | 0 | 108.0746 | 1165.6709 | 91.46% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.5
140 | 0 | 0 | 0 | 1.2089 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8283 | 42.6 | 0 | 105.8283 | 1059.3893 | 83.12% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42.6
141 | 0 | 0 | 0 | 1.4104 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8533 | 39.7 | 0 | 98.8533 | 961.3064 | 75.43% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.7
142 | 0 | 0 | 0 | 3.2238 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2026 | 36.1 | 0 | 90.2026 | 873.4508 | 68.53% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.1
143 | 0 | 0 | 0 | 3.4253 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4947 | 33.3 | 0 | 83.4947 | 793.5702 | 62.26% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.3
144 | 0 | 0 | 0 | 1.2089 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6585 | 31.7 | 0 | 79.6585 | 718.2196 | 56.35% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.7
145 | 0 | 0 | 0 | 4.6342 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9748 | 31 | 0 | 77.9748 | 644.8181 | 50.59% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31
146 | 0 | 0 | 0 | 5.6416 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4996 | 30.8 | 0 | 77.4996 | 571.9615 | 44.88% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.8
147 | 0 | 0 | 0 | 3.0223 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8987 | 31.8 | 0 | 79.8987 | 496.2901 | 38.94% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.8
148 | 0 | 0 | 0 | 2.0149 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7895 | 34.7 | 0 | 86.7895 | 412.2902 | 32.35% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.7
149 | 0 | 0 | 0 | 1.2089 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0837 | 39 | 0 | 97.0837 | 316.0839 | 24.8% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39
150 | 0 | 0 | 0 | 1.8134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5678 | 42.1 | 0 | 104.5678 | 211.0256 | 16.56% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42.1
151 | 0 | 0 | 0 | 1.6119 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.5491 | 45 | 0 | 111.5491 | 97.5861 | 7.657% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 45
152 | 151 | 18 | 8 | 1.0074 | 3.4 | 76.0009 | 0 | 0 | 0 | 1.1293 | 0 | 0 | 1.1293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5861 | 7.657% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 1.1293
153 | 685 | 158 | 33 | 1.0074 | 7.6 | 344.7724 | 171.9635 | 0 | 143.2859 | 34.8012 | 0 | 0 | 34.8012 | 0 | 0 | 0 | 0 | 0 | 143.2859 | 0 | 234.5232 | 18.4% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.8012
154 | 860 | 326 | 45 | 1.4104 | 12 | 432.853 | 247.4982 | 0 | 213.6692 | 77.8969 | 0 | 15.3485 | 62.5485 | 0 | 0 | 0 | 0 | 0 | 213.6692 | 0 | 438.7251 | 34.42% | 11.7723 | 0 | 11.7849 | 23.57% | 47.2
155 | 933 | 458 | 50 | 1.4104 | 14.9 | 469.5951 | 283.3838 | 0 | 247.2735 | 102.7 | 2.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 247.2735 | 0 | 675.0423 | 52.96% | 19.175 | 0 | 30.9805 | 61.96% | 47.3
156 | 963 | 537 | 53 | 3.0223 | 16.2 | 484.6946 | 297.5825 | 0 | 260.0499 | 103.8 | 4.0295 | 24.7705 | 75 | 0 | 0 | 0 | 0 | 0 | 260.0499 | 0 | 923.5698 | 72.46% | 18.999 | 0 | 50 | 100% | 46.2
157 | 966 | 553 | 55 | 3.2238 | 16.3 | 486.2046 | 294.62 | 0 | 257.2352 | 104.9 | 29.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 257.2352 | 0 | 1169.4074 | 91.75% | 0 | 0 | 50 | 100% | 45.1
158 | 939 | 504 | 55 | 2.8208 | 17.4 | 472.615 | 161.8456 | 112.241 | 140.5403 | 105.8 | 30.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 140.5403 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.2
159 | 875 | 397 | 52 | 7.6565 | 16.9 | 440.4027 | 0 | 224.5667 | 0 | 98.5941 | 27.0471 | 0 | 71.5471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.5
160 | 745 | 244 | 44 | 8.0595 | 16.1 | 374.9715 | 0 | 147.3329 | 0 | 54.0897 | 3.0949 | 0 | 50.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.9
161 | 410 | 76 | 24 | 8.8654 | 14 | 206.3601 | 0 | 0 | 0 | 12.7525 | 0 | 0 | 12.7525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9769 | 49.95% | 37.7525
162 | 1 | 1 | 1 | 7.052 | 10.5 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.6378 | 25.0461 | 0 | 64.6378 | 1215.2782 | 95.35% | 0 | 24.9539 | 0 | 0% | 50
163 | 0 | 0 | 0 | 3.4253 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.7389 | 50 | 0 | 123.7389 | 1087.6832 | 85.34% | 0 | 0 | 0 | 0% | 50
164 | 0 | 0 | 0 | 4.0297 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.4706 | 47 | 0 | 116.4706 | 968.7827 | 76.01% | 0 | 0 | 0 | 0% | 47
165 | 0 | 0 | 0 | 3.8283 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5881 | 42.5 | 0 | 105.5881 | 862.7692 | 67.69% | 0 | 0 | 0 | 0% | 42.5
166 | 0 | 0 | 0 | 2.2164 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.656 | 39.2 | 0 | 97.656 | 766.1106 | 60.11% | 0 | 0 | 0 | 0% | 39.2
167 | 0 | 0 | 0 | 4.4327 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4475 | 36.2 | 0 | 90.4475 | 677.9582 | 53.19% | 0 | 0 | 0 | 0% | 36.2
168 | 0 | 0 | 0 | 3.4253 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3608 | 34.5 | 0 | 86.3608 | 594.5977 | 46.65% | 0 | 0 | 0 | 0% | 34.5
169 | 0 | 0 | 0 | 3.6268 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6901 | 33.8 | 0 | 84.6901 | 513.2484 | 40.27% | 0 | 0 | 0 | 0% | 33.8
170 | 0 | 0 | 0 | 3.2238 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9289 | 33.9 | 0 | 84.9289 | 431.594 | 33.86% | 0 | 0 | 0 | 0% | 33.9
171 | 0 | 0 | 0 | 3.0223 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7752 | 35.1 | 0 | 87.7752 | 346.4454 | 27.18% | 0 | 0 | 0 | 0% | 35.1
172 | 0 | 0 | 0 | 4.4327 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5606 | 39.2 | 0 | 97.5606 | 249.6668 | 19.59% | 0 | 0 | 0 | 0% | 39.2
173 | 0 | 0 | 0 | 3.8283 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.7098 | 46.3 | 0 | 114.7098 | 132.5624 | 10.4% | 0 | 0 | 0 | 0% | 46.3
174 | 0 | 0 | 0 | 4.2312 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.7708 | 22.5935 | 0 | 58.7708 | 78.8384 | 6.186% | 0 | 0 | 0 | 0% | 22.5935
175 | 0 | 0 | 0 | 5.4401 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8384 | 6.186% | 0 | 0 | 0 | 0% | 0
176 | 124 | 17 | 8 | 5.4401 | 2.8 | 62.4114 | 0 | 0 | 0 | 1.6454 | 0 | 0 | 1.6454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8384 | 6.186% | 0 | 0 | 0 | 0% | 1.6454
177 | 625 | 152 | 37 | 5.4401 | 5.7 | 314.5734 | 157.3287 | 0 | 127.6924 | 33.774 | 0 | 0 | 33.774 | 0 | 0 | 0 | 0 | 0 | 127.6924 | 0 | 201.5492 | 15.81% | 0 | 0 | 0 | 0% | 33.774
178 | 818 | 320 | 51 | 4.6342 | 9.3 | 411.7136 | 235.9755 | 0 | 201.7792 | 75.033 | 0 | 12.5165 | 62.5165 | 0 | 0 | 0 | 0 | 0 | 201.7792 | 0 | 395.4566 | 31.03% | 9.6002 | 0 | 9.6118 | 19.22% | 50
179 | 896 | 452 | 60 | 5.2387 | 10.9 | 450.9724 | 272.4436 | 0 | 235.4317 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 235.4317 | 0 | 621.7037 | 48.78% | 19.175 | 0 | 28.8102 | 57.62% | 50
180 | 932 | 531 | 62 | 3.8283 | 12 | 469.0918 | 288.2731 | 0 | 250.9901 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 250.9901 | 0 | 862.9022 | 67.7% | 19.175 | 0 | 48.0085 | 96.02% | 50
181 | 946 | 549 | 61 | 2.4178 | 13.3 | 476.1382 | 288.726 | 0 | 251.9547 | 100.4 | 22.8067 | 2.5933 | 75 | 0 | 0 | 0 | 0 | 0 | 251.9547 | 0 | 1105.0276 | 86.7% | 1.989 | 0 | 50 | 100% | 49.6
182 | 934 | 505 | 57 | 2.0149 | 14.5 | 470.0984 | 237.8 | 35.1075 | 206.6624 | 100.9 | 25.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 206.6624 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.1
183 | 871 | 399 | 55 | 5.8431 | 14.9 | 438.3894 | 0 | 223.6674 | 0 | 93.8969 | 22.1985 | 0 | 71.6985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.5
184 | 742 | 247 | 47 | 7.858 | 14 | 373.4615 | 0 | 146.7984 | 0 | 53.2499 | 1.625 | 0 | 51.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
185 | 428 | 80 | 25 | 7.455 | 11.9 | 215.4198 | 0 | 0 | 0 | 13.702 | 0 | 0 | 13.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9734 | 49.95% | 38.702
186 | 1 | 1 | 1 | 4.6342 | 9 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.6206 | 25.0531 | 0 | 64.6206 | 1215.289 | 95.35% | 0 | 24.9469 | 0 | 0% | 50
187 | 0 | 0 | 0 | 3.4253 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.7389 | 50 | 0 | 123.7389 | 1087.6835 | 85.34% | 0 | 0 | 0 | 0% | 50
188 | 0 | 0 | 0 | 2.0149 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.4611 | 49.5 | 0 | 122.4611 | 961.5233 | 75.44% | 0 | 0 | 0 | 0% | 49.5
189 | 0 | 0 | 0 | 2.0149 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.6243 | 44.6 | 0 | 110.6243 | 849.4776 | 66.65% | 0 | 0 | 0 | 0% | 44.6
190 | 0 | 0 | 0 | 2.6193 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9648 | 41 | 0 | 101.9648 | 747.6909 | 58.66% | 0 | 0 | 0 | 0% | 41
191 | 0 | 0 | 0 | 2.6193 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2663 | 37.8 | 0 | 94.2663 | 655.0127 | 51.39% | 0 | 0 | 0 | 0% | 37.8
192 | 0 | 0 | 0 | 2.8208 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4691 | 35.8 | 0 | 89.4691 | 567.9579 | 44.56% | 0 | 0 | 0 | 0% | 35.8
193 | 0 | 0 | 0 | 2.2164 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9655 | 35.2 | 0 | 87.9655 | 482.5602 | 37.86% | 0 | 0 | 0 | 0% | 35.2
194 | 0 | 0 | 0 | 4.6342 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5522 | 35 | 0 | 87.5522 | 397.7006 | 31.2% | 0 | 0 | 0 | 0% | 35
195 | 0 | 0 | 0 | 4.8357 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9602 | 36 | 0 | 89.9602 | 310.029 | 24.33% | 0 | 0 | 0 | 0% | 36
196 | 0 | 0 | 0 | 5.2387 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0926 | 39.8 | 0 | 99.0926 | 211.5039 | 16.59% | 0 | 0 | 0 | 0% | 39.8
197 | 0 | 0 | 0 | 5.0372 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.6822 | 46.7 | 0 | 115.6822 | 93.2219 | 7.314% | 0 | 0 | 0 | 0% | 46.7
198 | 0 | 0 | 0 | 4.4327 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2219 | 7.314% | 0 | 0 | 0 | 0% | 0
199 | 0 | 0 | 0 | 5.2387 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2219 | 7.314% | 0 | 0 | 0 | 0% | 0
200 | 152 | 17 | 7 | 6.0446 | 7.1 | 76.5042 | 0 | 0 | 0 | 1.6784 | 0 | 0 | 1.6784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2219 | 7.314% | 0 | 0 | 0 | 0% | 1.6784
201 | 686 | 157 | 31 | 5.6416 | 9.4 | 345.2757 | 173.1672 | 0 | 142.5204 | 35.1232 | 0 | 0 | 35.1232 | 0 | 0 | 0 | 0 | 0 | 142.5204 | 0 | 231.169 | 18.14% | 0 | 0 | 0 | 0% | 35.1232
202 | 867 | 327 | 42 | 1.4104 | 14.1 | 436.3762 | 250.73 | 0 | 216.6736 | 74.1894 | 0 | 12.0947 | 62.0947 | 0 | 0 | 0 | 0 | 0 | 216.6736 | 0 | 440.8896 | 34.59% | 9.2766 | 0 | 9.2892 | 18.58% | 50
203 | 933 | 458 | 48 | 2.0149 | 15.7 | 469.5951 | 284.0178 | 0 | 247.6557 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 247.6557 | 0 | 680.5983 | 53.4% | 19.175 | 0 | 28.4903 | 56.98% | 50
204 | 956 | 535 | 52 | 2.4178 | 17.5 | 481.1714 | 295.9888 | 0 | 258.7992 | 100.1 | 0.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 258.7992 | 0 | 931.0927 | 73.05% | 19.175 | 0 | 47.6914 | 95.38% | 49.9
205 | 953 | 550 | 55 | 6.6491 | 17.2 | 479.6615 | 291.0743 | 0 | 252.2712 | 100.9 | 22.8942 | 3.0058 | 75 | 0 | 0 | 0 | 0 | 0 | 252.2712 | 0 | 1175.2687 | 92.21% | 2.3055 | 0 | 50 | 100% | 49.1
206 | 926 | 502 | 55 | 7.455 | 17.2 | 466.0719 | 150.58 | 120.2961 | 129.3465 | 101.3 | 26.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 129.3465 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.7
207 | 882 | 402 | 50 | 7.2535 | 16.8 | 443.9259 | 0 | 226.645 | 0 | 94.8443 | 22.8722 | 0 | 71.9722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.1
208 | 773 | 252 | 41 | 8.0595 | 16 | 389.0643 | 0 | 153.0223 | 0 | 54.2171 | 2.1086 | 0 | 52.1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
209 | 483 | 84 | 23 | 8.0595 | 14.4 | 243.1023 | 0 | 0 | 0 | 15.0858 | 0 | 0 | 15.0858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9699 | 49.94% | 40.0858
210 | 1 | 1 | 1 | 2.0149 | 11.3 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.742 | 25.0602 | 0 | 64.742 | 1215.1706 | 95.34% | 0 | 24.9398 | 0 | 0% | 50
211 | 0 | 0 | 0 | 0.80595 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.7749 | 50 | 0 | 123.7749 | 1087.5354 | 85.33% | 0 | 0 | 0 | 0% | 50
212 | 0 | 0 | 0 | 3.6268 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.3348 | 49 | 0 | 121.3348 | 962.8189 | 75.54% | 0 | 0 | 0 | 0% | 49
213 | 0 | 0 | 0 | 2.4178 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.2636 | 44 | 0 | 109.2636 | 852.4901 | 66.89% | 0 | 0 | 0 | 0% | 44
214 | 0 | 0 | 0 | 3.2238 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.8394 | 40.5 | 0 | 100.8394 | 752.0999 | 59.01% | 0 | 0 | 0 | 0% | 40.5
215 | 0 | 0 | 0 | 4.8357 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8895 | 37.6 | 0 | 93.8895 | 659.9861 | 51.78% | 0 | 0 | 0 | 0% | 37.6
216 | 0 | 0 | 0 | 3.4253 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.242 | 35.7 | 0 | 89.242 | 573.2014 | 44.97% | 0 | 0 | 0 | 0% | 35.7
217 | 0 | 0 | 0 | 3.6268 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8107 | 35.1 | 0 | 87.8107 | 488.079 | 38.3% | 0 | 0 | 0 | 0% | 35.1
218 | 0 | 0 | 0 | 6.2461 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5952 | 35 | 0 | 87.5952 | 403.2259 | 31.64% | 0 | 0 | 0 | 0% | 35
219 | 0 | 0 | 0 | 5.6416 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7243 | 35.9 | 0 | 89.7243 | 315.8259 | 24.78% | 0 | 0 | 0 | 0% | 35.9
220 | 0 | 0 | 0 | 4.6342 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5711 | 40 | 0 | 99.5711 | 216.7117 | 17% | 0 | 0 | 0 | 0% | 40
221 | 0 | 0 | 0 | 4.0297 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.405 | 47 | 0 | 116.405 | 97.5648 | 7.655% | 0 | 0 | 0 | 0% | 47
222 | 0 | 0 | 0 | 2.4178 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5648 | 7.655% | 0 | 0 | 0 | 0% | 0
223 | 0 | 0 | 0 | 6.2461 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5648 | 7.655% | 0 | 0 | 0 | 0% | 0
224 | 154 | 18 | 8 | 4.2312 | 4.3 | 77.5109 | 0 | 0 | 0 | 1.836 | 0 | 0 | 1.836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5648 | 7.655% | 0 | 0 | 0 | 0% | 1.836
225 | 690 | 159 | 32 | 3.6268 | 8.2 | 347.289 | 174.6762 | 0 | 144.8663 | 35.4929 | 0 | 0 | 35.4929 | 0 | 0 | 0 | 0 | 0 | 144.8663 | 0 | 237.7614 | 18.66% | 0 | 0 | 0 | 0% | 35.4929
226 | 869 | 330 | 44 | 7.455 | 10.2 | 437.3828 | 251.9494 | 0 | 214.8662 | 80.8344 | 0 | 15.4172 | 65.4172 | 0 | 0 | 0 | 0 | 0 | 214.8662 | 0 | 445.7016 | 34.97% | 11.825 | 0 | 11.8427 | 23.69% | 50
227 | 932 | 461 | 51 | 9.8729 | 11.3 | 469.0918 | 284.0501 | 0 | 243.4644 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 243.4644 | 0 | 681.3181 | 53.46% | 19.175 | 0 | 31.0465 | 62.09% | 50
228 | 956 | 539 | 55 | 10.2758 | 12 | 481.1714 | 296.2963 | 0 | 254.7749 | 100 | 0.32581 | 24.6742 | 75 | 0 | 0 | 0 | 0 | 0 | 254.7749 | 0 | 927.8806 | 72.8% | 18.9251 | 0 | 50 | 100% | 50
229 | 944 | 554 | 62 | 11.4848 | 12.1 | 475.1316 | 288.5486 | 0 | 246.7431 | 100.1 | 25.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 246.7431 | 0 | 1166.6701 | 91.54% | 0 | 0 | 50 | 100% | 49.9
230 | 922 | 509 | 61 | 10.6788 | 11.9 | 464.0586 | 163.5912 | 106.4476 | 139.185 | 100.5 | 25.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 139.185 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.5
231 | 861 | 404 | 59 | 10.6788 | 11.8 | 433.3563 | 0 | 221.4213 | 0 | 97.0424 | 23.5212 | 0 | 73.5212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
232 | 725 | 253 | 52 | 12.0892 | 10.7 | 364.9051 | 0 | 143.6333 | 0 | 54.7168 | 2.3584 | 0 | 52.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
233 | 400 | 85 | 31 | 11.4848 | 9 | 201.327 | 0 | 0 | 0 | 14.84 | 0 | 0 | 14.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9663 | 49.93% | 39.84
234 | 1 | 2 | 1 | 7.858 | 7.1 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.5304 | 25.0672 | 0 | 64.5304 | 1215.3628 | 95.36% | 0 | 24.9328 | 0 | 0% | 50
235 | 0 | 0 | 0 | 5.4401 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.6308 | 50 | 0 | 123.6308 | 1087.7388 | 85.35% | 0 | 0 | 0 | 0% | 50
236 | 0 | 0 | 0 | 4.4327 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.6308 | 50 | 0 | 123.6308 | 960.0972 | 75.33% | 0 | 0 | 0 | 0% | 50
237 | 0 | 0 | 0 | 3.0223 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0645 | 45.2 | 0 | 112.0645 | 846.3105 | 66.4% | 0 | 0 | 0 | 0% | 45.2
238 | 0 | 0 | 0 | 2.4178 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.1107 | 41.5 | 0 | 103.1107 | 743.0966 | 58.3% | 0 | 0 | 0 | 0% | 41.5
239 | 0 | 0 | 0 | 3.4253 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8925 | 38.5 | 0 | 95.8925 | 648.409 | 50.88% | 0 | 0 | 0 | 0% | 38.5
240 | 0 | 0 | 0 | 4.6342 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5622 | 36.7 | 0 | 91.5622 | 558.8153 | 43.85% | 0 | 0 | 0 | 0% | 36.7
241 | 0 | 0 | 0 | 6.2461 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8773 | 36 | 0 | 89.8773 | 471.1713 | 36.97% | 0 | 0 | 0 | 0% | 36
242 | 0 | 0 | 0 | 3.2238 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3955 | 35.8 | 0 | 89.3955 | 384.0736 | 30.13% | 0 | 0 | 0 | 0% | 35.8
243 | 0 | 0 | 0 | 3.8283 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0431 | 36.9 | 0 | 92.0431 | 293.874 | 23.06% | 0 | 0 | 0 | 0% | 36.9
244 | 0 | 0 | 0 | 3.8283 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8813 | 41 | 0 | 101.8813 | 191.9365 | 15.06% | 0 | 0 | 0 | 0% | 41
245 | 0 | 0 | 0 | 5.2387 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.5234 | 47.9 | 0 | 118.5234 | 70.2054 | 5.508% | 0 | 0 | 0 | 0% | 47.9
246 | 0 | 0 | 0 | 4.2312 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2054 | 5.508% | 0 | 0 | 0 | 0% | 0
247 | 0 | 0 | 0 | 3.4253 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2054 | 5.508% | 0 | 0 | 0 | 0% | 0
248 | 119 | 17 | 9 | 3.4253 | 0.8 | 59.8948 | 0 | 0 | 0 | 1.7586 | 0 | 0 | 1.7586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2054 | 5.508% | 0 | 0 | 0 | 0% | 1.7586
249 | 620 | 154 | 38 | 4.6342 | 3.9 | 312.0568 | 157.4159 | 0 | 128.1714 | 34.0901 | 0 | 0 | 34.0901 | 0 | 0 | 0 | 0 | 0 | 128.1714 | 0 | 194.585 | 15.27% | 0 | 0 | 0 | 0% | 34.0901
250 | 809 | 323 | 55 | 2.2164 | 7.1 | 407.1838 | 235.1692 | 0 | 201.9515 | 74.6208 | 0 | 12.3104 | 62.3104 | 0 | 0 | 0 | 0 | 0 | 201.9515 | 0 | 390.5619 | 30.64% | 9.4421 | 0 | 9.4576 | 18.92% | 50
251 | 902 | 460 | 61 | 1.2089 | 9.5 | 453.9923 | 275.2456 | 0 | 239.6587 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 239.6587 | 0 | 623.1305 | 48.89% | 19.175 | 0 | 28.6641 | 57.33% | 50
252 | 930 | 538 | 65 | 2.2164 | 9.8 | 468.0852 | 288.5518 | 0 | 251.8452 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 251.8452 | 0 | 867.525 | 68.07% | 19.175 | 0 | 47.8706 | 95.74% | 50
253 | 945 | 559 | 65 | 3.2238 | 10.5 | 475.6349 | 289.0924 | 0 | 251.9805 | 100 | 22.2283 | 2.7717 | 75 | 0 | 0 | 0 | 0 | 0 | 251.9805 | 0 | 1112.0509 | 87.25% | 2.1259 | 0 | 50 | 100% | 50
254 | 922 | 514 | 65 | 4.0297 | 11.2 | 464.0586 | 223.3944 | 46.9673 | 193.3493 | 100.2 | 25.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 193.3493 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.8
255 | 843 | 406 | 66 | 7.2535 | 11.3 | 424.2966 | 0 | 216.9841 | 0 | 96.3219 | 23.161 | 0 | 73.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
256 | 726 | 258 | 55 | 8.4625 | 10.6 | 365.4084 | 0 | 143.9724 | 0 | 55.1525 | 2.5762 | 0 | 52.5762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
257 | 422 | 87 | 30 | 7.2535 | 9.2 | 212.3999 | 0 | 0 | 0 | 15.6104 | 0 | 0 | 15.6104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9628 | 49.93% | 40.6104
258 | 1 | 2 | 2 | 4.6342 | 6.6 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.5398 | 25.0743 | 0 | 64.5398 | 1215.3553 | 95.36% | 0 | 24.9257 | 0 | 0% | 50
259 | 0 | 0 | 0 | 5.6416 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.6189 | 50 | 0 | 123.6189 | 1087.7501 | 85.35% | 0 | 0 | 0 | 0% | 50
260 | 0 | 0 | 0 | 2.6193 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.6585 | 49.6 | 0 | 122.6585 | 961.3276 | 75.43% | 0 | 0 | 0 | 0% | 49.6
261 | 0 | 0 | 0 | 1.6119 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7885 | 45.5 | 0 | 112.7885 | 846.6915 | 66.43% | 0 | 0 | 0 | 0% | 45.5
262 | 0 | 0 | 0 | 3.0223 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2453 | 42.4 | 0 | 105.2453 | 740.9261 | 58.13% | 0 | 0 | 0 | 0% | 42.4
263 | 0 | 0 | 0 | 2.6193 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3213 | 39.1 | 0 | 97.3213 | 644.5244 | 50.57% | 0 | 0 | 0 | 0% | 39.1
264 | 0 | 0 | 0 | 1.8134 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.081 | 36.5 | 0 | 91.081 | 555.519 | 43.59% | 0 | 0 | 0 | 0% | 36.5
265 | 0 | 0 | 0 | 4.4327 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.949 | 35.2 | 0 | 87.949 | 470.1114 | 36.89% | 0 | 0 | 0 | 0% | 35.2
266 | 0 | 0 | 0 | 3.0223 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5143 | 34.6 | 0 | 86.5143 | 386.4229 | 30.32% | 0 | 0 | 0 | 0% | 34.6
267 | 0 | 0 | 0 | 1.8134 | -0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0378 | 34.4 | 0 | 86.0378 | 303.3078 | 23.8% | 0 | 0 | 0 | 0% | 34.4
268 | 0 | 0 | 0 | 1.6119 | -1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6725 | 35.5 | 0 | 88.6725 | 217.0258 | 17.03% | 0 | 0 | 0 | 0% | 35.5
269 | 0 | 0 | 0 | 1.0074 | -0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2051 | 37.8 | 0 | 94.2051 | 124.2082 | 9.746% | 0 | 0 | 0 | 0% | 37.8
270 | 0 | 0 | 0 | 2.2164 | -0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.7036 | 20.016 | 0 | 52.7036 | 76.27 | 5.984% | 0 | 0 | 0 | 0% | 20.016
271 | 0 | 0 | 0 | 1.0074 | -0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.27 | 5.984% | 0 | 0 | 0 | 0% | 0
272 | 138 | 18 | 9 | 2.0149 | -0.2 | 69.4578 | 0 | 26.7103 | 0 | 1.9225 | 0 | 0 | 1.9225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.27 | 5.984% | 0 | 0 | 0 | 0% | 1.9225
273 | 657 | 158 | 35 | 2.0149 | 3.6 | 330.6795 | 167.3101 | 0 | 138.4751 | 35.3061 | 0 | 0 | 35.3061 | 0 | 0 | 0 | 0 | 0 | 138.4751 | 0 | 209.5558 | 16.44% | 0 | 0 | 0 | 0% | 35.3061
274 | 840 | 328 | 48 | 2.0149 | 7.1 | 422.7866 | 244.839 | 0 | 210.9549 | 78.7707 | 0 | 15.9354 | 62.8354 | 0 | 0 | 0 | 0 | 0 | 210.9549 | 0 | 412.6053 | 32.37% | 12.2224 | 0 | 12.2442 | 24.49% | 46.9
275 | 924 | 464 | 53 | 1.4104 | 10 | 465.0653 | 282.3188 | 0 | 246.253 | 103.5 | 3.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 246.253 | 0 | 649.6301 | 50.97% | 19.175 | 0 | 31.4534 | 62.91% | 46.5
276 | 961 | 547 | 55 | 2.6193 | 11.1 | 483.688 | 298.5095 | 0 | 261.0202 | 104.5 | 5.3624 | 24.1376 | 75 | 0 | 0 | 0 | 0 | 0 | 261.0202 | 0 | 900.8688 | 70.68% | 18.5135 | 0 | 50 | 100% | 45.5
277 | 963 | 564 | 57 | 2.2164 | 11.9 | 484.6946 | 294.8567 | 0 | 257.7927 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 257.7927 | 0 | 1149.0008 | 90.15% | 0 | 0 | 50 | 100% | 43.9
278 | 943 | 519 | 56 | 3.2238 | 12.6 | 474.6283 | 184.2584 | 92.6175 | 160.0145 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 160.0145 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
279 | 884 | 414 | 53 | 4.8357 | 13.1 | 444.9326 | 0 | 227.7623 | 0 | 103.161 | 30.2305 | 0 | 72.9305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.7
280 | 765 | 263 | 46 | 7.455 | 11.9 | 385.0378 | 0 | 151.8844 | 0 | 61.5621 | 7.831 | 0 | 53.731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.9
281 | 471 | 91 | 27 | 7.455 | 10.3 | 237.0625 | 0 | 0 | 0 | 16.5944 | 0 | 0 | 16.5944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9592 | 49.92% | 41.5944
282 | 2 | 2 | 2 | 4.8357 | 7.5 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.9385 | 23.4813 | 0 | 60.9385 | 1218.8393 | 95.63% | 0 | 24.9187 | 0 | 0% | 48.4
283 | 0 | 0 | 0 | 2.2164 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.5341 | 48.3 | 0 | 119.5341 | 1096.1953 | 86.01% | 0 | 0 | 0 | 0% | 48.3
284 | 0 | 0 | 0 | 1.4104 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.7181 | 46.3 | 0 | 114.7181 | 979.2987 | 76.84% | 0 | 0 | 0 | 0% | 46.3
285 | 0 | 0 | 0 | 1.0074 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.231 | 43.2 | 0 | 107.231 | 871.2702 | 68.36% | 0 | 0 | 0 | 0% | 43.2
286 | 0 | 0 | 0 | 2.0149 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8 | 39.3 | 0 | 97.8 | 774.309 | 60.75% | 0 | 0 | 0 | 0% | 39.3
287 | 0 | 0 | 0 | 1.0074 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3589 | 36.2 | 0 | 90.3589 | 686.1433 | 53.84% | 0 | 0 | 0 | 0% | 36.2
288 | 0 | 0 | 0 | 2.2164 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0875 | 34 | 0 | 85.0875 | 604.2195 | 47.41% | 0 | 0 | 0 | 0% | 34
289 | 0 | 0 | 0 | 1.4104 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4561 | 32.9 | 0 | 82.4561 | 525.4561 | 41.23% | 0 | 0 | 0 | 0% | 32.9
290 | 0 | 0 | 0 | 0.60446 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0192 | 32.3 | 0 | 81.0192 | 448.3797 | 35.18% | 0 | 0 | 0 | 0% | 32.3
291 | 0 | 0 | 0 | 2.4178 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7795 | 32.2 | 0 | 80.7795 | 371.5631 | 29.15% | 0 | 0 | 0 | 0% | 32.2
292 | 0 | 0 | 0 | 1.0074 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2168 | 32.8 | 0 | 82.2168 | 293.0311 | 22.99% | 0 | 0 | 0 | 0% | 32.8
293 | 0 | 0 | 0 | 1.2089 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5611 | 34.2 | 0 | 85.5611 | 210.4568 | 16.51% | 0 | 0 | 0 | 0% | 34.2
294 | 0 | 0 | 0 | 1.0074 | -0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6725 | 35.5 | 0 | 88.6725 | 124.1256 | 9.739% | 0 | 0 | 0 | 0% | 35.5
295 | 0 | 0 | 0 | 0.80595 | -0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.1256 | 9.739% | 0 | 0 | 0 | 0% | 0
296 | 159 | 19 | 8 | 1.4104 | 0.8 | 80.0275 | 0 | 30.9561 | 0 | 1.9496 | 0 | 0 | 1.9496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.1256 | 9.739% | 0 | 0 | 0 | 0% | 1.9496
297 | 696 | 163 | 32 | 1.0074 | 5 | 350.3089 | 177.7841 | 0 | 148.7567 | 36.1548 | 0 | 0 | 36.1548 | 0 | 0 | 0 | 0 | 0 | 148.7567 | 0 | 266.1302 | 20.88% | 0 | 0 | 0 | 0% | 36.1548
298 | 873 | 335 | 43 | 2.2164 | 9.4 | 439.3961 | 255.1615 | 0 | 220.4693 | 84.94 | 0 | 21.02 | 63.92 | 0 | 0 | 0 | 0 | 0 | 220.4693 | 0 | 476.5924 | 37.39% | 16.1224 | 0 | 16.1534 | 32.31% | 42.9
299 | 947 | 472 | 49 | 3.6268 | 11.7 | 476.6416 | 289.7281 | 0 | 252.4432 | 106.9 | 6.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 252.4432 | 0 | 717.5771 | 56.3% | 19.175 | 0 | 35.3653 | 70.73% | 43.1
300 | 978 | 555 | 52 | 5.2387 | 13.6 | 492.2444 | 304.1505 | 0 | 265.2408 | 107.2 | 13.1562 | 19.0438 | 75 | 0 | 0 | 0 | 0 | 0 | 265.2408 | 0 | 970.7786 | 76.17% | 14.6066 | 0 | 50 | 100% | 42.8
301 | 981 | 573 | 53 | 8.261 | 14.5 | 493.7544 | 300.6459 | 0 | 260.1184 | 109 | 34 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 260.1184 | 0 | 1219.0901 | 95.65% | 0 | 0 | 50 | 100% | 41
302 | 962 | 529 | 53 | 8.4625 | 15.3 | 484.1913 | 103.068 | 179.7579 | 88.6577 | 110.1 | 35.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 88.6577 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.9
303 | 914 | 425 | 49 | 7.2535 | 15.8 | 460.0321 | 0 | 235.749 | 0 | 109.7281 | 34.8641 | 0 | 74.8641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40
304 | 813 | 274 | 41 | 6.6491 | 16.1 | 409.197 | 0 | 161.6347 | 0 | 65.8754 | 11.0877 | 0 | 54.7877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.7
305 | 548 | 99 | 25 | 7.2535 | 14.1 | 275.8179 | 0 | 0 | 0 | 18.493 | 0 | 0 | 18.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9557 | 49.91% | 43.493
306 | 6 | 2 | 2 | 4.2312 | 10.1 | 3.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6169 | 23.2884 | 0 | 60.6169 | 1219.1523 | 95.66% | 0 | 24.9116 | 0 | 0% | 48.2
307 | 0 | 0 | 0 | 0.40297 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.1687 | 48.1 | 0 | 119.1687 | 1097.0657 | 86.08% | 0 | 0 | 0 | 0% | 48.1
308 | 0 | 0 | 0 | 1.8134 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.7297 | 46.3 | 0 | 114.7297 | 980.1512 | 76.9% | 0 | 0 | 0 | 0% | 46.3
309 | 0 | 0 | 0 | 2.0149 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3479 | 42.4 | 0 | 105.3479 | 874.4001 | 68.61% | 0 | 0 | 0 | 0% | 42.4
310 | 0 | 0 | 0 | 3.8283 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2177 | 38.6 | 0 | 96.2177 | 779.4434 | 61.16% | 0 | 0 | 0 | 0% | 38.6
311 | 0 | 0 | 0 | 5.4401 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7829 | 35.5 | 0 | 88.7829 | 693.2395 | 54.39% | 0 | 0 | 0 | 0% | 35.5
312 | 0 | 0 | 0 | 5.8431 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.456 | 34.1 | 0 | 85.456 | 611.0347 | 47.94% | 0 | 0 | 0 | 0% | 34.1
313 | 0 | 0 | 0 | 4.8357 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7366 | 33.4 | 0 | 83.7366 | 530.8205 | 41.65% | 0 | 0 | 0 | 0% | 33.4
314 | 0 | 0 | 0 | 2.8208 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7339 | 33.4 | 0 | 83.7339 | 450.5905 | 35.35% | 0 | 0 | 0 | 0% | 33.4
315 | 0 | 0 | 0 | 3.4253 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3608 | 34.5 | 0 | 86.3608 | 367.1633 | 28.81% | 0 | 0 | 0 | 0% | 34.5
316 | 0 | 0 | 0 | 5.6416 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1767 | 39 | 0 | 97.1767 | 270.9437 | 21.26% | 0 | 0 | 0 | 0% | 39
317 | 0 | 0 | 0 | 5.6416 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.485 | 46.2 | 0 | 114.485 | 154.0971 | 12.09% | 0 | 0 | 0 | 0% | 46.2
318 | 0 | 0 | 0 | 6.8506 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4783 | 30.7751 | 0 | 77.4783 | 81.195 | 6.371% | 0 | 0 | 0 | 0% | 30.7751
319 | 0 | 0 | 0 | 1.8134 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.195 | 6.371% | 0 | 0 | 0 | 0% | 0
320 | 159 | 19 | 8 | 2.4178 | 5.5 | 80.0275 | 0 | 31.1408 | 0 | 1.9284 | 0 | 0 | 1.9284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.195 | 6.371% | 0 | 0 | 0 | 0% | 1.9284
321 | 680 | 159 | 31 | 4.0297 | 9.8 | 342.2558 | 174.239 | 0 | 144.3137 | 35.3888 | 0 | 0 | 35.3888 | 0 | 0 | 0 | 0 | 0 | 144.3137 | 0 | 219.6043 | 17.23% | 0 | 0 | 0 | 0% | 35.3888
322 | 854 | 328 | 42 | 1.4104 | 14.7 | 429.833 | 250.3154 | 0 | 216.2904 | 72.0231 | 0 | 11.0116 | 61.0116 | 0 | 0 | 0 | 0 | 0 | 216.2904 | 0 | 427.0456 | 33.51% | 8.4459 | 0 | 8.4633 | 16.93% | 50
323 | 924 | 462 | 48 | 2.8208 | 16.2 | 465.0653 | 283.0766 | 0 | 246.4765 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 246.4765 | 0 | 663.4379 | 52.05% | 19.175 | 0 | 27.6779 | 55.36% | 50
324 | 951 | 542 | 51 | 4.2312 | 17.5 | 478.6548 | 296.1188 | 0 | 258.2743 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 258.2743 | 0 | 911.1454 | 71.49% | 19.175 | 0 | 46.8926 | 93.79% | 50
325 | 957 | 561 | 52 | 4.6342 | 18.2 | 481.6747 | 293.5763 | 0 | 255.7879 | 101 | 21.957 | 4.043 | 75 | 0 | 0 | 0 | 0 | 0 | 255.7879 | 0 | 1156.4683 | 90.74% | 3.101 | 0 | 50 | 100% | 49
326 | 934 | 517 | 53 | 6.0446 | 18.6 | 470.0984 | 177.5788 | 97.1823 | 153.3228 | 101.5 | 26.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 153.3228 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.5
327 | 885 | 415 | 49 | 5.8431 | 18.9 | 445.4359 | 0 | 228.5418 | 0 | 94.879 | 23.1395 | 0 | 71.7395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.6
328 | 779 | 267 | 42 | 6.0446 | 18.2 | 392.0842 | 0 | 155.1161 | 0 | 55.1098 | 2.5549 | 0 | 52.5549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
329 | 519 | 97 | 25 | 4.8357 | 16.2 | 261.2217 | 0 | 0 | 0 | 18.1382 | 0 | 0 | 18.1382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9522 | 49.9% | 43.1382
330 | 10 | 2 | 2 | 2.0149 | 13 | 5.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.98 | 25.0955 | 0 | 64.98 | 1214.9539 | 95.33% | 0 | 24.9045 | 0 | 0% | 50
331 | 0 | 0 | 0 | 3.0223 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.8591 | 50 | 0 | 123.8591 | 1087.295 | 85.31% | 0 | 0 | 0 | 0% | 50
332 | 0 | 0 | 0 | 3.2238 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.199 | 48.9 | 0 | 121.199 | 962.8431 | 75.55% | 0 | 0 | 0 | 0% | 48.9
333 | 0 | 0 | 0 | 4.0297 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5333 | 44.1 | 0 | 109.5333 | 852.2352 | 66.87% | 0 | 0 | 0 | 0% | 44.1
334 | 0 | 0 | 0 | 6.0446 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0131 | 40.5 | 0 | 101.0131 | 751.8529 | 58.99% | 0 | 0 | 0 | 0% | 40.5
335 | 0 | 0 | 0 | 4.6342 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4927 | 37.4 | 0 | 93.4927 | 660.3072 | 51.81% | 0 | 0 | 0 | 0% | 37.4
336 | 0 | 0 | 0 | 4.0297 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6153 | 35.8 | 0 | 89.6153 | 573.2499 | 44.98% | 0 | 0 | 0 | 0% | 35.8
337 | 0 | 0 | 0 | 5.4401 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3634 | 35.3 | 0 | 88.3634 | 487.5716 | 38.26% | 0 | 0 | 0 | 0% | 35.3
338 | 0 | 0 | 0 | 6.0446 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9562 | 35.1 | 0 | 87.9562 | 402.4321 | 31.58% | 0 | 0 | 0 | 0% | 35.1
339 | 0 | 0 | 0 | 5.4401 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3019 | 36.1 | 0 | 90.3019 | 314.4786 | 24.67% | 0 | 0 | 0 | 0% | 36.1
340 | 0 | 0 | 0 | 5.6416 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4004 | 39.9 | 0 | 99.4004 | 215.6628 | 16.92% | 0 | 0 | 0 | 0% | 39.9
341 | 0 | 0 | 0 | 5.6416 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.277 | 46.9 | 0 | 116.277 | 96.7965 | 7.595% | 0 | 0 | 0 | 0% | 46.9
342 | 0 | 0 | 0 | 5.0372 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7965 | 7.595% | 0 | 0 | 0 | 0% | 0
343 | 0 | 0 | 0 | 5.6416 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7965 | 7.595% | 0 | 0 | 0 | 0% | 0
344 | 39 | 17 | 15 | 5.2387 | 6.9 | 19.6294 | 0 | 7.6844 | 0 | 1.2337 | 0 | 0 | 1.2337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7965 | 7.595% | 0 | 0 | 0 | 0% | 1.2337
345 | 274 | 129 | 71 | 4.0297 | 8.5 | 137.909 | 70.4311 | 0 | 46.6891 | 21.7621 | 0 | 0 | 21.7621 | 0 | 0 | 0 | 0 | 0 | 46.6891 | 0 | 141.966 | 11.14% | 0 | 0 | 0 | 0% | 21.7621
346 | 703 | 315 | 75 | 5.6416 | 11.4 | 353.8321 | 206.5638 | 0 | 173.7921 | 66.0943 | 0 | 8.0472 | 58.0472 | 0 | 0 | 0 | 0 | 0 | 173.7921 | 0 | 310.1017 | 24.33% | 6.1722 | 0 | 6.1858 | 12.37% | 50
347 | 715 | 435 | 110 | 9.2684 | 13.6 | 359.8719 | 219.355 | 0 | 183.4692 | 94.2936 | 0 | 22.1468 | 72.1468 | 0 | 0 | 0 | 0 | 0 | 183.4692 | 0 | 487.5994 | 38.26% | 16.9866 | 0 | 23.2099 | 46.42% | 50
348 | 907 | 564 | 92 | 10.4773 | 14.7 | 456.5089 | 282.7801 | 0 | 241.9699 | 100.4 | 0.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 241.9699 | 0 | 721.6938 | 56.63% | 19.175 | 0 | 42.4273 | 84.85% | 49.6
349 | 718 | 504 | 117 | 9.8729 | 14.7 | 361.3819 | 220.4842 | 0 | 184.1783 | 101 | 16.1486 | 9.8514 | 75 | 0 | 0 | 0 | 0 | 0 | 184.1783 | 0 | 899.8776 | 70.61% | 7.556 | 0 | 50 | 100% | 49
350 | 701 | 520 | 166 | 9.6714 | 15.2 | 352.8255 | 206.3532 | 0 | 171.191 | 101.4 | 26.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 171.191 | 0 | 1065.4968 | 83.6% | 0 | 0 | 50 | 100% | 48.6
351 | 502 | 362 | 151 | 9.8729 | 14.6 | 252.6653 | 129.8043 | 0 | 99.3238 | 64.5152 | 7.8576 | 0 | 56.6576 | 0 | 0 | 0 | 0 | 0 | 99.3238 | 0 | 1161.5879 | 91.14% | 0 | 0 | 50 | 100% | 48.8
352 | 346 | 213 | 109 | 9.8729 | 13.4 | 174.1478 | 69.0165 | 0 | 42.056 | 34.9261 | 0 | 0 | 34.9261 | 0 | 0 | 0 | 0 | 0 | 42.056 | 0 | 1202.275 | 94.33% | 0 | 15.0739 | 34.8951 | 69.79% | 50
353 | 201 | 94 | 58 | 8.8654 | 12 | 101.1668 | 0 | 0 | 0 | 12.7724 | 0 | 0 | 12.7724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202.275 | 94.33% | 0 | 25 | 9.843 | 19.69% | 37.7724
354 | 1 | 2 | 2 | 6.8506 | 9.7 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0949 | 40.1767 | 0 | 100.0949 | 1102.8507 | 86.53% | 0 | 9.8233 | 0 | 0% | 50
355 | 0 | 0 | 0 | 5.8431 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.7389 | 50 | 0 | 123.7389 | 975.2327 | 76.52% | 0 | 0 | 0 | 0% | 50
356 | 0 | 0 | 0 | 4.6342 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.8158 | 49.2 | 0 | 121.8158 | 849.935 | 66.69% | 0 | 0 | 0 | 0% | 49.2
357 | 0 | 0 | 0 | 3.8283 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.7291 | 44.2 | 0 | 109.7291 | 739.0307 | 57.99% | 0 | 0 | 0 | 0% | 44.2
358 | 0 | 0 | 0 | 3.6268 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2582 | 40.7 | 0 | 101.2582 | 638.0769 | 50.06% | 0 | 0 | 0 | 0% | 40.7
359 | 0 | 0 | 0 | 3.8283 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.057 | 37.7 | 0 | 94.057 | 545.6702 | 42.81% | 0 | 0 | 0 | 0% | 37.7
360 | 0 | 0 | 0 | 4.4327 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9654 | 36 | 0 | 89.9654 | 458.0418 | 35.94% | 0 | 0 | 0 | 0% | 36
361 | 0 | 0 | 0 | 5.0372 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2767 | 35.3 | 0 | 88.2767 | 372.3499 | 29.22% | 0 | 0 | 0 | 0% | 35.3
362 | 0 | 0 | 0 | 0.80595 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2736 | 35.3 | 0 | 88.2736 | 286.636 | 22.49% | 0 | 0 | 0 | 0% | 35.3
363 | 0 | 0 | 0 | 1.2089 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.67 | 36.3 | 0 | 90.67 | 198.0962 | 15.54% | 0 | 0 | 0 | 0% | 36.3
364 | 0 | 0 | 0 | 0.60446 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7168 | 40.1 | 0 | 99.7168 | 98.6678 | 7.742% | 0 | 0 | 0 | 0% | 40.1
365 | 0 | 0 | 0 | 0.80595 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6678 | 7.742% | 0 | 0 | 0 | 0% | 0
366 | 0 | 0 | 0 | 2.0149 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6678 | 7.742% | 0 | 0 | 0 | 0% | 0
367 | 0 | 0 | 0 | 4.0297 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6678 | 7.742% | 0 | 0 | 0 | 0% | 0
368 | 33 | 13 | 10 | 3.0223 | 3.8 | 16.6095 | 0 | 6.5418 | 0 | 0.71813 | 0 | 0 | 0.71813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6678 | 7.742% | 0 | 0 | 0 | 0% | 0.71813
369 | 328 | 122 | 56 | 0.80595 | 5.1 | 165.0881 | 84.5841 | 0 | 61.5456 | 22.7004 | 0 | 0 | 22.7004 | 0 | 0 | 0 | 0 | 0 | 61.5456 | 0 | 158.3536 | 12.42% | 0 | 0 | 0 | 0% | 22.7004
370 | 598 | 301 | 94 | 1.2089 | 9.6 | 300.9838 | 175.9645 | 0 | 147.0119 | 54.124 | 2.062 | 0 | 52.062 | 0 | 0 | 0 | 0 | 0 | 147.0119 | 0 | 300.9232 | 23.61% | 0 | 0 | 0 | 0% | 50
371 | 778 | 450 | 96 | 3.2238 | 11.3 | 391.5809 | 239.0278 | 0 | 205.1493 | 98.0901 | 0 | 24.0451 | 74.0451 | 0 | 0 | 0 | 0 | 0 | 205.1493 | 0 | 499.8736 | 39.22% | 18.4426 | 0 | 18.4859 | 36.97% | 50
372 | 808 | 524 | 101 | 5.6416 | 12.5 | 406.6804 | 252.2489 | 0 | 216.3283 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 216.3283 | 0 | 709.665 | 55.68% | 19.175 | 0 | 37.706 | 75.41% | 50
373 | 804 | 553 | 118 | 6.0446 | 13.4 | 404.6672 | 247.1576 | 0 | 211.3694 | 100.5 | 9.5089 | 15.9911 | 75 | 0 | 0 | 0 | 0 | 0 | 211.3694 | 0 | 914.6475 | 71.76% | 12.2651 | 0 | 50 | 100% | 49.5
374 | 561 | 450 | 161 | 7.052 | 13.8 | 282.3611 | 165.2577 | 0 | 134.2353 | 85.371 | 18.0855 | 0 | 67.2855 | 0 | 0 | 0 | 0 | 0 | 134.2353 | 0 | 1044.8266 | 81.98% | 0 | 0 | 50 | 100% | 49.2
375 | 371 | 319 | 157 | 7.455 | 13.6 | 186.7308 | 96.0652 | 0 | 69.2169 | 45.9245 | 0 | 0 | 45.9245 | 0 | 0 | 0 | 0 | 0 | 69.2169 | 0 | 1111.952 | 87.25% | 0 | 3.3755 | 46.6171 | 93.23% | 49.3
376 | 343 | 216 | 112 | 7.6565 | 13.1 | 172.6379 | 68.5505 | 0 | 43.0161 | 35.0279 | 0 | 0 | 35.0279 | 0 | 0 | 0 | 0 | 0 | 43.0161 | 0 | 1153.6682 | 90.52% | 0 | 14.9721 | 31.612 | 63.22% | 50
377 | 163 | 92 | 67 | 7.052 | 12.4 | 82.0407 | 0 | 0 | 0 | 12.9591 | 0 | 0 | 12.9591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1153.6682 | 90.52% | 0 | 25 | 6.5562 | 13.11% | 37.9591
378 | 2 | 3 | 3 | 6.2461 | 10.5 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0443 | 43.4575 | 0 | 108.0443 | 1044.9268 | 81.99% | 0 | 6.5425 | 0 | 0% | 50
379 | 0 | 0 | 0 | 2.8208 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.7749 | 50 | 0 | 123.7749 | 917.2724 | 71.97% | 0 | 0 | 0 | 0% | 50
380 | 0 | 0 | 0 | 3.0223 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.3348 | 49 | 0 | 121.3348 | 792.5358 | 62.18% | 0 | 0 | 0 | 0% | 49
381 | 0 | 0 | 0 | 3.0223 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.4878 | 44.1 | 0 | 109.4878 | 681.8998 | 53.5% | 0 | 0 | 0 | 0% | 44.1
382 | 0 | 0 | 0 | 1.4104 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0244 | 40.6 | 0 | 101.0244 | 581.2088 | 45.6% | 0 | 0 | 0 | 0% | 40.6
383 | 0 | 0 | 0 | 2.0149 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0698 | 37.7 | 0 | 94.0698 | 488.7889 | 38.35% | 0 | 0 | 0 | 0% | 37.7
384 | 0 | 0 | 0 | 1.2089 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2065 | 36.1 | 0 | 90.2065 | 400.8621 | 31.45% | 0 | 0 | 0 | 0% | 36.1
385 | 0 | 0 | 0 | 1.6119 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5181 | 35.4 | 0 | 88.5181 | 314.8719 | 24.71% | 0 | 0 | 0 | 0% | 35.4
386 | 0 | 0 | 0 | 3.0223 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2767 | 35.3 | 0 | 88.2767 | 229.1357 | 17.98% | 0 | 0 | 0 | 0% | 35.3
387 | 0 | 0 | 0 | 4.4327 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2065 | 36.1 | 0 | 90.2065 | 141.1293 | 11.07% | 0 | 0 | 0 | 0% | 36.1
388 | 0 | 0 | 0 | 2.0149 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.1293 | 11.07% | 0 | 0 | 0 | 0% | 0
389 | 0 | 0 | 0 | 3.0223 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.1293 | 11.07% | 0 | 0 | 0 | 0% | 0
390 | 0 | 0 | 0 | 1.4104 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.1293 | 11.07% | 0 | 0 | 0 | 0% | 0
391 | 0 | 0 | 0 | 1.4104 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.1293 | 11.07% | 0 | 0 | 0 | 0% | 0
392 | 108 | 25 | 18 | 3.4253 | 4.5 | 54.3583 | 0 | 21.5415 | 0 | 2.377 | 0 | 0 | 2.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.1293 | 11.07% | 0 | 0 | 0 | 0% | 2.377
393 | 315 | 151 | 88 | 1.6119 | 7.3 | 158.545 | 81.4985 | 0 | 58.1553 | 25.5492 | 0 | 0 | 25.5492 | 0 | 0 | 0 | 0 | 0 | 58.1553 | 0 | 197.5981 | 15.5% | 0 | 0 | 0 | 0% | 25.5492
394 | 696 | 380 | 141 | 0.60446 | 11.2 | 350.3089 | 205.1023 | 0 | 174.4821 | 72.9382 | 0 | 11.4691 | 61.4691 | 0 | 0 | 0 | 0 | 0 | 174.4821 | 0 | 367.0201 | 28.8% | 8.7968 | 0 | 8.8187 | 17.64% | 50
395 | 526 | 365 | 121 | 2.8208 | 12.3 | 264.7449 | 161.845 | 0 | 133.0868 | 64.4767 | 0 | 7.2384 | 57.2384 | 0 | 0 | 0 | 0 | 0 | 133.0868 | 0 | 496.2473 | 38.94% | 5.5518 | 0 | 14.3843 | 28.77% | 50
396 | 855 | 555 | 105 | 4.4327 | 13.2 | 430.3364 | 267.2884 | 0 | 230.9885 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 230.9885 | 0 | 720.537 | 56.53% | 19.175 | 0 | 33.6072 | 67.21% | 50
397 | 793 | 591 | 160 | 3.0223 | 14.3 | 399.1307 | 244.0488 | 0 | 209.8867 | 100 | 3.6805 | 21.3195 | 75 | 0 | 0 | 0 | 0 | 0 | 209.8867 | 0 | 924.3369 | 72.52% | 16.352 | 0 | 50 | 100% | 50
398 | 594 | 491 | 186 | 5.8431 | 14.6 | 298.9705 | 175.1101 | 0 | 144.3327 | 94.1416 | 22.1708 | 0 | 71.9708 | 0 | 0 | 0 | 0 | 0 | 144.3327 | 0 | 1064.4839 | 83.52% | 0 | 0 | 50 | 100% | 49.8
399 | 350 | 350 | 196 | 3.2238 | 14.7 | 176.1611 | 90.7634 | 0 | 66.6069 | 47.8393 | 0 | 0 | 47.8393 | 0 | 0 | 0 | 0 | 0 | 66.6069 | 0 | 1129.1593 | 88.6% | 0 | 0 | 50 | 100% | 47.8393
400 | 7 | 86 | 82 | 6.8506 | 13.5 | 3.5232 | 0 | 1.402 | 0 | 6.6913 | 0 | 0 | 6.6913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1129.1593 | 88.6% | 0 | 25 | 24.9416 | 49.88% | 31.6913
401 | 91 | 78 | 67 | 8.8654 | 12.4 | 45.8019 | 0 | 0 | 0 | 10.274 | 0 | 0 | 10.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1129.1593 | 88.6% | 0 | 24.8835 | 0 | 0% | 35.1574
402 | 3 | 3 | 3 | 7.858 | 10.7 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.8591 | 50 | 0 | 123.8591 | 1001.4568 | 78.58% | 0 | 0 | 0 | 0% | 50
403 | 0 | 0 | 0 | 7.052 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.8591 | 50 | 0 | 123.8591 | 873.736 | 68.55% | 0 | 0 | 0 | 0% | 50
404 | 0 | 0 | 0 | 5.8431 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.1481 | 49.3 | 0 | 122.1481 | 748.0553 | 58.69% | 0 | 0 | 0 | 0% | 49.3
405 | 0 | 0 | 0 | 5.0372 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.7251 | 44.6 | 0 | 110.7251 | 635.9479 | 49.9% | 0 | 0 | 0 | 0% | 44.6
406 | 0 | 0 | 0 | 3.6268 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.7435 | 40.9 | 0 | 101.7435 | 534.3851 | 41.93% | 0 | 0 | 0 | 0% | 40.9
407 | 0 | 0 | 0 | 2.8208 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0284 | 38.1 | 0 | 95.0284 | 440.8005 | 34.59% | 0 | 0 | 0 | 0% | 38.1
408 | 0 | 0 | 0 | 3.0223 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.461 | 36.2 | 0 | 90.461 | 352.573 | 27.66% | 0 | 0 | 0 | 0% | 36.2
409 | 0 | 0 | 0 | 3.2238 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2767 | 35.3 | 0 | 88.2767 | 266.8352 | 20.94% | 0 | 0 | 0 | 0% | 35.3
410 | 0 | 0 | 0 | 4.4327 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5181 | 35.4 | 0 | 88.5181 | 180.7903 | 14.19% | 0 | 0 | 0 | 0% | 35.4
411 | 0 | 0 | 0 | 1.8134 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.7903 | 14.19% | 0 | 0 | 0 | 0% | 0
412 | 0 | 0 | 0 | 4.4327 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.7903 | 14.19% | 0 | 0 | 0 | 0% | 0
413 | 0 | 0 | 0 | 3.6268 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.7903 | 14.19% | 0 | 0 | 0 | 0% | 0
414 | 0 | 0 | 0 | 3.0223 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.7903 | 14.19% | 0 | 0 | 0 | 0% | 0
415 | 0 | 0 | 0 | 0.60446 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.7903 | 14.19% | 0 | 0 | 0 | 0% | 0
416 | 0 | 8 | 8 | 1.0074 | 5.4 | 0 | 0 | 0 | 0 | 0.048158 | 0 | 0 | 0.048158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.7903 | 14.19% | 0 | 0 | 0 | 0% | 0.048158
417 | 214 | 141 | 88 | 0.40297 | 7.5 | 107.7099 | 0 | 55.5518 | 0 | 20.2776 | 0 | 0 | 20.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180.7903 | 14.19% | 0 | 0 | 0 | 0% | 20.2776
418 | 547 | 281 | 95 | 3.0223 | 10.3 | 275.3146 | 161.4351 | 0 | 132.612 | 49.3486 | 0 | 0 | 49.3486 | 0 | 0 | 0 | 0 | 0 | 132.612 | 0 | 310.1396 | 24.33% | 0 | 0 | 0 | 0% | 49.3486
419 | 799 | 460 | 94 | 4.6342 | 11.8 | 402.1506 | 246.2193 | 0 | 211.2671 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 211.2671 | 0 | 516.2088 | 40.5% | 19.175 | 0 | 19.2255 | 38.45% | 50
420 | 716 | 522 | 142 | 7.6565 | 12.3 | 360.3752 | 224.1464 | 0 | 188.926 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 188.926 | 0 | 700.4867 | 54.96% | 19.175 | 0 | 38.451 | 76.9% | 50
421 | 735 | 570 | 168 | 7.2535 | 12.9 | 369.9383 | 226.4627 | 0 | 191.3637 | 100.4 | 10.3823 | 15.0177 | 75 | 0 | 0 | 0 | 0 | 0 | 191.3637 | 0 | 887.1422 | 69.61% | 11.5186 | 0 | 50 | 100% | 49.6
422 | 759 | 544 | 155 | 7.052 | 13.2 | 382.0179 | 223.9302 | 0 | 189.116 | 100.7 | 25.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 189.116 | 0 | 1071.6054 | 84.08% | 0 | 0 | 50 | 100% | 49.3
423 | 85 | 278 | 236 | 6.4476 | 12.8 | 42.782 | 0 | 22.0778 | 0 | 30.6022 | 0 | 0 | 30.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1071.6054 | 84.08% | 0 | 19.0978 | 30.8549 | 61.71% | 49.7
424 | 82 | 179 | 149 | 7.6565 | 12.2 | 41.272 | 0 | 16.4609 | 0 | 20.193 | 0 | 0 | 20.193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1071.6054 | 84.08% | 0 | 25 | 5.7919 | 11.58% | 45.193
425 | 6 | 42 | 41 | 6.6491 | 11.2 | 3.0199 | 0 | 0 | 0 | 3.0449 | 0 | 0 | 3.0449 | 0 | 0 | 0 | 102.6262 | 41.1766 | 0 | 102.6262 | 969.2988 | 76.05% | 0 | 5.7784 | 0 | 0% | 50
426 | 0 | 2 | 2 | 5.4401 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.8591 | 50 | 0 | 123.8591 | 841.5421 | 66.03% | 0 | 0 | 0 | 0% | 50
427 | 0 | 0 | 0 | 5.2387 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.823 | 50 | 0 | 123.823 | 713.7799 | 56% | 0 | 0 | 0 | 0% | 50
428 | 0 | 0 | 0 | 3.8283 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1726 | 48.5 | 0 | 120.1726 | 590.3939 | 46.32% | 0 | 0 | 0 | 0% | 48.5
429 | 0 | 0 | 0 | 2.4178 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4923 | 44.5 | 0 | 110.4923 | 478.5222 | 37.55% | 0 | 0 | 0 | 0% | 44.5
430 | 0 | 0 | 0 | 1.2089 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5318 | 41.2 | 0 | 102.5318 | 376.0605 | 29.51% | 0 | 0 | 0 | 0% | 41.2
431 | 0 | 0 | 0 | 1.0074 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8482 | 38 | 0 | 94.8482 | 282.7107 | 22.18% | 0 | 0 | 0 | 0% | 38
432 | 0 | 0 | 0 | 5.0372 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8558 | 35.9 | 0 | 89.8558 | 195.2637 | 15.32% | 0 | 0 | 0 | 0% | 35.9
433 | 0 | 0 | 0 | 4.4327 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.5962 | 20.2995 | 0 | 53.5962 | 146.5039 | 11.49% | 0 | 0 | 0 | 0% | 20.2995
434 | 0 | 0 | 0 | 3.2238 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.5039 | 11.49% | 0 | 0 | 0 | 0% | 0
435 | 0 | 0 | 0 | 1.6119 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.5039 | 11.49% | 0 | 0 | 0 | 0% | 0
436 | 0 | 0 | 0 | 4.0297 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.5039 | 11.49% | 0 | 0 | 0 | 0% | 0
437 | 0 | 0 | 0 | 3.2238 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.5039 | 11.49% | 0 | 0 | 0 | 0% | 0
438 | 0 | 0 | 0 | 2.2164 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.5039 | 11.49% | 0 | 0 | 0 | 0% | 0
439 | 0 | 0 | 0 | 2.8208 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.5039 | 11.49% | 0 | 0 | 0 | 0% | 0
440 | 154 | 22 | 11 | 2.8208 | 3.6 | 77.5109 | 0 | 31.1012 | 0 | 2.3174 | 0 | 0 | 2.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.5039 | 11.49% | 0 | 0 | 0 | 0% | 2.3174
441 | 551 | 154 | 44 | 2.8208 | 6.8 | 277.3279 | 143.5164 | 0 | 115.9914 | 32.8049 | 0 | 0 | 32.8049 | 0 | 0 | 0 | 0 | 0 | 115.9914 | 0 | 259.7519 | 20.38% | 0 | 0 | 0 | 0% | 32.8049
442 | 806 | 338 | 59 | 3.0223 | 10.7 | 405.6738 | 238.2355 | 0 | 204.4901 | 76.4998 | 0 | 14.4999 | 61.9999 | 0 | 0 | 0 | 0 | 0 | 204.4901 | 0 | 459.4054 | 36.05% | 11.1214 | 0 | 11.1523 | 22.3% | 47.5
443 | 831 | 462 | 77 | 6.8506 | 12.3 | 418.2567 | 256.4806 | 0 | 219.5003 | 102.4 | 2.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 219.5003 | 0 | 673.7141 | 52.86% | 19.175 | 0 | 30.3805 | 60.76% | 47.6
444 | 872 | 547 | 84 | 8.6639 | 13 | 438.8928 | 273.3729 | 0 | 234.183 | 103.5 | 3.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 234.183 | 0 | 902.3583 | 70.8% | 19.175 | 0 | 49.6087 | 99.22% | 46.5
445 | 850 | 566 | 99 | 6.8506 | 13.7 | 427.8198 | 262.2129 | 0 | 224.8727 | 105.3 | 30.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 224.8727 | 0 | 1121.9123 | 88.03% | 0 | 0 | 49.6087 | 99.22% | 44.7
446 | 668 | 476 | 126 | 7.455 | 14 | 336.216 | 197.2485 | 0 | 163.9395 | 103.5492 | 30.0246 | 0 | 73.5246 | 0 | 0 | 0 | 0 | 0 | 163.9395 | 0 | 1274.5104 | 100% | 0 | 0 | 49.6087 | 99.22% | 43.5
447 | 686 | 423 | 125 | 7.6565 | 14 | 345.2757 | 0 | 178.4828 | 0 | 93.0101 | 24.7051 | 0 | 68.3051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.6087 | 99.22% | 43.6
448 | 197 | 163 | 93 | 8.0595 | 12.5 | 99.1535 | 0 | 39.6448 | 0 | 22.6185 | 0 | 0 | 22.6185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.4815 | 26.0657 | 52.13% | 46.1
449 | 0 | 34 | 34 | 6.8506 | 10.8 | 0 | 0 | 0 | 0 | 2.1332 | 0 | 0 | 2.1332 | 0 | 0 | 0 | 54.1292 | 20.4668 | 0 | 54.1292 | 1225.3461 | 96.14% | 0 | 25 | 0.99894 | 1.998% | 47.6
450 | 0 | 3 | 3 | 3.0223 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.9903 | 48 | 0 | 118.9903 | 1103.4752 | 86.58% | 0 | 0 | 0.99894 | 1.998% | 48
451 | 0 | 0 | 0 | 3.2238 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.5043 | 47.4 | 0 | 117.5043 | 983.3393 | 77.15% | 0 | 0 | 0.99894 | 1.998% | 47.4
452 | 0 | 0 | 0 | 2.0149 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1753 | 45.2 | 0 | 112.1753 | 869.5062 | 68.22% | 0 | 0 | 0.99894 | 1.998% | 45.2
453 | 0 | 0 | 0 | 1.2089 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2478 | 41.9 | 0 | 104.2478 | 765.1193 | 60.03% | 0 | 0 | 0.99894 | 1.998% | 41.9
454 | 0 | 0 | 0 | 1.4104 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.531 | 38.7 | 0 | 96.531 | 669.8265 | 52.56% | 0 | 0 | 0.99894 | 1.998% | 38.7
455 | 0 | 0 | 0 | 1.0074 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8405 | 35.5 | 0 | 88.8405 | 583.5859 | 45.79% | 0 | 0 | 0.99894 | 1.998% | 35.5
456 | 0 | 0 | 0 | 1.6119 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3322 | 33.2 | 0 | 83.3322 | 503.9306 | 39.54% | 0 | 0 | 0.99894 | 1.998% | 33.2
457 | 0 | 0 | 0 | 1.8134 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.218 | 31.9 | 0 | 80.218 | 427.9501 | 33.58% | 0 | 0 | 0.99894 | 1.998% | 31.9
458 | 0 | 0 | 0 | 1.8134 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0152 | 31.4 | 0 | 79.0152 | 353.3519 | 27.72% | 0 | 0 | 0.99894 | 1.998% | 31.4
459 | 0 | 0 | 0 | 3.4253 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0464 | 31.4 | 0 | 79.0464 | 278.7324 | 21.87% | 0 | 0 | 0.99894 | 1.998% | 31.4
460 | 0 | 0 | 0 | 9.2684 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3169 | 31.9 | 0 | 80.3169 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 31.9
461 | 0 | 0 | 0 | 10.2758 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
462 | 0 | 0 | 0 | 5.0372 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
463 | 0 | 0 | 0 | 3.2238 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
464 | 12 | 8 | 7 | 2.2164 | 8.1 | 6.0398 | 0 | 2.4388 | 0 | 0.148 | 0 | 0 | 0.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0.148
465 | 0 | 43 | 43 | 4.8357 | 9.7 | 0 | 0 | 0 | 0 | 2.8718 | 0 | 0 | 2.8718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 2.8718
466 | 0 | 131 | 130 | 11.0818 | 12.3 | 0 | 0 | 0 | 0 | 10.9 | 0 | 0 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 10.9
467 | 9 | 185 | 179 | 10.0743 | 13.2 | 4.5299 | 0 | 2.7822 | 0 | 15.8726 | 0 | 0 | 15.8726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 15.8726
468 | 83 | 255 | 208 | 13.2981 | 14.6 | 41.7753 | 0 | 26.0589 | 0 | 26.7121 | 0 | 0 | 26.7121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 26.7121
469 | 1 | 130 | 128 | 10.4773 | 13.5 | 0.50332 | 0 | 0.30887 | 0 | 9.9015 | 0 | 0 | 9.9015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 9.9015
470 | 0 | 137 | 135 | 4.8357 | 13.4 | 0 | 0 | 0 | 0 | 10.5029 | 0 | 0 | 10.5029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 10.5029
471 | 22 | 113 | 102 | 4.0297 | 13.7 | 11.073 | 0 | 5.7342 | 0 | 10.0769 | 0 | 0 | 10.0769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 10.0769
472 | 0 | 92 | 91 | 6.2461 | 13.5 | 0 | 0 | 0 | 0 | 7.0868 | 0 | 0 | 7.0868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 7.0868
473 | 14 | 27 | 26 | 13.0966 | 12.4 | 7.0464 | 0 | 0 | 0 | 1.9983 | 0 | 0 | 1.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 1.9983
474 | 16 | 4 | 4 | 10.4773 | 12 | 8.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
475 | 0 | 0 | 0 | 4.8357 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
476 | 0 | 0 | 0 | 8.0595 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
477 | 0 | 0 | 0 | 3.2238 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
478 | 0 | 0 | 0 | 3.6268 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
479 | 0 | 0 | 0 | 5.8431 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
480 | 0 | 0 | 0 | 2.0149 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
481 | 0 | 0 | 0 | 1.4104 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
482 | 0 | 0 | 0 | 2.4178 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
483 | 0 | 0 | 0 | 2.4178 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
484 | 0 | 0 | 0 | 1.6119 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
485 | 0 | 0 | 0 | 1.8134 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
486 | 0 | 0 | 0 | 2.4178 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
487 | 0 | 0 | 0 | 2.6193 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 0
488 | 193 | 23 | 9 | 2.2164 | 3.5 | 97.1403 | 0 | 39.4724 | 0 | 2.37 | 0 | 0 | 2.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.6812 | 15.9% | 0 | 0 | 0.99894 | 1.998% | 2.37
489 | 708 | 174 | 32 | 2.2164 | 7 | 356.3487 | 185.6828 | 0 | 155.6096 | 38.7328 | 0 | 0 | 38.7328 | 0 | 0 | 0 | 0 | 0 | 155.6096 | 0 | 351.6244 | 27.59% | 0 | 0 | 0.99894 | 1.998% | 38.7328
490 | 875 | 350 | 44 | 6.4476 | 10.2 | 440.4027 | 259.4387 | 0 | 222.4733 | 80.7614 | 0 | 15.3807 | 65.3807 | 0 | 0 | 0 | 0 | 0 | 222.4733 | 0 | 564.5668 | 44.3% | 11.797 | 0 | 12.8308 | 25.66% | 50
491 | 945 | 490 | 49 | 8.0595 | 12.4 | 475.6349 | 292.6106 | 0 | 252.7648 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 252.7648 | 0 | 806.503 | 63.28% | 19.175 | 0 | 32.0625 | 64.12% | 50
492 | 977 | 581 | 57 | 8.6639 | 13 | 491.7411 | 307.2072 | 0 | 265.9186 | 100 | 1.6838 | 23.3162 | 75 | 0 | 0 | 0 | 0 | 0 | 265.9186 | 0 | 1061.0294 | 83.25% | 17.8835 | 0 | 49.9989 | 100% | 50
493 | 868 | 562 | 79 | 7.858 | 13.5 | 436.8795 | 268.4514 | 0 | 230.0766 | 100.3 | 25.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 230.0766 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 49.7
494 | 564 | 441 | 148 | 8.6639 | 13.5 | 283.871 | 0 | 166.8435 | 0 | 84.3835 | 17.5418 | 0 | 66.8418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 49.3
495 | 918 | 482 | 79 | 10.6788 | 13.7 | 462.0454 | 0 | 239.7248 | 0 | 100.7 | 25.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 49.3
496 | 828 | 317 | 57 | 9.2684 | 12.8 | 416.7468 | 0 | 167.5513 | 0 | 70.042 | 10.021 | 0 | 60.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 50
497 | 562 | 124 | 33 | 10.8803 | 11.4 | 282.8644 | 0 | 0 | 0 | 24.1231 | 0 | 0 | 24.1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.9288 | 49.86% | 49.1231
498 | 52 | 6 | 3 | 7.455 | 9.9 | 26.1725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.8194 | 25.1397 | 0 | 64.8194 | 1214.9425 | 95.33% | 0 | 24.8603 | 0 | 0% | 50
499 | 0 | 0 | 0 | 3.6268 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.7389 | 50 | 0 | 123.7389 | 1086.9683 | 85.29% | 0 | 0 | 0 | 0% | 50
500 | 0 | 0 | 0 | 1.4104 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.0133 | 48.9 | 0 | 121.0133 | 962.1996 | 75.5% | 0 | 0 | 0 | 0% | 48.9
501 | 0 | 0 | 0 | 2.0149 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.4228 | 44.1 | 0 | 109.4228 | 851.2818 | 66.79% | 0 | 0 | 0 | 0% | 44.1
502 | 0 | 0 | 0 | 3.0223 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2328 | 40.7 | 0 | 101.2328 | 750.0571 | 58.85% | 0 | 0 | 0 | 0% | 40.7
503 | 0 | 0 | 0 | 3.2238 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7881 | 37.6 | 0 | 93.7881 | 657.6917 | 51.6% | 0 | 0 | 0 | 0% | 37.6
504 | 0 | 0 | 0 | 3.4253 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9196 | 36 | 0 | 89.9196 | 569.836 | 44.71% | 0 | 0 | 0 | 0% | 36
505 | 0 | 0 | 0 | 2.8208 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2634 | 35.3 | 0 | 88.2634 | 483.9247 | 37.97% | 0 | 0 | 0 | 0% | 35.3
506 | 0 | 0 | 0 | 1.8134 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.949 | 35.2 | 0 | 87.949 | 398.2745 | 31.25% | 0 | 0 | 0 | 0% | 35.2
507 | 0 | 0 | 0 | 2.4178 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5997 | 36.3 | 0 | 90.5997 | 309.5169 | 24.29% | 0 | 0 | 0 | 0% | 36.3
508 | 0 | 0 | 0 | 5.0372 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.9877 | 40.2 | 0 | 99.9877 | 209.5712 | 16.44% | 0 | 0 | 0 | 0% | 40.2
509 | 0 | 0 | 0 | 3.0223 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.5712 | 16.44% | 0 | 0 | 0 | 0% | 0
510 | 0 | 0 | 0 | 4.6342 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.5712 | 16.44% | 0 | 0 | 0 | 0% | 0
511 | 0 | 0 | 0 | 3.0223 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.5712 | 16.44% | 0 | 0 | 0 | 0% | 0
512 | 192 | 41 | 27 | 2.6193 | 3.8 | 96.6369 | 0 | 39.5186 | 0 | 3.922 | 0 | 0 | 3.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.5712 | 16.44% | 0 | 0 | 0 | 0% | 3.922
513 | 288 | 165 | 115 | 9.6714 | 8.2 | 144.9554 | 75.7969 | 0 | 48.3228 | 28.0525 | 0 | 0 | 28.0525 | 0 | 0 | 0 | 0 | 0 | 48.3228 | 0 | 256.2185 | 20.1% | 0 | 0 | 0 | 0% | 28.0525
514 | 11 | 150 | 145 | 12.2907 | 8.8 | 5.5365 | 0 | 3.2667 | 0 | 13.404 | 0 | 0 | 13.404 | 0 | 0 | 0 | 60.8317 | 23.3998 | 0 | 60.8317 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 36.8038
515 | 0 | 157 | 155 | 8.6639 | 9.7 | 0 | 0 | 0 | 0 | 12.786 | 0 | 0 | 12.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 12.786
516 | 12 | 219 | 210 | 9.6714 | 10.4 | 6.0398 | 0 | 3.7792 | 0 | 19.0215 | 0 | 0 | 19.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 19.0215
517 | 7 | 280 | 272 | 6.4476 | 11.2 | 3.5232 | 0 | 2.1678 | 0 | 24.8283 | 0 | 0 | 24.8283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 24.8283
518 | 5 | 217 | 211 | 5.2387 | 11.3 | 2.5166 | 0 | 1.4806 | 0 | 18.446 | 0 | 0 | 18.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 18.446
519 | 0 | 127 | 125 | 4.4327 | 10.9 | 0 | 0 | 0 | 0 | 9.9005 | 0 | 0 | 9.9005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 9.9005
520 | 0 | 114 | 112 | 5.2387 | 11 | 0 | 0 | 0 | 0 | 9.2669 | 0 | 0 | 9.2669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 9.2669
521 | 110 | 54 | 41 | 8.8654 | 11 | 55.3649 | 0 | 0 | 0 | 8.253 | 0 | 0 | 8.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 8.253
522 | 14 | 4 | 3 | 12.0892 | 9.9 | 7.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
523 | 0 | 0 | 0 | 12.4922 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
524 | 0 | 0 | 0 | 16.9249 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
525 | 0 | 0 | 0 | 19.5442 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
526 | 0 | 0 | 0 | 18.9398 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
527 | 0 | 0 | 0 | 16.9249 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
528 | 0 | 0 | 0 | 16.5219 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
529 | 0 | 0 | 0 | 16.9249 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
530 | 0 | 0 | 0 | 12.0892 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
531 | 0 | 0 | 0 | 17.3279 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
532 | 0 | 0 | 0 | 12.8952 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
533 | 0 | 0 | 0 | 7.2535 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
534 | 0 | 0 | 0 | 5.0372 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
535 | 0 | 0 | 0 | 2.2164 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0
536 | 0 | 9 | 9 | 5.8431 | 7.5 | 0 | 0 | 0 | 0 | 0.098136 | 0 | 0 | 0.098136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3639 | 15.72% | 0 | 0 | 0 | 0% | 0.098136
537 | 325 | 129 | 52 | 19.1413 | 9.3 | 163.5782 | 85.8379 | 0 | 52.6566 | 23.1438 | 0 | 0 | 23.1438 | 0 | 0 | 0 | 0 | 0 | 52.6566 | 0 | 251.0457 | 19.7% | 0 | 0 | 0 | 0% | 23.1438
538 | 546 | 289 | 84 | 23.9769 | 10.1 | 274.8113 | 162.4114 | 0 | 121.3096 | 49.7391 | 0 | 0 | 49.7391 | 0 | 0 | 0 | 0 | 0 | 121.3096 | 0 | 367.8059 | 28.86% | 0 | 0 | 0 | 0% | 49.7391
539 | 507 | 420 | 174 | 27.2007 | 11.5 | 255.1819 | 157.5187 | 0 | 114.9682 | 76.461 | 0 | 13.2305 | 63.2305 | 0 | 0 | 0 | 0 | 0 | 114.9682 | 0 | 478.4624 | 37.54% | 10.1478 | 0 | 10.1797 | 20.36% | 50
540 | 617 | 527 | 185 | 27.2007 | 12.8 | 310.5468 | 194.6228 | 0 | 149.712 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 149.712 | 0 | 622.5598 | 48.85% | 19.175 | 0 | 29.4149 | 58.83% | 50
541 | 423 | 498 | 251 | 27.8052 | 13.3 | 212.9033 | 131.1818 | 0 | 90.0383 | 84.182 | 0 | 17.091 | 67.091 | 0 | 0 | 0 | 0 | 0 | 90.0383 | 0 | 709.2214 | 55.65% | 13.1088 | 0 | 42.5649 | 85.13% | 50
542 | 423 | 527 | 293 | 20.9546 | 14.4 | 212.9033 | 125.3841 | 0 | 88.6948 | 89.4018 | 10.0375 | 9.6634 | 69.7009 | 0 | 0 | 0 | 0 | 0 | 88.6948 | 0 | 794.5899 | 62.34% | 7.4118 | 0 | 50 | 100% | 50
543 | 294 | 362 | 219 | 16.7234 | 14.8 | 147.9753 | 77.0723 | 0 | 45.3919 | 47.3606 | 0 | 0 | 47.3606 | 0 | 0 | 0 | 0 | 0 | 45.3919 | 0 | 838.2795 | 65.77% | 0 | 2.6394 | 47.3527 | 94.71% | 50
544 | 63 | 176 | 155 | 17.1264 | 14.5 | 31.709 | 0 | 12.8281 | 0 | 19.3276 | 0 | 0 | 19.3276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 838.2795 | 65.77% | 0 | 25 | 22.278 | 44.56% | 44.3276
545 | 32 | 58 | 53 | 19.9472 | 13.1 | 16.1062 | 0 | 0 | 0 | 5.5856 | 0 | 0 | 5.5856 | 0 | 0 | 0 | 58.3903 | 22.2026 | 0 | 58.3903 | 784.878 | 61.58% | 0 | 22.2118 | 0 | 0% | 50
546 | 42 | 10 | 8 | 23.7755 | 12.5 | 21.1393 | 0 | 0 | 0 | 0.23074 | 0 | 0 | 0.23074 | 0 | 0 | 0 | 123.4814 | 49.7693 | 0 | 123.4814 | 657.3657 | 51.58% | 0 | 0 | 0 | 0% | 50
547 | 0 | 0 | 0 | 17.7308 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.0399 | 50 | 0 | 124.0399 | 529.1489 | 41.52% | 0 | 0 | 0 | 0% | 50
548 | 0 | 0 | 0 | 18.9398 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.3945 | 48.9 | 0 | 121.3945 | 404.1462 | 31.71% | 0 | 0 | 0 | 0% | 48.9
549 | 0 | 0 | 0 | 20.1487 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5069 | 44 | 0 | 109.5069 | 293.3339 | 23.02% | 0 | 0 | 0 | 0% | 44
550 | 0 | 0 | 0 | 17.9323 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0754 | 37.5663 | 0 | 94.0754 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 37.5663
551 | 0 | 0 | 0 | 12.2907 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0
552 | 0 | 0 | 0 | 8.8654 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0
553 | 0 | 0 | 0 | 13.4996 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0
554 | 0 | 0 | 0 | 14.7085 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0
555 | 0 | 0 | 0 | 15.716 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0
556 | 0 | 0 | 0 | 11.6862 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0
557 | 0 | 0 | 0 | 9.2684 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0
558 | 0 | 0 | 0 | 10.2758 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0
559 | 0 | 0 | 0 | 8.4625 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0
560 | 0 | 12 | 12 | 10.0743 | 13.7 | 0 | 0 | 0 | 0 | 0.24444 | 0 | 0 | 0.24444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 0.24444
561 | 6 | 103 | 100 | 14.1041 | 14.3 | 3.0199 | 0 | 1.5904 | 0 | 9.2975 | 0 | 0 | 9.2975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 9.2975
562 | 58 | 234 | 209 | 13.0966 | 15.4 | 29.1924 | 0 | 17.2808 | 0 | 25.513 | 0 | 0 | 25.513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.916 | 15.76% | 0 | 0 | 0 | 0% | 25.513
563 | 219 | 383 | 270 | 13.0966 | 17 | 110.2265 | 68.159 | 0 | 39.3986 | 46.1617 | 0 | 0 | 46.1617 | 0 | 0 | 0 | 0 | 0 | 39.3986 | 0 | 239.2382 | 18.77% | 0 | 0 | 0 | 0% | 46.1617
564 | 331 | 488 | 298 | 14.1041 | 18 | 166.5981 | 104.5802 | 0 | 73.1337 | 73.0928 | 0 | 11.5464 | 61.5464 | 0 | 0 | 0 | 0 | 0 | 73.1337 | 0 | 310.3738 | 24.35% | 8.8561 | 0 | 8.8852 | 17.77% | 50
565 | 393 | 522 | 291 | 11.8877 | 18.7 | 197.8037 | 122.0526 | 0 | 91.097 | 83.6932 | 0 | 17.1466 | 66.5466 | 0 | 0 | 0 | 0 | 0 | 91.097 | 0 | 398.982 | 31.3% | 13.1515 | 0 | 22.0798 | 44.16% | 49.4
566 | 480 | 506 | 244 | 9.4699 | 19.1 | 241.5923 | 142.4323 | 0 | 111.6013 | 85.3585 | 0 | 18.2292 | 67.1292 | 0 | 0 | 0 | 0 | 0 | 111.6013 | 0 | 507.5343 | 39.82% | 13.9818 | 0 | 36.1076 | 72.22% | 48.9
567 | 343 | 412 | 252 | 7.455 | 18.6 | 172.6379 | 90.0976 | 0 | 63.968 | 58.171 | 0 | 4.6855 | 53.4855 | 0 | 0 | 0 | 0 | 0 | 63.968 | 0 | 569.7546 | 44.7% | 3.5938 | 0 | 39.7132 | 79.43% | 48.8
568 | 272 | 279 | 188 | 9.8729 | 18.5 | 136.9023 | 0 | 55.572 | 0 | 37.3033 | 0 | 0 | 37.3033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.7546 | 44.7% | 0 | 12.6967 | 26.9767 | 53.95% | 50
569 | 217 | 136 | 99 | 13.4996 | 17.5 | 109.2199 | 0 | 0 | 0 | 19.6503 | 0 | 0 | 19.6503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.7546 | 44.7% | 0 | 25 | 1.8979 | 3.796% | 44.6503
570 | 18 | 11 | 10 | 11.8877 | 16 | 9.0597 | 0 | 0 | 0 | 0.23917 | 0 | 0 | 0.23917 | 0 | 0 | 0 | 123.765 | 49.7608 | 0 | 123.765 | 442.2169 | 34.7% | 0 | 0 | 1.8979 | 3.796% | 50
571 | 0 | 0 | 0 | 10.2758 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.2697 | 50 | 0 | 124.2697 | 313.9405 | 24.63% | 0 | 0 | 1.8979 | 3.796% | 50
572 | 0 | 0 | 0 | 9.2684 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.9382 | 45.3299 | 0 | 112.9382 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 45.3299
573 | 0 | 0 | 0 | 7.6565 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
574 | 0 | 0 | 0 | 5.6416 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
575 | 0 | 0 | 0 | 4.6342 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
576 | 0 | 0 | 0 | 4.6342 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
577 | 0 | 0 | 0 | 3.2238 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
578 | 0 | 0 | 0 | 2.6193 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
579 | 0 | 0 | 0 | 3.6268 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
580 | 0 | 0 | 0 | 3.8283 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
581 | 0 | 0 | 0 | 1.8134 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
582 | 0 | 0 | 0 | 3.2238 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
583 | 0 | 0 | 0 | 3.8283 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 0
584 | 185 | 25 | 10 | 3.8283 | 11.3 | 93.1137 | 0 | 38.8181 | 0 | 2.4432 | 0 | 0 | 2.4432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2851 | 15.64% | 0 | 0 | 1.8979 | 3.796% | 2.4432
585 | 686 | 176 | 33 | 5.6416 | 14.7 | 345.2757 | 182.4892 | 0 | 151.2835 | 37.9666 | 0 | 0 | 37.9666 | 0 | 0 | 0 | 0 | 0 | 151.2835 | 0 | 347.517 | 27.27% | 0 | 0 | 1.8979 | 3.796% | 37.9666
586 | 856 | 351 | 43 | 5.6416 | 17.2 | 430.8397 | 255.466 | 0 | 219.3944 | 74.7759 | 0 | 12.3879 | 62.3879 | 0 | 0 | 0 | 0 | 0 | 219.3944 | 0 | 562.4859 | 44.13% | 9.5015 | 0 | 11.4317 | 22.86% | 50
587 | 927 | 490 | 49 | 4.6342 | 18.5 | 466.5752 | 289.0197 | 0 | 251.4821 | 100.2 | 0.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 251.4821 | 0 | 808.8951 | 63.47% | 19.175 | 0 | 30.6719 | 61.34% | 49.8
588 | 950 | 573 | 53 | 5.2387 | 19.4 | 478.1515 | 300.6598 | 0 | 262.088 | 102.1 | 2.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 262.088 | 0 | 1065.6964 | 83.62% | 19.175 | 0 | 49.9121 | 99.82% | 47.9
589 | 964 | 604 | 57 | 6.0446 | 19.8 | 485.198 | 299.8274 | 0 | 260.8296 | 103.2 | 28.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 260.8296 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9121 | 99.82% | 46.8
590 | 904 | 557 | 73 | 7.2535 | 20.2 | 454.9989 | 0 | 268.5469 | 0 | 103.9 | 28.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9121 | 99.82% | 46.1
591 | 886 | 459 | 59 | 7.2535 | 19.8 | 445.9392 | 0 | 233.2173 | 0 | 102.8248 | 28.4624 | 0 | 74.3624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9121 | 99.82% | 45.9
592 | 813 | 310 | 45 | 5.8431 | 19.3 | 409.197 | 0 | 166.6922 | 0 | 64.3938 | 8.4469 | 0 | 55.9469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9121 | 99.82% | 47.5
593 | 607 | 135 | 30 | 4.6342 | 18.4 | 305.5137 | 0 | 0 | 0 | 26.7566 | 0 | 0 | 26.7566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.1434 | 26.6936 | 53.39% | 49.9
594 | 76 | 9 | 5 | 3.0223 | 15.6 | 38.2521 | 0 | 0 | 0 | 0.23757 | 0 | 0 | 0.23757 | 0 | 0 | 0 | 64.5308 | 24.7624 | 0 | 64.5308 | 1215.3114 | 95.36% | 0 | 25 | 1.6113 | 3.223% | 50
595 | 0 | 0 | 0 | 2.2164 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.1566 | 49.2 | 0 | 122.1566 | 1089.7884 | 85.51% | 0 | 0 | 1.6113 | 3.223% | 49.2
596 | 0 | 0 | 0 | 1.4104 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.7335 | 46.2 | 0 | 114.7335 | 972.9664 | 76.34% | 0 | 0 | 1.6113 | 3.223% | 46.2
597 | 0 | 0 | 0 | 1.8134 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6911 | 42.5 | 0 | 105.6911 | 866.7659 | 68.01% | 0 | 0 | 1.6113 | 3.223% | 42.5
598 | 0 | 0 | 0 | 1.6119 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.6685 | 40 | 0 | 99.6685 | 767.6253 | 60.23% | 0 | 0 | 1.6113 | 3.223% | 40
599 | 0 | 0 | 0 | 4.6342 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9818 | 37.2 | 0 | 92.9818 | 676.4992 | 53.08% | 0 | 0 | 1.6113 | 3.223% | 37.2
600 | 0 | 0 | 0 | 3.8283 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4514 | 34.9 | 0 | 87.4514 | 591.829 | 46.44% | 0 | 0 | 1.6113 | 3.223% | 34.9
601 | 0 | 0 | 0 | 5.4401 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0376 | 33.9 | 0 | 85.0376 | 510.0525 | 40.02% | 0 | 0 | 1.6113 | 3.223% | 33.9
602 | 0 | 0 | 0 | 5.8431 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.122 | 33.5 | 0 | 84.122 | 429.4141 | 33.69% | 0 | 0 | 1.6113 | 3.223% | 33.5
603 | 0 | 0 | 0 | 4.2312 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3374 | 33.2 | 0 | 83.3374 | 349.629 | 27.43% | 0 | 0 | 1.6113 | 3.223% | 33.2
604 | 0 | 0 | 0 | 3.6268 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4767 | 34.1 | 0 | 85.4767 | 267.2357 | 20.97% | 0 | 0 | 1.6113 | 3.223% | 34.1
605 | 0 | 0 | 0 | 4.2312 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.0269 | 25.2834 | 0 | 65.0269 | 207.409 | 16.27% | 0 | 0 | 1.6113 | 3.223% | 25.2834
606 | 0 | 0 | 0 | 5.4401 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.409 | 16.27% | 0 | 0 | 1.6113 | 3.223% | 0
607 | 0 | 0 | 0 | 3.2238 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.409 | 16.27% | 0 | 0 | 1.6113 | 3.223% | 0
608 | 203 | 28 | 11 | 3.0223 | 6.8 | 102.1734 | 0 | 42.871 | 0 | 2.8233 | 0 | 0 | 2.8233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207.409 | 16.27% | 0 | 0 | 1.6113 | 3.223% | 2.8233
609 | 711 | 184 | 34 | 1.2089 | 11.1 | 357.8587 | 189.8284 | 0 | 159.8755 | 39.0569 | 0 | 0 | 39.0569 | 0 | 0 | 0 | 0 | 0 | 159.8755 | 0 | 360.4442 | 28.28% | 0 | 0 | 1.6113 | 3.223% | 39.0569
610 | 872 | 361 | 45 | 1.2089 | 14.8 | 438.8928 | 260.6797 | 0 | 226.015 | 80.5965 | 0 | 18.3482 | 62.2482 | 0 | 0 | 0 | 0 | 0 | 226.015 | 0 | 576.7891 | 45.26% | 14.0731 | 0 | 15.7341 | 31.47% | 43.9
611 | 941 | 502 | 51 | 7.6565 | 16.3 | 473.6217 | 293.9135 | 0 | 254.3038 | 106.4 | 6.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 254.3038 | 0 | 820.2125 | 64.36% | 19.175 | 0 | 34.9769 | 69.95% | 43.6
612 | 972 | 590 | 53 | 8.4625 | 17.2 | 489.2245 | 308.1522 | 0 | 267.0158 | 107.6 | 13.0845 | 19.5155 | 75 | 0 | 0 | 0 | 0 | 0 | 267.0158 | 0 | 1075.8041 | 84.41% | 14.9684 | 0 | 49.9983 | 100% | 42.4
613 | 978 | 614 | 55 | 8.4625 | 17.7 | 492.2444 | 304.6426 | 0 | 263.7681 | 109.6 | 34.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 263.7681 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9983 | 100% | 40.4
614 | 961 | 572 | 54 | 8.4625 | 18.1 | 483.688 | 0 | 285.8107 | 0 | 110.7 | 35.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9983 | 100% | 39.3
615 | 919 | 471 | 51 | 9.4699 | 17.9 | 462.5487 | 0 | 242.4318 | 0 | 111.1 | 36.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9983 | 100% | 38.9
616 | 828 | 319 | 45 | 9.4699 | 17.4 | 416.7468 | 0 | 170.3982 | 0 | 74.7775 | 16.8888 | 0 | 57.8888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9983 | 100% | 41
617 | 611 | 139 | 31 | 8.4625 | 16 | 307.5269 | 0 | 0 | 0 | 27.9779 | 0 | 0 | 27.9779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 15.9221 | 34.0223 | 68.04% | 43.9
618 | 83 | 10 | 5 | 6.4476 | 13.2 | 41.7753 | 0 | 0 | 0 | 0.31786 | 0 | 0 | 0.31786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 8.9369 | 17.87% | 25.3179
619 | 0 | 0 | 0 | 1.8134 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1381 | 35.991 | 0 | 90.1381 | 1186.9274 | 93.13% | 0 | 8.909 | 0 | 0% | 44.9
620 | 0 | 0 | 0 | 1.0074 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.133 | 43.1 | 0 | 107.133 | 1079.133 | 84.67% | 0 | 0 | 0 | 0% | 43.1
621 | 0 | 0 | 0 | 3.4253 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0573 | 40.2 | 0 | 100.0573 | 979.5437 | 76.86% | 0 | 0 | 0 | 0% | 40.2
622 | 0 | 0 | 0 | 1.2089 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4174 | 37 | 0 | 92.4174 | 889.1028 | 69.76% | 0 | 0 | 0 | 0% | 37
623 | 0 | 0 | 0 | 1.0074 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1697 | 34.4 | 0 | 86.1697 | 805.9999 | 63.24% | 0 | 0 | 0 | 0% | 34.4
624 | 0 | 0 | 0 | 2.6193 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.639 | 32.5 | 0 | 81.639 | 728.3372 | 57.15% | 0 | 0 | 0 | 0% | 32.5
625 | 0 | 0 | 0 | 4.4327 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5033 | 31.2 | 0 | 78.5033 | 654.3218 | 51.34% | 0 | 0 | 0 | 0% | 31.2
626 | 0 | 0 | 0 | 2.4178 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7906 | 30.9 | 0 | 77.7906 | 581.1324 | 45.6% | 0 | 0 | 0 | 0% | 30.9
627 | 0 | 0 | 0 | 2.4178 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7997 | 30.9 | 0 | 77.7997 | 507.9306 | 39.85% | 0 | 0 | 0 | 0% | 30.9
628 | 0 | 0 | 0 | 4.6342 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9999 | 31.4 | 0 | 78.9999 | 433.3156 | 34% | 0 | 0 | 0 | 0% | 31.4
629 | 0 | 0 | 0 | 5.8431 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3806 | 32.4 | 0 | 81.3806 | 355.8571 | 27.92% | 0 | 0 | 0 | 0% | 32.4
630 | 0 | 0 | 0 | 5.6416 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2592 | 33.6 | 0 | 84.2592 | 274.9523 | 21.57% | 0 | 0 | 0 | 0% | 33.6
631 | 0 | 0 | 0 | 3.4253 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.443 | 31.1624 | 0 | 78.443 | 200.9457 | 15.77% | 0 | 0 | 0 | 0% | 31.1624
632 | 156 | 25 | 12 | 5.6416 | 9.7 | 78.5175 | 0 | 33.159 | 0 | 2.5779 | 0 | 0 | 2.5779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.9457 | 15.77% | 0 | 0 | 0 | 0% | 2.5779
633 | 697 | 187 | 37 | 9.4699 | 13 | 350.8122 | 186.7732 | 0 | 152.8651 | 39.4973 | 0 | 0 | 39.4973 | 0 | 0 | 0 | 0 | 0 | 152.8651 | 0 | 345.2812 | 27.09% | 0 | 0 | 0 | 0% | 39.4973
634 | 893 | 373 | 48 | 12.8952 | 16.4 | 449.4624 | 267.4126 | 0 | 226.0331 | 93.0536 | 1.2768 | 25 | 66.7768 | 0 | 0 | 0 | 0 | 0 | 226.0331 | 0 | 558.7019 | 43.84% | 19.175 | 0 | 19.2455 | 38.49% | 40.5
635 | 965 | 519 | 54 | 17.7308 | 18.7 | 485.7013 | 301.9622 | 0 | 255.7164 | 109.2 | 9.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 255.7164 | 0 | 800.1496 | 62.78% | 19.175 | 0 | 38.4911 | 76.98% | 40.8
636 | 1002 | 615 | 61 | 20.3502 | 20.1 | 504.324 | 318.2225 | 0 | 269.3605 | 109.6 | 19.6499 | 14.9501 | 75 | 0 | 0 | 0 | 0 | 0 | 269.3605 | 0 | 1054.4802 | 82.74% | 11.4667 | 0 | 50 | 100% | 40.4
637 | 991 | 642 | 74 | 20.9546 | 20 | 498.7875 | 309.1722 | 0 | 260.5934 | 111.6 | 36.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 260.5934 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.4
638 | 989 | 642 | 107 | 17.5294 | 20.1 | 497.7809 | 0 | 294.492 | 0 | 112.7 | 37.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.3
639 | 780 | 475 | 119 | 11.2833 | 19.6 | 392.5876 | 0 | 206.2312 | 0 | 112.3391 | 37.5195 | 0 | 74.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.3
640 | 841 | 330 | 49 | 14.1041 | 17.6 | 423.2899 | 0 | 173.7446 | 0 | 79.6485 | 19.9742 | 0 | 59.6742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.7
641 | 643 | 147 | 33 | 13.9026 | 15.7 | 323.6331 | 0 | 0 | 0 | 30.2206 | 0 | 0 | 30.2206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 12.9794 | 36.9748 | 73.95% | 43.2
642 | 96 | 11 | 5 | 12.2907 | 13.4 | 48.3185 | 0 | 0 | 0 | 0.38861 | 0 | 0 | 0.38861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 11.886 | 23.77% | 25.3886
643 | 0 | 0 | 0 | 4.2312 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8937 | 33.3554 | 0 | 83.8937 | 1194.4781 | 93.72% | 0 | 11.8446 | 0 | 0% | 45.2
644 | 0 | 0 | 0 | 2.0149 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.6902 | 43.7 | 0 | 108.6902 | 1084.9992 | 85.13% | 0 | 0 | 0 | 0% | 43.7
645 | 0 | 0 | 0 | 1.6119 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4294 | 39.9 | 0 | 99.4294 | 986.2925 | 77.39% | 0 | 0 | 0 | 0% | 39.9
646 | 0 | 0 | 0 | 2.0149 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2141 | 36.5 | 0 | 91.2141 | 897.2899 | 70.4% | 0 | 0 | 0 | 0% | 36.5
647 | 0 | 0 | 0 | 2.0149 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2314 | 34 | 0 | 85.2314 | 815.3755 | 63.98% | 0 | 0 | 0 | 0% | 34
648 | 0 | 0 | 0 | 3.0223 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6189 | 32.5 | 0 | 81.6189 | 737.7303 | 57.88% | 0 | 0 | 0 | 0% | 32.5
649 | 0 | 0 | 0 | 2.6193 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3933 | 32 | 0 | 80.3933 | 661.4891 | 51.9% | 0 | 0 | 0 | 0% | 32
650 | 0 | 0 | 0 | 3.2238 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6886 | 32.1 | 0 | 80.6886 | 584.9603 | 45.9% | 0 | 0 | 0 | 0% | 32.1
651 | 0 | 0 | 0 | 2.4178 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7995 | 33.4 | 0 | 83.7995 | 504.7175 | 39.6% | 0 | 0 | 0 | 0% | 33.4
652 | 0 | 0 | 0 | 2.4178 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0178 | 38.1 | 0 | 95.0178 | 411.0712 | 32.25% | 0 | 0 | 0 | 0% | 38.1
653 | 0 | 0 | 0 | 3.2238 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.8231 | 45.1 | 0 | 111.8231 | 297.3777 | 23.33% | 0 | 0 | 0 | 0% | 45.1
654 | 0 | 0 | 0 | 3.0223 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.8203 | 43.0132 | 0 | 106.8203 | 189.6634 | 14.88% | 0 | 0 | 0 | 0% | 43.0132
655 | 0 | 0 | 0 | 2.4178 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.6634 | 14.88% | 0 | 0 | 0 | 0% | 0
656 | 213 | 30 | 11 | 2.6193 | 6.4 | 107.2066 | 0 | 45.569 | 0 | 2.9514 | 0 | 0 | 2.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.6634 | 14.88% | 0 | 0 | 0 | 0% | 2.9514
657 | 730 | 193 | 36 | 2.8208 | 10.6 | 367.4217 | 196.3382 | 0 | 165.3691 | 40.6313 | 0 | 0 | 40.6313 | 0 | 0 | 0 | 0 | 0 | 165.3691 | 0 | 347.6417 | 27.28% | 0 | 0 | 0 | 0% | 40.6313
658 | 831 | 367 | 61 | 1.2089 | 13.7 | 418.2567 | 249.2753 | 0 | 215.397 | 74.4017 | 0 | 12.2008 | 62.2008 | 0 | 0 | 0 | 0 | 0 | 215.397 | 0 | 553.4119 | 43.42% | 9.358 | 0 | 9.3938 | 18.79% | 50
659 | 896 | 503 | 67 | 4.2312 | 15.6 | 450.9724 | 280.8932 | 0 | 243.8949 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 243.8949 | 0 | 786.4064 | 61.7% | 19.175 | 0 | 28.6421 | 57.28% | 50
660 | 1001 | 617 | 60 | 14.3056 | 17.7 | 503.8207 | 318.4766 | 0 | 273.0228 | 100.8 | 0.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 273.0228 | 0 | 1047.2269 | 82.17% | 19.175 | 0 | 47.8904 | 95.78% | 49.2
661 | 914 | 634 | 103 | 16.7234 | 18.7 | 460.0321 | 285.6045 | 0 | 240.9867 | 101.6 | 23.86 | 2.74 | 75 | 0 | 0 | 0 | 0 | 0 | 240.9867 | 0 | 1274.5104 | 100% | 2.1016 | 0 | 50 | 100% | 48.4
662 | 942 | 592 | 77 | 13.2981 | 19.9 | 474.125 | 0 | 280.8464 | 0 | 102.1 | 27.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.9
663 | 946 | 492 | 53 | 15.716 | 20.3 | 476.1382 | 0 | 250.7119 | 0 | 102.2 | 27.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.8
664 | 862 | 341 | 49 | 18.7383 | 19.7 | 433.8596 | 0 | 178.8019 | 0 | 72.6201 | 11.6601 | 0 | 60.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.3
665 | 577 | 141 | 34 | 15.9175 | 18.2 | 290.4141 | 0 | 0 | 0 | 28.0138 | 0 | 0 | 28.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 21.9862 | 27.9332 | 55.87% | 50
666 | 46 | 10 | 6 | 12.8952 | 15.5 | 23.1526 | 0 | 0 | 0 | 0.19858 | 0 | 0 | 0.19858 | 0 | 0 | 0 | 64.6119 | 24.8014 | 0 | 64.6119 | 1215.3066 | 95.35% | 0 | 25 | 2.8403 | 5.681% | 50
667 | 0 | 0 | 0 | 7.6565 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.2484 | 47.169 | 0 | 117.2484 | 1095.8649 | 85.98% | 0 | 2.831 | 0 | 0% | 50
668 | 0 | 0 | 0 | 9.4699 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.5339 | 46.9 | 0 | 116.5339 | 977.1845 | 76.67% | 0 | 0 | 0 | 0% | 46.9
669 | 0 | 0 | 0 | 4.2312 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6568 | 42.4 | 0 | 105.6568 | 871.4113 | 68.37% | 0 | 0 | 0 | 0% | 42.4
670 | 0 | 0 | 0 | 2.2164 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5524 | 39.1 | 0 | 97.5524 | 775.0005 | 60.81% | 0 | 0 | 0 | 0% | 39.1
671 | 0 | 0 | 0 | 4.2312 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3385 | 36.5 | 0 | 91.3385 | 685.9695 | 53.82% | 0 | 0 | 0 | 0% | 36.5
672 | 0 | 0 | 0 | 3.4253 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4867 | 34.9 | 0 | 87.4867 | 601.4098 | 47.19% | 0 | 0 | 0 | 0% | 34.9
673 | 0 | 0 | 0 | 3.8283 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2949 | 34.4 | 0 | 86.2949 | 518.2916 | 40.67% | 0 | 0 | 0 | 0% | 34.4
674 | 0 | 0 | 0 | 3.2238 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8233 | 34.2 | 0 | 85.8233 | 435.7372 | 34.19% | 0 | 0 | 0 | 0% | 34.2
675 | 0 | 0 | 0 | 4.0297 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1467 | 35.2 | 0 | 88.1467 | 350.277 | 27.48% | 0 | 0 | 0 | 0% | 35.2
676 | 0 | 0 | 0 | 2.6193 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6953 | 39.2 | 0 | 97.6953 | 253.4646 | 19.89% | 0 | 0 | 0 | 0% | 39.2
677 | 0 | 0 | 0 | 3.4253 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.4646 | 19.89% | 0 | 0 | 0 | 0% | 0
678 | 0 | 0 | 0 | 2.6193 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.4646 | 19.89% | 0 | 0 | 0 | 0% | 0
679 | 0 | 0 | 0 | 2.6193 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.4646 | 19.89% | 0 | 0 | 0 | 0% | 0
680 | 104 | 30 | 22 | 4.0297 | 6.9 | 52.345 | 0 | 22.3944 | 0 | 2.8863 | 0 | 0 | 2.8863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.4646 | 19.89% | 0 | 0 | 0 | 0% | 2.8863
681 | 37 | 96 | 88 | 3.6268 | 9.9 | 18.6227 | 0 | 9.9876 | 0 | 9.9299 | 0 | 0 | 9.9299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.4646 | 19.89% | 0 | 0 | 0 | 0% | 9.9299
682 | 20 | 160 | 149 | 7.052 | 12.1 | 10.0663 | 0 | 6.0098 | 0 | 14.0234 | 0 | 0 | 14.0234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.4646 | 19.89% | 0 | 0 | 0 | 0% | 14.0234
683 | 21 | 199 | 185 | 9.0669 | 12.6 | 10.5697 | 0 | 6.5959 | 0 | 17.2428 | 0 | 0 | 17.2428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.4646 | 19.89% | 0 | 0 | 0 | 0% | 17.2428
684 | 91 | 242 | 185 | 5.8431 | 13.9 | 45.8019 | 0 | 29.0056 | 0 | 26.1188 | 0 | 0 | 26.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.4646 | 19.89% | 0 | 0 | 0 | 0% | 26.1188
685 | 742 | 544 | 109 | 12.2907 | 17.4 | 373.4615 | 232.2371 | 0 | 193.8255 | 100.5 | 0.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 193.8255 | 0 | 439.6146 | 34.49% | 19.175 | 0 | 19.2511 | 38.5% | 49.5
686 | 720 | 509 | 111 | 23.574 | 18.3 | 362.3885 | 214.9362 | 0 | 171.0908 | 101 | 1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 171.0908 | 0 | 603.9302 | 47.39% | 19.175 | 0 | 38.5022 | 77% | 49
687 | 434 | 365 | 153 | 24.1784 | 17.1 | 218.4397 | 115.3015 | 0 | 77.7548 | 56.0005 | 0 | 3.4503 | 52.5503 | 0 | 0 | 0 | 0 | 0 | 77.7548 | 0 | 678.6059 | 53.24% | 2.6463 | 0 | 41.159 | 82.32% | 49.1
688 | 515 | 272 | 94 | 22.9695 | 16 | 259.2085 | 107.2727 | 0 | 70.5101 | 45.2983 | 0 | 0 | 45.2983 | 0 | 0 | 0 | 0 | 0 | 70.5101 | 0 | 746.3237 | 58.56% | 0 | 4.7017 | 36.4394 | 72.88% | 50
689 | 351 | 142 | 70 | 24.9844 | 14.6 | 176.6644 | 0 | 0 | 0 | 23.2185 | 0 | 0 | 23.2185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746.3237 | 58.56% | 0 | 25 | 11.3439 | 22.69% | 48.2185
690 | 3 | 7 | 7 | 21.3576 | 12.9 | 1.51 | 0 | 0 | 0 | 0.016208 | 0 | 0 | 0.016208 | 0 | 0 | 0 | 96.7225 | 38.6828 | 0 | 96.7225 | 651.0251 | 51.08% | 0 | 11.301 | 0 | 0% | 50
691 | 0 | 0 | 0 | 14.3056 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.052 | 50 | 0 | 124.052 | 523.1286 | 41.05% | 0 | 0 | 0 | 0% | 50
692 | 0 | 0 | 0 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.9815 | 47.5 | 0 | 117.9815 | 402.519 | 31.58% | 0 | 0 | 0 | 0% | 47.5
693 | 0 | 0 | 0 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.1017 | 43 | 0 | 107.1017 | 294.8523 | 23.13% | 0 | 0 | 0 | 0% | 43
694 | 0 | 0 | 0 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.336 | 35.2976 | 0 | 88.336 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 35.2976
695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0
696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0
697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0
698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0
699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0
700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0
701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0
702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0
703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0
704 | 0 | 14 | 14 | 10.0743 | 5.6 | 0 | 0 | 0 | 0 | 0.37611 | 0 | 0 | 0.37611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 0.37611
705 | 8 | 95 | 91 | 17.3279 | 11.7 | 4.0265 | 0 | 2.1674 | 0 | 8.0962 | 0 | 0 | 8.0962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.0699 | 16.4% | 0 | 0 | 0 | 0% | 8.0962
706 | 283 | 296 | 182 | 20.1487 | 13 | 142.4388 | 85.1888 | 0 | 51.5545 | 39.7795 | 0 | 0 | 39.7795 | 0 | 0 | 0 | 0 | 0 | 51.5545 | 0 | 259.0225 | 20.32% | 0 | 0 | 0 | 0% | 39.7795
707 | 451 | 458 | 230 | 22.1636 | 14.3 | 226.9961 | 141.9258 | 0 | 103.5213 | 74.9604 | 0 | 12.4802 | 62.4802 | 0 | 0 | 0 | 0 | 0 | 103.5213 | 0 | 359.3272 | 28.19% | 9.5723 | 0 | 9.6114 | 19.22% | 50
708 | 516 | 525 | 227 | 23.7755 | 14.9 | 259.7118 | 164.7606 | 0 | 123.8787 | 96.7986 | 0 | 23.8493 | 72.9493 | 0 | 0 | 0 | 0 | 0 | 123.8787 | 0 | 479.3568 | 37.61% | 18.2924 | 0 | 27.9786 | 55.96% | 49.1
709 | 282 | 470 | 298 | 19.3427 | 14.8 | 141.9355 | 88.4102 | 0 | 55.4191 | 65.287 | 0 | 8.3935 | 56.8935 | 0 | 0 | 0 | 0 | 0 | 55.4191 | 0 | 533.054 | 41.82% | 6.4378 | 0 | 34.4428 | 68.89% | 48.5
710 | 168 | 372 | 273 | 16.9249 | 15.5 | 84.5573 | 0 | 50.2185 | 0 | 42.8471 | 0 | 0 | 42.8471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533.054 | 41.82% | 0 | 5.4529 | 28.9685 | 57.94% | 48.3
711 | 132 | 283 | 214 | 15.716 | 15.7 | 66.4379 | 0 | 35.1575 | 0 | 32.1434 | 0 | 0 | 32.1434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533.054 | 41.82% | 0 | 16.5566 | 12.3466 | 24.69% | 48.7
712 | 1 | 119 | 117 | 11.8877 | 14.6 | 0.50332 | 0 | 0.2092 | 0 | 9.4992 | 0 | 0 | 9.4992 | 0 | 0 | 0 | 72.1651 | 28.2025 | 0 | 72.1651 | 466.4111 | 36.6% | 0 | 12.2983 | 1.3878e-15 | 2.776e-15% | 50
713 | 0 | 53 | 52 | 13.0966 | 13.6 | 0 | 0 | 0 | 0 | 3.7228 | 0 | 0 | 3.7228 | 0 | 0 | 0 | 115.0773 | 46.2772 | 0 | 115.0773 | 349.1595 | 27.4% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 50
714 | 0 | 4 | 4 | 12.0892 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.0762 | 50 | 0 | 124.0762 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 50
715 | 0 | 0 | 0 | 13.7011 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
716 | 0 | 0 | 0 | 16.119 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
717 | 0 | 0 | 0 | 14.7085 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
718 | 0 | 0 | 0 | 9.4699 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
719 | 0 | 0 | 0 | 11.8877 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
720 | 0 | 0 | 0 | 10.0743 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
721 | 0 | 0 | 0 | 15.5145 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
722 | 0 | 0 | 0 | 12.0892 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
723 | 0 | 0 | 0 | 17.5294 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
724 | 0 | 0 | 0 | 14.1041 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
725 | 0 | 0 | 0 | 8.0595 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
726 | 0 | 0 | 0 | 9.6714 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
727 | 0 | 0 | 0 | 8.0595 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
728 | 0 | 15 | 15 | 2.8208 | 10.7 | 0 | 0 | 0 | 0 | 0.41441 | 0 | 0 | 0.41441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0.41441
729 | 0 | 44 | 44 | 4.2312 | 10.6 | 0 | 0 | 0 | 0 | 2.9524 | 0 | 0 | 2.9524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 2.9524
730 | 177 | 203 | 134 | 7.455 | 13.1 | 89.0872 | 0 | 53.3751 | 0 | 25.3383 | 0 | 0 | 25.3383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 25.3383
731 | 0 | 156 | 154 | 6.8506 | 14.6 | 0 | 0 | 0 | 0 | 12.2647 | 0 | 0 | 12.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 12.2647
732 | 97 | 307 | 247 | 14.5071 | 17.3 | 48.8218 | 0 | 30.9986 | 0 | 31.6344 | 0 | 0 | 31.6344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.003 | 17.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 31.6344
733 | 356 | 508 | 290 | 20.5517 | 18.9 | 179.181 | 111.8007 | 0 | 76.4146 | 79.1868 | 0 | 15.5434 | 63.6434 | 0 | 0 | 0 | 0 | 0 | 76.4146 | 0 | 295.2077 | 23.16% | 11.9218 | 0 | 11.9719 | 23.94% | 48.1
734 | 529 | 457 | 159 | 20.9546 | 19.3 | 266.2549 | 158.3452 | 0 | 119.712 | 82.8869 | 0 | 17.5435 | 65.3435 | 0 | 0 | 0 | 0 | 0 | 119.712 | 0 | 411.4576 | 32.28% | 13.4558 | 0 | 25.4843 | 50.97% | 47.8
735 | 908 | 492 | 59 | 18.9398 | 19.5 | 457.0122 | 242.4734 | 0 | 199.4437 | 102.1 | 2.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 199.4437 | 0 | 605.1334 | 47.48% | 19.175 | 0 | 44.7399 | 89.48% | 47.9
736 | 677 | 336 | 93 | 20.3502 | 18.6 | 340.7459 | 142.2663 | 0 | 105.0825 | 61.2677 | 0 | 5.9839 | 55.2839 | 0 | 0 | 0 | 0 | 0 | 105.0825 | 0 | 707.1769 | 55.49% | 4.5896 | 0 | 49.3489 | 98.7% | 49.3
737 | 228 | 115 | 78 | 19.5442 | 16.9 | 114.7564 | 0 | 0 | 0 | 18.3766 | 0 | 0 | 18.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707.1769 | 55.49% | 0 | 25 | 24.2477 | 48.5% | 43.3766
738 | 51 | 14 | 10 | 16.119 | 16.2 | 25.6692 | 0 | 0 | 0 | 0.93178 | 0 | 0 | 0.93178 | 0 | 0 | 0 | 64.9352 | 24.9182 | 0 | 64.9352 | 647.4718 | 50.8% | 0 | 24.15 | 2.7756e-15 | 5.551e-15% | 50
739 | 0 | 0 | 0 | 18.5368 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.2213 | 50 | 0 | 124.2213 | 519.2701 | 40.74% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 50
740 | 0 | 0 | 0 | 17.9323 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.7084 | 46.9 | 0 | 116.7084 | 400.1494 | 31.4% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 46.9
741 | 0 | 0 | 0 | 10.4773 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.4627 | 42.7 | 0 | 106.4627 | 293.1317 | 23% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42.7
742 | 0 | 0 | 0 | 8.0595 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3717 | 27.9198 | 0 | 71.3717 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27.9198
743 | 0 | 0 | 0 | 9.8729 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
744 | 0 | 0 | 0 | 11.8877 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
745 | 0 | 0 | 0 | 14.1041 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
746 | 0 | 0 | 0 | 15.1115 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
747 | 0 | 0 | 0 | 10.4773 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
748 | 0 | 0 | 0 | 11.0818 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
749 | 0 | 0 | 0 | 14.5071 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
750 | 0 | 0 | 0 | 10.2758 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
751 | 0 | 0 | 0 | 15.313 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
752 | 51 | 31 | 27 | 19.7457 | 14.1 | 25.6692 | 0 | 11.1973 | 0 | 2.1888 | 0 | 0 | 2.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1716 | 17.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 2.1888
753 | 478 | 196 | 79 | 17.7308 | 14.8 | 240.5857 | 130.4529 | 0 | 95.2226 | 33.3709 | 0 | 0 | 33.3709 | 0 | 0 | 0 | 0 | 0 | 95.2226 | 0 | 319.5544 | 25.07% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.3709
754 | 59 | 150 | 129 | 15.5145 | 14.7 | 29.6957 | 0 | 17.8235 | 0 | 15.3863 | 0 | 0 | 15.3863 | 0 | 0 | 0 | 87.1865 | 34.6137 | 0 | 87.1865 | 235.405 | 18.47% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 50
755 | 10 | 136 | 129 | 14.91 | 14.7 | 5.0332 | 0 | 3.1592 | 0 | 10.7913 | 0 | 0 | 10.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235.405 | 18.47% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 10.7913
756 | 245 | 316 | 171 | 24.5814 | 15.1 | 123.3128 | 78.3628 | 0 | 42.1011 | 40.6626 | 0 | 0 | 40.6626 | 0 | 0 | 0 | 0 | 0 | 42.1011 | 0 | 276.1709 | 21.67% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 40.6626
757 | 776 | 593 | 129 | 26.7978 | 16.6 | 390.5743 | 244.1255 | 0 | 196.3047 | 102.5 | 2.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 196.3047 | 0 | 466.25 | 36.58% | 19.175 | 0 | 19.2583 | 38.52% | 47.5
758 | 950 | 606 | 72 | 24.3799 | 16.8 | 478.1515 | 284.7642 | 0 | 235.685 | 103 | 3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 235.685 | 0 | 694.4605 | 54.49% | 19.175 | 0 | 38.5166 | 77.03% | 47
759 | 858 | 480 | 71 | 26.5963 | 15.2 | 431.8463 | 229.7395 | 0 | 183.0609 | 103.2 | 13.293 | 14.907 | 75 | 0 | 0 | 0 | 0 | 0 | 183.0609 | 0 | 871.7158 | 68.4% | 11.4337 | 0 | 50 | 100% | 46.8
760 | 855 | 352 | 51 | 25.7903 | 14.5 | 430.3364 | 180.5053 | 0 | 137.5186 | 76.994 | 14.497 | 0 | 62.497 | 0 | 0 | 0 | 0 | 0 | 137.5186 | 0 | 1004.8732 | 78.84% | 0 | 0 | 50 | 100% | 48
761 | 650 | 165 | 36 | 22.1636 | 13.3 | 327.1563 | 0 | 0 | 0 | 33.6601 | 0 | 0 | 33.6601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.8732 | 78.84% | 0 | 16.3399 | 33.5917 | 67.18% | 50
762 | 46 | 11 | 7 | 25.1859 | 11.8 | 23.1526 | 0 | 0 | 0 | 0.6603 | 0 | 0 | 0.6603 | 0 | 0 | 0 | 63.1818 | 24.3397 | 0 | 63.1818 | 946.9708 | 74.3% | 0 | 25 | 8.4861 | 16.97% | 50
763 | 0 | 0 | 0 | 21.5591 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5935 | 40.7486 | 0 | 101.5935 | 845.7801 | 66.36% | 0 | 8.4514 | 0 | 0% | 49.2
764 | 0 | 0 | 0 | 21.3576 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.6321 | 46.2 | 0 | 114.6321 | 728.9717 | 57.2% | 0 | 0 | 0 | 0% | 46.2
765 | 0 | 0 | 0 | 13.9026 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8283 | 42.6 | 0 | 105.8283 | 622.4952 | 48.84% | 0 | 0 | 0 | 0% | 42.6
766 | 0 | 0 | 0 | 19.9472 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.076 | 40.2 | 0 | 100.076 | 522.7985 | 41.02% | 0 | 0 | 0 | 0% | 40.2
767 | 0 | 0 | 0 | 21.3576 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4055 | 37.4 | 0 | 93.4055 | 431.1149 | 33.83% | 0 | 0 | 0 | 0% | 37.4
768 | 0 | 0 | 0 | 18.3353 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1196 | 35.2 | 0 | 88.1196 | 345.6086 | 27.12% | 0 | 0 | 0 | 0% | 35.2
769 | 0 | 0 | 0 | 15.716 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4905 | 34.1 | 0 | 85.4905 | 263.2617 | 20.66% | 0 | 0 | 0 | 0% | 34.1
770 | 0 | 0 | 0 | 23.574 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.2617 | 20.66% | 0 | 0 | 0 | 0% | 0
771 | 0 | 0 | 0 | 12.6937 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.2617 | 20.66% | 0 | 0 | 0 | 0% | 0
772 | 0 | 0 | 0 | 11.0818 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.2617 | 20.66% | 0 | 0 | 0 | 0% | 0
773 | 0 | 0 | 0 | 12.4922 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.2617 | 20.66% | 0 | 0 | 0 | 0% | 0
774 | 0 | 0 | 0 | 13.7011 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.2617 | 20.66% | 0 | 0 | 0 | 0% | 0
775 | 0 | 0 | 0 | 14.5071 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.2617 | 20.66% | 0 | 0 | 0 | 0% | 0
776 | 226 | 32 | 14 | 13.4996 | 8.3 | 113.7497 | 0 | 49.9408 | 0 | 3.5529 | 0 | 0 | 3.5529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.2617 | 20.66% | 0 | 0 | 0 | 0% | 3.5529
777 | 304 | 117 | 47 | 12.0892 | 9 | 153.0085 | 83.272 | 0 | 54.1886 | 21.8589 | 0 | 0 | 21.8589 | 0 | 0 | 0 | 0 | 0 | 54.1886 | 0 | 315.4853 | 24.75% | 0 | 0 | 0 | 0% | 21.8589
778 | 657 | 327 | 65 | 12.4922 | 10.4 | 330.6795 | 198.8332 | 0 | 162.2184 | 63.3099 | 0 | 8.7049 | 54.6049 | 0 | 0 | 0 | 0 | 0 | 162.2184 | 0 | 471.8217 | 37.02% | 6.6767 | 0 | 6.7066 | 13.41% | 45.9
779 | 897 | 558 | 103 | 12.0892 | 11.4 | 451.4757 | 283.9465 | 0 | 241.9705 | 104.4 | 4.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 241.9705 | 0 | 705.0183 | 55.32% | 19.175 | 0 | 25.9675 | 51.94% | 45.6
780 | 945 | 630 | 83 | 7.858 | 11.8 | 475.6349 | 302.5214 | 0 | 262.0519 | 105.7 | 5.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 262.0519 | 0 | 957.5682 | 75.13% | 19.175 | 0 | 45.2285 | 90.46% | 44.3
781 | 869 | 621 | 97 | 9.0669 | 12.3 | 437.3828 | 273.8694 | 0 | 234.3803 | 107.6 | 26.4068 | 6.1932 | 75 | 0 | 0 | 0 | 0 | 0 | 234.3803 | 0 | 1183.4499 | 92.86% | 4.7502 | 0 | 50 | 100% | 42.4
782 | 968 | 638 | 88 | 9.8729 | 12.7 | 487.2112 | 290.5809 | 0 | 249.7039 | 108.5 | 33.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 249.7039 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.5
783 | 514 | 362 | 115 | 8.4625 | 11.7 | 258.7051 | 0 | 138.0118 | 0 | 70.6531 | 14.8266 | 0 | 55.8266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41
784 | 712 | 332 | 70 | 14.7085 | 11.5 | 358.362 | 0 | 151.0343 | 0 | 69.2986 | 13.2993 | 0 | 55.9993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.7
785 | 569 | 162 | 49 | 12.2907 | 10.2 | 286.3876 | 0 | 0 | 0 | 31.9386 | 0 | 0 | 31.9386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 13.7614 | 36.1791 | 72.36% | 45.7
786 | 12 | 8 | 7 | 17.5294 | 8.6 | 6.0398 | 0 | 0 | 0 | 0.12985 | 0 | 0 | 0.12985 | 0 | 0 | 0 | 56.1012 | 21.3701 | 0 | 56.1012 | 1223.4473 | 95.99% | 0 | 25 | 11.0701 | 22.14% | 46.5
787 | 0 | 0 | 0 | 11.6862 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2952 | 35.2772 | 0 | 88.2952 | 1137.876 | 89.28% | 0 | 11.0228 | 0 | 0% | 46.3
788 | 0 | 0 | 0 | 11.4848 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.2303 | 44.4 | 0 | 110.2303 | 1026.3348 | 80.53% | 0 | 0 | 0 | 0% | 44.4
789 | 0 | 0 | 0 | 6.8506 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2053 | 41.5 | 0 | 103.2053 | 923.0704 | 72.43% | 0 | 0 | 0 | 0% | 41.5
790 | 0 | 0 | 0 | 5.0372 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0191 | 38.5 | 0 | 96.0191 | 828.347 | 64.99% | 0 | 0 | 0 | 0% | 38.5
791 | 0 | 0 | 0 | 10.4773 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3582 | 35.3 | 0 | 88.3582 | 742.6671 | 58.27% | 0 | 0 | 0 | 0% | 35.3
792 | 0 | 0 | 0 | 11.4848 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0674 | 33.1 | 0 | 83.0674 | 663.2849 | 52.04% | 0 | 0 | 0 | 0% | 33.1
793 | 0 | 0 | 0 | 9.2684 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9492 | 31.8 | 0 | 79.9492 | 587.5751 | 46.1% | 0 | 0 | 0 | 0% | 31.8
794 | 0 | 0 | 0 | 5.6416 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9765 | 31.4 | 0 | 78.9765 | 512.9767 | 40.25% | 0 | 0 | 0 | 0% | 31.4
795 | 0 | 0 | 0 | 5.4401 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4501 | 31.6 | 0 | 79.4501 | 437.8014 | 34.35% | 0 | 0 | 0 | 0% | 31.6
796 | 0 | 0 | 0 | 7.455 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.112 | 32.3 | 0 | 81.112 | 360.6311 | 28.3% | 0 | 0 | 0 | 0% | 32.3
797 | 0 | 0 | 0 | 5.2387 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7339 | 33.4 | 0 | 83.7339 | 280.2984 | 21.99% | 0 | 0 | 0 | 0% | 33.4
798 | 0 | 0 | 0 | 6.2461 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8897 | 34.3 | 0 | 85.8897 | 197.3379 | 15.48% | 0 | 0 | 0 | 0% | 34.3
799 | 0 | 0 | 0 | 6.0446 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197.3379 | 15.48% | 0 | 0 | 0 | 0% | 0
800 | 281 | 41 | 15 | 6.8506 | 5.7 | 141.4322 | 62.4959 | 0 | 38.0914 | 4.3891 | 0 | 0 | 4.3891 | 0 | 0 | 0 | 0 | 0 | 38.0914 | 0 | 233.4002 | 18.31% | 0 | 0 | 0 | 0% | 4.3891
801 | 751 | 215 | 39 | 4.8357 | 7.5 | 377.9914 | 206.4755 | 0 | 174.1162 | 43.6921 | 0.84603 | 0 | 42.846 | 0 | 0 | 0 | 0 | 0 | 174.1162 | 0 | 398.2407 | 31.25% | 0 | 0 | 0 | 0% | 42
802 | 895 | 399 | 50 | 6.6491 | 8.8 | 450.4691 | 271.3527 | 0 | 233.4745 | 94.543 | 1.5215 | 25 | 68.0215 | 0 | 0 | 0 | 0 | 0 | 233.4745 | 0 | 619.2774 | 48.59% | 19.175 | 0 | 19.2636 | 38.53% | 41.5
803 | 975 | 550 | 54 | 7.858 | 9.8 | 490.7345 | 309.2585 | 0 | 268.2653 | 108.3 | 8.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 268.2653 | 0 | 873.2515 | 68.52% | 19.175 | 0 | 38.5273 | 77.05% | 41.7
804 | 1005 | 642 | 56 | 9.8729 | 10.7 | 505.834 | 322.016 | 0 | 278.8979 | 108.6 | 18.711 | 14.889 | 75 | 0 | 0 | 0 | 0 | 0 | 278.8979 | 0 | 1137.2918 | 89.23% | 11.4199 | 0 | 50 | 100% | 41.4
805 | 1012 | 669 | 58 | 9.6714 | 11.7 | 509.3572 | 276.7491 | 42.7661 | 239.6768 | 110.5 | 35.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 239.6768 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.5
806 | 1001 | 629 | 56 | 10.2758 | 12.1 | 503.8207 | 0 | 300.935 | 0 | 111.6 | 36.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.4
807 | 961 | 524 | 54 | 8.6639 | 12.4 | 483.688 | 0 | 258.7711 | 0 | 111.9 | 36.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.1
808 | 883 | 368 | 47 | 6.6491 | 12.4 | 444.4293 | 0 | 188.2295 | 0 | 85.6374 | 22.7687 | 0 | 62.8687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.1
809 | 711 | 179 | 34 | 7.455 | 11.5 | 357.8587 | 0 | 0 | 0 | 35.867 | 0 | 0 | 35.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.633 | 41.3284 | 82.66% | 44.5
810 | 176 | 22 | 8 | 4.6342 | 9.5 | 88.5839 | 0 | 0 | 0 | 1.8464 | 0 | 0 | 1.8464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.2161 | 32.43% | 26.8464
811 | 0 | 0 | 0 | 3.4253 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9809 | 30.5559 | 0 | 76.9809 | 1202.3786 | 94.34% | 0 | 16.1441 | 0 | 0% | 46.7
812 | 0 | 0 | 0 | 3.4253 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.824 | 45.1 | 0 | 111.824 | 1088.8683 | 85.43% | 0 | 0 | 0 | 0% | 45.1
813 | 0 | 0 | 0 | 2.2164 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4247 | 41.6 | 0 | 103.4247 | 985.3674 | 77.31% | 0 | 0 | 0 | 0% | 41.6
814 | 0 | 0 | 0 | 3.4253 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2766 | 37.8 | 0 | 94.2766 | 892.6748 | 70.04% | 0 | 0 | 0 | 0% | 37.8
815 | 0 | 0 | 0 | 1.6119 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7077 | 35.1 | 0 | 87.7077 | 807.561 | 63.36% | 0 | 0 | 0 | 0% | 35.1
816 | 0 | 0 | 0 | 3.8283 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1456 | 33.6 | 0 | 84.1456 | 726.7732 | 57.02% | 0 | 0 | 0 | 0% | 33.6
817 | 0 | 0 | 0 | 2.4178 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6953 | 33 | 0 | 82.6953 | 647.6927 | 50.82% | 0 | 0 | 0 | 0% | 33
818 | 0 | 0 | 0 | 1.8134 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2203 | 32.8 | 0 | 82.2203 | 569.1693 | 44.66% | 0 | 0 | 0 | 0% | 32.8
819 | 0 | 0 | 0 | 4.2312 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5625 | 34.2 | 0 | 85.5625 | 486.6054 | 38.18% | 0 | 0 | 0 | 0% | 34.2
820 | 0 | 0 | 0 | 5.6416 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3633 | 38.7 | 0 | 96.3633 | 391.2425 | 30.7% | 0 | 0 | 0 | 0% | 38.7
821 | 0 | 0 | 0 | 5.0372 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1493 | 46.1 | 0 | 114.1493 | 274.6978 | 21.55% | 0 | 0 | 0 | 0% | 46.1
822 | 0 | 0 | 0 | 3.8283 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.6189 | 50 | 0 | 123.6189 | 146.8631 | 11.52% | 0 | 0 | 0 | 0% | 50
823 | 0 | 0 | 0 | 2.8208 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.3439 | 27.6726 | 0 | 70.3439 | 81.793 | 6.418% | 0 | 0 | 0 | 0% | 27.6726
824 | 299 | 43 | 14 | 5.0372 | 2 | 150.4919 | 66.9277 | 0 | 43.0374 | 4.5283 | 0 | 0 | 4.5283 | 0 | 0 | 0 | 0 | 0 | 43.0374 | 0 | 123.0262 | 9.653% | 0 | 0 | 0 | 0% | 4.5283
825 | 789 | 223 | 37 | 2.6193 | 6.1 | 397.1174 | 217.7265 | 0 | 185.4168 | 44.3183 | 0 | 0 | 44.3183 | 0 | 0 | 0 | 0 | 0 | 185.4168 | 0 | 300.6697 | 23.59% | 0 | 0 | 0 | 0% | 44.3183
826 | 929 | 411 | 47 | 1.8134 | 9.7 | 467.5819 | 282.1758 | 0 | 245.9628 | 85.487 | 0 | 17.7435 | 67.7435 | 0 | 0 | 0 | 0 | 0 | 245.9628 | 0 | 536.321 | 42.08% | 13.6093 | 0 | 13.6741 | 27.35% | 50
827 | 989 | 558 | 52 | 6.8506 | 11.2 | 497.7809 | 314.337 | 0 | 273.6596 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 273.6596 | 0 | 798.5079 | 62.65% | 19.175 | 0 | 32.9405 | 65.88% | 50
828 | 1012 | 648 | 55 | 7.052 | 12.8 | 509.3572 | 324.5529 | 0 | 283.1028 | 100 | 2.8637 | 22.1363 | 75 | 0 | 0 | 0 | 0 | 0 | 283.1028 | 0 | 1069.7422 | 83.93% | 16.9785 | 0 | 50 | 100% | 50
829 | 1006 | 671 | 59 | 7.858 | 13.6 | 506.3373 | 279.8273 | 38.3805 | 243.309 | 100.8 | 25.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 243.309 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.2
830 | 992 | 629 | 58 | 9.2684 | 14.3 | 499.2908 | 0 | 298.6854 | 0 | 101.3 | 26.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.7
831 | 950 | 523 | 54 | 9.6714 | 14.3 | 478.1515 | 0 | 256.5596 | 0 | 101.5 | 26.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.5
832 | 863 | 365 | 48 | 8.8654 | 14.1 | 434.3629 | 0 | 184.8956 | 0 | 74.0242 | 12.1621 | 0 | 61.8621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.7
833 | 669 | 176 | 36 | 8.6639 | 12.8 | 336.7193 | 0 | 0 | 0 | 34.5272 | 0 | 0 | 34.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 15.4728 | 34.4558 | 68.91% | 50
834 | 157 | 22 | 9 | 6.6491 | 10.4 | 79.0208 | 0 | 0 | 0 | 1.8968 | 0 | 0 | 1.8968 | 0 | 0 | 0 | 60.2175 | 23.1032 | 0 | 60.2175 | 1219.5483 | 95.69% | 0 | 25 | 9.3396 | 18.68% | 50
835 | 0 | 0 | 0 | 3.4253 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.3042 | 40.7027 | 0 | 101.3042 | 1118.6495 | 87.77% | 0 | 9.2973 | 0 | 0% | 50
836 | 0 | 0 | 0 | 1.0074 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.338 | 48.2 | 0 | 119.338 | 996.2813 | 78.17% | 0 | 0 | 0 | 0% | 48.2
837 | 0 | 0 | 0 | 1.8134 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.2281 | 43.6 | 0 | 108.2281 | 887.1225 | 69.6% | 0 | 0 | 0 | 0% | 43.6
838 | 0 | 0 | 0 | 2.4178 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4813 | 40.4 | 0 | 100.4813 | 787.0323 | 61.75% | 0 | 0 | 0 | 0% | 40.4
839 | 0 | 0 | 0 | 4.8357 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5764 | 37.5 | 0 | 93.5764 | 695.2132 | 54.55% | 0 | 0 | 0 | 0% | 37.5
840 | 0 | 0 | 0 | 4.4327 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4832 | 35.8 | 0 | 89.4832 | 608.1657 | 47.72% | 0 | 0 | 0 | 0% | 35.8
841 | 0 | 0 | 0 | 2.4178 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7931 | 35.1 | 0 | 87.7931 | 523.0542 | 41.04% | 0 | 0 | 0 | 0% | 35.1
842 | 0 | 0 | 0 | 1.4104 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5522 | 35 | 0 | 87.5522 | 438.2034 | 34.38% | 0 | 0 | 0 | 0% | 35
843 | 0 | 0 | 0 | 2.2164 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9267 | 36 | 0 | 89.9267 | 350.5426 | 27.5% | 0 | 0 | 0 | 0% | 36
844 | 0 | 0 | 0 | 3.6268 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2654 | 39.9 | 0 | 99.2654 | 251.7426 | 19.75% | 0 | 0 | 0 | 0% | 39.9
845 | 0 | 0 | 0 | 3.0223 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.4412 | 46.6 | 0 | 115.4412 | 133.7797 | 10.5% | 0 | 0 | 0 | 0% | 46.6
846 | 0 | 0 | 0 | 2.2164 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.728 | 23.4301 | 0 | 60.728 | 78.1712 | 6.133% | 0 | 0 | 0 | 0% | 23.4301
847 | 0 | 0 | 0 | 1.8134 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1712 | 6.133% | 0 | 0 | 0 | 0% | 0
848 | 282 | 43 | 15 | 0.40297 | 3.8 | 141.9355 | 63.5278 | 0 | 41.948 | 4.5438 | 0 | 0 | 4.5438 | 0 | 0 | 0 | 0 | 0 | 41.948 | 0 | 118.5078 | 9.298% | 0 | 0 | 0 | 0% | 4.5438
849 | 740 | 215 | 38 | 1.2089 | 10.5 | 372.4549 | 204.9621 | 0 | 174.1246 | 41.1249 | 0 | 0 | 41.1249 | 0 | 0 | 0 | 0 | 0 | 174.1246 | 0 | 285.9437 | 22.44% | 0 | 0 | 0 | 0% | 41.1249
850 | 898 | 402 | 46 | 1.4104 | 14 | 451.979 | 273.2612 | 0 | 237.7272 | 79.0522 | 0 | 14.5261 | 64.5261 | 0 | 0 | 0 | 0 | 0 | 237.7272 | 0 | 514.5389 | 40.37% | 11.1415 | 0 | 11.1962 | 22.39% | 50
851 | 964 | 549 | 51 | 2.0149 | 15.9 | 485.198 | 306.8437 | 0 | 269.0083 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 269.0083 | 0 | 773.2137 | 60.67% | 19.175 | 0 | 30.4653 | 60.93% | 50
852 | 992 | 639 | 54 | 4.6342 | 17.4 | 499.2908 | 318.4321 | 0 | 278.8727 | 101.4 | 1.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 278.8727 | 0 | 1041.3739 | 81.71% | 19.175 | 0 | 49.7345 | 99.47% | 48.6
853 | 999 | 666 | 55 | 5.6416 | 18.2 | 502.8141 | 312.2331 | 4.3547 | 272.8296 | 102.4 | 27.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 272.8296 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7345 | 99.47% | 47.6
854 | 985 | 626 | 55 | 5.6416 | 18.9 | 495.7676 | 0 | 297.0425 | 0 | 102.9 | 27.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7345 | 99.47% | 47.1
855 | 951 | 524 | 52 | 8.4625 | 18.8 | 478.6548 | 0 | 257.6026 | 0 | 103.1 | 28.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7345 | 99.47% | 46.9
856 | 877 | 371 | 46 | 9.2684 | 18.5 | 441.4093 | 0 | 188.8687 | 0 | 75.3926 | 13.6463 | 0 | 61.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7345 | 99.47% | 48.1
857 | 700 | 182 | 34 | 8.4625 | 17 | 352.3222 | 0 | 0 | 0 | 34.961 | 0 | 0 | 34.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 15.039 | 34.624 | 69.25% | 50
858 | 185 | 24 | 9 | 5.6416 | 14 | 93.1137 | 0 | 0 | 0 | 2.0781 | 0 | 0 | 2.0781 | 0 | 0 | 0 | 60.1614 | 22.9219 | 0 | 60.1614 | 1219.6185 | 95.69% | 0 | 25 | 9.5043 | 19.01% | 50
859 | 0 | 0 | 0 | 3.2238 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0213 | 40.5402 | 0 | 101.0213 | 1119.1736 | 87.81% | 0 | 9.4598 | 0 | 0% | 50
860 | 0 | 0 | 0 | 1.8134 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.2053 | 47.7 | 0 | 118.2053 | 998.2492 | 78.32% | 0 | 0 | 0 | 0% | 47.7
861 | 0 | 0 | 0 | 1.6119 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.0416 | 43.1 | 0 | 107.0416 | 890.5194 | 69.87% | 0 | 0 | 0 | 0% | 43.1
862 | 0 | 0 | 0 | 1.6119 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3319 | 39.9 | 0 | 99.3319 | 791.838 | 62.13% | 0 | 0 | 0 | 0% | 39.9
863 | 0 | 0 | 0 | 0.80595 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6145 | 37.1 | 0 | 92.6145 | 701.1489 | 55.01% | 0 | 0 | 0 | 0% | 37.1
864 | 0 | 0 | 0 | 1.0074 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5181 | 35.4 | 0 | 88.5181 | 615.2158 | 48.27% | 0 | 0 | 0 | 0% | 35.4
865 | 0 | 0 | 0 | 2.2164 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8386 | 34.7 | 0 | 86.8386 | 531.2558 | 41.68% | 0 | 0 | 0 | 0% | 34.7
866 | 0 | 0 | 0 | 1.6119 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0759 | 34.8 | 0 | 87.0759 | 446.9876 | 35.07% | 0 | 0 | 0 | 0% | 34.8
867 | 0 | 0 | 0 | 0.80595 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.242 | 35.7 | 0 | 89.242 | 360.1649 | 28.26% | 0 | 0 | 0 | 0% | 35.7
868 | 0 | 0 | 0 | 1.0074 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3745 | 39.5 | 0 | 98.3745 | 262.5208 | 20.6% | 0 | 0 | 0 | 0% | 39.5
869 | 0 | 0 | 0 | 0.60446 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.2359 | 46.1 | 0 | 114.2359 | 145.9827 | 11.45% | 0 | 0 | 0 | 0% | 46.1
870 | 0 | 0 | 0 | 1.0074 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.6538 | 27.7896 | 0 | 70.6538 | 80.6557 | 6.328% | 0 | 0 | 0 | 0% | 27.7896
871 | 0 | 0 | 0 | 1.2089 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6557 | 6.328% | 0 | 0 | 0 | 0% | 0
872 | 279 | 44 | 15 | 2.0149 | 7 | 140.4256 | 63.254 | 0 | 41.0851 | 4.9332 | 0 | 0 | 4.9332 | 0 | 0 | 0 | 0 | 0 | 41.0851 | 0 | 120.1154 | 9.424% | 0 | 0 | 0 | 0% | 4.9332
873 | 734 | 216 | 37 | 0.60446 | 13.2 | 369.435 | 204.0544 | 0 | 173.4929 | 40.1919 | 0 | 0 | 40.1919 | 0 | 0 | 0 | 0 | 0 | 173.4929 | 0 | 286.7448 | 22.5% | 0 | 0 | 0 | 0% | 40.1919
874 | 877 | 398 | 48 | 1.2089 | 15.7 | 441.4093 | 267.3643 | 0 | 232.2702 | 76.4673 | 0 | 13.4837 | 62.9837 | 0 | 0 | 0 | 0 | 0 | 232.2702 | 0 | 509.8263 | 40% | 10.342 | 0 | 10.3942 | 20.79% | 49.5
875 | 949 | 545 | 51 | 3.2238 | 17.9 | 477.6482 | 302.3329 | 0 | 264.3966 | 101 | 1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 264.3966 | 0 | 763.7633 | 59.93% | 19.175 | 0 | 29.666 | 59.33% | 49
876 | 979 | 635 | 53 | 4.4327 | 18.8 | 492.7477 | 314.5532 | 0 | 275.3437 | 102.4 | 2.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 275.3437 | 0 | 1028.2142 | 80.68% | 19.175 | 0 | 48.9379 | 97.88% | 47.6
877 | 988 | 662 | 54 | 5.0372 | 19.4 | 497.2776 | 313.7007 | 0 | 274.3335 | 103.3 | 28.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 274.3335 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9379 | 97.88% | 46.7
878 | 977 | 624 | 53 | 6.8506 | 19.9 | 491.7411 | 0 | 295.1027 | 0 | 103.9 | 28.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9379 | 97.88% | 46.1
879 | 932 | 519 | 52 | 8.0595 | 20 | 469.0918 | 0 | 253.2342 | 0 | 104.2 | 29.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9379 | 97.88% | 45.8
880 | 859 | 367 | 46 | 10.4773 | 19.3 | 432.3496 | 0 | 185.974 | 0 | 74.3921 | 13.6961 | 0 | 60.6961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9379 | 97.88% | 47
881 | 696 | 183 | 34 | 10.8803 | 17.8 | 350.3089 | 0 | 0 | 0 | 34.8751 | 0 | 0 | 34.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 15.1249 | 33.7389 | 67.48% | 50
882 | 190 | 25 | 9 | 7.858 | 15.3 | 95.6303 | 0 | 0 | 0 | 2.218 | 0 | 0 | 2.218 | 0 | 0 | 0 | 59.9895 | 22.782 | 0 | 59.9895 | 1219.7909 | 95.71% | 0 | 25 | 8.6157 | 17.23% | 50
883 | 0 | 0 | 0 | 2.6193 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.308 | 41.4258 | 0 | 103.308 | 1116.8493 | 87.63% | 0 | 8.5742 | 0 | 0% | 50
884 | 0 | 0 | 0 | 1.0074 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.3459 | 46.5 | 0 | 115.3459 | 999.3674 | 78.41% | 0 | 0 | 0 | 0% | 46.5
885 | 0 | 0 | 0 | 1.2089 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7291 | 42.1 | 0 | 104.7291 | 894.4872 | 70.18% | 0 | 0 | 0 | 0% | 42.1
886 | 0 | 0 | 0 | 0.60446 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2338 | 39 | 0 | 97.2338 | 798.4032 | 62.64% | 0 | 0 | 0 | 0% | 39
887 | 0 | 0 | 0 | 3.0223 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0061 | 36.4 | 0 | 91.0061 | 709.698 | 55.68% | 0 | 0 | 0 | 0% | 36.4
888 | 0 | 0 | 0 | 2.6193 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1614 | 34.8 | 0 | 87.1614 | 625.485 | 49.08% | 0 | 0 | 0 | 0% | 34.8
889 | 0 | 0 | 0 | 3.6268 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5073 | 34.1 | 0 | 85.5073 | 543.2675 | 42.63% | 0 | 0 | 0 | 0% | 34.1
890 | 0 | 0 | 0 | 4.8357 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4905 | 34.1 | 0 | 85.4905 | 461.039 | 36.17% | 0 | 0 | 0 | 0% | 34.1
891 | 0 | 0 | 0 | 3.2238 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.621 | 35 | 0 | 87.621 | 376.1929 | 29.52% | 0 | 0 | 0 | 0% | 35
892 | 0 | 0 | 0 | 3.2238 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7041 | 38.8 | 0 | 96.7041 | 280.569 | 22.01% | 0 | 0 | 0 | 0% | 38.8
893 | 0 | 0 | 0 | 4.8357 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1736 | 45.2 | 0 | 112.1736 | 166.6094 | 13.07% | 0 | 0 | 0 | 0% | 45.2
894 | 0 | 0 | 0 | 4.0297 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0818 | 29.2953 | 0 | 74.0818 | 97.605 | 7.658% | 0 | 0 | 0 | 0% | 29.2953
895 | 0 | 0 | 0 | 4.4327 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.605 | 7.658% | 0 | 0 | 0 | 0% | 0
896 | 109 | 39 | 28 | 4.6342 | 9.2 | 54.8616 | 0 | 24.8695 | 0 | 3.5192 | 0 | 0 | 3.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.605 | 7.658% | 0 | 0 | 0 | 0% | 3.5192
897 | 436 | 188 | 76 | 2.8208 | 12.1 | 219.4464 | 121.6591 | 0 | 95.5832 | 30.6154 | 0 | 0 | 30.6154 | 0 | 0 | 0 | 0 | 0 | 95.5832 | 0 | 189.1819 | 14.84% | 0 | 0 | 0 | 0% | 30.6154
898 | 749 | 406 | 102 | 2.0149 | 15.9 | 376.9847 | 228.7662 | 0 | 196.0521 | 73.8662 | 0 | 12.2331 | 61.6331 | 0 | 0 | 0 | 0 | 0 | 196.0521 | 0 | 377.0167 | 29.58% | 9.3828 | 0 | 9.4315 | 18.86% | 49.4
899 | 616 | 472 | 145 | 1.6119 | 17.9 | 310.0435 | 196.4184 | 0 | 165.9277 | 80.4129 | 0 | 15.8064 | 64.6064 | 0 | 0 | 0 | 0 | 0 | 165.9277 | 0 | 535.9897 | 42.05% | 12.1235 | 0 | 21.6179 | 43.24% | 48.8
900 | 815 | 620 | 128 | 3.4253 | 19.2 | 410.2037 | 262.1087 | 0 | 226.5736 | 102.7 | 2.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 226.5736 | 0 | 753.0668 | 59.09% | 19.175 | 0 | 40.8925 | 81.79% | 47.3
901 | 772 | 653 | 170 | 5.0372 | 19.4 | 388.561 | 245.3821 | 0 | 210.4417 | 103.5 | 16.6872 | 11.8128 | 75 | 0 | 0 | 0 | 0 | 0 | 210.4417 | 0 | 954.6881 | 74.91% | 9.0604 | 0 | 50 | 100% | 46.5
902 | 773 | 589 | 134 | 7.2535 | 19.6 | 389.0643 | 233.8677 | 0 | 198.4789 | 104.1 | 29.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 198.4789 | 0 | 1144.848 | 89.83% | 0 | 0 | 50 | 100% | 45.9
903 | 916 | 522 | 59 | 7.2535 | 19.8 | 461.0387 | 212.5454 | 37.1265 | 181.3851 | 104.4 | 29.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 181.3851 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.6
904 | 822 | 366 | 53 | 7.2535 | 19.4 | 413.7269 | 0 | 178.9294 | 0 | 70.9417 | 12.1709 | 0 | 58.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.6
905 | 638 | 181 | 40 | 7.455 | 17.8 | 321.1165 | 0 | 0 | 0 | 33.1914 | 0 | 0 | 33.1914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 16.8086 | 33.1067 | 66.21% | 50
906 | 175 | 26 | 11 | 4.6342 | 15 | 88.0805 | 0 | 0 | 0 | 2.3059 | 0 | 0 | 2.3059 | 0 | 0 | 0 | 59.7594 | 22.6941 | 0 | 59.7594 | 1220.0142 | 95.72% | 0 | 25 | 7.9799 | 15.96% | 50
907 | 0 | 0 | 0 | 1.2089 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8363 | 42.0595 | 0 | 104.8363 | 1115.2848 | 87.51% | 0 | 7.9405 | 0 | 0% | 50
908 | 0 | 0 | 0 | 1.8134 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.643 | 46.6 | 0 | 115.643 | 997.5231 | 78.27% | 0 | 0 | 0 | 0% | 46.6
909 | 0 | 0 | 0 | 3.6268 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2102 | 42.3 | 0 | 105.2102 | 892.0817 | 69.99% | 0 | 0 | 0 | 0% | 42.3
910 | 0 | 0 | 0 | 4.4327 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0377 | 39.3 | 0 | 98.0377 | 795.1384 | 62.39% | 0 | 0 | 0 | 0% | 39.3
911 | 0 | 0 | 0 | 6.0446 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4121 | 36.5 | 0 | 91.4121 | 706.1466 | 55.41% | 0 | 0 | 0 | 0% | 36.5
912 | 0 | 0 | 0 | 3.6268 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2475 | 34.8 | 0 | 87.2475 | 621.9161 | 48.8% | 0 | 0 | 0 | 0% | 34.8
913 | 0 | 0 | 0 | 2.4178 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5157 | 34.1 | 0 | 85.5157 | 539.7042 | 42.35% | 0 | 0 | 0 | 0% | 34.1
914 | 0 | 0 | 0 | 3.2238 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4767 | 34.1 | 0 | 85.4767 | 457.4956 | 35.9% | 0 | 0 | 0 | 0% | 34.1
915 | 0 | 0 | 0 | 3.6268 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6382 | 35 | 0 | 87.6382 | 372.6429 | 29.24% | 0 | 0 | 0 | 0% | 35
916 | 0 | 0 | 0 | 4.6342 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8056 | 38.8 | 0 | 96.8056 | 277.0227 | 21.74% | 0 | 0 | 0 | 0% | 38.8
917 | 0 | 0 | 0 | 5.0372 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.9027 | 45.5 | 0 | 112.9027 | 162.2118 | 12.73% | 0 | 0 | 0 | 0% | 45.5
918 | 0 | 0 | 0 | 4.8357 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7948 | 32.9735 | 0 | 82.7948 | 83.122 | 6.522% | 0 | 0 | 0 | 0% | 32.9735
919 | 0 | 0 | 0 | 4.8357 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.122 | 6.522% | 0 | 0 | 0 | 0% | 0
920 | 255 | 46 | 17 | 5.6416 | 9 | 128.3459 | 58.5496 | 0 | 35.0868 | 5.2997 | 0 | 0 | 5.2997 | 0 | 0 | 0 | 0 | 0 | 35.0868 | 0 | 116.7813 | 9.163% | 0 | 0 | 0 | 0% | 5.2997
921 | 708 | 221 | 43 | 2.6193 | 12.2 | 356.3487 | 198.2889 | 0 | 167.293 | 40.6697 | 0 | 0 | 40.6697 | 0 | 0 | 0 | 0 | 0 | 167.293 | 0 | 277.2682 | 21.75% | 0 | 0 | 0 | 0% | 40.6697
922 | 859 | 407 | 56 | 5.6416 | 14.5 | 432.3496 | 262.8531 | 0 | 226.2418 | 81.2759 | 0 | 16.2379 | 65.0379 | 0 | 0 | 0 | 0 | 0 | 226.2418 | 0 | 494.3054 | 38.78% | 12.4545 | 0 | 12.5209 | 25.04% | 48.8
923 | 932 | 555 | 62 | 6.8506 | 16 | 469.0918 | 297.4423 | 0 | 258.0588 | 101.7 | 1.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 258.0588 | 0 | 741.8653 | 58.21% | 19.175 | 0 | 31.7982 | 63.6% | 48.3
924 | 960 | 646 | 67 | 3.0223 | 17.2 | 483.1847 | 309.039 | 0 | 270.6949 | 103.4 | 4.7948 | 23.6052 | 75 | 0 | 0 | 0 | 0 | 0 | 270.6949 | 0 | 1001.5471 | 78.58% | 18.1052 | 0 | 50 | 100% | 46.6
925 | 966 | 672 | 68 | 3.2238 | 18.6 | 486.2046 | 307.2978 | 0 | 269.0149 | 104.5 | 29.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 269.0149 | 0 | 1259.6174 | 98.83% | 0 | 0 | 50 | 100% | 45.5
926 | 950 | 631 | 68 | 5.2387 | 19.3 | 478.1515 | 0 | 287.9001 | 0 | 105 | 30 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.6174 | 98.83% | 0 | 0 | 50 | 100% | 45
927 | 933 | 534 | 59 | 7.052 | 19.6 | 469.5951 | 0 | 255.1254 | 0 | 105.5 | 30.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.6174 | 98.83% | 0 | 0 | 50 | 100% | 44.5
928 | 860 | 380 | 51 | 8.6639 | 19.3 | 432.853 | 0 | 188.2389 | 0 | 76.9359 | 15.7179 | 0 | 61.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.6174 | 98.83% | 0 | 0 | 50 | 100% | 45.5
929 | 670 | 189 | 38 | 7.858 | 18 | 337.2226 | 0 | 0 | 0 | 34.4492 | 0 | 0 | 34.4492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.6174 | 98.83% | 0 | 14.2508 | 35.6753 | 71.35% | 48.7
930 | 171 | 26 | 11 | 5.8431 | 14.5 | 86.0673 | 0 | 0 | 0 | 2.3843 | 0 | 0 | 2.3843 | 0 | 0 | 0 | 57.1921 | 21.6157 | 0 | 57.1921 | 1207.5742 | 94.75% | 0 | 25 | 10.5451 | 21.09% | 49
931 | 0 | 0 | 0 | 2.0149 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5035 | 37.8088 | 0 | 94.5035 | 1114.9268 | 87.48% | 0 | 10.4912 | 0 | 0% | 48.3
932 | 0 | 0 | 0 | 2.4178 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.6594 | 45.4 | 0 | 112.6594 | 1000.602 | 78.51% | 0 | 0 | 0 | 0% | 45.4
933 | 0 | 0 | 0 | 2.4178 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.7664 | 41.7 | 0 | 103.7664 | 896.8546 | 70.37% | 0 | 0 | 0 | 0% | 41.7
934 | 0 | 0 | 0 | 0.80595 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9419 | 39.3 | 0 | 97.9419 | 799.9058 | 62.76% | 0 | 0 | 0 | 0% | 39.3
935 | 0 | 0 | 0 | 0.40297 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1703 | 36.5 | 0 | 91.1703 | 710.9063 | 55.78% | 0 | 0 | 0 | 0% | 36.5
936 | 0 | 0 | 0 | 2.0149 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5992 | 34.6 | 0 | 86.5992 | 627.2512 | 49.22% | 0 | 0 | 0 | 0% | 34.6
937 | 0 | 0 | 0 | 2.8208 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9731 | 33.5 | 0 | 83.9731 | 546.7622 | 42.9% | 0 | 0 | 0 | 0% | 33.5
938 | 0 | 0 | 0 | 3.6268 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8142 | 33 | 0 | 82.8142 | 467.6921 | 36.7% | 0 | 0 | 0 | 0% | 33
939 | 0 | 0 | 0 | 1.8134 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0767 | 32.7 | 0 | 82.0767 | 389.4592 | 30.56% | 0 | 0 | 0 | 0% | 32.7
940 | 0 | 0 | 0 | 3.4253 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4684 | 33.7 | 0 | 84.4684 | 308.3419 | 24.19% | 0 | 0 | 0 | 0% | 33.7
941 | 0 | 0 | 0 | 4.6342 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.242 | 35.7 | 0 | 89.242 | 221.4717 | 17.38% | 0 | 0 | 0 | 0% | 35.7
942 | 0 | 0 | 0 | 5.8431 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7925 | 38 | 0 | 94.7925 | 128.0744 | 10.05% | 0 | 0 | 0 | 0% | 38
943 | 0 | 0 | 0 | 4.6342 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128.0744 | 10.05% | 0 | 0 | 0 | 0% | 0
944 | 290 | 52 | 18 | 4.6342 | 7.6 | 145.962 | 67.0054 | 0 | 43.3568 | 5.7772 | 0 | 0 | 5.7772 | 0 | 0 | 0 | 0 | 0 | 43.3568 | 0 | 169.3995 | 13.29% | 0 | 0 | 0 | 0% | 5.7772
945 | 750 | 234 | 43 | 1.8134 | 9.8 | 377.488 | 210.8296 | 0 | 179.3287 | 42.8889 | 0 | 0 | 42.8889 | 0 | 0 | 0 | 0 | 0 | 179.3287 | 0 | 340.3251 | 26.7% | 0 | 0 | 0 | 0% | 42.8889
946 | 898 | 424 | 55 | 1.4104 | 14.7 | 451.979 | 275.302 | 0 | 239.649 | 87.4477 | 0 | 21.9739 | 65.4739 | 0 | 0 | 0 | 0 | 0 | 239.649 | 0 | 568.7444 | 44.62% | 16.854 | 0 | 16.9462 | 33.89% | 43.5
947 | 963 | 574 | 61 | 3.4253 | 16.7 | 484.6946 | 307.6107 | 0 | 269.2169 | 106.8 | 6.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 269.2169 | 0 | 825.346 | 64.76% | 19.175 | 0 | 36.2262 | 72.45% | 43.2
948 | 997 | 669 | 63 | 4.4327 | 18 | 501.8074 | 321.2635 | 0 | 281.5978 | 108 | 15.1399 | 17.8601 | 75 | 0 | 0 | 0 | 0 | 0 | 281.5978 | 0 | 1093.7485 | 85.82% | 13.6987 | 0 | 50 | 100% | 42
949 | 1000 | 694 | 65 | 5.6416 | 18.1 | 503.3174 | 291.3314 | 27.0487 | 254.6617 | 109.8 | 34.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 254.6617 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.2
950 | 987 | 654 | 64 | 5.8431 | 19 | 496.7743 | 0 | 299.625 | 0 | 111 | 36 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39
951 | 937 | 546 | 63 | 6.8506 | 19 | 471.6084 | 0 | 257.0626 | 0 | 111.5 | 36.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.5
952 | 832 | 385 | 61 | 8.261 | 18 | 418.7601 | 0 | 183.1592 | 0 | 82.3907 | 21.0954 | 0 | 61.2954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.2
953 | 624 | 192 | 48 | 7.6565 | 16.1 | 314.0701 | 0 | 0 | 0 | 33.7022 | 0 | 0 | 33.7022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.8978 | 40.0495 | 80.1% | 43.6
954 | 153 | 28 | 14 | 4.6342 | 13.4 | 77.0076 | 0 | 0 | 0 | 2.5075 | 0 | 0 | 2.5075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 14.9159 | 29.83% | 27.5075
955 | 0 | 0 | 0 | 2.2164 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2673 | 29.7629 | 0 | 75.2673 | 1204.5155 | 94.51% | 0 | 14.8371 | 0 | 0% | 44.6
956 | 0 | 0 | 0 | 1.8134 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.6526 | 42.9 | 0 | 106.6526 | 1097.3649 | 86.1% | 0 | 0 | 0 | 0% | 42.9
957 | 0 | 0 | 0 | 1.6119 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1709 | 39.8 | 0 | 99.1709 | 998.9816 | 78.38% | 0 | 0 | 0 | 0% | 39.8
958 | 0 | 0 | 0 | 1.0074 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4011 | 37 | 0 | 92.4011 | 908.5943 | 71.29% | 0 | 0 | 0 | 0% | 37
959 | 0 | 0 | 0 | 2.0149 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7082 | 34.2 | 0 | 85.7082 | 826.1297 | 64.82% | 0 | 0 | 0 | 0% | 34.2
960 | 0 | 0 | 0 | 0.80595 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1683 | 31.9 | 0 | 80.1683 | 750.2081 | 58.86% | 0 | 0 | 0 | 0% | 31.9
961 | 0 | 0 | 0 | 2.2164 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2276 | 31.1 | 0 | 78.2276 | 676.5201 | 53.08% | 0 | 0 | 0 | 0% | 31.1
962 | 0 | 0 | 0 | 2.0149 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7838 | 30.5 | 0 | 76.7838 | 604.4908 | 47.43% | 0 | 0 | 0 | 0% | 30.5
963 | 0 | 0 | 0 | 1.8134 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2878 | 30.3 | 0 | 76.2878 | 533.0031 | 41.82% | 0 | 0 | 0 | 0% | 30.3
964 | 0 | 0 | 0 | 1.4104 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7529 | 30.9 | 0 | 77.7529 | 459.8339 | 36.08% | 0 | 0 | 0 | 0% | 30.9
965 | 0 | 0 | 0 | 1.0074 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1389 | 31.9 | 0 | 80.1389 | 383.8427 | 30.12% | 0 | 0 | 0 | 0% | 31.9
966 | 0 | 0 | 0 | 2.0149 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7767 | 33 | 0 | 82.7767 | 304.7073 | 23.91% | 0 | 0 | 0 | 0% | 33
967 | 0 | 0 | 0 | 1.4104 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7243 | 35.9 | 0 | 89.7243 | 217.2461 | 17.05% | 0 | 0 | 0 | 0% | 35.9
968 | 295 | 68 | 34 | 1.8134 | 7.6 | 148.4786 | 68.5877 | 0 | 45.8769 | 7.5612 | 0 | 0 | 7.5612 | 0 | 0 | 0 | 78.6193 | 31.2388 | 45.8769 | 78.6193 | 186.2657 | 14.61% | 0 | 0 | 0 | 0% | 38.8
969 | 631 | 222 | 52 | 1.8134 | 12.1 | 317.5933 | 178.0337 | 0 | 148.7019 | 37.7919 | 0 | 0 | 37.7919 | 0 | 0 | 0 | 0 | 0 | 148.7019 | 0 | 326.2009 | 25.59% | 0 | 0 | 0 | 0% | 37.7919
970 | 908 | 435 | 57 | 5.0372 | 16.1 | 457.0122 | 278.8914 | 0 | 241.7086 | 95.6995 | 2.8497 | 25 | 67.8497 | 0 | 0 | 0 | 0 | 0 | 241.7086 | 0 | 553.6595 | 43.44% | 19.175 | 0 | 19.2827 | 38.57% | 40
971 | 957 | 591 | 75 | 8.6639 | 17.6 | 481.6747 | 305.9695 | 0 | 264.8728 | 109.6 | 9.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 264.8728 | 0 | 802.9166 | 63% | 19.175 | 0 | 38.5655 | 77.13% | 40.4
972 | 976 | 667 | 67 | 5.4401 | 18.3 | 491.2378 | 314.808 | 0 | 275.1009 | 109.7 | 19.8752 | 14.8248 | 75 | 0 | 0 | 0 | 0 | 0 | 275.1009 | 0 | 1061.7989 | 83.31% | 11.3706 | 0 | 50 | 100% | 40.3
973 | 957 | 707 | 98 | 5.4401 | 19.5 | 481.6747 | 301.4544 | 3.4951 | 262.8982 | 111.7 | 36.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 262.8982 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.3
974 | 764 | 605 | 140 | 6.4476 | 19.8 | 384.5345 | 0 | 232.3335 | 0 | 112.9 | 37.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.1
975 | 664 | 506 | 154 | 5.8431 | 19.9 | 334.2027 | 0 | 182.7777 | 0 | 100.9114 | 31.9557 | 0 | 68.9557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37
976 | 683 | 368 | 98 | 4.4327 | 19.7 | 343.7658 | 0 | 151.2481 | 0 | 71.2405 | 16.2703 | 0 | 54.9703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.7
977 | 444 | 191 | 79 | 7.858 | 18.9 | 223.4729 | 0 | 0 | 0 | 28.5401 | 0 | 0 | 28.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 14.0599 | 35.8633 | 71.73% | 42.6
978 | 8 | 21 | 20 | 3.6268 | 16.7 | 4.0265 | 0 | 0 | 0 | 0.84742 | 0 | 0 | 0.84742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.7259 | 21.45% | 25.8474
979 | 0 | 0 | 0 | 3.6268 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.084 | 33.732 | 0 | 85.084 | 1193.4293 | 93.64% | 0 | 10.668 | 0 | 0% | 44.4
980 | 0 | 0 | 0 | 1.2089 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3794 | 42.7 | 0 | 106.3794 | 1086.8577 | 85.28% | 0 | 0 | 0 | 0% | 42.7
981 | 0 | 0 | 0 | 2.4178 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3947 | 39.4 | 0 | 98.3947 | 989.6359 | 77.65% | 0 | 0 | 0 | 0% | 39.4
982 | 0 | 0 | 0 | 1.2089 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.372 | 36.1 | 0 | 90.372 | 901.7769 | 70.75% | 0 | 0 | 0 | 0% | 36.1
983 | 0 | 0 | 0 | 2.6193 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3614 | 33.6 | 0 | 84.3614 | 821.0325 | 64.42% | 0 | 0 | 0 | 0% | 33.6
984 | 0 | 0 | 0 | 3.8283 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7544 | 32.1 | 0 | 80.7544 | 744.552 | 58.42% | 0 | 0 | 0 | 0% | 32.1
985 | 0 | 0 | 0 | 4.2312 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5358 | 31.6 | 0 | 79.5358 | 669.4685 | 52.53% | 0 | 0 | 0 | 0% | 31.6
986 | 0 | 0 | 0 | 4.8357 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5436 | 31.6 | 0 | 79.5436 | 594.3724 | 46.64% | 0 | 0 | 0 | 0% | 31.6
987 | 0 | 0 | 0 | 4.4327 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3697 | 32.8 | 0 | 82.3697 | 515.8784 | 40.48% | 0 | 0 | 0 | 0% | 32.8
988 | 0 | 0 | 0 | 3.0223 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1251 | 37.3 | 0 | 93.1251 | 424.5576 | 33.31% | 0 | 0 | 0 | 0% | 37.3
989 | 0 | 0 | 0 | 3.0223 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.0325 | 43.9 | 0 | 109.0325 | 314.3786 | 24.67% | 0 | 0 | 0 | 0% | 43.9
990 | 0 | 0 | 0 | 3.0223 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.4586 | 47.4 | 0 | 117.4586 | 194.0956 | 15.23% | 0 | 0 | 0 | 0% | 47.4
991 | 0 | 0 | 0 | 2.2164 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.8427 | 43.0121 | 0 | 106.8427 | 86.3865 | 6.778% | 0 | 0 | 0 | 0% | 43.0121
992 | 275 | 54 | 20 | 2.8208 | 8 | 138.4123 | 64.3357 | 0 | 41.7183 | 6.3298 | 0 | 0 | 6.3298 | 0 | 0 | 0 | 0 | 0 | 41.7183 | 0 | 126.2988 | 9.91% | 0 | 0 | 0 | 0% | 6.3298
993 | 717 | 234 | 46 | 3.6268 | 12.1 | 360.8786 | 203.0444 | 0 | 171.412 | 41.7457 | 0 | 0 | 41.7457 | 0 | 0 | 0 | 0 | 0 | 171.412 | 0 | 290.2904 | 22.78% | 0 | 0 | 0 | 0% | 41.7457
994 | 829 | 407 | 59 | 2.8208 | 15.3 | 417.2501 | 255.107 | 0 | 220.229 | 76.1954 | 0 | 13.7977 | 62.3977 | 0 | 0 | 0 | 0 | 0 | 220.229 | 0 | 500.9857 | 39.31% | 10.5829 | 0 | 10.6438 | 21.29% | 48.6
995 | 926 | 563 | 61 | 4.4327 | 17.2 | 466.0719 | 296.3267 | 0 | 258.3913 | 101.7 | 1.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 258.3913 | 0 | 748.1914 | 58.7% | 19.175 | 0 | 29.9293 | 59.86% | 48.3
996 | 961 | 655 | 62 | 3.4253 | 18.4 | 483.688 | 310.2805 | 0 | 271.7166 | 103.3 | 3.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 271.7166 | 0 | 1008.1455 | 79.1% | 19.175 | 0 | 49.2148 | 98.43% | 46.7
997 | 963 | 680 | 65 | 3.2238 | 19.2 | 484.6946 | 307.1278 | 0 | 268.862 | 104.2 | 29.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 268.862 | 0 | 1265.3685 | 99.28% | 0 | 0 | 49.2148 | 98.43% | 45.8
998 | 939 | 653 | 83 | 8.8654 | 19.5 | 472.615 | 0 | 286.0593 | 0 | 104.8 | 29.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.3685 | 99.28% | 0 | 0 | 49.2148 | 98.43% | 45.2
999 | 862 | 592 | 139 | 11.0818 | 18.9 | 433.8596 | 0 | 238.0924 | 0 | 105.1 | 30.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.3685 | 99.28% | 0 | 0 | 49.2148 | 98.43% | 44.9
1000 | 275 | 334 | 214 | 8.8654 | 18.2 | 138.4123 | 0 | 61.2644 | 0 | 39.353 | 0 | 0 | 39.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.3685 | 99.28% | 0 | 6.147 | 43.0333 | 86.07% | 45.5
1001 | 48 | 109 | 96 | 10.0743 | 16.2 | 24.1592 | 0 | 0 | 0 | 10.6983 | 0 | 0 | 10.6983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.3685 | 99.28% | 0 | 25 | 17.8928 | 35.79% | 35.6983
1002 | 1 | 25 | 25 | 7.2535 | 15.1 | 0.50332 | 0 | 0 | 0 | 1.0854 | 0 | 0 | 1.0854 | 0 | 0 | 0 | 78.8864 | 31.1216 | 0 | 78.8864 | 1191.7015 | 93.5% | 0 | 17.793 | 0 | 0% | 50
1003 | 0 | 0 | 0 | 6.2461 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.1837 | 49.2 | 0 | 122.1837 | 1066.4065 | 83.67% | 0 | 0 | 0 | 0% | 49.2
1004 | 0 | 0 | 0 | 5.6416 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.1693 | 45.5 | 0 | 113.1693 | 951.8058 | 74.68% | 0 | 0 | 0 | 0% | 45.5
1005 | 0 | 0 | 0 | 5.2387 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.763 | 41.2 | 0 | 102.763 | 849.4834 | 66.65% | 0 | 0 | 0 | 0% | 41.2
1006 | 0 | 0 | 0 | 8.4625 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4062 | 38.6 | 0 | 96.4062 | 754.5506 | 59.2% | 0 | 0 | 0 | 0% | 38.6
1007 | 0 | 0 | 0 | 8.4625 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8527 | 36.3 | 0 | 90.8527 | 666.1216 | 52.26% | 0 | 0 | 0 | 0% | 36.3
1008 | 0 | 0 | 0 | 8.8654 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.013 | 34.7 | 0 | 87.013 | 582.1829 | 45.68% | 0 | 0 | 0 | 0% | 34.7
1009 | 0 | 0 | 0 | 6.0446 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3422 | 34 | 0 | 85.3422 | 500.2599 | 39.25% | 0 | 0 | 0 | 0% | 34
1010 | 0 | 0 | 0 | 7.052 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5662 | 34.1 | 0 | 85.5662 | 418.031 | 32.8% | 0 | 0 | 0 | 0% | 34.1
1011 | 0 | 0 | 0 | 6.8506 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6899 | 35 | 0 | 87.6899 | 333.1639 | 26.14% | 0 | 0 | 0 | 0% | 35
1012 | 0 | 0 | 0 | 7.6565 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.801 | 38.8 | 0 | 96.801 | 237.5391 | 18.64% | 0 | 0 | 0 | 0% | 38.8
1013 | 0 | 0 | 0 | 7.2535 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4185 | 45.3 | 0 | 112.4185 | 123.2894 | 9.673% | 0 | 0 | 0 | 0% | 45.3
1014 | 0 | 0 | 0 | 6.8506 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2894 | 9.673% | 0 | 0 | 0 | 0% | 0
1015 | 0 | 0 | 0 | 4.6342 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2894 | 9.673% | 0 | 0 | 0 | 0% | 0
1016 | 0 | 13 | 13 | 4.4327 | 9.1 | 0 | 0 | 0 | 0 | 0.42812 | 0 | 0 | 0.42812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2894 | 9.673% | 0 | 0 | 0 | 0% | 0.42812
1017 | 18 | 95 | 88 | 6.6491 | 9.8 | 9.0597 | 0 | 5.1161 | 0 | 7.879 | 0 | 0 | 7.879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2894 | 9.673% | 0 | 0 | 0 | 0% | 7.879
1018 | 52 | 265 | 237 | 10.0743 | 11 | 26.1725 | 0 | 16.0322 | 0 | 26.9129 | 0 | 0 | 26.9129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2894 | 9.673% | 0 | 0 | 0 | 0% | 26.9129
1019 | 403 | 561 | 326 | 11.4848 | 12.1 | 202.8369 | 129.0806 | 0 | 97.5917 | 87.3587 | 0 | 19.3293 | 68.0293 | 0 | 0 | 0 | 0 | 0 | 97.5917 | 0 | 217.2233 | 17.04% | 14.8256 | 0 | 14.9131 | 29.83% | 48.7
1020 | 762 | 620 | 140 | 10.8803 | 12.7 | 383.5278 | 246.2785 | 0 | 207.5213 | 103 | 3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 207.5213 | 0 | 416.9664 | 32.72% | 19.175 | 0 | 34.2013 | 68.4% | 47
1021 | 910 | 687 | 99 | 12.8952 | 13.4 | 458.0188 | 290.4807 | 0 | 247.7392 | 103.8 | 8.323 | 20.477 | 75 | 0 | 0 | 0 | 0 | 0 | 247.7392 | 0 | 655.42 | 51.43% | 15.7059 | 0 | 50 | 100% | 46.2
1022 | 897 | 650 | 101 | 13.2981 | 13.5 | 451.4757 | 273.7594 | 0 | 231.6488 | 104.3 | 29.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 231.6488 | 0 | 878.3863 | 68.92% | 0 | 0 | 50 | 100% | 45.7
1023 | 847 | 556 | 107 | 12.0892 | 13.4 | 426.3098 | 234.7641 | 0 | 196.2047 | 104.6 | 29.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 196.2047 | 0 | 1067.237 | 83.74% | 0 | 0 | 50 | 100% | 45.4
1024 | 754 | 390 | 89 | 11.2833 | 13.1 | 379.5013 | 169.0025 | 0 | 135.144 | 76.1279 | 15.1139 | 0 | 61.0139 | 0 | 0 | 0 | 0 | 0 | 135.144 | 0 | 1197.3156 | 93.94% | 0 | 0 | 50 | 100% | 45.9
1025 | 561 | 191 | 57 | 11.0818 | 12.3 | 282.3611 | 0 | 0 | 0 | 32.7346 | 0 | 0 | 32.7346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1197.3156 | 93.94% | 0 | 16.7654 | 33.1382 | 66.28% | 49.5
1026 | 149 | 32 | 17 | 9.6714 | 10.8 | 74.9943 | 0 | 0 | 0 | 2.9562 | 0 | 0 | 2.9562 | 0 | 0 | 0 | 57.8119 | 22.0438 | 0 | 57.8119 | 1144.6532 | 89.81% | 0 | 25 | 7.9936 | 15.99% | 50
1027 | 0 | 0 | 0 | 6.8506 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6497 | 41.6515 | 0 | 103.6497 | 1041.0525 | 81.68% | 0 | 7.9485 | 0 | 0% | 49.6
1028 | 0 | 0 | 0 | 6.8506 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3149 | 45.7 | 0 | 113.3149 | 925.8507 | 72.64% | 0 | 0 | 0 | 0% | 45.7
1029 | 0 | 0 | 0 | 4.8357 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7029 | 41.3 | 0 | 102.7029 | 823.2152 | 64.59% | 0 | 0 | 0 | 0% | 41.3
1030 | 0 | 0 | 0 | 3.6268 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9778 | 38.5 | 0 | 95.9778 | 728.54 | 57.16% | 0 | 0 | 0 | 0% | 38.5
1031 | 0 | 0 | 0 | 3.4253 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2065 | 36.1 | 0 | 90.2065 | 640.6454 | 50.27% | 0 | 0 | 0 | 0% | 36.1
1032 | 0 | 0 | 0 | 2.2164 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1234 | 34.4 | 0 | 86.1234 | 557.5538 | 43.75% | 0 | 0 | 0 | 0% | 34.4
1033 | 0 | 0 | 0 | 3.2238 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9289 | 33.9 | 0 | 84.9289 | 475.8942 | 37.34% | 0 | 0 | 0 | 0% | 33.9
1034 | 0 | 0 | 0 | 4.6342 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4511 | 33.7 | 0 | 84.4511 | 394.7942 | 30.98% | 0 | 0 | 0 | 0% | 33.7
1035 | 0 | 0 | 0 | 3.6268 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0759 | 34.8 | 0 | 87.0759 | 310.4835 | 24.36% | 0 | 0 | 0 | 0% | 34.8
1036 | 0 | 0 | 0 | 4.4327 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1974 | 38.6 | 0 | 96.1974 | 215.3984 | 16.9% | 0 | 0 | 0 | 0% | 38.6
1037 | 0 | 0 | 0 | 3.8283 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9425 | 29.267 | 0 | 73.9425 | 146.4682 | 11.49% | 0 | 0 | 0 | 0% | 29.267
1038 | 0 | 0 | 0 | 3.6268 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.4682 | 11.49% | 0 | 0 | 0 | 0% | 0
1039 | 0 | 0 | 0 | 4.6342 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.4682 | 11.49% | 0 | 0 | 0 | 0% | 0
1040 | 256 | 56 | 22 | 3.8283 | 4 | 128.8493 | 60.6224 | 0 | 38.1041 | 6.7834 | 0 | 0 | 6.7834 | 0 | 0 | 0 | 0 | 0 | 38.1041 | 0 | 182.8618 | 14.35% | 0 | 0 | 0 | 0% | 6.7834
1041 | 722 | 249 | 53 | 5.4401 | 7.6 | 363.3952 | 205.9652 | 0 | 173.3058 | 43.7083 | 0 | 0 | 43.7083 | 0 | 0 | 0 | 0 | 0 | 173.3058 | 0 | 348.3877 | 27.34% | 0 | 0 | 0 | 0% | 43.7083
1042 | 857 | 438 | 70 | 11.0818 | 10.2 | 431.343 | 264.7233 | 0 | 224.4675 | 89.4979 | 0 | 20.349 | 69.149 | 0 | 0 | 0 | 0 | 0 | 224.4675 | 0 | 562.7785 | 44.16% | 15.6077 | 0 | 15.702 | 31.4% | 48.8
1043 | 939 | 587 | 69 | 12.0892 | 11.4 | 472.615 | 301.037 | 0 | 257.9997 | 102 | 2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 257.9997 | 0 | 809.1963 | 63.49% | 19.175 | 0 | 34.9929 | 69.99% | 48
1044 | 982 | 682 | 67 | 11.8877 | 12.7 | 494.2577 | 317.7084 | 0 | 273.6548 | 103.5 | 9.0517 | 19.4483 | 75 | 0 | 0 | 0 | 0 | 0 | 273.6548 | 0 | 1070.5664 | 84% | 14.9169 | 0 | 50 | 100% | 46.5
1045 | 1001 | 713 | 64 | 12.8952 | 13.8 | 503.8207 | 319.8153 | 0 | 275.0211 | 104.4 | 29.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 275.0211 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.6
1046 | 980 | 671 | 66 | 13.0966 | 14.3 | 493.251 | 0 | 299.6419 | 0 | 104.9 | 29.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.1
1047 | 946 | 567 | 63 | 14.5071 | 14 | 476.1382 | 0 | 263.1329 | 0 | 105.3 | 30.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.7
1048 | 875 | 410 | 56 | 13.9026 | 13.4 | 440.4027 | 0 | 197.3398 | 0 | 84.5605 | 19.7302 | 0 | 64.8302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.1
1049 | 703 | 215 | 44 | 12.4922 | 12.3 | 353.8321 | 0 | 0 | 0 | 37.7303 | 0 | 0 | 37.7303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 11.2697 | 38.6639 | 77.33% | 49
1050 | 203 | 38 | 16 | 11.6862 | 10.2 | 102.1734 | 0 | 0 | 0 | 3.4172 | 0 | 0 | 3.4172 | 0 | 0 | 0 | 56.6829 | 21.5828 | 0 | 56.6829 | 1222.924 | 95.95% | 0 | 25 | 13.516 | 27.03% | 50
1051 | 0 | 0 | 0 | 8.8654 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9522 | 35.9629 | 0 | 89.9522 | 1135.4811 | 89.09% | 0 | 13.4371 | 0 | 0% | 49.4
1052 | 0 | 0 | 0 | 9.2684 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.1108 | 45.6 | 0 | 113.1108 | 1020.5623 | 80.07% | 0 | 0 | 0 | 0% | 45.6
1053 | 0 | 0 | 0 | 8.261 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7133 | 41.3 | 0 | 102.7133 | 917.9251 | 72.02% | 0 | 0 | 0 | 0% | 41.3
1054 | 0 | 0 | 0 | 6.0446 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9778 | 38.5 | 0 | 95.9778 | 823.2494 | 64.59% | 0 | 0 | 0 | 0% | 38.5
1055 | 0 | 0 | 0 | 4.8357 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7243 | 35.9 | 0 | 89.7243 | 735.9154 | 57.74% | 0 | 0 | 0 | 0% | 35.9
1056 | 0 | 0 | 0 | 6.8506 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.885 | 34.3 | 0 | 85.885 | 653.1156 | 51.24% | 0 | 0 | 0 | 0% | 34.3
1057 | 0 | 0 | 0 | 5.8431 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2121 | 33.6 | 0 | 84.2121 | 572.3238 | 44.91% | 0 | 0 | 0 | 0% | 33.6
1058 | 0 | 0 | 0 | 4.0297 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9731 | 33.5 | 0 | 83.9731 | 491.8043 | 38.59% | 0 | 0 | 0 | 0% | 33.5
1059 | 0 | 0 | 0 | 4.6342 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1223 | 34.4 | 0 | 86.1223 | 408.6668 | 32.06% | 0 | 0 | 0 | 0% | 34.4
1060 | 0 | 0 | 0 | 4.2312 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2161 | 38.2 | 0 | 95.2161 | 314.7407 | 24.7% | 0 | 0 | 0 | 0% | 38.2
1061 | 0 | 0 | 0 | 3.6268 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3402 | 44.9 | 0 | 111.3402 | 201.623 | 15.82% | 0 | 0 | 0 | 0% | 44.9
1062 | 0 | 0 | 0 | 4.6342 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9914 | 35.2142 | 0 | 87.9914 | 116.059 | 9.106% | 0 | 0 | 0 | 0% | 35.2142
1063 | 0 | 0 | 0 | 3.8283 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.059 | 9.106% | 0 | 0 | 0 | 0% | 0
1064 | 264 | 59 | 24 | 3.4253 | 3.4 | 132.8758 | 62.7558 | 0 | 40.0736 | 7.5136 | 0 | 0 | 7.5136 | 0 | 0 | 0 | 0 | 0 | 40.0736 | 0 | 154.3692 | 12.11% | 0 | 0 | 0 | 0% | 7.5136
1065 | 716 | 250 | 52 | 4.6342 | 7.8 | 360.3752 | 204.9999 | 0 | 172.8348 | 43.226 | 0 | 0 | 43.226 | 0 | 0 | 0 | 0 | 0 | 172.8348 | 0 | 319.5987 | 25.08% | 0 | 0 | 0 | 0% | 43.226
1066 | 866 | 439 | 64 | 9.2684 | 11 | 435.8729 | 268.0115 | 0 | 228.7184 | 88.0014 | 0 | 19.8007 | 68.2007 | 0 | 0 | 0 | 0 | 0 | 228.7184 | 0 | 538.2527 | 42.23% | 15.1871 | 0 | 15.2811 | 30.56% | 48.4
1067 | 938 | 589 | 68 | 11.2833 | 12.1 | 472.1117 | 300.9938 | 0 | 258.4878 | 102.1 | 2.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 258.4878 | 0 | 785.3662 | 61.62% | 19.175 | 0 | 34.5748 | 69.15% | 47.9
1068 | 964 | 682 | 73 | 11.2833 | 13.3 | 485.198 | 312.2086 | 0 | 268.9291 | 103.6 | 8.6126 | 19.9874 | 75 | 0 | 0 | 0 | 0 | 0 | 268.9291 | 0 | 1042.4615 | 81.79% | 15.3303 | 0 | 50 | 100% | 46.4
1069 | 972 | 709 | 74 | 12.0892 | 14.4 | 489.2245 | 310.8327 | 0 | 267.176 | 104.3 | 29.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 267.176 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.7
1070 | 946 | 665 | 77 | 12.8952 | 14.8 | 476.1382 | 0 | 289.7883 | 0 | 104.9 | 29.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.1
1071 | 902 | 560 | 75 | 13.7011 | 14.7 | 453.9923 | 0 | 251.7974 | 0 | 105 | 30 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45
1072 | 821 | 404 | 67 | 13.0966 | 14.2 | 413.2236 | 0 | 186.325 | 0 | 80.4296 | 17.6148 | 0 | 62.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.2
1073 | 638 | 212 | 53 | 12.4922 | 12.9 | 321.1165 | 0 | 0 | 0 | 35.8654 | 0 | 0 | 35.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 13.0346 | 36.8867 | 73.77% | 48.9
1074 | 168 | 38 | 19 | 11.6862 | 10.8 | 84.5573 | 0 | 0 | 0 | 3.5448 | 0 | 0 | 3.5448 | 0 | 0 | 0 | 56.4446 | 21.4552 | 0 | 56.4446 | 1223.1603 | 95.97% | 0 | 25 | 11.7351 | 23.47% | 50
1075 | 0 | 0 | 0 | 7.858 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.761 | 37.5349 | 0 | 93.761 | 1131.2826 | 88.76% | 0 | 11.6651 | 0 | 0% | 49.2
1076 | 0 | 0 | 0 | 7.6565 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.1398 | 45.6 | 0 | 113.1398 | 1016.3782 | 79.75% | 0 | 0 | 0 | 0% | 45.6
1077 | 0 | 0 | 0 | 6.0446 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.044 | 41.4 | 0 | 103.044 | 913.4711 | 71.67% | 0 | 0 | 0 | 0% | 41.4
1078 | 0 | 0 | 0 | 3.6268 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7272 | 38.8 | 0 | 96.7272 | 817.9554 | 64.18% | 0 | 0 | 0 | 0% | 38.8
1079 | 0 | 0 | 0 | 4.2312 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5149 | 36.2 | 0 | 90.5149 | 729.8157 | 57.26% | 0 | 0 | 0 | 0% | 36.2
1080 | 0 | 0 | 0 | 4.0297 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4228 | 34.5 | 0 | 86.4228 | 646.4639 | 50.72% | 0 | 0 | 0 | 0% | 34.5
1081 | 0 | 0 | 0 | 4.6342 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9381 | 33.9 | 0 | 84.9381 | 564.817 | 44.32% | 0 | 0 | 0 | 0% | 33.9
1082 | 0 | 0 | 0 | 4.0297 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6901 | 33.8 | 0 | 84.6901 | 483.4433 | 37.93% | 0 | 0 | 0 | 0% | 33.8
1083 | 0 | 0 | 0 | 3.6268 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8376 | 34.7 | 0 | 86.8376 | 399.4422 | 31.34% | 0 | 0 | 0 | 0% | 34.7
1084 | 0 | 0 | 0 | 4.6342 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9515 | 38.5 | 0 | 95.9515 | 304.6689 | 23.9% | 0 | 0 | 0 | 0% | 38.5
1085 | 0 | 0 | 0 | 4.4327 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3417 | 44.9 | 0 | 111.3417 | 191.5635 | 15.03% | 0 | 0 | 0 | 0% | 44.9
1086 | 0 | 0 | 0 | 3.6268 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.0906 | 28.8836 | 0 | 73.0906 | 123.5676 | 9.695% | 0 | 0 | 0 | 0% | 28.8836
1087 | 0 | 0 | 0 | 3.2238 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.5676 | 9.695% | 0 | 0 | 0 | 0% | 0
1088 | 218 | 59 | 30 | 3.4253 | 5.2 | 109.7232 | 0 | 52.0178 | 0 | 7.3465 | 0 | 0 | 7.3465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.5676 | 9.695% | 0 | 0 | 0 | 0% | 7.3465
1089 | 617 | 245 | 70 | 4.6342 | 8.1 | 310.5468 | 177.053 | 0 | 146.7018 | 40.3084 | 0 | 0 | 40.3084 | 0 | 0 | 0 | 0 | 0 | 146.7018 | 0 | 263.7426 | 20.69% | 0 | 0 | 0 | 0% | 40.3084
1090 | 777 | 432 | 90 | 9.0669 | 10.5 | 391.0776 | 240.925 | 0 | 203.6648 | 82.9918 | 0 | 17.1959 | 65.7959 | 0 | 0 | 0 | 0 | 0 | 203.6648 | 0 | 458.3464 | 35.96% | 13.1892 | 0 | 13.2727 | 26.55% | 48.6
1091 | 858 | 581 | 98 | 11.6862 | 11.6 | 431.8463 | 275.5779 | 0 | 234.318 | 102 | 2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 234.318 | 0 | 682.2396 | 53.53% | 19.175 | 0 | 32.5691 | 65.14% | 48
1092 | 897 | 674 | 102 | 13.0966 | 12.2 | 451.4757 | 290.8144 | 0 | 247.8927 | 103.6 | 6.017 | 22.583 | 75 | 0 | 0 | 0 | 0 | 0 | 247.8927 | 0 | 919.1036 | 72.11% | 17.3212 | 0 | 50 | 100% | 46.4
1093 | 908 | 698 | 101 | 13.2981 | 12.8 | 457.0122 | 290.6347 | 0 | 247.6148 | 104.8 | 29.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 247.6148 | 0 | 1155.702 | 90.68% | 0 | 0 | 50 | 100% | 45.2
1094 | 896 | 660 | 98 | 14.3056 | 13.7 | 450.9724 | 230.0731 | 44.9213 | 194.2584 | 105.6 | 30.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 194.2584 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.4
1095 | 860 | 558 | 91 | 14.5071 | 13.9 | 432.853 | 0 | 240.9504 | 0 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.9
1096 | 779 | 402 | 79 | 13.9026 | 14.1 | 392.0842 | 0 | 177.9185 | 0 | 78.4778 | 17.0389 | 0 | 61.4389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.4
1097 | 611 | 213 | 58 | 12.8952 | 13.3 | 307.5269 | 0 | 0 | 0 | 35.1429 | 0 | 0 | 35.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 12.7571 | 37.1641 | 74.33% | 47.9
1098 | 162 | 38 | 19 | 10.6788 | 11.2 | 81.5374 | 0 | 0 | 0 | 3.479 | 0 | 0 | 3.479 | 0 | 0 | 0 | 53.3575 | 20.121 | 0 | 53.3575 | 1226.1031 | 96.2% | 0 | 25 | 12.009 | 24.02% | 48.6
1099 | 0 | 0 | 0 | 8.4625 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4925 | 35.7644 | 0 | 89.4925 | 1139.2096 | 89.38% | 0 | 11.9356 | 0 | 0% | 47.7
1100 | 0 | 0 | 0 | 8.0595 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4816 | 44.5 | 0 | 110.4816 | 1027.4638 | 80.62% | 0 | 0 | 0 | 0% | 44.5
1101 | 0 | 0 | 0 | 6.2461 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9907 | 41 | 0 | 101.9907 | 925.6888 | 72.63% | 0 | 0 | 0 | 0% | 41
1102 | 0 | 0 | 0 | 5.0372 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9891 | 38.5 | 0 | 95.9891 | 831.0311 | 65.2% | 0 | 0 | 0 | 0% | 38.5
1103 | 0 | 0 | 0 | 3.6268 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4832 | 35.8 | 0 | 89.4832 | 743.9896 | 58.37% | 0 | 0 | 0 | 0% | 35.8
1104 | 0 | 0 | 0 | 5.2387 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6961 | 33.8 | 0 | 84.6961 | 662.6476 | 51.99% | 0 | 0 | 0 | 0% | 33.8
1105 | 0 | 0 | 0 | 4.8357 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3048 | 32.8 | 0 | 82.3048 | 584.1584 | 45.83% | 0 | 0 | 0 | 0% | 32.8
1106 | 0 | 0 | 0 | 4.0297 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.099 | 32.3 | 0 | 81.099 | 507.0757 | 39.79% | 0 | 0 | 0 | 0% | 32.3
1107 | 0 | 0 | 0 | 5.8431 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6191 | 32.1 | 0 | 80.6191 | 430.5438 | 33.78% | 0 | 0 | 0 | 0% | 32.1
1108 | 0 | 0 | 0 | 6.0446 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7767 | 33 | 0 | 82.7767 | 351.4353 | 27.57% | 0 | 0 | 0 | 0% | 33
1109 | 0 | 0 | 0 | 7.6565 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0353 | 35.2 | 0 | 88.0353 | 265.9626 | 20.87% | 0 | 0 | 0 | 0% | 35.2
1110 | 0 | 0 | 0 | 7.455 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.336 | 37.4 | 0 | 93.336 | 174.2742 | 13.67% | 0 | 0 | 0 | 0% | 37.4
1111 | 0 | 1 | 1 | 7.455 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6251 | 31.6861 | 0 | 79.6251 | 98.8142 | 7.753% | 0 | 0 | 0 | 0% | 31.6861
1112 | 291 | 71 | 32 | 7.2535 | 6.2 | 146.4654 | 69.7014 | 0 | 44.166 | 9.2989 | 0 | 0 | 9.2989 | 0 | 0 | 0 | 0 | 0 | 44.166 | 0 | 140.699 | 11.04% | 0 | 0 | 0 | 0% | 9.2989
1113 | 682 | 266 | 73 | 9.2684 | 9.4 | 343.2625 | 196.033 | 0 | 161.5668 | 45.0942 | 0.8971 | 0 | 44.1971 | 0 | 0 | 0 | 0 | 0 | 161.5668 | 0 | 293.9207 | 23.06% | 0 | 0 | 0 | 0% | 43.3
1114 | 812 | 454 | 94 | 14.1041 | 12.1 | 408.6937 | 252.2568 | 0 | 211.0105 | 94.5248 | 0.96238 | 25 | 68.5624 | 0 | 0 | 0 | 0 | 0 | 211.0105 | 0 | 494.0324 | 38.76% | 19.175 | 0 | 19.2991 | 38.6% | 42.6
1115 | 734 | 542 | 125 | 16.9249 | 13 | 369.435 | 235.9703 | 0 | 194.3797 | 107.8 | 7.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 194.3797 | 0 | 678.3722 | 53.23% | 19.175 | 0 | 38.5983 | 77.2% | 42.2
1116 | 686 | 632 | 187 | 18.9398 | 13.6 | 345.2757 | 222.6423 | 0 | 180.7178 | 108.8 | 19.0303 | 14.7697 | 75 | 0 | 0 | 0 | 0 | 0 | 180.7178 | 0 | 849.7558 | 66.67% | 11.3284 | 0 | 50 | 100% | 41.2
1117 | 734 | 678 | 186 | 18.3353 | 14.4 | 369.435 | 235.1607 | 0 | 192.8834 | 110.6 | 35.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 192.8834 | 0 | 1032.6766 | 81.03% | 0 | 0 | 50 | 100% | 39.4
1118 | 841 | 682 | 149 | 17.5294 | 15 | 423.2899 | 258.6133 | 0 | 214.9808 | 111.8 | 36.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 214.9808 | 0 | 1236.5535 | 97.02% | 0 | 0 | 50 | 100% | 38.2
1119 | 719 | 531 | 130 | 15.716 | 15.4 | 361.8852 | 0 | 202.1929 | 0 | 110.3056 | 36.3528 | 0 | 73.9528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.5535 | 97.02% | 0 | 0 | 50 | 100% | 37.6
1120 | 562 | 360 | 121 | 14.91 | 15 | 282.8644 | 0 | 129.1837 | 0 | 63.4979 | 12.3989 | 0 | 51.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.5535 | 97.02% | 0 | 0 | 50 | 100% | 38.7
1121 | 270 | 160 | 86 | 14.91 | 12.8 | 135.8957 | 0 | 0 | 0 | 21.1771 | 0 | 0 | 21.1771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.5535 | 97.02% | 0 | 21.4229 | 28.4417 | 56.88% | 42.6
1122 | 3 | 24 | 24 | 12.4922 | 10.3 | 1.51 | 0 | 0 | 0 | 1.0811 | 0 | 0 | 1.0811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.5535 | 97.02% | 0 | 25 | 3.2825 | 6.565% | 26.0811
1123 | 0 | 0 | 0 | 9.4699 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.7231 | 40.4371 | 0 | 100.7231 | 1136.4019 | 89.16% | 0 | 3.2629 | 0 | 0% | 43.7
1124 | 0 | 0 | 0 | 10.4773 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9941 | 41.8 | 0 | 103.9941 | 1032.3918 | 81% | 0 | 0 | 0 | 0% | 41.8
1125 | 0 | 0 | 0 | 8.0595 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7272 | 38.8 | 0 | 96.7272 | 936.9039 | 73.51% | 0 | 0 | 0 | 0% | 38.8
1126 | 0 | 0 | 0 | 8.8654 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7388 | 35.9 | 0 | 89.7388 | 849.6116 | 66.66% | 0 | 0 | 0 | 0% | 35.9
1127 | 0 | 0 | 0 | 4.8357 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5059 | 33.3 | 0 | 83.5059 | 769.7292 | 60.39% | 0 | 0 | 0 | 0% | 33.3
1128 | 0 | 0 | 0 | 5.4401 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1778 | 31.5 | 0 | 79.1778 | 694.9387 | 54.53% | 0 | 0 | 0 | 0% | 31.5
1129 | 0 | 0 | 0 | 5.4401 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.529 | 30.4 | 0 | 76.529 | 623.2038 | 48.9% | 0 | 0 | 0 | 0% | 30.4
1130 | 0 | 0 | 0 | 7.052 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1245 | 29.8 | 0 | 75.1245 | 553.0531 | 43.39% | 0 | 0 | 0 | 0% | 29.8
1131 | 0 | 0 | 0 | 7.2535 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1245 | 29.8 | 0 | 75.1245 | 482.8893 | 37.89% | 0 | 0 | 0 | 0% | 29.8
1132 | 0 | 0 | 0 | 6.4476 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2878 | 30.3 | 0 | 76.2878 | 411.3907 | 32.28% | 0 | 0 | 0 | 0% | 30.3
1133 | 0 | 0 | 0 | 5.4401 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6968 | 31.3 | 0 | 78.6968 | 337.0888 | 26.45% | 0 | 0 | 0 | 0% | 31.3
1134 | 0 | 0 | 0 | 4.2312 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.099 | 32.3 | 0 | 81.099 | 259.9468 | 20.4% | 0 | 0 | 0 | 0% | 32.3
1135 | 0 | 0 | 0 | 4.8357 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0007 | 35.6 | 0 | 89.0007 | 173.3219 | 13.6% | 0 | 0 | 0 | 0% | 35.6
1136 | 11 | 42 | 40 | 5.2387 | 6.3 | 5.5365 | 0 | 2.6449 | 0 | 3.0983 | 0 | 0 | 3.0983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.3219 | 13.6% | 0 | 0 | 0 | 0% | 3.0983
1137 | 57 | 153 | 136 | 5.8431 | 8.6 | 28.6891 | 0 | 16.4113 | 0 | 15.6995 | 0 | 0 | 15.6995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.3219 | 13.6% | 0 | 0 | 0 | 0% | 15.6995
1138 | 72 | 222 | 183 | 7.2535 | 10.5 | 36.2389 | 0 | 22.4102 | 0 | 21.6875 | 0 | 0 | 21.6875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.3219 | 13.6% | 0 | 0 | 0 | 0% | 21.6875
1139 | 431 | 469 | 217 | 11.2833 | 12 | 216.9298 | 138.6898 | 0 | 106.7327 | 82.0052 | 0 | 21.6526 | 60.3526 | 0 | 0 | 0 | 0 | 0 | 106.7327 | 0 | 273.9681 | 21.5% | 16.6075 | 0 | 16.7174 | 33.43% | 38.7
1140 | 666 | 663 | 225 | 13.4996 | 13.2 | 335.2094 | 216.3827 | 0 | 178.067 | 111.7 | 11.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 178.067 | 0 | 441.8809 | 34.67% | 19.175 | 0 | 36.0194 | 72.04% | 38.3
1141 | 708 | 677 | 198 | 13.0966 | 14 | 356.3487 | 227.0463 | 0 | 188.325 | 113.4 | 20.2922 | 18.1078 | 75 | 0 | 0 | 0 | 0 | 0 | 188.325 | 0 | 619.4668 | 48.6% | 13.8887 | 0 | 50 | 100% | 36.6
1142 | 680 | 624 | 188 | 13.2981 | 14.5 | 342.2558 | 209.5149 | 0 | 171.8648 | 114.4 | 39.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 171.8648 | 0 | 781.531 | 61.32% | 0 | 0 | 50 | 100% | 35.6
1143 | 792 | 560 | 120 | 12.0892 | 15 | 398.6274 | 223.5588 | 0 | 185.7006 | 114.6 | 39.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 185.7006 | 0 | 956.642 | 75.06% | 0 | 0 | 50 | 100% | 35.4
1144 | 697 | 400 | 103 | 12.4922 | 14.6 | 350.8122 | 161.2584 | 0 | 127.1587 | 80.4766 | 21.8383 | 0 | 58.6383 | 0 | 0 | 0 | 0 | 0 | 127.1587 | 0 | 1076.5496 | 84.47% | 0 | 0 | 50 | 100% | 36.8
1145 | 444 | 201 | 82 | 11.8877 | 13.6 | 223.4729 | 0 | 0 | 0 | 29.5196 | 0 | 0 | 29.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1076.5496 | 84.47% | 0 | 11.7804 | 38.1435 | 76.29% | 41.3
1146 | 67 | 35 | 26 | 10.0743 | 11.6 | 33.7223 | 0 | 0 | 0 | 2.7433 | 0 | 0 | 2.7433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1076.5496 | 84.47% | 0 | 25 | 12.9812 | 25.96% | 27.7433
1147 | 0 | 0 | 0 | 6.8506 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3788 | 30.7018 | 0 | 77.3788 | 1004.0143 | 78.78% | 0 | 12.8982 | 2.7756e-15 | 5.551e-15% | 43.6
1148 | 0 | 0 | 0 | 4.8357 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2163 | 41.9 | 0 | 104.2163 | 899.6824 | 70.59% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.9
1149 | 0 | 0 | 0 | 5.4401 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2644 | 38.6 | 0 | 96.2644 | 804.7311 | 63.14% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38.6
1150 | 0 | 0 | 0 | 5.2387 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5994 | 35.4 | 0 | 88.5994 | 718.8194 | 56.4% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.4
1151 | 0 | 0 | 0 | 5.2387 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0522 | 33.1 | 0 | 83.0522 | 639.4802 | 50.17% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.1
1152 | 0 | 0 | 0 | 5.4401 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6792 | 31.7 | 0 | 79.6792 | 564.0974 | 44.26% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.7
1153 | 0 | 0 | 0 | 4.8357 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4562 | 31.2 | 0 | 78.4562 | 490.1037 | 38.45% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.2
1154 | 0 | 0 | 0 | 5.2387 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4679 | 31.2 | 0 | 78.4679 | 416.0948 | 32.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.2
1155 | 0 | 0 | 0 | 5.0372 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3389 | 32.4 | 0 | 81.3389 | 338.6856 | 26.57% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.4
1156 | 0 | 0 | 0 | 4.4327 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8926 | 36.8 | 0 | 91.8926 | 248.7136 | 19.51% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.8
1157 | 0 | 0 | 0 | 4.4327 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9025 | 35.5593 | 0 | 88.9025 | 162.1965 | 12.73% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.5593
1158 | 0 | 0 | 0 | 5.2387 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.1965 | 12.73% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1159 | 0 | 1 | 1 | 5.8431 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.1965 | 12.73% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1160 | 50 | 63 | 54 | 4.8357 | 5.4 | 25.1659 | 0 | 12.068 | 0 | 6.0131 | 0 | 0 | 6.0131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.1965 | 12.73% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 6.0131
1161 | 288 | 238 | 149 | 6.4476 | 8.8 | 144.9554 | 83.058 | 0 | 57.5045 | 30.6359 | 0 | 0 | 30.6359 | 0 | 0 | 0 | 0 | 0 | 57.5045 | 0 | 216.4925 | 16.99% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.6359
1162 | 290 | 369 | 234 | 11.0818 | 11.3 | 145.962 | 90.4353 | 0 | 61.8978 | 45.0378 | 0 | 0 | 45.0378 | 0 | 0 | 0 | 0 | 0 | 61.8978 | 0 | 274.9367 | 21.57% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 45.0378
1163 | 359 | 484 | 271 | 12.8952 | 12.7 | 180.6909 | 115.6296 | 0 | 84.38 | 68.3468 | 0 | 9.8734 | 58.4734 | 0 | 0 | 0 | 0 | 0 | 84.38 | 0 | 354.6086 | 27.82% | 7.5729 | 0 | 7.6241 | 15.25% | 48.6
1164 | 483 | 634 | 309 | 13.7011 | 13.7 | 243.1023 | 157.0958 | 0 | 122.5152 | 103 | 3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 122.5152 | 0 | 470.288 | 36.9% | 19.175 | 0 | 26.9288 | 53.86% | 47
1165 | 512 | 680 | 325 | 13.4996 | 14.6 | 257.6985 | 164.3497 | 0 | 129.435 | 103.9 | 3.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 129.435 | 0 | 592.5011 | 46.49% | 19.175 | 0 | 46.2335 | 92.47% | 46.1
1166 | 208 | 471 | 328 | 13.9026 | 14.6 | 104.69 | 64.2144 | 0 | 35.4004 | 57.213 | 0.97876 | 4.8777 | 51.3565 | 0 | 0 | 0 | 0 | 0 | 35.4004 | 0 | 625.9264 | 49.11% | 3.7412 | 0 | 50 | 100% | 45.5
1167 | 200 | 438 | 319 | 12.8952 | 14.6 | 100.6635 | 0 | 56.6693 | 0 | 51.256 | 3.078 | 0 | 48.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625.9264 | 49.11% | 0 | 0 | 50 | 100% | 45.1
1168 | 95 | 256 | 208 | 12.0892 | 14 | 47.8152 | 0 | 22.1238 | 0 | 25.7627 | 0 | 0 | 25.7627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625.9264 | 49.11% | 0 | 19.8373 | 30.0317 | 60.06% | 45.6
1169 | 18 | 119 | 113 | 11.4848 | 12.5 | 9.0597 | 0 | 0 | 0 | 10.3329 | 0 | 0 | 10.3329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625.9264 | 49.11% | 0 | 25 | 4.8655 | 9.731% | 35.3329
1170 | 2 | 28 | 27 | 10.0743 | 11.2 | 1.0066 | 0 | 0 | 0 | 1.3863 | 0 | 0 | 1.3863 | 0 | 0 | 0 | 108.8911 | 43.7792 | 0 | 108.8911 | 516.1155 | 40.5% | 0 | 4.8345 | 6.9389e-16 | 1.388e-15% | 50
1171 | 0 | 0 | 0 | 7.455 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.6625 | 49.1 | 0 | 121.6625 | 390.8927 | 30.67% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 49.1
1172 | 0 | 0 | 0 | 5.6416 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.932 | 45.1 | 0 | 111.932 | 277.2183 | 21.75% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 45.1
1173 | 0 | 0 | 0 | 7.052 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2806 | 40.7 | 0 | 101.2806 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 40.7
1174 | 0 | 0 | 0 | 6.6491 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1175 | 0 | 0 | 0 | 4.6342 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1176 | 0 | 0 | 0 | 5.2387 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1177 | 0 | 0 | 0 | 4.2312 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1178 | 0 | 0 | 0 | 4.2312 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1179 | 0 | 0 | 0 | 3.2238 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1180 | 0 | 0 | 0 | 3.6268 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1181 | 0 | 0 | 0 | 2.6193 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1182 | 0 | 0 | 0 | 4.0297 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1183 | 0 | 0 | 0 | 4.8357 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1184 | 47 | 57 | 49 | 4.2312 | 6.6 | 23.6559 | 0 | 11.3868 | 0 | 5.2157 | 0 | 0 | 5.2157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 5.2157
1185 | 191 | 227 | 162 | 3.8283 | 9.1 | 96.1336 | 0 | 55.1747 | 0 | 26.2006 | 0 | 0 | 26.2006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.0955 | 13.82% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 26.2006
1186 | 436 | 401 | 193 | 3.8283 | 12.1 | 219.4464 | 136.2237 | 0 | 108.7234 | 51.1903 | 1.2952 | 0 | 49.8952 | 0 | 0 | 0 | 0 | 0 | 108.7234 | 0 | 280.3711 | 22% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 48.6
1187 | 576 | 586 | 244 | 7.6565 | 13.2 | 289.9108 | 185.6973 | 0 | 152.9909 | 99.3745 | 0.63723 | 25 | 73.7372 | 0 | 0 | 0 | 0 | 0 | 152.9909 | 0 | 427.1032 | 33.51% | 19.175 | 0 | 19.3074 | 38.61% | 48.1
1188 | 593 | 646 | 248 | 9.4699 | 14.1 | 298.4672 | 193.0837 | 0 | 158.7847 | 103.5 | 3.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 158.7847 | 0 | 579.392 | 45.46% | 19.175 | 0 | 38.6148 | 77.23% | 46.5
1189 | 524 | 635 | 271 | 9.2684 | 14.6 | 263.7383 | 168.3656 | 0 | 135.8207 | 104.4 | 14.658 | 14.742 | 75 | 0 | 0 | 0 | 0 | 0 | 135.8207 | 0 | 709.6563 | 55.68% | 11.3071 | 0 | 50 | 100% | 45.6
1190 | 494 | 605 | 277 | 8.261 | 15.1 | 248.6388 | 152.8165 | 0 | 121.9392 | 102.1422 | 28.6711 | 0 | 73.4711 | 0 | 0 | 0 | 0 | 0 | 121.9392 | 0 | 826.6071 | 64.86% | 0 | 0 | 50 | 100% | 44.8
1191 | 569 | 563 | 239 | 7.6565 | 15.3 | 286.3876 | 161.8456 | 0 | 130.6929 | 96.7788 | 26.0894 | 0 | 70.6894 | 0 | 0 | 0 | 0 | 0 | 130.6929 | 0 | 951.9534 | 74.69% | 0 | 0 | 50 | 100% | 44.6
1192 | 441 | 383 | 189 | 8.6639 | 14.9 | 221.963 | 103.3825 | 0 | 75.2467 | 51.936 | 3.468 | 0 | 48.468 | 0 | 0 | 0 | 0 | 0 | 75.2467 | 0 | 1024.1219 | 80.35% | 0 | 0 | 50 | 100% | 45
1193 | 248 | 195 | 123 | 10.4773 | 13.4 | 124.8227 | 0 | 0 | 0 | 24.0455 | 0 | 0 | 24.0455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.1219 | 80.35% | 0 | 24.8545 | 24.9777 | 49.96% | 48.9
1194 | 15 | 42 | 39 | 9.6714 | 11 | 7.5498 | 0 | 0 | 0 | 3.0324 | 0 | 0 | 3.0324 | 0 | 0 | 0 | 58.0934 | 22.1573 | 0 | 58.0934 | 971.13 | 76.2% | 0 | 24.8103 | 0 | 0% | 50
1195 | 0 | 0 | 0 | 7.2535 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.6141 | 49.1 | 0 | 121.6141 | 845.959 | 66.38% | 0 | 0 | 0 | 0% | 49.1
1196 | 0 | 0 | 0 | 6.2461 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1736 | 45.2 | 0 | 112.1736 | 732.0396 | 57.44% | 0 | 0 | 0 | 0% | 45.2
1197 | 0 | 0 | 0 | 2.6193 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2891 | 40.7 | 0 | 101.2891 | 630.9682 | 49.51% | 0 | 0 | 0 | 0% | 40.7
1198 | 0 | 0 | 0 | 4.2312 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0704 | 38.1 | 0 | 95.0704 | 537.3244 | 42.16% | 0 | 0 | 0 | 0% | 38.1
1199 | 0 | 0 | 0 | 3.8283 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7908 | 35.5 | 0 | 88.7908 | 451.0066 | 35.39% | 0 | 0 | 0 | 0% | 35.5
1200 | 0 | 0 | 0 | 3.8283 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9455 | 33.9 | 0 | 84.9455 | 369.2536 | 28.97% | 0 | 0 | 0 | 0% | 33.9
1201 | 0 | 0 | 0 | 3.4253 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4975 | 33.3 | 0 | 83.4975 | 289.2091 | 22.69% | 0 | 0 | 0 | 0% | 33.3
1202 | 0 | 0 | 0 | 3.8283 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0161 | 33.1 | 0 | 83.0161 | 209.7141 | 16.45% | 0 | 0 | 0 | 0% | 33.1
1203 | 0 | 0 | 0 | 3.0223 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7141 | 16.45% | 0 | 0 | 0 | 0% | 0
1204 | 0 | 0 | 0 | 4.0297 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7141 | 16.45% | 0 | 0 | 0 | 0% | 0
1205 | 0 | 0 | 0 | 4.0297 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7141 | 16.45% | 0 | 0 | 0 | 0% | 0
1206 | 0 | 0 | 0 | 4.4327 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7141 | 16.45% | 0 | 0 | 0 | 0% | 0
1207 | 0 | 0 | 0 | 3.6268 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7141 | 16.45% | 0 | 0 | 0 | 0% | 0
1208 | 54 | 55 | 46 | 4.6342 | 4.6 | 27.1791 | 0 | 13.1318 | 0 | 5.4257 | 0 | 0 | 5.4257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7141 | 16.45% | 0 | 0 | 0 | 0% | 5.4257
1209 | 304 | 225 | 129 | 2.4178 | 7.7 | 153.0085 | 87.9617 | 0 | 64.3637 | 29.0275 | 0 | 0 | 29.0275 | 0 | 0 | 0 | 0 | 0 | 64.3637 | 0 | 271.4416 | 21.3% | 0 | 0 | 0 | 0% | 29.0275
1210 | 493 | 416 | 184 | 4.2312 | 10.6 | 248.1355 | 154.3259 | 0 | 125.5487 | 60.4863 | 0 | 6.2432 | 54.2432 | 0 | 0 | 0 | 0 | 0 | 125.5487 | 0 | 391.8482 | 30.74% | 4.7885 | 0 | 4.8222 | 9.644% | 48
1211 | 608 | 572 | 211 | 8.4625 | 12 | 306.017 | 196.1989 | 0 | 162.2857 | 100.0016 | 1.2008 | 25 | 73.8008 | 0 | 0 | 0 | 0 | 0 | 162.2857 | 0 | 547.487 | 42.96% | 19.175 | 0 | 24.1324 | 48.26% | 47.6
1212 | 654 | 662 | 224 | 7.2535 | 13 | 329.1696 | 213.1799 | 0 | 178.9511 | 104.1 | 4.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 178.9511 | 0 | 719.1086 | 56.42% | 19.175 | 0 | 43.4425 | 86.89% | 45.9
1213 | 679 | 692 | 224 | 4.8357 | 14.1 | 341.7525 | 218.3837 | 0 | 185.2704 | 104.7 | 21.2103 | 8.4897 | 75 | 0 | 0 | 0 | 0 | 0 | 185.2704 | 0 | 896.7908 | 70.36% | 6.5116 | 0 | 50 | 100% | 45.3
1214 | 664 | 652 | 216 | 3.6268 | 14.9 | 334.2027 | 205.8244 | 0 | 174.0554 | 105.6 | 30.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 174.0554 | 0 | 1063.7173 | 83.46% | 0 | 0 | 50 | 100% | 44.4
1215 | 575 | 528 | 197 | 5.4401 | 15.4 | 289.4075 | 163.9665 | 0 | 134.0403 | 89.6416 | 22.8708 | 0 | 66.7708 | 0 | 0 | 0 | 0 | 0 | 134.0403 | 0 | 1192.2675 | 93.55% | 0 | 0 | 50 | 100% | 43.9
1216 | 59 | 180 | 150 | 7.455 | 14.4 | 29.6957 | 0 | 13.9051 | 0 | 16.8353 | 0 | 0 | 16.8353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1192.2675 | 93.55% | 0 | 25 | 24.8277 | 49.66% | 41.8353
1217 | 1 | 85 | 84 | 9.2684 | 13 | 0.50332 | 0 | 0 | 0 | 6.499 | 0 | 0 | 6.499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1192.2675 | 93.55% | 0 | 24.6578 | 0 | 0% | 31.1568
1218 | 3 | 29 | 29 | 8.261 | 11.4 | 1.51 | 0 | 0 | 0 | 1.6316 | 0 | 0 | 1.6316 | 0 | 0 | 0 | 119.9781 | 48.3684 | 0 | 119.9781 | 1069.3008 | 83.9% | 0 | 0 | 0 | 0% | 50
1219 | 0 | 0 | 0 | 7.6565 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.4008 | 49 | 0 | 121.4008 | 944.4841 | 74.11% | 0 | 0 | 0 | 0% | 49
1220 | 0 | 0 | 0 | 5.8431 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.6228 | 45.8 | 0 | 113.6228 | 828.9182 | 65.04% | 0 | 0 | 0 | 0% | 45.8
1221 | 0 | 0 | 0 | 6.2461 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4913 | 41.6 | 0 | 103.4913 | 725.3639 | 56.91% | 0 | 0 | 0 | 0% | 41.6
1222 | 0 | 0 | 0 | 4.0297 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1958 | 39 | 0 | 97.1958 | 629.1972 | 49.37% | 0 | 0 | 0 | 0% | 39
1223 | 0 | 0 | 0 | 4.8357 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4921 | 36.6 | 0 | 91.4921 | 539.8431 | 42.36% | 0 | 0 | 0 | 0% | 36.6
1224 | 0 | 0 | 0 | 4.4327 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3715 | 35.3 | 0 | 88.3715 | 454.1081 | 35.63% | 0 | 0 | 0 | 0% | 35.3
1225 | 0 | 0 | 0 | 3.4253 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6295 | 34.6 | 0 | 86.6295 | 370.3661 | 29.06% | 0 | 0 | 0 | 0% | 34.6
1226 | 0 | 0 | 0 | 4.2312 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3625 | 34.5 | 0 | 86.3625 | 286.8858 | 22.51% | 0 | 0 | 0 | 0% | 34.5
1227 | 0 | 0 | 0 | 1.8134 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2767 | 35.3 | 0 | 88.2767 | 201.0833 | 15.78% | 0 | 0 | 0 | 0% | 35.3
1228 | 0 | 0 | 0 | 4.6342 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.0833 | 15.78% | 0 | 0 | 0 | 0% | 0
1229 | 0 | 0 | 0 | 6.6491 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.0833 | 15.78% | 0 | 0 | 0 | 0% | 0
1230 | 0 | 0 | 0 | 4.8357 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.0833 | 15.78% | 0 | 0 | 0 | 0% | 0
1231 | 0 | 1 | 1 | 2.4178 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.0833 | 15.78% | 0 | 0 | 0 | 0% | 0
1232 | 95 | 67 | 51 | 6.0446 | 5.9 | 47.8152 | 0 | 23.188 | 0 | 6.9606 | 0 | 0 | 6.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.0833 | 15.78% | 0 | 0 | 0 | 0% | 6.9606
1233 | 375 | 246 | 128 | 5.2387 | 8.4 | 188.744 | 108.6829 | 0 | 82.2695 | 32.7301 | 0 | 0 | 32.7301 | 0 | 0 | 0 | 0 | 0 | 82.2695 | 0 | 280.6479 | 22.02% | 0 | 0 | 0 | 0% | 32.7301
1234 | 572 | 439 | 169 | 8.6639 | 10.8 | 287.8975 | 179.396 | 0 | 146.484 | 70.3388 | 0 | 11.3194 | 59.0194 | 0 | 0 | 0 | 0 | 0 | 146.484 | 0 | 422.3156 | 33.14% | 8.682 | 0 | 8.7444 | 17.49% | 47.7
1235 | 670 | 590 | 191 | 9.2684 | 12.2 | 337.2226 | 216.4106 | 0 | 180.6893 | 102.7 | 2.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 180.6893 | 0 | 597.0639 | 46.85% | 19.175 | 0 | 28.0573 | 56.11% | 47.3
1236 | 712 | 680 | 202 | 9.8729 | 13.2 | 358.362 | 232.3431 | 0 | 195.2932 | 104.4 | 4.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 195.2932 | 0 | 785.9359 | 61.67% | 19.175 | 0 | 47.3702 | 94.74% | 45.6
1237 | 732 | 709 | 202 | 9.0669 | 14 | 368.4283 | 235.6647 | 0 | 198.9119 | 105.3 | 26.8957 | 3.4043 | 75 | 0 | 0 | 0 | 0 | 0 | 198.9119 | 0 | 978.3077 | 76.76% | 2.6111 | 0 | 50 | 100% | 44.7
1238 | 713 | 668 | 198 | 6.6491 | 14.8 | 358.8653 | 221.4697 | 0 | 187.0891 | 105.9 | 30.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 187.0891 | 0 | 1159.2454 | 90.96% | 0 | 0 | 50 | 100% | 44.1
1239 | 680 | 566 | 176 | 6.0446 | 15.4 | 342.2558 | 194.2741 | 0 | 162.0357 | 103.0332 | 29.6666 | 0 | 73.3666 | 0 | 0 | 0 | 0 | 0 | 162.0357 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.7
1240 | 584 | 409 | 150 | 7.6565 | 15.3 | 293.9374 | 0 | 138.2358 | 0 | 65.3481 | 10.674 | 0 | 54.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44
1241 | 394 | 218 | 106 | 9.6714 | 14.1 | 198.3071 | 0 | 0 | 0 | 29.4294 | 0 | 0 | 29.4294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 18.5706 | 31.2988 | 62.6% | 48
1242 | 84 | 46 | 35 | 9.6714 | 11.9 | 42.2787 | 0 | 0 | 0 | 4.2143 | 0 | 0 | 4.2143 | 0 | 0 | 0 | 53.8249 | 20.2857 | 0 | 53.8249 | 1225.6442 | 96.17% | 0 | 25 | 6.1219 | 12.24% | 49.5
1243 | 0 | 0 | 0 | 8.0595 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.499 | 42.4201 | 0 | 105.499 | 1119.8314 | 87.86% | 0 | 6.0799 | 0 | 0% | 48.5
1244 | 0 | 0 | 0 | 5.6416 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.6903 | 45 | 0 | 111.6903 | 1006.5939 | 78.98% | 0 | 0 | 0 | 0% | 45
1245 | 0 | 0 | 0 | 4.6342 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5039 | 40.8 | 0 | 101.5039 | 905.3417 | 71.03% | 0 | 0 | 0 | 0% | 40.8
1246 | 0 | 0 | 0 | 3.6268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0178 | 38.1 | 0 | 95.0178 | 811.7844 | 63.69% | 0 | 0 | 0 | 0% | 38.1
1247 | 0 | 0 | 0 | 4.6342 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0007 | 35.6 | 0 | 89.0007 | 725.2672 | 56.91% | 0 | 0 | 0 | 0% | 35.6
1248 | 0 | 0 | 0 | 4.2312 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1795 | 34 | 0 | 85.1795 | 643.3154 | 50.48% | 0 | 0 | 0 | 0% | 34
1249 | 0 | 0 | 0 | 2.6193 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7339 | 33.4 | 0 | 83.7339 | 563.0782 | 44.18% | 0 | 0 | 0 | 0% | 33.4
1250 | 0 | 0 | 0 | 6.4476 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5143 | 33.3 | 0 | 83.5143 | 483.1127 | 37.91% | 0 | 0 | 0 | 0% | 33.3
1251 | 0 | 0 | 0 | 6.2461 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1399 | 34.4 | 0 | 86.1399 | 399.9565 | 31.38% | 0 | 0 | 0 | 0% | 34.4
1252 | 0 | 0 | 0 | 5.8431 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5011 | 38.3 | 0 | 95.5011 | 305.721 | 23.99% | 0 | 0 | 0 | 0% | 38.3
1253 | 0 | 0 | 0 | 6.4476 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.3848 | 44.5 | 0 | 110.3848 | 193.7311 | 15.2% | 0 | 0 | 0 | 0% | 44.5
1254 | 0 | 0 | 0 | 4.4327 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.7311 | 15.2% | 0 | 0 | 0 | 0% | 0
1255 | 0 | 1 | 1 | 5.2387 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.7311 | 15.2% | 0 | 0 | 0 | 0% | 0
1256 | 226 | 82 | 47 | 2.4178 | 6.8 | 113.7497 | 0 | 55.3663 | 0 | 10.4622 | 0 | 0 | 10.4622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.7311 | 15.2% | 0 | 0 | 0 | 0% | 10.4622
1257 | 577 | 278 | 96 | 1.2089 | 9.1 | 290.4141 | 167.4987 | 0 | 138.988 | 40.223 | 0 | 0 | 40.223 | 0 | 0 | 0 | 0 | 0 | 138.988 | 0 | 326.8912 | 25.65% | 0 | 0 | 0 | 0% | 40.223
1258 | 778 | 479 | 110 | 1.6119 | 13.4 | 391.5809 | 244.2611 | 0 | 210.6002 | 82.8894 | 0 | 17.8947 | 64.9947 | 0 | 0 | 0 | 0 | 0 | 210.6002 | 0 | 528.6609 | 41.48% | 13.7252 | 0 | 13.8259 | 27.65% | 47.1
1259 | 937 | 647 | 90 | 1.8134 | 16 | 471.6084 | 302.9389 | 0 | 265.4533 | 103.3 | 3.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 265.4533 | 0 | 782.9836 | 61.43% | 19.175 | 0 | 33.1415 | 66.28% | 46.7
1260 | 995 | 744 | 78 | 2.6193 | 17.9 | 500.8008 | 325.056 | 0 | 285.7939 | 105.1 | 8.2802 | 21.8198 | 75 | 0 | 0 | 0 | 0 | 0 | 285.7939 | 0 | 1056.794 | 82.92% | 16.7358 | 0 | 50 | 100% | 44.9
1261 | 996 | 766 | 78 | 5.0372 | 18.7 | 501.3041 | 320.982 | 0 | 281.1189 | 106.3 | 31.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 281.1189 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.7
1262 | 983 | 723 | 77 | 6.8506 | 19.5 | 494.761 | 0 | 305.9741 | 0 | 107 | 32 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43
1263 | 944 | 614 | 73 | 9.0669 | 19.2 | 475.1316 | 0 | 270.2152 | 0 | 107.6 | 32.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
1264 | 863 | 449 | 67 | 8.261 | 18.4 | 434.3629 | 0 | 205.1745 | 0 | 85.7979 | 21.6989 | 0 | 64.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
1265 | 685 | 245 | 54 | 7.858 | 17.6 | 344.7724 | 0 | 0 | 0 | 37.1774 | 0 | 0 | 37.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.7226 | 41.2148 | 82.43% | 45.9
1266 | 225 | 53 | 22 | 6.4476 | 15.4 | 113.2464 | 0 | 0 | 0 | 5.4268 | 0 | 0 | 5.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.0348 | 32.07% | 30.4268
1267 | 0 | 0 | 0 | 3.4253 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2422 | 30.5793 | 0 | 77.2422 | 1202.3101 | 94.34% | 0 | 15.9207 | 0 | 0% | 46.5
1268 | 0 | 0 | 0 | 1.8134 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0936 | 43.5 | 0 | 108.0936 | 1093.4068 | 85.79% | 0 | 0 | 0 | 0% | 43.5
1269 | 0 | 0 | 0 | 1.2089 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.8333 | 40.1 | 0 | 99.8333 | 994.1318 | 78% | 0 | 0 | 0 | 0% | 40.1
1270 | 0 | 0 | 0 | 1.6119 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5647 | 37.9 | 0 | 94.5647 | 901.1637 | 70.71% | 0 | 0 | 0 | 0% | 37.9
1271 | 0 | 0 | 0 | 2.0149 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3093 | 35.3 | 0 | 88.3093 | 815.5041 | 63.99% | 0 | 0 | 0 | 0% | 35.3
1272 | 0 | 0 | 0 | 1.4104 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5389 | 33.3 | 0 | 83.5389 | 735.5829 | 57.71% | 0 | 0 | 0 | 0% | 33.3
1273 | 0 | 0 | 0 | 2.0149 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3764 | 32.4 | 0 | 81.3764 | 658.2104 | 51.64% | 0 | 0 | 0 | 0% | 32.4
1274 | 0 | 0 | 0 | 2.4178 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1781 | 31.9 | 0 | 80.1781 | 582.2398 | 45.68% | 0 | 0 | 0 | 0% | 31.9
1275 | 0 | 0 | 0 | 5.0372 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9634 | 31.8 | 0 | 79.9634 | 506.542 | 39.74% | 0 | 0 | 0 | 0% | 31.8
1276 | 0 | 0 | 0 | 5.4401 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6186 | 32.9 | 0 | 82.6186 | 427.7124 | 33.56% | 0 | 0 | 0 | 0% | 32.9
1277 | 0 | 0 | 0 | 2.6193 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3998 | 34.5 | 0 | 86.3998 | 344.252 | 27.01% | 0 | 0 | 0 | 0% | 34.5
1278 | 0 | 0 | 0 | 3.8283 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1725 | 36.9 | 0 | 92.1725 | 253.9837 | 19.93% | 0 | 0 | 0 | 0% | 36.9
1279 | 1 | 1 | 1 | 2.6193 | 7.1 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9528 | 33.0582 | 0 | 82.9528 | 174.6279 | 13.7% | 0 | 0 | 0 | 0% | 33.0582
1280 | 471 | 97 | 32 | 3.4253 | 9.2 | 237.0625 | 115.8081 | 0 | 89.9247 | 14.8386 | 0 | 0 | 14.8386 | 0 | 0 | 0 | 0 | 0 | 89.9247 | 0 | 259.8167 | 20.39% | 0 | 0 | 0 | 0% | 14.8386
1281 | 805 | 311 | 59 | 2.6193 | 14.8 | 405.1705 | 234.0632 | 0 | 200.8242 | 52.3666 | 0 | 4.9833 | 47.3833 | 0 | 0 | 0 | 0 | 0 | 200.8242 | 0 | 450.0647 | 35.31% | 3.8222 | 0 | 3.8508 | 7.702% | 42.4
1282 | 911 | 505 | 71 | 2.4178 | 18.1 | 458.5221 | 286.2348 | 0 | 249.6224 | 95.5218 | 2.0609 | 25 | 68.4609 | 0 | 0 | 0 | 0 | 0 | 249.6224 | 0 | 686.541 | 53.87% | 19.175 | 0 | 23.1691 | 46.34% | 41.4
1283 | 958 | 654 | 80 | 3.0223 | 20.4 | 482.1781 | 310.0226 | 0 | 271.6358 | 108.9 | 8.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 271.6358 | 0 | 943.8713 | 74.06% | 19.175 | 0 | 42.4874 | 84.97% | 41.1
1284 | 990 | 752 | 85 | 4.4327 | 22.3 | 498.2842 | 323.7868 | 0 | 284.0115 | 109.9 | 25.178 | 9.722 | 75 | 0 | 0 | 0 | 0 | 0 | 284.0115 | 0 | 1212.9256 | 95.17% | 7.4568 | 0 | 50 | 100% | 40.1
1285 | 982 | 776 | 93 | 4.0297 | 23.2 | 494.2577 | 203.598 | 113.1948 | 178.4254 | 111.5 | 36.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 178.4254 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.5
1286 | 910 | 716 | 111 | 7.2535 | 23.7 | 458.0188 | 0 | 283.8498 | 0 | 112.8 | 37.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.2
1287 | 690 | 560 | 156 | 9.2684 | 23.4 | 347.289 | 0 | 197.8932 | 0 | 105.9352 | 34.6176 | 0 | 71.3176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.7
1288 | 546 | 412 | 162 | 9.8729 | 22.5 | 274.8113 | 0 | 130.3856 | 0 | 67.4585 | 15.1793 | 0 | 52.2793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.1
1289 | 221 | 203 | 133 | 9.6714 | 20.4 | 111.2331 | 0 | 0 | 0 | 23.0709 | 0 | 0 | 23.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 17.7291 | 32.1411 | 64.28% | 40.8
1290 | 32 | 50 | 44 | 6.0446 | 17.9 | 16.1062 | 0 | 0 | 0 | 3.8742 | 0 | 0 | 3.8742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 6.9571 | 13.91% | 28.8742
1291 | 0 | 0 | 0 | 2.6193 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1091 | 35.4927 | 0 | 89.1091 | 1188.3695 | 93.24% | 0 | 6.9073 | 0 | 0% | 42.4
1292 | 0 | 0 | 0 | 1.4104 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4761 | 40.7 | 0 | 101.4761 | 1087.4473 | 85.32% | 0 | 0 | 0 | 0% | 40.7
1293 | 0 | 0 | 0 | 2.0149 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2016 | 37.7 | 0 | 94.2016 | 995.0736 | 78.07% | 0 | 0 | 0 | 0% | 37.7
1294 | 0 | 0 | 0 | 3.2238 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9661 | 35.1 | 0 | 87.9661 | 909.9921 | 71.4% | 0 | 0 | 0 | 0% | 35.1
1295 | 0 | 0 | 0 | 2.6193 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7437 | 32.5 | 0 | 81.7437 | 832.3787 | 65.31% | 0 | 0 | 0 | 0% | 32.5
1296 | 0 | 0 | 0 | 1.8134 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3515 | 30.7 | 0 | 77.3515 | 759.8119 | 59.62% | 0 | 0 | 0 | 0% | 30.7
1297 | 0 | 0 | 0 | 2.6193 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2242 | 29.8 | 0 | 75.2242 | 689.6636 | 54.11% | 0 | 0 | 0 | 0% | 29.8
1298 | 0 | 0 | 0 | 3.4253 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3742 | 29.4 | 0 | 74.3742 | 620.4842 | 48.68% | 0 | 0 | 0 | 0% | 29.4
1299 | 0 | 0 | 0 | 4.6342 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.4011 | 29.4 | 0 | 74.4011 | 551.2929 | 43.26% | 0 | 0 | 0 | 0% | 29.4
1300 | 0 | 0 | 0 | 5.0372 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.6985 | 30 | 0 | 75.6985 | 480.617 | 37.71% | 0 | 0 | 0 | 0% | 30
1301 | 0 | 0 | 0 | 7.455 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4446 | 30.7 | 0 | 77.4446 | 407.9859 | 32.01% | 0 | 0 | 0 | 0% | 30.7
1302 | 0 | 0 | 0 | 8.8654 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8158 | 31.7 | 0 | 79.8158 | 332.5374 | 26.09% | 0 | 0 | 0 | 0% | 31.7
1303 | 1 | 2 | 2 | 8.0595 | 9.1 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4085 | 34.9 | 0 | 87.4085 | 247.881 | 19.45% | 0 | 0 | 0 | 0% | 34.9
1304 | 325 | 89 | 40 | 8.6639 | 9.9 | 163.5782 | 80.1987 | 0 | 53.279 | 12.3144 | 0 | 0 | 12.3144 | 0 | 0 | 0 | 64.0156 | 24.7856 | 53.279 | 64.0156 | 239.0906 | 18.76% | 0 | 0 | 0 | 0% | 37.1
1305 | 660 | 288 | 75 | 8.8654 | 13.4 | 332.1895 | 192.2109 | 0 | 158.3235 | 48.3764 | 0 | 5.3382 | 43.0382 | 0 | 0 | 0 | 0 | 0 | 158.3235 | 0 | 387.4527 | 30.4% | 4.0944 | 0 | 4.1256 | 8.251% | 37.7
1306 | 810 | 481 | 90 | 10.2758 | 15.7 | 407.6871 | 254.6928 | 0 | 215.7725 | 97.1679 | 4.934 | 25 | 67.234 | 0 | 0 | 0 | 0 | 0 | 215.7725 | 0 | 589.6492 | 46.26% | 19.175 | 0 | 23.4467 | 46.89% | 37.3
1307 | 905 | 640 | 92 | 14.5071 | 16.6 | 455.5022 | 293.1497 | 0 | 249.3819 | 112.6 | 12.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 249.3819 | 0 | 823.3405 | 64.6% | 19.175 | 0 | 42.7677 | 85.54% | 37.4
1308 | 937 | 739 | 100 | 14.1041 | 17 | 471.6084 | 306.8003 | 0 | 262.2611 | 113.1 | 28.742 | 9.358 | 75 | 0 | 0 | 0 | 0 | 0 | 262.2611 | 0 | 1069.1006 | 83.88% | 7.1776 | 0 | 50 | 100% | 36.9
1309 | 922 | 769 | 120 | 14.1041 | 16.9 | 464.0586 | 297.743 | 0 | 253.8763 | 114.6 | 39.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 253.8763 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.4
1310 | 815 | 681 | 134 | 13.4996 | 16.9 | 410.2037 | 0 | 254.7595 | 0 | 115.7 | 40.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.3
1311 | 864 | 622 | 115 | 13.2981 | 17.4 | 434.8662 | 0 | 248.2855 | 0 | 116.2 | 41.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.8
1312 | 811 | 450 | 83 | 14.1041 | 17 | 408.1904 | 0 | 194.5361 | 0 | 92.0682 | 28.6841 | 0 | 63.3841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.7
1313 | 469 | 208 | 66 | 12.6937 | 15.5 | 236.0559 | 0 | 0 | 0 | 29.1342 | 0 | 0 | 29.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.9658 | 39.9598 | 79.92% | 39.1
1314 | 113 | 45 | 28 | 9.4699 | 13.5 | 56.8749 | 0 | 0 | 0 | 3.9895 | 0 | 0 | 3.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 14.7726 | 29.55% | 28.9895
1315 | 0 | 0 | 0 | 10.4773 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.6118 | 27.2366 | 0 | 69.6118 | 1210.5068 | 94.98% | 0 | 14.6634 | 0 | 0% | 41.9
1316 | 0 | 0 | 0 | 9.0669 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.3924 | 40.3 | 0 | 100.3924 | 1110.709 | 87.15% | 0 | 0 | 0 | 0% | 40.3
1317 | 0 | 0 | 0 | 4.6342 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6786 | 37.1 | 0 | 92.6786 | 1020.0485 | 80.03% | 0 | 0 | 0 | 0% | 37.1
1318 | 0 | 0 | 0 | 3.6268 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7294 | 34.2 | 0 | 85.7294 | 937.5873 | 73.56% | 0 | 0 | 0 | 0% | 34.2
1319 | 0 | 0 | 0 | 2.6193 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6919 | 32.1 | 0 | 80.6919 | 861.1163 | 67.56% | 0 | 0 | 0 | 0% | 32.1
1320 | 0 | 0 | 0 | 3.4253 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.285 | 30.7 | 0 | 77.285 | 788.55 | 61.87% | 0 | 0 | 0 | 0% | 30.7
1321 | 0 | 0 | 0 | 4.4327 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3162 | 30.3 | 0 | 76.3162 | 717.0827 | 56.26% | 0 | 0 | 0 | 0% | 30.3
1322 | 0 | 0 | 0 | 2.4178 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7702 | 30.5 | 0 | 76.7702 | 645.0494 | 50.61% | 0 | 0 | 0 | 0% | 30.5
1323 | 0 | 0 | 0 | 1.6119 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6585 | 31.7 | 0 | 79.6585 | 569.6494 | 44.7% | 0 | 0 | 0 | 0% | 31.7
1324 | 0 | 0 | 0 | 3.0223 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4475 | 36.2 | 0 | 90.4475 | 481.4106 | 37.77% | 0 | 0 | 0 | 0% | 36.2
1325 | 0 | 0 | 0 | 5.4401 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3479 | 42.4 | 0 | 105.3479 | 375.5189 | 29.46% | 0 | 0 | 0 | 0% | 42.4
1326 | 0 | 0 | 0 | 5.6416 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.008 | 46 | 0 | 114.008 | 259.2602 | 20.34% | 0 | 0 | 0 | 0% | 46
1327 | 0 | 1 | 1 | 8.261 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.649 | 47.5 | 0 | 117.649 | 138.6381 | 10.88% | 0 | 0 | 0 | 0% | 47.5
1328 | 309 | 95 | 41 | 5.0372 | 7.4 | 155.5251 | 76.523 | 0 | 51.9629 | 12.1419 | 0 | 0 | 12.1419 | 0 | 0 | 0 | 0 | 0 | 51.9629 | 0 | 188.0825 | 14.76% | 0 | 0 | 0 | 0% | 12.1419
1329 | 696 | 299 | 71 | 6.0446 | 9.3 | 350.3089 | 203.0185 | 0 | 170.1835 | 44.859 | 0 | 0 | 44.859 | 0 | 0 | 0 | 0 | 0 | 170.1835 | 0 | 350.0176 | 27.46% | 0 | 0 | 0 | 0% | 44.859
1330 | 869 | 497 | 75 | 8.0595 | 12.5 | 437.3828 | 273.4495 | 0 | 234.6245 | 93.5348 | 0 | 23.4174 | 70.1174 | 0 | 0 | 0 | 0 | 0 | 234.6245 | 0 | 573.2704 | 44.98% | 17.9611 | 0 | 18.1005 | 36.2% | 46.7
1331 | 949 | 652 | 74 | 8.261 | 15.3 | 477.6482 | 307.695 | 0 | 266.6747 | 103.4 | 3.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 266.6747 | 0 | 827.02 | 64.89% | 19.175 | 0 | 37.4244 | 74.85% | 46.6
1332 | 979 | 746 | 77 | 10.6788 | 17 | 492.7477 | 320.9184 | 0 | 277.5305 | 105 | 13.7305 | 16.2695 | 75 | 0 | 0 | 0 | 0 | 0 | 277.5305 | 0 | 1091.0993 | 85.61% | 12.4787 | 0 | 50 | 100% | 45
1333 | 985 | 772 | 77 | 11.4848 | 17.3 | 495.7676 | 265.7386 | 52.6796 | 229.2566 | 105.9 | 30.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 229.2566 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.1
1334 | 984 | 733 | 72 | 11.2833 | 17.3 | 495.2643 | 0 | 307.995 | 0 | 106.7 | 31.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.3
1335 | 957 | 627 | 67 | 10.2758 | 17.1 | 481.6747 | 0 | 275.5605 | 0 | 107.2 | 32.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.8
1336 | 898 | 466 | 59 | 9.6714 | 16.7 | 451.979 | 0 | 216.379 | 0 | 88.4819 | 22.8909 | 0 | 65.5909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.7
1337 | 771 | 267 | 45 | 9.4699 | 16 | 388.0577 | 0 | 0 | 0 | 40.1087 | 0 | 0 | 40.1087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.1913 | 43.7616 | 87.52% | 46.3
1338 | 318 | 68 | 22 | 8.6639 | 13.7 | 160.0549 | 0 | 0 | 0 | 7.4429 | 0 | 0 | 7.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.571 | 37.14% | 32.4429
1339 | 0 | 0 | 0 | 6.4476 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7289 | 29.0691 | 0 | 73.7289 | 1206.2156 | 94.64% | 0 | 18.4309 | 0 | 0% | 47.5
1340 | 0 | 0 | 0 | 6.0446 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5736 | 43.7 | 0 | 108.5736 | 1096.7786 | 86.05% | 0 | 0 | 0 | 0% | 43.7
1341 | 0 | 0 | 0 | 4.6342 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1408 | 39.4 | 0 | 98.1408 | 999.5551 | 78.43% | 0 | 0 | 0 | 0% | 39.4
1342 | 0 | 0 | 0 | 3.4253 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3793 | 37 | 0 | 92.3793 | 909.1633 | 71.33% | 0 | 0 | 0 | 0% | 37
1343 | 0 | 0 | 0 | 2.2164 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3634 | 34.5 | 0 | 86.3634 | 825.8141 | 64.79% | 0 | 0 | 0 | 0% | 34.5
1344 | 0 | 0 | 0 | 2.2164 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0161 | 33.1 | 0 | 83.0161 | 746.4881 | 58.57% | 0 | 0 | 0 | 0% | 33.1
1345 | 0 | 0 | 0 | 2.6193 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8184 | 32.6 | 0 | 81.8184 | 668.5751 | 52.46% | 0 | 0 | 0 | 0% | 32.6
1346 | 0 | 0 | 0 | 4.6342 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8184 | 32.6 | 0 | 81.8184 | 590.6489 | 46.34% | 0 | 0 | 0 | 0% | 32.6
1347 | 0 | 0 | 0 | 3.4253 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9731 | 33.5 | 0 | 83.9731 | 510.1351 | 40.03% | 0 | 0 | 0 | 0% | 33.5
1348 | 0 | 0 | 0 | 2.8208 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.839 | 37.2 | 0 | 92.839 | 419.0826 | 32.88% | 0 | 0 | 0 | 0% | 37.2
1349 | 0 | 0 | 0 | 1.6119 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.231 | 43.2 | 0 | 107.231 | 310.9089 | 24.39% | 0 | 0 | 0 | 0% | 43.2
1350 | 0 | 0 | 0 | 4.6342 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.9947 | 46 | 0 | 113.9947 | 194.6577 | 15.27% | 0 | 0 | 0 | 0% | 46
1351 | 3 | 2 | 2 | 4.4327 | 6 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3606 | 44.0724 | 0 | 109.3606 | 83.8936 | 6.582% | 0 | 0 | 0 | 0% | 44.0724
1352 | 481 | 103 | 32 | 2.8208 | 8.4 | 242.0957 | 119.5398 | 0 | 93.6254 | 15.3745 | 0 | 0 | 15.3745 | 0 | 0 | 0 | 0 | 0 | 93.6254 | 0 | 173.5504 | 13.62% | 0 | 0 | 0 | 0% | 15.3745
1353 | 786 | 310 | 51 | 2.2164 | 11.8 | 395.6075 | 229.634 | 0 | 196.7742 | 46.1901 | 0 | 0 | 46.1901 | 0 | 0 | 0 | 0 | 0 | 196.7742 | 0 | 361.9838 | 28.4% | 0 | 0 | 0 | 0% | 46.1901
1354 | 912 | 506 | 59 | 5.6416 | 14.5 | 459.0255 | 287.1942 | 0 | 249.1643 | 93.2395 | 0 | 23.4198 | 69.8198 | 0 | 0 | 0 | 0 | 0 | 249.1643 | 0 | 600.5865 | 47.12% | 17.963 | 0 | 18.1049 | 36.21% | 46.4
1355 | 970 | 658 | 63 | 9.4699 | 16.5 | 488.2179 | 314.8036 | 0 | 272.5636 | 103.7 | 3.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 272.5636 | 0 | 861.5967 | 67.6% | 19.175 | 0 | 37.4315 | 74.86% | 46.3
1356 | 992 | 751 | 66 | 8.0595 | 18.1 | 499.2908 | 325.5535 | 0 | 283.5165 | 105.2 | 13.942 | 16.258 | 75 | 0 | 0 | 0 | 0 | 0 | 283.5165 | 0 | 1133.0955 | 88.9% | 12.4699 | 0 | 50 | 100% | 44.8
1357 | 997 | 775 | 67 | 10.8803 | 19.1 | 501.8074 | 206.6735 | 115.9617 | 178.7652 | 106.2 | 31.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 178.7652 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.8
1358 | 984 | 732 | 66 | 12.4922 | 19.3 | 495.2643 | 0 | 308.2766 | 0 | 106.9 | 31.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.1
1359 | 957 | 628 | 62 | 14.1041 | 19.1 | 481.6747 | 0 | 276.1184 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
1360 | 900 | 469 | 56 | 14.3056 | 18.5 | 452.9856 | 0 | 217.8494 | 0 | 88.4625 | 22.9313 | 0 | 65.5313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
1361 | 763 | 269 | 46 | 12.6937 | 17.3 | 384.0312 | 0 | 0 | 0 | 40.0584 | 0 | 0 | 40.0584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.3416 | 43.6093 | 87.22% | 46.4
1362 | 333 | 70 | 21 | 8.6639 | 15.7 | 167.6047 | 0 | 0 | 0 | 7.3482 | 0 | 0 | 7.3482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.4151 | 36.83% | 32.3482
1363 | 0 | 0 | 0 | 4.4327 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7955 | 29.0264 | 0 | 73.7955 | 1206.3289 | 94.65% | 0 | 18.2736 | 0 | 0% | 47.3
1364 | 0 | 0 | 0 | 4.4327 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.1252 | 43.5 | 0 | 108.1252 | 1097.481 | 86.11% | 0 | 0 | 0 | 0% | 43.5
1365 | 0 | 0 | 0 | 2.6193 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2368 | 39.4 | 0 | 98.2368 | 1000.2689 | 78.48% | 0 | 0 | 0 | 0% | 39.4
1366 | 0 | 0 | 0 | 1.2089 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1669 | 36.9 | 0 | 92.1669 | 910.1819 | 71.41% | 0 | 0 | 0 | 0% | 36.9
1367 | 0 | 0 | 0 | 0.80595 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3625 | 34.5 | 0 | 86.3625 | 826.8441 | 64.88% | 0 | 0 | 0 | 0% | 34.5
1368 | 0 | 0 | 0 | 1.4104 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0161 | 33.1 | 0 | 83.0161 | 747.5288 | 58.65% | 0 | 0 | 0 | 0% | 33.1
1369 | 0 | 0 | 0 | 0.80595 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0581 | 32.7 | 0 | 82.0581 | 669.3419 | 52.52% | 0 | 0 | 0 | 0% | 32.7
1370 | 0 | 0 | 0 | 1.0074 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2977 | 32.8 | 0 | 82.2977 | 590.857 | 46.36% | 0 | 0 | 0 | 0% | 32.8
1371 | 0 | 0 | 0 | 1.6119 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4511 | 33.7 | 0 | 84.4511 | 509.7788 | 40% | 0 | 0 | 0 | 0% | 33.7
1372 | 0 | 0 | 0 | 4.4327 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5764 | 37.5 | 0 | 93.5764 | 417.8884 | 32.79% | 0 | 0 | 0 | 0% | 37.5
1373 | 0 | 0 | 0 | 1.8134 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.2649 | 43.2 | 0 | 107.2649 | 309.7301 | 24.3% | 0 | 0 | 0 | 0% | 43.2
1374 | 0 | 0 | 0 | 2.0149 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.9947 | 46 | 0 | 113.9947 | 193.4972 | 15.18% | 0 | 0 | 0 | 0% | 46
1375 | 10 | 2 | 2 | 2.4178 | 5.3 | 5.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.8957 | 43.4614 | 0 | 107.8957 | 84.5079 | 6.631% | 0 | 0 | 0 | 0% | 43.4614
1376 | 567 | 113 | 28 | 0.80595 | 8.2 | 285.381 | 141.406 | 0 | 114.7565 | 17.1103 | 0 | 0 | 17.1103 | 0 | 0 | 0 | 0 | 0 | 114.7565 | 0 | 194.4276 | 15.26% | 0 | 0 | 0 | 0% | 17.1103
1377 | 830 | 321 | 45 | 1.8134 | 13.8 | 417.7534 | 242.8701 | 0 | 209.2405 | 47.4831 | 0.44157 | 0 | 47.0416 | 0 | 0 | 0 | 0 | 0 | 209.2405 | 0 | 394.8488 | 30.98% | 0 | 0 | 0 | 0% | 46.6
1378 | 935 | 515 | 53 | 2.0149 | 16.9 | 470.6018 | 294.6549 | 0 | 257.7047 | 90.7344 | 0 | 22.2672 | 68.4672 | 0 | 0 | 0 | 0 | 0 | 257.7047 | 0 | 641.6916 | 50.35% | 17.0789 | 0 | 17.2164 | 34.43% | 46.2
1379 | 986 | 667 | 58 | 3.4253 | 18 | 496.2709 | 320.3013 | 0 | 281.0591 | 104.2 | 4.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 281.0591 | 0 | 910.9044 | 71.47% | 19.175 | 0 | 36.5457 | 73.09% | 45.8
1380 | 1001 | 756 | 62 | 3.4253 | 19.1 | 503.8207 | 328.8869 | 0 | 289.1052 | 105.7 | 13.2987 | 17.4013 | 75 | 0 | 0 | 0 | 0 | 0 | 289.1052 | 0 | 1187.8242 | 93.2% | 13.3468 | 0 | 50 | 100% | 44.3
1381 | 1001 | 779 | 64 | 4.0297 | 20.1 | 503.8207 | 139.6402 | 184.6319 | 122.5475 | 106.5 | 31.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 122.5475 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.5
1382 | 980 | 734 | 67 | 9.6714 | 19.5 | 493.251 | 0 | 307.3074 | 0 | 107.1 | 32.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.9
1383 | 945 | 627 | 65 | 9.2684 | 19.1 | 475.6349 | 0 | 273.2147 | 0 | 107.6 | 32.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
1384 | 877 | 466 | 60 | 10.0743 | 18.7 | 441.4093 | 0 | 213.2569 | 0 | 85.5026 | 21.5513 | 0 | 63.9513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
1385 | 736 | 267 | 48 | 9.4699 | 17.8 | 370.4416 | 0 | 0 | 0 | 38.7977 | 0 | 0 | 38.7977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.4023 | 42.5393 | 85.08% | 46.2
1386 | 304 | 71 | 23 | 7.052 | 16.1 | 153.0085 | 0 | 0 | 0 | 7.2116 | 0 | 0 | 7.2116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.3415 | 34.68% | 32.2116
1387 | 0 | 0 | 0 | 4.8357 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6047 | 29.3942 | 0 | 74.6047 | 1205.4291 | 94.58% | 0 | 17.2058 | 2.7756e-15 | 5.551e-15% | 46.6
1388 | 0 | 0 | 0 | 1.4104 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3942 | 43.2 | 0 | 107.3942 | 1097.4393 | 86.11% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.2
1389 | 0 | 0 | 0 | 1.8134 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2334 | 39.4 | 0 | 98.2334 | 1000.2264 | 78.48% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.4
1390 | 0 | 0 | 0 | 1.2089 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6671 | 37.1 | 0 | 92.6671 | 909.581 | 71.37% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.1
1391 | 0 | 0 | 0 | 2.2164 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3999 | 34.9 | 0 | 87.3999 | 825.0924 | 64.74% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.9
1392 | 0 | 0 | 0 | 2.0149 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8164 | 33.4 | 0 | 83.8164 | 744.931 | 58.45% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.4
1393 | 0 | 0 | 0 | 1.8134 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8387 | 33 | 0 | 82.8387 | 665.8984 | 52.25% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33
1394 | 0 | 0 | 0 | 2.2164 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5855 | 32.9 | 0 | 82.5855 | 587.1326 | 46.07% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.9
1395 | 0 | 0 | 0 | 1.4104 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4973 | 33.7 | 0 | 84.4973 | 506.0624 | 39.71% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.7
1396 | 0 | 0 | 0 | 1.8134 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9214 | 36.8 | 0 | 91.9214 | 416.1627 | 32.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.8
1397 | 0 | 0 | 0 | 1.0074 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4622 | 41.2 | 0 | 102.4622 | 313.6968 | 24.61% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.2
1398 | 0 | 0 | 0 | 3.0223 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5489 | 43.7 | 0 | 108.5489 | 204.0695 | 16.01% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.7
1399 | 22 | 3 | 3 | 2.4178 | 8 | 11.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4152 | 45.3 | 0 | 112.4152 | 89.7822 | 7.044% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 45.3
1400 | 584 | 120 | 29 | 1.2089 | 9.9 | 293.9374 | 146.1498 | 0 | 119.1525 | 17.6358 | 0 | 0 | 17.6358 | 0 | 0 | 0 | 0 | 0 | 119.1525 | 0 | 203.8383 | 15.99% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 17.6358
1401 | 849 | 334 | 47 | 0.40297 | 16.3 | 427.3165 | 248.8173 | 0 | 215.2704 | 49.3641 | 2.1321 | 0 | 47.2321 | 0 | 0 | 0 | 0 | 0 | 215.2704 | 0 | 409.9012 | 32.16% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 45.1
1402 | 950 | 530 | 55 | 1.2089 | 20.1 | 478.1515 | 299.602 | 0 | 262.5841 | 91.7263 | 0 | 23.5132 | 68.2132 | 0 | 0 | 0 | 0 | 0 | 262.5841 | 0 | 661.2541 | 51.88% | 18.0346 | 0 | 18.1823 | 36.36% | 44.7
1403 | 995 | 681 | 60 | 3.4253 | 22 | 500.8008 | 323.5331 | 0 | 284.1181 | 105.6 | 5.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 284.1181 | 0 | 933.22 | 73.22% | 19.175 | 0 | 37.5144 | 75.03% | 44.4
1404 | 1011 | 772 | 65 | 6.4476 | 22.6 | 508.8539 | 332.5588 | 0 | 291.1614 | 107 | 15.8538 | 16.1462 | 75 | 0 | 0 | 0 | 0 | 0 | 291.1614 | 0 | 1211.928 | 95.09% | 12.3841 | 0 | 50 | 100% | 43
1405 | 1001 | 795 | 74 | 7.455 | 23.2 | 503.8207 | 112.4526 | 212.165 | 98.0757 | 107.8 | 32.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 98.0757 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.2
1406 | 969 | 751 | 86 | 9.2684 | 23.7 | 487.7145 | 0 | 304.142 | 0 | 108.4 | 33.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
1407 | 954 | 644 | 70 | 11.0818 | 23.7 | 480.1648 | 0 | 276.3883 | 0 | 108.9 | 33.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
1408 | 866 | 478 | 71 | 11.6862 | 23.2 | 435.8729 | 0 | 211.5556 | 0 | 86.8622 | 22.8311 | 0 | 64.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
1409 | 627 | 264 | 71 | 8.261 | 22.3 | 315.58 | 0 | 0 | 0 | 35.6877 | 0 | 0 | 35.6877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.2123 | 40.7136 | 81.43% | 44.9
1410 | 263 | 81 | 38 | 6.4476 | 19.8 | 132.3725 | 0 | 0 | 0 | 7.7151 | 0 | 0 | 7.7151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.5122 | 31.02% | 32.7151
1411 | 1 | 0 | 0 | 3.8283 | 14.4 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3088 | 30.5113 | 0 | 77.3088 | 1202.5316 | 94.35% | 0 | 15.3887 | 0 | 0% | 45.9
1412 | 0 | 0 | 0 | 2.2164 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.1282 | 42.6 | 0 | 106.1282 | 1096.2535 | 86.01% | 0 | 0 | 0 | 0% | 42.6
1413 | 0 | 0 | 0 | 1.4104 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8664 | 39.2 | 0 | 97.8664 | 999.6149 | 78.43% | 0 | 0 | 0 | 0% | 39.2
1414 | 0 | 0 | 0 | 1.6119 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3038 | 36.9 | 0 | 92.3038 | 909.5139 | 71.36% | 0 | 0 | 0 | 0% | 36.9
1415 | 0 | 0 | 0 | 2.8208 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5047 | 34.9 | 0 | 87.5047 | 825.0094 | 64.73% | 0 | 0 | 0 | 0% | 34.9
1416 | 0 | 0 | 0 | 2.4178 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9069 | 33.4 | 0 | 83.9069 | 744.8336 | 58.44% | 0 | 0 | 0 | 0% | 33.4
1417 | 0 | 0 | 0 | 2.2164 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4708 | 32.8 | 0 | 82.4708 | 666.3606 | 52.28% | 0 | 0 | 0 | 0% | 32.8
1418 | 0 | 0 | 0 | 2.2164 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4672 | 32.8 | 0 | 82.4672 | 587.8744 | 46.13% | 0 | 0 | 0 | 0% | 32.8
1419 | 0 | 0 | 0 | 2.0149 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5759 | 33.7 | 0 | 84.5759 | 506.795 | 39.76% | 0 | 0 | 0 | 0% | 33.7
1420 | 0 | 0 | 0 | 1.2089 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8856 | 37.2 | 0 | 92.8856 | 415.7648 | 32.62% | 0 | 0 | 0 | 0% | 37.2
1421 | 0 | 0 | 0 | 4.0297 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4885 | 42 | 0 | 104.4885 | 311.03 | 24.4% | 0 | 0 | 0 | 0% | 42
1422 | 0 | 0 | 0 | 3.2238 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.2112 | 44.8 | 0 | 111.2112 | 198.226 | 15.55% | 0 | 0 | 0 | 0% | 44.8
1423 | 20 | 5 | 5 | 1.6119 | 8.3 | 10.0663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.1368 | 44.3557 | 0 | 110.1368 | 86.6594 | 6.799% | 0 | 0 | 0 | 0% | 44.3557
1424 | 397 | 112 | 42 | 1.8134 | 11.2 | 199.817 | 99.6918 | 0 | 75.2106 | 14.3974 | 0 | 0 | 14.3974 | 0 | 0 | 0 | 0 | 0 | 75.2106 | 0 | 158.6699 | 12.45% | 0 | 0 | 0 | 0% | 14.3974
1425 | 756 | 329 | 68 | 1.6119 | 16 | 380.5079 | 221.9046 | 0 | 189.7549 | 45.7125 | 0 | 0 | 45.7125 | 0 | 0 | 0 | 0 | 0 | 189.7549 | 0 | 340.3511 | 26.7% | 0 | 0 | 0 | 0% | 45.7125
1426 | 773 | 520 | 127 | 1.6119 | 19.7 | 389.0643 | 243.9591 | 0 | 210.3428 | 83.9748 | 0 | 18.9874 | 64.9874 | 0 | 0 | 0 | 0 | 0 | 210.3428 | 0 | 541.7442 | 42.51% | 14.5634 | 0 | 14.6847 | 29.37% | 46
1427 | 494 | 561 | 248 | 3.0223 | 20.8 | 248.6388 | 160.7816 | 0 | 132.0883 | 83.3326 | 0 | 18.9663 | 64.3663 | 0 | 0 | 0 | 0 | 0 | 132.0883 | 0 | 668.2123 | 52.43% | 14.5472 | 0 | 29.3531 | 58.71% | 45.4
1428 | 626 | 675 | 229 | 5.6416 | 20.9 | 315.0767 | 206.1387 | 0 | 173.5493 | 106 | 6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 173.5493 | 0 | 834.3774 | 65.47% | 19.175 | 0 | 48.688 | 97.38% | 44
1429 | 730 | 766 | 231 | 6.8506 | 21.7 | 367.4217 | 236.9883 | 0 | 201.6386 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 201.6386 | 0 | 1027.4366 | 80.61% | 0 | 0 | 48.688 | 97.38% | 42.6
1430 | 523 | 671 | 300 | 7.858 | 22.2 | 263.235 | 164.31 | 0 | 133.0229 | 108.1 | 33.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 133.0229 | 0 | 1154.7996 | 90.61% | 0 | 0 | 48.688 | 97.38% | 41.9
1431 | 427 | 578 | 313 | 9.2684 | 22 | 214.9165 | 123.9674 | 0 | 94.4951 | 86.5546 | 22.4773 | 0 | 64.0773 | 0 | 0 | 0 | 0 | 0 | 94.4951 | 0 | 1245.2742 | 97.71% | 0 | 0 | 48.688 | 97.38% | 41.6
1432 | 257 | 368 | 236 | 8.4625 | 20.8 | 129.3526 | 0 | 63.0747 | 0 | 38.7488 | 0 | 0 | 38.7488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1245.2742 | 97.71% | 0 | 2.7512 | 45.9143 | 91.83% | 41.5
1433 | 18 | 143 | 137 | 7.2535 | 17.9 | 9.0597 | 0 | 0 | 0 | 12.0227 | 0 | 0 | 12.0227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1245.2742 | 97.71% | 0 | 25 | 20.7096 | 41.42% | 37.0227
1434 | 27 | 47 | 42 | 5.0372 | 15.8 | 13.5896 | 0 | 0 | 0 | 3.4872 | 0 | 0 | 3.4872 | 0 | 0 | 0 | 58.8549 | 22.2712 | 0 | 58.8549 | 1191.6544 | 93.5% | 0 | 20.5415 | 0 | 0% | 46.3
1435 | 0 | 0 | 0 | 2.8208 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7341 | 45.3 | 0 | 112.7341 | 1077.6491 | 84.55% | 0 | 0 | 0 | 0% | 45.3
1436 | 0 | 0 | 0 | 0.60446 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6568 | 42.4 | 0 | 105.6568 | 971.9476 | 76.26% | 0 | 0 | 0 | 0% | 42.4
1437 | 0 | 0 | 0 | 0.60446 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9681 | 39.2 | 0 | 97.9681 | 875.3147 | 68.68% | 0 | 0 | 0 | 0% | 39.2
1438 | 0 | 0 | 0 | 3.0223 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7099 | 37 | 0 | 92.7099 | 784.9359 | 61.59% | 0 | 0 | 0 | 0% | 37
1439 | 0 | 0 | 0 | 2.2164 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9647 | 34.6 | 0 | 86.9647 | 701.3089 | 55.03% | 0 | 0 | 0 | 0% | 34.6
1440 | 0 | 0 | 0 | 2.4178 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3754 | 33.1 | 0 | 83.3754 | 621.994 | 48.8% | 0 | 0 | 0 | 0% | 33.1
1441 | 0 | 0 | 0 | 4.0297 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0247 | 32.1 | 0 | 81.0247 | 545.5078 | 42.8% | 0 | 0 | 0 | 0% | 32.1
1442 | 0 | 0 | 0 | 4.0297 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0737 | 31.7 | 0 | 80.0737 | 470.1352 | 36.89% | 0 | 0 | 0 | 0% | 31.7
1443 | 0 | 0 | 0 | 4.6342 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0182 | 31.7 | 0 | 80.0182 | 394.7469 | 30.97% | 0 | 0 | 0 | 0% | 31.7
1444 | 0 | 0 | 0 | 4.2312 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8689 | 32.5 | 0 | 81.8689 | 317.0782 | 24.88% | 0 | 0 | 0 | 0% | 32.5
1445 | 0 | 0 | 0 | 4.4327 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1314 | 33.9 | 0 | 85.1314 | 235.3757 | 18.47% | 0 | 0 | 0 | 0% | 33.9
1446 | 0 | 0 | 0 | 2.0149 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3019 | 36.1 | 0 | 90.3019 | 147.37 | 11.56% | 0 | 0 | 0 | 0% | 36.1
1447 | 0 | 2 | 2 | 4.0297 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.37 | 11.56% | 0 | 0 | 0 | 0% | 0
1448 | 394 | 112 | 41 | 2.8208 | 11.1 | 198.3071 | 99.2731 | 0 | 74.4454 | 14.3221 | 0 | 0 | 14.3221 | 0 | 0 | 0 | 0 | 0 | 74.4454 | 0 | 218.0201 | 17.11% | 0 | 0 | 0 | 0% | 14.3221
1449 | 703 | 319 | 73 | 2.0149 | 16 | 353.8321 | 206.6644 | 0 | 175.4225 | 46.5693 | 0 | 2.6346 | 43.9346 | 0 | 0 | 0 | 0 | 0 | 175.4225 | 0 | 384.4994 | 30.17% | 2.0208 | 0 | 2.0379 | 4.076% | 41.3
1450 | 785 | 502 | 99 | 1.4104 | 18.8 | 395.1041 | 247.9255 | 0 | 214.0846 | 85.5008 | 0 | 22.3504 | 63.1504 | 0 | 0 | 0 | 0 | 0 | 214.0846 | 0 | 587.6698 | 46.11% | 17.1428 | 0 | 19.3259 | 38.65% | 40.8
1451 | 846 | 655 | 117 | 4.8357 | 20.7 | 425.8065 | 275.609 | 0 | 238.7603 | 109.5 | 9.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 238.7603 | 0 | 814.2578 | 63.89% | 19.175 | 0 | 38.6635 | 77.33% | 40.5
1452 | 709 | 697 | 189 | 10.2758 | 20.7 | 356.852 | 233.5324 | 0 | 196.3646 | 110.8 | 21.1439 | 14.6561 | 75 | 0 | 0 | 0 | 0 | 0 | 196.3646 | 0 | 1000.6115 | 78.51% | 11.2412 | 0 | 50 | 100% | 39.2
1453 | 682 | 722 | 217 | 10.2758 | 21 | 343.2625 | 221.6449 | 0 | 185.1804 | 112.4 | 37.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 185.1804 | 0 | 1176.3512 | 92.3% | 0 | 0 | 50 | 100% | 37.6
1454 | 304 | 532 | 307 | 7.6565 | 20.8 | 153.0085 | 95.5981 | 0 | 68.8171 | 77.3577 | 20.4788 | 0 | 56.8788 | 0 | 0 | 0 | 0 | 0 | 68.8171 | 0 | 1241.6599 | 97.42% | 0 | 0 | 50 | 100% | 36.4
1455 | 322 | 491 | 289 | 6.6491 | 20.8 | 162.0682 | 0 | 93.6814 | 0 | 71.2252 | 17.7626 | 0 | 53.4626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241.6599 | 97.42% | 0 | 0 | 50 | 100% | 35.7
1456 | 298 | 373 | 227 | 9.4699 | 19.1 | 149.9886 | 0 | 73.4792 | 0 | 47.6289 | 5.9144 | 0 | 41.7144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241.6599 | 97.42% | 0 | 0 | 50 | 100% | 35.8
1457 | 326 | 225 | 117 | 7.2535 | 18.3 | 164.0815 | 0 | 0 | 0 | 25.8439 | 0 | 0 | 25.8439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241.6599 | 97.42% | 0 | 13.3561 | 36.5327 | 73.07% | 39.2
1458 | 58 | 56 | 46 | 7.052 | 16.6 | 29.1924 | 0 | 0 | 0 | 4.6582 | 0 | 0 | 4.6582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241.6599 | 97.42% | 0 | 25 | 11.3239 | 22.65% | 29.6582
1459 | 0 | 0 | 0 | 4.4327 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4453 | 29.6691 | 0 | 75.4453 | 1171.8903 | 91.95% | 0 | 11.2309 | 0 | 0% | 40.9
1460 | 0 | 0 | 0 | 0.20149 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9777 | 39.2 | 0 | 97.9777 | 1075.2432 | 84.37% | 0 | 0 | 0 | 0% | 39.2
1461 | 0 | 0 | 0 | 1.0074 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6098 | 37 | 0 | 92.6098 | 984.8526 | 77.27% | 0 | 0 | 0 | 0% | 37
1462 | 0 | 0 | 0 | 1.0074 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3105 | 34.4 | 0 | 86.3105 | 901.7974 | 70.76% | 0 | 0 | 0 | 0% | 34.4
1463 | 0 | 0 | 0 | 0.80595 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7225 | 32.1 | 0 | 80.7225 | 825.3177 | 64.76% | 0 | 0 | 0 | 0% | 32.1
1464 | 0 | 0 | 0 | 1.0074 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6123 | 30.4 | 0 | 76.6123 | 753.5843 | 59.13% | 0 | 0 | 0 | 0% | 30.4
1465 | 0 | 0 | 0 | 1.6119 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.7798 | 29.6 | 0 | 74.7798 | 683.9267 | 53.66% | 0 | 0 | 0 | 0% | 29.6
1466 | 0 | 0 | 0 | 2.6193 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9337 | 29.2 | 0 | 73.9337 | 615.2376 | 48.27% | 0 | 0 | 0 | 0% | 29.2
1467 | 0 | 0 | 0 | 1.4104 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8882 | 29.2 | 0 | 73.8882 | 546.5365 | 42.88% | 0 | 0 | 0 | 0% | 29.2
1468 | 0 | 0 | 0 | 1.0074 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2025 | 29.8 | 0 | 75.2025 | 476.3518 | 37.38% | 0 | 0 | 0 | 0% | 29.8
1469 | 0 | 0 | 0 | 2.2164 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.8802 | 30.1 | 0 | 75.8802 | 405.3855 | 31.81% | 0 | 0 | 0 | 0% | 30.1
1470 | 0 | 0 | 0 | 1.0074 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7684 | 31.3 | 0 | 78.7684 | 331.0659 | 25.98% | 0 | 0 | 0 | 0% | 31.3
1471 | 40 | 5 | 4 | 0.80595 | 7.9 | 20.1327 | 0 | 7.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7223 | 34.2 | 0 | 85.7223 | 248.4711 | 19.5% | 0 | 0 | 0 | 0% | 34.2
1472 | 560 | 129 | 33 | 2.0149 | 11.3 | 281.8577 | 141.5704 | 0 | 114.4656 | 17.6462 | 0 | 0 | 17.6462 | 0 | 0 | 0 | 0 | 0 | 114.4656 | 0 | 355.4522 | 27.89% | 0 | 0 | 0 | 0% | 17.6462
1473 | 812 | 339 | 51 | 1.8134 | 16.4 | 408.6937 | 239.0708 | 0 | 205.7425 | 56.5953 | 0 | 9.9476 | 46.6476 | 0 | 0 | 0 | 0 | 0 | 205.7425 | 0 | 547.7418 | 42.98% | 7.6298 | 0 | 7.6956 | 15.39% | 36.7
1474 | 917 | 534 | 60 | 1.2089 | 20.7 | 461.542 | 289.8226 | 0 | 253.4576 | 97.1529 | 5.4264 | 25 | 66.7264 | 0 | 0 | 0 | 0 | 0 | 253.4576 | 0 | 784.6265 | 61.56% | 19.175 | 0 | 27.0358 | 54.07% | 36.3
1475 | 962 | 682 | 66 | 2.4178 | 22.1 | 484.1913 | 313.6976 | 0 | 275.2806 | 113.6 | 13.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 275.2806 | 0 | 1041.9073 | 81.75% | 19.175 | 0 | 46.3761 | 92.75% | 36.4
1476 | 979 | 771 | 71 | 3.0223 | 22.8 | 492.7477 | 322.5522 | 0 | 283.346 | 113.9 | 34.2157 | 4.6843 | 75 | 0 | 0 | 0 | 0 | 0 | 283.346 | 0 | 1274.5104 | 100% | 3.5929 | 0 | 50 | 100% | 36.1
1477 | 986 | 798 | 73 | 8.0595 | 23.2 | 496.2709 | 0 | 320.7913 | 0 | 115.5 | 40.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.5
1478 | 982 | 757 | 69 | 8.261 | 23.5 | 494.2577 | 0 | 309.1038 | 0 | 116.6 | 41.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.4
1479 | 954 | 651 | 66 | 9.4699 | 23.7 | 480.1648 | 0 | 278.1454 | 0 | 117.1 | 42.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.9
1480 | 902 | 491 | 57 | 10.4773 | 23.2 | 453.9923 | 0 | 223.4552 | 0 | 94.6173 | 30.4587 | 0 | 64.1587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.7
1481 | 805 | 295 | 44 | 10.4773 | 21.8 | 405.1705 | 0 | 0 | 0 | 43.2229 | 2.7114 | 0 | 40.5114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.8
1482 | 417 | 86 | 23 | 8.0595 | 19.5 | 209.8834 | 0 | 0 | 0 | 8.925 | 0 | 0 | 8.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.7883 | 49.58% | 33.925
1483 | 0 | 1 | 0 | 6.8506 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.5802 | 0 | 0% | 24.5802
1484 | 0 | 0 | 0 | 7.052 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6028 | 39.3 | 0 | 98.6028 | 1177.5505 | 92.39% | 0 | 0 | 0 | 0% | 39.3
1485 | 0 | 0 | 0 | 4.2312 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6312 | 36.1 | 0 | 90.6312 | 1089.6694 | 85.5% | 0 | 0 | 0 | 0% | 36.1
1486 | 0 | 0 | 0 | 1.6119 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9834 | 33.4 | 0 | 83.9834 | 1009.4804 | 79.21% | 0 | 0 | 0 | 0% | 33.4
1487 | 0 | 0 | 0 | 1.6119 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6349 | 31.2 | 0 | 78.6349 | 935.5139 | 73.4% | 0 | 0 | 0 | 0% | 31.2
1488 | 0 | 0 | 0 | 3.8283 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2333 | 30.2 | 0 | 76.2333 | 864.3188 | 67.82% | 0 | 0 | 0 | 0% | 30.2
1489 | 0 | 0 | 0 | 1.6119 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.765 | 29.6 | 0 | 74.765 | 794.647 | 62.35% | 0 | 0 | 0 | 0% | 29.6
1490 | 0 | 0 | 0 | 1.6119 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4199 | 29.9 | 0 | 75.4199 | 724.2291 | 56.82% | 0 | 0 | 0 | 0% | 29.9
1491 | 0 | 0 | 0 | 3.4253 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2928 | 31.1 | 0 | 78.2928 | 650.4996 | 51.04% | 0 | 0 | 0 | 0% | 31.1
1492 | 0 | 0 | 0 | 4.6342 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3879 | 35.3 | 0 | 88.3879 | 564.7635 | 44.31% | 0 | 0 | 0 | 0% | 35.3
1493 | 0 | 0 | 0 | 4.2312 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4304 | 39.9 | 0 | 99.4304 | 465.9347 | 36.56% | 0 | 0 | 0 | 0% | 39.9
1494 | 0 | 0 | 0 | 4.4327 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.4122 | 42.8 | 0 | 106.4122 | 358.8608 | 28.16% | 0 | 0 | 0 | 0% | 42.8
1495 | 18 | 4 | 3 | 4.6342 | 9.8 | 9.0597 | 0 | 3.363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4205 | 45.3 | 0 | 112.4205 | 244.5592 | 19.19% | 0 | 0 | 0 | 0% | 45.3
1496 | 460 | 123 | 34 | 4.2312 | 11.1 | 231.526 | 116.6738 | 0 | 90.4948 | 15.4348 | 0 | 0 | 15.4348 | 0 | 0 | 0 | 77.155 | 30.5652 | 90.4948 | 77.155 | 258.068 | 20.25% | 0 | 0 | 0 | 0% | 46
1497 | 807 | 343 | 55 | 2.6193 | 16.3 | 406.1771 | 237.957 | 0 | 204.4239 | 48.9223 | 1.5111 | 0 | 47.4111 | 0 | 0 | 0 | 0 | 0 | 204.4239 | 0 | 451.6152 | 35.43% | 0 | 0 | 0 | 0% | 45.9
1498 | 901 | 536 | 68 | 2.2164 | 18.9 | 453.489 | 284.9681 | 0 | 248.499 | 89.8646 | 0 | 22.1323 | 67.7323 | 0 | 0 | 0 | 0 | 0 | 248.499 | 0 | 686.8924 | 53.89% | 16.9755 | 0 | 17.1242 | 34.25% | 45.6
1499 | 957 | 696 | 80 | 3.4253 | 20.7 | 481.6747 | 312.3638 | 0 | 273.678 | 104.5 | 4.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 273.678 | 0 | 946.009 | 74.23% | 19.175 | 0 | 36.4673 | 72.93% | 45.5
1500 | 984 | 784 | 77 | 4.4327 | 21.8 | 495.2643 | 324.287 | 0 | 284.4733 | 105.7 | 13.2096 | 17.4904 | 75 | 0 | 0 | 0 | 0 | 0 | 284.4733 | 0 | 1215.3464 | 95.36% | 13.4152 | 0 | 50 | 100% | 44.3
1501 | 972 | 798 | 81 | 5.4401 | 22.5 | 489.2245 | 194.3455 | 122.2374 | 169.9359 | 106.7 | 31.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 169.9359 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.3
1502 | 955 | 754 | 82 | 5.6416 | 23.7 | 480.6681 | 0 | 300.8962 | 0 | 107.6 | 32.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
1503 | 896 | 642 | 88 | 7.455 | 23.6 | 450.9724 | 0 | 261.7977 | 0 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
1504 | 547 | 439 | 166 | 9.0669 | 23.1 | 275.3146 | 0 | 136.1494 | 0 | 61.7991 | 9.6996 | 0 | 52.0996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
1505 | 424 | 233 | 109 | 10.4773 | 21 | 213.4066 | 0 | 0 | 0 | 29.9189 | 0 | 0 | 29.9189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 15.4811 | 34.3857 | 68.77% | 45.4
1506 | 258 | 87 | 46 | 6.6491 | 18.8 | 129.8559 | 0 | 0 | 0 | 8.3868 | 0 | 0 | 8.3868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 9.1696 | 18.34% | 33.3868
1507 | 1 | 1 | 1 | 3.0223 | 14.9 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9762 | 37.0081 | 0 | 92.9762 | 1184.126 | 92.91% | 0 | 9.0919 | 0 | 0% | 46.1
1508 | 0 | 0 | 0 | 3.8283 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3898 | 42.7 | 0 | 106.3898 | 1077.5461 | 84.55% | 0 | 0 | 0 | 0% | 42.7
1509 | 0 | 0 | 0 | 1.8134 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7462 | 38.7 | 0 | 96.7462 | 982.3276 | 77.07% | 0 | 0 | 0 | 0% | 38.7
1510 | 0 | 0 | 0 | 2.6193 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9559 | 36.3 | 0 | 90.9559 | 893.901 | 70.14% | 0 | 0 | 0 | 0% | 36.3
1511 | 0 | 0 | 0 | 2.0149 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6826 | 34.1 | 0 | 85.6826 | 811.7085 | 63.69% | 0 | 0 | 0 | 0% | 34.1
1512 | 0 | 0 | 0 | 4.8357 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3874 | 32.7 | 0 | 82.3874 | 733.5206 | 57.55% | 0 | 0 | 0 | 0% | 32.7
1513 | 0 | 0 | 0 | 4.4327 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1517 | 32.2 | 0 | 81.1517 | 656.7394 | 51.53% | 0 | 0 | 0 | 0% | 32.2
1514 | 0 | 0 | 0 | 2.6193 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0546 | 32.2 | 0 | 81.0546 | 579.9452 | 45.5% | 0 | 0 | 0 | 0% | 32.2
1515 | 0 | 0 | 0 | 4.2312 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2602 | 33.1 | 0 | 83.2602 | 500.5756 | 39.28% | 0 | 0 | 0 | 0% | 33.1
1516 | 0 | 0 | 0 | 2.6193 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1055 | 36.4 | 0 | 91.1055 | 411.7773 | 32.31% | 0 | 0 | 0 | 0% | 36.4
1517 | 0 | 0 | 0 | 3.6268 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0944 | 41.4 | 0 | 103.0944 | 308.7279 | 24.22% | 0 | 0 | 0 | 0% | 41.4
1518 | 0 | 0 | 0 | 4.6342 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5974 | 44.1 | 0 | 109.5974 | 197.9292 | 15.53% | 0 | 0 | 0 | 0% | 44.1
1519 | 23 | 6 | 5 | 4.4327 | 10.8 | 11.5763 | 0 | 4.3237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8434 | 43.777 | 0 | 108.8434 | 88.0137 | 6.906% | 0 | 0 | 0 | 0% | 43.777
1520 | 13 | 64 | 63 | 4.6342 | 12 | 6.5431 | 0 | 3.3081 | 0 | 4.9888 | 0 | 0 | 4.9888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0137 | 6.906% | 0 | 0 | 0 | 0% | 4.9888
1521 | 1 | 137 | 135 | 3.6268 | 14.2 | 0.50332 | 0 | 0.29531 | 0 | 10.754 | 0 | 0 | 10.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0137 | 6.906% | 0 | 0 | 0 | 0% | 10.754
1522 | 21 | 258 | 242 | 3.6268 | 16.1 | 10.5697 | 0 | 6.6466 | 0 | 21.3766 | 0 | 0 | 21.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0137 | 6.906% | 0 | 0 | 0 | 0% | 21.3766
1523 | 204 | 519 | 376 | 2.2164 | 18.2 | 102.6767 | 66.6486 | 0 | 44.0478 | 56.5681 | 0 | 5.3341 | 51.2341 | 0 | 0 | 0 | 0 | 0 | 44.0478 | 0 | 130.1594 | 10.21% | 4.0912 | 0 | 4.1277 | 8.255% | 45.9
1524 | 333 | 581 | 328 | 3.4253 | 19.6 | 167.6047 | 109.7732 | 0 | 84.1744 | 77.1416 | 0 | 16.2708 | 60.8708 | 0 | 0 | 0 | 0 | 0 | 84.1744 | 0 | 210.6988 | 16.53% | 12.4797 | 0 | 16.7185 | 33.44% | 44.6
1525 | 600 | 693 | 239 | 6.8506 | 20.5 | 301.9904 | 195.6367 | 0 | 162.9158 | 106.4 | 6.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 162.9158 | 0 | 366.5793 | 28.76% | 19.175 | 0 | 36.0644 | 72.13% | 43.6
1526 | 574 | 649 | 235 | 5.0372 | 21.3 | 288.9042 | 181.0293 | 0 | 150.3993 | 104.4483 | 12.8157 | 18.0085 | 73.6241 | 0 | 0 | 0 | 0 | 0 | 150.3993 | 0 | 510.4838 | 40.05% | 13.8125 | 0 | 50 | 100% | 42.8
1527 | 432 | 525 | 247 | 7.052 | 21.3 | 217.4331 | 126.4979 | 0 | 98.1238 | 75.5446 | 16.5723 | 0 | 58.9723 | 0 | 0 | 0 | 0 | 0 | 98.1238 | 0 | 604.3702 | 47.42% | 0 | 0 | 50 | 100% | 42.4
1528 | 269 | 344 | 206 | 8.8654 | 20.6 | 135.3924 | 67.2717 | 0 | 41.3007 | 37.3069 | 0 | 0 | 37.3069 | 0 | 0 | 0 | 0 | 0 | 41.3007 | 0 | 643.8874 | 50.52% | 0 | 5.0931 | 44.8624 | 89.72% | 42.4
1529 | 241 | 212 | 134 | 7.2535 | 20 | 121.2995 | 0 | 0 | 0 | 23.3946 | 0 | 0 | 23.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643.8874 | 50.52% | 0 | 22.5054 | 22.1597 | 44.32% | 45.9
1530 | 94 | 73 | 55 | 5.8431 | 18.8 | 47.3118 | 0 | 0 | 0 | 6.0288 | 0 | 0 | 6.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643.8874 | 50.52% | 0 | 21.9675 | 2.7756e-15 | 5.551e-15% | 27.9963
1531 | 0 | 1 | 0 | 3.6268 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.7503 | 46.4 | 0 | 115.7503 | 526.593 | 41.32% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 46.4
1532 | 0 | 0 | 0 | 2.0149 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.5054 | 43.1 | 0 | 107.5054 | 418.776 | 32.86% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.1
1533 | 0 | 0 | 0 | 1.2089 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7024 | 39.5 | 0 | 98.7024 | 321.1636 | 25.2% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.5
1534 | 0 | 0 | 0 | 0.60446 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4442 | 36.9 | 0 | 92.4442 | 230.9489 | 18.12% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.9
1535 | 0 | 0 | 0 | 0.20149 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8705 | 34.6 | 0 | 86.8705 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.6
1536 | 0 | 0 | 0 | 0.20149 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1537 | 0 | 0 | 0 | 0.40297 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1538 | 0 | 0 | 0 | 2.0149 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1539 | 0 | 0 | 0 | 1.2089 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1540 | 0 | 0 | 0 | 2.6193 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1541 | 0 | 0 | 0 | 1.4104 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1542 | 0 | 0 | 0 | 2.2164 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1543 | 0 | 4 | 4 | 1.6119 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
1544 | 109 | 91 | 65 | 7.6565 | 10.2 | 54.8616 | 0 | 27.8261 | 0 | 8.3675 | 0 | 0 | 8.3675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1958 | 11.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 8.3675
1545 | 295 | 292 | 180 | 11.4848 | 14.8 | 148.4786 | 87.2444 | 0 | 58.8538 | 33.2049 | 0 | 0 | 33.2049 | 0 | 0 | 0 | 0 | 0 | 58.8538 | 0 | 203.7959 | 15.99% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.2049
1546 | 324 | 484 | 305 | 11.8877 | 17.2 | 163.0748 | 102.6184 | 0 | 72.6187 | 57.7176 | 0 | 4.8588 | 52.8588 | 0 | 0 | 0 | 0 | 0 | 72.6187 | 0 | 273.6339 | 21.47% | 3.7267 | 0 | 3.7604 | 7.521% | 48
1547 | 101 | 423 | 349 | 10.2758 | 18.1 | 50.8351 | 0 | 33.0288 | 0 | 39.9584 | 0 | 0 | 39.9584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.6339 | 21.47% | 0 | 3.7273 | 0 | 0% | 43.6857
1548 | 294 | 615 | 387 | 11.4848 | 20.2 | 147.9753 | 96.9433 | 0 | 67.727 | 82.7555 | 0 | 18.2277 | 64.5277 | 0 | 0 | 0 | 0 | 0 | 67.727 | 0 | 338.7674 | 26.58% | 13.9807 | 0 | 14.1073 | 28.21% | 46.3
1549 | 240 | 566 | 376 | 14.3056 | 22.1 | 120.7962 | 78.3414 | 0 | 48.3258 | 69.7025 | 0 | 12.2512 | 57.4512 | 0 | 0 | 0 | 0 | 0 | 48.3258 | 0 | 385.2427 | 30.23% | 9.3967 | 0 | 23.5892 | 47.18% | 45.2
1550 | 313 | 595 | 358 | 17.9323 | 22.4 | 157.5383 | 98.8116 | 0 | 65.7534 | 81.4145 | 0 | 18.4572 | 62.9572 | 0 | 0 | 0 | 0 | 0 | 65.7534 | 0 | 448.4782 | 35.19% | 14.1567 | 0 | 37.8742 | 75.75% | 44.5
1551 | 9 | 300 | 290 | 21.9621 | 20.3 | 4.5299 | 0 | 2.6411 | 0 | 24.5731 | 0 | 0 | 24.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 448.4782 | 35.19% | 0 | 19.8269 | 17.8709 | 35.74% | 44.4
1552 | 541 | 538 | 274 | 22.9695 | 19.6 | 272.2947 | 135.9363 | 0 | 97.5997 | 80.2907 | 0 | 17.8953 | 62.3953 | 0 | 0 | 0 | 0 | 0 | 97.5997 | 0 | 542.3404 | 42.55% | 13.7257 | 0 | 31.7216 | 63.44% | 44.5
1553 | 189 | 177 | 103 | 21.3576 | 17.8 | 95.127 | 0 | 0 | 0 | 18.19 | 0 | 0 | 18.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542.3404 | 42.55% | 0 | 25 | 6.498 | 13% | 43.19
1554 | 9 | 38 | 37 | 23.3725 | 16.2 | 4.5299 | 0 | 0 | 0 | 2.4753 | 0 | 0 | 2.4753 | 0 | 0 | 0 | 100.5006 | 40.085 | 0 | 100.5006 | 442.9168 | 34.75% | 0 | 6.4397 | 0.00033537 | 0.0006707% | 49
1555 | 0 | 2 | 2 | 21.3576 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.0333 | 47.4 | 0 | 118.0333 | 322.4858 | 25.3% | 0 | 0 | 0.00033537 | 0.0006707% | 47.4
1556 | 0 | 0 | 0 | 14.91 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.7426 | 44 | 0 | 109.7426 | 211.8589 | 16.62% | 0 | 0 | 0.00033537 | 0.0006707% | 44
1557 | 0 | 0 | 0 | 15.1115 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.8017 | 39.9 | 0 | 99.8017 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 39.9
1558 | 0 | 0 | 0 | 16.5219 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1559 | 0 | 0 | 0 | 15.1115 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1560 | 0 | 0 | 0 | 15.1115 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1561 | 0 | 0 | 0 | 11.0818 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1562 | 0 | 0 | 0 | 4.6342 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1563 | 0 | 0 | 0 | 2.6193 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1564 | 0 | 0 | 0 | 3.8283 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1565 | 0 | 0 | 0 | 3.2238 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1566 | 0 | 0 | 0 | 4.6342 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1567 | 0 | 4 | 3 | 4.2312 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 0
1568 | 35 | 79 | 70 | 2.0149 | 8.6 | 17.6161 | 0 | 8.9634 | 0 | 6.5433 | 0 | 0 | 6.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8742 | 8.856% | 0 | 0 | 0.00033537 | 0.0006707% | 6.5433
1569 | 219 | 251 | 167 | 2.4178 | 10.8 | 110.2265 | 64.8628 | 0 | 42.3529 | 26.9858 | 0 | 0 | 26.9858 | 0 | 0 | 0 | 0 | 0 | 42.3529 | 0 | 153.8467 | 12.07% | 0 | 0 | 0.00033537 | 0.0006707% | 26.9858
1570 | 691 | 514 | 135 | 2.6193 | 13.6 | 347.7923 | 219.007 | 0 | 186.6638 | 78.7203 | 0 | 16.1101 | 62.6101 | 0 | 0 | 0 | 0 | 0 | 186.6638 | 0 | 334.4268 | 26.24% | 12.3565 | 0 | 12.4705 | 24.94% | 46.5
1571 | 951 | 718 | 91 | 3.0223 | 15.3 | 478.6548 | 311.1204 | 0 | 272.6172 | 103.9 | 3.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 272.6172 | 0 | 598.1587 | 46.93% | 19.175 | 0 | 31.8221 | 63.64% | 46.1
1572 | 528 | 552 | 161 | 4.2312 | 15.6 | 265.7516 | 174.15 | 0 | 144.2225 | 87.0331 | 0 | 21.1165 | 65.9165 | 0 | 0 | 0 | 0 | 0 | 144.2225 | 0 | 737.6807 | 57.88% | 16.1964 | 0 | 48.1676 | 96.34% | 44.8
1573 | 897 | 837 | 159 | 8.261 | 16.6 | 451.4757 | 293.1267 | 0 | 253.2106 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 253.2106 | 0 | 982.6386 | 77.1% | 0 | 0 | 48.1676 | 96.34% | 43.9
1574 | 245 | 373 | 190 | 7.455 | 16.2 | 123.3128 | 77.4211 | 0 | 51.4594 | 40.8714 | 0 | 0 | 40.8714 | 0 | 0 | 0 | 0 | 0 | 51.4594 | 0 | 1032.4208 | 81.01% | 0 | 0 | 48.1676 | 96.34% | 40.8714
1575 | 29 | 119 | 99 | 5.2387 | 15.2 | 14.5962 | 0 | 8.5291 | 0 | 9.9579 | 0 | 0 | 9.9579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1032.4208 | 81.01% | 0 | 25 | 22.9414 | 45.88% | 34.9579
1576 | 111 | 230 | 165 | 8.261 | 15.4 | 55.8682 | 0 | 28.0236 | 0 | 22.187 | 0 | 0 | 22.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1032.4208 | 81.01% | 0 | 20.613 | 2.1407 | 4.281% | 42.8
1577 | 441 | 258 | 125 | 5.8431 | 15.8 | 221.963 | 81.6071 | 0 | 56.5492 | 32.2954 | 0 | 0 | 32.2954 | 0 | 0 | 0 | 0 | 0 | 56.5492 | 0 | 1087.1269 | 85.3% | 0 | 0 | 2.1407 | 4.281% | 32.2954
1578 | 288 | 107 | 58 | 2.4178 | 15.6 | 144.9554 | 0 | 0 | 0 | 9.9006 | 0 | 0 | 9.9006 | 0 | 0 | 0 | 95.6697 | 38.0994 | 0 | 95.6697 | 993.5238 | 77.95% | 0 | 0 | 2.1407 | 4.281% | 48
1579 | 0 | 1 | 1 | 2.6193 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.5609 | 46.9 | 0 | 116.5609 | 874.7168 | 68.63% | 0 | 0 | 2.1407 | 4.281% | 46.9
1580 | 0 | 0 | 0 | 2.4178 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7538 | 43.7 | 0 | 108.7538 | 765.1092 | 60.03% | 0 | 0 | 2.1407 | 4.281% | 43.7
1581 | 0 | 0 | 0 | 2.6193 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7447 | 39.6 | 0 | 98.7447 | 667.1539 | 52.35% | 0 | 0 | 2.1407 | 4.281% | 39.6
1582 | 0 | 0 | 0 | 1.6119 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.926 | 37.2 | 0 | 92.926 | 576.0602 | 45.2% | 0 | 0 | 2.1407 | 4.281% | 37.2
1583 | 0 | 0 | 0 | 3.4253 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1614 | 34.8 | 0 | 87.1614 | 491.7195 | 38.58% | 0 | 0 | 2.1407 | 4.281% | 34.8
1584 | 0 | 0 | 0 | 2.4178 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7995 | 33.4 | 0 | 83.7995 | 411.4153 | 32.28% | 0 | 0 | 2.1407 | 4.281% | 33.4
1585 | 0 | 0 | 0 | 4.2312 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3742 | 32.8 | 0 | 82.3742 | 332.812 | 26.11% | 0 | 0 | 2.1407 | 4.281% | 32.8
1586 | 0 | 0 | 0 | 4.0297 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3227 | 32.8 | 0 | 82.3227 | 254.1731 | 19.94% | 0 | 0 | 2.1407 | 4.281% | 32.8
1587 | 0 | 0 | 0 | 4.6342 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0036 | 33.5 | 0 | 84.0036 | 173.5013 | 13.61% | 0 | 0 | 2.1407 | 4.281% | 33.5
1588 | 0 | 0 | 0 | 5.2387 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.5013 | 13.61% | 0 | 0 | 2.1407 | 4.281% | 0
1589 | 0 | 0 | 0 | 2.6193 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.5013 | 13.61% | 0 | 0 | 2.1407 | 4.281% | 0
1590 | 0 | 0 | 0 | 4.8357 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.5013 | 13.61% | 0 | 0 | 2.1407 | 4.281% | 0
1591 | 58 | 10 | 7 | 2.2164 | 4.9 | 29.1924 | 0 | 11.0999 | 0 | 0.21001 | 0 | 0 | 0.21001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.5013 | 13.61% | 0 | 0 | 2.1407 | 4.281% | 0.21001
1592 | 531 | 147 | 43 | 2.8208 | 7.8 | 267.2615 | 136.4136 | 0 | 109.2443 | 18.6057 | 0 | 0 | 18.6057 | 0 | 0 | 0 | 0 | 0 | 109.2443 | 0 | 278.3258 | 21.84% | 0 | 0 | 2.1407 | 4.281% | 18.6057
1593 | 769 | 358 | 66 | 2.6193 | 11.2 | 387.0511 | 228.0909 | 0 | 195.1658 | 48.6426 | 0.97132 | 0 | 47.6713 | 0 | 0 | 0 | 0 | 0 | 195.1658 | 0 | 465.5955 | 36.53% | 0 | 0 | 2.1407 | 4.281% | 46.7
1594 | 885 | 554 | 75 | 2.0149 | 14.2 | 445.4359 | 280.6855 | 0 | 244.4995 | 90.9958 | 0 | 22.4479 | 68.5479 | 0 | 0 | 0 | 0 | 0 | 244.4995 | 0 | 700.203 | 54.94% | 17.2175 | 0 | 19.5191 | 39.04% | 46.1
1595 | 935 | 704 | 82 | 5.2387 | 15.7 | 470.6018 | 305.9455 | 0 | 266.9388 | 104.4 | 4.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 266.9388 | 0 | 956.3419 | 75.04% | 19.175 | 0 | 38.8732 | 77.75% | 45.6
1596 | 950 | 794 | 91 | 6.4476 | 16.4 | 478.1515 | 313.4241 | 0 | 273.1556 | 106 | 16.6282 | 14.3718 | 75 | 0 | 0 | 0 | 0 | 0 | 273.1556 | 0 | 1218.4462 | 95.6% | 11.0232 | 0 | 49.9994 | 100% | 44
1597 | 910 | 806 | 113 | 6.0446 | 17 | 458.0188 | 163.3786 | 134.111 | 142.0308 | 107.1 | 32.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 142.0308 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9994 | 100% | 42.9
1598 | 360 | 549 | 277 | 5.6416 | 17.2 | 181.1943 | 0 | 113.8748 | 0 | 75.5704 | 16.6852 | 0 | 58.8852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9994 | 100% | 42.2
1599 | 124 | 329 | 249 | 4.0297 | 16.8 | 62.4114 | 0 | 36.55 | 0 | 32.5541 | 0 | 0 | 32.5541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.0459 | 40.8704 | 81.74% | 41.6
1600 | 597 | 461 | 165 | 6.8506 | 17.1 | 300.4805 | 0 | 151.4406 | 0 | 69.9835 | 2.4999 | 11.7919 | 55.6918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 9.0444 | 0 | 49.9995 | 100% | 41.4
1601 | 660 | 299 | 80 | 9.0669 | 16.1 | 332.1895 | 0 | 123.2634 | 0 | 38.3146 | 0 | 0 | 38.3146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.7854 | 44.1609 | 88.32% | 44.1
1602 | 304 | 89 | 36 | 7.858 | 14.3 | 153.0085 | 0 | 0 | 0 | 8.4112 | 0 | 0 | 8.4112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.9304 | 37.86% | 33.4112
1603 | 1 | 1 | 1 | 3.6268 | 12.1 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.2986 | 26.1417 | 0 | 67.2986 | 1212.6986 | 95.15% | 0 | 18.7583 | 0 | 0% | 44.9
1604 | 0 | 0 | 0 | 1.0074 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5433 | 42.4 | 0 | 105.5433 | 1106.9123 | 86.85% | 0 | 0 | 0 | 0% | 42.4
1605 | 0 | 0 | 0 | 2.4178 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5272 | 39.1 | 0 | 97.5272 | 1010.4914 | 79.28% | 0 | 0 | 0 | 0% | 39.1
1606 | 0 | 0 | 0 | 3.2238 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4808 | 37 | 0 | 92.4808 | 920.0433 | 72.19% | 0 | 0 | 0 | 0% | 37
1607 | 0 | 0 | 0 | 4.4327 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4712 | 34.5 | 0 | 86.4712 | 836.6448 | 65.64% | 0 | 0 | 0 | 0% | 34.5
1608 | 0 | 0 | 0 | 5.0372 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9233 | 32.6 | 0 | 81.9233 | 758.6987 | 59.53% | 0 | 0 | 0 | 0% | 32.6
1609 | 0 | 0 | 0 | 5.0372 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9934 | 31.8 | 0 | 79.9934 | 683.0057 | 53.59% | 0 | 0 | 0 | 0% | 31.8
1610 | 0 | 0 | 0 | 3.4253 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2465 | 31.5 | 0 | 79.2465 | 608.1493 | 47.72% | 0 | 0 | 0 | 0% | 31.5
1611 | 0 | 0 | 0 | 3.6268 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2348 | 31.5 | 0 | 79.2348 | 533.2755 | 41.84% | 0 | 0 | 0 | 0% | 31.5
1612 | 0 | 0 | 0 | 2.8208 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6149 | 32.5 | 0 | 81.6149 | 455.5596 | 35.74% | 0 | 0 | 0 | 0% | 32.5
1613 | 0 | 0 | 0 | 1.4104 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9731 | 33.5 | 0 | 83.9731 | 374.966 | 29.42% | 0 | 0 | 0 | 0% | 33.5
1614 | 0 | 0 | 0 | 1.2089 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9566 | 36 | 0 | 89.9566 | 287.2015 | 22.53% | 0 | 0 | 0 | 0% | 36
1615 | 89 | 12 | 7 | 1.0074 | 4.8 | 44.7952 | 0 | 17.1314 | 0 | 0.32261 | 0 | 0 | 0.32261 | 0 | 0 | 0 | 97.1075 | 38.9774 | 0 | 97.1075 | 190.9451 | 14.98% | 0 | 0 | 0 | 0% | 39.3
1616 | 618 | 160 | 37 | 1.4104 | 9.5 | 311.0501 | 159.2552 | 0 | 131.184 | 20.1261 | 0 | 0 | 20.1261 | 0 | 0 | 0 | 54.7438 | 20.7739 | 131.184 | 54.7438 | 265.1948 | 20.81% | 0 | 0 | 0 | 0% | 40.9
1617 | 839 | 375 | 53 | 1.8134 | 14.4 | 422.2833 | 249.2109 | 0 | 215.1155 | 57.0167 | 0 | 8.1084 | 48.9084 | 0 | 0 | 0 | 0 | 0 | 215.1155 | 0 | 468.3357 | 36.75% | 6.2191 | 0 | 6.2782 | 12.56% | 40.8
1618 | 934 | 572 | 60 | 8.0595 | 16.8 | 470.0984 | 296.4266 | 0 | 256.3879 | 103.9254 | 6.7627 | 25 | 72.1627 | 0 | 0 | 0 | 0 | 0 | 256.3879 | 0 | 710.4514 | 55.74% | 19.175 | 0 | 25.6354 | 51.27% | 40.4
1619 | 979 | 722 | 65 | 10.2758 | 17.7 | 492.7477 | 320.4046 | 0 | 277.3192 | 109.9 | 9.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 277.3192 | 0 | 972.3333 | 76.29% | 19.175 | 0 | 44.9926 | 89.99% | 40.1
1620 | 999 | 811 | 67 | 9.4699 | 19 | 502.8141 | 329.6811 | 0 | 286.534 | 110.8 | 29.333 | 6.467 | 75 | 0 | 0 | 0 | 0 | 0 | 286.534 | 0 | 1242.9171 | 97.52% | 4.9602 | 0 | 50 | 100% | 39.2
1621 | 999 | 834 | 70 | 11.6862 | 19.4 | 502.8141 | 0 | 326.6836 | 0 | 112.6 | 37.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.9171 | 97.52% | 0 | 0 | 50 | 100% | 37.4
1622 | 985 | 788 | 71 | 11.0818 | 19.4 | 495.7676 | 0 | 311.8859 | 0 | 113.9 | 38.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.9171 | 97.52% | 0 | 0 | 50 | 100% | 36.1
1623 | 957 | 679 | 67 | 9.4699 | 19.4 | 481.6747 | 0 | 282.7121 | 0 | 114.4 | 39.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.9171 | 97.52% | 0 | 0 | 50 | 100% | 35.6
1624 | 894 | 513 | 62 | 9.2684 | 19.4 | 449.9657 | 0 | 227.8638 | 0 | 93.3502 | 28.8751 | 0 | 64.4751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.9171 | 97.52% | 0 | 0 | 50 | 100% | 35.6
1625 | 777 | 313 | 53 | 8.4625 | 18.6 | 391.0776 | 0 | 146.454 | 0 | 42.0051 | 1.7026 | 0 | 40.3026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.9171 | 97.52% | 0 | 0 | 50 | 100% | 38.6
1626 | 437 | 100 | 29 | 8.261 | 16.9 | 219.9497 | 0 | 0 | 0 | 9.7474 | 0 | 0 | 9.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.9171 | 97.52% | 0 | 25 | 24.7662 | 49.53% | 34.7474
1627 | 1 | 1 | 1 | 6.4476 | 14.1 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.9171 | 97.52% | 0 | 24.5368 | 0 | 0% | 24.5368
1628 | 0 | 0 | 0 | 4.4327 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6933 | 39.1 | 0 | 97.6933 | 1146.5487 | 89.96% | 0 | 0 | 0 | 0% | 39.1
1629 | 0 | 0 | 0 | 2.4178 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5762 | 36.6 | 0 | 91.5762 | 1057.2777 | 82.96% | 0 | 0 | 0 | 0% | 36.6
1630 | 0 | 0 | 0 | 2.4178 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2935 | 34 | 0 | 85.2935 | 975.3741 | 76.53% | 0 | 0 | 0 | 0% | 34
1631 | 0 | 0 | 0 | 0.60446 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7371 | 31.7 | 0 | 79.7371 | 900.0255 | 70.62% | 0 | 0 | 0 | 0% | 31.7
1632 | 0 | 0 | 0 | 2.6193 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.6386 | 30 | 0 | 75.6386 | 829.3933 | 65.08% | 0 | 0 | 0 | 0% | 30
1633 | 0 | 0 | 0 | 2.2164 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6606 | 29.1 | 0 | 73.6606 | 760.9561 | 59.71% | 0 | 0 | 0 | 0% | 29.1
1634 | 0 | 0 | 0 | 2.4178 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5549 | 28.6 | 0 | 72.5549 | 693.7313 | 54.43% | 0 | 0 | 0 | 0% | 28.6
1635 | 0 | 0 | 0 | 1.0074 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7576 | 28.7 | 0 | 72.7576 | 626.2511 | 49.14% | 0 | 0 | 0 | 0% | 28.7
1636 | 0 | 0 | 0 | 3.6268 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5416 | 29.5 | 0 | 74.5416 | 556.8004 | 43.69% | 0 | 0 | 0 | 0% | 29.5
1637 | 0 | 0 | 0 | 2.4178 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2007 | 29.8 | 0 | 75.2007 | 486.6009 | 38.18% | 0 | 0 | 0 | 0% | 29.8
1638 | 0 | 0 | 0 | 2.8208 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0518 | 31 | 0 | 78.0518 | 413.1228 | 32.41% | 0 | 0 | 0 | 0% | 31
1639 | 104 | 14 | 7 | 1.2089 | 7.8 | 52.345 | 0 | 20.1331 | 0 | 0.55179 | 0 | 0 | 0.55179 | 0 | 0 | 0 | 83.4422 | 33.2482 | 0 | 83.4422 | 333.2719 | 26.15% | 0 | 0 | 0 | 0% | 33.8
1640 | 637 | 165 | 35 | 1.4104 | 10.5 | 320.6132 | 164.6527 | 0 | 136.2369 | 20.4439 | 0 | 0 | 20.4439 | 0 | 0 | 0 | 0 | 0 | 136.2369 | 0 | 460.4902 | 36.13% | 0 | 0 | 0 | 0% | 20.4439
1641 | 842 | 378 | 50 | 1.6119 | 16.1 | 423.7932 | 250.4576 | 0 | 216.353 | 60.6349 | 0 | 12.1674 | 48.4674 | 0 | 0 | 0 | 0 | 0 | 216.353 | 0 | 662.5212 | 51.98% | 9.3324 | 0 | 9.4224 | 18.84% | 36.3
1642 | 926 | 571 | 58 | 1.8134 | 19.2 | 466.0719 | 294.0842 | 0 | 257.2579 | 100.915 | 7.6075 | 25 | 68.3075 | 0 | 0 | 0 | 0 | 0 | 257.2579 | 0 | 902.7491 | 70.83% | 19.175 | 0 | 28.7824 | 57.56% | 35.7
1643 | 971 | 720 | 63 | 5.4401 | 20.7 | 488.7212 | 317.847 | 0 | 277.9726 | 113.9 | 13.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 277.9726 | 0 | 1162.3205 | 91.2% | 19.175 | 0 | 48.1424 | 96.28% | 36.1
1644 | 984 | 806 | 68 | 8.4625 | 20.6 | 495.2643 | 219.12 | 105.7007 | 190.663 | 114.3 | 39.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 190.663 | 0 | 1274.5104 | 100% | 0 | 0 | 48.1424 | 96.28% | 35.7
1645 | 978 | 826 | 74 | 8.6639 | 21.1 | 492.2444 | 0 | 319.9139 | 0 | 115.9 | 40.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.1424 | 96.28% | 34.1
1646 | 965 | 781 | 74 | 9.2684 | 21.6 | 485.7013 | 0 | 305.8604 | 0 | 116.9 | 41.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.1424 | 96.28% | 33.1
1647 | 937 | 674 | 70 | 11.8877 | 21 | 471.6084 | 0 | 277.4241 | 0 | 117.3 | 42.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.1424 | 96.28% | 32.7
1648 | 881 | 512 | 63 | 11.2833 | 21.4 | 443.4226 | 0 | 225.6238 | 0 | 93.9779 | 30.4389 | 0 | 63.5389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.1424 | 96.28% | 33.1
1649 | 767 | 311 | 51 | 9.0669 | 21.5 | 386.0444 | 0 | 145.8993 | 0 | 41.5336 | 2.3168 | 0 | 39.2168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.1424 | 96.28% | 36.9
1650 | 455 | 101 | 29 | 6.6491 | 20.4 | 229.0094 | 0 | 0 | 0 | 9.853 | 0 | 0 | 9.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 22.905 | 45.81% | 34.853
1651 | 2 | 2 | 1 | 4.0297 | 16.5 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.6895 | 0 | 0% | 22.6895
1652 | 0 | 0 | 0 | 2.0149 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5841 | 38.6 | 0 | 96.5841 | 1179.5397 | 92.55% | 0 | 0 | 0 | 0% | 38.6
1653 | 0 | 0 | 0 | 0.80595 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.302 | 35.6 | 0 | 89.302 | 1093.0387 | 85.76% | 0 | 0 | 0 | 0% | 35.6
1654 | 0 | 0 | 0 | 1.2089 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0628 | 33 | 0 | 83.0628 | 1013.9783 | 79.56% | 0 | 0 | 0 | 0% | 33
1655 | 0 | 0 | 0 | 0.40297 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4617 | 31.1 | 0 | 78.4617 | 940.2762 | 73.78% | 0 | 0 | 0 | 0% | 31.1
1656 | 0 | 0 | 0 | 1.4104 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.8411 | 30 | 0 | 75.8411 | 869.6191 | 68.23% | 0 | 0 | 0 | 0% | 30
1657 | 0 | 0 | 0 | 1.6119 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5091 | 29.4 | 0 | 74.5091 | 800.4234 | 62.8% | 0 | 0 | 0 | 0% | 29.4
1658 | 0 | 0 | 0 | 5.6416 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8369 | 29.5 | 0 | 74.8369 | 730.9723 | 57.35% | 0 | 0 | 0 | 0% | 29.5
1659 | 0 | 0 | 0 | 5.0372 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8728 | 30.8 | 0 | 77.8728 | 658.0644 | 51.63% | 0 | 0 | 0 | 0% | 30.8
1660 | 0 | 0 | 0 | 3.2238 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0443 | 35.1 | 0 | 88.0443 | 572.868 | 44.95% | 0 | 0 | 0 | 0% | 35.1
1661 | 0 | 0 | 0 | 2.2164 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.308 | 40.2 | 0 | 100.308 | 473.1671 | 37.13% | 0 | 0 | 0 | 0% | 40.2
1662 | 0 | 0 | 0 | 3.6268 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7921 | 43.3 | 0 | 107.7921 | 364.6387 | 28.61% | 0 | 0 | 0 | 0% | 43.3
1663 | 110 | 15 | 7 | 1.2089 | 10.7 | 55.3649 | 0 | 21.4146 | 0 | 0.53667 | 0 | 0 | 0.53667 | 0 | 0 | 0 | 110.7196 | 44.5633 | 0 | 110.7196 | 252.4391 | 19.81% | 0 | 0 | 0 | 0% | 45.1
1664 | 619 | 165 | 37 | 1.4104 | 14.9 | 311.5535 | 160.482 | 0 | 132.3454 | 19.9504 | 0 | 0 | 19.9504 | 0 | 0 | 0 | 65.8092 | 25.3496 | 132.3454 | 65.8092 | 317.3428 | 24.9% | 0 | 0 | 0 | 0% | 45.3
1665 | 821 | 376 | 52 | 1.2089 | 19.8 | 413.2236 | 244.5546 | 0 | 211.0356 | 48.4729 | 1.5364 | 0 | 46.9364 | 0 | 0 | 0 | 0 | 0 | 211.0356 | 0 | 516.897 | 40.56% | 0 | 0 | 0 | 0% | 45.4
1666 | 909 | 566 | 61 | 1.6119 | 22.3 | 457.5155 | 288.8762 | 0 | 252.4261 | 88.0742 | 0 | 21.3871 | 66.6871 | 0 | 0 | 0 | 0 | 0 | 252.4261 | 0 | 755.5898 | 59.28% | 16.4039 | 0 | 16.5644 | 33.13% | 45.3
1667 | 941 | 709 | 70 | 4.8357 | 24 | 473.6217 | 308.0849 | 0 | 269.2497 | 105.1 | 5.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 269.2497 | 0 | 1010.1909 | 79.26% | 19.175 | 0 | 35.9271 | 71.85% | 44.9
1668 | 940 | 794 | 86 | 13.7011 | 23.2 | 473.1183 | 310.3821 | 0 | 266.046 | 106.4 | 13.2299 | 18.1701 | 75 | 0 | 0 | 0 | 0 | 0 | 266.046 | 0 | 1261.7627 | 99% | 13.9365 | 0 | 50 | 100% | 43.6
1669 | 918 | 818 | 108 | 14.5071 | 22 | 462.0454 | 0 | 300.3794 | 0 | 107.3 | 32.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.7627 | 99% | 0 | 0 | 50 | 100% | 42.7
1670 | 885 | 776 | 123 | 14.5071 | 20.8 | 445.4359 | 0 | 280.7873 | 0 | 108.1 | 33.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.7627 | 99% | 0 | 0 | 50 | 100% | 41.9
1671 | 827 | 667 | 130 | 15.1115 | 19.9 | 416.2435 | 0 | 245.4068 | 0 | 108.8 | 33.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.7627 | 99% | 0 | 0 | 50 | 100% | 41.2
1672 | 763 | 492 | 101 | 14.5071 | 18.6 | 384.0312 | 0 | 196.3384 | 0 | 81.4728 | 20.2864 | 0 | 61.1864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.7627 | 99% | 0 | 0 | 50 | 100% | 40.9
1673 | 642 | 296 | 76 | 13.9026 | 17.5 | 323.1298 | 0 | 123.2412 | 0 | 36.8829 | 0 | 0 | 36.8829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.7627 | 99% | 0 | 7.2171 | 42.7134 | 85.43% | 44.1
1674 | 330 | 95 | 40 | 11.8877 | 15.9 | 166.0947 | 0 | 0 | 0 | 9.0304 | 0 | 0 | 9.0304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.7627 | 99% | 0 | 25 | 17.4722 | 34.94% | 34.0304
1675 | 0 | 2 | 2 | 10.0743 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.7995 | 28.0944 | 0 | 71.7995 | 1195.6574 | 93.81% | 0 | 17.3056 | 0 | 0% | 45.4
1676 | 0 | 0 | 0 | 8.0595 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9339 | 42.1 | 0 | 104.9339 | 1090.7578 | 85.58% | 0 | 0 | 0 | 0% | 42.1
1677 | 0 | 0 | 0 | 7.455 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7226 | 38.3 | 0 | 95.7226 | 996.6588 | 78.2% | 0 | 0 | 0 | 0% | 38.3
1678 | 0 | 0 | 0 | 6.4476 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6188 | 36.2 | 0 | 90.6188 | 908.4906 | 71.28% | 0 | 0 | 0 | 0% | 36.2
1679 | 0 | 0 | 0 | 6.4476 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1018 | 33.9 | 0 | 85.1018 | 826.8555 | 64.88% | 0 | 0 | 0 | 0% | 33.9
1680 | 0 | 0 | 0 | 4.0297 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9993 | 32.6 | 0 | 81.9993 | 748.9328 | 58.76% | 0 | 0 | 0 | 0% | 32.6
1681 | 0 | 0 | 0 | 3.2238 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9628 | 32.2 | 0 | 80.9628 | 672.1329 | 52.74% | 0 | 0 | 0 | 0% | 32.2
1682 | 0 | 0 | 0 | 3.2238 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6986 | 32.1 | 0 | 80.6986 | 595.6075 | 46.73% | 0 | 0 | 0 | 0% | 32.1
1683 | 0 | 0 | 0 | 4.0297 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8485 | 33 | 0 | 82.8485 | 516.5182 | 40.53% | 0 | 0 | 0 | 0% | 33
1684 | 0 | 0 | 0 | 3.8283 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4477 | 36.6 | 0 | 91.4477 | 427.1484 | 33.51% | 0 | 0 | 0 | 0% | 36.6
1685 | 0 | 0 | 0 | 2.6193 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9716 | 41.4 | 0 | 102.9716 | 324.0739 | 25.43% | 0 | 0 | 0 | 0% | 41.4
1686 | 0 | 0 | 0 | 3.0223 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.0024 | 44.3 | 0 | 110.0024 | 212.6715 | 16.69% | 0 | 0 | 0 | 0% | 44.3
1687 | 92 | 16 | 9 | 0.60446 | 6.8 | 46.3052 | 0 | 18.0097 | 0 | 0.60403 | 0 | 0 | 0.60403 | 0 | 0 | 0 | 87.8135 | 35.1082 | 0 | 87.8135 | 127.389 | 9.995% | 0 | 0 | 0 | 0% | 35.7122
1688 | 590 | 170 | 43 | 0.40297 | 10.6 | 296.9573 | 153.4179 | 0 | 126.1496 | 20.0676 | 0 | 0 | 20.0676 | 0 | 0 | 0 | 0 | 0 | 126.1496 | 0 | 247.3933 | 19.41% | 0 | 0 | 0 | 0% | 20.0676
1689 | 818 | 385 | 58 | 1.0074 | 15.1 | 411.7136 | 244.0001 | 0 | 210.5861 | 50.5481 | 2.4241 | 0 | 48.1241 | 0 | 0 | 0 | 0 | 0 | 210.5861 | 0 | 447.7207 | 35.13% | 0 | 0 | 0 | 0% | 45.7
1690 | 920 | 582 | 66 | 4.0297 | 17.6 | 463.052 | 292.563 | 0 | 255.0517 | 95.5299 | 0.064969 | 25 | 70.465 | 0 | 0 | 0 | 0 | 0 | 255.0517 | 0 | 690.3476 | 54.17% | 19.175 | 0 | 19.3654 | 38.73% | 45.4
1691 | 967 | 731 | 70 | 8.261 | 19.7 | 486.7079 | 316.6565 | 0 | 275.1121 | 105 | 5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 275.1121 | 0 | 952.0577 | 74.7% | 19.175 | 0 | 38.7308 | 77.46% | 45
1692 | 985 | 819 | 74 | 9.0669 | 20.6 | 495.7676 | 325.3311 | 0 | 282.7436 | 106.4 | 16.852 | 14.548 | 75 | 0 | 0 | 0 | 0 | 0 | 282.7436 | 0 | 1221.0274 | 95.8% | 11.1583 | 0 | 50 | 100% | 43.6
1693 | 980 | 837 | 77 | 9.6714 | 21.2 | 493.251 | 143.9192 | 176.8463 | 124.7843 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 124.7843 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
1694 | 961 | 789 | 79 | 8.8654 | 21.8 | 483.688 | 0 | 305.2092 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42
1695 | 918 | 676 | 79 | 9.0669 | 22.4 | 462.0454 | 0 | 273.0261 | 0 | 108.3 | 33.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
1696 | 855 | 512 | 72 | 8.6639 | 21.7 | 430.3364 | 0 | 221.0639 | 0 | 82.8376 | 20.6188 | 0 | 62.2188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
1697 | 747 | 314 | 57 | 8.6639 | 20.6 | 375.9781 | 0 | 144.7065 | 0 | 38.8466 | 0 | 0 | 38.8466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.8534 | 44.0893 | 88.18% | 44.7
1698 | 428 | 103 | 34 | 8.261 | 17.3 | 215.4198 | 0 | 0 | 0 | 9.9509 | 0 | 0 | 9.9509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.8446 | 37.69% | 34.9509
1699 | 4 | 2 | 2 | 5.0372 | 14.3 | 2.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2026 | 27.3378 | 0 | 70.2026 | 1209.9601 | 94.94% | 0 | 18.6622 | 2.7756e-15 | 5.551e-15% | 46
1700 | 0 | 0 | 0 | 3.0223 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8977 | 42.5 | 0 | 105.8977 | 1103.952 | 86.62% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42.5
1701 | 0 | 0 | 0 | 2.4178 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9152 | 38.8 | 0 | 96.9152 | 1008.4486 | 79.12% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38.8
1702 | 0 | 0 | 0 | 2.2164 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3672 | 36.5 | 0 | 91.3672 | 919.462 | 72.14% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.5
1703 | 0 | 0 | 0 | 1.6119 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8178 | 34.2 | 0 | 85.8178 | 836.9818 | 65.67% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.2
1704 | 0 | 0 | 0 | 2.4178 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3178 | 33.1 | 0 | 83.3178 | 757.6547 | 59.45% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.1
1705 | 0 | 0 | 0 | 3.4253 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3874 | 32.7 | 0 | 82.3874 | 679.4564 | 53.31% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.7
1706 | 0 | 0 | 0 | 5.8431 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6998 | 32.8 | 0 | 82.6998 | 600.9604 | 47.15% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.8
1707 | 0 | 0 | 0 | 4.8357 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1219 | 33.7 | 0 | 85.1219 | 519.871 | 40.79% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.7
1708 | 0 | 0 | 0 | 2.4178 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.792 | 37 | 0 | 92.792 | 429.3847 | 33.69% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37
1709 | 0 | 0 | 0 | 3.6268 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5316 | 41.8 | 0 | 104.5316 | 325.2062 | 25.52% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.8
1710 | 0 | 0 | 0 | 2.2164 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.1269 | 44.6 | 0 | 111.1269 | 212.9702 | 16.71% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 44.6
1711 | 79 | 17 | 11 | 2.4178 | 13.5 | 39.7621 | 0 | 15.5494 | 0 | 0.62212 | 0 | 0 | 0.62212 | 0 | 0 | 0 | 112.8822 | 45.3779 | 0 | 112.8822 | 98.4468 | 7.724% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 46
1712 | 516 | 164 | 43 | 3.4253 | 16.4 | 259.7118 | 134.5687 | 0 | 107.3566 | 18.0188 | 0 | 0 | 18.0188 | 0 | 0 | 0 | 0 | 0 | 107.3566 | 0 | 201.126 | 15.78% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 18.0188
1713 | 903 | 414 | 50 | 11.4848 | 20.9 | 454.4956 | 269.7255 | 0 | 229.2095 | 58.7696 | 0 | 6.1348 | 52.6348 | 0 | 0 | 0 | 0 | 0 | 229.2095 | 0 | 420.3493 | 32.98% | 4.7054 | 0 | 4.7528 | 9.506% | 46.5
1714 | 976 | 618 | 66 | 15.313 | 22.8 | 491.2378 | 310.5716 | 0 | 265.2415 | 103.7 | 3.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 265.2415 | 0 | 674.0347 | 52.89% | 19.175 | 0 | 24.1209 | 48.24% | 46.3
1715 | 977 | 802 | 129 | 19.1413 | 24.1 | 491.7411 | 319.9902 | 0 | 271.8817 | 104.1 | 4.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 271.8817 | 0 | 934.071 | 73.29% | 19.175 | 0 | 43.4891 | 86.98% | 45.9
1716 | 1036 | 850 | 62 | 14.91 | 24.7 | 521.4368 | 342.2707 | 0 | 295.2387 | 105.6 | 22.1959 | 8.4041 | 75 | 0 | 0 | 0 | 0 | 0 | 295.2387 | 0 | 1216.4466 | 95.44% | 6.4459 | 0 | 50 | 100% | 44.4
1717 | 1007 | 858 | 73 | 12.4922 | 24.9 | 506.8406 | 112.1388 | 217.5665 | 96.8918 | 106.5 | 31.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 96.8918 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.5
1718 | 907 | 789 | 112 | 13.9026 | 23.1 | 456.5089 | 0 | 288.3519 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
1719 | 352 | 410 | 183 | 13.0966 | 21 | 177.1677 | 0 | 104.9272 | 0 | 51.8491 | 4.7746 | 0 | 47.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
1720 | 434 | 445 | 218 | 10.6788 | 20.8 | 218.4397 | 0 | 112.7484 | 0 | 54.7958 | 6.2479 | 0 | 48.5479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
1721 | 108 | 152 | 115 | 13.7011 | 17.9 | 54.3583 | 0 | 21.1115 | 0 | 14.6529 | 0 | 0 | 14.6529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.752 | 49.5% | 39.6529
1722 | 155 | 66 | 41 | 10.8803 | 16.1 | 78.0142 | 0 | 0 | 0 | 5.7019 | 0 | 0 | 5.7019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.5089 | 2.7756e-15 | 5.551e-15% | 30.2107
1723 | 2 | 2 | 2 | 9.4699 | 14 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.1336 | 46.7 | 0 | 116.1336 | 1156.4744 | 90.74% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 46.7
1724 | 0 | 0 | 0 | 7.6565 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.1017 | 43 | 0 | 107.1017 | 1049.0511 | 82.31% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43
1725 | 0 | 0 | 0 | 8.0595 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8473 | 39.2 | 0 | 97.8473 | 952.4087 | 74.73% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.2
1726 | 0 | 0 | 0 | 6.4476 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2969 | 36.9 | 0 | 92.2969 | 862.3039 | 67.66% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.9
1727 | 0 | 0 | 0 | 6.2461 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.486 | 34.9 | 0 | 87.486 | 777.7956 | 61.03% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.9
1728 | 0 | 0 | 0 | 3.8283 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0557 | 33.5 | 0 | 84.0557 | 697.3306 | 54.71% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.5
1729 | 0 | 0 | 0 | 1.6119 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8582 | 33 | 0 | 82.8582 | 618.2876 | 48.51% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33
1730 | 0 | 0 | 0 | 1.4104 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.824 | 33 | 0 | 82.824 | 539.2306 | 42.31% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33
1731 | 0 | 0 | 0 | 0.60446 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9289 | 33.9 | 0 | 84.9289 | 457.568 | 35.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.9
1732 | 0 | 0 | 0 | 1.6119 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0955 | 37.3 | 0 | 93.0955 | 366.2348 | 28.74% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.3
1733 | 0 | 0 | 0 | 3.6268 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1462 | 41.9 | 0 | 104.1462 | 261.7714 | 20.54% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.9
1734 | 0 | 0 | 0 | 4.2312 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3424 | 44.9 | 0 | 111.3424 | 148.6587 | 11.66% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 44.9
1735 | 155 | 21 | 10 | 3.2238 | 6 | 78.0142 | 0 | 30.6726 | 0 | 0.88181 | 0 | 0 | 0.88181 | 0 | 0 | 0 | 69.2218 | 27.1404 | 0 | 69.2218 | 84.8743 | 6.659% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 28.0222
1736 | 669 | 187 | 39 | 3.2238 | 10 | 336.7193 | 174.974 | 0 | 145.32 | 22.2194 | 0 | 0 | 22.2194 | 0 | 0 | 0 | 0 | 0 | 145.32 | 0 | 224.1415 | 17.59% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 22.2194
1737 | 871 | 408 | 52 | 2.4178 | 13.1 | 438.3894 | 260.5213 | 0 | 225.4108 | 56.2404 | 0 | 5.0702 | 51.1702 | 0 | 0 | 0 | 0 | 0 | 225.4108 | 0 | 440.1637 | 34.54% | 3.8888 | 0 | 3.9286 | 7.857% | 46.1
1738 | 951 | 602 | 59 | 3.0223 | 14.8 | 478.6548 | 302.8094 | 0 | 264.886 | 98.0053 | 0.95263 | 25 | 72.0526 | 0 | 0 | 0 | 0 | 0 | 264.886 | 0 | 694.0168 | 54.45% | 19.175 | 0 | 23.2995 | 46.6% | 46.1
1739 | 990 | 750 | 64 | 2.2164 | 16.1 | 498.2842 | 324.3073 | 0 | 285.2277 | 104.4 | 4.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 285.2277 | 0 | 967.3643 | 75.9% | 19.175 | 0 | 42.6704 | 85.34% | 45.6
1740 | 1003 | 835 | 68 | 3.2238 | 17.4 | 504.8273 | 331.4604 | 0 | 291.5758 | 106.1 | 21.6405 | 9.4595 | 75 | 0 | 0 | 0 | 0 | 0 | 291.5758 | 0 | 1246.7955 | 97.83% | 7.2554 | 0 | 50 | 100% | 43.9
1741 | 1003 | 856 | 69 | 7.052 | 18.3 | 504.8273 | 0 | 328.4982 | 0 | 106.9 | 31.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.7955 | 97.83% | 0 | 0 | 50 | 100% | 43.1
1742 | 986 | 807 | 71 | 9.6714 | 18.7 | 496.2709 | 0 | 313.7871 | 0 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.7955 | 97.83% | 0 | 0 | 50 | 100% | 42.5
1743 | 954 | 696 | 69 | 11.0818 | 18.2 | 480.1648 | 0 | 285.0233 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.7955 | 97.83% | 0 | 0 | 50 | 100% | 42
1744 | 894 | 530 | 63 | 10.8803 | 17.5 | 449.9657 | 0 | 233.3591 | 0 | 87.8251 | 23.0125 | 0 | 64.8125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.7955 | 97.83% | 0 | 0 | 50 | 100% | 41.8
1745 | 783 | 327 | 52 | 10.0743 | 16.6 | 394.0975 | 0 | 154.4419 | 0 | 40.3358 | 0 | 0 | 40.3358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.7955 | 97.83% | 0 | 4.2642 | 45.6929 | 91.39% | 44.6
1746 | 508 | 113 | 31 | 7.455 | 15.3 | 255.6852 | 0 | 0 | 0 | 10.8569 | 0 | 0 | 10.8569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.7955 | 97.83% | 0 | 25 | 20.441 | 40.88% | 35.8569
1747 | 9 | 3 | 2 | 4.4327 | 13 | 4.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9541 | 25.9627 | 0 | 66.9541 | 1185.3501 | 93% | 0 | 20.2373 | 0 | 0% | 46.2
1748 | 0 | 0 | 0 | 1.6119 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7879 | 42.9 | 0 | 106.7879 | 1078.2022 | 84.6% | 0 | 0 | 0 | 0% | 42.9
1749 | 0 | 0 | 0 | 1.2089 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.7909 | 39.2 | 0 | 97.7909 | 981.551 | 77.01% | 0 | 0 | 0 | 0% | 39.2
1750 | 0 | 0 | 0 | 1.8134 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2236 | 36.9 | 0 | 92.2236 | 891.4381 | 69.94% | 0 | 0 | 0 | 0% | 36.9
1751 | 0 | 0 | 0 | 2.0149 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6843 | 34.6 | 0 | 86.6843 | 807.8135 | 63.38% | 0 | 0 | 0 | 0% | 34.6
1752 | 0 | 0 | 0 | 1.8134 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8164 | 33.4 | 0 | 83.8164 | 727.6464 | 57.09% | 0 | 0 | 0 | 0% | 33.4
1753 | 0 | 0 | 0 | 1.6119 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5997 | 32.9 | 0 | 82.5997 | 648.8873 | 50.91% | 0 | 0 | 0 | 0% | 32.9
1754 | 0 | 0 | 0 | 3.8283 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3424 | 32.8 | 0 | 82.3424 | 570.3933 | 44.75% | 0 | 0 | 0 | 0% | 32.8
1755 | 0 | 0 | 0 | 3.4253 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5342 | 33.7 | 0 | 84.5342 | 489.3106 | 38.39% | 0 | 0 | 0 | 0% | 33.7
1756 | 0 | 0 | 0 | 3.0223 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.855 | 37.2 | 0 | 92.855 | 398.2554 | 31.25% | 0 | 0 | 0 | 0% | 37.2
1757 | 0 | 0 | 0 | 2.4178 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4247 | 41.6 | 0 | 103.4247 | 294.6393 | 23.12% | 0 | 0 | 0 | 0% | 41.6
1758 | 0 | 0 | 0 | 2.0149 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.3848 | 44.5 | 0 | 110.3848 | 182.6838 | 14.33% | 0 | 0 | 0 | 0% | 44.5
1759 | 189 | 23 | 10 | 1.6119 | 7.3 | 95.127 | 0 | 37.5992 | 0 | 0.9669 | 0 | 0 | 0.9669 | 0 | 0 | 0 | 63.827 | 24.7521 | 0 | 63.827 | 124.0797 | 9.735% | 0 | 0 | 0 | 0% | 25.719
1760 | 695 | 195 | 38 | 0.80595 | 12.4 | 349.8056 | 182.2919 | 0 | 153.0141 | 22.5381 | 0 | 0 | 22.5381 | 0 | 0 | 0 | 0 | 0 | 153.0141 | 0 | 269.8433 | 21.17% | 0 | 0 | 0 | 0% | 22.5381
1761 | 876 | 414 | 52 | 0.80595 | 17.2 | 440.906 | 262.3696 | 0 | 227.7445 | 54.3022 | 0 | 4.2011 | 50.1011 | 0 | 0 | 0 | 0 | 0 | 227.7445 | 0 | 486.7962 | 38.19% | 3.2222 | 0 | 3.2556 | 6.511% | 45.9
1762 | 958 | 611 | 59 | 3.2238 | 19.3 | 482.1781 | 305.2304 | 0 | 267.0993 | 97.599 | 1.0495 | 25 | 71.5495 | 0 | 0 | 0 | 0 | 0 | 267.0993 | 0 | 741.2392 | 58.16% | 19.175 | 0 | 22.6293 | 45.26% | 45.5
1763 | 1001 | 762 | 64 | 5.2387 | 20.8 | 503.8207 | 327.9699 | 0 | 287.5656 | 105 | 5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 287.5656 | 0 | 1015.1787 | 79.65% | 19.175 | 0 | 42.003 | 84.01% | 45
1764 | 1020 | 851 | 66 | 4.2312 | 22.1 | 513.3837 | 337.1721 | 0 | 296.6349 | 106.7 | 21.3806 | 10.3194 | 75 | 0 | 0 | 0 | 0 | 0 | 296.6349 | 0 | 1274.5104 | 100% | 7.915 | 0 | 50 | 100% | 43.3
1765 | 1021 | 872 | 67 | 4.4327 | 22.8 | 513.8871 | 0 | 334.4983 | 0 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
1766 | 1007 | 823 | 66 | 6.8506 | 23.6 | 506.8406 | 0 | 320.7977 | 0 | 108.8 | 33.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
1767 | 974 | 709 | 65 | 7.858 | 24 | 490.2311 | 0 | 291.6621 | 0 | 109.3 | 34.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.7
1768 | 916 | 541 | 61 | 4.0297 | 23.9 | 461.0387 | 0 | 240.2399 | 0 | 85.6132 | 22.6566 | 0 | 62.9566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.3
1769 | 800 | 334 | 52 | 7.6565 | 22.8 | 402.6539 | 0 | 159.2131 | 0 | 39.771 | 0 | 0 | 39.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 3.029 | 46.94 | 93.88% | 42.8
1770 | 525 | 118 | 31 | 7.2535 | 20.7 | 264.2416 | 0 | 0 | 0 | 10.8353 | 0 | 0 | 10.8353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 21.6846 | 43.37% | 35.8353
1771 | 10 | 2 | 2 | 4.6342 | 17.8 | 5.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.6739 | 22.5345 | 0 | 59.6739 | 1220.0954 | 95.73% | 0 | 21.4655 | 0 | 0% | 44
1772 | 0 | 0 | 0 | 1.4104 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0918 | 41.2 | 0 | 103.0918 | 1117.7693 | 87.7% | 0 | 0 | 0 | 0% | 41.2
1773 | 0 | 0 | 0 | 2.4178 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2249 | 38 | 0 | 95.2249 | 1024.5477 | 80.39% | 0 | 0 | 0 | 0% | 38
1774 | 0 | 0 | 0 | 1.6119 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7414 | 36.2 | 0 | 90.7414 | 936.4002 | 73.47% | 0 | 0 | 0 | 0% | 36.2
1775 | 0 | 0 | 0 | 2.0149 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3943 | 34 | 0 | 85.3943 | 854.4957 | 67.05% | 0 | 0 | 0 | 0% | 34
1776 | 0 | 0 | 0 | 3.6268 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5977 | 32.4 | 0 | 81.5977 | 777.1594 | 60.98% | 0 | 0 | 0 | 0% | 32.4
1777 | 0 | 0 | 0 | 2.6193 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8367 | 31.7 | 0 | 79.8367 | 701.7887 | 55.06% | 0 | 0 | 0 | 0% | 31.7
1778 | 0 | 0 | 0 | 2.0149 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5802 | 31.2 | 0 | 78.5802 | 627.8088 | 49.26% | 0 | 0 | 0 | 0% | 31.2
1779 | 0 | 0 | 0 | 2.2164 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3237 | 31.1 | 0 | 78.3237 | 554.0957 | 43.48% | 0 | 0 | 0 | 0% | 31.1
1780 | 0 | 0 | 0 | 2.6193 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4822 | 32 | 0 | 80.4822 | 477.8394 | 37.49% | 0 | 0 | 0 | 0% | 32
1781 | 0 | 0 | 0 | 2.0149 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3742 | 32.8 | 0 | 82.3742 | 399.3101 | 31.33% | 0 | 0 | 0 | 0% | 32.8
1782 | 0 | 0 | 0 | 3.8283 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8701 | 35.5 | 0 | 88.8701 | 312.9963 | 24.56% | 0 | 0 | 0 | 0% | 35.5
1783 | 198 | 26 | 11 | 0.80595 | 8.4 | 99.6568 | 0 | 39.5955 | 0 | 1.016 | 0 | 0 | 1.016 | 0 | 0 | 0 | 94.081 | 37.684 | 0 | 94.081 | 220.5093 | 17.3% | 0 | 0 | 0 | 0% | 38.7
1784 | 700 | 202 | 40 | 2.8208 | 12.5 | 352.3222 | 184.1189 | 0 | 153.9636 | 23.1287 | 0 | 0 | 23.1287 | 0 | 0 | 0 | 0 | 0 | 153.9636 | 0 | 365.7003 | 28.69% | 0 | 0 | 0 | 0% | 23.1287
1785 | 880 | 422 | 52 | 1.8134 | 17.1 | 442.9193 | 263.9184 | 0 | 228.8285 | 61.369 | 0 | 10.5345 | 50.8345 | 0 | 0 | 0 | 0 | 0 | 228.8285 | 0 | 581.4907 | 45.62% | 8.08 | 0 | 8.1648 | 16.33% | 40.3
1786 | 965 | 620 | 58 | 1.8134 | 20.4 | 485.7013 | 307.6518 | 0 | 269.8515 | 101.8758 | 6.1879 | 25 | 70.6879 | 0 | 0 | 0 | 0 | 0 | 269.8515 | 0 | 835.9667 | 65.59% | 19.175 | 0 | 27.5413 | 55.08% | 39.5
1787 | 1007 | 770 | 61 | 2.8208 | 22.1 | 506.8406 | 329.9947 | 0 | 290.3804 | 110.5 | 10.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 290.3804 | 0 | 1109.8019 | 87.08% | 19.175 | 0 | 46.9178 | 93.84% | 39.5
1788 | 1027 | 858 | 63 | 5.6416 | 23 | 516.907 | 288.1365 | 51.4388 | 253.0754 | 111.6 | 32.6232 | 3.9768 | 75 | 0 | 0 | 0 | 0 | 0 | 253.0754 | 0 | 1274.5104 | 100% | 3.0502 | 0 | 50 | 100% | 38.4
1789 | 1031 | 881 | 64 | 6.4476 | 23.8 | 518.9202 | 0 | 337.8808 | 0 | 113.4 | 38.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.6
1790 | 1021 | 833 | 63 | 10.8803 | 24 | 513.8871 | 0 | 325.5906 | 0 | 114.7 | 39.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.3
1791 | 988 | 718 | 62 | 11.8877 | 24.1 | 497.2776 | 0 | 296.5302 | 0 | 114.9 | 39.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.1
1792 | 924 | 547 | 58 | 12.0892 | 23.8 | 465.0653 | 0 | 243.4888 | 0 | 94.4556 | 29.6778 | 0 | 64.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.1
1793 | 806 | 339 | 50 | 11.2833 | 22.8 | 405.6738 | 0 | 161.8399 | 0 | 42.0894 | 2.1447 | 0 | 39.9447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.8
1794 | 522 | 121 | 32 | 8.8654 | 21.4 | 262.7317 | 0 | 0 | 0 | 10.7924 | 0 | 0 | 10.7924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.7411 | 49.48% | 35.7924
1795 | 17 | 3 | 3 | 7.2535 | 18.6 | 8.5564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.4876 | 0 | 0% | 24.4876
1796 | 0 | 0 | 0 | 4.2312 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0993 | 38.7 | 0 | 97.0993 | 1179.2848 | 92.53% | 0 | 0 | 0 | 0% | 38.7
1797 | 0 | 0 | 0 | 2.0149 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0971 | 35.9 | 0 | 90.0971 | 1091.9737 | 85.68% | 0 | 0 | 0 | 0% | 35.9
1798 | 0 | 0 | 0 | 0.60446 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0331 | 33.4 | 0 | 84.0331 | 1011.7939 | 79.39% | 0 | 0 | 0 | 0% | 33.4
1799 | 0 | 0 | 0 | 0.40297 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9335 | 31.3 | 0 | 78.9335 | 937.5558 | 73.56% | 0 | 0 | 0 | 0% | 31.3
1800 | 0 | 0 | 0 | 1.4104 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2967 | 29.8 | 0 | 75.2967 | 867.4116 | 68.06% | 0 | 0 | 0 | 0% | 29.8
1801 | 0 | 0 | 0 | 2.0149 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5319 | 29 | 0 | 73.5319 | 799.2169 | 62.71% | 0 | 0 | 0 | 0% | 29
1802 | 0 | 0 | 0 | 1.4104 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.6231 | 28.6 | 0 | 72.6231 | 731.9902 | 57.43% | 0 | 0 | 0 | 0% | 28.6
1803 | 0 | 0 | 0 | 3.2238 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8669 | 28.7 | 0 | 72.8669 | 664.5086 | 52.14% | 0 | 0 | 0 | 0% | 28.7
1804 | 0 | 0 | 0 | 5.2387 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.011 | 29.2 | 0 | 74.011 | 595.7919 | 46.75% | 0 | 0 | 0 | 0% | 29.2
1805 | 0 | 0 | 0 | 4.8357 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.011 | 29.2 | 0 | 74.011 | 527.0631 | 41.35% | 0 | 0 | 0 | 0% | 29.2
1806 | 0 | 0 | 0 | 3.4253 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8877 | 30.9 | 0 | 77.8877 | 453.86 | 35.61% | 0 | 0 | 0 | 0% | 30.9
1807 | 203 | 28 | 11 | 4.2312 | 9.7 | 102.1734 | 0 | 40.8044 | 0 | 1.0454 | 0 | 0 | 1.0454 | 0 | 0 | 0 | 81.8467 | 32.5546 | 0 | 81.8467 | 375.9778 | 29.5% | 0 | 0 | 0 | 0% | 33.6
1808 | 720 | 210 | 39 | 3.0223 | 14.1 | 362.3885 | 189.9037 | 0 | 159.2896 | 23.4692 | 0 | 0 | 23.4692 | 0 | 0 | 0 | 0 | 0 | 159.2896 | 0 | 524.4398 | 41.15% | 0 | 0 | 0 | 0% | 23.4692
1809 | 897 | 434 | 53 | 1.4104 | 18.9 | 451.4757 | 269.3708 | 0 | 234.0872 | 66.2658 | 0 | 14.9329 | 51.3329 | 0 | 0 | 0 | 0 | 0 | 234.0872 | 0 | 742.6151 | 58.27% | 11.4535 | 0 | 11.5755 | 23.15% | 36.4
1810 | 971 | 632 | 61 | 5.4401 | 21.8 | 488.7212 | 309.7545 | 0 | 270.4478 | 109.9608 | 11.8804 | 25 | 73.0804 | 0 | 0 | 0 | 0 | 0 | 270.4478 | 0 | 994.6796 | 78.04% | 19.175 | 0 | 30.9547 | 61.91% | 36.2
1811 | 989 | 771 | 69 | 3.4253 | 23.9 | 497.7809 | 324.1532 | 0 | 284.716 | 113.4 | 13.8308 | 24.5692 | 75 | 0 | 0 | 0 | 0 | 0 | 284.716 | 0 | 1260.0423 | 98.86% | 18.8446 | 0 | 50 | 100% | 36.6
1812 | 1001 | 856 | 75 | 9.4699 | 25.4 | 503.8207 | 0 | 331.0546 | 0 | 113.7 | 38.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.0423 | 98.86% | 0 | 0 | 50 | 100% | 36.3
1813 | 1006 | 877 | 74 | 8.261 | 25.5 | 506.3373 | 0 | 329.7919 | 0 | 115.6 | 40.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.0423 | 98.86% | 0 | 0 | 50 | 100% | 34.4
1814 | 980 | 821 | 76 | 9.4699 | 25.6 | 493.251 | 0 | 312.8363 | 0 | 116.8 | 41.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.0423 | 98.86% | 0 | 0 | 50 | 100% | 33.2
1815 | 952 | 711 | 74 | 10.4773 | 25.9 | 479.1582 | 0 | 286.379 | 0 | 117.3 | 42.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.0423 | 98.86% | 0 | 0 | 50 | 100% | 32.7
1816 | 909 | 549 | 65 | 12.0892 | 25.8 | 457.5155 | 0 | 240.6702 | 0 | 94.7031 | 30.7015 | 0 | 64.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.0423 | 98.86% | 0 | 0 | 50 | 100% | 33.3
1817 | 786 | 343 | 59 | 11.6862 | 24.9 | 395.6075 | 0 | 159.2243 | 0 | 43.0612 | 3.2806 | 0 | 39.7806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.0423 | 98.86% | 0 | 0 | 50 | 100% | 36.5
1818 | 501 | 125 | 39 | 9.4699 | 23.4 | 252.162 | 0 | 0 | 0 | 10.964 | 0 | 0 | 10.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.0423 | 98.86% | 0 | 25 | 24.7375 | 49.48% | 35.964
1819 | 13 | 3 | 3 | 4.4327 | 20.7 | 6.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.0423 | 98.86% | 0 | 24.4806 | 0 | 0% | 24.4806
1820 | 0 | 0 | 0 | 3.4253 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1048 | 38.1 | 0 | 96.1048 | 1166.4754 | 91.52% | 0 | 0 | 0 | 0% | 38.1
1821 | 0 | 0 | 0 | 2.6193 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1632 | 35.3 | 0 | 89.1632 | 1080.7887 | 84.8% | 0 | 0 | 0 | 0% | 35.3
1822 | 0 | 0 | 0 | 2.6193 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8063 | 32.8 | 0 | 82.8063 | 1002.2789 | 78.64% | 0 | 0 | 0 | 0% | 32.8
1823 | 0 | 0 | 0 | 2.4178 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3925 | 31 | 0 | 78.3925 | 928.8375 | 72.88% | 0 | 0 | 0 | 0% | 31
1824 | 0 | 0 | 0 | 3.6268 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7666 | 29.9 | 0 | 75.7666 | 858.4081 | 67.35% | 0 | 0 | 0 | 0% | 29.9
1825 | 0 | 0 | 0 | 3.4253 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6099 | 29.4 | 0 | 74.6099 | 789.195 | 61.92% | 0 | 0 | 0 | 0% | 29.4
1826 | 0 | 0 | 0 | 4.0297 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2529 | 29.7 | 0 | 75.2529 | 719.2358 | 56.43% | 0 | 0 | 0 | 0% | 29.7
1827 | 0 | 0 | 0 | 7.455 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7418 | 30.8 | 0 | 77.7418 | 646.3092 | 50.71% | 0 | 0 | 0 | 0% | 30.8
1828 | 0 | 0 | 0 | 7.2535 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0986 | 34.3 | 0 | 86.0986 | 563.4101 | 44.21% | 0 | 0 | 0 | 0% | 34.3
1829 | 0 | 0 | 0 | 5.0372 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1527 | 38.5 | 0 | 96.1527 | 468.5702 | 36.76% | 0 | 0 | 0 | 0% | 38.5
1830 | 0 | 0 | 0 | 6.4476 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0071 | 41.8 | 0 | 104.0071 | 364.2968 | 28.58% | 0 | 0 | 0 | 0% | 41.8
1831 | 72 | 24 | 16 | 8.0595 | 9 | 36.2389 | 0 | 14.546 | 0 | 0.87117 | 0 | 0 | 0.87117 | 0 | 0 | 0 | 106.4815 | 42.8288 | 0 | 106.4815 | 257.0605 | 20.17% | 0 | 0 | 0 | 0% | 43.7
1832 | 442 | 183 | 73 | 8.6639 | 11.2 | 222.4663 | 116.8979 | 0 | 88.1873 | 19.3101 | 0 | 0 | 19.3101 | 0 | 0 | 0 | 63.8943 | 24.6899 | 88.1873 | 63.8943 | 281.6779 | 22.1% | 0 | 0 | 0 | 0% | 44
1833 | 435 | 375 | 195 | 12.0892 | 13.6 | 218.9431 | 130.8012 | 0 | 98.8599 | 42.0746 | 0 | 0 | 42.0746 | 0 | 0 | 0 | 0 | 0 | 98.8599 | 0 | 374.8987 | 29.42% | 0 | 0 | 0 | 0% | 42.0746
1834 | 338 | 449 | 240 | 12.4922 | 14.2 | 170.1213 | 107.8892 | 0 | 77.135 | 50.9905 | 0 | 3.3953 | 47.5953 | 0 | 0 | 0 | 0 | 0 | 77.135 | 0 | 447.6338 | 35.12% | 2.6042 | 0 | 2.6323 | 5.265% | 44.2
1835 | 652 | 694 | 224 | 13.7011 | 15.6 | 328.1629 | 213.7359 | 0 | 175.5629 | 105.8 | 5.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 175.5629 | 0 | 613.1822 | 48.11% | 19.175 | 0 | 22.0143 | 44.03% | 44.2
1836 | 446 | 662 | 301 | 16.119 | 14.9 | 224.4796 | 147.5368 | 0 | 112.3638 | 102.5275 | 4.8637 | 25 | 72.6637 | 0 | 0 | 0 | 0 | 0 | 112.3638 | 0 | 719.1365 | 56.42% | 19.175 | 0 | 41.3963 | 82.79% | 42.8
1837 | 798 | 917 | 268 | 15.716 | 16.2 | 401.6473 | 261.6872 | 0 | 218.9481 | 108.3 | 22.2025 | 11.0975 | 75 | 0 | 0 | 0 | 0 | 0 | 218.9481 | 0 | 925.5953 | 72.62% | 8.5118 | 0 | 50 | 100% | 41.7
1838 | 208 | 492 | 322 | 15.716 | 15.5 | 104.69 | 66.466 | 0 | 36.2755 | 56.6503 | 7.9251 | 0 | 48.7251 | 0 | 0 | 0 | 0 | 0 | 36.2755 | 0 | 959.8016 | 75.31% | 0 | 0 | 50 | 100% | 40.8
1839 | 312 | 546 | 328 | 15.5145 | 15.6 | 157.035 | 94.0701 | 0 | 62.5702 | 73.3311 | 16.5156 | 0 | 56.8156 | 0 | 0 | 0 | 0 | 0 | 62.5702 | 0 | 1018.8026 | 79.94% | 0 | 0 | 50 | 100% | 40.3
1840 | 36 | 225 | 204 | 14.7085 | 14.3 | 18.1194 | 0 | 9.5765 | 0 | 19.6168 | 0 | 0 | 19.6168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.8026 | 79.94% | 0 | 20.4832 | 29.2988 | 58.6% | 40.1
1841 | 1 | 157 | 155 | 13.9026 | 13.2 | 0.50332 | 0 | 0.20436 | 0 | 12.5215 | 0 | 0 | 12.5215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.8026 | 79.94% | 0 | 25 | 4.0318 | 8.064% | 37.5215
1842 | 0 | 37 | 36 | 11.4848 | 12.1 | 0 | 0 | 0 | 0 | 2.2732 | 0 | 0 | 2.2732 | 0 | 0 | 0 | 97.5522 | 39.0365 | 0 | 97.5522 | 922.6053 | 72.39% | 0 | 3.9903 | 0 | 0% | 45.3
1843 | 0 | 1 | 1 | 11.2833 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.1631 | 44.3 | 0 | 110.1631 | 811.3908 | 63.66% | 0 | 0 | 0 | 0% | 44.3
1844 | 0 | 0 | 0 | 9.2684 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.6726 | 41.2 | 0 | 102.6726 | 709.008 | 55.63% | 0 | 0 | 0 | 0% | 41.2
1845 | 0 | 0 | 0 | 7.455 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7508 | 37.5 | 0 | 93.7508 | 617.1534 | 48.42% | 0 | 0 | 0 | 0% | 37.5
1846 | 0 | 0 | 0 | 5.6416 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4492 | 35.3 | 0 | 88.4492 | 531.4672 | 41.7% | 0 | 0 | 0 | 0% | 35.3
1847 | 0 | 0 | 0 | 5.6416 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6761 | 33.3 | 0 | 83.6761 | 451.523 | 35.43% | 0 | 0 | 0 | 0% | 33.3
1848 | 0 | 0 | 0 | 5.4401 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5616 | 32 | 0 | 80.5616 | 375.2622 | 29.44% | 0 | 0 | 0 | 0% | 32
1849 | 0 | 0 | 0 | 4.8357 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3507 | 31.5 | 0 | 79.3507 | 300.3915 | 23.57% | 0 | 0 | 0 | 0% | 31.5
1850 | 0 | 0 | 0 | 4.4327 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1102 | 31.4 | 0 | 79.1102 | 225.7798 | 17.72% | 0 | 0 | 0 | 0% | 31.4
1851 | 0 | 0 | 0 | 4.4327 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.4997 | 27.6416 | 0 | 70.4997 | 160.779 | 12.61% | 0 | 0 | 0 | 0% | 27.6416
1852 | 0 | 0 | 0 | 3.6268 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 0 | 0 | 0 | 0% | 0
1853 | 0 | 0 | 0 | 3.0223 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 0 | 0 | 0 | 0% | 0
1854 | 0 | 0 | 0 | 3.0223 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 0 | 0 | 0 | 0% | 0
1855 | 0 | 12 | 12 | 2.6193 | 10 | 0 | 0 | 0 | 0 | 0.2536 | 0 | 0 | 0.2536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 0 | 0 | 0 | 0% | 0.2536
1856 | 27 | 112 | 103 | 2.4178 | 10.5 | 13.5896 | 0 | 7.16 | 0 | 9.1252 | 0 | 0 | 9.1252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 0 | 0 | 0 | 0% | 9.1252
1857 | 15 | 213 | 203 | 4.2312 | 11.2 | 7.5498 | 0 | 4.5162 | 0 | 17.4486 | 0 | 0 | 17.4486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 0 | 0 | 0 | 0% | 17.4486
1858 | 0 | 280 | 276 | 2.4178 | 12.2 | 0 | 0 | 0 | 0 | 22.5007 | 0 | 0 | 22.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 0 | 0 | 0 | 0% | 22.5007
1859 | 6 | 398 | 387 | 4.2312 | 13.4 | 3.0199 | 0 | 1.9672 | 0 | 32.6506 | 0 | 0 | 32.6506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 0 | 0 | 0 | 0% | 32.6506
1860 | 69 | 499 | 434 | 7.455 | 14.6 | 34.7289 | 0 | 22.8305 | 0 | 48.6909 | 0 | 3.6454 | 45.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 2.796 | 0 | 2.8266 | 5.653% | 41.4
1861 | 140 | 499 | 375 | 11.2833 | 14.7 | 70.4644 | 0 | 45.9246 | 0 | 56.1171 | 0 | 8.0585 | 48.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.779 | 12.61% | 6.1809 | 0 | 9.0752 | 18.15% | 40
1862 | 296 | 581 | 347 | 8.0595 | 15.4 | 148.9819 | 94.6832 | 0 | 67.6336 | 80.6017 | 0 | 20.8009 | 59.8009 | 0 | 0 | 0 | 0 | 0 | 67.6336 | 0 | 224.8984 | 17.65% | 15.9543 | 0 | 25.204 | 50.41% | 39
1863 | 14 | 225 | 212 | 8.0595 | 15.4 | 7.0464 | 0 | 4.2308 | 0 | 17.6866 | 0 | 0 | 17.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224.8984 | 17.65% | 0 | 21.2134 | 3.7619 | 7.524% | 38.9
1864 | 1 | 125 | 122 | 11.4848 | 13.7 | 0.50332 | 0 | 0.26726 | 0 | 9.2131 | 0 | 0 | 9.2131 | 0 | 0 | 0 | 64.3895 | 24.7939 | 0 | 64.3895 | 165.561 | 12.99% | 0 | 3.7218 | 0 | 0% | 37.7287
1865 | 93 | 141 | 104 | 11.4848 | 12.7 | 46.8085 | 0 | 19.1716 | 0 | 12.9406 | 0 | 0 | 12.9406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 12.9406
1866 | 69 | 78 | 63 | 12.6937 | 11.7 | 34.7289 | 0 | 0 | 0 | 6.0279 | 0 | 0 | 6.0279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 6.0279
1867 | 0 | 2 | 2 | 10.2758 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1868 | 0 | 0 | 0 | 10.2758 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1869 | 0 | 0 | 0 | 8.6639 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1870 | 0 | 0 | 0 | 6.0446 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1871 | 0 | 0 | 0 | 6.0446 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1872 | 0 | 0 | 0 | 4.2312 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1873 | 0 | 0 | 0 | 5.2387 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1874 | 0 | 0 | 0 | 5.4401 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1875 | 0 | 0 | 0 | 4.2312 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1876 | 0 | 0 | 0 | 2.6193 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1877 | 0 | 0 | 0 | 1.8134 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1878 | 0 | 0 | 0 | 2.4178 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 0
1879 | 207 | 36 | 16 | 4.2312 | 6.3 | 104.1867 | 0 | 42.236 | 0 | 1.2586 | 0 | 0 | 1.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.561 | 12.99% | 0 | 0 | 0 | 0% | 1.2586
1880 | 682 | 223 | 50 | 5.4401 | 8.5 | 343.2625 | 181.3363 | 0 | 150.2445 | 24.438 | 0 | 0 | 24.438 | 0 | 0 | 0 | 0 | 0 | 150.2445 | 0 | 307.7296 | 24.14% | 0 | 0 | 0 | 0% | 24.438
1881 | 839 | 465 | 95 | 11.4848 | 10.7 | 422.2833 | 252.9261 | 0 | 213.237 | 65.9323 | 0 | 9.7662 | 56.1662 | 0 | 0 | 0 | 0 | 0 | 213.237 | 0 | 509.5048 | 39.98% | 7.4906 | 0 | 7.5733 | 15.15% | 46.4
1882 | 755 | 563 | 113 | 10.6788 | 11.9 | 380.0046 | 241.2807 | 0 | 203.0184 | 88.5076 | 0 | 21.1038 | 67.4038 | 0 | 0 | 0 | 0 | 0 | 203.0184 | 0 | 701.6107 | 55.05% | 16.1866 | 0 | 23.9384 | 47.88% | 46.3
1883 | 628 | 699 | 238 | 11.4848 | 12.8 | 316.0833 | 205.9387 | 0 | 169.6303 | 103.8 | 3.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 169.6303 | 0 | 862.1231 | 67.64% | 19.175 | 0 | 43.325 | 86.65% | 46.2
1884 | 708 | 828 | 263 | 12.8952 | 14.1 | 356.3487 | 234.3145 | 0 | 195.3179 | 105.4 | 21.7922 | 8.6078 | 75 | 0 | 0 | 0 | 0 | 0 | 195.3179 | 0 | 1046.9423 | 82.14% | 6.6022 | 0 | 50 | 100% | 44.6
1885 | 187 | 500 | 339 | 13.2981 | 13.2 | 94.1204 | 61.3617 | 0 | 33.3391 | 55.1124 | 5.7062 | 0 | 49.4062 | 0 | 0 | 0 | 0 | 0 | 33.3391 | 0 | 1078.4894 | 84.62% | 0 | 0 | 50 | 100% | 43.7
1886 | 555 | 780 | 346 | 16.3204 | 12.5 | 279.3412 | 177.7131 | 0 | 140.3049 | 107.1 | 32.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 140.3049 | 0 | 1211.2527 | 95.04% | 0 | 0 | 50 | 100% | 42.9
1887 | 548 | 680 | 305 | 14.3056 | 12.9 | 275.8179 | 165.9831 | 0 | 130.4171 | 106.9263 | 32.2632 | 0 | 74.6632 | 0 | 0 | 0 | 0 | 0 | 130.4171 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
1888 | 611 | 544 | 202 | 14.3056 | 13.4 | 307.5269 | 0 | 164.0618 | 0 | 78.4632 | 18.1816 | 0 | 60.2816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
1889 | 179 | 198 | 118 | 14.91 | 11.7 | 90.0938 | 0 | 37.2203 | 0 | 18.7704 | 0 | 0 | 18.7704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.728 | 49.46% | 43.7704
1890 | 103 | 77 | 55 | 12.2907 | 9.7 | 51.8417 | 0 | 0 | 0 | 5.8322 | 0 | 0 | 5.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.462 | 0 | 0% | 30.2941
1891 | 0 | 2 | 2 | 10.0743 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.0003 | 47.2 | 0 | 117.0003 | 1154.7897 | 90.61% | 0 | 0 | 0 | 0% | 47.2
1892 | 0 | 0 | 0 | 9.0669 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.83 | 43.4 | 0 | 107.83 | 1045.9873 | 82.07% | 0 | 0 | 0 | 0% | 43.4
1893 | 0 | 0 | 0 | 9.2684 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6953 | 39.2 | 0 | 97.6953 | 949.1428 | 74.47% | 0 | 0 | 0 | 0% | 39.2
1894 | 0 | 0 | 0 | 4.6342 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9272 | 36.8 | 0 | 91.9272 | 859.1429 | 67.41% | 0 | 0 | 0 | 0% | 36.8
1895 | 0 | 0 | 0 | 2.6193 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0765 | 34.8 | 0 | 87.0765 | 774.75 | 60.79% | 0 | 0 | 0 | 0% | 34.8
1896 | 0 | 0 | 0 | 3.8283 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7339 | 33.4 | 0 | 83.7339 | 694.4034 | 54.48% | 0 | 0 | 0 | 0% | 33.4
1897 | 0 | 0 | 0 | 2.0149 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2977 | 32.8 | 0 | 82.2977 | 615.7632 | 48.31% | 0 | 0 | 0 | 0% | 32.8
1898 | 0 | 0 | 0 | 3.0223 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7523 | 33 | 0 | 82.7523 | 536.5368 | 42.1% | 0 | 0 | 0 | 0% | 33
1899 | 0 | 0 | 0 | 8.0595 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1912 | 34 | 0 | 85.1912 | 454.4162 | 35.65% | 0 | 0 | 0 | 0% | 34
1900 | 0 | 0 | 0 | 10.2758 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.374 | 37.4 | 0 | 93.374 | 362.6185 | 28.45% | 0 | 0 | 0 | 0% | 37.4
1901 | 0 | 0 | 0 | 7.455 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9276 | 41.8 | 0 | 103.9276 | 258.2137 | 20.26% | 0 | 0 | 0 | 0% | 41.8
1902 | 0 | 0 | 0 | 8.4625 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1526 | 45.2 | 0 | 112.1526 | 143.9903 | 11.3% | 0 | 0 | 0 | 0% | 45.2
1903 | 192 | 36 | 16 | 7.858 | 8.1 | 96.6369 | 0 | 39.3658 | 0 | 1.292 | 0 | 0 | 1.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143.9903 | 11.3% | 0 | 0 | 0 | 0% | 1.292
1904 | 688 | 225 | 47 | 8.261 | 9.4 | 346.2824 | 183.4097 | 0 | 150.4127 | 24.431 | 0 | 0 | 24.431 | 0 | 0 | 0 | 0 | 0 | 150.4127 | 0 | 288.4223 | 22.63% | 0 | 0 | 0 | 0% | 24.431
1905 | 853 | 446 | 66 | 13.2981 | 10.5 | 429.3297 | 257.4694 | 0 | 216.3036 | 61.7125 | 0 | 7.6063 | 54.1063 | 0 | 0 | 0 | 0 | 0 | 216.3036 | 0 | 496.1251 | 38.93% | 5.834 | 0 | 5.8992 | 11.8% | 46.5
1906 | 791 | 591 | 114 | 13.4996 | 11.2 | 398.1241 | 252.9321 | 0 | 211.9862 | 94.8427 | 0 | 24.2713 | 70.5713 | 0 | 0 | 0 | 0 | 0 | 211.9862 | 0 | 699.6822 | 54.9% | 18.6161 | 0 | 24.7233 | 49.45% | 46.3
1907 | 271 | 437 | 240 | 12.0892 | 11.5 | 136.399 | 88.8834 | 0 | 59.9276 | 47.9138 | 1.0069 | 0 | 46.9069 | 0 | 0 | 0 | 0 | 0 | 59.9276 | 0 | 757.2269 | 59.41% | 0 | 0 | 24.7233 | 49.45% | 45.9
1908 | 232 | 540 | 347 | 12.8952 | 12.5 | 116.7696 | 76.7988 | 0 | 47.3668 | 66.9737 | 0 | 11.2868 | 55.6868 | 0 | 0 | 0 | 0 | 0 | 47.3668 | 0 | 802.7103 | 62.98% | 8.657 | 0 | 33.4771 | 66.95% | 44.4
1909 | 31 | 320 | 287 | 11.8877 | 12.5 | 15.6028 | 0 | 10.1755 | 0 | 27.6072 | 0 | 0 | 27.6072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.7103 | 62.98% | 0 | 15.9928 | 17.3082 | 34.62% | 43.6
1910 | 360 | 565 | 278 | 12.8952 | 13.3 | 181.1943 | 115.3914 | 0 | 84.163 | 76.8926 | 0 | 16.9963 | 59.8963 | 0 | 0 | 0 | 0 | 0 | 84.163 | 0 | 883.5268 | 69.32% | 13.0362 | 0 | 30.4906 | 60.98% | 42.9
1911 | 176 | 413 | 282 | 13.7011 | 13.2 | 88.5839 | 0 | 53.4303 | 0 | 40.1042 | 0 | 0 | 40.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883.5268 | 69.32% | 0 | 0 | 30.4906 | 60.98% | 40.1042
1912 | 737 | 563 | 159 | 11.8877 | 13.7 | 370.9449 | 198.8157 | 0 | 162.6772 | 86.8632 | 0 | 22.3316 | 64.5316 | 0 | 0 | 0 | 0 | 0 | 162.6772 | 0 | 1039.7356 | 81.58% | 17.1283 | 0 | 47.8111 | 95.62% | 42.2
1913 | 427 | 240 | 95 | 11.6862 | 12.9 | 214.9165 | 89.5514 | 0 | 60.7982 | 28.1757 | 0 | 0 | 28.1757 | 0 | 0 | 0 | 0 | 0 | 60.7982 | 0 | 1098.1163 | 86.16% | 0 | 16.6243 | 31.003 | 62.01% | 44.8
1914 | 423 | 126 | 47 | 12.4922 | 11.9 | 212.9033 | 0 | 0 | 0 | 10.6574 | 0 | 0 | 10.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1098.1163 | 86.16% | 0 | 25 | 5.7257 | 11.45% | 35.6574
1915 | 17 | 5 | 4 | 9.8729 | 10 | 8.5564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.1324 | 41.4367 | 0 | 103.1324 | 995.0683 | 78.07% | 0 | 5.6633 | 6.9389e-16 | 1.388e-15% | 47.1
1916 | 0 | 0 | 0 | 7.052 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0936 | 43.5 | 0 | 108.0936 | 886.1265 | 69.53% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 43.5
1917 | 0 | 0 | 0 | 5.6416 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7119 | 39.6 | 0 | 98.7119 | 788.2529 | 61.85% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 39.6
1918 | 0 | 0 | 0 | 5.6416 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9716 | 37.2 | 0 | 92.9716 | 697.2267 | 54.71% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 37.2
1919 | 0 | 0 | 0 | 7.455 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1614 | 34.8 | 0 | 87.1614 | 612.9465 | 48.09% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 34.8
1920 | 0 | 0 | 0 | 5.6416 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0499 | 33.5 | 0 | 84.0499 | 532.4297 | 41.78% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 33.5
1921 | 0 | 0 | 0 | 7.6565 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.568 | 32.9 | 0 | 82.568 | 453.5985 | 35.59% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 32.9
1922 | 0 | 0 | 0 | 3.8283 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3191 | 32.8 | 0 | 82.3191 | 375.0355 | 29.43% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 32.8
1923 | 0 | 0 | 0 | 1.2089 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4511 | 33.7 | 0 | 84.4511 | 293.8709 | 23.06% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 33.7
1924 | 0 | 0 | 0 | 2.4178 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.083 | 37.3 | 0 | 93.083 | 202.4393 | 15.88% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 37.3
1925 | 0 | 0 | 0 | 6.8506 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.6461 | 23.3837 | 0 | 60.6461 | 146.8912 | 11.53% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 23.3837
1926 | 0 | 0 | 0 | 5.6416 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.8912 | 11.53% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
1927 | 34 | 25 | 20 | 5.4401 | 7.7 | 17.1128 | 0 | 7.0044 | 0 | 0.94477 | 0 | 0 | 0.94477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.8912 | 11.53% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0.94477
1928 | 454 | 208 | 84 | 5.0372 | 8.5 | 228.5061 | 121.3407 | 0 | 94.4144 | 20.96 | 0 | 0 | 20.96 | 0 | 0 | 0 | 0 | 0 | 94.4144 | 0 | 236.9398 | 18.59% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 20.96
1929 | 689 | 451 | 137 | 7.858 | 11.2 | 346.7857 | 208.2256 | 0 | 173.948 | 56.7497 | 0 | 5.0749 | 51.6749 | 0 | 0 | 0 | 0 | 0 | 173.948 | 0 | 402.8444 | 31.61% | 3.8924 | 0 | 3.9366 | 7.873% | 46.6
1930 | 721 | 580 | 134 | 9.8729 | 12.3 | 362.8918 | 230.6805 | 0 | 193.6992 | 87.7855 | 0 | 20.7428 | 67.0428 | 0 | 0 | 0 | 0 | 0 | 193.6992 | 0 | 587.5868 | 46.1% | 15.9097 | 0 | 20.0268 | 40.05% | 46.3
1931 | 883 | 779 | 130 | 11.8877 | 13.5 | 444.4293 | 289.657 | 0 | 247.5866 | 104.3 | 4.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 247.5866 | 0 | 823.7249 | 64.63% | 19.175 | 0 | 39.4195 | 78.84% | 45.7
1932 | 903 | 862 | 134 | 12.0892 | 14.4 | 454.4956 | 298.9885 | 0 | 256.1956 | 105.9 | 17.2601 | 13.6399 | 75 | 0 | 0 | 0 | 0 | 0 | 256.1956 | 0 | 1068.0739 | 83.8% | 10.4618 | 0 | 50 | 100% | 44.1
1933 | 892 | 883 | 149 | 12.2907 | 15.3 | 448.9591 | 292.8853 | 0 | 250.4646 | 107 | 32 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 250.4646 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43
1934 | 855 | 844 | 173 | 11.0818 | 16.4 | 430.3364 | 0 | 274.3349 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42
1935 | 743 | 681 | 168 | 11.6862 | 16.6 | 373.9648 | 0 | 226.0762 | 0 | 108.5 | 33.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.5
1936 | 693 | 549 | 164 | 13.0966 | 16.3 | 348.7989 | 0 | 187.8117 | 0 | 82.252 | 20.626 | 0 | 61.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41
1937 | 378 | 282 | 130 | 12.6937 | 15.5 | 190.254 | 0 | 79.9506 | 0 | 28.965 | 0 | 0 | 28.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 14.435 | 35.4034 | 70.81% | 43.4
1938 | 198 | 99 | 59 | 11.8877 | 13.6 | 99.6568 | 0 | 0 | 0 | 7.707 | 0 | 0 | 7.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.1227 | 20.25% | 32.707
1939 | 1 | 5 | 4 | 8.261 | 11.8 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0086 | 35.0888 | 0 | 88.0086 | 1189.4785 | 93.33% | 0 | 10.0112 | 0 | 0% | 45.1
1940 | 0 | 0 | 0 | 6.0446 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.0927 | 42.2 | 0 | 105.0927 | 1084.2953 | 85.08% | 0 | 0 | 0 | 0% | 42.2
1941 | 0 | 0 | 0 | 7.2535 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3595 | 39 | 0 | 97.3595 | 988.1923 | 77.54% | 0 | 0 | 0 | 0% | 39
1942 | 0 | 0 | 0 | 6.6491 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2866 | 36.9 | 0 | 92.2866 | 898.0548 | 70.46% | 0 | 0 | 0 | 0% | 36.9
1943 | 0 | 0 | 0 | 5.6416 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.744 | 34.6 | 0 | 86.744 | 814.3911 | 63.9% | 0 | 0 | 0 | 0% | 34.6
1944 | 0 | 0 | 0 | 5.0372 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.139 | 32.7 | 0 | 82.139 | 736.1841 | 57.76% | 0 | 0 | 0 | 0% | 32.7
1945 | 0 | 0 | 0 | 4.2312 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4583 | 32 | 0 | 80.4583 | 659.9528 | 51.78% | 0 | 0 | 0 | 0% | 32
1946 | 0 | 0 | 0 | 2.0149 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0152 | 31.4 | 0 | 79.0152 | 585.3972 | 45.93% | 0 | 0 | 0 | 0% | 31.4
1947 | 0 | 0 | 0 | 1.8134 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7745 | 31.3 | 0 | 78.7745 | 511.1082 | 40.1% | 0 | 0 | 0 | 0% | 31.3
1948 | 0 | 0 | 0 | 1.4104 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1532 | 32.3 | 0 | 81.1532 | 433.9862 | 34.05% | 0 | 0 | 0 | 0% | 32.3
1949 | 0 | 0 | 0 | 2.0149 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0409 | 33.1 | 0 | 83.0409 | 354.5632 | 27.82% | 0 | 0 | 0 | 0% | 33.1
1950 | 0 | 0 | 0 | 4.2312 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2272 | 36.1 | 0 | 90.2272 | 266.5496 | 20.91% | 0 | 0 | 0 | 0% | 36.1
1951 | 127 | 36 | 21 | 2.0149 | 7.3 | 63.9213 | 0 | 26.2872 | 0 | 1.4066 | 0 | 0 | 1.4066 | 0 | 0 | 0 | 94.7729 | 37.9934 | 0 | 94.7729 | 173.1428 | 13.59% | 0 | 0 | 0 | 0% | 39.4
1952 | 549 | 218 | 68 | 5.4401 | 10.5 | 276.3212 | 147.1039 | 0 | 118.3476 | 22.4288 | 0 | 0 | 22.4288 | 0 | 0 | 0 | 0 | 0 | 118.3476 | 0 | 285.2791 | 22.38% | 0 | 0 | 0 | 0% | 22.4288
1953 | 659 | 405 | 99 | 12.0892 | 13 | 331.6862 | 199.4032 | 0 | 163.0872 | 52.2438 | 0 | 5.5219 | 46.7219 | 0 | 0 | 0 | 0 | 0 | 163.0872 | 0 | 439.8069 | 34.51% | 4.2353 | 0 | 4.284 | 8.568% | 41.2
1954 | 435 | 522 | 257 | 13.0966 | 14.1 | 218.9431 | 139.2545 | 0 | 106.2171 | 71.5922 | 0 | 15.4961 | 56.0961 | 0 | 0 | 0 | 0 | 0 | 106.2171 | 0 | 540.4494 | 42.4% | 11.8855 | 0 | 16.3061 | 32.61% | 40.6
1955 | 313 | 564 | 321 | 13.0966 | 14.5 | 157.5383 | 102.6925 | 0 | 71.862 | 74.8122 | 0 | 17.1561 | 57.6561 | 0 | 0 | 0 | 0 | 0 | 71.862 | 0 | 608.5398 | 47.75% | 13.1587 | 0 | 29.6161 | 59.23% | 40.5
1956 | 377 | 589 | 279 | 14.7085 | 15 | 189.7507 | 124.8558 | 0 | 91.8181 | 88.3346 | 0 | 24.4173 | 63.9173 | 0 | 0 | 0 | 0 | 0 | 91.8181 | 0 | 695.539 | 54.57% | 18.7281 | 0 | 48.5594 | 97.12% | 39.5
1957 | 76 | 468 | 397 | 14.91 | 12.1 | 38.2521 | 0 | 24.9623 | 0 | 47.6568 | 5.0284 | 0 | 42.6284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 695.539 | 54.57% | 0 | 0 | 48.5594 | 97.12% | 37.6
1958 | 307 | 709 | 451 | 12.2907 | 13.4 | 154.5184 | 98.6044 | 0 | 68.5465 | 105.4707 | 34.5353 | 0 | 70.9353 | 0 | 0 | 0 | 0 | 0 | 68.5465 | 0 | 760.488 | 59.67% | 0 | 0 | 48.5594 | 97.12% | 36.4
1959 | 13 | 269 | 255 | 10.8803 | 12.6 | 6.5431 | 0 | 3.96 | 0 | 21.5162 | 0 | 0 | 21.5162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.488 | 59.67% | 0 | 14.1838 | 34.2148 | 68.43% | 35.7
1960 | 4 | 134 | 130 | 10.6788 | 12.6 | 2.0133 | 0 | 1.089 | 0 | 10.0923 | 0 | 0 | 10.0923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.488 | 59.67% | 0 | 25 | 8.9306 | 17.86% | 35.0923
1961 | 0 | 45 | 45 | 10.0743 | 11.6 | 0 | 0 | 0 | 0 | 3.0269 | 0 | 0 | 3.0269 | 0 | 0 | 0 | 66.791 | 25.9421 | 0 | 66.791 | 699.1496 | 54.86% | 0 | 8.8309 | 0 | 0% | 37.8
1962 | 0 | 54 | 53 | 9.2684 | 11.7 | 0 | 0 | 0 | 0 | 3.657 | 0 | 0 | 3.657 | 0 | 0 | 0 | 92.7225 | 37.043 | 0 | 92.7225 | 608.5855 | 47.75% | 0 | 0 | 0 | 0% | 40.7
1963 | 0 | 3 | 3 | 8.261 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5059 | 40.7 | 0 | 101.5059 | 507.5733 | 39.82% | 0 | 0 | 0 | 0% | 40.7
1964 | 0 | 0 | 0 | 7.2535 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4346 | 38.6 | 0 | 96.4346 | 412.5427 | 32.37% | 0 | 0 | 0 | 0% | 38.6
1965 | 0 | 0 | 0 | 7.858 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1599 | 36 | 0 | 90.1599 | 324.8588 | 25.49% | 0 | 0 | 0 | 0% | 36
1966 | 0 | 0 | 0 | 6.2461 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6559 | 33.7 | 0 | 84.6559 | 243.7198 | 19.12% | 0 | 0 | 0 | 0% | 33.7
1967 | 0 | 0 | 0 | 5.0372 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6737 | 30.4129 | 0 | 76.6737 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 30.4129
1968 | 0 | 0 | 0 | 3.8283 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1969 | 0 | 0 | 0 | 7.052 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1970 | 0 | 0 | 0 | 7.2535 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1971 | 0 | 0 | 0 | 7.455 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1972 | 0 | 0 | 0 | 6.2461 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1973 | 0 | 0 | 0 | 5.8431 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1974 | 0 | 0 | 0 | 5.4401 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1975 | 9 | 30 | 29 | 6.6491 | 10.4 | 4.5299 | 0 | 1.8715 | 0 | 1.4415 | 0 | 0 | 1.4415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 1.4415
1976 | 50 | 125 | 113 | 9.4699 | 12.6 | 25.1659 | 0 | 13.431 | 0 | 10.542 | 0 | 0 | 10.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 10.542
1977 | 0 | 118 | 116 | 11.2833 | 13 | 0 | 0 | 0 | 0 | 8.735 | 0 | 0 | 8.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 8.735
1978 | 30 | 243 | 218 | 10.8803 | 13.9 | 15.0995 | 0 | 9.6084 | 0 | 20.3799 | 0 | 0 | 20.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 20.3799
1979 | 8 | 292 | 280 | 11.0818 | 15 | 4.0265 | 0 | 2.6252 | 0 | 23.0383 | 0 | 0 | 23.0383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 23.0383
1980 | 83 | 537 | 458 | 12.2907 | 16.2 | 41.7753 | 0 | 27.4945 | 0 | 60.5269 | 0 | 12.1634 | 48.3634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 9.3294 | 0 | 9.4379 | 18.88% | 36.2
1981 | 2 | 387 | 377 | 12.2907 | 16.5 | 1.0066 | 0 | 0.65711 | 0 | 30.8395 | 0 | 0 | 30.8395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 3.6605 | 5.7354 | 11.47% | 34.5
1982 | 1 | 181 | 178 | 14.1041 | 16 | 0.50332 | 0 | 0.3215 | 0 | 13.5673 | 0 | 0 | 13.5673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 5.6703 | 0 | 0% | 19.2377
1983 | 4 | 267 | 260 | 12.8952 | 16 | 2.0133 | 0 | 1.2196 | 0 | 20.9666 | 0 | 0 | 20.9666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 20.9666
1984 | 16 | 256 | 244 | 12.0892 | 16.2 | 8.0531 | 0 | 4.3761 | 0 | 20.6549 | 0 | 0 | 20.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 20.6549
1985 | 3 | 143 | 140 | 11.2833 | 15.7 | 1.51 | 0 | 0.64523 | 0 | 10.9745 | 0 | 0 | 10.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 10.9745
1986 | 0 | 52 | 51 | 9.8729 | 14.8 | 0 | 0 | 0 | 0 | 3.4454 | 0 | 0 | 3.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 3.4454
1987 | 0 | 4 | 4 | 7.6565 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1988 | 0 | 0 | 0 | 6.6491 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1989 | 0 | 0 | 0 | 6.4476 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1990 | 0 | 0 | 0 | 3.4253 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1991 | 0 | 0 | 0 | 1.6119 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1992 | 0 | 0 | 0 | 2.8208 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1993 | 0 | 0 | 0 | 4.6342 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1994 | 0 | 0 | 0 | 3.2238 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1995 | 0 | 0 | 0 | 2.8208 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1996 | 0 | 0 | 0 | 3.2238 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1997 | 0 | 0 | 0 | 3.8283 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1998 | 0 | 0 | 0 | 3.4253 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 0
1999 | 177 | 57 | 36 | 3.8283 | 10.5 | 89.0872 | 0 | 36.9762 | 0 | 2.6968 | 0 | 0 | 2.6968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.8537 | 13.48% | 0 | 0 | 0 | 0% | 2.6968
2000 | 590 | 236 | 70 | 5.2387 | 13.4 | 296.9573 | 158.8763 | 0 | 129.375 | 23.6768 | 0 | 0 | 23.6768 | 0 | 0 | 0 | 0 | 0 | 129.375 | 0 | 294.498 | 23.11% | 0 | 0 | 0 | 0% | 23.6768
2001 | 770 | 447 | 87 | 10.2758 | 16.3 | 387.5544 | 233.5516 | 0 | 196.2684 | 57.0789 | 0 | 6.1895 | 50.8895 | 0 | 0 | 0 | 0 | 0 | 196.2684 | 0 | 480.5556 | 37.71% | 4.7473 | 0 | 4.8028 | 9.606% | 44.7
2002 | 856 | 637 | 98 | 12.4922 | 17.5 | 430.8397 | 274.2853 | 0 | 232.775 | 99.6841 | 2.542 | 25 | 72.142 | 0 | 0 | 0 | 0 | 0 | 232.775 | 0 | 701.2205 | 55.02% | 19.175 | 0 | 24.2021 | 48.4% | 44.6
2003 | 903 | 767 | 55 | 12.0892 | 18.3 | 454.4956 | 296.3612 | 0 | 253.886 | 105.5 | 5.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 253.886 | 0 | 941.8982 | 73.9% | 19.175 | 0 | 43.6014 | 87.2% | 44.5
2004 | 924 | 741 | 75 | 10.8803 | 19 | 465.0653 | 306.1545 | 0 | 263.7135 | 106.7 | 23.4541 | 8.2459 | 75 | 0 | 0 | 0 | 0 | 0 | 263.7135 | 0 | 1191.8922 | 93.52% | 6.3246 | 0 | 50 | 100% | 43.3
2005 | 929 | 871 | 108 | 12.2907 | 20.1 | 467.5819 | 231.1764 | 74.1497 | 198.4569 | 107.7 | 32.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 198.4569 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
2006 | 912 | 824 | 111 | 13.2981 | 20.2 | 459.0255 | 0 | 293.287 | 0 | 108.3 | 33.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
2007 | 876 | 711 | 105 | 14.91 | 20.2 | 440.906 | 0 | 267.3483 | 0 | 108.9 | 33.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
2008 | 820 | 551 | 95 | 15.5145 | 19.6 | 412.7203 | 0 | 225.1435 | 0 | 84.1276 | 21.7138 | 0 | 62.4138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.7
2009 | 696 | 349 | 79 | 14.5071 | 18.7 | 350.3089 | 0 | 150.9329 | 0 | 37.7901 | 0 | 0 | 37.7901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.3099 | 44.6288 | 89.26% | 43.1
2010 | 398 | 135 | 55 | 14.5071 | 16.6 | 200.3203 | 0 | 0 | 0 | 10.4968 | 0 | 0 | 10.4968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 19.34 | 38.68% | 35.4968
2011 | 26 | 8 | 6 | 10.2758 | 14.5 | 13.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.4113 | 26.0807 | 0 | 67.4113 | 1212.4765 | 95.13% | 0 | 19.1193 | 0 | 0% | 45.2
2012 | 0 | 0 | 0 | 6.8506 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.7282 | 41.6 | 0 | 103.7282 | 1108.7425 | 86.99% | 0 | 0 | 0 | 0% | 41.6
2013 | 0 | 0 | 0 | 7.6565 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7601 | 37.9 | 0 | 94.7601 | 1015.56 | 79.68% | 0 | 0 | 0 | 0% | 37.9
2014 | 0 | 0 | 0 | 6.8506 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6879 | 35.4 | 0 | 88.6879 | 929.424 | 72.92% | 0 | 0 | 0 | 0% | 35.4
2015 | 0 | 0 | 0 | 3.8283 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1535 | 33.5 | 0 | 84.1535 | 848.7514 | 66.59% | 0 | 0 | 0 | 0% | 33.5
2016 | 0 | 0 | 0 | 3.2238 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2635 | 32.3 | 0 | 81.2635 | 771.5003 | 60.53% | 0 | 0 | 0 | 0% | 32.3
2017 | 0 | 0 | 0 | 4.6342 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0616 | 31.8 | 0 | 80.0616 | 695.654 | 54.58% | 0 | 0 | 0 | 0% | 31.8
2018 | 0 | 0 | 0 | 6.8506 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3415 | 31.9 | 0 | 80.3415 | 619.5126 | 48.61% | 0 | 0 | 0 | 0% | 31.9
2019 | 0 | 0 | 0 | 7.6565 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7309 | 32.9 | 0 | 82.7309 | 540.5116 | 42.41% | 0 | 0 | 0 | 0% | 32.9
2020 | 0 | 0 | 0 | 6.0446 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8457 | 36.3 | 0 | 90.8457 | 451.7633 | 35.45% | 0 | 0 | 0 | 0% | 36.3
2021 | 0 | 0 | 0 | 5.8431 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.8749 | 40.5 | 0 | 100.8749 | 350.9895 | 27.54% | 0 | 0 | 0 | 0% | 40.5
2022 | 0 | 0 | 0 | 6.6491 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3336 | 43.6 | 0 | 108.3336 | 241.3418 | 18.94% | 0 | 0 | 0 | 0% | 43.6
2023 | 38 | 52 | 46 | 6.2461 | 10.1 | 19.1261 | 0 | 7.9744 | 0 | 2.8108 | 0 | 0 | 2.8108 | 0 | 0 | 0 | 104.2321 | 41.8892 | 0 | 104.2321 | 136.5607 | 10.71% | 0 | 0 | 0 | 0% | 44.7
2024 | 233 | 193 | 122 | 9.0669 | 13.6 | 117.273 | 62.8952 | 0 | 37.2208 | 17.4108 | 0 | 0 | 17.4108 | 0 | 0 | 0 | 0 | 0 | 37.2208 | 0 | 171.9932 | 13.49% | 0 | 0 | 0 | 0% | 17.4108
2025 | 275 | 323 | 200 | 13.9026 | 16.1 | 138.4123 | 83.4603 | 0 | 53.4908 | 33.3576 | 0 | 0 | 33.3576 | 0 | 0 | 0 | 0 | 0 | 53.4908 | 0 | 222.9141 | 17.49% | 0 | 0 | 0 | 0% | 33.3576
2026 | 69 | 348 | 301 | 15.313 | 16 | 34.7289 | 0 | 22.1195 | 0 | 30.9026 | 0 | 0 | 30.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222.9141 | 17.49% | 0 | 0 | 0 | 0% | 30.9026
2027 | 312 | 654 | 412 | 16.3204 | 16.6 | 157.035 | 102.4133 | 0 | 69.7524 | 86.3376 | 0 | 20.7688 | 65.5688 | 0 | 0 | 0 | 0 | 0 | 69.7524 | 0 | 289.3153 | 22.7% | 15.9297 | 0 | 16.1183 | 32.24% | 44.8
2028 | 377 | 754 | 439 | 19.7457 | 18.1 | 189.7507 | 124.9427 | 0 | 89.1495 | 106.6 | 6.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 89.1495 | 0 | 374.1818 | 29.36% | 19.175 | 0 | 35.5204 | 71.04% | 43.4
2029 | 565 | 906 | 432 | 21.5591 | 18.1 | 284.3743 | 185.7526 | 0 | 144.9531 | 107.5 | 13.8428 | 18.6572 | 75 | 0 | 0 | 0 | 0 | 0 | 144.9531 | 0 | 512.1707 | 40.19% | 14.3101 | 0 | 50 | 100% | 42.5
2030 | 437 | 746 | 398 | 19.5442 | 17.5 | 219.9497 | 140.5704 | 0 | 103.8558 | 108.1 | 33.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 103.8558 | 0 | 611.0369 | 47.94% | 0 | 0 | 50 | 100% | 41.9
2031 | 479 | 738 | 396 | 19.9472 | 16.9 | 241.089 | 146.325 | 0 | 109.179 | 108.6 | 33.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 109.179 | 0 | 714.9705 | 56.1% | 0 | 0 | 50 | 100% | 41.4
2032 | 191 | 428 | 312 | 18.5368 | 15.8 | 96.1336 | 0 | 52.5633 | 0 | 40.5093 | 0 | 0 | 40.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.9705 | 56.1% | 0 | 0 | 50 | 100% | 40.5093
2033 | 12 | 148 | 142 | 18.1338 | 14.1 | 6.0398 | 0 | 2.6236 | 0 | 11.5854 | 0 | 0 | 11.5854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.9705 | 56.1% | 0 | 25 | 24.7078 | 49.42% | 36.5854
2034 | 0 | 70 | 69 | 17.9323 | 13.2 | 0 | 0 | 0 | 0 | 4.9461 | 0 | 0 | 4.9461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.9705 | 56.1% | 0 | 24.4224 | 0 | 0% | 29.3685
2035 | 0 | 3 | 3 | 16.9249 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.6102 | 45.7 | 0 | 113.6102 | 599.6376 | 47.05% | 0 | 0 | 0 | 0% | 45.7
2036 | 0 | 0 | 0 | 15.313 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2106 | 41.8 | 0 | 104.2106 | 495.4711 | 38.88% | 0 | 0 | 0 | 0% | 41.8
2037 | 0 | 0 | 0 | 14.7085 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0716 | 38 | 0 | 95.0716 | 402.1157 | 31.55% | 0 | 0 | 0 | 0% | 38
2038 | 0 | 0 | 0 | 11.2833 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4349 | 35.7 | 0 | 89.4349 | 315.2352 | 24.73% | 0 | 0 | 0 | 0% | 35.7
2039 | 0 | 0 | 0 | 13.7011 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.624 | 33.7 | 0 | 84.624 | 234.0617 | 18.36% | 0 | 0 | 0 | 0% | 33.7
2040 | 0 | 0 | 0 | 15.313 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7155 | 32.5 | 0 | 81.7155 | 156.2976 | 12.26% | 0 | 0 | 0 | 0% | 32.5
2041 | 0 | 0 | 0 | 16.3204 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.6809 | 21.1685 | 0 | 55.6809 | 105.518 | 8.279% | 0 | 0 | 0 | 0% | 21.1685
2042 | 0 | 0 | 0 | 15.9175 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.518 | 8.279% | 0 | 0 | 0 | 0% | 0
2043 | 0 | 0 | 0 | 13.4996 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.518 | 8.279% | 0 | 0 | 0 | 0% | 0
2044 | 0 | 0 | 0 | 15.1115 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.518 | 8.279% | 0 | 0 | 0 | 0% | 0
2045 | 0 | 0 | 0 | 13.4996 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.518 | 8.279% | 0 | 0 | 0 | 0% | 0
2046 | 0 | 0 | 0 | 12.8952 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.518 | 8.279% | 0 | 0 | 0 | 0% | 0
2047 | 210 | 51 | 24 | 14.1041 | 9.3 | 105.6967 | 0 | 44.266 | 0 | 1.9864 | 0 | 0 | 1.9864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.518 | 8.279% | 0 | 0 | 0 | 0% | 1.9864
2048 | 659 | 251 | 59 | 15.9175 | 10.6 | 331.6862 | 178.3147 | 0 | 141.0157 | 25.2602 | 0 | 0 | 25.2602 | 0 | 0 | 0 | 0 | 0 | 141.0157 | 0 | 239.9958 | 18.83% | 0 | 0 | 0 | 0% | 25.2602
2049 | 862 | 477 | 71 | 16.7234 | 12 | 433.8596 | 261.6843 | 0 | 218.1922 | 65.4633 | 0 | 10.1316 | 55.3316 | 0 | 0 | 0 | 0 | 0 | 218.1922 | 0 | 448.0719 | 35.16% | 7.771 | 0 | 7.8641 | 15.73% | 45.2
2050 | 927 | 665 | 83 | 15.716 | 13.2 | 466.5752 | 297.2516 | 0 | 252.3166 | 104.8 | 4.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 252.3166 | 0 | 688.6902 | 54.04% | 19.175 | 0 | 27.2689 | 54.54% | 45.2
2051 | 961 | 805 | 90 | 15.9175 | 14.5 | 483.688 | 315.4949 | 0 | 269.1581 | 105 | 5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 269.1581 | 0 | 945.3691 | 74.18% | 19.175 | 0 | 46.6737 | 93.35% | 45
2052 | 976 | 885 | 92 | 16.7234 | 15.2 | 491.2378 | 323.5343 | 0 | 276.2172 | 106.4 | 27.1146 | 4.2854 | 75 | 0 | 0 | 0 | 0 | 0 | 276.2172 | 0 | 1208.7799 | 94.84% | 3.2869 | 0 | 50 | 100% | 43.6
2053 | 995 | 911 | 88 | 18.1338 | 16.3 | 500.8008 | 137.9921 | 189.2336 | 117.6106 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 117.6106 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
2054 | 959 | 860 | 103 | 19.3427 | 16.3 | 482.6814 | 0 | 308.5642 | 0 | 108.3 | 33.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
2055 | 898 | 752 | 124 | 17.7308 | 15.9 | 451.979 | 0 | 274.5792 | 0 | 108.8 | 33.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
2056 | 838 | 576 | 104 | 16.5219 | 15.6 | 421.78 | 0 | 231.1485 | 0 | 89.1357 | 24.1179 | 0 | 65.0179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.9
2057 | 736 | 367 | 78 | 16.9249 | 14.6 | 370.4416 | 0 | 162.2161 | 0 | 39.7252 | 0 | 0 | 39.7252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 3.5748 | 46.3829 | 92.77% | 43.3
2058 | 495 | 151 | 48 | 15.1115 | 13.3 | 249.1421 | 0 | 0 | 0 | 11.2622 | 0 | 0 | 11.2622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 21.0868 | 42.17% | 36.2622
2059 | 45 | 10 | 7 | 14.1041 | 11.4 | 22.6493 | 0 | 0 | 0 | 0.0055788 | 0 | 0 | 0.0055788 | 0 | 0 | 0 | 64.0647 | 24.7541 | 0 | 64.0647 | 1215.7873 | 95.39% | 0 | 20.8403 | 0 | 0% | 45.6
2060 | 0 | 0 | 0 | 10.4773 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.77 | 42.1 | 0 | 104.77 | 1110.8457 | 87.16% | 0 | 0 | 0 | 0% | 42.1
2061 | 0 | 0 | 0 | 6.8506 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1427 | 38.1 | 0 | 95.1427 | 1017.2804 | 79.82% | 0 | 0 | 0 | 0% | 38.1
2062 | 0 | 0 | 0 | 3.6268 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8092 | 35.9 | 0 | 89.8092 | 929.9238 | 72.96% | 0 | 0 | 0 | 0% | 35.9
2063 | 0 | 0 | 0 | 3.4253 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4698 | 34.1 | 0 | 85.4698 | 847.696 | 66.51% | 0 | 0 | 0 | 0% | 34.1
2064 | 0 | 0 | 0 | 3.6268 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3334 | 32.8 | 0 | 82.3334 | 769.1742 | 60.35% | 0 | 0 | 0 | 0% | 32.8
2065 | 0 | 0 | 0 | 2.6193 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8591 | 32.2 | 0 | 80.8591 | 692.3452 | 54.32% | 0 | 0 | 0 | 0% | 32.2
2066 | 0 | 0 | 0 | 4.6342 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8948 | 32.2 | 0 | 80.8948 | 615.5035 | 48.29% | 0 | 0 | 0 | 0% | 32.2
2067 | 0 | 0 | 0 | 5.0372 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0472 | 33.1 | 0 | 83.0472 | 536.085 | 42.06% | 0 | 0 | 0 | 0% | 33.1
2068 | 0 | 0 | 0 | 4.0297 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1828 | 36.5 | 0 | 91.1828 | 446.9545 | 35.07% | 0 | 0 | 0 | 0% | 36.5
2069 | 0 | 0 | 0 | 2.2164 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0173 | 40.6 | 0 | 101.0173 | 346.1023 | 27.16% | 0 | 0 | 0 | 0% | 40.6
2070 | 0 | 0 | 0 | 1.0074 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.6848 | 43.8 | 0 | 108.6848 | 236.1018 | 18.52% | 0 | 0 | 0 | 0% | 43.8
2071 | 323 | 61 | 21 | 2.0149 | 5.7 | 162.5715 | 68.3859 | 0 | 45.606 | 2.0058 | 0 | 0 | 2.0058 | 0 | 0 | 0 | 106.2945 | 42.7942 | 45.606 | 106.2945 | 172.3364 | 13.52% | 0 | 0 | 0 | 0% | 44.8
2072 | 745 | 266 | 48 | 1.0074 | 9.7 | 374.9715 | 202.0614 | 0 | 171.4507 | 26.2983 | 0 | 0 | 26.2983 | 0 | 0 | 0 | 0 | 0 | 171.4507 | 0 | 335.8472 | 26.35% | 0 | 0 | 0 | 0% | 26.2983
2073 | 893 | 485 | 61 | 2.8208 | 12.2 | 449.4624 | 271.1703 | 0 | 235.2259 | 63.5091 | 0 | 9.2546 | 54.2546 | 0 | 0 | 0 | 0 | 0 | 235.2259 | 0 | 560.1797 | 43.95% | 7.0983 | 0 | 7.1843 | 14.37% | 45
2074 | 965 | 676 | 68 | 9.8729 | 14.5 | 485.7013 | 309.4037 | 0 | 267.2373 | 105 | 5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 267.2373 | 0 | 815.0411 | 63.95% | 19.175 | 0 | 26.5919 | 53.18% | 45
2075 | 983 | 812 | 79 | 11.0818 | 15.4 | 494.761 | 322.7668 | 0 | 278.9633 | 105.1 | 5.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 278.9633 | 0 | 1081.0854 | 84.82% | 19.175 | 0 | 45.9995 | 92% | 44.9
2076 | 983 | 890 | 89 | 13.0966 | 15.7 | 494.761 | 272.0305 | 53.9001 | 234.2589 | 106.6 | 26.4468 | 5.1532 | 75 | 0 | 0 | 0 | 0 | 0 | 234.2589 | 0 | 1274.5104 | 100% | 3.9525 | 0 | 50 | 100% | 43.4
2077 | 993 | 910 | 86 | 12.0892 | 16.2 | 499.7942 | 0 | 326.6716 | 0 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
2078 | 988 | 862 | 82 | 13.9026 | 16.2 | 497.2776 | 0 | 317.9788 | 0 | 108.2 | 33.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
2079 | 965 | 751 | 77 | 14.7085 | 15.9 | 485.7013 | 0 | 295.3413 | 0 | 108.8 | 33.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
2080 | 900 | 582 | 74 | 14.91 | 15.7 | 452.9856 | 0 | 248.8181 | 0 | 90.1935 | 24.7467 | 0 | 65.4467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.7
2081 | 808 | 378 | 61 | 15.716 | 14.8 | 406.6804 | 0 | 179.5098 | 0 | 40.9567 | 0 | 0 | 40.9567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.9567
2082 | 580 | 160 | 40 | 15.313 | 13.2 | 291.9241 | 0 | 0 | 0 | 11.7082 | 0 | 0 | 11.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.7006 | 49.4% | 36.7082
2083 | 70 | 11 | 6 | 11.6862 | 11.2 | 35.2322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.4057 | 20.9918 | 0 | 55.4057 | 1224.146 | 96.05% | 0 | 24.4082 | 2.7756e-15 | 5.551e-15% | 45.4
2084 | 0 | 0 | 0 | 7.2535 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5293 | 42 | 0 | 104.5293 | 1119.5503 | 87.84% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42
2085 | 0 | 0 | 0 | 5.8431 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3646 | 38.2 | 0 | 95.3646 | 1025.7544 | 80.48% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38.2
2086 | 0 | 0 | 0 | 6.2461 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5171 | 36.2 | 0 | 90.5171 | 937.6245 | 73.57% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.2
2087 | 0 | 0 | 0 | 4.6342 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6728 | 34.2 | 0 | 85.6728 | 855.1424 | 67.1% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.2
2088 | 0 | 0 | 0 | 4.2312 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.568 | 32.9 | 0 | 82.568 | 776.3801 | 60.92% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.9
2089 | 0 | 0 | 0 | 1.6119 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8184 | 32.6 | 0 | 81.8184 | 698.4601 | 54.8% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.6
2090 | 0 | 0 | 0 | 2.8208 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3556 | 32.4 | 0 | 81.3556 | 621.0953 | 48.73% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.4
2091 | 0 | 0 | 0 | 2.0149 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4947 | 33.3 | 0 | 83.4947 | 541.1493 | 42.46% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.3
2092 | 0 | 0 | 0 | 3.8283 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6519 | 36.7 | 0 | 91.6519 | 451.5028 | 35.43% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.7
2093 | 0 | 0 | 0 | 5.2387 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4991 | 40.8 | 0 | 101.4991 | 350.1467 | 27.47% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 40.8
2094 | 0 | 0 | 0 | 7.052 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7559 | 43.8 | 0 | 108.7559 | 240.2126 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.8
2095 | 54 | 56 | 48 | 9.2684 | 9.6 | 27.1791 | 0 | 11.4827 | 0 | 3.1543 | 0 | 0 | 3.1543 | 0 | 0 | 0 | 103.8764 | 41.7457 | 0 | 103.8764 | 136.1138 | 10.68% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 44.9
2096 | 74 | 159 | 138 | 10.0743 | 10.7 | 37.2455 | 0 | 20.1173 | 0 | 13.5015 | 0 | 0 | 13.5015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.1138 | 10.68% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 13.5015
2097 | 502 | 437 | 188 | 12.4922 | 12.1 | 252.6653 | 152.4796 | 0 | 118.9529 | 46.5097 | 0.55485 | 0 | 45.9548 | 0 | 0 | 0 | 0 | 0 | 118.9529 | 0 | 249.5466 | 19.58% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 45.4
2098 | 653 | 624 | 201 | 14.1041 | 13.2 | 328.6663 | 209.3462 | 0 | 171.1686 | 91.3623 | 0 | 23.0312 | 68.3312 | 0 | 0 | 0 | 0 | 0 | 171.1686 | 0 | 412.772 | 32.39% | 17.6649 | 0 | 17.8817 | 35.76% | 45.3
2099 | 651 | 756 | 259 | 15.1115 | 14.3 | 327.6596 | 213.7872 | 0 | 174.7019 | 105.2 | 5.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 174.7019 | 0 | 579.3668 | 45.46% | 19.175 | 0 | 37.2921 | 74.58% | 44.8
2100 | 760 | 850 | 220 | 15.1115 | 15.5 | 382.5212 | 252.0497 | 0 | 210.316 | 106.5 | 15.1326 | 16.3674 | 75 | 0 | 0 | 0 | 0 | 0 | 210.316 | 0 | 779.9229 | 61.19% | 12.5538 | 0 | 50 | 100% | 43.5
2101 | 828 | 914 | 219 | 15.5145 | 15.8 | 416.7468 | 272.4769 | 0 | 229.1586 | 107.7 | 32.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 229.1586 | 0 | 998.4473 | 78.34% | 0 | 0 | 50 | 100% | 42.3
2102 | 729 | 837 | 250 | 15.313 | 16.1 | 366.9184 | 234.6832 | 0 | 194.2514 | 108.5 | 33.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 194.2514 | 0 | 1183.6843 | 92.87% | 0 | 0 | 50 | 100% | 41.5
2103 | 770 | 736 | 189 | 16.9249 | 15.7 | 387.5544 | 153.8228 | 82.0573 | 126.7756 | 109 | 34 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 126.7756 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41
2104 | 288 | 397 | 226 | 16.119 | 14.9 | 144.9554 | 0 | 79.8028 | 0 | 39.4523 | 0 | 0 | 39.4523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.4523
2105 | 433 | 309 | 143 | 15.1115 | 14.3 | 217.9364 | 0 | 96.9581 | 0 | 31.9578 | 0 | 0 | 31.9578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 10.3422 | 39.5325 | 79.06% | 42.3
2106 | 400 | 158 | 71 | 15.1115 | 13.3 | 201.327 | 0 | 0 | 0 | 11.5307 | 0 | 0 | 11.5307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 14.2289 | 28.46% | 36.5307
2107 | 28 | 16 | 14 | 13.7011 | 11.9 | 14.0929 | 0 | 0 | 0 | 0.3896 | 0 | 0 | 0.3896 | 0 | 0 | 0 | 75.0942 | 29.6516 | 0 | 75.0942 | 1204.795 | 94.53% | 0 | 14.0588 | 0 | 0% | 44.1
2108 | 0 | 0 | 0 | 12.2907 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.6826 | 41.2 | 0 | 102.6826 | 1102.4822 | 86.5% | 0 | 0 | 0 | 0% | 41.2
2109 | 0 | 0 | 0 | 12.2907 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9356 | 38 | 0 | 94.9356 | 1009.2724 | 79.19% | 0 | 0 | 0 | 0% | 38
2110 | 0 | 0 | 0 | 10.2758 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8236 | 36.3 | 0 | 90.8236 | 920.8553 | 72.25% | 0 | 0 | 0 | 0% | 36.3
2111 | 0 | 0 | 0 | 7.455 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4905 | 34.1 | 0 | 85.4905 | 838.6812 | 65.8% | 0 | 0 | 0 | 0% | 34.1
2112 | 0 | 0 | 0 | 7.6565 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4152 | 32.4 | 0 | 81.4152 | 761.3657 | 59.74% | 0 | 0 | 0 | 0% | 32.4
2113 | 0 | 0 | 0 | 4.6342 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.479 | 31.6 | 0 | 79.479 | 686.2873 | 53.85% | 0 | 0 | 0 | 0% | 31.6
2114 | 0 | 0 | 0 | 6.2461 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2758 | 31.1 | 0 | 78.2758 | 612.5951 | 48.07% | 0 | 0 | 0 | 0% | 31.1
2115 | 0 | 0 | 0 | 5.2387 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.797 | 30.9 | 0 | 77.797 | 539.4482 | 42.33% | 0 | 0 | 0 | 0% | 30.9
2116 | 0 | 0 | 0 | 4.4327 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.484 | 31.6 | 0 | 79.484 | 464.3313 | 36.43% | 0 | 0 | 0 | 0% | 31.6
2117 | 0 | 0 | 0 | 4.6342 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.639 | 32.5 | 0 | 81.639 | 386.6566 | 30.34% | 0 | 0 | 0 | 0% | 32.5
2118 | 0 | 0 | 0 | 5.8431 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7986 | 35.5 | 0 | 88.7986 | 300.3649 | 23.57% | 0 | 0 | 0 | 0% | 35.5
2119 | 188 | 58 | 31 | 5.8431 | 7.9 | 94.6237 | 0 | 40.1489 | 0 | 2.4698 | 0 | 0 | 2.4698 | 0 | 0 | 0 | 90.1014 | 36.0302 | 0 | 90.1014 | 212.5717 | 16.68% | 0 | 0 | 0 | 0% | 38.5
2120 | 520 | 239 | 80 | 9.0669 | 10.6 | 261.725 | 141.6899 | 0 | 110.9328 | 23.1431 | 0 | 0 | 23.1431 | 0 | 0 | 0 | 0 | 0 | 110.9328 | 0 | 317.1426 | 24.88% | 0 | 0 | 0 | 0% | 23.1431
2121 | 630 | 461 | 146 | 12.4922 | 12.4 | 317.09 | 191.4094 | 0 | 155.2997 | 58.9421 | 0 | 9.321 | 49.621 | 0 | 0 | 0 | 0 | 0 | 155.2997 | 0 | 463.5359 | 36.37% | 7.1492 | 0 | 7.238 | 14.48% | 40.3
2122 | 363 | 566 | 332 | 13.7011 | 13.6 | 182.7042 | 116.3622 | 0 | 84.646 | 75.1011 | 0 | 17.5506 | 57.5506 | 0 | 0 | 0 | 0 | 0 | 84.646 | 0 | 543.3275 | 42.63% | 13.4613 | 0 | 20.8665 | 41.73% | 40
2123 | 741 | 749 | 183 | 14.1041 | 15.1 | 372.9582 | 243.3792 | 0 | 202.9187 | 110.2 | 10.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 202.9187 | 0 | 734.609 | 57.64% | 19.175 | 0 | 40.2796 | 80.56% | 39.8
2124 | 651 | 793 | 250 | 16.3204 | 15.8 | 327.6596 | 215.9508 | 0 | 176.0725 | 111.1 | 23.5822 | 12.5178 | 75 | 0 | 0 | 0 | 0 | 0 | 176.0725 | 0 | 900.5838 | 70.66% | 9.6011 | 0 | 50 | 100% | 38.9
2125 | 836 | 860 | 154 | 17.5294 | 16 | 420.7733 | 275.1962 | 0 | 230.5555 | 112.8 | 37.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 230.5555 | 0 | 1117.9171 | 87.71% | 0 | 0 | 50 | 100% | 37.2
2126 | 859 | 833 | 143 | 15.716 | 16.2 | 432.3496 | 239.0956 | 37.4984 | 201.3567 | 113.9 | 38.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 201.3567 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.1
2127 | 823 | 721 | 136 | 15.313 | 16.2 | 414.2302 | 0 | 252.3492 | 0 | 114.7 | 39.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.3
2128 | 607 | 526 | 170 | 14.3056 | 15.9 | 305.5137 | 0 | 168.5752 | 0 | 76.4591 | 20.5796 | 0 | 55.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.3
2129 | 373 | 318 | 159 | 14.1041 | 15.2 | 187.7374 | 0 | 84.1748 | 0 | 29.9982 | 0 | 0 | 29.9982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.3018 | 42.6086 | 85.22% | 37.3
2130 | 56 | 101 | 86 | 12.6937 | 13.7 | 28.1858 | 0 | 0 | 0 | 7.2408 | 0 | 0 | 7.2408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.3016 | 34.6% | 32.2408
2131 | 0 | 7 | 7 | 12.0892 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.867 | 23.3079 | 0 | 60.867 | 1218.9157 | 95.64% | 0 | 17.0921 | 0 | 0% | 40.4
2132 | 0 | 0 | 0 | 11.0818 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6655 | 38.7 | 0 | 96.6655 | 1123.7022 | 88.17% | 0 | 0 | 0 | 0% | 38.7
2133 | 0 | 0 | 0 | 9.4699 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.151 | 36 | 0 | 90.151 | 1036.122 | 81.3% | 0 | 0 | 0 | 0% | 36
2134 | 0 | 0 | 0 | 9.8729 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1584 | 33.5 | 0 | 84.1584 | 955.6645 | 74.98% | 0 | 0 | 0 | 0% | 33.5
2135 | 0 | 0 | 0 | 7.858 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6349 | 31.2 | 0 | 78.6349 | 881.7145 | 69.18% | 0 | 0 | 0 | 0% | 31.2
2136 | 0 | 0 | 0 | 8.0595 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.494 | 29.9 | 0 | 75.494 | 811.3325 | 63.66% | 0 | 0 | 0 | 0% | 29.9
2137 | 0 | 0 | 0 | 5.2387 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5041 | 29 | 0 | 73.5041 | 743.1445 | 58.31% | 0 | 0 | 0 | 0% | 29
2138 | 0 | 0 | 0 | 6.0446 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.829 | 28.7 | 0 | 72.829 | 675.6798 | 53.01% | 0 | 0 | 0 | 0% | 28.7
2139 | 0 | 0 | 0 | 3.0223 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6951 | 29.1 | 0 | 73.6951 | 607.2253 | 47.64% | 0 | 0 | 0 | 0% | 29.1
2140 | 0 | 0 | 0 | 3.4253 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2099 | 29.8 | 0 | 75.2099 | 537.0432 | 42.14% | 0 | 0 | 0 | 0% | 29.8
2141 | 0 | 0 | 0 | 4.2312 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2171 | 29.8 | 0 | 75.2171 | 466.8478 | 36.63% | 0 | 0 | 0 | 0% | 29.8
2142 | 0 | 0 | 0 | 5.0372 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2338 | 31.9 | 0 | 80.2338 | 390.8412 | 30.67% | 0 | 0 | 0 | 0% | 31.9
2143 | 0 | 8 | 8 | 4.4327 | 9.5 | 0 | 0 | 0 | 0 | 0.16095 | 0 | 0 | 0.16095 | 0 | 0 | 0 | 86.3427 | 34.4391 | 0 | 86.3427 | 307.5387 | 24.13% | 0 | 0 | 0 | 0% | 34.6
2144 | 0 | 22 | 22 | 5.8431 | 9.5 | 0 | 0 | 0 | 0 | 1.2599 | 0 | 0 | 1.2599 | 0 | 0 | 0 | 88.5008 | 35.3401 | 0 | 88.5008 | 221.6263 | 17.39% | 0 | 0 | 0 | 0% | 36.6
2145 | 0 | 43 | 43 | 3.8283 | 9.8 | 0 | 0 | 0 | 0 | 2.863 | 0 | 0 | 2.863 | 0 | 0 | 0 | 86.6021 | 34.537 | 0 | 86.6021 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 37.4
2146 | 0 | 59 | 57 | 3.0223 | 10.1 | 0 | 0 | 0 | 0 | 3.9107 | 0 | 0 | 3.9107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 3.9107
2147 | 0 | 84 | 81 | 2.6193 | 10.5 | 0 | 0 | 0 | 0 | 5.7402 | 0 | 0 | 5.7402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 5.7402
2148 | 0 | 70 | 69 | 1.6119 | 11 | 0 | 0 | 0 | 0 | 4.7799 | 0 | 0 | 4.7799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 4.7799
2149 | 0 | 89 | 88 | 1.8134 | 11.5 | 0 | 0 | 0 | 0 | 6.2385 | 0 | 0 | 6.2385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 6.2385
2150 | 0 | 83 | 82 | 4.6342 | 11.9 | 0 | 0 | 0 | 0 | 5.7854 | 0 | 0 | 5.7854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 5.7854
2151 | 0 | 65 | 63 | 3.6268 | 12 | 0 | 0 | 0 | 0 | 4.3313 | 0 | 0 | 4.3313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 4.3313
2152 | 0 | 44 | 43 | 3.2238 | 11.4 | 0 | 0 | 0 | 0 | 2.8264 | 0 | 0 | 2.8264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 2.8264
2153 | 0 | 41 | 40 | 2.2164 | 11.4 | 0 | 0 | 0 | 0 | 2.6279 | 0 | 0 | 2.6279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 2.6279
2154 | 1 | 37 | 36 | 3.4253 | 11.6 | 0.50332 | 0 | 0 | 0 | 2.3174 | 0 | 0 | 2.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 2.3174
2155 | 0 | 3 | 3 | 2.2164 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2156 | 0 | 0 | 0 | 1.4104 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2157 | 0 | 0 | 0 | 1.0074 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2158 | 0 | 0 | 0 | 1.8134 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2159 | 0 | 0 | 0 | 1.4104 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2160 | 0 | 0 | 0 | 1.0074 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2161 | 0 | 0 | 0 | 0.20149 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2162 | 0 | 0 | 0 | 1.8134 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2163 | 0 | 0 | 0 | 1.2089 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2164 | 0 | 0 | 0 | 0.80595 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2165 | 0 | 0 | 0 | 1.0074 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2166 | 0 | 0 | 0 | 3.4253 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 0
2167 | 195 | 67 | 34 | 3.6268 | 10.1 | 98.1469 | 0 | 41.9961 | 0 | 2.7619 | 0 | 0 | 2.7619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.9827 | 10.83% | 0 | 0 | 0 | 0% | 2.7619
2168 | 523 | 272 | 106 | 2.4178 | 11.6 | 263.235 | 142.8965 | 0 | 115.5843 | 24.9526 | 0 | 0 | 24.9526 | 0 | 0 | 0 | 0 | 0 | 115.5843 | 0 | 245.9677 | 19.3% | 0 | 0 | 0 | 0% | 24.9526
2169 | 218 | 351 | 252 | 2.2164 | 13.4 | 109.7232 | 66.2675 | 0 | 43.6813 | 33.5759 | 0 | 0 | 33.5759 | 0 | 0 | 0 | 0 | 0 | 43.6813 | 0 | 286.7771 | 22.5% | 0 | 0 | 0 | 0% | 33.5759
2170 | 311 | 482 | 266 | 3.0223 | 14.8 | 156.5317 | 99.6718 | 0 | 74.7687 | 46.6332 | 0.36662 | 0 | 46.2666 | 0 | 0 | 0 | 0 | 0 | 74.7687 | 0 | 356.63 | 27.98% | 0 | 0 | 0 | 0% | 45.9
2171 | 821 | 797 | 160 | 4.8357 | 16.1 | 413.2236 | 269.7332 | 0 | 233.1715 | 105.3 | 5.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 233.1715 | 0 | 574.4713 | 45.07% | 19.175 | 0 | 19.4167 | 38.83% | 44.7
2172 | 929 | 916 | 137 | 4.8357 | 17.2 | 467.5819 | 308.3133 | 0 | 269.3686 | 106.3 | 6.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 269.3686 | 0 | 826.1298 | 64.82% | 19.175 | 0 | 38.8335 | 77.67% | 43.7
2173 | 926 | 928 | 139 | 7.6565 | 18.1 | 466.0719 | 305.0136 | 0 | 264.618 | 107.1 | 17.7226 | 14.3774 | 75 | 0 | 0 | 0 | 0 | 0 | 264.618 | 0 | 1073.3501 | 84.22% | 11.0275 | 0 | 50 | 100% | 42.9
2174 | 918 | 874 | 130 | 10.0743 | 18.5 | 462.0454 | 295.7211 | 0 | 254.5362 | 107.7 | 32.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 254.5362 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
2175 | 527 | 582 | 190 | 12.6937 | 18.1 | 265.2483 | 0 | 161.8856 | 0 | 80.2888 | 19.3944 | 0 | 60.8944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.5
2176 | 545 | 503 | 197 | 8.6639 | 18.1 | 274.308 | 0 | 152.0329 | 0 | 63.7557 | 10.9279 | 0 | 52.8279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.9
2177 | 587 | 406 | 158 | 5.6416 | 18.3 | 295.4473 | 0 | 133.853 | 0 | 38.4137 | 0 | 0 | 38.4137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.1863 | 43.7367 | 87.47% | 44.6
2178 | 23 | 63 | 56 | 10.2758 | 16 | 11.5763 | 0 | 0 | 0 | 4.218 | 0 | 0 | 4.218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.425 | 36.85% | 29.218
2179 | 0 | 7 | 7 | 6.0446 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7375 | 24.9015 | 0 | 64.7375 | 1215.083 | 95.34% | 0 | 18.1985 | 0 | 0% | 43.1
2180 | 0 | 0 | 0 | 3.8283 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0547 | 39.2 | 0 | 98.0547 | 1118.2597 | 87.74% | 0 | 0 | 0 | 0% | 39.2
2181 | 0 | 0 | 0 | 5.4401 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2363 | 36.4 | 0 | 91.2363 | 1029.3991 | 80.77% | 0 | 0 | 0 | 0% | 36.4
2182 | 0 | 0 | 0 | 6.0446 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9119 | 34.2 | 0 | 85.9119 | 946.7771 | 74.29% | 0 | 0 | 0 | 0% | 34.2
2183 | 0 | 0 | 0 | 5.0372 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5284 | 32.8 | 0 | 82.5284 | 868.1732 | 68.12% | 0 | 0 | 0 | 0% | 32.8
2184 | 0 | 0 | 0 | 3.4253 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0636 | 32.2 | 0 | 81.0636 | 791.2651 | 62.08% | 0 | 0 | 0 | 0% | 32.2
2185 | 0 | 0 | 0 | 2.8208 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5616 | 32 | 0 | 80.5616 | 714.9118 | 56.09% | 0 | 0 | 0 | 0% | 32
2186 | 0 | 0 | 0 | 1.8134 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4672 | 32.8 | 0 | 82.4672 | 636.2719 | 49.92% | 0 | 0 | 0 | 0% | 32.8
2187 | 0 | 0 | 0 | 2.2164 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8368 | 36.3 | 0 | 90.8368 | 547.6112 | 42.97% | 0 | 0 | 0 | 0% | 36.3
2188 | 0 | 0 | 0 | 1.6119 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.5257 | 41.6 | 0 | 103.5257 | 443.828 | 34.82% | 0 | 0 | 0 | 0% | 41.6
2189 | 0 | 0 | 0 | 2.2164 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.2462 | 44.4 | 0 | 110.2462 | 331.989 | 26.05% | 0 | 0 | 0 | 0% | 44.4
2190 | 0 | 0 | 0 | 2.8208 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.1398 | 45.6 | 0 | 113.1398 | 216.6592 | 17% | 0 | 0 | 0 | 0% | 45.6
2191 | 134 | 73 | 31 | 2.4178 | 8.4 | 67.4445 | 0 | 28.9785 | 0 | 2.4069 | 0 | 0 | 2.4069 | 0 | 0 | 0 | 108.5405 | 43.6931 | 0 | 108.5405 | 106.7867 | 8.379% | 0 | 0 | 0 | 0% | 46.1
2192 | 570 | 283 | 60 | 1.0074 | 11.4 | 286.8909 | 155.8907 | 0 | 128.213 | 22.4836 | 0 | 0 | 22.4836 | 0 | 0 | 0 | 0 | 0 | 128.213 | 0 | 229.2481 | 17.99% | 0 | 0 | 0 | 0% | 22.4836
2193 | 768 | 500 | 119 | 2.0149 | 14.2 | 386.5478 | 233.5135 | 0 | 200.5223 | 59.3086 | 0 | 6.5543 | 52.7543 | 0 | 0 | 0 | 0 | 0 | 200.5223 | 0 | 420.775 | 33.01% | 5.0272 | 0 | 5.0912 | 10.18% | 46.2
2194 | 663 | 596 | 158 | 3.6268 | 16.1 | 333.6994 | 212.4608 | 0 | 180.2176 | 79.6953 | 0 | 16.9976 | 62.6976 | 0 | 0 | 0 | 0 | 0 | 180.2176 | 0 | 592.908 | 46.52% | 13.0372 | 0 | 18.2947 | 36.59% | 45.7
2195 | 868 | 810 | 141 | 5.8431 | 17.9 | 436.8795 | 285.2152 | 0 | 247.2174 | 105.8 | 5.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 247.2174 | 0 | 829.0353 | 65.05% | 19.175 | 0 | 37.7142 | 75.43% | 44.2
2196 | 968 | 942 | 132 | 6.2461 | 19.6 | 487.2112 | 321.3315 | 0 | 280.7146 | 106.5 | 15.6836 | 15.8164 | 75 | 0 | 0 | 0 | 0 | 0 | 280.7146 | 0 | 1097.157 | 86.08% | 12.1311 | 0 | 50 | 100% | 43.5
2197 | 910 | 957 | 183 | 5.6416 | 20.7 | 458.0188 | 251.3713 | 48.4653 | 218.8948 | 107.1 | 32.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 218.8948 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.9
2198 | 938 | 914 | 153 | 5.4401 | 21.6 | 472.1117 | 0 | 302.2297 | 0 | 107.6 | 32.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
2199 | 645 | 754 | 282 | 9.6714 | 21.9 | 324.6397 | 0 | 198.3127 | 0 | 108.3 | 33.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
2200 | 402 | 490 | 252 | 11.6862 | 20.7 | 202.3336 | 0 | 112.3888 | 0 | 53.1752 | 5.5876 | 0 | 47.5876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42
2201 | 247 | 271 | 171 | 10.4773 | 19.7 | 124.3194 | 0 | 56.609 | 0 | 24.9721 | 0 | 0 | 24.9721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 19.5279 | 30.2261 | 60.45% | 44.5
2202 | 206 | 130 | 76 | 7.858 | 18.9 | 103.6834 | 0 | 0 | 0 | 8.5501 | 0 | 0 | 8.5501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 4.9101 | 9.82% | 33.5501
2203 | 1 | 10 | 10 | 5.0372 | 17.1 | 0.50332 | 0 | 0 | 0 | 0.13085 | 0 | 0 | 0.13085 | 0 | 0 | 0 | 95.9572 | 38.1193 | 0 | 95.9572 | 1180.9628 | 92.66% | 0 | 4.8499 | 0 | 0% | 43.1
2204 | 0 | 0 | 0 | 3.6268 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.842 | 39.4 | 0 | 98.842 | 1083.7336 | 85.03% | 0 | 0 | 0 | 0% | 39.4
2205 | 0 | 0 | 0 | 2.2164 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.476 | 36.8 | 0 | 92.476 | 993.9013 | 77.98% | 0 | 0 | 0 | 0% | 36.8
2206 | 0 | 0 | 0 | 1.8134 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0334 | 34.6 | 0 | 87.0334 | 910.2597 | 71.42% | 0 | 0 | 0 | 0% | 34.6
2207 | 0 | 0 | 0 | 3.0223 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6802 | 33.2 | 0 | 83.6802 | 830.6468 | 65.17% | 0 | 0 | 0 | 0% | 33.2
2208 | 0 | 0 | 0 | 1.8134 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3548 | 32.7 | 0 | 82.3548 | 752.4494 | 59.04% | 0 | 0 | 0 | 0% | 32.7
2209 | 0 | 0 | 0 | 1.0074 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8689 | 32.5 | 0 | 81.8689 | 674.8085 | 52.95% | 0 | 0 | 0 | 0% | 32.5
2210 | 0 | 0 | 0 | 1.6119 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5068 | 33.2 | 0 | 83.5068 | 595.158 | 46.7% | 0 | 0 | 0 | 0% | 33.2
2211 | 0 | 0 | 0 | 1.2089 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5848 | 36.6 | 0 | 91.5848 | 505.8048 | 39.69% | 0 | 0 | 0 | 0% | 36.6
2212 | 0 | 0 | 0 | 3.0223 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.878 | 41.7 | 0 | 103.878 | 401.9178 | 31.54% | 0 | 0 | 0 | 0% | 41.7
2213 | 0 | 0 | 0 | 4.0297 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.6001 | 44.5 | 0 | 110.6001 | 289.9838 | 22.75% | 0 | 0 | 0 | 0% | 44.5
2214 | 0 | 1 | 1 | 4.0297 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.4538 | 45.7 | 0 | 113.4538 | 174.5591 | 13.7% | 0 | 0 | 0 | 0% | 45.7
2215 | 368 | 82 | 30 | 3.2238 | 11.1 | 185.2208 | 79.9087 | 0 | 55.9958 | 3.0842 | 0 | 0 | 3.0842 | 0 | 0 | 0 | 88.0265 | 35.1213 | 55.9958 | 88.0265 | 142.8796 | 11.21% | 0 | 0 | 0 | 0% | 38.2055
2216 | 727 | 289 | 56 | 1.2089 | 15.1 | 365.9117 | 199.0209 | 0 | 168.515 | 26.4864 | 0 | 0 | 26.4864 | 0 | 0 | 0 | 0 | 0 | 168.515 | 0 | 304.1856 | 23.87% | 0 | 0 | 0 | 0% | 26.4864
2217 | 874 | 502 | 63 | 1.4104 | 16.9 | 439.8994 | 265.8071 | 0 | 230.7412 | 58.3271 | 0 | 6.0636 | 52.2636 | 0 | 0 | 0 | 0 | 0 | 230.7412 | 0 | 525.0558 | 41.2% | 4.6507 | 0 | 4.7107 | 9.421% | 46.2
2218 | 948 | 690 | 67 | 3.4253 | 19.1 | 477.1449 | 303.7576 | 0 | 265.6586 | 98.6664 | 1.4332 | 25 | 72.2332 | 0 | 0 | 0 | 0 | 0 | 265.6586 | 0 | 779.3496 | 61.15% | 19.175 | 0 | 24.133 | 48.27% | 45.8
2219 | 976 | 825 | 72 | 4.8357 | 20.2 | 491.2378 | 320.7477 | 0 | 281.002 | 105.7 | 5.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 281.002 | 0 | 1048.3304 | 82.25% | 19.175 | 0 | 43.5552 | 87.11% | 44.3
2220 | 993 | 907 | 75 | 9.6714 | 21.1 | 499.7942 | 313.6372 | 16.0701 | 272.523 | 106.7 | 23.4044 | 8.2956 | 75 | 0 | 0 | 0 | 0 | 0 | 272.523 | 0 | 1274.5104 | 100% | 6.3627 | 0 | 50 | 100% | 43.3
2221 | 981 | 918 | 83 | 13.4996 | 21 | 493.7544 | 0 | 323.3303 | 0 | 107.2 | 32.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.8
2222 | 932 | 857 | 100 | 9.6714 | 21.3 | 469.0918 | 0 | 300.3618 | 0 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
2223 | 858 | 735 | 117 | 10.6788 | 21.9 | 431.8463 | 0 | 264.0392 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42
2224 | 838 | 581 | 92 | 12.4922 | 22.4 | 421.78 | 0 | 234.7945 | 0 | 79.8524 | 18.6762 | 0 | 61.1762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
2225 | 742 | 378 | 72 | 11.6862 | 22.6 | 373.4615 | 0 | 170.9101 | 0 | 37.1771 | 0 | 0 | 37.1771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.4229 | 42.4825 | 84.97% | 44.6
2226 | 484 | 159 | 48 | 11.0818 | 21.5 | 243.6056 | 0 | 0 | 0 | 10.1282 | 0 | 0 | 10.1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.1636 | 34.33% | 35.1282
2227 | 78 | 15 | 9 | 10.0743 | 19.9 | 39.2588 | 0 | 0 | 0 | 0.012257 | 0 | 0 | 0.012257 | 0 | 0 | 0 | 67.4876 | 25.84 | 0 | 67.4876 | 1212.5936 | 95.14% | 0 | 16.9478 | 0 | 0% | 42.8
2228 | 0 | 0 | 0 | 10.8803 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1758 | 39.3 | 0 | 99.1758 | 1115.6805 | 87.54% | 0 | 0 | 0 | 0% | 39.3
2229 | 0 | 0 | 0 | 8.4625 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9746 | 36.8 | 0 | 92.9746 | 1025.8744 | 80.49% | 0 | 0 | 0 | 0% | 36.8
2230 | 0 | 0 | 0 | 6.4476 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4649 | 34.6 | 0 | 87.4649 | 942.257 | 73.93% | 0 | 0 | 0 | 0% | 34.6
2231 | 0 | 0 | 0 | 5.0372 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9079 | 33.2 | 0 | 83.9079 | 862.6672 | 67.69% | 0 | 0 | 0 | 0% | 33.2
2232 | 0 | 0 | 0 | 5.0372 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1042 | 32.5 | 0 | 82.1042 | 785.0612 | 61.6% | 0 | 0 | 0 | 0% | 32.5
2233 | 0 | 0 | 0 | 3.0223 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7511 | 32.4 | 0 | 81.7511 | 707.7272 | 55.53% | 0 | 0 | 0 | 0% | 32.4
2234 | 0 | 0 | 0 | 3.2238 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5976 | 33.2 | 0 | 83.5976 | 628.1009 | 49.28% | 0 | 0 | 0 | 0% | 33.2
2235 | 0 | 0 | 0 | 3.0223 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6356 | 36.6 | 0 | 91.6356 | 538.7759 | 42.27% | 0 | 0 | 0 | 0% | 36.6
2236 | 0 | 0 | 0 | 3.4253 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5803 | 42 | 0 | 104.5803 | 434.0717 | 34.06% | 0 | 0 | 0 | 0% | 42
2237 | 0 | 0 | 0 | 7.052 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0304 | 45.1 | 0 | 112.0304 | 320.4429 | 25.14% | 0 | 0 | 0 | 0% | 45.1
2238 | 0 | 1 | 1 | 5.6416 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.8292 | 46.7 | 0 | 115.8292 | 202.1829 | 15.86% | 0 | 0 | 0 | 0% | 46.7
2239 | 41 | 47 | 38 | 6.6491 | 10.5 | 20.636 | 0 | 8.9389 | 0 | 2.5673 | 0 | 0 | 2.5673 | 0 | 0 | 0 | 110.145 | 44.3327 | 0 | 110.145 | 90.6911 | 7.116% | 0 | 0 | 0 | 0% | 46.9
2240 | 265 | 226 | 141 | 8.8654 | 11.9 | 133.3791 | 72.6144 | 0 | 45.9333 | 20.1333 | 0 | 0 | 20.1333 | 0 | 0 | 0 | 0 | 0 | 45.9333 | 0 | 134.6923 | 10.57% | 0 | 0 | 0 | 0% | 20.1333
2241 | 122 | 312 | 252 | 9.6714 | 12.6 | 61.4047 | 0 | 37.1122 | 0 | 28.0398 | 0 | 0 | 28.0398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6923 | 10.57% | 0 | 0 | 0 | 0% | 28.0398
2242 | 24 | 331 | 310 | 8.8654 | 13.1 | 12.0796 | 0 | 7.6892 | 0 | 26.7969 | 0 | 0 | 26.7969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6923 | 10.57% | 0 | 0 | 0 | 0% | 26.7969
2243 | 450 | 713 | 350 | 11.6862 | 14 | 226.4928 | 147.9061 | 0 | 115.3239 | 99.8669 | 2.8835 | 25 | 71.9835 | 0 | 0 | 0 | 0 | 0 | 115.3239 | 0 | 245.165 | 19.24% | 19.175 | 0 | 19.4251 | 38.85% | 44.1
2244 | 112 | 595 | 489 | 10.2758 | 14.2 | 56.3715 | 0 | 37.1962 | 0 | 63.1515 | 0 | 9.9758 | 53.1758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245.165 | 19.24% | 7.6514 | 0 | 27.1763 | 54.35% | 43.2
2245 | 38 | 404 | 364 | 10.0743 | 14.2 | 19.1261 | 0 | 12.5284 | 0 | 34.6029 | 0 | 0 | 34.6029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245.165 | 19.24% | 0 | 8.0971 | 18.9749 | 37.95% | 42.7
2246 | 1 | 155 | 152 | 8.6639 | 13.6 | 0.50332 | 0 | 0.32235 | 0 | 11.4382 | 0 | 0 | 11.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245.165 | 19.24% | 0 | 18.7336 | 0 | 0% | 30.1718
2247 | 0 | 91 | 90 | 9.6714 | 13.2 | 0 | 0 | 0 | 0 | 6.4144 | 0 | 0 | 6.4144 | 0 | 0 | 0 | 88.8427 | 35.3856 | 0 | 88.8427 | 159.097 | 12.48% | 0 | 0 | 0 | 0% | 41.8
2248 | 0 | 47 | 46 | 8.6639 | 12.7 | 0 | 0 | 0 | 0 | 3.0435 | 0 | 0 | 3.0435 | 0 | 0 | 0 | 65.3252 | 25.2553 | 0 | 65.3252 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 28.2988
2249 | 0 | 23 | 23 | 6.2461 | 12.3 | 0 | 0 | 0 | 0 | 1.3119 | 0 | 0 | 1.3119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 1.3119
2250 | 0 | 7 | 7 | 3.2238 | 12.1 | 0 | 0 | 0 | 0 | 0.11824 | 0 | 0 | 0.11824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0.11824
2251 | 0 | 0 | 0 | 5.2387 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2252 | 0 | 0 | 0 | 6.0446 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2253 | 0 | 0 | 0 | 4.6342 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2254 | 0 | 0 | 0 | 4.8357 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2255 | 0 | 0 | 0 | 5.0372 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2256 | 0 | 0 | 0 | 5.8431 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2257 | 0 | 0 | 0 | 2.8208 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2258 | 0 | 0 | 0 | 2.2164 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2259 | 0 | 0 | 0 | 2.2164 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2260 | 0 | 0 | 0 | 1.2089 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2261 | 0 | 0 | 0 | 1.2089 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2262 | 1 | 1 | 1 | 0.80595 | 7.5 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 0
2263 | 64 | 58 | 49 | 0.80595 | 7.9 | 32.2123 | 0 | 14.0093 | 0 | 3.4843 | 0 | 0 | 3.4843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 3.4843
2264 | 1 | 119 | 117 | 2.6193 | 9.9 | 0.50332 | 0 | 0.27427 | 0 | 8.9591 | 0 | 0 | 8.9591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.019 | 7.769% | 0 | 0 | 0 | 0% | 8.9591
2265 | 582 | 412 | 98 | 5.0372 | 12.1 | 292.9307 | 177.0845 | 0 | 146.6256 | 42.108 | 0 | 0 | 42.108 | 0 | 0 | 0 | 0 | 0 | 146.6256 | 0 | 239.0705 | 18.76% | 0 | 0 | 0 | 0% | 42.108
2266 | 804 | 694 | 151 | 11.6862 | 14.7 | 404.6672 | 257.5623 | 0 | 217.5348 | 100.3466 | 1.3733 | 25 | 73.9733 | 0 | 0 | 0 | 0 | 0 | 217.5348 | 0 | 446.852 | 35.06% | 19.175 | 0 | 19.4269 | 38.85% | 47.6
2267 | 722 | 767 | 204 | 16.5219 | 15.2 | 363.3952 | 237.3394 | 0 | 195.9502 | 104.2 | 4.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 195.9502 | 0 | 634.0166 | 49.75% | 19.175 | 0 | 38.8538 | 77.71% | 45.8
2268 | 458 | 794 | 392 | 19.3427 | 14 | 230.5194 | 152.1415 | 0 | 114.6793 | 105.2 | 15.8563 | 14.3437 | 75 | 0 | 0 | 0 | 0 | 0 | 114.6793 | 0 | 743.5542 | 58.34% | 11.0016 | 0 | 50 | 100% | 44.8
2269 | 75 | 360 | 291 | 16.3204 | 13.8 | 37.7488 | 0 | 24.7346 | 0 | 31.6691 | 0 | 0 | 31.6691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743.5542 | 58.34% | 0 | 12.4309 | 37.4078 | 74.82% | 44.1
2270 | 1 | 230 | 226 | 14.91 | 12.9 | 0.50332 | 0 | 0.32242 | 0 | 17.655 | 0 | 0 | 17.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743.5542 | 58.34% | 0 | 25 | 12.0827 | 24.17% | 42.655
2271 | 1 | 141 | 139 | 13.0966 | 10.1 | 0.50332 | 0 | 0.30828 | 0 | 10.5626 | 0 | 0 | 10.5626 | 0 | 0 | 0 | 54.8608 | 20.8091 | 0 | 54.8608 | 693.5655 | 54.42% | 0 | 11.9283 | 0 | 0% | 43.3
2272 | 3 | 209 | 205 | 8.8654 | 10.7 | 1.51 | 0 | 0.84417 | 0 | 16.3456 | 0 | 0 | 16.3456 | 0 | 0 | 0 | 69.4409 | 27.1544 | 0 | 69.4409 | 629.537 | 49.39% | 0 | 0 | 0 | 0% | 43.5
2273 | 145 | 266 | 198 | 9.0669 | 12 | 72.981 | 0 | 33.7292 | 0 | 22.9199 | 0 | 0 | 22.9199 | 0 | 0 | 0 | 57.8024 | 21.9801 | 0 | 57.8024 | 576.7229 | 45.25% | 0 | 0 | 0 | 0% | 44.9
2274 | 214 | 137 | 80 | 10.0743 | 12.6 | 107.7099 | 0 | 0 | 0 | 9.0463 | 0 | 0 | 9.0463 | 0 | 0 | 0 | 93.7685 | 37.4537 | 0 | 93.7685 | 484.7541 | 38.03% | 0 | 0 | 0 | 0% | 46.5
2275 | 96 | 17 | 9 | 14.91 | 11.4 | 48.3185 | 0 | 0 | 0 | 0.025557 | 0 | 0 | 0.025557 | 0 | 0 | 0 | 106.9775 | 42.9744 | 0 | 106.9775 | 376.9934 | 29.58% | 0 | 0 | 0 | 0% | 43
2276 | 0 | 0 | 0 | 17.3279 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.9587 | 40.1 | 0 | 99.9587 | 277.3747 | 21.76% | 0 | 0 | 0 | 0% | 40.1
2277 | 0 | 0 | 0 | 11.2833 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9576 | 37.6 | 0 | 93.9576 | 184.9169 | 14.51% | 0 | 0 | 0 | 0% | 37.6
2278 | 0 | 0 | 0 | 9.2684 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.6346 | 25.497 | 0 | 65.6346 | 124.4453 | 9.764% | 0 | 0 | 0 | 0% | 25.497
2279 | 0 | 0 | 0 | 5.6416 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.4453 | 9.764% | 0 | 0 | 0 | 0% | 0
2280 | 0 | 0 | 0 | 3.2238 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.4453 | 9.764% | 0 | 0 | 0 | 0% | 0
2281 | 0 | 0 | 0 | 6.2461 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.4453 | 9.764% | 0 | 0 | 0 | 0% | 0
2282 | 0 | 0 | 0 | 12.2907 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.4453 | 9.764% | 0 | 0 | 0 | 0% | 0
2283 | 0 | 0 | 0 | 11.8877 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.4453 | 9.764% | 0 | 0 | 0 | 0% | 0
2284 | 0 | 0 | 0 | 13.9026 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.4453 | 9.764% | 0 | 0 | 0 | 0% | 0
2285 | 0 | 0 | 0 | 13.2981 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.4453 | 9.764% | 0 | 0 | 0 | 0% | 0
2286 | 3 | 1 | 1 | 14.91 | 8.9 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.4453 | 9.764% | 0 | 0 | 0 | 0% | 0
2287 | 462 | 101 | 31 | 15.313 | 9.4 | 232.5326 | 101.5299 | 0 | 69.2366 | 3.6959 | 0 | 0 | 3.6959 | 0 | 0 | 0 | 0 | 0 | 69.2366 | 0 | 190.2346 | 14.93% | 0 | 0 | 0 | 0% | 3.6959
2288 | 783 | 322 | 59 | 17.1264 | 11.1 | 394.0975 | 214.9537 | 0 | 174.4939 | 29.7045 | 0 | 0 | 29.7045 | 0 | 0 | 0 | 0 | 0 | 174.4939 | 0 | 356.0403 | 27.94% | 0 | 0 | 0 | 0% | 29.7045
2289 | 903 | 527 | 60 | 19.9472 | 12.5 | 454.4956 | 274.8168 | 0 | 228.6328 | 71.6273 | 0 | 14.7136 | 56.9136 | 0 | 0 | 0 | 0 | 0 | 228.6328 | 0 | 573.2892 | 44.98% | 11.2854 | 0 | 11.4352 | 22.87% | 42.2
2290 | 961 | 710 | 65 | 17.7308 | 14 | 483.688 | 307.825 | 0 | 260.949 | 108 | 8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 260.949 | 0 | 821.2453 | 64.44% | 19.175 | 0 | 30.8649 | 61.73% | 42
2291 | 896 | 813 | 109 | 13.9026 | 15.3 | 450.9724 | 294.5586 | 0 | 251.0084 | 108.9 | 9.2791 | 24.6209 | 75 | 0 | 0 | 0 | 0 | 0 | 251.0084 | 0 | 1059.7557 | 83.15% | 18.8843 | 0 | 50 | 100% | 41.1
2292 | 677 | 774 | 196 | 9.8729 | 15.7 | 340.7459 | 224.943 | 0 | 188.3818 | 110.8 | 35.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 188.3818 | 0 | 1238.7578 | 97.19% | 0 | 0 | 50 | 100% | 39.2
2293 | 303 | 511 | 244 | 12.8952 | 15.9 | 152.5052 | 0 | 99.958 | 0 | 68.3325 | 15.2662 | 0 | 53.0662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.7578 | 97.19% | 0 | 0 | 50 | 100% | 37.8
2294 | 552 | 619 | 170 | 17.9323 | 15.7 | 277.8312 | 0 | 178.0116 | 0 | 98.1573 | 30.4786 | 0 | 67.6786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.7578 | 97.19% | 0 | 0 | 50 | 100% | 37.2
2295 | 193 | 287 | 137 | 15.1115 | 14.8 | 97.1403 | 0 | 59.5507 | 0 | 28.9716 | 0 | 0 | 28.9716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.7578 | 97.19% | 0 | 8.1284 | 41.765 | 83.53% | 37.1
2296 | 35 | 259 | 233 | 16.3204 | 13.2 | 17.6161 | 0 | 9.8695 | 0 | 21.5131 | 0 | 0 | 21.5131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.7578 | 97.19% | 0 | 16.1869 | 25.3653 | 50.73% | 37.7
2297 | 6 | 71 | 68 | 13.9026 | 11.2 | 3.0199 | 0 | 1.4024 | 0 | 5.0948 | 0 | 0 | 5.0948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.7578 | 97.19% | 0 | 25 | 0.035773 | 0.07155% | 30.0948
2298 | 70 | 67 | 54 | 15.313 | 9.8 | 35.2322 | 0 | 0 | 0 | 4.8843 | 0 | 0 | 4.8843 | 0 | 0 | 0 | 93.0244 | 37.2157 | 0 | 93.0244 | 1147.6826 | 90.05% | 0 | 0 | 0.035773 | 0.07155% | 42.1
2299 | 5 | 11 | 10 | 10.0743 | 9.2 | 2.5166 | 0 | 0 | 0 | 0.15952 | 0 | 0 | 0.15952 | 0 | 0 | 0 | 99.2871 | 39.8405 | 0 | 99.2871 | 1049.0803 | 82.31% | 0 | 0 | 0.035773 | 0.07155% | 40
2300 | 0 | 0 | 0 | 15.5145 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8854 | 38 | 0 | 94.8854 | 955.7526 | 74.99% | 0 | 0 | 0.035773 | 0.07155% | 38
2301 | 0 | 0 | 0 | 13.7011 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6382 | 35 | 0 | 87.6382 | 870.8641 | 68.33% | 0 | 0 | 0.035773 | 0.07155% | 35
2302 | 0 | 0 | 0 | 13.2981 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6591 | 32.5 | 0 | 81.6591 | 793.1712 | 62.23% | 0 | 0 | 0.035773 | 0.07155% | 32.5
2303 | 0 | 0 | 0 | 15.716 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0873 | 30.6 | 0 | 77.0873 | 720.808 | 56.56% | 0 | 0 | 0.035773 | 0.07155% | 30.6
2304 | 0 | 0 | 0 | 16.3204 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5609 | 29.5 | 0 | 74.5609 | 651.3218 | 51.1% | 0 | 0 | 0.035773 | 0.07155% | 29.5
2305 | 0 | 0 | 0 | 15.1115 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6672 | 29.1 | 0 | 73.6672 | 582.8046 | 45.73% | 0 | 0 | 0.035773 | 0.07155% | 29.1
2306 | 0 | 0 | 0 | 13.9026 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4501 | 29 | 0 | 73.4501 | 514.5199 | 40.37% | 0 | 0 | 0.035773 | 0.07155% | 29
2307 | 0 | 0 | 0 | 16.9249 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5875 | 29.5 | 0 | 74.5875 | 444.9958 | 34.92% | 0 | 0 | 0.035773 | 0.07155% | 29.5
2308 | 0 | 0 | 0 | 15.9175 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.635 | 30.4 | 0 | 76.635 | 373.12 | 29.28% | 0 | 0 | 0.035773 | 0.07155% | 30.4
2309 | 0 | 0 | 0 | 17.3279 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3314 | 31.1 | 0 | 78.3314 | 299.2738 | 23.48% | 0 | 0 | 0.035773 | 0.07155% | 31.1
2310 | 9 | 1 | 1 | 19.5442 | 9.5 | 4.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5326 | 34.1 | 0 | 85.5326 | 216.8516 | 17.01% | 0 | 0 | 0.035773 | 0.07155% | 34.1
2311 | 475 | 101 | 27 | 19.5442 | 10 | 239.0758 | 104.7955 | 0 | 69.8469 | 3.429 | 0 | 0 | 3.429 | 0 | 0 | 0 | 0 | 0 | 69.8469 | 0 | 282.4087 | 22.16% | 0 | 0 | 0.035773 | 0.07155% | 3.429
2312 | 774 | 319 | 57 | 20.3502 | 11.3 | 389.5677 | 212.6761 | 0 | 170.5144 | 29.325 | 0 | 0 | 29.325 | 0 | 0 | 0 | 0 | 0 | 170.5144 | 0 | 442.4506 | 34.72% | 0 | 0 | 0.035773 | 0.07155% | 29.325
2313 | 722 | 573 | 194 | 21.7606 | 12.8 | 363.3952 | 219.7803 | 0 | 176.3695 | 79.3137 | 0 | 20.4069 | 58.9069 | 0 | 0 | 0 | 0 | 0 | 176.3695 | 0 | 607.988 | 47.7% | 15.6521 | 0 | 15.898 | 31.8% | 38.5
2314 | 891 | 748 | 141 | 23.171 | 14 | 448.4558 | 285.3729 | 0 | 236.8219 | 111.3 | 11.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 236.8219 | 0 | 830.2651 | 65.14% | 19.175 | 0 | 35.3304 | 70.66% | 38.7
2315 | 971 | 877 | 110 | 23.3725 | 15.3 | 488.7212 | 319.224 | 0 | 268.307 | 111.6 | 17.7289 | 18.8711 | 75 | 0 | 0 | 0 | 0 | 0 | 268.307 | 0 | 1082.0935 | 84.9% | 14.4741 | 0 | 49.9989 | 100% | 38.4
2316 | 970 | 956 | 125 | 24.1784 | 16.1 | 488.2179 | 322.3718 | 0 | 270.8157 | 113.6 | 38.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 270.8157 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 36.4
2317 | 958 | 985 | 152 | 21.7606 | 17 | 482.1781 | 0 | 316.1338 | 0 | 114.7 | 39.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 35.3
2318 | 971 | 990 | 186 | 19.7457 | 17.6 | 488.7212 | 0 | 313.1991 | 0 | 114.9 | 39.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 35.1
2319 | 820 | 936 | 331 | 19.3427 | 18.3 | 412.7203 | 0 | 253.2318 | 0 | 114.5 | 39.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 35.5
2320 | 839 | 797 | 293 | 16.7234 | 18.9 | 422.2833 | 0 | 237.0805 | 0 | 113.3 | 38.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 36.7
2321 | 455 | 399 | 202 | 18.1338 | 18 | 229.0094 | 0 | 106.8606 | 0 | 36.0785 | 0 | 0 | 36.0785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 3.2215 | 46.7346 | 93.47% | 39.3
2322 | 296 | 175 | 95 | 15.313 | 16.9 | 148.9819 | 0 | 0 | 0 | 11.0765 | 0 | 0 | 11.0765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 21.4026 | 42.81% | 36.0765
2323 | 14 | 19 | 18 | 9.2684 | 16 | 7.0464 | 0 | 0 | 0 | 0.54492 | 0 | 0 | 0.54492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 21.1234 | 0 | 0% | 21.6683
2324 | 0 | 0 | 0 | 7.2535 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9328 | 37.8 | 0 | 94.9328 | 1181.8256 | 92.73% | 0 | 0 | 0 | 0% | 37.8
2325 | 0 | 0 | 0 | 3.2238 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4528 | 34.7 | 0 | 87.4528 | 1097.8741 | 86.14% | 0 | 0 | 0 | 0% | 34.7
2326 | 0 | 0 | 0 | 1.0074 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3689 | 32.2 | 0 | 81.3689 | 1021.0912 | 80.12% | 0 | 0 | 0 | 0% | 32.2
2327 | 0 | 0 | 0 | 1.6119 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9424 | 30.8 | 0 | 77.9424 | 948.2287 | 74.4% | 0 | 0 | 0 | 0% | 30.8
2328 | 0 | 0 | 0 | 1.8134 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6847 | 30.3 | 0 | 76.6847 | 876.745 | 68.79% | 0 | 0 | 0 | 0% | 30.3
2329 | 0 | 0 | 0 | 2.4178 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6543 | 30.3 | 0 | 76.6543 | 805.2511 | 63.18% | 0 | 0 | 0 | 0% | 30.3
2330 | 0 | 0 | 0 | 2.0149 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2201 | 31.4 | 0 | 79.2201 | 730.6801 | 57.33% | 0 | 0 | 0 | 0% | 31.4
2331 | 0 | 0 | 0 | 2.8208 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2195 | 35.6 | 0 | 89.2195 | 644.1075 | 50.54% | 0 | 0 | 0 | 0% | 35.6
2332 | 0 | 0 | 0 | 2.4178 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6572 | 41.6 | 0 | 103.6572 | 540.4774 | 42.41% | 0 | 0 | 0 | 0% | 41.6
2333 | 0 | 0 | 0 | 1.4104 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0304 | 45.1 | 0 | 112.0304 | 426.7844 | 33.49% | 0 | 0 | 0 | 0% | 45.1
2334 | 0 | 1 | 1 | 1.6119 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.643 | 47 | 0 | 116.643 | 307.5946 | 24.13% | 0 | 0 | 0 | 0% | 47
2335 | 35 | 65 | 58 | 2.6193 | 12 | 17.6161 | 0 | 7.7517 | 0 | 3.9723 | 0 | 0 | 3.9723 | 0 | 0 | 0 | 109.0927 | 43.8277 | 0 | 109.0927 | 197.5174 | 15.5% | 0 | 0 | 0 | 0% | 47.8
2336 | 208 | 263 | 182 | 2.6193 | 15 | 104.69 | 0 | 57.2045 | 0 | 21.0849 | 0 | 0 | 21.0849 | 0 | 0 | 0 | 69.1326 | 26.8151 | 0 | 69.1326 | 133.8173 | 10.5% | 0 | 0 | 0 | 0% | 47.9
2337 | 167 | 425 | 333 | 9.0669 | 17.7 | 84.054 | 0 | 50.8467 | 0 | 37.6433 | 0 | 0 | 37.6433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.8173 | 10.5% | 0 | 0 | 0 | 0% | 37.6433
2338 | 228 | 537 | 369 | 13.9026 | 18.3 | 114.7564 | 73.0171 | 0 | 43.3561 | 50.2133 | 1.5566 | 0 | 48.6566 | 0 | 0 | 0 | 0 | 0 | 43.3561 | 0 | 175.1043 | 13.74% | 0 | 0 | 0 | 0% | 47.1
2339 | 795 | 814 | 180 | 11.0818 | 19.4 | 400.1373 | 261.3701 | 0 | 221.593 | 104.5 | 4.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 221.593 | 0 | 386.1222 | 30.3% | 19.175 | 0 | 19.4353 | 38.87% | 45.5
2340 | 886 | 919 | 157 | 8.4625 | 20.4 | 445.9392 | 294.5239 | 0 | 254.4599 | 105.5 | 5.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 254.4599 | 0 | 628.4385 | 49.31% | 19.175 | 0 | 38.8706 | 77.74% | 44.5
2341 | 935 | 1028 | 213 | 8.6639 | 21.4 | 470.6018 | 308.6359 | 0 | 267.435 | 106.2 | 16.884 | 14.316 | 75 | 0 | 0 | 0 | 0 | 0 | 267.435 | 0 | 883.1108 | 69.29% | 10.9804 | 0 | 50 | 100% | 43.8
2342 | 778 | 875 | 224 | 7.455 | 21.7 | 391.5809 | 250.9992 | 0 | 214.2142 | 106.9 | 31.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 214.2142 | 0 | 1087.102 | 85.3% | 0 | 0 | 50 | 100% | 43.1
2343 | 630 | 689 | 223 | 12.2907 | 21.5 | 317.09 | 194.722 | 0 | 158.8096 | 97.0653 | 27.2826 | 0 | 69.7826 | 0 | 0 | 0 | 0 | 0 | 158.8096 | 0 | 1238.3328 | 97.16% | 0 | 0 | 50 | 100% | 42.5
2344 | 897 | 623 | 87 | 14.3056 | 21.7 | 451.4757 | 0 | 253.9924 | 0 | 84.1669 | 20.6335 | 0 | 63.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.3328 | 97.16% | 0 | 0 | 50 | 100% | 42.9
2345 | 736 | 402 | 80 | 16.5219 | 21.7 | 370.4416 | 0 | 173.6707 | 0 | 37.1889 | 0 | 0 | 37.1889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.3328 | 97.16% | 0 | 8.2111 | 41.6787 | 83.36% | 45.4
2346 | 33 | 77 | 67 | 13.2981 | 19.8 | 16.6095 | 0 | 0 | 0 | 5.0895 | 0 | 0 | 5.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.3328 | 97.16% | 0 | 25 | 16.3428 | 32.69% | 30.0895
2347 | 3 | 10 | 10 | 8.4625 | 17.7 | 1.51 | 0 | 0 | 0 | 0.13997 | 0 | 0 | 0.13997 | 0 | 0 | 0 | 71.0531 | 27.5335 | 0 | 71.0531 | 1172.9805 | 92.03% | 0 | 16.1266 | 0 | 0% | 43.8
2348 | 0 | 0 | 0 | 7.6565 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.7256 | 40.1 | 0 | 100.7256 | 1073.7493 | 84.25% | 0 | 0 | 0 | 0% | 40.1
2349 | 0 | 0 | 0 | 6.8506 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3624 | 37.1 | 0 | 93.3624 | 983.0805 | 77.13% | 0 | 0 | 0 | 0% | 37.1
2350 | 0 | 0 | 0 | 8.4625 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4895 | 34.7 | 0 | 87.4895 | 899.157 | 70.55% | 0 | 0 | 0 | 0% | 34.7
2351 | 0 | 0 | 0 | 8.8654 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9192 | 33.2 | 0 | 83.9192 | 819.5527 | 64.3% | 0 | 0 | 0 | 0% | 33.2
2352 | 0 | 0 | 0 | 9.8729 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6652 | 32.7 | 0 | 82.6652 | 741.3638 | 58.17% | 0 | 0 | 0 | 0% | 32.7
2353 | 0 | 0 | 0 | 10.8803 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0554 | 32.5 | 0 | 82.0554 | 663.7312 | 52.08% | 0 | 0 | 0 | 0% | 32.5
2354 | 0 | 0 | 0 | 7.2535 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8941 | 33.3 | 0 | 83.8941 | 583.8026 | 45.81% | 0 | 0 | 0 | 0% | 33.3
2355 | 0 | 0 | 0 | 5.0372 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0179 | 36.7 | 0 | 92.0179 | 494.1772 | 38.77% | 0 | 0 | 0 | 0% | 36.7
2356 | 0 | 0 | 0 | 9.8729 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7133 | 42 | 0 | 104.7133 | 389.4494 | 30.56% | 0 | 0 | 0 | 0% | 42
2357 | 0 | 0 | 0 | 12.6937 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4074 | 45.2 | 0 | 112.4074 | 275.5066 | 21.62% | 0 | 0 | 0 | 0% | 45.2
2358 | 15 | 3 | 2 | 8.6639 | 12.5 | 7.5498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.0396 | 46.7 | 0 | 116.0396 | 157.2118 | 12.34% | 0 | 0 | 0 | 0% | 46.7
2359 | 505 | 110 | 30 | 13.0966 | 13.4 | 254.1753 | 112.2746 | 0 | 80.9767 | 3.809 | 0 | 0 | 3.809 | 0 | 0 | 0 | 0 | 0 | 80.9767 | 0 | 234.6234 | 18.41% | 0 | 0 | 0 | 0% | 3.809
2360 | 790 | 326 | 53 | 12.2907 | 14.9 | 397.6207 | 217.459 | 0 | 179.8702 | 29.0893 | 0 | 0 | 29.0893 | 0 | 0 | 0 | 0 | 0 | 179.8702 | 0 | 406.5746 | 31.9% | 0 | 0 | 0 | 0% | 29.0893
2361 | 900 | 539 | 64 | 15.9175 | 16 | 452.9856 | 274.0823 | 0 | 230.4432 | 64.8192 | 0 | 8.4596 | 56.3596 | 0 | 0 | 0 | 0 | 0 | 230.4432 | 0 | 626.8722 | 49.19% | 6.4885 | 0 | 6.5775 | 13.15% | 47.9
2362 | 959 | 723 | 69 | 13.9026 | 17 | 482.6814 | 307.0888 | 0 | 262.6535 | 102.6 | 2.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 262.6535 | 0 | 877.9621 | 68.89% | 19.175 | 0 | 26.0155 | 52.03% | 47.4
2363 | 995 | 861 | 71 | 15.716 | 18 | 500.8008 | 327.133 | 0 | 280.2824 | 104.3 | 4.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 280.2824 | 0 | 1145.9047 | 89.91% | 19.175 | 0 | 45.4535 | 90.91% | 45.7
2364 | 1011 | 941 | 73 | 14.7085 | 18.9 | 508.8539 | 277.5185 | 58.6022 | 238.9047 | 105.2 | 24.3526 | 5.8474 | 75 | 0 | 0 | 0 | 0 | 0 | 238.9047 | 0 | 1274.5104 | 100% | 4.4849 | 0 | 50 | 100% | 44.8
2365 | 991 | 970 | 108 | 13.7011 | 19.6 | 498.7875 | 0 | 327.2176 | 0 | 106 | 31 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44
2366 | 830 | 927 | 237 | 13.7011 | 20.4 | 417.7534 | 0 | 267.8312 | 0 | 106 | 31 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44
2367 | 934 | 796 | 110 | 20.3502 | 20.3 | 470.0984 | 0 | 288.9263 | 0 | 106.3 | 31.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.7
2368 | 929 | 630 | 74 | 21.1561 | 19.4 | 467.5819 | 0 | 263.5878 | 0 | 86.2488 | 21.1744 | 0 | 65.0744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.9
2369 | 835 | 425 | 68 | 17.5294 | 18.6 | 420.27 | 0 | 197.9472 | 0 | 40.3658 | 0 | 0 | 40.3658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.3342 | 44.5935 | 89.19% | 45.7
2370 | 662 | 200 | 43 | 13.7011 | 17.7 | 333.1961 | 0 | 0 | 0 | 11.6072 | 0 | 0 | 11.6072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 19.2541 | 38.51% | 36.6072
2371 | 135 | 23 | 10 | 11.4848 | 15.8 | 67.9478 | 0 | 0 | 0 | 0.062851 | 0 | 0 | 0.062851 | 0 | 0 | 0 | 64.7208 | 24.8406 | 0 | 64.7208 | 1215.2104 | 95.35% | 0 | 18.9965 | 0 | 0% | 43.9
2372 | 0 | 0 | 0 | 10.0743 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.379 | 40.1 | 0 | 100.379 | 1115.9782 | 87.56% | 0 | 0 | 0 | 0% | 40.1
2373 | 0 | 0 | 0 | 9.2684 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5849 | 37.3 | 0 | 93.5849 | 1024.7432 | 80.4% | 0 | 0 | 0 | 0% | 37.3
2374 | 0 | 0 | 0 | 11.2833 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2249 | 35.1 | 0 | 88.2249 | 939.6662 | 73.73% | 0 | 0 | 0 | 0% | 35.1
2375 | 0 | 0 | 0 | 8.261 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6181 | 33.6 | 0 | 84.6181 | 858.9142 | 67.39% | 0 | 0 | 0 | 0% | 33.6
2376 | 0 | 0 | 0 | 7.052 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.112 | 33 | 0 | 83.112 | 779.8701 | 61.19% | 0 | 0 | 0 | 0% | 33
2377 | 0 | 0 | 0 | 6.8506 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8569 | 32.9 | 0 | 82.8569 | 701.0993 | 55.01% | 0 | 0 | 0 | 0% | 32.9
2378 | 0 | 0 | 0 | 3.0223 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4929 | 33.6 | 0 | 84.4929 | 620.31 | 48.67% | 0 | 0 | 0 | 0% | 33.6
2379 | 0 | 0 | 0 | 3.2238 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5825 | 37 | 0 | 92.5825 | 529.8393 | 41.57% | 0 | 0 | 0 | 0% | 37
2380 | 0 | 0 | 0 | 2.0149 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2102 | 42.3 | 0 | 105.2102 | 424.2606 | 33.29% | 0 | 0 | 0 | 0% | 42.3
2381 | 0 | 0 | 0 | 4.0297 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.1504 | 45.6 | 0 | 113.1504 | 309.1771 | 24.26% | 0 | 0 | 0 | 0% | 45.6
2382 | 16 | 3 | 2 | 10.8803 | 11 | 8.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.3902 | 46.9 | 0 | 116.3902 | 190.312 | 14.93% | 0 | 0 | 0 | 0% | 46.9
2383 | 534 | 116 | 27 | 16.5219 | 12.4 | 268.7715 | 119.1726 | 0 | 85.5345 | 3.7109 | 0 | 0 | 3.7109 | 0 | 0 | 0 | 103.9392 | 41.6875 | 85.5345 | 103.9392 | 168.249 | 13.2% | 0 | 0 | 0 | 0% | 45.3983
2384 | 820 | 334 | 46 | 14.5071 | 13.9 | 412.7203 | 225.9137 | 0 | 186.3846 | 29.5461 | 0 | 0 | 29.5461 | 0 | 0 | 0 | 0 | 0 | 186.3846 | 0 | 346.9327 | 27.22% | 0 | 0 | 0 | 0% | 29.5461
2385 | 927 | 550 | 55 | 15.9175 | 15.3 | 466.5752 | 282.364 | 0 | 238.2432 | 66.9334 | 0 | 9.8167 | 57.1167 | 0 | 0 | 0 | 0 | 0 | 238.2432 | 0 | 575.3323 | 45.14% | 7.5294 | 0 | 7.6338 | 15.27% | 47.3
2386 | 970 | 729 | 63 | 15.716 | 16.6 | 488.2179 | 310.5797 | 0 | 264.7836 | 103.1 | 3.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 264.7836 | 0 | 829.1757 | 65.06% | 19.175 | 0 | 27.0745 | 54.15% | 46.9
2387 | 994 | 931 | 135 | 12.8952 | 17.9 | 500.2975 | 326.8137 | 0 | 281.6983 | 104.8 | 4.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 281.6983 | 0 | 1099.235 | 86.25% | 19.175 | 0 | 46.5154 | 93.03% | 45.2
2388 | 935 | 994 | 184 | 11.0818 | 19.2 | 470.6018 | 252.6532 | 58.1996 | 217.7906 | 105.5 | 26.0189 | 4.4811 | 75 | 0 | 0 | 0 | 0 | 0 | 217.7906 | 0 | 1274.5104 | 100% | 3.437 | 0 | 50 | 100% | 44.5
2389 | 993 | 1029 | 160 | 11.8877 | 20.4 | 499.7942 | 0 | 327.9739 | 0 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.9
2390 | 664 | 879 | 317 | 11.4848 | 19.3 | 334.2027 | 0 | 214.3091 | 0 | 106.7 | 31.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.3
2391 | 173 | 348 | 217 | 7.6565 | 18.1 | 87.0739 | 0 | 53.5608 | 0 | 32.784 | 0 | 0 | 32.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.916 | 39.9481 | 79.9% | 42.7
2392 | 797 | 578 | 104 | 11.4848 | 18.8 | 401.144 | 0 | 226.5874 | 0 | 75.6668 | 3.3575 | 12.926 | 59.3834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 9.9142 | 0 | 50 | 100% | 43.1
2393 | 637 | 337 | 69 | 12.4922 | 17.8 | 320.6132 | 0 | 151.7005 | 0 | 32.2607 | 0 | 0 | 32.2607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 12.8393 | 36.9844 | 73.97% | 45.1
2394 | 671 | 202 | 42 | 9.0669 | 17.1 | 337.726 | 0 | 0 | 0 | 11.5214 | 0 | 0 | 11.5214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 11.6405 | 23.28% | 36.5214
2395 | 66 | 19 | 13 | 6.2461 | 15.4 | 33.2189 | 0 | 0 | 0 | 0.2158 | 0 | 0 | 0.2158 | 0 | 0 | 0 | 80.0798 | 31.6009 | 0 | 80.0798 | 1199.4933 | 94.11% | 0 | 11.4833 | 0 | 0% | 43.3
2396 | 0 | 0 | 0 | 7.052 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5229 | 40.2 | 0 | 100.5229 | 1100.0007 | 86.31% | 0 | 0 | 0 | 0% | 40.2
2397 | 0 | 0 | 0 | 12.2907 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6492 | 37.4 | 0 | 93.6492 | 1008.5006 | 79.13% | 0 | 0 | 0 | 0% | 37.4
2398 | 0 | 0 | 0 | 6.6491 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4428 | 34.9 | 0 | 87.4428 | 924.0098 | 72.5% | 0 | 0 | 0 | 0% | 34.9
2399 | 0 | 0 | 0 | 4.0297 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3897 | 33.6 | 0 | 84.3897 | 843.2732 | 66.16% | 0 | 0 | 0 | 0% | 33.6
2400 | 0 | 0 | 0 | 4.6342 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7137 | 32.9 | 0 | 82.7137 | 764.5292 | 59.99% | 0 | 0 | 0 | 0% | 32.9
2401 | 0 | 0 | 0 | 7.2535 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2498 | 32.7 | 0 | 82.2498 | 686.3428 | 53.85% | 0 | 0 | 0 | 0% | 32.7
2402 | 0 | 0 | 0 | 3.6268 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3874 | 33.6 | 0 | 84.3874 | 605.5681 | 47.51% | 0 | 0 | 0 | 0% | 33.6
2403 | 0 | 0 | 0 | 4.0297 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5135 | 37 | 0 | 92.5135 | 515.1139 | 40.42% | 0 | 0 | 0 | 0% | 37
2404 | 0 | 0 | 0 | 2.2164 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7291 | 42.1 | 0 | 104.7291 | 410.1235 | 32.18% | 0 | 0 | 0 | 0% | 42.1
2405 | 0 | 0 | 0 | 2.2164 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4049 | 45.3 | 0 | 112.4049 | 295.9218 | 23.22% | 0 | 0 | 0 | 0% | 45.3
2406 | 31 | 4 | 2 | 1.4104 | 7.6 | 15.6028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.5229 | 46.6 | 0 | 115.5229 | 177.9575 | 13.96% | 0 | 0 | 0 | 0% | 46.6
2407 | 558 | 119 | 27 | 1.6119 | 10.4 | 280.8511 | 124.8571 | 0 | 98.9537 | 3.9525 | 0 | 0 | 3.9525 | 0 | 0 | 0 | 92.6595 | 37.0525 | 98.9537 | 92.6595 | 182.0113 | 14.28% | 0 | 0 | 0 | 0% | 41.005
2408 | 821 | 336 | 43 | 2.0149 | 13.7 | 413.2236 | 226.3838 | 0 | 193.8004 | 28.7711 | 0 | 0 | 28.7711 | 0 | 0 | 0 | 0 | 0 | 193.8004 | 0 | 367.5916 | 28.84% | 0 | 0 | 0 | 0% | 28.7711
2409 | 927 | 550 | 51 | 2.0149 | 16.2 | 466.5752 | 282.4222 | 0 | 246.1495 | 62.1059 | 0 | 7.703 | 54.403 | 0 | 0 | 0 | 0 | 0 | 246.1495 | 0 | 603.3007 | 47.34% | 5.9082 | 0 | 5.991 | 11.98% | 46.7
2410 | 980 | 735 | 59 | 3.0223 | 17.2 | 493.251 | 313.7502 | 0 | 275.0825 | 101.043 | 2.3215 | 25 | 73.7215 | 0 | 0 | 0 | 0 | 0 | 275.0825 | 0 | 866.7155 | 68% | 19.175 | 0 | 25.435 | 50.87% | 46.4
2411 | 895 | 881 | 162 | 3.6268 | 18.4 | 450.4691 | 294.2724 | 0 | 256.7894 | 105.1 | 5.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 256.7894 | 0 | 1112.6131 | 87.3% | 19.175 | 0 | 44.879 | 89.76% | 44.9
2412 | 893 | 977 | 201 | 7.455 | 19.2 | 449.4624 | 235.0577 | 61.8308 | 203.6628 | 105.7 | 24.1157 | 6.5843 | 75 | 0 | 0 | 0 | 0 | 0 | 203.6628 | 0 | 1274.5104 | 100% | 5.0502 | 0 | 50 | 100% | 44.3
2413 | 998 | 1015 | 140 | 9.4699 | 19.4 | 502.3108 | 0 | 329.7207 | 0 | 106.2 | 31.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.8
2414 | 939 | 950 | 163 | 8.4625 | 20 | 472.615 | 0 | 303.1282 | 0 | 106.7 | 31.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.3
2415 | 534 | 618 | 221 | 7.6565 | 19.9 | 268.7715 | 0 | 165.4617 | 0 | 80.1211 | 18.7606 | 0 | 61.3606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
2416 | 848 | 712 | 197 | 9.0669 | 20.5 | 426.8131 | 0 | 241.5611 | 0 | 96.0025 | 26.6513 | 0 | 69.3513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.7
2417 | 707 | 404 | 106 | 8.6639 | 20.1 | 355.8454 | 0 | 169.1304 | 0 | 37.7536 | 0 | 0 | 37.7536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.7464 | 43.16 | 86.32% | 44.5
2418 | 688 | 217 | 51 | 8.4625 | 19.1 | 346.2824 | 0 | 0 | 0 | 12.3146 | 0 | 0 | 12.3146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.8128 | 35.63% | 37.3146
2419 | 160 | 26 | 10 | 7.858 | 17.1 | 80.5308 | 0 | 0 | 0 | 0.058588 | 0 | 0 | 0.058588 | 0 | 0 | 0 | 67.0001 | 25.7723 | 0 | 67.0001 | 1213.0478 | 95.18% | 0 | 17.5691 | 0 | 0% | 43.4
2420 | 0 | 0 | 0 | 4.6342 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6885 | 40.2 | 0 | 100.6885 | 1113.5559 | 87.37% | 0 | 0 | 0 | 0% | 40.2
2421 | 0 | 0 | 0 | 3.6268 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9904 | 37.5 | 0 | 93.9904 | 1021.7731 | 80.17% | 0 | 0 | 0 | 0% | 37.5
2422 | 0 | 0 | 0 | 1.4104 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1295 | 35.1 | 0 | 88.1295 | 936.7132 | 73.5% | 0 | 0 | 0 | 0% | 35.1
2423 | 0 | 0 | 0 | 2.0149 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9999 | 33.4 | 0 | 83.9999 | 856.5517 | 67.21% | 0 | 0 | 0 | 0% | 33.4
2424 | 0 | 0 | 0 | 1.6119 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5366 | 32.8 | 0 | 82.5366 | 778.0936 | 61.05% | 0 | 0 | 0 | 0% | 32.8
2425 | 0 | 0 | 0 | 1.6119 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2536 | 32.7 | 0 | 82.2536 | 699.9083 | 54.92% | 0 | 0 | 0 | 0% | 32.7
2426 | 0 | 0 | 0 | 1.8134 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8989 | 33.4 | 0 | 83.8989 | 619.7096 | 48.62% | 0 | 0 | 0 | 0% | 33.4
2427 | 0 | 0 | 0 | 3.2238 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7536 | 36.7 | 0 | 91.7536 | 530.1036 | 41.59% | 0 | 0 | 0 | 0% | 36.7
2428 | 0 | 0 | 0 | 3.0223 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.5257 | 41.6 | 0 | 103.5257 | 426.5351 | 33.47% | 0 | 0 | 0 | 0% | 41.6
2429 | 0 | 0 | 0 | 2.4178 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.2303 | 44.4 | 0 | 110.2303 | 314.929 | 24.71% | 0 | 0 | 0 | 0% | 44.4
2430 | 29 | 4 | 3 | 2.2164 | 7.8 | 14.5962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.8461 | 45.9 | 0 | 113.8461 | 198.9801 | 15.61% | 0 | 0 | 0 | 0% | 45.9
2431 | 523 | 122 | 32 | 1.8134 | 11 | 263.235 | 117.3061 | 0 | 91.9937 | 4.1775 | 0 | 0 | 4.1775 | 0 | 0 | 0 | 104.8855 | 42.1225 | 91.9937 | 104.8855 | 181.7762 | 14.26% | 0 | 0 | 0 | 0% | 46.3
2432 | 792 | 338 | 52 | 2.0149 | 14 | 398.6274 | 218.5729 | 0 | 186.4834 | 28.7705 | 0 | 0 | 28.7705 | 0 | 0 | 0 | 0 | 0 | 186.4834 | 0 | 360.3804 | 28.28% | 0 | 0 | 0 | 0% | 28.7705
2433 | 905 | 553 | 62 | 5.0372 | 17.1 | 455.5022 | 275.7756 | 0 | 238.7852 | 63.9882 | 0 | 8.9441 | 55.0441 | 0 | 0 | 0 | 0 | 0 | 238.7852 | 0 | 589.0766 | 46.22% | 6.8601 | 0 | 6.9574 | 13.91% | 46.1
2434 | 965 | 737 | 67 | 10.4773 | 19.1 | 485.7013 | 308.9174 | 0 | 266.5295 | 104.6 | 4.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 266.5295 | 0 | 844.3449 | 66.25% | 19.175 | 0 | 26.4041 | 52.81% | 45.4
2435 | 989 | 868 | 73 | 11.4848 | 19.9 | 497.7809 | 325.1887 | 0 | 281.1075 | 106 | 6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 281.1075 | 0 | 1113.5752 | 87.37% | 19.175 | 0 | 45.8509 | 91.7% | 44
2436 | 989 | 942 | 83 | 10.0743 | 20 | 497.7809 | 233.5367 | 95.2672 | 202.6833 | 107.1 | 26.7661 | 5.3339 | 75 | 0 | 0 | 0 | 0 | 0 | 202.6833 | 0 | 1274.5104 | 100% | 4.0911 | 0 | 50 | 100% | 42.9
2437 | 988 | 955 | 87 | 10.6788 | 20.4 | 497.2776 | 0 | 326.5103 | 0 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
2438 | 969 | 904 | 92 | 13.9026 | 20.3 | 487.7145 | 0 | 312.8756 | 0 | 108.6 | 33.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.4
2439 | 931 | 781 | 88 | 13.2981 | 20 | 468.5885 | 0 | 288.7062 | 0 | 109.3 | 34.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.7
2440 | 892 | 617 | 76 | 12.0892 | 19.7 | 448.9591 | 0 | 254.5867 | 0 | 83.1096 | 21.2548 | 0 | 61.8548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.6
2441 | 806 | 414 | 63 | 11.0818 | 19.3 | 405.6738 | 0 | 193.6697 | 0 | 37.9454 | 0 | 0 | 37.9454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 4.0546 | 45.8885 | 91.78% | 42
2442 | 633 | 199 | 44 | 10.2758 | 18.1 | 318.5999 | 0 | 0 | 0 | 10.9976 | 0 | 0 | 10.9976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 20.5378 | 41.08% | 35.9976
2443 | 147 | 26 | 11 | 9.6714 | 16 | 73.9877 | 0 | 0 | 0 | 0.10716 | 0 | 0 | 0.10716 | 0 | 0 | 0 | 56.0026 | 21.0389 | 0 | 56.0026 | 1223.61 | 96.01% | 0 | 20.2539 | 0 | 0% | 41.4
2444 | 0 | 0 | 0 | 7.455 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2144 | 38.8 | 0 | 97.2144 | 1128.1342 | 88.52% | 0 | 0 | 0 | 0% | 38.8
2445 | 0 | 0 | 0 | 6.4476 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.294 | 36.8 | 0 | 92.294 | 1038.3294 | 81.47% | 0 | 0 | 0 | 0% | 36.8
2446 | 0 | 0 | 0 | 1.6119 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6501 | 34.5 | 0 | 86.6501 | 955.0039 | 74.93% | 0 | 0 | 0 | 0% | 34.5
2447 | 0 | 0 | 0 | 2.4178 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3223 | 32.7 | 0 | 82.3223 | 876.8419 | 68.8% | 0 | 0 | 0 | 0% | 32.7
2448 | 0 | 0 | 0 | 2.6193 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9153 | 31.7 | 0 | 79.9153 | 801.4974 | 62.89% | 0 | 0 | 0 | 0% | 31.7
2449 | 0 | 0 | 0 | 1.4104 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6172 | 31.2 | 0 | 78.6172 | 727.544 | 57.08% | 0 | 0 | 0 | 0% | 31.2
2450 | 0 | 0 | 0 | 3.2238 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0981 | 31 | 0 | 78.0981 | 654.1377 | 51.32% | 0 | 0 | 0 | 0% | 31
2451 | 0 | 0 | 0 | 3.4253 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2893 | 31.9 | 0 | 80.2893 | 578.1937 | 45.37% | 0 | 0 | 0 | 0% | 31.9
2452 | 0 | 0 | 0 | 4.4327 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4114 | 33.2 | 0 | 83.4114 | 498.5405 | 39.12% | 0 | 0 | 0 | 0% | 33.2
2453 | 0 | 0 | 0 | 2.2164 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3797 | 35.3 | 0 | 88.3797 | 412.8244 | 32.39% | 0 | 0 | 0 | 0% | 35.3
2454 | 34 | 5 | 3 | 1.6119 | 8.1 | 17.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0125 | 38.5 | 0 | 96.0125 | 318.0569 | 24.96% | 0 | 0 | 0 | 0% | 38.5
2455 | 529 | 126 | 33 | 1.2089 | 11.3 | 266.2549 | 118.9344 | 0 | 93.6937 | 4.3135 | 0 | 0 | 4.3135 | 0 | 0 | 0 | 90.3777 | 36.0865 | 93.6937 | 90.3777 | 318.3259 | 24.98% | 0 | 0 | 0 | 0% | 40.4
2456 | 788 | 342 | 54 | 1.4104 | 16.3 | 396.6141 | 217.6516 | 0 | 185.8523 | 28.5752 | 0 | 0 | 28.5752 | 0 | 0 | 0 | 0 | 0 | 185.8523 | 0 | 493.5142 | 38.72% | 0 | 0 | 0 | 0% | 28.5752
2457 | 900 | 557 | 65 | 2.6193 | 18.9 | 452.9856 | 274.3069 | 0 | 238.2957 | 67.7418 | 0 | 13.7209 | 54.0209 | 0 | 0 | 0 | 0 | 0 | 238.2957 | 0 | 718.1368 | 56.35% | 10.5239 | 0 | 10.6746 | 21.35% | 40.3
2458 | 967 | 742 | 67 | 4.2312 | 20.4 | 486.7079 | 309.5276 | 0 | 270.7531 | 106.8578 | 8.4789 | 25 | 73.3789 | 0 | 0 | 0 | 0 | 0 | 270.7531 | 0 | 973.3544 | 76.37% | 19.175 | 0 | 30.1241 | 60.25% | 39.9
2459 | 996 | 876 | 69 | 6.2461 | 21.6 | 501.3041 | 327.5 | 0 | 286.5217 | 111.2 | 11.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 286.5217 | 0 | 1243.4359 | 97.56% | 19.175 | 0 | 49.5737 | 99.15% | 38.8
2460 | 1001 | 949 | 74 | 7.858 | 22.4 | 503.8207 | 0 | 332.7924 | 0 | 113 | 38 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.4359 | 97.56% | 0 | 0 | 49.5737 | 99.15% | 37
2461 | 992 | 956 | 80 | 11.4848 | 22.7 | 499.2908 | 0 | 327.9249 | 0 | 114 | 39 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.4359 | 97.56% | 0 | 0 | 49.5737 | 99.15% | 36
2462 | 974 | 901 | 82 | 12.6937 | 22.5 | 490.2311 | 0 | 314.5521 | 0 | 114.7 | 39.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.4359 | 97.56% | 0 | 0 | 49.5737 | 99.15% | 35.3
2463 | 942 | 786 | 81 | 11.6862 | 22.4 | 474.125 | 0 | 292.3491 | 0 | 114.9 | 39.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.4359 | 97.56% | 0 | 0 | 49.5737 | 99.15% | 35.1
2464 | 905 | 624 | 71 | 11.6862 | 22.4 | 455.5022 | 0 | 258.7882 | 0 | 87.5467 | 26.1234 | 0 | 61.4234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.4359 | 97.56% | 0 | 0 | 49.5737 | 99.15% | 35.3
2465 | 824 | 422 | 61 | 11.0818 | 21.7 | 414.7335 | 0 | 198.8599 | 0 | 39.0034 | 1.0517 | 0 | 37.9517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.4359 | 97.56% | 0 | 0 | 49.5737 | 99.15% | 36.9
2466 | 644 | 202 | 41 | 10.6788 | 20.3 | 324.1364 | 0 | 0 | 0 | 10.6758 | 0 | 0 | 10.6758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.4359 | 97.56% | 0 | 25 | 24.2195 | 48.44% | 35.6758
2467 | 154 | 27 | 12 | 9.8729 | 18.3 | 77.5109 | 0 | 0 | 0 | 0.15156 | 0 | 0 | 0.15156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.4359 | 97.56% | 0 | 23.8812 | 0 | 0% | 24.0327
2468 | 0 | 0 | 0 | 6.8506 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2489 | 36.2 | 0 | 91.2489 | 1155.2877 | 90.65% | 0 | 0 | 0 | 0% | 36.2
2469 | 0 | 0 | 0 | 2.4178 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5021 | 33.9 | 0 | 85.5021 | 1073.6725 | 84.24% | 0 | 0 | 0 | 0% | 33.9
2470 | 0 | 0 | 0 | 3.0223 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.81 | 31.6 | 0 | 79.81 | 998.5962 | 78.35% | 0 | 0 | 0 | 0% | 31.6
2471 | 0 | 0 | 0 | 2.8208 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1725 | 30.1 | 0 | 76.1725 | 927.6889 | 72.79% | 0 | 0 | 0 | 0% | 30.1
2472 | 0 | 0 | 0 | 2.8208 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1556 | 29.2 | 0 | 74.1556 | 859.0084 | 67.4% | 0 | 0 | 0 | 0% | 29.2
2473 | 0 | 0 | 0 | 4.6342 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9358 | 28.6 | 0 | 72.9358 | 791.7547 | 62.12% | 0 | 0 | 0 | 0% | 28.6
2474 | 0 | 0 | 0 | 2.8208 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5963 | 28.5 | 0 | 72.5963 | 724.7666 | 56.87% | 0 | 0 | 0 | 0% | 28.5
2475 | 0 | 0 | 0 | 1.8134 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8392 | 29.1 | 0 | 73.8392 | 656.3002 | 51.49% | 0 | 0 | 0 | 0% | 29.1
2476 | 0 | 0 | 0 | 0.80595 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5257 | 29.4 | 0 | 74.5257 | 587.0874 | 46.06% | 0 | 0 | 0 | 0% | 29.4
2477 | 0 | 0 | 0 | 3.2238 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.758 | 30.4 | 0 | 76.758 | 515.283 | 40.43% | 0 | 0 | 0 | 0% | 30.4
2478 | 37 | 6 | 4 | 4.8357 | 12.3 | 18.6227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0331 | 33.4 | 0 | 84.0331 | 434.993 | 34.13% | 0 | 0 | 0 | 0% | 33.4
2479 | 493 | 132 | 44 | 2.4178 | 14.5 | 248.1355 | 111.1029 | 0 | 85.7689 | 4.9306 | 0 | 0 | 4.9306 | 0 | 0 | 0 | 77.464 | 30.5694 | 85.7689 | 77.464 | 442.4609 | 34.72% | 0 | 0 | 0 | 0% | 35.5
2480 | 709 | 331 | 65 | 1.6119 | 17.9 | 356.852 | 195.9937 | 0 | 165.5283 | 27.1187 | 0 | 0 | 27.1187 | 0 | 0 | 0 | 0 | 0 | 165.5283 | 0 | 596.3368 | 46.79% | 0 | 0 | 0 | 0% | 27.1187
2481 | 877 | 550 | 66 | 4.2312 | 20.6 | 441.4093 | 267.3497 | 0 | 231.2098 | 70.0207 | 0 | 16.9104 | 53.1104 | 0 | 0 | 0 | 0 | 0 | 231.2098 | 0 | 811.2706 | 63.65% | 12.9702 | 0 | 13.1578 | 26.32% | 36.2
2482 | 935 | 730 | 72 | 6.4476 | 22.3 | 470.6018 | 299.2562 | 0 | 260.0977 | 107.8737 | 10.7869 | 25 | 72.0869 | 0 | 0 | 0 | 0 | 0 | 260.0977 | 0 | 1053.0586 | 82.62% | 19.175 | 0 | 32.6101 | 65.22% | 36.3
2483 | 965 | 862 | 75 | 7.2535 | 23.7 | 485.7013 | 317.3161 | 0 | 276.4244 | 114.1 | 16.7506 | 22.3494 | 75 | 0 | 0 | 0 | 0 | 0 | 276.4244 | 0 | 1274.5104 | 100% | 17.142 | 0 | 50 | 100% | 35.9
2484 | 975 | 935 | 79 | 9.0669 | 24.7 | 490.7345 | 0 | 324.1473 | 0 | 115.7 | 40.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.3
2485 | 973 | 946 | 81 | 8.261 | 25.2 | 489.7278 | 0 | 321.734 | 0 | 116.7 | 41.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.3
2486 | 963 | 892 | 78 | 11.0818 | 25.6 | 484.6946 | 0 | 311.0602 | 0 | 117.2 | 42.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.8
2487 | 940 | 780 | 74 | 11.2833 | 25.6 | 473.1183 | 0 | 291.9561 | 0 | 117.2 | 42.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.8
2488 | 892 | 616 | 68 | 11.0818 | 25.8 | 448.9591 | 0 | 255.547 | 0 | 85.5625 | 26.0812 | 0 | 59.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.4
2489 | 805 | 414 | 58 | 11.8877 | 24.7 | 405.1705 | 0 | 195.1092 | 0 | 37.4814 | 1.0407 | 0 | 36.4407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.4
2490 | 606 | 198 | 45 | 10.2758 | 23.4 | 305.0103 | 0 | 0 | 0 | 10.3628 | 0 | 0 | 10.3628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.6422 | 49.28% | 35.3628
2491 | 67 | 22 | 14 | 6.2461 | 20.9 | 33.7223 | 0 | 0 | 0 | 0.24613 | 0 | 0 | 0.24613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.2946 | 0 | 0% | 24.5408
2492 | 0 | 0 | 0 | 5.2387 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8142 | 35.9 | 0 | 90.8142 | 1187.1689 | 93.15% | 0 | 0 | 0 | 0% | 35.9
2493 | 0 | 0 | 0 | 1.8134 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.818 | 33.5 | 0 | 84.818 | 1106.6746 | 86.83% | 0 | 0 | 0 | 0% | 33.5
2494 | 0 | 0 | 0 | 0.80595 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9806 | 31.5 | 0 | 79.9806 | 1031.8513 | 80.96% | 0 | 0 | 0 | 0% | 31.5
2495 | 0 | 0 | 0 | 1.8134 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.582 | 30.1 | 0 | 76.582 | 960.918 | 75.4% | 0 | 0 | 0 | 0% | 30.1
2496 | 0 | 0 | 0 | 1.6119 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.5711 | 29.7 | 0 | 75.5711 | 890.9874 | 69.91% | 0 | 0 | 0 | 0% | 29.7
2497 | 0 | 0 | 0 | 2.2164 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4245 | 29.6 | 0 | 75.4245 | 821.2922 | 64.44% | 0 | 0 | 0 | 0% | 29.6
2498 | 0 | 0 | 0 | 2.2164 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2061 | 30.4 | 0 | 77.2061 | 749.4984 | 58.81% | 0 | 0 | 0 | 0% | 30.4
2499 | 0 | 0 | 0 | 0.60446 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0646 | 34.2 | 0 | 86.0646 | 666.9148 | 52.33% | 0 | 0 | 0 | 0% | 34.2
2500 | 0 | 0 | 0 | 3.4253 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5206 | 38.1 | 0 | 95.5206 | 573.2501 | 44.98% | 0 | 0 | 0 | 0% | 38.1
2501 | 0 | 0 | 0 | 3.6268 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.0072 | 40.8 | 0 | 102.0072 | 471.8462 | 37.02% | 0 | 0 | 0 | 0% | 40.8
2502 | 3 | 5 | 5 | 3.0223 | 13.8 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9446 | 42.9 | 0 | 106.9446 | 364.4503 | 28.6% | 0 | 0 | 0 | 0% | 42.9
2503 | 158 | 83 | 53 | 4.4327 | 16.3 | 79.5241 | 0 | 35.6908 | 0 | 4.1639 | 0 | 0 | 4.1639 | 0 | 0 | 0 | 99.9239 | 39.8361 | 0 | 99.9239 | 265.7266 | 20.85% | 0 | 0 | 0 | 0% | 44
2504 | 452 | 345 | 177 | 2.6193 | 20.5 | 227.4995 | 125.052 | 0 | 98.8257 | 27.7947 | 0 | 0 | 27.7947 | 0 | 0 | 0 | 0 | 0 | 98.8257 | 0 | 359.1727 | 28.18% | 0 | 0 | 0 | 0% | 27.7947
2505 | 390 | 459 | 233 | 2.4178 | 23.7 | 196.2938 | 118.9131 | 0 | 93.3065 | 39.8883 | 0 | 0 | 39.8883 | 0 | 0 | 0 | 0 | 0 | 93.3065 | 0 | 447.3999 | 35.1% | 0 | 0 | 0 | 0% | 39.8883
2506 | 402 | 637 | 341 | 5.2387 | 25.2 | 202.3336 | 128.6522 | 0 | 101.2579 | 68.6768 | 0 | 12.0384 | 56.6384 | 0 | 0 | 0 | 0 | 0 | 101.2579 | 0 | 543.1458 | 42.62% | 9.2335 | 0 | 9.3683 | 18.74% | 44.6
2507 | 560 | 793 | 331 | 6.8506 | 26.3 | 281.8577 | 184.1476 | 0 | 152.2934 | 105.4512 | 6.1256 | 25 | 74.3256 | 0 | 0 | 0 | 0 | 0 | 152.2934 | 0 | 687.149 | 53.91% | 19.175 | 0 | 28.8234 | 57.65% | 43.2
2508 | 70 | 588 | 514 | 8.8654 | 26.5 | 35.2322 | 0 | 23.272 | 0 | 54.7771 | 0 | 6.3385 | 48.4385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 687.149 | 53.91% | 4.8617 | 0 | 33.7561 | 67.51% | 42.1
2509 | 88 | 517 | 429 | 8.4625 | 25.6 | 44.2919 | 0 | 29.1038 | 0 | 44.1496 | 1.3248 | 0 | 42.8248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 687.149 | 53.91% | 0 | 0 | 33.7561 | 67.51% | 41.5
2510 | 171 | 519 | 363 | 7.052 | 26.6 | 86.0673 | 0 | 55.2455 | 0 | 48.1811 | 0 | 3.4905 | 44.6905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 687.149 | 53.91% | 2.6772 | 0 | 36.4725 | 72.94% | 41.2
2511 | 212 | 526 | 366 | 10.6788 | 27.5 | 106.7033 | 65.8959 | 0 | 39.1866 | 51.851 | 0 | 5.7255 | 46.1255 | 0 | 0 | 0 | 0 | 0 | 39.1866 | 0 | 724.2025 | 56.82% | 4.3915 | 0 | 40.9281 | 81.86% | 40.4
2512 | 515 | 568 | 245 | 10.4773 | 27.9 | 259.2085 | 147.8114 | 0 | 116.342 | 62.766 | 0 | 11.133 | 51.633 | 0 | 0 | 0 | 0 | 0 | 116.342 | 0 | 834.2113 | 65.45% | 8.539 | 0 | 49.5919 | 99.18% | 40.5
2513 | 397 | 373 | 191 | 7.2535 | 25.8 | 199.817 | 96.6278 | 0 | 70.0918 | 30.6691 | 0 | 0 | 30.6691 | 0 | 0 | 0 | 0 | 0 | 70.0918 | 0 | 900.4876 | 70.65% | 0 | 11.3309 | 38.0973 | 76.19% | 42
2514 | 211 | 166 | 109 | 6.4476 | 23.4 | 106.2 | 0 | 0 | 0 | 10.3802 | 0 | 0 | 10.3802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900.4876 | 70.65% | 0 | 25 | 12.7353 | 25.47% | 35.3802
2515 | 24 | 22 | 20 | 5.0372 | 20.4 | 12.0796 | 0 | 0 | 0 | 0.60804 | 0 | 0 | 0.60804 | 0 | 0 | 0 | 72.0905 | 27.8378 | 0 | 72.0905 | 834.0884 | 65.44% | 0 | 12.5541 | 0 | 0% | 41
2516 | 0 | 0 | 0 | 2.6193 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5243 | 37.9 | 0 | 95.5243 | 741.0669 | 58.15% | 0 | 0 | 0 | 0% | 37.9
2517 | 0 | 0 | 0 | 4.4327 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8908 | 35.7 | 0 | 89.8908 | 654.2385 | 51.33% | 0 | 0 | 0 | 0% | 35.7
2518 | 0 | 0 | 0 | 4.0297 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6683 | 33.6 | 0 | 84.6683 | 573.4106 | 44.99% | 0 | 0 | 0 | 0% | 33.6
2519 | 0 | 0 | 0 | 3.4253 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4956 | 32.3 | 0 | 81.4956 | 496.2824 | 38.94% | 0 | 0 | 0 | 0% | 32.3
2520 | 0 | 0 | 0 | 3.0223 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8258 | 31.6 | 0 | 79.8258 | 421.1163 | 33.04% | 0 | 0 | 0 | 0% | 31.6
2521 | 0 | 0 | 0 | 4.4327 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7626 | 31.6 | 0 | 79.7626 | 345.9332 | 27.14% | 0 | 0 | 0 | 0% | 31.6
2522 | 0 | 0 | 0 | 2.4178 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5279 | 32.3 | 0 | 81.5279 | 268.7518 | 21.09% | 0 | 0 | 0 | 0% | 32.3
2523 | 0 | 0 | 0 | 3.6268 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2075 | 35.1 | 0 | 88.2075 | 183.4789 | 14.4% | 0 | 0 | 0 | 0% | 35.1
2524 | 0 | 0 | 0 | 4.2312 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.4789 | 14.4% | 0 | 0 | 0 | 0% | 0
2525 | 0 | 0 | 0 | 4.8357 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.4789 | 14.4% | 0 | 0 | 0 | 0% | 0
2526 | 13 | 4 | 4 | 2.8208 | 11.9 | 6.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.4789 | 14.4% | 0 | 0 | 0 | 0% | 0
2527 | 520 | 136 | 36 | 4.6342 | 14.7 | 261.725 | 117.7204 | 0 | 91.3748 | 4.5879 | 0 | 0 | 4.5879 | 0 | 0 | 0 | 0 | 0 | 91.3748 | 0 | 269.5154 | 21.15% | 0 | 0 | 0 | 0% | 4.5879
2528 | 785 | 353 | 57 | 2.0149 | 17.6 | 395.1041 | 217.3573 | 0 | 185.3661 | 28.8241 | 0 | 0 | 28.8241 | 0 | 0 | 0 | 0 | 0 | 185.3661 | 0 | 444.0521 | 34.84% | 0 | 0 | 0 | 0% | 28.8241
2529 | 889 | 563 | 67 | 3.4253 | 19.9 | 447.4492 | 271.1133 | 0 | 235.0166 | 63.0145 | 0 | 9.3072 | 53.7072 | 0 | 0 | 0 | 0 | 0 | 235.0166 | 0 | 665.3385 | 52.2% | 7.1387 | 0 | 7.2439 | 14.49% | 44.4
2530 | 926 | 737 | 80 | 3.4253 | 21.5 | 466.0719 | 296.3209 | 0 | 258.785 | 97.9333 | 1.9166 | 25 | 71.0166 | 0 | 0 | 0 | 0 | 0 | 258.785 | 0 | 909.0047 | 71.32% | 19.175 | 0 | 26.7018 | 53.4% | 44.1
2531 | 941 | 867 | 94 | 5.8431 | 22.3 | 473.6217 | 309.4432 | 0 | 269.9208 | 107.2 | 7.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 269.9208 | 0 | 1163.1562 | 91.26% | 19.175 | 0 | 46.1597 | 92.32% | 42.8
2532 | 937 | 949 | 121 | 7.858 | 22.8 | 471.6084 | 253.0002 | 58.5114 | 219.7978 | 108.3 | 28.3659 | 4.9341 | 75 | 0 | 0 | 0 | 0 | 0 | 219.7978 | 0 | 1274.5104 | 100% | 3.7845 | 0 | 50 | 100% | 41.7
2533 | 583 | 762 | 235 | 7.455 | 22.9 | 293.434 | 0 | 192.8204 | 0 | 108.0231 | 33.4616 | 0 | 74.5616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
2534 | 917 | 892 | 114 | 10.4773 | 23.2 | 461.542 | 0 | 296.3138 | 0 | 109.5 | 34.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.5
2535 | 912 | 784 | 98 | 12.8952 | 22.7 | 459.0255 | 0 | 283.6899 | 0 | 110.2 | 35.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.8
2536 | 669 | 588 | 165 | 12.8952 | 22.3 | 336.7193 | 0 | 192.3562 | 0 | 71.5591 | 15.8795 | 0 | 55.6795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.8
2537 | 456 | 349 | 162 | 13.4996 | 20.9 | 229.5127 | 0 | 111.4483 | 0 | 31.6822 | 0 | 0 | 31.6822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.4178 | 40.4447 | 80.89% | 41.1
2538 | 621 | 211 | 54 | 12.0892 | 20 | 312.5601 | 0 | 0 | 0 | 11.1283 | 0 | 0 | 11.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.0792 | 30.16% | 36.1283
2539 | 143 | 28 | 14 | 11.2833 | 17.6 | 71.9744 | 0 | 0 | 0 | 0.24812 | 0 | 0 | 0.24812 | 0 | 0 | 0 | 66.1964 | 25.3894 | 0 | 66.1964 | 1213.7793 | 95.23% | 0 | 14.8625 | 0 | 0% | 40.5
2540 | 0 | 0 | 0 | 11.0818 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0416 | 37.9 | 0 | 95.0416 | 1120.8116 | 87.94% | 0 | 0 | 0 | 0% | 37.9
2541 | 0 | 0 | 0 | 7.2535 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8479 | 35.8 | 0 | 89.8479 | 1033.7562 | 81.11% | 0 | 0 | 0 | 0% | 35.8
2542 | 0 | 0 | 0 | 6.8506 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2631 | 33.5 | 0 | 84.2631 | 953.267 | 74.79% | 0 | 0 | 0 | 0% | 33.5
2543 | 0 | 0 | 0 | 7.052 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1517 | 32.2 | 0 | 81.1517 | 876.4743 | 68.77% | 0 | 0 | 0 | 0% | 32.2
2544 | 0 | 0 | 0 | 6.2461 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9232 | 31.7 | 0 | 79.9232 | 801.0819 | 62.85% | 0 | 0 | 0 | 0% | 31.7
2545 | 0 | 0 | 0 | 6.6491 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1653 | 31.4 | 0 | 79.1653 | 726.5212 | 57% | 0 | 0 | 0 | 0% | 31.4
2546 | 0 | 0 | 0 | 5.4401 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5807 | 32 | 0 | 80.5807 | 650.2594 | 51.02% | 0 | 0 | 0 | 0% | 32
2547 | 0 | 0 | 0 | 5.2387 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0392 | 34.7 | 0 | 87.0392 | 566.2331 | 44.43% | 0 | 0 | 0 | 0% | 34.7
2548 | 0 | 0 | 0 | 5.0372 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1925 | 38.1 | 0 | 95.1925 | 472.5799 | 37.08% | 0 | 0 | 0 | 0% | 38.1
2549 | 0 | 0 | 0 | 5.2387 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1556 | 40.6 | 0 | 101.1556 | 371.7497 | 29.17% | 0 | 0 | 0 | 0% | 40.6
2550 | 3 | 9 | 9 | 6.0446 | 10.5 | 1.51 | 0 | 0 | 0 | 0.11329 | 0 | 0 | 0.11329 | 0 | 0 | 0 | 106.4322 | 42.7867 | 0 | 106.4322 | 264.6837 | 20.77% | 0 | 0 | 0 | 0% | 42.9
2551 | 163 | 137 | 101 | 6.4476 | 11.5 | 82.0407 | 0 | 36.9806 | 0 | 7.6637 | 0 | 0 | 7.6637 | 0 | 0 | 0 | 90.0326 | 35.9363 | 0 | 90.0326 | 177.0808 | 13.89% | 0 | 0 | 0 | 0% | 43.6
2552 | 272 | 290 | 182 | 9.4699 | 14 | 136.9023 | 75.3741 | 0 | 48.1949 | 23.5829 | 0 | 0 | 23.5829 | 0 | 0 | 0 | 54.3157 | 20.4171 | 48.1949 | 54.3157 | 173.2864 | 13.6% | 0 | 0 | 0 | 0% | 44
2553 | 447 | 521 | 260 | 11.2833 | 16.5 | 224.9829 | 136.3452 | 0 | 104.6377 | 50.1892 | 0 | 2.9946 | 47.1946 | 0 | 0 | 0 | 0 | 0 | 104.6377 | 0 | 272.2311 | 21.36% | 2.2969 | 0 | 2.3311 | 4.662% | 44.2
2554 | 483 | 675 | 320 | 12.0892 | 18.6 | 243.1023 | 154.5467 | 0 | 121.299 | 83.1384 | 0 | 19.6192 | 63.5192 | 0 | 0 | 0 | 0 | 0 | 121.299 | 0 | 386.9306 | 30.36% | 15.0479 | 0 | 17.6032 | 35.21% | 43.9
2555 | 582 | 815 | 326 | 12.8952 | 20.4 | 292.9307 | 191.3938 | 0 | 155.2909 | 107.5 | 7.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 155.2909 | 0 | 533.7726 | 41.88% | 19.175 | 0 | 37.0638 | 74.13% | 42.5
2556 | 574 | 875 | 355 | 14.1041 | 21.4 | 288.9042 | 190.8292 | 0 | 154.069 | 108.7 | 17.0817 | 16.6183 | 75 | 0 | 0 | 0 | 0 | 0 | 154.069 | 0 | 679.4591 | 53.31% | 12.7462 | 0 | 50 | 100% | 41.3
2557 | 458 | 829 | 407 | 15.5145 | 21.7 | 230.5194 | 151.4838 | 0 | 116.5555 | 109.2 | 34.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 116.5555 | 0 | 789.6732 | 61.96% | 0 | 0 | 50 | 100% | 40.8
2558 | 585 | 842 | 334 | 16.5219 | 22.3 | 294.4407 | 189.068 | 0 | 151.0645 | 109.8 | 34.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 151.0645 | 0 | 932.5187 | 73.17% | 0 | 0 | 50 | 100% | 40.2
2559 | 286 | 612 | 385 | 16.9249 | 22 | 143.9488 | 89.0298 | 0 | 57.5991 | 71.0071 | 15.6035 | 0 | 55.4035 | 0 | 0 | 0 | 0 | 0 | 57.5991 | 0 | 986.984 | 77.44% | 0 | 0 | 50 | 100% | 39.8
2560 | 219 | 490 | 348 | 15.9175 | 21.1 | 110.2265 | 63.0794 | 0 | 33.4979 | 44.7444 | 2.3722 | 0 | 42.3722 | 0 | 0 | 0 | 0 | 0 | 33.4979 | 0 | 1018.6594 | 79.93% | 0 | 0 | 50 | 100% | 40
2561 | 188 | 350 | 262 | 15.313 | 19.6 | 94.6237 | 0 | 46.135 | 0 | 28.6285 | 0 | 0 | 28.6285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.6594 | 79.93% | 0 | 12.3715 | 37.4461 | 74.89% | 41
2562 | 45 | 123 | 108 | 14.7085 | 18.2 | 22.6493 | 0 | 7.9828 | 0 | 8.2967 | 0 | 0 | 8.2967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.6594 | 79.93% | 0 | 25 | 12.0768 | 24.15% | 33.2967
2563 | 0 | 16 | 16 | 12.6937 | 17 | 0 | 0 | 0 | 0 | 0.44695 | 0 | 0 | 0.44695 | 0 | 0 | 0 | 70.3216 | 27.2513 | 0 | 70.3216 | 953.9984 | 74.85% | 0 | 11.9017 | 0 | 0% | 39.6
2564 | 0 | 0 | 0 | 10.4773 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.491 | 36.7 | 0 | 92.491 | 864.4586 | 67.83% | 0 | 0 | 0 | 0% | 36.7
2565 | 0 | 0 | 0 | 7.052 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0215 | 34.4 | 0 | 87.0215 | 781.4071 | 61.31% | 0 | 0 | 0 | 0% | 34.4
2566 | 0 | 0 | 0 | 2.4178 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4569 | 32.1 | 0 | 81.4569 | 704.93 | 55.31% | 0 | 0 | 0 | 0% | 32.1
2567 | 0 | 0 | 0 | 4.0297 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.804 | 30.6 | 0 | 77.804 | 632.6434 | 49.64% | 0 | 0 | 0 | 0% | 30.6
2568 | 0 | 0 | 0 | 2.6193 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4389 | 29.6 | 0 | 75.4389 | 562.9864 | 44.17% | 0 | 0 | 0 | 0% | 29.6
2569 | 0 | 0 | 0 | 3.4253 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.7861 | 29.3 | 0 | 74.7861 | 493.9595 | 38.76% | 0 | 0 | 0 | 0% | 29.3
2570 | 0 | 0 | 0 | 3.2238 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.7976 | 29.4 | 0 | 74.7976 | 424.7661 | 33.33% | 0 | 0 | 0 | 0% | 29.4
2571 | 0 | 0 | 0 | 4.2312 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7838 | 30.3 | 0 | 76.7838 | 353.256 | 27.72% | 0 | 0 | 0 | 0% | 30.3
2572 | 0 | 0 | 0 | 5.4401 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7863 | 31.6 | 0 | 79.7863 | 278.098 | 21.82% | 0 | 0 | 0 | 0% | 31.6
2573 | 0 | 0 | 0 | 2.2164 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0546 | 33 | 0 | 83.0546 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 33
2574 | 0 | 12 | 12 | 3.4253 | 12.2 | 0 | 0 | 0 | 0 | 0.27557 | 0 | 0 | 0.27557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 0.27557
2575 | 4 | 31 | 30 | 3.4253 | 13.2 | 2.0133 | 0 | 0.90945 | 0 | 1.8385 | 0 | 0 | 1.8385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 1.8385
2576 | 0 | 41 | 41 | 2.8208 | 13.8 | 0 | 0 | 0 | 0 | 2.6798 | 0 | 0 | 2.6798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 2.6798
2577 | 0 | 29 | 29 | 4.8357 | 13.2 | 0 | 0 | 0 | 0 | 1.74 | 0 | 0 | 1.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 1.74
2578 | 0 | 28 | 28 | 8.4625 | 10.7 | 0 | 0 | 0 | 0 | 1.6687 | 0 | 0 | 1.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 1.6687
2579 | 0 | 49 | 49 | 6.2461 | 9.3 | 0 | 0 | 0 | 0 | 3.2747 | 0 | 0 | 3.2747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 3.2747
2580 | 0 | 62 | 61 | 3.6268 | 9.4 | 0 | 0 | 0 | 0 | 4.1887 | 0 | 0 | 4.1887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 4.1887
2581 | 0 | 109 | 107 | 5.6416 | 10.7 | 0 | 0 | 0 | 0 | 7.7743 | 0 | 0 | 7.7743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 7.7743
2582 | 0 | 129 | 127 | 3.6268 | 11.8 | 0 | 0 | 0 | 0 | 9.3225 | 0 | 0 | 9.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198.9445 | 15.61% | 0 | 0 | 0 | 0% | 9.3225
2583 | 225 | 532 | 354 | 8.0595 | 13.2 | 113.2464 | 70.0915 | 0 | 44.1554 | 61.1238 | 0 | 13.2619 | 47.8619 | 0 | 0 | 0 | 0 | 0 | 44.1554 | 0 | 240.2079 | 18.85% | 10.1719 | 0 | 10.325 | 20.65% | 34.6
2584 | 574 | 555 | 193 | 8.261 | 14.5 | 288.9042 | 165.6162 | 0 | 133.8429 | 70.2014 | 0 | 17.5507 | 52.6507 | 0 | 0 | 0 | 0 | 0 | 133.8429 | 0 | 365.2842 | 28.66% | 13.4614 | 0 | 23.989 | 47.98% | 35.1
2585 | 274 | 281 | 170 | 9.6714 | 14.2 | 137.909 | 67.5078 | 0 | 40.858 | 25.0642 | 0 | 0 | 25.0642 | 0 | 0 | 0 | 0 | 0 | 40.858 | 0 | 403.4661 | 31.66% | 0 | 11.4358 | 12.3829 | 24.77% | 36.5
2586 | 578 | 209 | 60 | 6.0446 | 14.5 | 290.9175 | 103.367 | 0 | 76.8366 | 11.146 | 0 | 0 | 11.146 | 0 | 0 | 0 | 0 | 0 | 76.8366 | 0 | 475.27 | 37.29% | 0 | 12.2013 | 0 | 0% | 23.3473
2587 | 55 | 20 | 13 | 5.8431 | 13.3 | 27.6825 | 0 | 0 | 0 | 0.26648 | 0 | 0 | 0.26648 | 0 | 0 | 0 | 91.8494 | 36.6335 | 0 | 91.8494 | 385.7039 | 30.26% | 0 | 0 | 0 | 0% | 36.9
2588 | 0 | 0 | 0 | 4.6342 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9304 | 34.6 | 0 | 86.9304 | 301.8649 | 23.68% | 0 | 0 | 0 | 0% | 34.6
2589 | 0 | 0 | 0 | 3.8283 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1079 | 32.6 | 0 | 82.1079 | 223.7701 | 17.56% | 0 | 0 | 0 | 0% | 32.6
2590 | 0 | 0 | 0 | 3.0223 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.8561 | 25.9815 | 0 | 66.8561 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 25.9815
2591 | 0 | 0 | 0 | 1.8134 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 0
2592 | 0 | 0 | 0 | 2.4178 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 0
2593 | 0 | 0 | 0 | 4.0297 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 0
2594 | 0 | 0 | 0 | 2.4178 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 0
2595 | 0 | 0 | 0 | 1.4104 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 0
2596 | 0 | 0 | 0 | 1.2089 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 0
2597 | 0 | 0 | 0 | 1.2089 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 0
2598 | 0 | 5 | 5 | 1.8134 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 0
2599 | 0 | 56 | 56 | 1.0074 | 9 | 0 | 0 | 0 | 0 | 3.8362 | 0 | 0 | 3.8362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 3.8362
2600 | 8 | 136 | 132 | 1.2089 | 10.4 | 4.0265 | 0 | 2.2204 | 0 | 10.2248 | 0 | 0 | 10.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2007 | 12.73% | 0 | 0 | 0 | 0% | 10.2248
2601 | 297 | 366 | 181 | 2.0149 | 12.4 | 149.4853 | 90.6261 | 0 | 66.9069 | 31.8672 | 0 | 0 | 31.8672 | 0 | 0 | 0 | 0 | 0 | 66.9069 | 0 | 224.8175 | 17.64% | 0 | 0 | 0 | 0% | 31.8672
2602 | 148 | 422 | 309 | 5.6416 | 13.8 | 74.491 | 0 | 47.3478 | 0 | 38.696 | 1.698 | 0 | 36.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224.8175 | 17.64% | 0 | 0 | 0 | 0% | 35.3
2603 | 269 | 641 | 407 | 8.0595 | 14.9 | 135.3924 | 88.4678 | 0 | 62.0939 | 83.0737 | 0 | 24.1368 | 58.9368 | 0 | 0 | 0 | 0 | 0 | 62.0939 | 0 | 282.93 | 22.2% | 18.513 | 0 | 18.7932 | 37.59% | 34.8
2604 | 179 | 672 | 501 | 9.6714 | 15.2 | 90.0938 | 59.509 | 0 | 34.0707 | 86.8145 | 1.7572 | 25 | 60.0572 | 0 | 0 | 0 | 0 | 0 | 34.0707 | 0 | 314.816 | 24.7% | 19.175 | 0 | 38.2584 | 76.52% | 33.3
2605 | 29 | 347 | 314 | 8.4625 | 14.8 | 14.5962 | 0 | 9.5925 | 0 | 28.5046 | 0 | 0 | 28.5046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.816 | 24.7% | 0 | 3.5954 | 34.6091 | 69.22% | 32.1
2606 | 13 | 478 | 457 | 11.8877 | 14.3 | 6.5431 | 0 | 4.203 | 0 | 44.4204 | 0 | 6.3602 | 38.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.816 | 24.7% | 4.8783 | 0 | 39.5613 | 79.12% | 31.7
2607 | 48 | 420 | 374 | 7.858 | 14.7 | 24.1592 | 0 | 14.9634 | 0 | 37.6522 | 0 | 2.9761 | 34.6761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.816 | 24.7% | 2.2827 | 0 | 41.8785 | 83.76% | 31.7
2608 | 1 | 267 | 263 | 5.8431 | 15 | 0.50332 | 0 | 0.28902 | 0 | 20.5119 | 0 | 0 | 20.5119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.816 | 24.7% | 0 | 11.7881 | 29.9138 | 59.83% | 32.3
2609 | 0 | 139 | 137 | 4.8357 | 14.3 | 0 | 0 | 0 | 0 | 10.2641 | 0 | 0 | 10.2641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.816 | 24.7% | 0 | 23.7359 | 5.8215 | 11.64% | 34
2610 | 0 | 70 | 69 | 2.4178 | 14.2 | 0 | 0 | 0 | 0 | 4.8356 | 0 | 0 | 4.8356 | 0 | 0 | 0 | 67.4781 | 26.1285 | 0 | 67.4781 | 252.4771 | 19.81% | 0 | 5.736 | 6.9389e-16 | 1.388e-15% | 36.7
2611 | 26 | 8 | 4 | 5.2387 | 13.5 | 13.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7011 | 34.8991 | 0 | 87.7011 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 34.8991
2612 | 0 | 0 | 0 | 3.0223 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2613 | 0 | 0 | 0 | 3.8283 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2614 | 0 | 0 | 0 | 2.8208 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2615 | 0 | 0 | 0 | 1.4104 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2616 | 0 | 0 | 0 | 2.4178 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2617 | 0 | 0 | 0 | 1.8134 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2618 | 0 | 0 | 0 | 2.2164 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2619 | 0 | 0 | 0 | 1.6119 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2620 | 0 | 0 | 0 | 1.4104 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2621 | 0 | 0 | 0 | 1.6119 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2622 | 0 | 1 | 1 | 2.4178 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
2623 | 0 | 17 | 17 | 7.6565 | 9.9 | 0 | 0 | 0 | 0 | 0.86318 | 0 | 0 | 0.86318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0.86318
2624 | 0 | 42 | 42 | 9.8729 | 9.6 | 0 | 0 | 0 | 0 | 2.8114 | 0 | 0 | 2.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 2.8114
2625 | 0 | 83 | 82 | 7.052 | 9.8 | 0 | 0 | 0 | 0 | 5.915 | 0 | 0 | 5.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 5.915
2626 | 0 | 164 | 162 | 3.8283 | 10.5 | 0 | 0 | 0 | 0 | 12.2415 | 0 | 0 | 12.2415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 12.2415
2627 | 1 | 360 | 353 | 1.6119 | 11.6 | 0.50332 | 0 | 0.32889 | 0 | 27.7623 | 0 | 0 | 27.7623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 27.7623
2628 | 30 | 580 | 539 | 2.0149 | 13.5 | 15.0995 | 0 | 9.9735 | 0 | 56.1438 | 0 | 10.6219 | 45.5219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.4184 | 13.14% | 8.147 | 0 | 8.2714 | 16.54% | 34.9
2629 | 650 | 969 | 373 | 3.6268 | 15.6 | 327.1563 | 215.0114 | 0 | 182.5852 | 116.3 | 16.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 182.5852 | 0 | 338.2543 | 26.54% | 19.175 | 0 | 27.7393 | 55.48% | 33.7
2630 | 810 | 949 | 247 | 9.8729 | 17.7 | 407.6871 | 261.9245 | 0 | 222.8098 | 116.8 | 16.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 222.8098 | 0 | 546.7265 | 42.9% | 19.175 | 0 | 47.2072 | 94.41% | 33.2
2631 | 73 | 313 | 250 | 8.8654 | 17.2 | 36.7422 | 0 | 22.7726 | 0 | 25.5871 | 0 | 0 | 25.5871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546.7265 | 42.9% | 0 | 7.6129 | 39.4793 | 78.96% | 33.2
2632 | 11 | 170 | 163 | 12.4922 | 15.6 | 5.5365 | 0 | 3.1844 | 0 | 12.9219 | 0 | 0 | 12.9219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546.7265 | 42.9% | 0 | 20.7781 | 18.3868 | 36.77% | 33.7
2633 | 2 | 78 | 77 | 9.6714 | 13.8 | 1.0066 | 0 | 0.49658 | 0 | 5.5678 | 0 | 0 | 5.5678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546.7265 | 42.9% | 0 | 18.1131 | 0 | 0% | 23.6808
2634 | 0 | 69 | 68 | 8.6639 | 13.5 | 0 | 0 | 0 | 0 | 4.7867 | 0 | 0 | 4.7867 | 0 | 0 | 0 | 83.6872 | 33.2133 | 0 | 83.6872 | 466.6406 | 36.61% | 0 | 0 | 0 | 0% | 38
2635 | 0 | 4 | 4 | 9.2684 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9824 | 36.3 | 0 | 90.9824 | 377.68 | 29.63% | 0 | 0 | 0 | 0% | 36.3
2636 | 0 | 0 | 0 | 8.261 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4112 | 34 | 0 | 85.4112 | 295.2789 | 23.17% | 0 | 0 | 0 | 0% | 34
2637 | 0 | 0 | 0 | 7.6565 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6916 | 31.6 | 0 | 79.6916 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 31.6
2638 | 0 | 0 | 0 | 6.0446 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2639 | 0 | 0 | 0 | 6.0446 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2640 | 0 | 0 | 0 | 5.6416 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2641 | 0 | 0 | 0 | 6.4476 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2642 | 0 | 0 | 0 | 8.6639 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2643 | 0 | 0 | 0 | 9.2684 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2644 | 0 | 0 | 0 | 6.8506 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2645 | 0 | 0 | 0 | 8.8654 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2646 | 0 | 0 | 0 | 8.261 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2647 | 0 | 4 | 4 | 5.8431 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2648 | 0 | 19 | 19 | 7.6565 | 11.3 | 0 | 0 | 0 | 0 | 1.0155 | 0 | 0 | 1.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 1.0155
2649 | 0 | 40 | 40 | 8.8654 | 12.4 | 0 | 0 | 0 | 0 | 2.5859 | 0 | 0 | 2.5859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 2.5859
2650 | 0 | 68 | 68 | 6.6491 | 12.5 | 0 | 0 | 0 | 0 | 4.7096 | 0 | 0 | 4.7096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 4.7096
2651 | 0 | 64 | 64 | 2.8208 | 11.8 | 0 | 0 | 0 | 0 | 4.3834 | 0 | 0 | 4.3834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 4.3834
2652 | 0 | 147 | 145 | 2.0149 | 11.9 | 0 | 0 | 0 | 0 | 10.72 | 0 | 0 | 10.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 10.72
2653 | 0 | 335 | 327 | 1.8134 | 13.6 | 0 | 0 | 0 | 0 | 25.3128 | 0 | 0 | 25.3128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 25.3128
2654 | 1 | 325 | 319 | 1.8134 | 14.7 | 0.50332 | 0 | 0.32342 | 0 | 24.6761 | 0 | 0 | 24.6761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 24.6761
2655 | 1 | 275 | 270 | 2.2164 | 15.2 | 0.50332 | 0 | 0.31216 | 0 | 20.7497 | 0 | 0 | 20.7497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 20.7497
2656 | 1 | 241 | 237 | 1.8134 | 15.4 | 0.50332 | 0 | 0.28996 | 0 | 18.1529 | 0 | 0 | 18.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 18.1529
2657 | 1 | 111 | 110 | 3.6268 | 15.3 | 0.50332 | 0 | 0.24922 | 0 | 8.0858 | 0 | 0 | 8.0858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 8.0858
2658 | 2 | 97 | 96 | 6.0446 | 14 | 1.0066 | 0 | 0.36604 | 0 | 6.9179 | 0 | 0 | 6.9179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 6.9179
2659 | 0 | 14 | 14 | 3.2238 | 13.7 | 0 | 0 | 0 | 0 | 0.41116 | 0 | 0 | 0.41116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0.41116
2660 | 0 | 0 | 0 | 1.4104 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2661 | 0 | 0 | 0 | 1.6119 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2662 | 0 | 0 | 0 | 0.60446 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2663 | 0 | 0 | 0 | 0.60446 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2664 | 0 | 0 | 0 | 1.4104 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2665 | 0 | 0 | 0 | 0.60446 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2666 | 0 | 0 | 0 | 1.8134 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2667 | 0 | 0 | 0 | 1.8134 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2668 | 0 | 0 | 0 | 1.2089 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2669 | 0 | 0 | 0 | 1.0074 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2670 | 0 | 5 | 6 | 1.8134 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 0
2671 | 5 | 79 | 76 | 2.2164 | 11.3 | 2.5166 | 0 | 1.1465 | 0 | 5.2966 | 0 | 0 | 5.2966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.7407 | 17.24% | 0 | 0 | 0 | 0% | 5.2966
2672 | 223 | 285 | 179 | 2.0149 | 13.4 | 112.2398 | 62.0376 | 0 | 40.0716 | 21.1251 | 0 | 0 | 21.1251 | 0 | 0 | 0 | 0 | 0 | 40.0716 | 0 | 257.3025 | 20.19% | 0 | 0 | 0 | 0% | 21.1251
2673 | 572 | 594 | 251 | 2.4178 | 15.6 | 287.8975 | 174.6371 | 0 | 145.3372 | 65.7186 | 0 | 13.5093 | 52.2093 | 0 | 0 | 0 | 0 | 0 | 145.3372 | 0 | 393.5364 | 30.88% | 10.3616 | 0 | 10.5217 | 21.04% | 38.7
2674 | 475 | 711 | 350 | 3.6268 | 16.4 | 239.0758 | 151.9245 | 0 | 123.6184 | 87.0558 | 0 | 24.0279 | 63.0279 | 0 | 0 | 0 | 0 | 0 | 123.6184 | 0 | 509.412 | 39.97% | 18.4294 | 0 | 29.2359 | 58.47% | 39
2675 | 102 | 627 | 526 | 4.0297 | 16.9 | 51.3384 | 0 | 33.5437 | 0 | 65.8127 | 0 | 13.9563 | 51.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509.412 | 39.97% | 10.7045 | 0 | 40.1058 | 80.21% | 37.9
2676 | 37 | 549 | 501 | 7.6565 | 17.9 | 18.6227 | 0 | 12.3006 | 0 | 53.7659 | 0 | 8.6829 | 45.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509.412 | 39.97% | 6.6598 | 0 | 46.8686 | 93.74% | 36.4
2677 | 194 | 558 | 371 | 10.6788 | 18.7 | 97.6436 | 64.1771 | 0 | 37.4611 | 63.5459 | 9.9524 | 4.0206 | 49.5729 | 0 | 0 | 0 | 0 | 0 | 37.4611 | 0 | 544.5267 | 42.72% | 3.0838 | 0 | 50 | 100% | 35.6
2678 | 0 | 166 | 163 | 6.8506 | 17.5 | 0 | 0 | 0 | 0 | 11.9842 | 0 | 0 | 11.9842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.5267 | 42.72% | 0 | 23.1158 | 26.5307 | 53.06% | 35.1
2679 | 0 | 174 | 171 | 6.6491 | 17.1 | 0 | 0 | 0 | 0 | 12.6751 | 0 | 0 | 12.6751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.5267 | 42.72% | 0 | 22.2249 | 3.9648 | 7.93% | 34.9
2680 | 21 | 219 | 202 | 5.2387 | 17.8 | 10.5697 | 0 | 6.0987 | 0 | 16.4833 | 0 | 0 | 16.4833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.5267 | 42.72% | 0 | 3.906 | 0 | 0% | 20.3893
2681 | 3 | 140 | 137 | 7.052 | 17.3 | 1.51 | 0 | 0.75042 | 0 | 10.2605 | 0 | 0 | 10.2605 | 0 | 0 | 0 | 70.3378 | 27.2395 | 0 | 70.3378 | 479.2436 | 37.6% | 0 | 0 | 0 | 0% | 37.5
2682 | 28 | 78 | 71 | 2.8208 | 17.2 | 14.0929 | 0 | 5.1623 | 0 | 5.2733 | 0 | 0 | 5.2733 | 0 | 0 | 0 | 88.5195 | 35.0267 | 0 | 88.5195 | 393.5515 | 30.88% | 0 | 0 | 0 | 0% | 40.3
2683 | 15 | 23 | 21 | 2.4178 | 16.2 | 7.5498 | 0 | 0 | 0 | 0.78984 | 0 | 0 | 0.78984 | 0 | 0 | 0 | 93.3685 | 37.1102 | 0 | 93.3685 | 301.936 | 23.69% | 0 | 0 | 0 | 0% | 37.9
2684 | 0 | 0 | 0 | 1.8134 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.184 | 35 | 0 | 88.184 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 35
2685 | 0 | 0 | 0 | 2.6193 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0
2686 | 0 | 0 | 0 | 2.4178 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0
2687 | 0 | 0 | 0 | 1.6119 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0
2688 | 0 | 0 | 0 | 2.2164 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0
2689 | 0 | 0 | 0 | 1.6119 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0
2690 | 0 | 0 | 0 | 2.8208 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0
2691 | 0 | 0 | 0 | 1.6119 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0
2692 | 0 | 0 | 0 | 1.6119 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0
2693 | 0 | 0 | 0 | 1.8134 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0
2694 | 3 | 8 | 8 | 1.8134 | 10.7 | 1.51 | 0 | 0 | 0 | 0.047444 | 0 | 0 | 0.047444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.2729 | 16.97% | 0 | 0 | 0 | 0% | 0.047444
2695 | 284 | 146 | 82 | 5.4401 | 13.2 | 142.9421 | 65.254 | 0 | 41.4808 | 7.0558 | 0 | 0 | 7.0558 | 0 | 0 | 0 | 0 | 0 | 41.4808 | 0 | 255.2399 | 20.03% | 0 | 0 | 0 | 0% | 7.0558
2696 | 163 | 218 | 162 | 18.3353 | 15.1 | 82.0407 | 0 | 45.3804 | 0 | 18.0225 | 0 | 0 | 18.0225 | 0 | 0 | 0 | 65.6656 | 25.2775 | 0 | 65.6656 | 194.2881 | 15.24% | 0 | 0 | 0 | 0% | 43.3
2697 | 1 | 200 | 198 | 18.1338 | 15.4 | 0.50332 | 0 | 0.30537 | 0 | 15.2036 | 0 | 0 | 15.2036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.2881 | 15.24% | 0 | 0 | 0 | 0% | 15.2036
2698 | 35 | 328 | 299 | 14.91 | 16 | 17.6161 | 0 | 11.1936 | 0 | 26.8379 | 0 | 0 | 26.8379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.2881 | 15.24% | 0 | 0 | 0 | 0% | 26.8379
2699 | 3 | 297 | 290 | 17.5294 | 15.8 | 1.51 | 0 | 0.98644 | 0 | 22.7994 | 0 | 0 | 22.7994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.2881 | 15.24% | 0 | 0 | 0 | 0% | 22.7994
2700 | 2 | 144 | 141 | 13.4996 | 14.1 | 1.0066 | 0 | 0.66489 | 0 | 10.584 | 0 | 0 | 10.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.2881 | 15.24% | 0 | 0 | 0 | 0% | 10.584
2701 | 3 | 318 | 309 | 9.6714 | 13.7 | 1.51 | 0 | 0.99246 | 0 | 24.4378 | 0 | 0 | 24.4378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.2881 | 15.24% | 0 | 0 | 0 | 0% | 24.4378
2702 | 28 | 403 | 371 | 11.4848 | 14.8 | 14.0929 | 0 | 9.0586 | 0 | 33.1641 | 0 | 0 | 33.1641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.2881 | 15.24% | 0 | 0 | 0 | 0% | 33.1641
2703 | 35 | 290 | 260 | 11.8877 | 14.4 | 17.6161 | 0 | 10.94 | 0 | 23.6873 | 0 | 0 | 23.6873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.2881 | 15.24% | 0 | 0 | 0 | 0% | 23.6873
2704 | 523 | 513 | 197 | 14.3056 | 15.4 | 263.235 | 152.1177 | 0 | 117.6173 | 59.9507 | 0 | 10.3253 | 49.6253 | 0 | 0 | 0 | 0 | 0 | 117.6173 | 0 | 304.6194 | 23.9% | 7.9195 | 0 | 8.0431 | 16.09% | 39.3
2705 | 666 | 405 | 88 | 14.7085 | 16 | 335.2094 | 167.1926 | 0 | 131.4209 | 33.6119 | 0 | 0 | 33.6119 | 0 | 0 | 0 | 0 | 0 | 131.4209 | 0 | 427.8992 | 33.57% | 0 | 7.5881 | 0.33789 | 0.6758% | 41.2
2706 | 141 | 103 | 72 | 11.8877 | 14.2 | 70.9678 | 0 | 26.182 | 0 | 6.7656 | 0 | 0 | 6.7656 | 0 | 0 | 0 | 93.151 | 37.1344 | 0 | 93.151 | 336.4373 | 26.4% | 0 | 0 | 0.33789 | 0.6758% | 43.9
2707 | 66 | 27 | 22 | 13.2981 | 12.8 | 33.2189 | 0 | 0 | 0 | 0.83259 | 0 | 0 | 0.83259 | 0 | 0 | 0 | 100.0267 | 40.0674 | 0 | 100.0267 | 236.4869 | 18.56% | 0 | 0 | 0.33789 | 0.6758% | 40.9
2708 | 0 | 0 | 0 | 10.6788 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.409 | 20.1028 | 0 | 53.409 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 20.1028
2709 | 0 | 0 | 0 | 9.4699 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0
2710 | 0 | 0 | 0 | 9.4699 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0
2711 | 0 | 0 | 0 | 8.4625 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0
2712 | 0 | 0 | 0 | 6.6491 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0
2713 | 0 | 0 | 0 | 4.4327 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0
2714 | 0 | 0 | 0 | 2.8208 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0
2715 | 0 | 0 | 0 | 4.0297 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0
2716 | 0 | 0 | 0 | 4.0297 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0
2717 | 0 | 0 | 0 | 3.0223 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0
2718 | 115 | 19 | 9 | 1.4104 | 6.4 | 57.8815 | 0 | 0 | 0 | 0.037502 | 0 | 0 | 0.037502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.636 | 14.72% | 0 | 0 | 0.33789 | 0.6758% | 0.037502
2719 | 632 | 176 | 36 | 1.6119 | 9.3 | 318.0966 | 145.5136 | 0 | 118.3861 | 5.3978 | 0 | 0 | 5.3978 | 0 | 0 | 0 | 0 | 0 | 118.3861 | 0 | 298.9948 | 23.46% | 0 | 0 | 0.33789 | 0.6758% | 5.3978
2720 | 826 | 391 | 51 | 1.8134 | 12.1 | 415.7402 | 230.1386 | 0 | 197.4021 | 30.2984 | 0 | 0 | 30.2984 | 0 | 0 | 0 | 0 | 0 | 197.4021 | 0 | 484.6792 | 38.03% | 0 | 0 | 0.33789 | 0.6758% | 30.2984
2721 | 914 | 598 | 59 | 6.8506 | 13.3 | 460.0321 | 279.1568 | 0 | 240.7808 | 66.0831 | 0 | 9.9415 | 56.1415 | 0 | 0 | 0 | 0 | 0 | 240.7808 | 0 | 711.1674 | 55.8% | 7.6252 | 0 | 8.0824 | 16.16% | 46.2
2722 | 957 | 771 | 66 | 8.4625 | 15 | 481.6747 | 306.0433 | 0 | 265.0086 | 103.9842 | 4.0921 | 25 | 74.8921 | 0 | 0 | 0 | 0 | 0 | 265.0086 | 0 | 960.4453 | 75.36% | 19.175 | 0 | 27.5576 | 55.12% | 45.8
2723 | 968 | 901 | 83 | 8.0595 | 15.9 | 487.2112 | 318.2503 | 0 | 276.6425 | 105.5 | 5.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 276.6425 | 0 | 1220.6665 | 95.78% | 19.175 | 0 | 47.0328 | 94.07% | 44.5
2724 | 846 | 940 | 172 | 7.2535 | 16.5 | 425.8065 | 204.4033 | 76.8451 | 176.2903 | 106.5 | 27.6911 | 3.8089 | 75 | 0 | 0 | 0 | 0 | 0 | 176.2903 | 0 | 1274.5104 | 100% | 2.9214 | 0 | 50 | 100% | 43.5
2725 | 827 | 925 | 168 | 9.0669 | 17.3 | 416.2435 | 0 | 273.5977 | 0 | 107.1 | 32.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.9
2726 | 955 | 928 | 100 | 11.8877 | 18.3 | 480.6681 | 0 | 309.0097 | 0 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
2727 | 932 | 810 | 92 | 11.6862 | 19.1 | 469.0918 | 0 | 291.4066 | 0 | 107.8 | 32.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.2
2728 | 891 | 638 | 74 | 12.0892 | 18.8 | 448.4558 | 0 | 259.5386 | 0 | 77.5883 | 17.5442 | 0 | 60.0442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
2729 | 812 | 438 | 63 | 9.4699 | 18.8 | 408.6937 | 0 | 204.5604 | 0 | 36.3967 | 0 | 0 | 36.3967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.8033 | 42.0757 | 84.15% | 44.2
2730 | 653 | 224 | 46 | 8.6639 | 18.2 | 328.6663 | 0 | 122.101 | 0 | 10.2831 | 0 | 0 | 10.2831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.6877 | 33.38% | 35.2831
2731 | 204 | 41 | 16 | 6.8506 | 16.7 | 102.6767 | 0 | 0 | 0 | 0.42147 | 0 | 0 | 0.42147 | 0 | 0 | 0 | 67.1149 | 25.8454 | 0 | 67.1149 | 1212.7983 | 95.16% | 0 | 16.4331 | 0 | 0% | 42.7
2732 | 0 | 0 | 0 | 7.052 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0277 | 39.1 | 0 | 98.0277 | 1116.2345 | 87.58% | 0 | 0 | 0 | 0% | 39.1
2733 | 0 | 0 | 0 | 9.6714 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9611 | 36.2 | 0 | 90.9611 | 1027.9107 | 80.65% | 0 | 0 | 0 | 0% | 36.2
2734 | 0 | 0 | 0 | 6.4476 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3332 | 33.9 | 0 | 85.3332 | 946.1341 | 74.24% | 0 | 0 | 0 | 0% | 33.9
2735 | 0 | 0 | 0 | 3.6268 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9175 | 32.5 | 0 | 81.9175 | 868.363 | 68.13% | 0 | 0 | 0 | 0% | 32.5
2736 | 0 | 0 | 0 | 7.455 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0737 | 31.7 | 0 | 80.0737 | 792.847 | 62.21% | 0 | 0 | 0 | 0% | 31.7
2737 | 0 | 0 | 0 | 12.0892 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6885 | 31.5 | 0 | 79.6885 | 717.8831 | 56.33% | 0 | 0 | 0 | 0% | 31.5
2738 | 0 | 0 | 0 | 11.8877 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6087 | 32.3 | 0 | 81.6087 | 640.6453 | 50.27% | 0 | 0 | 0 | 0% | 32.3
2739 | 0 | 0 | 0 | 8.0595 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6517 | 35.7 | 0 | 89.6517 | 553.6448 | 43.44% | 0 | 0 | 0 | 0% | 35.7
2740 | 0 | 0 | 0 | 6.0446 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9406 | 39.6 | 0 | 98.9406 | 455.515 | 35.74% | 0 | 0 | 0 | 0% | 39.6
2741 | 0 | 0 | 0 | 6.8506 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.583 | 43.2 | 0 | 107.583 | 347.1059 | 27.23% | 0 | 0 | 0 | 0% | 43.2
2742 | 15 | 15 | 14 | 9.0669 | 12.9 | 7.5498 | 0 | 0 | 0 | 0.34442 | 0 | 0 | 0.34442 | 0 | 0 | 0 | 111.5617 | 44.8556 | 0 | 111.5617 | 233.8821 | 18.35% | 0 | 0 | 0 | 0% | 45.2
2743 | 109 | 112 | 85 | 8.261 | 13.7 | 54.8616 | 0 | 25.1481 | 0 | 6.4094 | 0 | 0 | 6.4094 | 0 | 0 | 0 | 98.242 | 39.2906 | 0 | 98.242 | 136.5636 | 10.71% | 0 | 0 | 0 | 0% | 45.7
2744 | 29 | 158 | 145 | 7.858 | 14.8 | 14.5962 | 0 | 8.086 | 0 | 11.9856 | 0 | 0 | 11.9856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.5636 | 10.71% | 0 | 0 | 0 | 0% | 11.9856
2745 | 170 | 355 | 244 | 15.1115 | 15.8 | 85.564 | 0 | 51.9316 | 0 | 29.6318 | 0 | 0 | 29.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.5636 | 10.71% | 0 | 0 | 0 | 0% | 29.6318
2746 | 280 | 548 | 328 | 16.9249 | 17 | 140.9289 | 89.5364 | 0 | 57.8398 | 52.5722 | 0 | 3.5861 | 48.9861 | 0 | 0 | 0 | 0 | 0 | 57.8398 | 0 | 191.6187 | 15.03% | 2.7505 | 0 | 2.794 | 5.588% | 45.4
2747 | 685 | 876 | 287 | 17.9323 | 18.7 | 344.7724 | 225.1793 | 0 | 183.8936 | 106.1 | 6.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 183.8936 | 0 | 366.6585 | 28.77% | 19.175 | 0 | 22.272 | 44.54% | 43.9
2748 | 885 | 986 | 178 | 18.9398 | 20.1 | 445.4359 | 294.2124 | 0 | 247.9373 | 107.2 | 7.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 247.9373 | 0 | 602.6585 | 47.29% | 19.175 | 0 | 41.7501 | 83.5% | 42.8
2749 | 824 | 978 | 218 | 16.7234 | 20.8 | 414.7335 | 272.6139 | 0 | 228.783 | 107.7 | 22.1113 | 10.5887 | 75 | 0 | 0 | 0 | 0 | 0 | 228.783 | 0 | 820.4265 | 64.37% | 8.1216 | 0 | 50 | 100% | 42.3
2750 | 350 | 595 | 277 | 11.4848 | 20.2 | 176.1611 | 113.2663 | 0 | 83.1318 | 69.2222 | 13.6611 | 0 | 55.5611 | 0 | 0 | 0 | 0 | 0 | 83.1318 | 0 | 899.5558 | 70.58% | 0 | 0 | 50 | 100% | 41.9
2751 | 146 | 391 | 274 | 12.2907 | 20.2 | 73.4843 | 0 | 45.6532 | 0 | 33.7484 | 0 | 0 | 33.7484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 899.5558 | 70.58% | 0 | 7.4516 | 42.4318 | 84.86% | 41.2
2752 | 773 | 659 | 165 | 12.4922 | 21.9 | 389.0643 | 225.4926 | 0 | 187.4819 | 79.5305 | 9.3017 | 9.7135 | 60.5152 | 0 | 0 | 0 | 0 | 0 | 187.4819 | 0 | 1078.0112 | 84.58% | 7.4502 | 0 | 50 | 100% | 41.5
2753 | 794 | 460 | 92 | 15.1115 | 22.4 | 399.634 | 200.712 | 0 | 162.8086 | 37.8919 | 0 | 0 | 37.8919 | 0 | 0 | 0 | 0 | 0 | 162.8086 | 0 | 1232.9812 | 96.74% | 0 | 4.8081 | 45.1166 | 90.23% | 42.7
2754 | 690 | 232 | 43 | 15.716 | 20.7 | 347.289 | 0 | 129.8963 | 0 | 10.264 | 0 | 0 | 10.264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1232.9812 | 96.74% | 0 | 25 | 19.7247 | 39.45% | 35.264
2755 | 223 | 42 | 16 | 15.5145 | 18.8 | 112.2398 | 0 | 0 | 0 | 0.43709 | 0 | 0 | 0.43709 | 0 | 0 | 0 | 59.5834 | 22.4423 | 0 | 59.5834 | 1178.6464 | 92.48% | 0 | 19.4206 | 0 | 0% | 42.3
2756 | 0 | 0 | 0 | 12.8952 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5833 | 39.2 | 0 | 98.5833 | 1081.9794 | 84.89% | 0 | 0 | 0 | 0% | 39.2
2757 | 0 | 0 | 0 | 9.8729 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9179 | 36.5 | 0 | 91.9179 | 992.9794 | 77.91% | 0 | 0 | 0 | 0% | 36.5
2758 | 0 | 0 | 0 | 6.6491 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8562 | 34 | 0 | 85.8562 | 911.0661 | 71.48% | 0 | 0 | 0 | 0% | 34
2759 | 0 | 0 | 0 | 4.6342 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1042 | 32.5 | 0 | 82.1042 | 833.4383 | 65.39% | 0 | 0 | 0 | 0% | 32.5
2760 | 0 | 0 | 0 | 2.8208 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0103 | 31.7 | 0 | 80.0103 | 758.0607 | 59.48% | 0 | 0 | 0 | 0% | 31.7
2761 | 0 | 0 | 0 | 3.4253 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1944 | 31.8 | 0 | 80.1944 | 682.3898 | 53.54% | 0 | 0 | 0 | 0% | 31.8
2762 | 0 | 0 | 0 | 4.4327 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8123 | 32.5 | 0 | 81.8123 | 604.7257 | 47.45% | 0 | 0 | 0 | 0% | 32.5
2763 | 0 | 0 | 0 | 4.4327 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4525 | 35.7 | 0 | 89.4525 | 517.8867 | 40.63% | 0 | 0 | 0 | 0% | 35.7
2764 | 0 | 0 | 0 | 1.4104 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.6685 | 40 | 0 | 99.6685 | 418.7828 | 32.86% | 0 | 0 | 0 | 0% | 40
2765 | 0 | 0 | 0 | 2.8208 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.6438 | 42.9 | 0 | 106.6438 | 311.4374 | 24.44% | 0 | 0 | 0 | 0% | 42.9
2766 | 111 | 22 | 10 | 3.6268 | 9.2 | 55.8682 | 0 | 0 | 0 | 0.0795 | 0 | 0 | 0.0795 | 0 | 0 | 0 | 109.8223 | 44.2205 | 0 | 109.8223 | 200.2634 | 15.71% | 0 | 0 | 0 | 0% | 44.3
2767 | 620 | 184 | 42 | 3.4253 | 11.5 | 312.0568 | 143.3373 | 0 | 115.6305 | 5.8641 | 0 | 0 | 5.8641 | 0 | 0 | 0 | 73.5345 | 28.9581 | 115.6305 | 73.5345 | 242.0648 | 18.99% | 0 | 0 | 0 | 0% | 34.8222
2768 | 801 | 400 | 63 | 1.8134 | 14.7 | 403.1572 | 223.5077 | 0 | 191.1789 | 30.287 | 0 | 0 | 30.287 | 0 | 0 | 0 | 0 | 0 | 191.1789 | 0 | 423.5404 | 33.23% | 0 | 0 | 0 | 0% | 30.287
2769 | 876 | 603 | 81 | 6.0446 | 16.1 | 440.906 | 267.6505 | 0 | 230.5079 | 66.2497 | 0 | 10.9249 | 55.3249 | 0 | 0 | 0 | 0 | 0 | 230.5079 | 0 | 642.3488 | 50.4% | 8.3794 | 0 | 8.5131 | 17.03% | 44.4
2770 | 909 | 783 | 105 | 7.6565 | 17.2 | 457.5155 | 290.6544 | 0 | 251.2516 | 104.2043 | 5.1522 | 25 | 74.0522 | 0 | 0 | 0 | 0 | 0 | 251.2516 | 0 | 880.8479 | 69.11% | 19.175 | 0 | 27.9942 | 55.99% | 43.9
2771 | 939 | 915 | 114 | 7.2535 | 18.3 | 472.615 | 308.6383 | 0 | 268.2375 | 107.7 | 7.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 268.2375 | 0 | 1135.4709 | 89.09% | 19.175 | 0 | 47.4753 | 94.95% | 42.3
2772 | 948 | 997 | 132 | 5.2387 | 19 | 477.1449 | 248.9478 | 66.207 | 217.6703 | 108.7 | 30.4601 | 3.2399 | 75 | 0 | 0 | 0 | 0 | 0 | 217.6703 | 0 | 1274.5104 | 100% | 2.485 | 0 | 50 | 100% | 41.3
2773 | 719 | 879 | 211 | 4.2312 | 19.9 | 361.8852 | 0 | 237.8829 | 0 | 109.6 | 34.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.4
2774 | 867 | 929 | 173 | 9.6714 | 20.2 | 436.3762 | 0 | 280.6168 | 0 | 110.1 | 35.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.9
2775 | 897 | 827 | 130 | 8.4625 | 20 | 451.4757 | 0 | 280.5063 | 0 | 110.6 | 35.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.4
2776 | 855 | 645 | 99 | 8.4625 | 19.7 | 430.3364 | 0 | 249.7641 | 0 | 79.4252 | 19.9626 | 0 | 59.4626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.5
2777 | 780 | 442 | 76 | 8.4625 | 19.4 | 392.5876 | 0 | 197.8062 | 0 | 35.9606 | 0 | 0 | 35.9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 4.3394 | 45.592 | 91.18% | 40.3
2778 | 603 | 225 | 57 | 7.858 | 18.7 | 303.5004 | 0 | 114.2686 | 0 | 10.348 | 0 | 0 | 10.348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 20.1965 | 40.39% | 35.348
2779 | 196 | 44 | 20 | 4.4327 | 17.5 | 98.6502 | 0 | 0 | 0 | 0.70403 | 0 | 0 | 0.70403 | 0 | 0 | 0 | 54.65 | 20.4138 | 0 | 54.65 | 1224.8953 | 96.11% | 0 | 19.8822 | 0 | 0% | 41
2780 | 0 | 0 | 0 | 2.4178 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.892 | 38.2 | 0 | 95.892 | 1131.1185 | 88.75% | 0 | 0 | 0 | 0% | 38.2
2781 | 0 | 0 | 0 | 2.4178 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.649 | 36.1 | 0 | 90.649 | 1043.2656 | 81.86% | 0 | 0 | 0 | 0% | 36.1
2782 | 0 | 0 | 0 | 3.4253 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8231 | 33.7 | 0 | 84.8231 | 962.2398 | 75.5% | 0 | 0 | 0 | 0% | 33.7
2783 | 0 | 0 | 0 | 1.6119 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4816 | 31.9 | 0 | 80.4816 | 886.3307 | 69.54% | 0 | 0 | 0 | 0% | 31.9
2784 | 0 | 0 | 0 | 4.6342 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0823 | 30.9 | 0 | 78.0823 | 813.2141 | 63.81% | 0 | 0 | 0 | 0% | 30.9
2785 | 0 | 0 | 0 | 4.8357 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0899 | 30.5 | 0 | 77.0899 | 741.199 | 58.16% | 0 | 0 | 0 | 0% | 30.5
2786 | 0 | 0 | 0 | 2.2164 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5935 | 30.3 | 0 | 76.5935 | 669.7271 | 52.55% | 0 | 0 | 0 | 0% | 30.3
2787 | 0 | 0 | 0 | 2.2164 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4539 | 31.1 | 0 | 78.4539 | 596.0178 | 46.76% | 0 | 0 | 0 | 0% | 31.1
2788 | 0 | 0 | 0 | 2.4178 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0971 | 31.8 | 0 | 80.0971 | 520.3304 | 40.83% | 0 | 0 | 0 | 0% | 31.8
2789 | 0 | 0 | 0 | 2.2164 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0981 | 33.9 | 0 | 85.0981 | 438.6353 | 34.42% | 0 | 0 | 0 | 0% | 33.9
2790 | 110 | 23 | 11 | 3.6268 | 11 | 55.3649 | 0 | 0 | 0 | 0.12323 | 0 | 0 | 0.12323 | 0 | 0 | 0 | 91.5345 | 36.5768 | 0 | 91.5345 | 349.3089 | 27.41% | 0 | 0 | 0 | 0% | 36.7
2791 | 623 | 186 | 40 | 0.20149 | 14 | 313.5667 | 144.3241 | 0 | 117.7747 | 5.6468 | 0 | 0 | 5.6468 | 0 | 0 | 0 | 82.6288 | 32.7532 | 117.7747 | 82.6288 | 381.2125 | 29.91% | 0 | 0 | 0 | 0% | 38.4
2792 | 815 | 401 | 55 | 2.0149 | 16.8 | 410.2037 | 227.5831 | 0 | 194.9429 | 29.881 | 0 | 0 | 29.881 | 0 | 0 | 0 | 0 | 0 | 194.9429 | 0 | 563.8425 | 44.24% | 0 | 0 | 0 | 0% | 29.881
2793 | 902 | 607 | 64 | 3.8283 | 18.9 | 453.9923 | 275.646 | 0 | 239.1275 | 69.6068 | 0 | 15.4534 | 54.1534 | 0 | 0 | 0 | 0 | 0 | 239.1275 | 0 | 787.8663 | 61.82% | 11.8528 | 0 | 12.0437 | 24.09% | 38.7
2794 | 953 | 782 | 68 | 4.8357 | 19.9 | 479.6615 | 304.7029 | 0 | 266.0504 | 106.0519 | 8.8259 | 25 | 72.2259 | 0 | 0 | 0 | 0 | 0 | 266.0504 | 0 | 1037.1126 | 81.37% | 19.175 | 0 | 31.5275 | 63.06% | 38.4
2795 | 984 | 909 | 68 | 5.0372 | 20.6 | 495.2643 | 323.3909 | 0 | 283.3987 | 112.7 | 13.9978 | 23.7022 | 75 | 0 | 0 | 0 | 0 | 0 | 283.3987 | 0 | 1274.5104 | 100% | 18.1796 | 0 | 50 | 100% | 37.3
2796 | 992 | 977 | 70 | 5.2387 | 21.3 | 499.2908 | 0 | 329.7808 | 0 | 114.5 | 39.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.5
2797 | 988 | 981 | 72 | 5.4401 | 21.7 | 497.2776 | 0 | 326.892 | 0 | 115.7 | 40.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.3
2798 | 977 | 926 | 72 | 7.858 | 22.2 | 491.7411 | 0 | 316.2631 | 0 | 116.4 | 41.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.6
2799 | 958 | 814 | 68 | 9.8729 | 22.4 | 482.1781 | 0 | 299.6017 | 0 | 116.4 | 41.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.6
2800 | 923 | 653 | 61 | 9.2684 | 22 | 464.5619 | 0 | 269.997 | 0 | 84.8097 | 25.4549 | 0 | 59.3549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.9
2801 | 848 | 453 | 54 | 11.4848 | 20.8 | 426.8131 | 0 | 215.7154 | 0 | 37.5901 | 1.195 | 0 | 36.395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.2
2802 | 690 | 236 | 43 | 10.8803 | 19.6 | 347.289 | 0 | 131.5957 | 0 | 10.1351 | 0 | 0 | 10.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.6011 | 49.2% | 35.1351
2803 | 256 | 48 | 17 | 10.4773 | 17.6 | 128.8493 | 0 | 0 | 0 | 0.51593 | 0 | 0 | 0.51593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.2148 | 0 | 0% | 24.7307
2804 | 0 | 0 | 0 | 5.6416 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4517 | 35.1 | 0 | 88.4517 | 1189.4257 | 93.32% | 0 | 0 | 0 | 0% | 35.1
2805 | 0 | 0 | 0 | 4.2312 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5179 | 32.7 | 0 | 82.5179 | 1111.2425 | 87.19% | 0 | 0 | 0 | 0% | 32.7
2806 | 0 | 0 | 0 | 3.4253 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.8951 | 30.4 | 0 | 76.8951 | 1039.5088 | 81.56% | 0 | 0 | 0 | 0% | 30.4
2807 | 0 | 0 | 0 | 1.6119 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5094 | 28.9 | 0 | 73.5094 | 971.5663 | 76.23% | 0 | 0 | 0 | 0% | 28.9
2808 | 0 | 0 | 0 | 2.8208 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.0632 | 27.8 | 0 | 71.0632 | 906.1167 | 71.1% | 0 | 0 | 0 | 0% | 27.8
2809 | 0 | 0 | 0 | 3.2238 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.149 | 27.4 | 0 | 70.149 | 841.5361 | 66.03% | 0 | 0 | 0 | 0% | 27.4
2810 | 0 | 0 | 0 | 1.8134 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8216 | 27.3 | 0 | 69.8216 | 777.2566 | 60.98% | 0 | 0 | 0 | 0% | 27.3
2811 | 0 | 0 | 0 | 1.8134 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.4206 | 27.6 | 0 | 70.4206 | 712.3888 | 55.9% | 0 | 0 | 0 | 0% | 27.6
2812 | 0 | 0 | 0 | 2.4178 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2034 | 27.5 | 0 | 70.2034 | 647.7198 | 50.82% | 0 | 0 | 0 | 0% | 27.5
2813 | 0 | 0 | 0 | 3.4253 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.1488 | 28.8 | 0 | 73.1488 | 579.9613 | 45.5% | 0 | 0 | 0 | 0% | 28.8
2814 | 125 | 32 | 17 | 3.2238 | 11.4 | 62.9147 | 0 | 0 | 0 | 0.42156 | 0 | 0 | 0.42156 | 0 | 0 | 0 | 76.9693 | 30.4784 | 0 | 76.9693 | 507.923 | 39.85% | 0 | 0 | 0 | 0% | 30.9
2815 | 409 | 160 | 61 | 3.0223 | 13.4 | 205.8568 | 94.9408 | 0 | 70.427 | 6.224 | 0 | 0 | 6.224 | 0 | 0 | 0 | 68.1622 | 26.476 | 70.427 | 68.1622 | 510.3408 | 40.04% | 0 | 0 | 0 | 0% | 32.7
2816 | 777 | 403 | 69 | 6.0446 | 16.4 | 391.0776 | 217.132 | 0 | 183.4356 | 30.2816 | 0 | 0 | 30.2816 | 0 | 0 | 0 | 0 | 0 | 183.4356 | 0 | 679.9148 | 53.35% | 0 | 0 | 0 | 0% | 30.2816
2817 | 865 | 605 | 80 | 8.6639 | 18.7 | 435.3695 | 264.3887 | 0 | 225.883 | 75.7779 | 0 | 21.2889 | 54.4889 | 0 | 0 | 0 | 0 | 0 | 225.883 | 0 | 888.7286 | 69.73% | 16.3286 | 0 | 16.594 | 33.19% | 33.2
2818 | 963 | 791 | 67 | 8.6639 | 20.6 | 484.6946 | 307.8624 | 0 | 266.6983 | 114.4082 | 15.6541 | 25 | 73.7541 | 0 | 0 | 0 | 0 | 0 | 266.6983 | 0 | 1135.2735 | 89.08% | 19.175 | 0 | 36.0806 | 72.16% | 33.1
2819 | 948 | 902 | 87 | 9.2684 | 22 | 477.1449 | 228.4584 | 83.0657 | 197.8351 | 117.1 | 24.2425 | 17.8575 | 75 | 0 | 0 | 0 | 0 | 0 | 197.8351 | 0 | 1274.5104 | 100% | 13.6967 | 0 | 50 | 100% | 32.9
2820 | 964 | 976 | 92 | 11.2833 | 22.3 | 485.198 | 0 | 320.471 | 0 | 118.5 | 43.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 31.5
2821 | 908 | 958 | 118 | 13.2981 | 22.3 | 457.0122 | 0 | 300.4318 | 0 | 119.5 | 44.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 30.5
2822 | 923 | 932 | 121 | 14.5071 | 22.7 | 464.5619 | 0 | 298.8222 | 0 | 119.9 | 44.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 30.1
2823 | 937 | 829 | 96 | 14.3056 | 22.9 | 471.6084 | 0 | 293.0515 | 0 | 119.3 | 44.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 30.7
2824 | 886 | 657 | 86 | 13.7011 | 22.6 | 445.9392 | 0 | 259.5173 | 0 | 87.5785 | 27.9392 | 0 | 59.6392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 31.7
2825 | 789 | 453 | 79 | 13.0966 | 21.6 | 397.1174 | 0 | 201.3098 | 0 | 38.675 | 2.4375 | 0 | 36.2375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.8
2826 | 661 | 241 | 52 | 11.0818 | 20.3 | 332.6928 | 0 | 126.8524 | 0 | 10.5091 | 0 | 0 | 10.5091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.5975 | 49.19% | 35.5091
2827 | 227 | 50 | 21 | 10.2758 | 18 | 114.253 | 0 | 0 | 0 | 0.7807 | 0 | 0 | 0.7807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.2077 | 0 | 0% | 24.9884
2828 | 0 | 0 | 0 | 9.2684 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.005 | 34.5 | 0 | 87.005 | 1191.115 | 93.46% | 0 | 0 | 0 | 0% | 34.5
2829 | 0 | 0 | 0 | 4.8357 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5693 | 31.9 | 0 | 80.5693 | 1115.1565 | 87.5% | 0 | 0 | 0 | 0% | 31.9
2830 | 0 | 0 | 0 | 5.6416 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2331 | 30.1 | 0 | 76.2331 | 1044.2148 | 81.93% | 0 | 0 | 0 | 0% | 30.1
2831 | 0 | 0 | 0 | 4.8357 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3487 | 28.8 | 0 | 73.3487 | 976.4806 | 76.62% | 0 | 0 | 0 | 0% | 28.8
2832 | 0 | 0 | 0 | 2.8208 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.6398 | 28.5 | 0 | 72.6398 | 909.4712 | 71.36% | 0 | 0 | 0 | 0% | 28.5
2833 | 0 | 0 | 0 | 2.8208 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1965 | 28.3 | 0 | 72.1965 | 842.8868 | 66.13% | 0 | 0 | 0 | 0% | 28.3
2834 | 0 | 0 | 0 | 1.6119 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.7127 | 29.5 | 0 | 74.7127 | 773.4097 | 60.68% | 0 | 0 | 0 | 0% | 29.5
2835 | 0 | 0 | 0 | 2.8208 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2931 | 33.1 | 0 | 83.2931 | 693.9758 | 54.45% | 0 | 0 | 0 | 0% | 33.1
2836 | 0 | 0 | 0 | 4.8357 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7737 | 37 | 0 | 92.7737 | 603.4145 | 47.34% | 0 | 0 | 0 | 0% | 37
2837 | 0 | 0 | 0 | 3.4253 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.6257 | 39.9 | 0 | 99.6257 | 504.5281 | 39.59% | 0 | 0 | 0 | 0% | 39.9
2838 | 0 | 15 | 15 | 4.6342 | 13.3 | 0 | 0 | 0 | 0 | 0.40634 | 0 | 0 | 0.40634 | 0 | 0 | 0 | 102.0533 | 40.8937 | 0 | 102.0533 | 402.8135 | 31.61% | 0 | 0 | 0 | 0% | 41.3
2839 | 72 | 122 | 102 | 4.6342 | 15.1 | 36.2389 | 0 | 16.747 | 0 | 7.3678 | 0 | 0 | 7.3678 | 0 | 0 | 0 | 86.8152 | 34.4322 | 0 | 86.8152 | 319.4693 | 25.07% | 0 | 0 | 0 | 0% | 41.8
2840 | 246 | 318 | 207 | 7.455 | 16.9 | 123.8161 | 68.795 | 0 | 43.4391 | 23.8755 | 0 | 0 | 23.8755 | 0 | 0 | 0 | 0 | 0 | 43.4391 | 0 | 360.2688 | 28.27% | 0 | 0 | 0 | 0% | 23.8755
2841 | 521 | 548 | 220 | 9.0669 | 18.7 | 262.2284 | 159.2746 | 0 | 127.5095 | 52.6664 | 0 | 5.2332 | 47.4332 | 0 | 0 | 0 | 0 | 0 | 127.5095 | 0 | 480.0301 | 37.66% | 4.0139 | 0 | 4.0797 | 8.159% | 42.2
2842 | 597 | 739 | 283 | 10.2758 | 20.1 | 300.4805 | 190.8327 | 0 | 156.3372 | 92.1058 | 0.052887 | 25 | 67.0529 | 0 | 0 | 0 | 0 | 0 | 156.3372 | 0 | 626.8673 | 49.18% | 19.175 | 0 | 23.5691 | 47.14% | 42
2843 | 298 | 698 | 434 | 10.4773 | 20.6 | 149.9886 | 97.9157 | 0 | 69.229 | 82.5928 | 0 | 20.7464 | 61.8464 | 0 | 0 | 0 | 0 | 0 | 69.229 | 0 | 691.8896 | 54.29% | 15.9125 | 0 | 39.7426 | 79.49% | 41.1
2844 | 520 | 819 | 329 | 11.6862 | 20.7 | 261.725 | 172.8674 | 0 | 138.7927 | 109.8 | 21.6424 | 13.1576 | 75 | 0 | 0 | 0 | 0 | 0 | 138.7927 | 0 | 822.2485 | 64.51% | 10.0919 | 0 | 50 | 100% | 40.2
2845 | 756 | 945 | 240 | 10.6788 | 21.7 | 380.5079 | 250.1464 | 0 | 211.4683 | 110.4 | 35.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 211.4683 | 0 | 1020.8668 | 80.1% | 0 | 0 | 50 | 100% | 39.6
2846 | 317 | 674 | 385 | 9.0669 | 21.9 | 159.5516 | 102.642 | 0 | 74.473 | 80.1549 | 20.5274 | 0 | 59.6274 | 0 | 0 | 0 | 0 | 0 | 74.473 | 0 | 1090.8144 | 85.59% | 0 | 0 | 50 | 100% | 39.1
2847 | 291 | 579 | 341 | 8.6639 | 21.8 | 146.4654 | 91.0164 | 0 | 64.1318 | 62.1538 | 11.8769 | 0 | 50.2769 | 0 | 0 | 0 | 0 | 0 | 64.1318 | 0 | 1151.0492 | 90.31% | 0 | 0 | 50 | 100% | 38.4
2848 | 167 | 417 | 309 | 8.261 | 21.4 | 84.054 | 0 | 48.9786 | 0 | 34.6664 | 0 | 0 | 34.6664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151.0492 | 90.31% | 0 | 3.6336 | 46.3074 | 92.61% | 38.3
2849 | 404 | 362 | 179 | 9.2684 | 20.7 | 203.3402 | 103.3796 | 0 | 75.0126 | 29.6499 | 0 | 0 | 29.6499 | 0 | 0 | 0 | 0 | 0 | 75.0126 | 0 | 1221.5036 | 95.84% | 0 | 9.9501 | 36.1956 | 72.39% | 39.6
2850 | 547 | 226 | 64 | 9.4699 | 19.9 | 275.3146 | 105.6114 | 0 | 76.9715 | 10.1121 | 0 | 0 | 10.1121 | 0 | 0 | 0 | 0 | 0 | 76.9715 | 0 | 1274.5104 | 100% | 0 | 25 | 10.7887 | 21.58% | 35.1121
2851 | 247 | 58 | 27 | 8.8654 | 18.1 | 124.3194 | 0 | 0 | 0 | 1.1771 | 0 | 0 | 1.1771 | 0 | 0 | 0 | 71.943 | 27.9063 | 0 | 71.943 | 1208.2718 | 94.8% | 0 | 10.6166 | 0 | 0% | 39.7
2852 | 0 | 0 | 0 | 8.6639 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3096 | 36.3 | 0 | 91.3096 | 1119.8211 | 87.86% | 0 | 0 | 0 | 0% | 36.3
2853 | 0 | 0 | 0 | 6.2461 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0646 | 34.2 | 0 | 86.0646 | 1037.3182 | 81.39% | 0 | 0 | 0 | 0% | 34.2
2854 | 0 | 0 | 0 | 4.2312 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9846 | 32.1 | 0 | 80.9846 | 960.8142 | 75.39% | 0 | 0 | 0 | 0% | 32.1
2855 | 0 | 0 | 0 | 3.8283 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0591 | 30.9 | 0 | 78.0591 | 887.6689 | 69.65% | 0 | 0 | 0 | 0% | 30.9
2856 | 0 | 0 | 0 | 1.6119 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.8417 | 30.4 | 0 | 76.8417 | 815.9038 | 64.02% | 0 | 0 | 0 | 0% | 30.4
2857 | 0 | 0 | 0 | 2.4178 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7884 | 30.4 | 0 | 76.7884 | 744.128 | 58.39% | 0 | 0 | 0 | 0% | 30.4
2858 | 0 | 0 | 0 | 2.0149 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1784 | 31 | 0 | 78.1784 | 670.6711 | 52.62% | 0 | 0 | 0 | 0% | 31
2859 | 0 | 0 | 0 | 2.8208 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0986 | 34.3 | 0 | 86.0986 | 587.8044 | 46.12% | 0 | 0 | 0 | 0% | 34.3
2860 | 0 | 0 | 0 | 3.6268 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7787 | 37.9 | 0 | 94.7787 | 494.717 | 38.82% | 0 | 0 | 0 | 0% | 37.9
2861 | 0 | 0 | 0 | 2.6193 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.1103 | 41 | 0 | 102.1103 | 392.7536 | 30.82% | 0 | 0 | 0 | 0% | 41
2862 | 99 | 26 | 14 | 2.8208 | 10.6 | 49.8284 | 0 | 0 | 0 | 0.27606 | 0 | 0 | 0.27606 | 0 | 0 | 0 | 104.848 | 42.1239 | 0 | 104.848 | 287.5759 | 22.56% | 0 | 0 | 0 | 0% | 42.4
2863 | 572 | 187 | 48 | 1.0074 | 14.3 | 287.8975 | 133.312 | 0 | 107.0398 | 5.9249 | 0 | 0 | 5.9249 | 0 | 0 | 0 | 91.8266 | 36.5751 | 107.0398 | 91.8266 | 299.1591 | 23.47% | 0 | 0 | 0 | 0% | 42.5
2864 | 760 | 398 | 69 | 1.2089 | 16.7 | 382.5212 | 212.6927 | 0 | 181.3059 | 29.2284 | 0 | 0 | 29.2284 | 0 | 0 | 0 | 0 | 0 | 181.3059 | 0 | 470.3801 | 36.91% | 0 | 0 | 0 | 0% | 29.2284
2865 | 848 | 600 | 84 | 3.2238 | 18.7 | 426.8131 | 259.2816 | 0 | 224.001 | 62.5663 | 0 | 9.7832 | 52.7832 | 0 | 0 | 0 | 0 | 0 | 224.001 | 0 | 681.9212 | 53.5% | 7.5037 | 0 | 7.6278 | 15.26% | 43
2866 | 898 | 771 | 92 | 4.6342 | 20 | 451.979 | 287.0146 | 0 | 249.5995 | 97.6542 | 2.3771 | 25 | 70.2771 | 0 | 0 | 0 | 0 | 0 | 249.5995 | 0 | 917.637 | 72% | 19.175 | 0 | 27.1201 | 54.24% | 42.9
2867 | 924 | 894 | 99 | 5.2387 | 21.3 | 465.0653 | 303.5726 | 0 | 264.8181 | 108.1 | 8.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 264.8181 | 0 | 1167.7248 | 91.62% | 19.175 | 0 | 46.6124 | 93.22% | 41.9
2868 | 938 | 965 | 102 | 5.2387 | 22.5 | 472.1117 | 187.564 | 124.2608 | 163.9148 | 109 | 29.6552 | 4.3448 | 75 | 0 | 0 | 0 | 0 | 0 | 163.9148 | 0 | 1274.5104 | 100% | 3.3325 | 0 | 50 | 100% | 41
2869 | 929 | 969 | 109 | 7.052 | 23.1 | 467.5819 | 0 | 307.3974 | 0 | 109.6 | 34.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.4
2870 | 905 | 911 | 114 | 9.4699 | 23.5 | 455.5022 | 0 | 293.0668 | 0 | 110 | 35 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40
2871 | 864 | 797 | 118 | 10.2758 | 23.5 | 434.8662 | 0 | 270.2463 | 0 | 107.4326 | 34.1163 | 0 | 73.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.2
2872 | 795 | 628 | 112 | 7.052 | 23.8 | 400.1373 | 0 | 233.4516 | 0 | 72.5486 | 16.9243 | 0 | 55.6243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.7
2873 | 713 | 439 | 98 | 7.052 | 23.6 | 358.8653 | 0 | 182.9662 | 0 | 34.2081 | 0 | 0 | 34.2081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.0919 | 44.8247 | 89.65% | 39.3
2874 | 501 | 273 | 124 | 10.0743 | 21.4 | 252.162 | 0 | 97.2995 | 0 | 13.9452 | 0 | 0 | 13.9452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 19.4146 | 38.83% | 38.9452
2875 | 93 | 54 | 42 | 9.4699 | 18.4 | 46.8085 | 0 | 0 | 0 | 2.0109 | 0 | 0 | 2.0109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 19.1015 | 0 | 0% | 21.1124
2876 | 0 | 0 | 0 | 7.455 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6408 | 36 | 0 | 90.6408 | 1186.9281 | 93.13% | 0 | 0 | 0 | 0% | 36
2877 | 0 | 0 | 0 | 7.6565 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4344 | 33.9 | 0 | 85.4344 | 1105.318 | 86.72% | 0 | 0 | 0 | 0% | 33.9
2878 | 0 | 0 | 0 | 7.858 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5294 | 31.9 | 0 | 80.5294 | 1029.4022 | 80.77% | 0 | 0 | 0 | 0% | 31.9
2879 | 0 | 0 | 0 | 5.6416 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1498 | 30.1 | 0 | 76.1498 | 958.4994 | 75.21% | 0 | 0 | 0 | 0% | 30.1
2880 | 0 | 0 | 0 | 5.4401 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3226 | 29.3 | 0 | 74.3226 | 889.5787 | 69.8% | 0 | 0 | 0 | 0% | 29.3
2881 | 0 | 0 | 0 | 5.6416 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.1849 | 28.8 | 0 | 73.1849 | 821.8719 | 64.49% | 0 | 0 | 0 | 0% | 28.8
2882 | 0 | 0 | 0 | 5.8431 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0278 | 28.3 | 0 | 72.0278 | 755.3772 | 59.27% | 0 | 0 | 0 | 0% | 28.3
2883 | 0 | 0 | 0 | 4.4327 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.1205 | 27.9 | 0 | 71.1205 | 689.8462 | 54.13% | 0 | 0 | 0 | 0% | 27.9
2884 | 0 | 0 | 0 | 4.8357 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8826 | 27.8 | 0 | 70.8826 | 624.5329 | 49% | 0 | 0 | 0 | 0% | 27.8
2885 | 0 | 0 | 0 | 7.6565 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7825 | 29.1 | 0 | 73.7825 | 556.0487 | 43.63% | 0 | 0 | 0 | 0% | 29.1
2886 | 51 | 22 | 16 | 5.8431 | 11.2 | 25.6692 | 0 | 0 | 0 | 0.41721 | 0 | 0 | 0.41721 | 0 | 0 | 0 | 78.165 | 30.9828 | 0 | 78.165 | 482.6146 | 37.87% | 0 | 0 | 0 | 0% | 31.4
2887 | 430 | 182 | 70 | 5.8431 | 12.9 | 216.4265 | 100.417 | 0 | 74.1882 | 6.9042 | 0 | 0 | 6.9042 | 0 | 0 | 0 | 67.9273 | 26.3958 | 74.1882 | 67.9273 | 488.9694 | 38.37% | 0 | 0 | 0 | 0% | 33.3
2888 | 729 | 398 | 78 | 6.0446 | 15 | 366.9184 | 204.1654 | 0 | 171.3667 | 29.6667 | 0 | 0 | 29.6667 | 0 | 0 | 0 | 0 | 0 | 171.3667 | 0 | 647.8728 | 50.83% | 0 | 0 | 0 | 0% | 29.6667
2889 | 845 | 604 | 85 | 7.858 | 17.9 | 425.3032 | 258.3961 | 0 | 220.7674 | 72.788 | 0 | 19.044 | 53.744 | 0 | 0 | 0 | 0 | 0 | 220.7674 | 0 | 852.5841 | 66.9% | 14.6067 | 0 | 14.8505 | 29.7% | 34.7
2890 | 891 | 779 | 101 | 9.6714 | 20 | 448.4558 | 284.7449 | 0 | 244.4658 | 108.7618 | 11.8809 | 25 | 71.8809 | 0 | 0 | 0 | 0 | 0 | 244.4658 | 0 | 1079.2702 | 84.68% | 19.175 | 0 | 34.3456 | 68.69% | 35
2891 | 810 | 869 | 164 | 10.4773 | 21.5 | 407.6871 | 266.0923 | 0 | 226.4352 | 115.7 | 20.6251 | 20.0749 | 75 | 0 | 0 | 0 | 0 | 0 | 226.4352 | 0 | 1274.5104 | 100% | 15.3974 | 0 | 50 | 100% | 34.3
2892 | 815 | 965 | 208 | 11.8877 | 22.6 | 410.2037 | 0 | 270.934 | 0 | 117.6 | 42.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.4
2893 | 826 | 952 | 181 | 12.0892 | 23.2 | 415.7402 | 0 | 273.323 | 0 | 118.6 | 43.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 31.4
2894 | 862 | 906 | 143 | 11.4848 | 23.8 | 433.8596 | 0 | 279.174 | 0 | 118.9 | 43.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 31.1
2895 | 852 | 796 | 125 | 11.2833 | 24.3 | 428.8264 | 0 | 266.5027 | 0 | 115.5732 | 42.1866 | 0 | 73.3866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 31.2
2896 | 875 | 651 | 82 | 11.2833 | 24.3 | 440.4027 | 0 | 257.0771 | 0 | 83.568 | 25.834 | 0 | 57.734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 31.9
2897 | 815 | 457 | 66 | 11.6862 | 23.7 | 410.2037 | 0 | 209.7152 | 0 | 36.9464 | 1.5232 | 0 | 35.4232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.9
2898 | 645 | 241 | 52 | 10.8803 | 21.8 | 324.6397 | 0 | 125.9811 | 0 | 10.0941 | 0 | 0 | 10.0941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.5865 | 49.17% | 35.0941
2899 | 80 | 34 | 22 | 10.0743 | 19.1 | 40.2654 | 0 | 0 | 0 | 0.9036 | 0 | 0 | 0.9036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.1865 | 0 | 0% | 25.0901
2900 | 0 | 0 | 0 | 11.2833 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9704 | 33.6 | 0 | 84.9704 | 1193.7252 | 93.66% | 0 | 0 | 0 | 0% | 33.6
2901 | 0 | 0 | 0 | 10.4773 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0143 | 31.2 | 0 | 79.0143 | 1119.74 | 87.86% | 0 | 0 | 0 | 0% | 31.2
2902 | 0 | 0 | 0 | 8.8654 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5045 | 29.3 | 0 | 74.5045 | 1050.7966 | 82.45% | 0 | 0 | 0 | 0% | 29.3
2903 | 0 | 0 | 0 | 8.8654 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.802 | 28.1 | 0 | 71.802 | 984.6181 | 77.25% | 0 | 0 | 0 | 0% | 28.1
2904 | 0 | 0 | 0 | 6.2461 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.9447 | 27.7 | 0 | 70.9447 | 919.2575 | 72.13% | 0 | 0 | 0 | 0% | 27.7
2905 | 0 | 0 | 0 | 4.2312 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.7119 | 27.6 | 0 | 70.7119 | 854.1116 | 67.01% | 0 | 0 | 0 | 0% | 27.6
2906 | 0 | 0 | 0 | 4.2312 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.447 | 28.4 | 0 | 72.447 | 787.2832 | 61.77% | 0 | 0 | 0 | 0% | 28.4
2907 | 0 | 0 | 0 | 4.6342 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0006 | 32.1 | 0 | 81.0006 | 710.7033 | 55.76% | 0 | 0 | 0 | 0% | 32.1
2908 | 0 | 0 | 0 | 4.8357 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1529 | 35.5 | 0 | 89.1529 | 624.3676 | 48.99% | 0 | 0 | 0 | 0% | 35.5
2909 | 0 | 0 | 0 | 4.8357 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3169 | 38.5 | 0 | 96.3169 | 529.5275 | 41.55% | 0 | 0 | 0 | 0% | 38.5
2910 | 23 | 25 | 22 | 5.4401 | 14.5 | 11.5763 | 0 | 0 | 0 | 0.74786 | 0 | 0 | 0.74786 | 0 | 0 | 0 | 98.2755 | 39.2521 | 0 | 98.2755 | 432.5057 | 33.94% | 0 | 0 | 0 | 0% | 40
2911 | 218 | 165 | 103 | 8.261 | 15.2 | 109.7232 | 0 | 51.0101 | 0 | 8.212 | 0 | 0 | 8.212 | 0 | 0 | 0 | 83.3783 | 32.988 | 0 | 83.3783 | 353.3401 | 27.72% | 0 | 0 | 0 | 0% | 41.2
2912 | 426 | 335 | 138 | 4.4327 | 18.3 | 214.4132 | 119.3929 | 0 | 93.0066 | 24.357 | 0 | 0 | 24.357 | 0 | 0 | 0 | 0 | 0 | 93.0066 | 0 | 440.3513 | 34.55% | 0 | 0 | 0 | 0% | 24.357
2913 | 574 | 547 | 193 | 12.2907 | 20.1 | 288.9042 | 175.5477 | 0 | 140.9771 | 53.7232 | 0 | 5.7616 | 47.9616 | 0 | 0 | 0 | 0 | 0 | 140.9771 | 0 | 572.2408 | 44.9% | 4.4192 | 0 | 4.4936 | 8.987% | 42.2
2914 | 762 | 771 | 190 | 13.4996 | 21.5 | 383.5278 | 243.4924 | 0 | 203.6099 | 100.1134 | 3.9567 | 25 | 71.1567 | 0 | 0 | 0 | 0 | 0 | 203.6099 | 0 | 762.7257 | 59.84% | 19.175 | 0 | 23.9914 | 47.98% | 42.2
2915 | 522 | 745 | 290 | 14.5071 | 22.3 | 262.7317 | 171.4655 | 0 | 135.8218 | 96.6214 | 2.6607 | 25 | 68.9607 | 0 | 0 | 0 | 0 | 0 | 135.8218 | 0 | 889.7921 | 69.81% | 19.175 | 0 | 43.4893 | 86.98% | 41.3
2916 | 326 | 752 | 435 | 13.7011 | 22.9 | 164.0815 | 108.3731 | 0 | 77.1505 | 92.1905 | 17.5973 | 8.348 | 66.2452 | 0 | 0 | 0 | 0 | 0 | 77.1505 | 0 | 961.9694 | 75.48% | 6.4029 | 0 | 50 | 100% | 40.3
2917 | 141 | 589 | 446 | 14.3056 | 23.2 | 70.9678 | 0 | 46.658 | 0 | 60.0984 | 10.1492 | 0 | 49.9492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 961.9694 | 75.48% | 0 | 0 | 50 | 100% | 39.8
2918 | 27 | 415 | 384 | 14.7085 | 21.8 | 13.5896 | 0 | 8.7454 | 0 | 31.8925 | 0 | 0 | 31.8925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 961.9694 | 75.48% | 0 | 7.7075 | 42.164 | 84.33% | 39.6
2919 | 13 | 312 | 298 | 16.7234 | 20.8 | 6.5431 | 0 | 4.0665 | 0 | 23.688 | 0 | 0 | 23.688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 961.9694 | 75.48% | 0 | 15.312 | 26.5964 | 53.19% | 39
2920 | 23 | 281 | 263 | 17.1264 | 19.7 | 11.5763 | 0 | 6.7603 | 0 | 21.398 | 0 | 0 | 21.398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 961.9694 | 75.48% | 0 | 17.602 | 8.6999 | 17.4% | 39
2921 | 110 | 272 | 220 | 14.3056 | 19.2 | 55.3649 | 0 | 28.3804 | 0 | 20.9535 | 0 | 0 | 20.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 961.9694 | 75.48% | 0 | 8.5576 | 0 | 0% | 29.5111
2922 | 93 | 161 | 134 | 11.4848 | 18.5 | 46.8085 | 0 | 18.2652 | 0 | 10.4036 | 0 | 0 | 10.4036 | 0 | 0 | 0 | 80.737 | 31.6964 | 0 | 80.737 | 886.5741 | 69.56% | 0 | 0 | 0 | 0% | 42.1
2923 | 38 | 40 | 34 | 9.6714 | 17.3 | 19.1261 | 0 | 0 | 0 | 1.6653 | 0 | 0 | 1.6653 | 0 | 0 | 0 | 95.7805 | 38.0347 | 0 | 95.7805 | 793.141 | 62.23% | 0 | 0 | 0 | 0% | 39.7
2924 | 0 | 0 | 0 | 6.8506 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5683 | 36.4 | 0 | 91.5683 | 704.324 | 55.26% | 0 | 0 | 0 | 0% | 36.4
2925 | 0 | 0 | 0 | 7.6565 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4562 | 34.3 | 0 | 86.4562 | 621.4495 | 48.76% | 0 | 0 | 0 | 0% | 34.3
2926 | 0 | 0 | 0 | 8.8654 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8391 | 32.8 | 0 | 82.8391 | 542.8783 | 42.6% | 0 | 0 | 0 | 0% | 32.8
2927 | 0 | 0 | 0 | 6.2461 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6641 | 31.1 | 0 | 78.6641 | 469.0962 | 36.81% | 0 | 0 | 0 | 0% | 31.1
2928 | 0 | 0 | 0 | 4.6342 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3764 | 30.6 | 0 | 77.3764 | 396.6941 | 31.13% | 0 | 0 | 0 | 0% | 30.6
2929 | 0 | 0 | 0 | 3.0223 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9103 | 30.4 | 0 | 76.9103 | 324.831 | 25.49% | 0 | 0 | 0 | 0% | 30.4
2930 | 0 | 0 | 0 | 2.4178 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5239 | 31.1 | 0 | 78.5239 | 250.9961 | 19.69% | 0 | 0 | 0 | 0% | 31.1
2931 | 0 | 0 | 0 | 1.6119 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1986 | 33.9 | 0 | 85.1986 | 169.1629 | 13.27% | 0 | 0 | 0 | 0% | 33.9
2932 | 0 | 0 | 0 | 2.4178 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.1629 | 13.27% | 0 | 0 | 0 | 0% | 0
2933 | 0 | 0 | 0 | 2.4178 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.1629 | 13.27% | 0 | 0 | 0 | 0% | 0
2934 | 105 | 27 | 15 | 4.8357 | 11 | 52.8483 | 0 | 0 | 0 | 0.3218 | 0 | 0 | 0.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.1629 | 13.27% | 0 | 0 | 0 | 0% | 0.3218
2935 | 540 | 190 | 49 | 5.8431 | 13.3 | 271.7914 | 126.6047 | 0 | 98.8134 | 5.9203 | 0 | 0 | 5.9203 | 0 | 0 | 0 | 0 | 0 | 98.8134 | 0 | 261.7554 | 20.54% | 0 | 0 | 0 | 0% | 5.9203
2936 | 788 | 419 | 71 | 8.4625 | 15.4 | 396.6141 | 221.0081 | 0 | 185.5531 | 30.9371 | 0 | 0 | 30.9371 | 0 | 0 | 0 | 0 | 0 | 185.5531 | 0 | 435.6268 | 34.18% | 0 | 0 | 0 | 0% | 30.9371
2937 | 814 | 611 | 104 | 6.6491 | 17.5 | 409.7004 | 248.9787 | 0 | 212.7534 | 63.6811 | 0 | 10.0406 | 53.6406 | 0 | 0 | 0 | 0 | 0 | 212.7534 | 0 | 634.986 | 49.82% | 7.7011 | 0 | 7.8319 | 15.66% | 43.6
2938 | 924 | 797 | 91 | 2.8208 | 19.7 | 465.0653 | 295.227 | 0 | 257.9665 | 98.1036 | 2.3518 | 25 | 70.7518 | 0 | 0 | 0 | 0 | 0 | 257.9665 | 0 | 876.7119 | 68.79% | 19.175 | 0 | 27.3325 | 54.67% | 43.4
2939 | 948 | 925 | 101 | 3.4253 | 21.4 | 477.1449 | 311.3691 | 0 | 272.758 | 107.9 | 7.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 272.758 | 0 | 1132.2982 | 88.84% | 19.175 | 0 | 46.8332 | 93.67% | 42.1
2940 | 861 | 956 | 157 | 4.4327 | 22.3 | 433.3563 | 278.5655 | 7.6581 | 242.2879 | 109.1 | 30.0401 | 4.0599 | 75 | 0 | 0 | 0 | 0 | 0 | 242.2879 | 0 | 1274.5104 | 100% | 3.1139 | 0 | 50 | 100% | 40.9
2941 | 860 | 953 | 150 | 8.261 | 22.5 | 432.853 | 0 | 284.5881 | 0 | 109.7 | 34.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.3
2942 | 902 | 937 | 138 | 11.8877 | 22.1 | 453.9923 | 0 | 292.1904 | 0 | 110.2 | 35.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.8
2943 | 481 | 603 | 222 | 14.3056 | 19.9 | 242.0957 | 0 | 150.4629 | 0 | 72.019 | 16.3095 | 0 | 55.7095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.4
2944 | 427 | 436 | 162 | 13.9026 | 18.9 | 214.9165 | 0 | 125.5574 | 0 | 39.4563 | 0.078143 | 0 | 39.3781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.3
2945 | 433 | 332 | 114 | 10.6788 | 18.6 | 217.9364 | 0 | 112.0031 | 0 | 25.3642 | 0 | 0 | 25.3642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 14.4358 | 35.3213 | 70.64% | 39.8
2946 | 449 | 225 | 86 | 8.0595 | 18.8 | 225.9895 | 0 | 88.6563 | 0 | 10.5184 | 0 | 0 | 10.5184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 9.8998 | 19.8% | 35.5184
2947 | 1 | 11 | 11 | 9.6714 | 16.1 | 0.50332 | 0 | 0 | 0 | 0.31243 | 0 | 0 | 0.31243 | 0 | 0 | 0 | 74.8989 | 29.3511 | 0 | 74.8989 | 1205.412 | 94.58% | 0 | 9.7364 | 0 | 0% | 39.4
2948 | 0 | 0 | 0 | 8.4625 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8865 | 36.6 | 0 | 91.8865 | 1116.1186 | 87.57% | 0 | 0 | 0 | 0% | 36.6
2949 | 0 | 0 | 0 | 7.2535 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2883 | 34.7 | 0 | 87.2883 | 1032.1637 | 80.99% | 0 | 0 | 0 | 0% | 34.7
2950 | 0 | 0 | 0 | 6.8506 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7571 | 32.8 | 0 | 82.7571 | 953.6733 | 74.83% | 0 | 0 | 0 | 0% | 32.8
2951 | 0 | 0 | 0 | 10.4773 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1292 | 31.3 | 0 | 79.1292 | 879.4107 | 69% | 0 | 0 | 0 | 0% | 31.3
2952 | 0 | 0 | 0 | 8.8654 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9638 | 30.4 | 0 | 76.9638 | 807.646 | 63.37% | 0 | 0 | 0 | 0% | 30.4
2953 | 0 | 0 | 0 | 8.261 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7666 | 29.9 | 0 | 75.7666 | 737.2228 | 57.84% | 0 | 0 | 0 | 0% | 29.9
2954 | 0 | 0 | 0 | 8.261 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7055 | 29.9 | 0 | 75.7055 | 666.7887 | 52.32% | 0 | 0 | 0 | 0% | 29.9
2955 | 0 | 0 | 0 | 6.2461 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.315 | 30.6 | 0 | 77.315 | 594.4348 | 46.64% | 0 | 0 | 0 | 0% | 30.6
2956 | 0 | 0 | 0 | 5.4401 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2915 | 31 | 0 | 78.2915 | 520.953 | 40.87% | 0 | 0 | 0 | 0% | 31
2957 | 0 | 0 | 0 | 6.0446 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7561 | 33.7 | 0 | 84.7561 | 439.7918 | 34.51% | 0 | 0 | 0 | 0% | 33.7
2958 | 0 | 7 | 7 | 6.0446 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1924 | 36.8 | 0 | 92.1924 | 349.7871 | 27.44% | 0 | 0 | 0 | 0% | 36.8
2959 | 16 | 90 | 84 | 5.6416 | 13 | 8.0531 | 0 | 3.7586 | 0 | 5.9827 | 0 | 0 | 5.9827 | 0 | 0 | 0 | 82.7002 | 32.8173 | 0 | 82.7002 | 271.1207 | 21.27% | 0 | 0 | 0 | 0% | 38.8
2960 | 4 | 174 | 171 | 4.4327 | 13.9 | 2.0133 | 0 | 1.1227 | 0 | 12.9729 | 0 | 0 | 12.9729 | 0 | 0 | 0 | 67.2099 | 26.0271 | 0 | 67.2099 | 209.2622 | 16.42% | 0 | 0 | 0 | 0% | 39
2961 | 53 | 313 | 278 | 3.8283 | 15.2 | 26.6758 | 0 | 16.2132 | 0 | 24.7381 | 0 | 0 | 24.7381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.2622 | 16.42% | 0 | 0 | 0 | 0% | 24.7381
2962 | 18 | 372 | 352 | 5.6416 | 15.8 | 9.0597 | 0 | 5.7506 | 0 | 28.5633 | 0 | 0 | 28.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.2622 | 16.42% | 0 | 0 | 0 | 0% | 28.5633
2963 | 398 | 769 | 408 | 8.8654 | 18 | 200.3203 | 130.7113 | 0 | 100.8637 | 97.3755 | 4.7878 | 25 | 67.5878 | 0 | 0 | 0 | 0 | 0 | 100.8637 | 0 | 303.4022 | 23.81% | 19.175 | 0 | 19.5035 | 39.01% | 37.8
2964 | 843 | 1004 | 217 | 13.0966 | 18.8 | 424.2966 | 280.2387 | 0 | 238.0632 | 113.9 | 13.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 238.0632 | 0 | 525.5959 | 41.24% | 19.175 | 0 | 39.007 | 78.01% | 36.1
2965 | 898 | 992 | 150 | 12.0892 | 19.3 | 451.979 | 297.1701 | 0 | 254.663 | 114.9 | 25.8089 | 14.0911 | 75 | 0 | 0 | 0 | 0 | 0 | 254.663 | 0 | 763.2828 | 59.89% | 10.8078 | 0 | 50 | 100% | 35.1
2966 | 918 | 935 | 117 | 12.6937 | 19.6 | 462.0454 | 297.402 | 0 | 254.517 | 115.5 | 40.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 254.517 | 0 | 1000.8335 | 78.53% | 0 | 0 | 50 | 100% | 34.5
2967 | 895 | 824 | 112 | 14.5071 | 19 | 450.4691 | 279.9714 | 0 | 236.9501 | 115.8 | 40.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 236.9501 | 0 | 1221.9882 | 95.88% | 0 | 0 | 50 | 100% | 34.2
2968 | 839 | 659 | 107 | 13.7011 | 18.5 | 422.2833 | 117.9043 | 128.8947 | 98.6207 | 83.4022 | 24.4011 | 0 | 59.0011 | 0 | 0 | 0 | 0 | 0 | 98.6207 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.6
2969 | 718 | 454 | 101 | 13.4996 | 17.8 | 361.3819 | 0 | 186.1855 | 0 | 35.1889 | 0 | 0 | 35.1889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.1889
2970 | 70 | 123 | 97 | 12.0892 | 15.9 | 35.2322 | 0 | 13.8934 | 0 | 7.6085 | 0 | 0 | 7.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.5756 | 49.15% | 32.6085
2971 | 0 | 27 | 27 | 8.6639 | 15.1 | 0 | 0 | 0 | 0 | 1.3727 | 0 | 0 | 1.3727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.1654 | 0 | 0% | 25.5381
2972 | 0 | 0 | 0 | 4.8357 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9199 | 34.9 | 0 | 87.9199 | 1190.015 | 93.37% | 0 | 0 | 0 | 0% | 34.9
2973 | 0 | 0 | 0 | 3.0223 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0717 | 32.5 | 0 | 82.0717 | 1112.4178 | 87.28% | 0 | 0 | 0 | 0% | 32.5
2974 | 0 | 0 | 0 | 2.6193 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.174 | 30.5 | 0 | 77.174 | 1040.4229 | 81.63% | 0 | 0 | 0 | 0% | 30.5
2975 | 0 | 0 | 0 | 1.6119 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9576 | 29.1 | 0 | 73.9576 | 972.0064 | 76.27% | 0 | 0 | 0 | 0% | 29.1
2976 | 0 | 0 | 0 | 1.8134 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.7092 | 28.1 | 0 | 71.7092 | 905.9489 | 71.08% | 0 | 0 | 0 | 0% | 28.1
2977 | 0 | 0 | 0 | 2.4178 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.7905 | 27.7 | 0 | 70.7905 | 840.7649 | 65.97% | 0 | 0 | 0 | 0% | 27.7
2978 | 0 | 0 | 0 | 2.2164 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.7905 | 27.7 | 0 | 70.7905 | 775.5716 | 60.85% | 0 | 0 | 0 | 0% | 27.7
2979 | 0 | 0 | 0 | 2.2164 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.6805 | 28.1 | 0 | 71.6805 | 709.5119 | 55.67% | 0 | 0 | 0 | 0% | 28.1
2980 | 0 | 0 | 0 | 2.2164 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.0204 | 27.8 | 0 | 71.0204 | 644.0775 | 50.54% | 0 | 0 | 0 | 0% | 27.8
2981 | 0 | 0 | 0 | 2.8208 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.331 | 29.3 | 0 | 74.331 | 575.1098 | 45.12% | 0 | 0 | 0 | 0% | 29.3
2982 | 143 | 36 | 15 | 4.2312 | 14 | 71.9744 | 0 | 0 | 0 | 0.30868 | 0 | 0 | 0.30868 | 0 | 0 | 0 | 79.8446 | 31.5913 | 0 | 79.8446 | 499.9772 | 39.23% | 0 | 0 | 0 | 0% | 31.9
2983 | 647 | 212 | 44 | 2.2164 | 17.4 | 325.6463 | 152.2863 | 0 | 124.462 | 6.1175 | 0 | 0 | 6.1175 | 0 | 0 | 0 | 71.7883 | 27.8825 | 124.462 | 71.7883 | 548.9745 | 43.07% | 0 | 0 | 0 | 0% | 34
2984 | 810 | 425 | 60 | 1.6119 | 20.4 | 407.6871 | 227.5042 | 0 | 195.0262 | 29.6154 | 0 | 0 | 29.6154 | 0 | 0 | 0 | 0 | 0 | 195.0262 | 0 | 729.3439 | 57.23% | 0 | 0 | 0 | 0% | 29.6154
2985 | 897 | 628 | 67 | 1.6119 | 22.8 | 451.4757 | 274.4365 | 0 | 238.7886 | 69.3405 | 0 | 17.1203 | 52.2203 | 0 | 0 | 0 | 0 | 0 | 238.7886 | 0 | 950.1868 | 74.55% | 13.1312 | 0 | 13.3581 | 26.72% | 35.1
2986 | 931 | 793 | 76 | 6.2461 | 23.9 | 468.5885 | 297.4033 | 0 | 258.5311 | 105.5966 | 10.2483 | 25 | 70.3483 | 0 | 0 | 0 | 0 | 0 | 258.5311 | 0 | 1189.2886 | 93.31% | 19.175 | 0 | 32.8643 | 65.73% | 35.1
2987 | 920 | 908 | 103 | 13.2981 | 22.9 | 463.052 | 153.9746 | 148.1479 | 131.8038 | 115.6 | 18.6382 | 21.9618 | 75 | 0 | 0 | 0 | 0 | 0 | 131.8038 | 0 | 1274.5104 | 100% | 16.8447 | 0 | 50 | 100% | 34.4
2988 | 910 | 980 | 130 | 11.8877 | 23 | 458.0188 | 0 | 302.5104 | 0 | 117.1 | 42.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.9
2989 | 903 | 997 | 149 | 12.0892 | 23.6 | 454.4956 | 0 | 298.8316 | 0 | 117.9 | 42.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.1
2990 | 700 | 848 | 218 | 11.2833 | 23.8 | 352.3222 | 0 | 226.7976 | 0 | 118.2 | 43.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 31.8
2991 | 860 | 820 | 131 | 8.261 | 25.1 | 432.853 | 0 | 269.0248 | 0 | 114.1233 | 41.0616 | 0 | 73.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32
2992 | 829 | 658 | 109 | 10.8803 | 25 | 417.2501 | 0 | 243.9464 | 0 | 81.1214 | 24.1607 | 0 | 56.9607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.8
2993 | 724 | 449 | 92 | 9.6714 | 23.9 | 364.4018 | 0 | 188.1925 | 0 | 33.6884 | 0 | 0 | 33.6884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.6884
2994 | 578 | 239 | 63 | 9.8729 | 22.2 | 290.9175 | 0 | 115.2949 | 0 | 9.9132 | 0 | 0 | 9.9132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.5719 | 49.14% | 34.9132
2995 | 222 | 56 | 26 | 6.4476 | 20 | 111.7365 | 0 | 0 | 0 | 1.1461 | 0 | 0 | 1.1461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.1583 | 0 | 0% | 25.3044
2996 | 0 | 0 | 0 | 4.8357 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.756 | 34.7 | 0 | 87.756 | 1190.5413 | 93.41% | 0 | 0 | 0 | 0% | 34.7
2997 | 0 | 0 | 0 | 2.0149 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7934 | 32.3 | 0 | 81.7934 | 1113.4596 | 87.36% | 0 | 0 | 0 | 0% | 32.3
2998 | 0 | 0 | 0 | 2.2164 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5533 | 30.6 | 0 | 77.5533 | 1041.1393 | 81.69% | 0 | 0 | 0 | 0% | 30.6
2999 | 0 | 0 | 0 | 0.80595 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.0011 | 29.5 | 0 | 75.0011 | 971.698 | 76.24% | 0 | 0 | 0 | 0% | 29.5
3000 | 0 | 0 | 0 | 1.4104 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2003 | 29.1 | 0 | 74.2003 | 903.2055 | 70.87% | 0 | 0 | 0 | 0% | 29.1
3001 | 0 | 0 | 0 | 2.0149 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5155 | 29.2 | 0 | 74.5155 | 834.4029 | 65.47% | 0 | 0 | 0 | 0% | 29.2
3002 | 0 | 0 | 0 | 1.0074 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7092 | 30.2 | 0 | 76.7092 | 763.1529 | 59.88% | 0 | 0 | 0 | 0% | 30.2
3003 | 0 | 0 | 0 | 2.6193 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3705 | 33.8 | 0 | 85.3705 | 681.7146 | 53.49% | 0 | 0 | 0 | 0% | 33.8
3004 | 0 | 0 | 0 | 1.4104 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0603 | 37.9 | 0 | 95.0603 | 588.6068 | 46.18% | 0 | 0 | 0 | 0% | 37.9
3005 | 0 | 0 | 0 | 4.0297 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0817 | 41.2 | 0 | 103.0817 | 486.0576 | 38.14% | 0 | 0 | 0 | 0% | 41.2
3006 | 121 | 36 | 18 | 4.0297 | 15.7 | 60.9014 | 0 | 0 | 0 | 0.46023 | 0 | 0 | 0.46023 | 0 | 0 | 0 | 105.1271 | 42.0398 | 0 | 105.1271 | 381.1025 | 29.9% | 0 | 0 | 0 | 0% | 42.5
3007 | 594 | 209 | 52 | 2.4178 | 18.8 | 298.9705 | 140.0834 | 0 | 112.9464 | 6.2684 | 0 | 0 | 6.2684 | 0 | 0 | 0 | 92.1823 | 36.4316 | 112.9464 | 92.1823 | 398.3924 | 31.26% | 0 | 0 | 0 | 0% | 42.7
3008 | 779 | 423 | 72 | 3.2238 | 18.4 | 392.0842 | 218.9533 | 0 | 186.4325 | 29.9902 | 0 | 0 | 29.9902 | 0 | 0 | 0 | 0 | 0 | 186.4325 | 0 | 574.0713 | 45.04% | 0 | 0 | 0 | 0% | 29.9902
3009 | 860 | 623 | 86 | 3.8283 | 19.3 | 432.853 | 263.1509 | 0 | 227.4061 | 64.0712 | 0 | 10.7856 | 53.2856 | 0 | 0 | 0 | 0 | 0 | 227.4061 | 0 | 788.3603 | 61.86% | 8.2726 | 0 | 8.4167 | 16.83% | 42.5
3010 | 904 | 791 | 96 | 6.0446 | 20.7 | 454.9989 | 288.7507 | 0 | 250.4932 | 98.7468 | 2.9234 | 25 | 70.8234 | 0 | 0 | 0 | 0 | 0 | 250.4932 | 0 | 1024.4048 | 80.38% | 19.175 | 0 | 27.9257 | 55.85% | 42.9
3011 | 937 | 917 | 97 | 6.0446 | 23.6 | 471.6084 | 307.682 | 0 | 268.1821 | 108 | 8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 268.1821 | 0 | 1274.5104 | 100% | 19.175 | 0 | 47.4348 | 94.87% | 42
3012 | 941 | 986 | 108 | 5.4401 | 25.6 | 473.6217 | 0 | 312.8146 | 0 | 108.9 | 30.6128 | 3.2872 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 2.5213 | 0 | 50 | 100% | 41.1
3013 | 935 | 999 | 122 | 11.2833 | 26.2 | 470.6018 | 0 | 309.4284 | 0 | 109.6 | 34.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.4
3014 | 869 | 929 | 151 | 11.4848 | 26.4 | 437.3828 | 0 | 281.5768 | 0 | 109.7 | 34.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.3
3015 | 635 | 760 | 248 | 12.8952 | 25.9 | 319.6065 | 0 | 198.6403 | 0 | 95.0735 | 27.6868 | 0 | 67.3868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.7
3016 | 611 | 617 | 209 | 11.0818 | 25 | 307.5269 | 0 | 179.8586 | 0 | 65.1252 | 12.7126 | 0 | 52.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.7
3017 | 440 | 394 | 174 | 10.0743 | 23.9 | 221.4597 | 0 | 114.6362 | 0 | 29.7075 | 0 | 0 | 29.7075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 11.1925 | 38.6143 | 77.23% | 40.9
3018 | 377 | 243 | 126 | 8.0595 | 22.4 | 189.7507 | 0 | 75.5654 | 0 | 12.5284 | 0 | 0 | 12.5284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 13.1819 | 26.36% | 37.5284
3019 | 66 | 50 | 38 | 6.0446 | 19.8 | 33.2189 | 0 | 0 | 0 | 1.9422 | 0 | 0 | 1.9422 | 0 | 0 | 0 | 67.1571 | 25.6993 | 0 | 67.1571 | 1212.8605 | 95.16% | 0 | 12.9585 | 0 | 0% | 40.6
3020 | 0 | 0 | 0 | 3.4253 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5794 | 37.1 | 0 | 93.5794 | 1122.145 | 88.05% | 0 | 0 | 0 | 0% | 37.1
3021 | 0 | 0 | 0 | 2.0149 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8743 | 34.8 | 0 | 87.8743 | 1037.8879 | 81.43% | 0 | 0 | 0 | 0% | 34.8
3022 | 0 | 0 | 0 | 1.0074 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7264 | 33.1 | 0 | 83.7264 | 958.5312 | 75.21% | 0 | 0 | 0 | 0% | 33.1
3023 | 0 | 0 | 0 | 0.60446 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0113 | 32 | 0 | 81.0113 | 882.2905 | 69.23% | 0 | 0 | 0 | 0% | 32
3024 | 0 | 0 | 0 | 1.0074 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6885 | 31.5 | 0 | 79.6885 | 807.4473 | 63.35% | 0 | 0 | 0 | 0% | 31.5
3025 | 0 | 0 | 0 | 1.4104 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.33 | 31.4 | 0 | 79.33 | 732.8738 | 57.5% | 0 | 0 | 0 | 0% | 31.4
3026 | 0 | 0 | 0 | 1.8134 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9605 | 32.1 | 0 | 80.9605 | 656.3161 | 51.5% | 0 | 0 | 0 | 0% | 32.1
3027 | 0 | 0 | 0 | 1.8134 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.457 | 34.8 | 0 | 87.457 | 571.9834 | 44.88% | 0 | 0 | 0 | 0% | 34.8
3028 | 0 | 0 | 0 | 2.4178 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.785 | 38.7 | 0 | 96.785 | 476.5964 | 37.39% | 0 | 0 | 0 | 0% | 38.7
3029 | 0 | 0 | 0 | 3.6268 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6978 | 41.6 | 0 | 103.6978 | 372.9206 | 29.26% | 0 | 0 | 0 | 0% | 41.6
3030 | 68 | 36 | 18 | 2.6193 | 12.2 | 34.2256 | 0 | 0 | 0 | 0.52461 | 0 | 0 | 0.52461 | 0 | 0 | 0 | 106.3202 | 42.6754 | 0 | 106.3202 | 266.1544 | 20.88% | 0 | 0 | 0 | 0% | 43.2
3031 | 577 | 219 | 56 | 1.4104 | 13.4 | 290.4141 | 136.3374 | 0 | 109.7343 | 6.6228 | 0 | 0 | 6.6228 | 0 | 0 | 0 | 91.9632 | 36.6772 | 109.7343 | 91.9632 | 280.3524 | 22% | 0 | 0 | 0 | 0% | 43.3
3032 | 768 | 429 | 79 | 1.4104 | 17.3 | 386.5478 | 216.0149 | 0 | 184.3285 | 30.0852 | 0 | 0 | 30.0852 | 0 | 0 | 0 | 0 | 0 | 184.3285 | 0 | 455.0086 | 35.7% | 0 | 0 | 0 | 0% | 30.0852
3033 | 914 | 643 | 70 | 3.8283 | 21 | 460.0321 | 279.7118 | 0 | 242.9832 | 64.6829 | 0 | 10.3414 | 54.3414 | 0 | 0 | 0 | 0 | 0 | 242.9832 | 0 | 685.2416 | 53.77% | 7.9319 | 0 | 8.0712 | 16.14% | 44
3034 | 941 | 810 | 86 | 6.6491 | 22.6 | 473.6217 | 300.5415 | 0 | 261.1718 | 100.6305 | 3.5652 | 25 | 72.0652 | 0 | 0 | 0 | 0 | 0 | 261.1718 | 0 | 932.7089 | 73.18% | 19.175 | 0 | 27.583 | 55.17% | 43.5
3035 | 925 | 923 | 111 | 7.455 | 24.1 | 465.5686 | 303.72 | 0 | 263.6604 | 107.5 | 7.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 263.6604 | 0 | 1182.5341 | 92.78% | 19.175 | 0 | 47.0949 | 94.19% | 42.5
3036 | 948 | 994 | 109 | 8.261 | 25 | 477.1449 | 195.5074 | 119.6332 | 169.8687 | 108.4 | 29.6778 | 3.7222 | 75 | 0 | 0 | 0 | 0 | 0 | 169.8687 | 0 | 1274.5104 | 100% | 2.8549 | 0 | 50 | 100% | 41.6
3037 | 935 | 995 | 116 | 9.0669 | 25 | 470.6018 | 0 | 309.4351 | 0 | 108.9 | 33.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
3038 | 940 | 937 | 98 | 9.2684 | 25.8 | 473.1183 | 0 | 304.6062 | 0 | 108.8 | 33.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
3039 | 887 | 825 | 116 | 8.261 | 26.4 | 446.4425 | 0 | 277.4687 | 0 | 104.3322 | 31.6661 | 0 | 72.6661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41
3040 | 776 | 638 | 121 | 9.4699 | 25.5 | 390.5743 | 0 | 228.5037 | 0 | 67.7612 | 13.2306 | 0 | 54.5306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.3
3041 | 704 | 450 | 102 | 9.8729 | 23.8 | 354.3354 | 0 | 183.8273 | 0 | 33.64 | 0 | 0 | 33.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.26 | 40.5788 | 81.16% | 42.9
3042 | 507 | 235 | 77 | 9.2684 | 21.4 | 255.1819 | 0 | 102.0976 | 0 | 10.2941 | 0 | 0 | 10.2941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.1429 | 30.29% | 35.2941
3043 | 120 | 49 | 30 | 5.8431 | 19 | 60.3981 | 0 | 0 | 0 | 1.458 | 0 | 0 | 1.458 | 0 | 0 | 0 | 64.7163 | 24.6581 | 0 | 64.7163 | 1215.2286 | 95.35% | 0 | 14.884 | 0 | 0% | 41
3044 | 0 | 0 | 0 | 4.0297 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2308 | 37.8 | 0 | 95.2308 | 1122.5739 | 88.08% | 0 | 0 | 0 | 0% | 37.8
3045 | 0 | 0 | 0 | 1.6119 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7843 | 36 | 0 | 90.7843 | 1034.9855 | 81.21% | 0 | 0 | 0 | 0% | 36
3046 | 0 | 0 | 0 | 1.4104 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6998 | 33.9 | 0 | 85.6998 | 953.3691 | 74.8% | 0 | 0 | 0 | 0% | 33.9
3047 | 0 | 0 | 0 | 1.6119 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5841 | 32.6 | 0 | 82.5841 | 875.4651 | 68.69% | 0 | 0 | 0 | 0% | 32.6
3048 | 0 | 0 | 0 | 1.8134 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2767 | 32.1 | 0 | 81.2767 | 798.9675 | 62.69% | 0 | 0 | 0 | 0% | 32.1
3049 | 0 | 0 | 0 | 3.0223 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8732 | 32 | 0 | 80.8732 | 722.7409 | 56.71% | 0 | 0 | 0 | 0% | 32
3050 | 0 | 0 | 0 | 3.0223 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3112 | 32.6 | 0 | 82.3112 | 644.8017 | 50.59% | 0 | 0 | 0 | 0% | 32.6
3051 | 0 | 0 | 0 | 1.4104 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2409 | 35.5 | 0 | 89.2409 | 558.5325 | 43.82% | 0 | 0 | 0 | 0% | 35.5
3052 | 0 | 0 | 0 | 2.0149 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.7777 | 39.1 | 0 | 97.7777 | 462.0428 | 36.25% | 0 | 0 | 0 | 0% | 39.1
3053 | 0 | 0 | 0 | 2.6193 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2106 | 41.8 | 0 | 104.2106 | 357.8499 | 28.08% | 0 | 0 | 0 | 0% | 41.8
3054 | 117 | 42 | 25 | 2.4178 | 12.8 | 58.8881 | 0 | 0 | 0 | 0.88441 | 0 | 0 | 0.88441 | 0 | 0 | 0 | 105.4535 | 42.3156 | 0 | 105.4535 | 252.1622 | 19.79% | 0 | 0 | 0 | 0% | 43.2
3055 | 326 | 173 | 92 | 1.4104 | 17.7 | 164.0815 | 77.1776 | 0 | 54.0614 | 7.8343 | 0 | 0 | 7.8343 | 0 | 0 | 0 | 91.1097 | 36.0657 | 54.0614 | 91.1097 | 215.5348 | 16.91% | 0 | 0 | 0 | 0% | 43.9
3056 | 653 | 437 | 136 | 6.2461 | 22.5 | 328.6663 | 183.799 | 0 | 152.2605 | 30.9298 | 0 | 0 | 30.9298 | 0 | 0 | 0 | 0 | 0 | 152.2605 | 0 | 360.0956 | 28.25% | 0 | 0 | 0 | 0% | 30.9298
3057 | 227 | 435 | 291 | 8.4625 | 24.4 | 114.253 | 69.4784 | 0 | 43.6036 | 34.8639 | 0 | 0 | 34.8639 | 0 | 0 | 0 | 0 | 0 | 43.6036 | 0 | 401.4942 | 31.5% | 0 | 0 | 0 | 0% | 34.8639
3058 | 423 | 594 | 248 | 8.4625 | 25.1 | 212.9033 | 135.0881 | 0 | 105.3625 | 56.328 | 0 | 5.864 | 50.464 | 0 | 0 | 0 | 0 | 0 | 105.3625 | 0 | 501.5285 | 39.35% | 4.4977 | 0 | 4.5774 | 9.155% | 44.6
3059 | 939 | 927 | 101 | 11.2833 | 26.7 | 472.615 | 308.2964 | 0 | 265.6728 | 107 | 7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 265.6728 | 0 | 753.7663 | 59.14% | 19.175 | 0 | 24.092 | 48.18% | 43
3060 | 820 | 929 | 159 | 12.8952 | 28.2 | 412.7203 | 272.5892 | 0 | 231.2733 | 107.9 | 7.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 231.2733 | 0 | 973.3441 | 76.37% | 19.175 | 0 | 43.6067 | 87.21% | 42.1
3061 | 703 | 895 | 226 | 12.8952 | 29.1 | 353.8321 | 232.6495 | 0 | 194.2192 | 108.1 | 24.9097 | 8.1903 | 75 | 0 | 0 | 0 | 0 | 0 | 194.2192 | 0 | 1157.7418 | 90.84% | 6.282 | 0 | 50 | 100% | 41.9
3062 | 401 | 703 | 332 | 10.0743 | 29.3 | 201.8303 | 129.953 | 0 | 99.7175 | 80.1682 | 19.3341 | 0 | 60.8341 | 0 | 0 | 0 | 0 | 0 | 99.7175 | 0 | 1252.4165 | 98.27% | 0 | 0 | 50 | 100% | 41.5
3063 | 867 | 830 | 131 | 10.2758 | 30.1 | 436.3762 | 0 | 271.2083 | 0 | 103.5739 | 31.237 | 0 | 72.337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.4165 | 98.27% | 0 | 0 | 50 | 100% | 41.1
3064 | 789 | 657 | 129 | 13.7011 | 30.4 | 397.1174 | 0 | 232.403 | 0 | 69.1917 | 13.9459 | 0 | 55.2459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.4165 | 98.27% | 0 | 0 | 50 | 100% | 41.3
3065 | 723 | 453 | 94 | 16.5219 | 30.1 | 363.8985 | 0 | 189.1941 | 0 | 33.0298 | 0 | 0 | 33.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.4165 | 98.27% | 0 | 9.2702 | 40.567 | 81.13% | 42.3
3066 | 445 | 216 | 65 | 17.3279 | 28.6 | 223.9762 | 0 | 90.0165 | 0 | 8.494 | 0 | 0 | 8.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.4165 | 98.27% | 0 | 25 | 15.1275 | 30.25% | 33.494
3067 | 180 | 70 | 45 | 14.7085 | 26.8 | 90.5971 | 0 | 0 | 0 | 2.2581 | 0 | 0 | 2.2581 | 0 | 0 | 0 | 64.6729 | 24.0753 | 0 | 64.6729 | 1193.2553 | 93.62% | 0 | 14.8667 | 0 | 0% | 41.2
3068 | 0 | 0 | 0 | 8.6639 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5349 | 37.8 | 0 | 96.5349 | 1100.4407 | 86.34% | 0 | 0 | 0 | 0% | 37.8
3069 | 0 | 0 | 0 | 6.6491 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0875 | 35.7 | 0 | 91.0875 | 1013.622 | 79.53% | 0 | 0 | 0 | 0% | 35.7
3070 | 0 | 0 | 0 | 9.4699 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3434 | 33.8 | 0 | 86.3434 | 932.131 | 73.14% | 0 | 0 | 0 | 0% | 33.8
3071 | 0 | 0 | 0 | 10.0743 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3749 | 32.6 | 0 | 83.3749 | 853.98 | 67% | 0 | 0 | 0 | 0% | 32.6
3072 | 0 | 0 | 0 | 8.261 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0662 | 32.1 | 0 | 82.0662 | 777.2677 | 60.99% | 0 | 0 | 0 | 0% | 32.1
3073 | 0 | 0 | 0 | 10.2758 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7862 | 32 | 0 | 81.7862 | 700.8499 | 54.99% | 0 | 0 | 0 | 0% | 32
3074 | 0 | 0 | 0 | 6.6491 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9967 | 32.5 | 0 | 82.9967 | 623.0632 | 48.89% | 0 | 0 | 0 | 0% | 32.5
3075 | 0 | 0 | 0 | 6.0446 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9188 | 35.4 | 0 | 89.9188 | 537.0866 | 42.14% | 0 | 0 | 0 | 0% | 35.4
3076 | 0 | 0 | 0 | 4.2312 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2516 | 38.9 | 0 | 98.2516 | 441.1871 | 34.62% | 0 | 0 | 0 | 0% | 38.9
3077 | 0 | 0 | 0 | 6.2461 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2648 | 41.8 | 0 | 105.2648 | 337.0105 | 26.44% | 0 | 0 | 0 | 0% | 41.8
3078 | 9 | 26 | 25 | 3.6268 | 19.8 | 4.5299 | 0 | 0 | 0 | 0.95679 | 0 | 0 | 0.95679 | 0 | 0 | 0 | 106.5756 | 42.3432 | 0 | 106.5756 | 231.2595 | 18.14% | 0 | 0 | 0 | 0% | 43.3
3079 | 86 | 158 | 129 | 3.0223 | 20.5 | 43.2853 | 0 | 20.3987 | 0 | 9.0637 | 0 | 0 | 9.0637 | 0 | 0 | 0 | 84.3476 | 33.0816 | 0 | 84.3476 | 151.8434 | 11.91% | 0 | 0 | 0 | 0% | 42.1452
3080 | 401 | 405 | 215 | 2.4178 | 22.9 | 201.8303 | 112.9486 | 0 | 87.6058 | 28.3455 | 0 | 0 | 28.3455 | 0 | 0 | 0 | 0 | 0 | 87.6058 | 0 | 234.9101 | 18.43% | 0 | 0 | 0 | 0% | 28.3455
3081 | 657 | 601 | 176 | 4.0297 | 24.1 | 330.6795 | 201.1173 | 0 | 169.5738 | 53.7538 | 0 | 4.5769 | 49.1769 | 0 | 0 | 0 | 0 | 0 | 169.5738 | 0 | 395.698 | 31.05% | 3.5105 | 0 | 3.5732 | 7.146% | 44.6
3082 | 809 | 766 | 136 | 3.4253 | 25.2 | 407.1838 | 258.3386 | 0 | 223.1106 | 87.2608 | 0 | 21.4304 | 65.8304 | 0 | 0 | 0 | 0 | 0 | 223.1106 | 0 | 607.2488 | 47.65% | 16.4371 | 0 | 20.3038 | 40.61% | 44.4
3083 | 904 | 900 | 102 | 3.8283 | 26.7 | 454.9989 | 296.7868 | 0 | 259.1325 | 106.9 | 6.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 259.1325 | 0 | 852.9552 | 66.92% | 19.175 | 0 | 39.8213 | 79.64% | 43.1
3084 | 947 | 977 | 89 | 4.2312 | 28 | 476.6416 | 314.8064 | 0 | 275.7603 | 107.7 | 19.6621 | 13.0379 | 75 | 0 | 0 | 0 | 0 | 0 | 275.7603 | 0 | 1114.4277 | 87.44% | 10.0001 | 0 | 50 | 100% | 42.3
3085 | 777 | 937 | 201 | 7.455 | 28.4 | 391.0776 | 257.1302 | 0 | 220.0466 | 108.2 | 33.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 220.0466 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
3086 | 778 | 886 | 189 | 7.858 | 28.8 | 391.5809 | 0 | 252.1447 | 0 | 108.3 | 33.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
3087 | 868 | 831 | 134 | 11.2833 | 28.1 | 436.8795 | 0 | 271.5151 | 0 | 105.1202 | 31.9101 | 0 | 73.2101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.3
3088 | 839 | 662 | 102 | 10.4773 | 28.3 | 422.2833 | 0 | 247.2018 | 0 | 70.4384 | 14.6192 | 0 | 55.8192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
3089 | 775 | 460 | 74 | 7.6565 | 28.3 | 390.071 | 0 | 203.22 | 0 | 33.1313 | 0 | 0 | 33.1313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.9687 | 40.8725 | 81.75% | 42.1
3090 | 639 | 251 | 53 | 7.052 | 28.2 | 321.6198 | 0 | 129.8213 | 0 | 9.4684 | 0 | 0 | 9.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.4294 | 30.86% | 34.4684
3091 | 271 | 63 | 25 | 8.0595 | 26.5 | 136.399 | 0 | 0 | 0 | 1.0538 | 0 | 0 | 1.0538 | 0 | 0 | 0 | 65.9858 | 24.685 | 0 | 65.9858 | 1214.0755 | 95.26% | 0 | 15.1612 | 0 | 0% | 40.9
3092 | 0 | 0 | 0 | 3.8283 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2686 | 37.4 | 0 | 95.2686 | 1122.5768 | 88.08% | 0 | 0 | 0 | 0% | 37.4
3093 | 0 | 0 | 0 | 1.8134 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5084 | 35.6 | 0 | 90.5084 | 1036.1264 | 81.3% | 0 | 0 | 0 | 0% | 35.6
3094 | 0 | 0 | 0 | 1.8134 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4122 | 33.9 | 0 | 86.4122 | 954.5284 | 74.89% | 0 | 0 | 0 | 0% | 33.9
3095 | 0 | 0 | 0 | 2.0149 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9593 | 32.5 | 0 | 82.9593 | 876.8175 | 68.8% | 0 | 0 | 0 | 0% | 32.5
3096 | 0 | 0 | 0 | 1.2089 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4028 | 31.9 | 0 | 81.4028 | 800.8187 | 62.83% | 0 | 0 | 0 | 0% | 31.9
3097 | 0 | 0 | 0 | 1.0074 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5198 | 32 | 0 | 81.5198 | 724.6097 | 56.85% | 0 | 0 | 0 | 0% | 32
3098 | 0 | 0 | 0 | 1.4104 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3544 | 32.4 | 0 | 82.3544 | 647.2567 | 50.78% | 0 | 0 | 0 | 0% | 32.4
3099 | 0 | 0 | 0 | 3.6268 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1833 | 35.2 | 0 | 89.1833 | 561.8441 | 44.08% | 0 | 0 | 0 | 0% | 35.2
3100 | 0 | 0 | 0 | 4.8357 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3302 | 39 | 0 | 98.3302 | 465.6655 | 36.54% | 0 | 0 | 0 | 0% | 39
3101 | 0 | 0 | 0 | 3.4253 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.4476 | 42 | 0 | 105.4476 | 360.9306 | 28.32% | 0 | 0 | 0 | 0% | 42
3102 | 168 | 42 | 19 | 2.8208 | 17.3 | 84.5573 | 0 | 0 | 0 | 0.59587 | 0 | 0 | 0.59587 | 0 | 0 | 0 | 106.768 | 42.6041 | 0 | 106.768 | 254.4467 | 19.96% | 0 | 0 | 0 | 0% | 43.2
3103 | 647 | 223 | 47 | 1.8134 | 20.9 | 325.6463 | 153.7564 | 0 | 125.9779 | 6.255 | 0 | 0 | 6.255 | 0 | 0 | 0 | 94.6784 | 37.345 | 125.9779 | 94.6784 | 282.443 | 22.16% | 0 | 0 | 0 | 0% | 43.6
3104 | 804 | 429 | 58 | 1.0074 | 23.9 | 404.6672 | 226.62 | 0 | 194.4104 | 28.6362 | 0 | 0 | 28.6362 | 0 | 0 | 0 | 0 | 0 | 194.4104 | 0 | 467.0433 | 36.64% | 0 | 0 | 0 | 0% | 28.6362
3105 | 893 | 629 | 63 | 2.0149 | 25.7 | 449.4624 | 273.3991 | 0 | 237.6888 | 57.6645 | 0 | 6.6323 | 51.0323 | 0 | 0 | 0 | 0 | 0 | 237.6888 | 0 | 692.7382 | 54.35% | 5.0869 | 0 | 5.1785 | 10.36% | 44.4
3106 | 940 | 797 | 66 | 2.6193 | 27.2 | 473.1183 | 300.1472 | 0 | 262.6457 | 89.9717 | 0 | 22.7358 | 67.2358 | 0 | 0 | 0 | 0 | 0 | 262.6457 | 0 | 942.1306 | 73.92% | 17.4384 | 0 | 22.9309 | 45.86% | 44.5
3107 | 958 | 916 | 71 | 4.6342 | 28.4 | 482.1781 | 314.4974 | 0 | 275.3463 | 107 | 7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 275.3463 | 0 | 1203.5828 | 94.43% | 19.175 | 0 | 42.4512 | 84.9% | 43
3108 | 965 | 982 | 75 | 5.8431 | 29.1 | 485.7013 | 185.8355 | 134.9538 | 162.5593 | 108.1 | 23.4321 | 9.6679 | 75 | 0 | 0 | 0 | 0 | 0 | 162.5593 | 0 | 1274.5104 | 100% | 7.4153 | 0 | 50 | 100% | 41.9
3109 | 947 | 980 | 84 | 7.455 | 29.8 | 476.6416 | 0 | 313.3765 | 0 | 108.4 | 33.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
3110 | 930 | 924 | 87 | 8.8654 | 29.7 | 468.0852 | 0 | 301.4247 | 0 | 108.7 | 33.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.3
3111 | 894 | 812 | 92 | 8.8654 | 29.9 | 449.9657 | 0 | 279.6398 | 0 | 99.9047 | 29.7023 | 0 | 70.2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.5
3112 | 845 | 652 | 86 | 7.858 | 29.9 | 425.3032 | 0 | 249.0364 | 0 | 67.4934 | 13.5467 | 0 | 53.9467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.4
3113 | 652 | 429 | 96 | 9.8729 | 28.8 | 328.1629 | 0 | 171.3056 | 0 | 30.5035 | 0 | 0 | 30.5035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.8965 | 39.9269 | 79.85% | 40.4
3114 | 455 | 238 | 90 | 7.858 | 27.7 | 229.0094 | 0 | 92.8259 | 0 | 10.2525 | 0 | 0 | 10.2525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 14.48 | 28.96% | 35.2525
3115 | 225 | 68 | 37 | 6.2461 | 26.1 | 113.2464 | 0 | 0 | 0 | 1.7775 | 0 | 0 | 1.7775 | 0 | 0 | 0 | 63.6581 | 23.6962 | 0 | 63.6581 | 1216.3245 | 95.43% | 0 | 14.2263 | 0 | 0% | 39.7
3116 | 0 | 1 | 1 | 3.6268 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5006 | 37.1 | 0 | 94.5006 | 1125.6704 | 88.32% | 0 | 0 | 0 | 0% | 37.1
3117 | 0 | 0 | 0 | 1.0074 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5893 | 35.6 | 0 | 90.5893 | 1039.2163 | 81.54% | 0 | 0 | 0 | 0% | 35.6
3118 | 0 | 0 | 0 | 2.0149 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9414 | 33.7 | 0 | 85.9414 | 958.1544 | 75.18% | 0 | 0 | 0 | 0% | 33.7
3119 | 0 | 0 | 0 | 3.4253 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7059 | 32 | 0 | 81.7059 | 881.836 | 69.19% | 0 | 0 | 0 | 0% | 32
3120 | 0 | 0 | 0 | 2.6193 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2447 | 31 | 0 | 79.2447 | 808.2326 | 63.42% | 0 | 0 | 0 | 0% | 31
3121 | 0 | 0 | 0 | 0.60446 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2184 | 30.6 | 0 | 78.2184 | 735.7387 | 57.73% | 0 | 0 | 0 | 0% | 30.6
3122 | 0 | 0 | 0 | 4.2312 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5662 | 30.3 | 0 | 77.5662 | 663.9618 | 52.1% | 0 | 0 | 0 | 0% | 30.3
3123 | 0 | 0 | 0 | 4.4327 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5194 | 30.7 | 0 | 78.5194 | 591.124 | 46.38% | 0 | 0 | 0 | 0% | 30.7
3124 | 0 | 0 | 0 | 3.2238 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5199 | 31.2 | 0 | 79.5199 | 517.1233 | 40.57% | 0 | 0 | 0 | 0% | 31.2
3125 | 0 | 0 | 0 | 4.0297 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8752 | 33.8 | 0 | 85.8752 | 435.7188 | 34.19% | 0 | 0 | 0 | 0% | 33.8
3126 | 166 | 42 | 19 | 3.8283 | 18.7 | 83.5507 | 0 | 0 | 0 | 0.58592 | 0 | 0 | 0.58592 | 0 | 0 | 0 | 91.8818 | 36.3141 | 0 | 91.8818 | 347.1341 | 27.24% | 0 | 0 | 0 | 0% | 36.9
3127 | 644 | 224 | 46 | 1.0074 | 23.3 | 324.1364 | 153.3329 | 0 | 125.868 | 6.0831 | 0 | 0 | 6.0831 | 0 | 0 | 0 | 83.6337 | 32.6169 | 125.868 | 83.6337 | 386.4549 | 30.32% | 0 | 0 | 0 | 0% | 38.7
3128 | 807 | 435 | 60 | 1.2089 | 25.2 | 406.1771 | 227.6253 | 0 | 195.2907 | 28.7435 | 0 | 0 | 28.7435 | 0 | 0 | 0 | 0 | 0 | 195.2907 | 0 | 569.265 | 44.67% | 0 | 0 | 0 | 0% | 28.7435
3129 | 887 | 634 | 68 | 2.2164 | 27.2 | 446.4425 | 271.6014 | 0 | 235.9403 | 62.4557 | 0 | 11.5779 | 50.8779 | 0 | 0 | 0 | 0 | 0 | 235.9403 | 0 | 790.127 | 61.99% | 8.8802 | 0 | 9.0414 | 18.08% | 39.3
3130 | 929 | 800 | 74 | 4.4327 | 28.7 | 467.5819 | 296.6129 | 0 | 258.7985 | 95.9572 | 3.2786 | 25 | 67.6786 | 0 | 0 | 0 | 0 | 0 | 258.7985 | 0 | 1032.3864 | 81% | 19.175 | 0 | 28.5644 | 57.13% | 39.4
3131 | 952 | 922 | 78 | 5.0372 | 29.6 | 479.1582 | 312.5113 | 0 | 273.372 | 111.6 | 11.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 273.372 | 0 | 1274.5104 | 100% | 19.175 | 0 | 48.0875 | 96.18% | 38.4
3132 | 944 | 987 | 97 | 7.455 | 30.5 | 475.1316 | 0 | 313.8078 | 0 | 113.4 | 38.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.0875 | 96.18% | 36.6
3133 | 752 | 892 | 175 | 5.2387 | 30.6 | 378.4947 | 0 | 248.8387 | 0 | 114.6 | 39.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.0875 | 96.18% | 35.4
3134 | 874 | 912 | 125 | 8.4625 | 30.3 | 439.8994 | 0 | 283.2892 | 0 | 115.2 | 40.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.0875 | 96.18% | 34.8
3135 | 891 | 813 | 93 | 8.8654 | 30.2 | 448.4558 | 0 | 278.6913 | 0 | 105.1962 | 35.2981 | 0 | 69.8981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.0875 | 96.18% | 34.6
3136 | 848 | 657 | 87 | 8.6639 | 29.7 | 426.8131 | 0 | 249.9829 | 0 | 73.6989 | 19.4495 | 0 | 54.2495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.0875 | 96.18% | 34.8
3137 | 776 | 464 | 74 | 10.8803 | 28.9 | 390.5743 | 0 | 204.2713 | 0 | 33.0949 | 0 | 0 | 33.0949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.0875 | 96.18% | 33.0949
3138 | 645 | 258 | 55 | 13.4996 | 25.9 | 324.6397 | 0 | 132.1174 | 0 | 9.7347 | 0 | 0 | 9.7347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 22.6375 | 45.28% | 34.7347
3139 | 307 | 71 | 26 | 13.0966 | 22.2 | 154.5184 | 0 | 0 | 0 | 1.1508 | 0 | 0 | 1.1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.2372 | 0 | 0% | 23.388
3140 | 0 | 1 | 1 | 11.4848 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4213 | 34.4 | 0 | 87.4213 | 1191.4528 | 93.48% | 0 | 0 | 0 | 0% | 34.4
3141 | 0 | 0 | 0 | 9.2684 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4531 | 32.4 | 0 | 82.4531 | 1114.1233 | 87.42% | 0 | 0 | 0 | 0% | 32.4
3142 | 0 | 0 | 0 | 8.6639 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6985 | 30.5 | 0 | 77.6985 | 1042.1138 | 81.77% | 0 | 0 | 0 | 0% | 30.5
3143 | 0 | 0 | 0 | 6.4476 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0428 | 28.9 | 0 | 74.0428 | 973.826 | 76.41% | 0 | 0 | 0 | 0% | 28.9
3144 | 0 | 0 | 0 | 6.8506 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.243 | 28.1 | 0 | 72.243 | 907.2635 | 71.19% | 0 | 0 | 0 | 0% | 28.1
3145 | 0 | 0 | 0 | 5.4401 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.1585 | 27.6 | 0 | 71.1585 | 841.7369 | 66.04% | 0 | 0 | 0 | 0% | 27.6
3146 | 0 | 0 | 0 | 7.858 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.079 | 27.5 | 0 | 71.079 | 776.2833 | 60.91% | 0 | 0 | 0 | 0% | 27.5
3147 | 0 | 0 | 0 | 9.0669 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.1764 | 27.5 | 0 | 71.1764 | 710.7303 | 55.76% | 0 | 0 | 0 | 0% | 27.5
3148 | 0 | 0 | 0 | 9.4699 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.9125 | 27.4 | 0 | 70.9125 | 645.4191 | 50.64% | 0 | 0 | 0 | 0% | 27.4
3149 | 0 | 0 | 0 | 7.6565 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1621 | 28.9 | 0 | 74.1621 | 576.9607 | 45.27% | 0 | 0 | 0 | 0% | 28.9
3150 | 158 | 40 | 19 | 5.6416 | 16.2 | 79.5241 | 0 | 27.3874 | 0 | 0.62424 | 0 | 0 | 0.62424 | 0 | 0 | 0 | 78.4409 | 30.8758 | 0 | 78.4409 | 503.8188 | 39.53% | 0 | 0 | 0 | 0% | 31.5
3151 | 587 | 218 | 52 | 8.261 | 17.3 | 295.4473 | 140.0242 | 0 | 109.9868 | 6.2506 | 0 | 0 | 6.2506 | 0 | 0 | 0 | 70.136 | 27.1494 | 109.9868 | 70.136 | 540.9209 | 42.44% | 0 | 0 | 0 | 0% | 33.4
3152 | 766 | 432 | 72 | 10.4773 | 19.1 | 385.5411 | 216.2119 | 0 | 179.9362 | 29.6622 | 0 | 0 | 29.6622 | 0 | 0 | 0 | 0 | 0 | 179.9362 | 0 | 707.2092 | 55.49% | 0 | 0 | 0 | 0% | 29.6622
3153 | 847 | 629 | 84 | 12.2907 | 20.4 | 426.3098 | 259.3917 | 0 | 219.0366 | 71.3781 | 0 | 18.339 | 53.039 | 0 | 0 | 0 | 0 | 0 | 219.0366 | 0 | 909.6322 | 71.37% | 14.0661 | 0 | 14.3233 | 28.65% | 34.7
3154 | 892 | 793 | 92 | 12.4922 | 21.5 | 448.9591 | 284.7796 | 0 | 242.8211 | 105.5398 | 10.2699 | 25 | 70.2699 | 0 | 0 | 0 | 0 | 0 | 242.8211 | 0 | 1134.0357 | 88.98% | 19.175 | 0 | 33.8491 | 67.7% | 35
3155 | 920 | 914 | 94 | 12.4922 | 22.7 | 463.052 | 268.3686 | 33.6232 | 230.1459 | 115.2 | 19.5211 | 20.6789 | 75 | 0 | 0 | 0 | 0 | 0 | 230.1459 | 0 | 1274.5104 | 100% | 15.8607 | 0 | 50 | 100% | 34.8
3156 | 929 | 978 | 98 | 11.8877 | 23.6 | 467.5819 | 0 | 308.8209 | 0 | 116.5 | 41.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.5
3157 | 927 | 982 | 99 | 10.6788 | 24.6 | 466.5752 | 0 | 306.7344 | 0 | 117.5 | 42.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.5
3158 | 914 | 926 | 98 | 10.2758 | 25.4 | 460.0321 | 0 | 296.2681 | 0 | 117.8 | 42.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.2
3159 | 889 | 816 | 95 | 11.0818 | 25.4 | 447.4492 | 0 | 278.0536 | 0 | 110.6259 | 39.2129 | 0 | 71.4129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.2
3160 | 853 | 662 | 86 | 11.0818 | 25.1 | 429.3297 | 0 | 251.5147 | 0 | 78.1101 | 22.605 | 0 | 55.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.9
3161 | 779 | 469 | 74 | 10.8803 | 24.2 | 392.0842 | 0 | 205.22 | 0 | 33.6796 | 0 | 0 | 33.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.6796
3162 | 635 | 261 | 58 | 10.6788 | 22.5 | 319.6065 | 0 | 130.5713 | 0 | 9.975 | 0 | 0 | 9.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.5465 | 49.09% | 34.975
3163 | 291 | 72 | 29 | 9.2684 | 20.2 | 146.4654 | 0 | 0 | 0 | 1.3739 | 0 | 0 | 1.3739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.1091 | 0 | 0% | 25.4831
3164 | 0 | 1 | 1 | 7.858 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3993 | 34.5 | 0 | 87.3993 | 1191.1219 | 93.46% | 0 | 0 | 0 | 0% | 34.5
3165 | 0 | 0 | 0 | 3.8283 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6623 | 32.2 | 0 | 81.6623 | 1114.3221 | 87.43% | 0 | 0 | 0 | 0% | 32.2
3166 | 0 | 0 | 0 | 4.0297 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.28 | 30.4 | 0 | 77.28 | 1042.5558 | 81.8% | 0 | 0 | 0 | 0% | 30.4
3167 | 0 | 0 | 0 | 3.2238 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.7219 | 29.3 | 0 | 74.7219 | 973.5706 | 76.39% | 0 | 0 | 0 | 0% | 29.3
3168 | 0 | 0 | 0 | 3.0223 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.966 | 29 | 0 | 73.966 | 905.3027 | 71.03% | 0 | 0 | 0 | 0% | 29
3169 | 0 | 0 | 0 | 2.0149 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1557 | 29.1 | 0 | 74.1557 | 836.8215 | 65.66% | 0 | 0 | 0 | 0% | 29.1
3170 | 0 | 0 | 0 | 2.0149 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.5721 | 29.8 | 0 | 75.5721 | 766.6143 | 60.15% | 0 | 0 | 0 | 0% | 29.8
3171 | 0 | 0 | 0 | 5.0372 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7133 | 33.2 | 0 | 83.7133 | 686.9007 | 53.9% | 0 | 0 | 0 | 0% | 33.2
3172 | 0 | 0 | 0 | 4.6342 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5703 | 36.9 | 0 | 92.5703 | 596.63 | 46.81% | 0 | 0 | 0 | 0% | 36.9
3173 | 0 | 0 | 0 | 3.6268 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.625 | 39.9 | 0 | 99.625 | 497.7522 | 39.05% | 0 | 0 | 0 | 0% | 39.9
3174 | 204 | 48 | 21 | 6.0446 | 14.2 | 102.6767 | 0 | 35.5135 | 0 | 0.7523 | 0 | 0 | 0.7523 | 0 | 0 | 0 | 101.3244 | 40.5477 | 0 | 101.3244 | 397.0224 | 31.15% | 0 | 0 | 0 | 0% | 41.3
3175 | 649 | 231 | 50 | 7.052 | 16.8 | 326.653 | 155.1029 | 0 | 124.8205 | 6.6095 | 0 | 0 | 6.6095 | 0 | 0 | 0 | 88.8458 | 35.1905 | 124.8205 | 88.8458 | 428.6895 | 33.64% | 0 | 0 | 0 | 0% | 41.8
3176 | 818 | 446 | 64 | 8.8654 | 17.9 | 411.7136 | 231.0505 | 0 | 194.8025 | 30.706 | 0 | 0 | 30.706 | 0 | 0 | 0 | 0 | 0 | 194.8025 | 0 | 611.7749 | 48% | 0 | 0 | 0 | 0% | 30.706
3177 | 896 | 646 | 72 | 8.4625 | 19.2 | 450.9724 | 274.4392 | 0 | 235.4509 | 65.6405 | 0 | 11.2703 | 54.3703 | 0 | 0 | 0 | 0 | 0 | 235.4509 | 0 | 833.0639 | 65.36% | 8.6443 | 0 | 8.8037 | 17.61% | 43.1
3178 | 945 | 815 | 75 | 7.858 | 20.5 | 475.6349 | 301.6807 | 0 | 261.4523 | 99.8954 | 3.1977 | 25 | 71.6977 | 0 | 0 | 0 | 0 | 0 | 261.4523 | 0 | 1078.7903 | 84.64% | 19.175 | 0 | 28.3323 | 56.66% | 43.5
3179 | 962 | 934 | 81 | 7.455 | 21.6 | 484.1913 | 281.8272 | 33.9229 | 245.2765 | 107.5 | 7.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 245.2765 | 0 | 1274.5104 | 100% | 19.175 | 0 | 47.8609 | 95.72% | 42.5
3180 | 968 | 998 | 84 | 5.4401 | 23.5 | 487.2112 | 0 | 321.785 | 0 | 108.4 | 30.6615 | 2.7385 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 2.1004 | 0 | 50 | 100% | 41.6
3181 | 960 | 1000 | 89 | 9.0669 | 24 | 483.1847 | 0 | 317.6405 | 0 | 108.7 | 33.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.3
3182 | 937 | 940 | 94 | 10.4773 | 24.1 | 471.6084 | 0 | 303.7355 | 0 | 108.6 | 33.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.4
3183 | 907 | 828 | 94 | 12.4922 | 23.6 | 456.5089 | 0 | 283.6691 | 0 | 105.3359 | 32.218 | 0 | 73.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.9
3184 | 854 | 668 | 92 | 15.1115 | 22.3 | 429.833 | 0 | 251.8629 | 0 | 73.0447 | 16.2224 | 0 | 56.8224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.6
3185 | 760 | 471 | 86 | 14.7085 | 21.2 | 382.5212 | 0 | 200.3622 | 0 | 34.425 | 0 | 0 | 34.425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.675 | 43.2029 | 86.41% | 41.1
3186 | 592 | 259 | 69 | 13.9026 | 19.9 | 297.9639 | 0 | 122.1802 | 0 | 10.317 | 0 | 0 | 10.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.7454 | 35.49% | 35.317
3187 | 239 | 70 | 33 | 10.8803 | 18.2 | 120.2929 | 0 | 0 | 0 | 1.61 | 0 | 0 | 1.61 | 0 | 0 | 0 | 56.7443 | 21.2632 | 0 | 56.7443 | 1222.8692 | 95.95% | 0 | 17.4268 | 0 | 0% | 40.3
3188 | 0 | 1 | 1 | 7.455 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1034 | 37 | 0 | 93.1034 | 1132.4329 | 88.85% | 0 | 0 | 0 | 0% | 37
3189 | 0 | 0 | 0 | 8.0595 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6231 | 35.2 | 0 | 88.6231 | 1047.0322 | 82.15% | 0 | 0 | 0 | 0% | 35.2
3190 | 0 | 0 | 0 | 8.6639 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7133 | 33.2 | 0 | 83.7133 | 967.3863 | 75.9% | 0 | 0 | 0 | 0% | 33.2
3191 | 0 | 0 | 0 | 7.455 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0407 | 32.1 | 0 | 81.0407 | 890.8602 | 69.9% | 0 | 0 | 0 | 0% | 32.1
3192 | 0 | 0 | 0 | 7.858 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8021 | 31.6 | 0 | 79.8021 | 815.7333 | 64% | 0 | 0 | 0 | 0% | 31.6
3193 | 0 | 0 | 0 | 7.858 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7863 | 31.6 | 0 | 79.7863 | 740.5952 | 58.11% | 0 | 0 | 0 | 0% | 31.6
3194 | 0 | 0 | 0 | 3.4253 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9766 | 32.1 | 0 | 80.9766 | 664.0349 | 52.1% | 0 | 0 | 0 | 0% | 32.1
3195 | 0 | 0 | 0 | 4.0297 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1593 | 34.7 | 0 | 87.1593 | 579.9911 | 45.51% | 0 | 0 | 0 | 0% | 34.7
3196 | 0 | 0 | 0 | 4.4327 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5518 | 38.2 | 0 | 95.5518 | 486.0329 | 38.13% | 0 | 0 | 0 | 0% | 38.2
3197 | 0 | 0 | 0 | 4.0297 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4514 | 41.1 | 0 | 102.4514 | 383.7703 | 30.11% | 0 | 0 | 0 | 0% | 41.1
3198 | 242 | 50 | 20 | 3.8283 | 11.5 | 121.8028 | 0 | 42.3084 | 0 | 0.72458 | 0 | 0 | 0.72458 | 0 | 0 | 0 | 104.1004 | 41.7754 | 0 | 104.1004 | 279.5667 | 21.94% | 0 | 0 | 0 | 0% | 42.5
3199 | 682 | 239 | 47 | 4.4327 | 14.1 | 343.2625 | 163.2919 | 0 | 133.8658 | 6.5682 | 0 | 0 | 6.5682 | 0 | 0 | 0 | 91.2062 | 36.3318 | 133.8658 | 91.2062 | 317.4721 | 24.91% | 0 | 0 | 0 | 0% | 42.9
3200 | 840 | 454 | 60 | 6.6491 | 16.2 | 422.7866 | 237.4296 | 0 | 202.0662 | 31.0593 | 0 | 0 | 31.0593 | 0 | 0 | 0 | 0 | 0 | 202.0662 | 0 | 508.7579 | 39.92% | 0 | 0 | 0 | 0% | 31.0593
3201 | 922 | 656 | 66 | 8.8654 | 18.1 | 464.0586 | 282.4464 | 0 | 242.7374 | 66.8823 | 0 | 11.4911 | 55.3911 | 0 | 0 | 0 | 0 | 0 | 242.7374 | 0 | 738.5451 | 57.95% | 8.8137 | 0 | 8.9775 | 17.95% | 43.9
3202 | 966 | 825 | 68 | 9.0669 | 19.8 | 486.2046 | 308.3662 | 0 | 266.9012 | 101.4909 | 3.6454 | 25 | 72.8454 | 0 | 0 | 0 | 0 | 0 | 266.9012 | 0 | 991.2069 | 77.77% | 19.175 | 0 | 28.5089 | 57.02% | 44.2
3203 | 985 | 945 | 71 | 8.6639 | 21.1 | 495.7676 | 323.2715 | 0 | 281.0746 | 106.9 | 6.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 281.0746 | 0 | 1257.286 | 98.65% | 19.175 | 0 | 48.0403 | 96.08% | 43.1
3204 | 991 | 1010 | 74 | 5.8431 | 22.1 | 498.7875 | 0 | 329.4304 | 0 | 107.5 | 29.9916 | 2.5084 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.286 | 98.65% | 1.9239 | 0 | 50 | 100% | 42.5
3205 | 986 | 1012 | 76 | 5.4401 | 23.2 | 496.2709 | 0 | 326.2291 | 0 | 107.6 | 32.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.286 | 98.65% | 0 | 0 | 50 | 100% | 42.4
3206 | 975 | 956 | 75 | 7.455 | 24.3 | 490.7345 | 0 | 316.0351 | 0 | 107.6 | 32.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.286 | 98.65% | 0 | 0 | 50 | 100% | 42.4
3207 | 952 | 844 | 73 | 9.0669 | 24.8 | 479.1582 | 0 | 297.7261 | 0 | 104.9996 | 31.5498 | 0 | 73.4498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.286 | 98.65% | 0 | 0 | 50 | 100% | 41.9
3208 | 916 | 686 | 68 | 8.4625 | 24.5 | 461.0387 | 0 | 270.2002 | 0 | 72.577 | 15.4885 | 0 | 57.0885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.286 | 98.65% | 0 | 0 | 50 | 100% | 41.6
3209 | 853 | 492 | 59 | 6.0446 | 24.4 | 429.3297 | 0 | 225.0373 | 0 | 34.6498 | 0 | 0 | 34.6498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.286 | 98.65% | 0 | 7.2502 | 42.6161 | 85.23% | 41.9
3210 | 703 | 274 | 49 | 4.6342 | 24.2 | 353.8321 | 0 | 145.6035 | 0 | 9.703 | 0 | 0 | 9.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.286 | 98.65% | 0 | 25 | 17.1549 | 34.31% | 34.703
3211 | 360 | 79 | 26 | 7.2535 | 21.9 | 181.1943 | 0 | 0 | 0 | 1.1493 | 0 | 0 | 1.1493 | 0 | 0 | 0 | 61.568 | 23.1061 | 0 | 61.568 | 1201.0592 | 94.24% | 0 | 16.8445 | 2.7756e-15 | 5.551e-15% | 41.1
3212 | 0 | 1 | 1 | 4.8357 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3199 | 37.7 | 0 | 95.3199 | 1108.6712 | 86.99% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.7
3213 | 0 | 0 | 0 | 4.4327 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.263 | 35.7 | 0 | 90.263 | 1021.9055 | 80.18% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.7
3214 | 0 | 0 | 0 | 1.8134 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4616 | 33.8 | 0 | 85.4616 | 940.5623 | 73.8% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.8
3215 | 0 | 0 | 0 | 2.2164 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7011 | 32.7 | 0 | 82.7011 | 862.3594 | 67.66% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.7
3216 | 0 | 0 | 0 | 0.80595 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0568 | 32.1 | 0 | 81.0568 | 785.8475 | 61.66% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.1
3217 | 0 | 0 | 0 | 1.2089 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5294 | 31.9 | 0 | 80.5294 | 709.8888 | 55.7% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.9
3218 | 0 | 0 | 0 | 1.0074 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4472 | 32.3 | 0 | 81.4472 | 632.7867 | 49.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.3
3219 | 0 | 0 | 0 | 1.4104 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8705 | 34.6 | 0 | 86.8705 | 549.0613 | 43.08% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.6
3220 | 0 | 0 | 0 | 1.6119 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0561 | 37.6 | 0 | 94.0561 | 456.8426 | 35.84% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.6
3221 | 0 | 0 | 0 | 1.2089 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0761 | 40.1 | 0 | 100.0761 | 357.4298 | 28.04% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 40.1
3222 | 241 | 51 | 21 | 1.0074 | 12.9 | 121.2995 | 0 | 42.3112 | 0 | 0.7754 | 0 | 0 | 0.7754 | 0 | 0 | 0 | 101.8566 | 40.8246 | 0 | 101.8566 | 255.95 | 20.08% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.6
3223 | 659 | 235 | 49 | 2.4178 | 16.1 | 331.6862 | 158.0757 | 0 | 129.7446 | 6.5352 | 0 | 0 | 6.5352 | 0 | 0 | 0 | 90.3505 | 35.8648 | 129.7446 | 90.3505 | 291.3893 | 22.86% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42.4
3224 | 816 | 447 | 63 | 2.8208 | 19.1 | 410.707 | 230.8058 | 0 | 197.7063 | 29.9136 | 0 | 0 | 29.9136 | 0 | 0 | 0 | 0 | 0 | 197.7063 | 0 | 478.6471 | 37.56% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 29.9136
3225 | 892 | 646 | 72 | 3.4253 | 22.2 | 448.9591 | 273.2992 | 0 | 237.0926 | 60.8573 | 0 | 8.3786 | 52.4786 | 0 | 0 | 0 | 0 | 0 | 237.0926 | 0 | 703.2097 | 55.17% | 6.4264 | 0 | 6.5468 | 13.09% | 44.1
3226 | 914 | 807 | 88 | 6.2461 | 24.1 | 460.0321 | 291.7506 | 0 | 253.2793 | 94.3354 | 0.11769 | 25 | 69.2177 | 0 | 0 | 0 | 0 | 0 | 253.2793 | 0 | 943.1035 | 74% | 19.175 | 0 | 26.081 | 52.16% | 44.1
3227 | 887 | 921 | 130 | 8.0595 | 26.3 | 446.4425 | 291.0849 | 0 | 251.6044 | 106.9 | 6.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 251.6044 | 0 | 1181.411 | 92.7% | 19.175 | 0 | 45.6152 | 91.23% | 43.1
3228 | 897 | 978 | 126 | 8.0595 | 28.8 | 451.4757 | 200.2956 | 97.887 | 173.4819 | 107.6 | 26.9883 | 5.6117 | 75 | 0 | 0 | 0 | 0 | 0 | 173.4819 | 0 | 1274.5104 | 100% | 4.3042 | 0 | 50 | 100% | 42.4
3229 | 951 | 999 | 92 | 11.6862 | 31.3 | 478.6548 | 0 | 314.6347 | 0 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
3230 | 948 | 947 | 86 | 13.4996 | 32.4 | 477.1449 | 0 | 307.2556 | 0 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
3231 | 936 | 842 | 79 | 15.1115 | 32.5 | 471.1051 | 0 | 292.7036 | 0 | 102.0716 | 30.2858 | 0 | 71.7858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.5
3232 | 905 | 685 | 70 | 14.1041 | 32.4 | 455.5022 | 0 | 267.002 | 0 | 70.0369 | 14.4184 | 0 | 55.6184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
3233 | 809 | 481 | 68 | 11.0818 | 32 | 407.1838 | 0 | 213.5702 | 0 | 33.1907 | 0 | 0 | 33.1907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.7093 | 41.1289 | 82.26% | 41.9
3234 | 640 | 281 | 70 | 9.2684 | 28.6 | 322.1231 | 0 | 133.0047 | 0 | 10.4158 | 0 | 0 | 10.4158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.6639 | 31.33% | 35.4158
3235 | 328 | 97 | 48 | 6.0446 | 24.9 | 165.0881 | 0 | 0 | 0 | 2.5055 | 0 | 0 | 2.5055 | 0 | 0 | 0 | 61.8607 | 23.0161 | 0 | 61.8607 | 1218.0413 | 95.57% | 0 | 15.3784 | 0 | 0% | 40.9
3236 | 0 | 1 | 1 | 4.2312 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9838 | 37.4 | 0 | 94.9838 | 1126.5289 | 88.39% | 0 | 0 | 0 | 0% | 37.4
3237 | 0 | 0 | 0 | 2.8208 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8226 | 35.7 | 0 | 90.8226 | 1039.7865 | 81.58% | 0 | 0 | 0 | 0% | 35.7
3238 | 0 | 0 | 0 | 11.6862 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5853 | 34 | 0 | 86.5853 | 957.8881 | 75.16% | 0 | 0 | 0 | 0% | 34
3239 | 0 | 0 | 0 | 13.7011 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7373 | 32.6 | 0 | 82.7373 | 879.9906 | 69.05% | 0 | 0 | 0 | 0% | 32.6
3240 | 0 | 0 | 0 | 12.4922 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8428 | 32.3 | 0 | 81.8428 | 802.9334 | 63% | 0 | 0 | 0 | 0% | 32.3
3241 | 0 | 0 | 0 | 10.4773 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5669 | 32.2 | 0 | 81.5669 | 726.1479 | 56.97% | 0 | 0 | 0 | 0% | 32.2
3242 | 0 | 0 | 0 | 8.261 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6772 | 32.7 | 0 | 82.6772 | 647.9308 | 50.84% | 0 | 0 | 0 | 0% | 32.7
3243 | 0 | 0 | 0 | 7.455 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2937 | 35.5 | 0 | 89.2937 | 561.669 | 44.07% | 0 | 0 | 0 | 0% | 35.5
3244 | 0 | 0 | 0 | 6.4476 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9181 | 38.7 | 0 | 96.9181 | 466.3371 | 36.59% | 0 | 0 | 0 | 0% | 38.7
3245 | 0 | 0 | 0 | 6.8506 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3642 | 41.4 | 0 | 103.3642 | 363.2881 | 28.5% | 0 | 0 | 0 | 0% | 41.4
3246 | 154 | 47 | 26 | 7.858 | 14.2 | 77.5109 | 0 | 27.1497 | 0 | 1.0623 | 0 | 0 | 1.0623 | 0 | 0 | 0 | 104.437 | 41.8377 | 0 | 104.437 | 258.9704 | 20.32% | 0 | 0 | 0 | 0% | 42.9
3247 | 540 | 224 | 68 | 8.6639 | 16 | 271.7914 | 129.7679 | 0 | 100.0635 | 7.2343 | 0 | 0 | 7.2343 | 0 | 0 | 0 | 91.2992 | 36.2657 | 100.0635 | 91.2992 | 265.3906 | 20.82% | 0 | 0 | 0 | 0% | 43.5
3248 | 739 | 435 | 84 | 10.2758 | 18.1 | 371.9515 | 209.1609 | 0 | 173.4893 | 29.7136 | 0 | 0 | 29.7136 | 0 | 0 | 0 | 0 | 0 | 173.4893 | 0 | 430.02 | 33.74% | 0 | 0 | 0 | 0% | 29.7136
3249 | 848 | 636 | 88 | 10.2758 | 19.8 | 426.8131 | 259.86 | 0 | 220.6897 | 61.4881 | 0 | 8.4441 | 53.0441 | 0 | 0 | 0 | 0 | 0 | 220.6897 | 0 | 639.4394 | 50.17% | 6.4766 | 0 | 6.5989 | 13.2% | 44.6
3250 | 900 | 803 | 91 | 8.8654 | 21.7 | 452.9856 | 287.2673 | 0 | 247.3905 | 94.6546 | 0 | 24.9773 | 69.6773 | 0 | 0 | 0 | 0 | 0 | 247.3905 | 0 | 874.1959 | 68.59% | 19.1576 | 0 | 26.1181 | 52.24% | 44.7
3251 | 923 | 921 | 96 | 5.0372 | 23.7 | 464.5619 | 302.8757 | 0 | 264.3283 | 106.7 | 6.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 264.3283 | 0 | 1125.0253 | 88.27% | 19.175 | 0 | 45.6551 | 91.31% | 43.3
3252 | 926 | 983 | 101 | 3.0223 | 26.1 | 466.0719 | 228.7022 | 79.1208 | 200.3294 | 107.3 | 26.7402 | 5.5598 | 75 | 0 | 0 | 0 | 0 | 0 | 200.3294 | 0 | 1274.5104 | 100% | 4.2643 | 0 | 50 | 100% | 42.7
3253 | 925 | 987 | 103 | 9.2684 | 26.6 | 465.5686 | 0 | 306.0182 | 0 | 107.6 | 32.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
3254 | 907 | 932 | 106 | 10.8803 | 26.3 | 456.5089 | 0 | 293.9397 | 0 | 107.7 | 32.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
3255 | 871 | 820 | 108 | 12.2907 | 25.2 | 438.3894 | 0 | 272.353 | 0 | 100.2705 | 29.2352 | 0 | 71.0352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
3256 | 830 | 663 | 98 | 12.6937 | 23.7 | 417.7534 | 0 | 244.9131 | 0 | 68.8798 | 13.5899 | 0 | 55.2899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
3257 | 722 | 470 | 96 | 12.2907 | 22 | 363.3952 | 0 | 190.7215 | 0 | 33.4169 | 0 | 0 | 33.4169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.7831 | 41.0524 | 82.1% | 42.2
3258 | 527 | 264 | 92 | 12.0892 | 20.5 | 265.2483 | 0 | 109.8758 | 0 | 11.4357 | 0 | 0 | 11.4357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.5838 | 31.17% | 36.4357
3259 | 178 | 62 | 35 | 9.8729 | 18.5 | 89.5905 | 0 | 0 | 0 | 1.7425 | 0 | 0 | 1.7425 | 0 | 0 | 0 | 62.3658 | 23.66 | 0 | 62.3658 | 1217.506 | 95.53% | 0 | 15.2975 | 0 | 0% | 40.7
3260 | 0 | 1 | 1 | 6.0446 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4688 | 37.5 | 0 | 94.4688 | 1125.7133 | 88.33% | 0 | 0 | 0 | 0% | 37.5
3261 | 0 | 0 | 0 | 5.0372 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4891 | 35.9 | 0 | 90.4891 | 1038.4146 | 81.48% | 0 | 0 | 0 | 0% | 35.9
3262 | 0 | 0 | 0 | 3.4253 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5587 | 34.3 | 0 | 86.5587 | 955.6504 | 74.98% | 0 | 0 | 0 | 0% | 34.3
3263 | 0 | 0 | 0 | 1.4104 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5902 | 33.1 | 0 | 83.5902 | 876.3297 | 68.76% | 0 | 0 | 0 | 0% | 33.1
3264 | 0 | 0 | 0 | 4.8357 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4638 | 32.5 | 0 | 82.4638 | 798.7074 | 62.67% | 0 | 0 | 0 | 0% | 32.5
3265 | 0 | 0 | 0 | 8.6639 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.334 | 32.2 | 0 | 82.334 | 721.6848 | 56.62% | 0 | 0 | 0 | 0% | 32.2
3266 | 0 | 0 | 0 | 18.1338 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9571 | 32.8 | 0 | 83.9571 | 642.857 | 50.44% | 0 | 0 | 0 | 0% | 32.8
3267 | 0 | 0 | 0 | 19.5442 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5772 | 35.2 | 0 | 89.5772 | 557.434 | 43.74% | 0 | 0 | 0 | 0% | 35.2
3268 | 0 | 0 | 0 | 13.9026 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8694 | 38.3 | 0 | 96.8694 | 463.2502 | 36.35% | 0 | 0 | 0 | 0% | 38.3
3269 | 0 | 0 | 0 | 8.8654 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8075 | 40.8 | 0 | 102.8075 | 361.9005 | 28.4% | 0 | 0 | 0 | 0% | 40.8
3270 | 101 | 55 | 43 | 19.5442 | 18.5 | 50.8351 | 0 | 17.8792 | 0 | 2.0407 | 0 | 0 | 2.0407 | 0 | 0 | 0 | 101.2815 | 40.2593 | 0 | 101.2815 | 262.0471 | 20.56% | 0 | 0 | 0 | 0% | 42.3
3271 | 20 | 141 | 135 | 23.3725 | 17.7 | 10.0663 | 0 | 4.8149 | 0 | 9.4565 | 0 | 0 | 9.4565 | 0 | 0 | 0 | 85.5347 | 33.7435 | 0 | 85.5347 | 180.7505 | 14.18% | 0 | 0 | 0 | 0% | 43.2
3272 | 74 | 291 | 248 | 19.7457 | 18.1 | 37.2455 | 0 | 20.9573 | 0 | 20.9493 | 0 | 0 | 20.9493 | 0 | 0 | 0 | 60.2137 | 22.7507 | 0 | 60.2137 | 125.6811 | 9.861% | 0 | 0 | 0 | 0% | 43.7
3273 | 342 | 582 | 346 | 17.7308 | 20.5 | 172.1345 | 104.8193 | 0 | 71.3642 | 48.5378 | 2.3189 | 0 | 46.2189 | 0 | 0 | 0 | 0 | 0 | 71.3642 | 0 | 193.1864 | 15.16% | 0 | 0 | 0 | 0% | 43.9
3274 | 426 | 753 | 407 | 21.9621 | 23.2 | 214.4132 | 135.967 | 0 | 98.3726 | 82.5896 | 0 | 19.5448 | 63.0448 | 0 | 0 | 0 | 0 | 0 | 98.3726 | 0 | 286.2398 | 22.46% | 14.9909 | 0 | 15.2761 | 30.55% | 43.5
3275 | 281 | 717 | 453 | 23.3725 | 24.2 | 141.4322 | 92.2014 | 0 | 56.8996 | 79.0449 | 0 | 18.4725 | 60.5725 | 0 | 0 | 0 | 0 | 0 | 56.8996 | 0 | 340.0627 | 26.68% | 14.1684 | 0 | 29.714 | 59.43% | 42.1
3276 | 176 | 678 | 495 | 20.1487 | 25.2 | 88.5839 | 0 | 58.5063 | 0 | 70.7593 | 0 | 14.9297 | 55.8297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340.0627 | 26.68% | 11.451 | 0 | 41.383 | 82.77% | 40.9
3277 | 658 | 1037 | 395 | 10.4773 | 26.1 | 331.1828 | 217.6758 | 0 | 181.4863 | 109.8 | 23.7751 | 11.0249 | 75 | 0 | 0 | 0 | 0 | 0 | 181.4863 | 0 | 511.7355 | 40.15% | 8.4561 | 0 | 50 | 100% | 40.2
3278 | 262 | 717 | 467 | 9.2684 | 24.8 | 131.8692 | 84.9006 | 0 | 58 | 79.0652 | 19.5326 | 0 | 59.5326 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 566.5993 | 44.46% | 0 | 0 | 50 | 100% | 40
3279 | 88 | 475 | 393 | 7.455 | 25.2 | 44.2919 | 0 | 27.5134 | 0 | 36.542 | 0 | 0 | 36.542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566.5993 | 44.46% | 0 | 2.858 | 47.0881 | 94.18% | 39.4
3280 | 6 | 229 | 222 | 9.0669 | 23.5 | 3.0199 | 0 | 1.7707 | 0 | 16.6353 | 0 | 0 | 16.6353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566.5993 | 44.46% | 0 | 22.6647 | 23.9956 | 47.99% | 39.3
3281 | 2 | 187 | 184 | 7.455 | 22 | 1.0066 | 0 | 0.52862 | 0 | 13.4917 | 0 | 0 | 13.4917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566.5993 | 44.46% | 0 | 23.5512 | 0 | 0% | 37.043
3282 | 298 | 205 | 109 | 5.0372 | 22.5 | 149.9886 | 62.3228 | 0 | 39.3336 | 10.2184 | 0 | 0 | 10.2184 | 0 | 0 | 0 | 78.0926 | 30.3816 | 39.3336 | 78.0926 | 531.5026 | 41.7% | 0 | 0 | 0 | 0% | 40.6
3283 | 64 | 48 | 41 | 8.261 | 20.9 | 32.2123 | 0 | 0 | 0 | 2.2871 | 0 | 0 | 2.2871 | 0 | 0 | 0 | 93.1567 | 36.7129 | 0 | 93.1567 | 441.8581 | 34.67% | 0 | 0 | 0 | 0% | 39
3284 | 0 | 2 | 2 | 6.0446 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.73 | 36.2 | 0 | 91.73 | 353.6367 | 27.75% | 0 | 0 | 0 | 0% | 36.2
3285 | 0 | 0 | 0 | 2.6193 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1173 | 34.8 | 0 | 88.1173 | 269.3298 | 21.13% | 0 | 0 | 0 | 0% | 34.8
3286 | 0 | 0 | 0 | 3.0223 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8187 | 33.1 | 0 | 83.8187 | 189.912 | 14.9% | 0 | 0 | 0 | 0% | 33.1
3287 | 0 | 0 | 0 | 6.6491 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.1049 | 21.4516 | 0 | 57.1049 | 137.8453 | 10.82% | 0 | 0 | 0 | 0% | 21.4516
3288 | 0 | 0 | 0 | 3.6268 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.8453 | 10.82% | 0 | 0 | 0 | 0% | 0
3289 | 0 | 0 | 0 | 4.4327 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.8453 | 10.82% | 0 | 0 | 0 | 0% | 0
3290 | 0 | 0 | 0 | 4.0297 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.8453 | 10.82% | 0 | 0 | 0 | 0% | 0
3291 | 0 | 0 | 0 | 2.8208 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.8453 | 10.82% | 0 | 0 | 0 | 0% | 0
3292 | 0 | 0 | 0 | 3.6268 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.8453 | 10.82% | 0 | 0 | 0 | 0% | 0
3293 | 0 | 0 | 0 | 2.2164 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.8453 | 10.82% | 0 | 0 | 0 | 0% | 0
3294 | 68 | 43 | 37 | 3.2238 | 13.4 | 34.2256 | 0 | 12.0864 | 0 | 1.8343 | 0 | 0 | 1.8343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137.8453 | 10.82% | 0 | 0 | 0 | 0% | 1.8343
3295 | 529 | 218 | 53 | 2.0149 | 16.4 | 266.2549 | 127.5848 | 0 | 101.3496 | 5.928 | 0 | 0 | 5.928 | 0 | 0 | 0 | 0 | 0 | 101.3496 | 0 | 233.4702 | 18.32% | 0 | 0 | 0 | 0% | 5.928
3296 | 803 | 455 | 69 | 2.0149 | 18.8 | 404.1639 | 227.5552 | 0 | 194.9264 | 29.647 | 0 | 0 | 29.647 | 0 | 0 | 0 | 0 | 0 | 194.9264 | 0 | 417.3863 | 32.75% | 0 | 0 | 0 | 0% | 29.647
3297 | 857 | 660 | 101 | 3.0223 | 20.5 | 431.343 | 262.7054 | 0 | 227.2848 | 67.3476 | 0 | 14.2738 | 53.0738 | 0 | 0 | 0 | 0 | 0 | 227.2848 | 0 | 631.833 | 49.57% | 10.948 | 0 | 11.1579 | 22.32% | 38.8
3298 | 864 | 791 | 102 | 4.2312 | 21.3 | 434.8662 | 275.753 | 0 | 239.1139 | 94.7349 | 2.9675 | 25 | 66.7675 | 0 | 0 | 0 | 0 | 0 | 239.1139 | 0 | 857.4407 | 67.28% | 19.175 | 0 | 30.7005 | 61.4% | 38.8
3299 | 896 | 946 | 141 | 7.6565 | 21.8 | 450.9724 | 293.9746 | 0 | 254.4708 | 112.4 | 12.7111 | 24.6889 | 75 | 0 | 0 | 0 | 0 | 0 | 254.4708 | 0 | 1097.5379 | 86.11% | 18.9364 | 0 | 50 | 100% | 37.6
3300 | 745 | 925 | 211 | 7.2535 | 22.5 | 374.9715 | 247.6549 | 0 | 211.253 | 114.3 | 39.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 211.253 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.7
3301 | 651 | 884 | 252 | 7.6565 | 22.9 | 327.6596 | 0 | 215.3492 | 0 | 115.3 | 40.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.7
3302 | 599 | 789 | 238 | 9.0669 | 22.9 | 301.4871 | 0 | 194.0815 | 0 | 104.9547 | 35.3274 | 0 | 69.6274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.3
3303 | 669 | 808 | 255 | 5.6416 | 23.4 | 336.7193 | 0 | 209.1382 | 0 | 101.977 | 33.8885 | 0 | 68.0885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.2
3304 | 895 | 737 | 125 | 10.0743 | 24.7 | 450.4691 | 0 | 264.1616 | 0 | 86.54 | 25.97 | 0 | 60.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.6
3305 | 827 | 504 | 78 | 12.2907 | 23.9 | 416.2435 | 0 | 218.7054 | 0 | 35.5521 | 0.12606 | 0 | 35.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.3
3306 | 705 | 288 | 55 | 13.0966 | 22.7 | 354.8388 | 0 | 147.8747 | 0 | 10.2468 | 0 | 0 | 10.2468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.5245 | 49.05% | 35.2468
3307 | 389 | 89 | 29 | 11.6862 | 21.3 | 195.7905 | 0 | 0 | 0 | 1.3527 | 0 | 0 | 1.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.0668 | 0 | 0% | 25.4195
3308 | 0 | 1 | 1 | 10.8803 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2166 | 33.9 | 0 | 86.2166 | 1192.8721 | 93.59% | 0 | 0 | 0 | 0% | 33.9
3309 | 0 | 0 | 0 | 5.6416 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.003 | 32.2 | 0 | 82.003 | 1116.0833 | 87.57% | 0 | 0 | 0 | 0% | 32.2
3310 | 0 | 0 | 0 | 6.8506 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0791 | 30.2 | 0 | 77.0791 | 1044.7898 | 81.98% | 0 | 0 | 0 | 0% | 30.2
3311 | 0 | 0 | 0 | 5.0372 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.852 | 28.8 | 0 | 73.852 | 976.6649 | 76.63% | 0 | 0 | 0 | 0% | 28.8
3312 | 0 | 0 | 0 | 3.8283 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.7838 | 27.9 | 0 | 71.7838 | 910.522 | 71.44% | 0 | 0 | 0 | 0% | 27.9
3313 | 0 | 0 | 0 | 3.0223 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.9621 | 27.6 | 0 | 70.9621 | 845.1547 | 66.31% | 0 | 0 | 0 | 0% | 27.6
3314 | 0 | 0 | 0 | 3.0223 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.7275 | 27.5 | 0 | 70.7275 | 780.0032 | 61.2% | 0 | 0 | 0 | 0% | 27.5
3315 | 0 | 0 | 0 | 2.2164 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.7383 | 27.5 | 0 | 70.7383 | 714.8321 | 56.09% | 0 | 0 | 0 | 0% | 27.5
3316 | 0 | 0 | 0 | 1.6119 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.9941 | 27.2 | 0 | 69.9941 | 650.3634 | 51.03% | 0 | 0 | 0 | 0% | 27.2
3317 | 0 | 0 | 0 | 2.2164 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7874 | 28.9 | 0 | 73.7874 | 582.2283 | 45.68% | 0 | 0 | 0 | 0% | 28.9
3318 | 0 | 21 | 21 | 3.6268 | 15.3 | 0 | 0 | 0 | 0 | 0.9841 | 0 | 0 | 0.9841 | 0 | 0 | 0 | 76.9738 | 30.3159 | 0 | 76.9738 | 510.6196 | 40.06% | 0 | 0 | 0 | 0% | 31.3
3319 | 1 | 102 | 101 | 3.0223 | 15.5 | 0.50332 | 0 | 0.24161 | 0 | 7.0865 | 0 | 0 | 7.0865 | 0 | 0 | 0 | 68.5004 | 26.5135 | 0 | 68.5004 | 447.5531 | 35.12% | 0 | 0 | 0 | 0% | 33.6
3320 | 347 | 367 | 196 | 2.0149 | 18.1 | 174.6511 | 98.3943 | 0 | 73.9751 | 25.3002 | 0 | 0 | 25.3002 | 0 | 0 | 0 | 0 | 0 | 73.9751 | 0 | 515.896 | 40.48% | 0 | 0 | 0 | 0% | 25.3002
3321 | 555 | 572 | 193 | 3.0223 | 19.7 | 279.3412 | 170.1594 | 0 | 140.8992 | 54.3204 | 0 | 9.5602 | 44.7602 | 0 | 0 | 0 | 0 | 0 | 140.8992 | 0 | 646.0678 | 50.69% | 7.3327 | 0 | 7.4743 | 14.95% | 35.2
3322 | 935 | 830 | 86 | 4.6342 | 21.1 | 470.6018 | 298.4028 | 0 | 260.2928 | 104.6712 | 9.5356 | 25 | 70.1356 | 0 | 0 | 0 | 0 | 0 | 260.2928 | 0 | 886.543 | 69.56% | 19.175 | 0 | 27.0198 | 54.04% | 35.6
3323 | 971 | 952 | 80 | 6.4476 | 22.3 | 488.7212 | 318.5616 | 0 | 278.0506 | 114.7 | 14.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 278.0506 | 0 | 1143.424 | 89.71% | 19.175 | 0 | 46.5652 | 93.13% | 35.3
3324 | 974 | 1021 | 91 | 5.6416 | 23.2 | 490.2311 | 263.3327 | 60.4476 | 230.5183 | 116.4 | 37.0067 | 4.3933 | 75 | 0 | 0 | 0 | 0 | 0 | 230.5183 | 0 | 1274.5104 | 100% | 3.3697 | 0 | 50 | 100% | 33.6
3325 | 970 | 1037 | 106 | 6.2461 | 23.5 | 488.2179 | 0 | 320.8569 | 0 | 117.7 | 42.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.3
3326 | 947 | 983 | 116 | 8.0595 | 23.8 | 476.6416 | 0 | 306.7856 | 0 | 118 | 43 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32
3327 | 916 | 852 | 98 | 11.6862 | 23.9 | 461.0387 | 0 | 286.3164 | 0 | 114.223 | 40.9615 | 0 | 73.2615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.3
3328 | 839 | 681 | 104 | 9.8729 | 23.3 | 422.2833 | 0 | 247.6586 | 0 | 78.9433 | 22.9216 | 0 | 56.0216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.1
3329 | 790 | 491 | 79 | 7.858 | 23.5 | 397.6207 | 0 | 209.027 | 0 | 34.0177 | 0 | 0 | 34.0177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.0177
3330 | 686 | 290 | 60 | 9.0669 | 23.6 | 345.2757 | 0 | 144.2911 | 0 | 10.4133 | 0 | 0 | 10.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.5208 | 49.04% | 35.4133
3331 | 112 | 67 | 47 | 11.2833 | 21.9 | 56.3715 | 0 | 0 | 0 | 2.5613 | 0 | 0 | 2.5613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.0597 | 0 | 0% | 26.6211
3332 | 0 | 1 | 1 | 6.6491 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7625 | 34.1 | 0 | 86.7625 | 1192.2737 | 93.55% | 0 | 0 | 0 | 0% | 34.1
3333 | 0 | 0 | 0 | 1.2089 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3247 | 32 | 0 | 81.3247 | 1116.0316 | 87.57% | 0 | 0 | 0 | 0% | 32
3334 | 0 | 0 | 0 | 1.8134 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0637 | 30.2 | 0 | 77.0637 | 1044.735 | 81.97% | 0 | 0 | 0 | 0% | 30.2
3335 | 0 | 0 | 0 | 3.2238 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5582 | 29.1 | 0 | 74.5582 | 975.9131 | 76.57% | 0 | 0 | 0 | 0% | 29.1
3336 | 0 | 0 | 0 | 4.2312 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9652 | 28.9 | 0 | 73.9652 | 907.6487 | 71.22% | 0 | 0 | 0 | 0% | 28.9
3337 | 0 | 0 | 0 | 4.4327 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.15 | 29 | 0 | 74.15 | 839.1948 | 65.84% | 0 | 0 | 0 | 0% | 29
3338 | 0 | 0 | 0 | 2.6193 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0084 | 29.9 | 0 | 76.0084 | 768.7353 | 60.32% | 0 | 0 | 0 | 0% | 29.9
3339 | 0 | 0 | 0 | 2.4178 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.874 | 33.2 | 0 | 83.874 | 689.0138 | 54.06% | 0 | 0 | 0 | 0% | 33.2
3340 | 0 | 0 | 0 | 3.6268 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0391 | 37 | 0 | 93.0391 | 598.4512 | 46.96% | 0 | 0 | 0 | 0% | 37
3341 | 0 | 0 | 0 | 3.0223 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.3602 | 40.5 | 0 | 101.3602 | 497.8668 | 39.06% | 0 | 0 | 0 | 0% | 40.5
3342 | 284 | 58 | 23 | 2.6193 | 14.9 | 142.9421 | 0 | 50.8811 | 0 | 0.96312 | 0 | 0 | 0.96312 | 0 | 0 | 0 | 103.3522 | 41.3369 | 0 | 103.3522 | 394.8964 | 30.98% | 0 | 0 | 0 | 0% | 42.3
3343 | 672 | 247 | 50 | 1.8134 | 18.5 | 338.2293 | 162.6512 | 0 | 134.2433 | 6.4947 | 0 | 0 | 6.4947 | 0 | 0 | 0 | 92.3045 | 36.5053 | 134.2433 | 92.3045 | 431.7451 | 33.88% | 0 | 0 | 0 | 0% | 43
3344 | 824 | 459 | 64 | 1.4104 | 21.2 | 414.7335 | 233.7963 | 0 | 201.0311 | 29.5028 | 0 | 0 | 29.5028 | 0 | 0 | 0 | 0 | 0 | 201.0311 | 0 | 620.8351 | 48.71% | 0 | 0 | 0 | 0% | 29.5028
3345 | 893 | 657 | 76 | 2.4178 | 22.8 | 449.4624 | 273.8362 | 0 | 237.948 | 60.2883 | 0 | 8.2941 | 51.9941 | 0 | 0 | 0 | 0 | 0 | 237.948 | 0 | 844.6493 | 66.27% | 6.3616 | 0 | 6.4854 | 12.97% | 43.7
3346 | 930 | 832 | 95 | 4.4327 | 23.5 | 468.0852 | 296.7982 | 0 | 258.9058 | 95.8746 | 1.1373 | 25 | 69.7373 | 0 | 0 | 0 | 0 | 0 | 258.9058 | 0 | 1088.1765 | 85.38% | 19.175 | 0 | 26.0337 | 52.07% | 43.6
3347 | 940 | 953 | 110 | 7.2535 | 24.2 | 473.1183 | 272.539 | 35.8341 | 236.9502 | 107.8 | 7.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 236.9502 | 0 | 1274.5104 | 100% | 19.175 | 0 | 45.5819 | 91.16% | 42.2
3348 | 952 | 1046 | 137 | 9.2684 | 24.6 | 479.1582 | 0 | 316.4677 | 0 | 108.5 | 27.8498 | 5.6502 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 4.3337 | 0 | 50 | 100% | 41.5
3349 | 480 | 728 | 263 | 8.0595 | 24.1 | 241.5923 | 0 | 158.766 | 0 | 87.0407 | 23.0204 | 0 | 64.0204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41
3350 | 406 | 691 | 315 | 6.0446 | 24.1 | 204.3469 | 0 | 131.5037 | 0 | 77.679 | 18.4395 | 0 | 59.2395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.8
3351 | 760 | 842 | 219 | 7.052 | 24.8 | 382.5212 | 0 | 237.5231 | 0 | 102.6565 | 31.2283 | 0 | 71.4283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.2
3352 | 739 | 652 | 141 | 10.2758 | 24.5 | 371.9515 | 0 | 218.1592 | 0 | 66.6866 | 13.3933 | 0 | 53.2933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.9
3353 | 82 | 270 | 224 | 9.8729 | 23.7 | 41.272 | 0 | 21.7067 | 0 | 19.39 | 0 | 0 | 19.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 21.31 | 28.2785 | 56.56% | 40.7
3354 | 522 | 271 | 99 | 7.2535 | 24 | 262.7317 | 0 | 110.0863 | 0 | 11.4635 | 0 | 0 | 11.4635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 2.7945 | 5.589% | 36.4635
3355 | 178 | 85 | 52 | 7.858 | 21.7 | 89.5905 | 0 | 0 | 0 | 2.8642 | 0 | 0 | 2.8642 | 0 | 0 | 0 | 87.1682 | 34.1932 | 0 | 87.1682 | 1192.0258 | 93.53% | 0 | 2.7426 | 0 | 0% | 39.8
3356 | 0 | 2 | 2 | 5.2387 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7451 | 36.6 | 0 | 92.7451 | 1102.717 | 86.52% | 0 | 0 | 0 | 0% | 36.6
3357 | 0 | 0 | 0 | 3.4253 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1088 | 34.7 | 0 | 88.1088 | 1018.7477 | 79.93% | 0 | 0 | 0 | 0% | 34.7
3358 | 0 | 0 | 0 | 3.2238 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6754 | 32.9 | 0 | 83.6754 | 939.9589 | 73.75% | 0 | 0 | 0 | 0% | 32.9
3359 | 0 | 0 | 0 | 4.4327 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.81 | 31.8 | 0 | 80.81 | 864.279 | 67.81% | 0 | 0 | 0 | 0% | 31.8
3360 | 0 | 0 | 0 | 5.8431 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7502 | 31.4 | 0 | 79.7502 | 789.7131 | 61.96% | 0 | 0 | 0 | 0% | 31.4
3361 | 0 | 0 | 0 | 5.6416 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.991 | 31.5 | 0 | 79.991 | 714.8553 | 56.09% | 0 | 0 | 0 | 0% | 31.5
3362 | 0 | 0 | 0 | 5.4401 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8754 | 31.9 | 0 | 80.8754 | 638.8591 | 50.13% | 0 | 0 | 0 | 0% | 31.9
3363 | 0 | 0 | 0 | 2.0149 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2241 | 34.6 | 0 | 87.2241 | 555.1056 | 43.55% | 0 | 0 | 0 | 0% | 34.6
3364 | 0 | 0 | 0 | 1.4104 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7412 | 38.2 | 0 | 95.7412 | 461.1453 | 36.18% | 0 | 0 | 0 | 0% | 38.2
3365 | 0 | 0 | 0 | 2.2164 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3816 | 41.4 | 0 | 103.3816 | 358.0304 | 28.09% | 0 | 0 | 0 | 0% | 41.4
3366 | 0 | 28 | 28 | 2.6193 | 14 | 0 | 0 | 0 | 0 | 1.4654 | 0 | 0 | 1.4654 | 0 | 0 | 0 | 102.9472 | 41.2346 | 0 | 102.9472 | 255.3568 | 20.04% | 0 | 0 | 0 | 0% | 42.7
3367 | 113 | 160 | 125 | 2.6193 | 16 | 56.8749 | 0 | 27.3986 | 0 | 9.0467 | 0 | 0 | 9.0467 | 0 | 0 | 0 | 86.4774 | 34.2533 | 0 | 86.4774 | 172.529 | 13.54% | 0 | 0 | 0 | 0% | 43.3
3368 | 22 | 260 | 246 | 4.2312 | 18.1 | 11.073 | 0 | 6.246 | 0 | 18.8053 | 0 | 0 | 18.8053 | 0 | 0 | 0 | 64.4405 | 24.5895 | 0 | 64.4405 | 113.329 | 8.892% | 0 | 0 | 0 | 0% | 43.3948
3369 | 390 | 566 | 295 | 6.2461 | 20.4 | 196.2938 | 119.614 | 0 | 92.2987 | 43.8474 | 0 | 0 | 43.8474 | 0 | 0 | 0 | 0 | 0 | 92.2987 | 0 | 200.5807 | 15.74% | 0 | 0 | 0 | 0% | 43.8474
3370 | 794 | 811 | 177 | 7.6565 | 22.3 | 399.634 | 253.3893 | 0 | 216.3229 | 94.0227 | 0 | 24.9114 | 69.1114 | 0 | 0 | 0 | 0 | 0 | 216.3229 | 0 | 405.0747 | 31.78% | 19.107 | 0 | 19.4817 | 38.96% | 44.2
3371 | 921 | 966 | 138 | 9.0669 | 23.6 | 463.5553 | 302.1235 | 0 | 261.1972 | 107 | 7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 261.1972 | 0 | 651.9892 | 51.16% | 19.175 | 0 | 39.0328 | 78.07% | 43
3372 | 287 | 490 | 214 | 13.2981 | 23.3 | 144.4521 | 95.406 | 0 | 65.3508 | 46.004 | 2.002 | 0 | 44.002 | 0 | 0 | 0 | 0 | 0 | 65.3508 | 0 | 713.7665 | 56% | 0 | 0 | 39.0328 | 78.07% | 42
3373 | 2 | 80 | 77 | 8.8654 | 16.5 | 1.0066 | 0 | 0.66149 | 0 | 5.4689 | 0 | 0 | 5.4689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 713.7665 | 56% | 0 | 25 | 13.5466 | 27.09% | 30.4689
3374 | 365 | 634 | 301 | 6.6491 | 18.8 | 183.7108 | 118.2038 | 0 | 90.7551 | 70.6894 | 0 | 14.6447 | 56.0447 | 0 | 0 | 0 | 0 | 0 | 90.7551 | 0 | 799.559 | 62.73% | 11.2325 | 0 | 25 | 50% | 41.4
3375 | 651 | 852 | 308 | 7.2535 | 20.8 | 327.6596 | 203.429 | 0 | 170.0396 | 102.1152 | 5.6576 | 25 | 71.4576 | 0 | 0 | 0 | 0 | 0 | 170.0396 | 0 | 960.3006 | 75.35% | 19.175 | 0 | 44.5522 | 89.1% | 40.8
3376 | 443 | 599 | 286 | 7.455 | 21.4 | 222.9696 | 130.7865 | 0 | 101.8567 | 55.5793 | 0.57403 | 6.9656 | 48.0397 | 0 | 0 | 0 | 0 | 0 | 101.8567 | 0 | 1056.5875 | 82.9% | 5.3426 | 0 | 50 | 100% | 40.5
3377 | 24 | 162 | 149 | 7.6565 | 20.4 | 12.0796 | 0 | 6.356 | 0 | 11.7891 | 0 | 0 | 11.7891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056.5875 | 82.9% | 0 | 25 | 24.5122 | 49.02% | 36.7891
3378 | 252 | 228 | 139 | 7.858 | 20.7 | 126.836 | 0 | 53.2781 | 0 | 11.9707 | 0 | 0 | 11.9707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056.5875 | 82.9% | 0 | 24.0432 | 0 | 0% | 36.0139
3379 | 21 | 44 | 40 | 7.6565 | 19.3 | 10.5697 | 0 | 0 | 0 | 2.3555 | 0 | 0 | 2.3555 | 0 | 0 | 0 | 95.8923 | 37.9445 | 0 | 95.8923 | 963.533 | 75.6% | 0 | 0 | 0 | 0% | 40.3
3380 | 0 | 2 | 2 | 7.6565 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3245 | 37 | 0 | 93.3245 | 873.1427 | 68.51% | 0 | 0 | 0 | 0% | 37
3381 | 0 | 0 | 0 | 7.858 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5042 | 35.1 | 0 | 88.5042 | 788.0618 | 61.83% | 0 | 0 | 0 | 0% | 35.1
3382 | 0 | 0 | 0 | 6.0446 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1354 | 33.3 | 0 | 84.1354 | 708.1662 | 55.56% | 0 | 0 | 0 | 0% | 33.3
3383 | 0 | 0 | 0 | 5.0372 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2096 | 32.1 | 0 | 81.2096 | 631.6733 | 49.56% | 0 | 0 | 0 | 0% | 32.1
3384 | 0 | 0 | 0 | 3.8283 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2327 | 31.7 | 0 | 80.2327 | 556.2953 | 43.65% | 0 | 0 | 0 | 0% | 31.7
3385 | 0 | 0 | 0 | 2.6193 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4411 | 31.8 | 0 | 80.4411 | 480.6217 | 37.71% | 0 | 0 | 0 | 0% | 31.8
3386 | 0 | 0 | 0 | 3.8283 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7835 | 32.4 | 0 | 81.7835 | 403.2356 | 31.64% | 0 | 0 | 0 | 0% | 32.4
3387 | 0 | 0 | 0 | 4.2312 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.66 | 34.9 | 0 | 87.66 | 318.6293 | 25% | 0 | 0 | 0 | 0% | 34.9
3388 | 0 | 0 | 0 | 4.2312 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5383 | 38.2 | 0 | 95.5383 | 224.6861 | 17.63% | 0 | 0 | 0 | 0% | 38.2
3389 | 0 | 0 | 0 | 2.2164 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.158 | 32.2161 | 0 | 81.158 | 147.7539 | 11.59% | 0 | 0 | 0 | 0% | 32.2161
3390 | 264 | 58 | 25 | 3.8283 | 13.1 | 132.8758 | 0 | 47.6645 | 0 | 1.1238 | 0 | 0 | 1.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.7539 | 11.59% | 0 | 0 | 0 | 0% | 1.1238
3391 | 640 | 243 | 53 | 1.2089 | 16.7 | 322.1231 | 155.4479 | 0 | 127.7406 | 6.5658 | 0 | 0 | 6.5658 | 0 | 0 | 0 | 0 | 0 | 127.7406 | 0 | 268.3561 | 21.06% | 0 | 0 | 0 | 0% | 6.5658
3392 | 797 | 453 | 68 | 1.4104 | 19.2 | 401.144 | 226.418 | 0 | 194.0714 | 28.9763 | 0 | 0 | 28.9763 | 0 | 0 | 0 | 0 | 0 | 194.0714 | 0 | 451.5825 | 35.43% | 0 | 0 | 0 | 0% | 28.9763
3393 | 871 | 646 | 77 | 2.4178 | 21.1 | 438.3894 | 267.1869 | 0 | 231.6948 | 58.2826 | 0 | 7.1413 | 51.1413 | 0 | 0 | 0 | 0 | 0 | 231.6948 | 0 | 670.3296 | 52.6% | 5.4774 | 0 | 5.5859 | 11.17% | 44
3394 | 914 | 811 | 83 | 3.4253 | 22.5 | 460.0321 | 291.6793 | 0 | 254.4711 | 90.41 | 0 | 23.005 | 67.405 | 0 | 0 | 0 | 0 | 0 | 254.4711 | 0 | 910.5804 | 71.45% | 17.6448 | 0 | 23.5803 | 47.16% | 44.4
3395 | 939 | 932 | 89 | 4.8357 | 24.2 | 472.615 | 308.0128 | 0 | 269.1854 | 106.5 | 6.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 269.1854 | 0 | 1164.7232 | 91.39% | 19.175 | 0 | 43.1352 | 86.27% | 43.5
3396 | 942 | 1000 | 102 | 6.2461 | 25.3 | 474.125 | 226.1683 | 86.9771 | 197.2987 | 107.1 | 23.3237 | 8.7763 | 75 | 0 | 0 | 0 | 0 | 0 | 197.2987 | 0 | 1274.5104 | 100% | 6.7314 | 0 | 50 | 100% | 42.9
3397 | 921 | 1006 | 122 | 9.4699 | 25.8 | 463.5553 | 0 | 304.5979 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
3398 | 720 | 851 | 187 | 12.6937 | 25.9 | 362.3885 | 0 | 233.1295 | 0 | 105.731 | 31.6155 | 0 | 74.1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
3399 | 830 | 866 | 181 | 8.4625 | 26.6 | 417.7534 | 0 | 259.3271 | 0 | 103.5777 | 30.8889 | 0 | 72.6889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
3400 | 775 | 683 | 148 | 9.0669 | 26.2 | 390.071 | 0 | 228.8147 | 0 | 68.844 | 13.622 | 0 | 55.222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
3401 | 754 | 487 | 92 | 10.2758 | 25.6 | 379.5013 | 0 | 199.7627 | 0 | 33.5967 | 0 | 0 | 33.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.4033 | 41.4315 | 82.86% | 42
3402 | 613 | 271 | 67 | 7.052 | 24.9 | 308.5336 | 0 | 129.9068 | 0 | 9.9825 | 0 | 0 | 9.9825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.9396 | 31.88% | 34.9825
3403 | 277 | 81 | 31 | 8.261 | 22.7 | 139.4189 | 0 | 0 | 0 | 1.4685 | 0 | 0 | 1.4685 | 0 | 0 | 0 | 63.505 | 23.899 | 0 | 63.505 | 1216.4308 | 95.44% | 0 | 15.6325 | 0 | 0% | 41
3404 | 0 | 2 | 2 | 6.8506 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7249 | 37.4 | 0 | 94.7249 | 1124.913 | 88.26% | 0 | 0 | 0 | 0% | 37.4
3405 | 0 | 0 | 0 | 6.8506 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4064 | 35.3 | 0 | 89.4064 | 1039.2807 | 81.54% | 0 | 0 | 0 | 0% | 35.3
3406 | 0 | 0 | 0 | 4.0297 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.643 | 33.4 | 0 | 84.643 | 959.1046 | 75.25% | 0 | 0 | 0 | 0% | 33.4
3407 | 0 | 0 | 0 | 3.6268 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3993 | 32.1 | 0 | 81.3993 | 882.6195 | 69.25% | 0 | 0 | 0 | 0% | 32.1
3408 | 0 | 0 | 0 | 2.0149 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0909 | 31.6 | 0 | 80.0909 | 807.5328 | 63.36% | 0 | 0 | 0 | 0% | 31.6
3409 | 0 | 0 | 0 | 0.80595 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7518 | 31.5 | 0 | 79.7518 | 732.7158 | 57.49% | 0 | 0 | 0 | 0% | 31.5
3410 | 0 | 0 | 0 | 1.2089 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1291 | 32.1 | 0 | 81.1291 | 656.1965 | 51.49% | 0 | 0 | 0 | 0% | 32.1
3411 | 0 | 0 | 0 | 3.0223 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1538 | 34.6 | 0 | 87.1538 | 572.4898 | 44.92% | 0 | 0 | 0 | 0% | 34.6
3412 | 0 | 0 | 0 | 3.2238 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2999 | 38 | 0 | 95.2999 | 479.1539 | 37.6% | 0 | 0 | 0 | 0% | 38
3413 | 0 | 0 | 0 | 2.0149 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.1086 | 40.9 | 0 | 102.1086 | 377.5131 | 29.62% | 0 | 0 | 0 | 0% | 40.9
3414 | 279 | 59 | 25 | 4.4327 | 16 | 140.4256 | 0 | 50.5631 | 0 | 1.1101 | 0 | 0 | 1.1101 | 0 | 0 | 0 | 103.3585 | 41.2899 | 0 | 103.3585 | 274.7439 | 21.56% | 0 | 0 | 0 | 0% | 42.4
3415 | 645 | 246 | 54 | 2.6193 | 18.2 | 324.6397 | 156.9323 | 0 | 128.6241 | 6.6131 | 0 | 0 | 6.6131 | 0 | 0 | 0 | 92.4452 | 36.5869 | 128.6241 | 92.4452 | 307.0473 | 24.09% | 0 | 0 | 0 | 0% | 43.2
3416 | 797 | 455 | 68 | 2.0149 | 21.5 | 401.144 | 226.5598 | 0 | 194.0035 | 28.7524 | 0 | 0 | 28.7524 | 0 | 0 | 0 | 0 | 0 | 194.0035 | 0 | 490.7541 | 38.51% | 0 | 0 | 0 | 0% | 28.7524
3417 | 867 | 651 | 83 | 2.0149 | 24.6 | 436.3762 | 265.9711 | 0 | 230.7129 | 56.3944 | 0 | 5.8472 | 50.5472 | 0 | 0 | 0 | 0 | 0 | 230.7129 | 0 | 709.222 | 55.65% | 4.4848 | 0 | 4.5743 | 9.149% | 44.7
3418 | 892 | 806 | 93 | 2.4178 | 26.6 | 448.9591 | 284.6547 | 0 | 248.1778 | 85.4625 | 0 | 20.2813 | 65.1813 | 0 | 0 | 0 | 0 | 0 | 248.1778 | 0 | 944.2278 | 74.09% | 15.5557 | 0 | 20.4405 | 40.88% | 44.9
3419 | 941 | 936 | 89 | 3.2238 | 27.7 | 473.6217 | 308.6548 | 0 | 270.3555 | 106.3 | 6.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 270.3555 | 0 | 1200.2342 | 94.17% | 19.175 | 0 | 39.9982 | 80% | 43.7
3420 | 870 | 977 | 143 | 4.8357 | 28.7 | 437.8861 | 138.2917 | 150.9202 | 120.3705 | 107.1 | 19.3151 | 12.7849 | 75 | 0 | 0 | 0 | 0 | 0 | 120.3705 | 0 | 1274.5104 | 100% | 9.806 | 0 | 50 | 100% | 42.9
3421 | 922 | 997 | 111 | 9.4699 | 29.2 | 464.0586 | 0 | 304.9107 | 0 | 107.3 | 32.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.7
3422 | 931 | 951 | 98 | 10.6788 | 29.4 | 468.5885 | 0 | 301.3979 | 0 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
3423 | 896 | 834 | 96 | 12.4922 | 29.3 | 450.9724 | 0 | 279.9071 | 0 | 98.6476 | 28.4238 | 0 | 70.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
3424 | 870 | 685 | 85 | 12.4922 | 29 | 437.8861 | 0 | 256.8725 | 0 | 68.3326 | 13.3663 | 0 | 54.9663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
3425 | 779 | 491 | 81 | 12.0892 | 28.3 | 392.0842 | 0 | 206.461 | 0 | 33.2805 | 0 | 0 | 33.2805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.6195 | 41.2098 | 82.42% | 41.9
3426 | 626 | 282 | 69 | 11.0818 | 27 | 315.0767 | 0 | 132.9561 | 0 | 10.1937 | 0 | 0 | 10.1937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.7142 | 31.43% | 35.1937
3427 | 304 | 94 | 41 | 9.2684 | 25.5 | 153.0085 | 0 | 0 | 0 | 2.1631 | 0 | 0 | 2.1631 | 0 | 0 | 0 | 62.4644 | 23.2277 | 0 | 62.4644 | 1217.4632 | 95.52% | 0 | 15.4092 | 0 | 0% | 40.8
3428 | 0 | 1 | 1 | 7.455 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0443 | 37.3 | 0 | 95.0443 | 1126.2306 | 88.37% | 0 | 0 | 0 | 0% | 37.3
3429 | 0 | 0 | 0 | 6.4476 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7706 | 35.6 | 0 | 90.7706 | 1039.74 | 81.58% | 0 | 0 | 0 | 0% | 35.6
3430 | 0 | 0 | 0 | 4.4327 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5659 | 33.9 | 0 | 86.5659 | 957.9819 | 75.16% | 0 | 0 | 0 | 0% | 33.9
3431 | 0 | 0 | 0 | 4.2312 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2006 | 32.6 | 0 | 83.2006 | 879.9856 | 69.04% | 0 | 0 | 0 | 0% | 32.6
3432 | 0 | 0 | 0 | 2.2164 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9375 | 32.2 | 0 | 81.9375 | 803.2089 | 63.02% | 0 | 0 | 0 | 0% | 32.2
3433 | 0 | 0 | 0 | 0.20149 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2923 | 32 | 0 | 81.2923 | 726.9862 | 57.04% | 0 | 0 | 0 | 0% | 32
3434 | 0 | 0 | 0 | 1.6119 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5296 | 32.5 | 0 | 82.5296 | 649.3354 | 50.95% | 0 | 0 | 0 | 0% | 32.5
3435 | 0 | 0 | 0 | 3.2238 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0776 | 34.9 | 0 | 88.0776 | 564.7558 | 44.31% | 0 | 0 | 0 | 0% | 34.9
3436 | 0 | 0 | 0 | 1.0074 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1696 | 38.3 | 0 | 96.1696 | 470.5661 | 36.92% | 0 | 0 | 0 | 0% | 38.3
3437 | 0 | 0 | 0 | 1.4104 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0514 | 41.2 | 0 | 103.0514 | 368.0801 | 28.88% | 0 | 0 | 0 | 0% | 41.2
3438 | 93 | 65 | 50 | 1.6119 | 16.9 | 46.8085 | 0 | 16.9171 | 0 | 2.6134 | 0 | 0 | 2.6134 | 0 | 0 | 0 | 101.1254 | 40.2866 | 0 | 101.1254 | 268.1438 | 21.04% | 0 | 0 | 0 | 0% | 42.9
3439 | 145 | 182 | 137 | 1.2089 | 20.2 | 72.981 | 0 | 35.3395 | 0 | 9.7505 | 0 | 0 | 9.7505 | 0 | 0 | 0 | 85.9081 | 33.7495 | 0 | 85.9081 | 186.8251 | 14.66% | 0 | 0 | 0 | 0% | 43.5
3440 | 61 | 250 | 219 | 0.80595 | 22 | 30.7024 | 0 | 17.3511 | 0 | 17.6102 | 0 | 0 | 17.6102 | 0 | 0 | 0 | 69.0674 | 26.3898 | 0 | 69.0674 | 123.2372 | 9.669% | 0 | 0 | 0 | 0% | 44
3441 | 33 | 299 | 273 | 2.2164 | 23.8 | 16.6095 | 0 | 10.123 | 0 | 21.9694 | 0 | 0 | 21.9694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2372 | 9.669% | 0 | 0 | 0 | 0% | 21.9694
3442 | 15 | 325 | 309 | 3.6268 | 24.8 | 7.5498 | 0 | 4.7868 | 0 | 23.6959 | 0 | 0 | 23.6959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2372 | 9.669% | 0 | 0 | 0 | 0% | 23.6959
3443 | 190 | 611 | 426 | 4.2312 | 26.2 | 95.6303 | 62.3188 | 0 | 39.6573 | 52.711 | 0 | 4.7555 | 47.9555 | 0 | 0 | 0 | 0 | 0 | 39.6573 | 0 | 160.721 | 12.61% | 3.6475 | 0 | 3.7208 | 7.442% | 43.2
3444 | 298 | 751 | 452 | 4.6342 | 27.6 | 149.9886 | 99.0639 | 0 | 73.7944 | 79.2846 | 0 | 18.6423 | 60.6423 | 0 | 0 | 0 | 0 | 0 | 73.7944 | 0 | 230.4711 | 18.08% | 14.2986 | 0 | 18.307 | 36.61% | 42
3445 | 208 | 727 | 513 | 4.2312 | 28.3 | 104.69 | 68.7827 | 0 | 45.3624 | 72.7498 | 0 | 15.6249 | 57.1249 | 0 | 0 | 0 | 0 | 0 | 45.3624 | 0 | 273.3474 | 21.45% | 11.9843 | 0 | 30.5323 | 61.06% | 41.5
3446 | 52 | 492 | 438 | 15.5145 | 25.9 | 26.1725 | 0 | 16.8314 | 0 | 38.4432 | 0 | 0 | 38.4432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.3474 | 21.45% | 0 | 2.6568 | 27.8225 | 55.65% | 41.1
3447 | 107 | 467 | 374 | 16.5219 | 23.4 | 53.855 | 0 | 33.4214 | 0 | 37.4764 | 0 | 0 | 37.4764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273.3474 | 21.45% | 0 | 3.1236 | 24.6366 | 49.27% | 40.6
3448 | 463 | 597 | 281 | 15.313 | 23.3 | 233.036 | 136.7063 | 0 | 102.7892 | 57.4092 | 0 | 8.5046 | 48.9046 | 0 | 0 | 0 | 0 | 0 | 102.7892 | 0 | 370.5032 | 29.07% | 6.523 | 0 | 31.2909 | 62.58% | 40.4
3449 | 235 | 338 | 206 | 15.313 | 21.4 | 118.2796 | 62.3032 | 0 | 33.2027 | 24.0838 | 0 | 0 | 24.0838 | 0 | 0 | 0 | 0 | 0 | 33.2027 | 0 | 401.8863 | 31.53% | 0 | 16.5162 | 14.445 | 28.89% | 40.6
3450 | 2 | 69 | 68 | 13.7011 | 19.1 | 1.0066 | 0 | 0.42566 | 0 | 4.7293 | 0 | 0 | 4.7293 | 0 | 0 | 0 | 58.3727 | 21.9085 | 0 | 58.3727 | 348.6346 | 27.35% | 0 | 14.1622 | 0 | 0% | 40.8
3451 | 10 | 46 | 44 | 14.5071 | 18.2 | 5.0332 | 0 | 0 | 0 | 2.6802 | 0 | 0 | 2.6802 | 0 | 0 | 0 | 92.5243 | 36.6198 | 0 | 92.5243 | 259.1563 | 20.33% | 0 | 0 | 0 | 0% | 39.3
3452 | 0 | 2 | 2 | 12.8952 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1226 | 36.5 | 0 | 92.1226 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 36.5
3453 | 0 | 0 | 0 | 11.4848 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 0
3454 | 0 | 0 | 0 | 8.8654 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 0
3455 | 0 | 0 | 0 | 6.4476 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 0
3456 | 0 | 0 | 0 | 6.0446 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 0
3457 | 0 | 0 | 0 | 6.2461 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 0
3458 | 0 | 0 | 0 | 4.4327 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 0
3459 | 0 | 0 | 0 | 4.0297 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 0
3460 | 0 | 0 | 0 | 3.0223 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 0
3461 | 0 | 0 | 0 | 2.4178 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9862 | 13.34% | 0 | 0 | 0 | 0% | 0
3462 | 325 | 62 | 23 | 0.80595 | 13.4 | 163.5782 | 59.3352 | 0 | 38.2182 | 0.98991 | 0 | 0 | 0.98991 | 0 | 0 | 0 | 0 | 0 | 38.2182 | 0 | 206.0968 | 16.17% | 0 | 0 | 0 | 0% | 0.98991
3463 | 625 | 245 | 60 | 1.2089 | 17.1 | 314.5734 | 152.5824 | 0 | 125.0915 | 6.6825 | 0 | 0 | 6.6825 | 0 | 0 | 0 | 80.1364 | 31.5408 | 125.0915 | 80.1364 | 248.9856 | 19.54% | 0 | 0 | 0 | 0% | 38.2233
3464 | 770 | 479 | 103 | 2.4178 | 19.2 | 387.5544 | 219.1593 | 0 | 186.9151 | 30.729 | 0 | 0 | 30.729 | 0 | 0 | 0 | 0 | 0 | 186.9151 | 0 | 425.3876 | 33.38% | 0 | 0 | 0 | 0% | 30.729
3465 | 888 | 658 | 75 | 3.4253 | 20.6 | 446.9458 | 272.3907 | 0 | 236.2235 | 64.8486 | 0 | 12.8743 | 51.9743 | 0 | 0 | 0 | 0 | 0 | 236.2235 | 0 | 648.3247 | 50.87% | 9.8746 | 0 | 10.0743 | 20.15% | 39.1
3466 | 937 | 840 | 91 | 5.2387 | 22.1 | 471.6084 | 299.0118 | 0 | 260.6004 | 100.764 | 5.732 | 25 | 70.032 | 0 | 0 | 0 | 0 | 0 | 260.6004 | 0 | 894.2675 | 70.17% | 19.175 | 0 | 29.6371 | 59.27% | 39.3
3467 | 126 | 365 | 250 | 4.6342 | 22 | 63.418 | 0 | 41.3257 | 0 | 29.8481 | 0 | 0 | 29.8481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 894.2675 | 70.17% | 0 | 8.2519 | 21.2197 | 42.44% | 38.1
3468 | 9 | 291 | 278 | 8.4625 | 21.8 | 4.5299 | 0 | 2.9919 | 0 | 21.4799 | 0 | 0 | 21.4799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 894.2675 | 70.17% | 0 | 14.9201 | 6 | 12% | 36.4
3469 | 27 | 312 | 280 | 7.455 | 21.6 | 13.5896 | 0 | 8.928 | 0 | 23.9937 | 0 | 0 | 23.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 894.2675 | 70.17% | 0 | 5.8822 | 0 | 0% | 29.8759
3470 | 52 | 322 | 268 | 3.4253 | 21.5 | 26.1725 | 0 | 16.8285 | 0 | 24.6818 | 0 | 0 | 24.6818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 894.2675 | 70.17% | 0 | 0 | 0 | 0% | 24.6818
3471 | 31 | 266 | 237 | 4.2312 | 21.7 | 15.6028 | 0 | 9.6813 | 0 | 20.1039 | 0 | 0 | 20.1039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 894.2675 | 70.17% | 0 | 0 | 0 | 0% | 20.1039
3472 | 14 | 184 | 172 | 6.4476 | 20.9 | 7.0464 | 0 | 4.1337 | 0 | 13.3011 | 0 | 0 | 13.3011 | 0 | 0 | 0 | 57.901 | 21.5989 | 0 | 57.901 | 841.5228 | 66.03% | 0 | 0 | 0 | 0% | 34.9
3473 | 83 | 177 | 127 | 5.8431 | 20.6 | 41.7753 | 0 | 22.0114 | 0 | 12.3322 | 0 | 0 | 12.3322 | 0 | 0 | 0 | 61.5056 | 23.1678 | 0 | 61.5056 | 785.3045 | 61.62% | 0 | 0 | 0 | 0% | 35.5
3474 | 100 | 144 | 105 | 8.261 | 19.1 | 50.3317 | 0 | 21.3242 | 0 | 8.2772 | 0 | 0 | 8.2772 | 0 | 0 | 0 | 73.681 | 28.6228 | 0 | 73.681 | 717.3493 | 56.28% | 0 | 0 | 0 | 0% | 36.9
3475 | 122 | 59 | 39 | 6.0446 | 18.7 | 61.4047 | 0 | 0 | 0 | 2.1375 | 0 | 0 | 2.1375 | 0 | 0 | 0 | 87.1915 | 34.3625 | 0 | 87.1915 | 634.3214 | 49.77% | 0 | 0 | 0 | 0% | 36.5
3476 | 0 | 2 | 2 | 4.6342 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7038 | 34.7 | 0 | 87.7038 | 550.2967 | 43.18% | 0 | 0 | 0 | 0% | 34.7
3477 | 0 | 0 | 0 | 5.2387 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3082 | 32.5 | 0 | 82.3082 | 472.5918 | 37.08% | 0 | 0 | 0 | 0% | 32.5
3478 | 0 | 0 | 0 | 3.0223 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6296 | 30.6 | 0 | 77.6296 | 400.2144 | 31.4% | 0 | 0 | 0 | 0% | 30.6
3479 | 0 | 0 | 0 | 1.2089 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9216 | 29 | 0 | 73.9216 | 331.937 | 26.04% | 0 | 0 | 0 | 0% | 29
3480 | 0 | 0 | 0 | 2.2164 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8805 | 28.1 | 0 | 71.8805 | 265.6106 | 20.84% | 0 | 0 | 0 | 0% | 28.1
3481 | 0 | 0 | 0 | 2.4178 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.7577 | 27.6 | 0 | 70.7577 | 200.3452 | 15.72% | 0 | 0 | 0 | 0% | 27.6
3482 | 0 | 0 | 0 | 3.2238 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3452 | 15.72% | 0 | 0 | 0 | 0% | 0
3483 | 0 | 0 | 0 | 1.6119 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3452 | 15.72% | 0 | 0 | 0 | 0% | 0
3484 | 0 | 0 | 0 | 1.2089 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3452 | 15.72% | 0 | 0 | 0 | 0% | 0
3485 | 0 | 1 | 1 | 1.8134 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3452 | 15.72% | 0 | 0 | 0 | 0% | 0
3486 | 318 | 62 | 24 | 1.6119 | 13.7 | 160.0549 | 0 | 58.266 | 0 | 1.0595 | 0 | 0 | 1.0595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.3452 | 15.72% | 0 | 0 | 0 | 0% | 1.0595
3487 | 664 | 250 | 49 | 1.6119 | 17.9 | 334.2027 | 162.3738 | 0 | 134.0522 | 6.1971 | 0 | 0 | 6.1971 | 0 | 0 | 0 | 0 | 0 | 134.0522 | 0 | 325.3804 | 25.53% | 0 | 0 | 0 | 0% | 6.1971
3488 | 799 | 455 | 64 | 1.6119 | 20.6 | 402.1506 | 227.556 | 0 | 195.0756 | 28.4341 | 0 | 0 | 28.4341 | 0 | 0 | 0 | 0 | 0 | 195.0756 | 0 | 507.3344 | 39.81% | 0 | 0 | 0 | 0% | 28.4341
3489 | 869 | 649 | 75 | 2.0149 | 22.2 | 437.3828 | 266.555 | 0 | 231.2483 | 66.3085 | 0 | 16.1042 | 50.2042 | 0 | 0 | 0 | 0 | 0 | 231.2483 | 0 | 723.028 | 56.73% | 12.352 | 0 | 12.603 | 25.21% | 34.1
3490 | 883 | 822 | 114 | 2.8208 | 23.2 | 444.4293 | 281.7803 | 0 | 245.3025 | 99.3333 | 7.4167 | 25 | 66.9167 | 0 | 0 | 0 | 0 | 0 | 245.3025 | 0 | 951.8304 | 74.68% | 19.175 | 0 | 32.1679 | 64.34% | 34.5
3491 | 161 | 475 | 325 | 5.2387 | 23 | 81.0341 | 0 | 52.8034 | 0 | 42.6573 | 0 | 4.1787 | 38.4787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 951.8304 | 74.68% | 3.205 | 0 | 35.438 | 70.88% | 34.3
3492 | 458 | 751 | 302 | 9.2684 | 23.7 | 230.5194 | 152.2543 | 0 | 121.012 | 96.8033 | 13.3944 | 18.6073 | 64.8017 | 0 | 0 | 0 | 0 | 0 | 121.012 | 0 | 1064.7026 | 83.54% | 14.2718 | 0 | 50 | 100% | 32.8
3493 | 763 | 988 | 249 | 12.8952 | 24.1 | 384.0312 | 252.2821 | 0 | 212.179 | 118.1 | 43.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 212.179 | 0 | 1262.6096 | 99.07% | 0 | 0 | 50 | 100% | 31.9
3494 | 902 | 950 | 119 | 13.0966 | 24.4 | 453.9923 | 0 | 291.8587 | 0 | 118.4 | 43.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6096 | 99.07% | 0 | 0 | 50 | 100% | 31.6
3495 | 870 | 830 | 109 | 13.9026 | 24.3 | 437.8861 | 0 | 271.6587 | 0 | 109.3319 | 38.6659 | 0 | 70.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6096 | 99.07% | 0 | 0 | 50 | 100% | 32
3496 | 849 | 680 | 89 | 13.9026 | 23.8 | 427.3165 | 0 | 250.6764 | 0 | 77.5063 | 22.4031 | 0 | 55.1031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6096 | 99.07% | 0 | 0 | 50 | 100% | 32.7
3497 | 786 | 492 | 74 | 13.0966 | 23.3 | 395.6075 | 0 | 208.4986 | 0 | 33.4951 | 0 | 0 | 33.4951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6096 | 99.07% | 0 | 0 | 50 | 100% | 33.4951
3498 | 661 | 287 | 58 | 10.2758 | 22.8 | 332.6928 | 0 | 141.2049 | 0 | 10.0704 | 0 | 0 | 10.0704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6096 | 99.07% | 0 | 25 | 24.4956 | 48.99% | 35.0704
3499 | 414 | 99 | 31 | 8.6639 | 21.5 | 208.3734 | 0 | 0 | 0 | 1.4638 | 0 | 0 | 1.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6096 | 99.07% | 0 | 24.0111 | 0 | 0% | 25.4749
3500 | 1 | 3 | 3 | 6.4476 | 19.6 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8699 | 34.6 | 0 | 87.8699 | 1178.9288 | 92.5% | 0 | 0 | 0 | 0% | 34.6
3501 | 0 | 0 | 0 | 4.6342 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4201 | 32.4 | 0 | 82.4201 | 1101.5608 | 86.43% | 0 | 0 | 0 | 0% | 32.4
3502 | 0 | 0 | 0 | 3.2238 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5969 | 30.5 | 0 | 77.5969 | 1029.5159 | 80.78% | 0 | 0 | 0 | 0% | 30.5
3503 | 0 | 0 | 0 | 1.0074 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.9982 | 29.4 | 0 | 74.9982 | 960.2647 | 75.34% | 0 | 0 | 0 | 0% | 29.4
3504 | 0 | 0 | 0 | 1.6119 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7743 | 28.9 | 0 | 73.7743 | 892.182 | 70% | 0 | 0 | 0 | 0% | 28.9
3505 | 0 | 0 | 0 | 2.0149 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6579 | 28.9 | 0 | 73.6579 | 824.1891 | 64.67% | 0 | 0 | 0 | 0% | 28.9
3506 | 0 | 0 | 0 | 2.0149 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4073 | 29.7 | 0 | 75.4073 | 754.2259 | 59.18% | 0 | 0 | 0 | 0% | 29.7
3507 | 0 | 0 | 0 | 1.4104 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.708 | 32.8 | 0 | 82.708 | 675.6545 | 53.01% | 0 | 0 | 0 | 0% | 32.8
3508 | 0 | 0 | 0 | 1.6119 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5741 | 36.5 | 0 | 91.5741 | 586.5104 | 46.02% | 0 | 0 | 0 | 0% | 36.5
3509 | 0 | 1 | 1 | 4.2312 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1055 | 40.1 | 0 | 100.1055 | 487.0589 | 38.22% | 0 | 0 | 0 | 0% | 40.1
3510 | 359 | 65 | 22 | 5.0372 | 14.5 | 180.6909 | 66.0106 | 0 | 42.414 | 1.0414 | 0 | 0 | 1.0414 | 0 | 0 | 0 | 102.1301 | 40.8586 | 42.414 | 102.1301 | 425.1366 | 33.36% | 0 | 0 | 0 | 0% | 41.9
3511 | 706 | 258 | 43 | 3.2238 | 17.3 | 355.3421 | 172.9289 | 0 | 143.4366 | 6.1874 | 0 | 0 | 6.1874 | 0 | 0 | 0 | 92.122 | 36.5126 | 143.4366 | 92.122 | 470.7026 | 36.93% | 0 | 0 | 0 | 0% | 42.7
3512 | 850 | 467 | 52 | 3.2238 | 20.3 | 427.8198 | 242.2327 | 0 | 208.1859 | 29.0606 | 0 | 0 | 29.0606 | 0 | 0 | 0 | 0 | 0 | 208.1859 | 0 | 666.6161 | 52.3% | 0 | 0 | 0 | 0% | 29.0606
3513 | 911 | 660 | 61 | 2.6193 | 22.9 | 458.5221 | 279.4325 | 0 | 243.1521 | 58.2644 | 0 | 7.1322 | 51.1322 | 0 | 0 | 0 | 0 | 0 | 243.1521 | 0 | 895.4345 | 70.26% | 5.4704 | 0 | 5.5824 | 11.16% | 44
3514 | 937 | 821 | 72 | 3.8283 | 24.4 | 471.6084 | 299.015 | 0 | 261.1727 | 90.2679 | 0 | 23.0339 | 67.2339 | 0 | 0 | 0 | 0 | 0 | 261.1727 | 0 | 1141.2111 | 89.54% | 17.667 | 0 | 23.6112 | 47.22% | 44.2
3515 | 829 | 907 | 155 | 4.2312 | 26.6 | 417.2501 | 271.881 | 0 | 235.5343 | 106.8 | 6.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 235.5343 | 0 | 1274.5104 | 100% | 19.175 | 0 | 43.1788 | 86.36% | 43.2
3516 | 932 | 999 | 104 | 7.2535 | 27.8 | 469.0918 | 0 | 309.8296 | 0 | 107.7 | 23.9852 | 8.7148 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 6.6843 | 0 | 50 | 100% | 42.3
3517 | 911 | 993 | 113 | 11.4848 | 28.3 | 458.5221 | 0 | 301.1982 | 0 | 107.7 | 32.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
3518 | 729 | 843 | 169 | 11.8877 | 28 | 366.9184 | 0 | 235.8407 | 0 | 102.6934 | 30.2967 | 0 | 72.3967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
3519 | 927 | 847 | 78 | 12.4922 | 28.9 | 466.5752 | 0 | 289.4104 | 0 | 99.7199 | 29.0099 | 0 | 70.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
3520 | 895 | 712 | 87 | 11.6862 | 28.5 | 450.4691 | 0 | 264.2521 | 0 | 71.0449 | 14.7225 | 0 | 56.3225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
3521 | 784 | 504 | 85 | 9.4699 | 28.1 | 394.6008 | 0 | 208.0142 | 0 | 33.6208 | 0 | 0 | 33.6208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.2792 | 41.5525 | 83.11% | 41.9
3522 | 543 | 315 | 119 | 9.2684 | 26.5 | 273.3013 | 0 | 116.1711 | 0 | 12.9987 | 0 | 0 | 12.9987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.044 | 32.09% | 37.9987
3523 | 247 | 100 | 60 | 7.6565 | 24.4 | 124.3194 | 0 | 0 | 0 | 3.2951 | 0 | 0 | 3.2951 | 0 | 0 | 0 | 58.6736 | 21.6803 | 0 | 58.6736 | 1221.0726 | 95.81% | 0 | 15.7246 | 0 | 0% | 40.7
3524 | 2 | 6 | 6 | 5.6416 | 20.7 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0594 | 37.1 | 0 | 94.0594 | 1130.3631 | 88.69% | 0 | 0 | 0 | 0% | 37.1
3525 | 0 | 0 | 0 | 3.2238 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4598 | 35.3 | 0 | 89.4598 | 1044.693 | 81.97% | 0 | 0 | 0 | 0% | 35.3
3526 | 0 | 0 | 0 | 1.2089 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7947 | 33.4 | 0 | 84.7947 | 964.482 | 75.67% | 0 | 0 | 0 | 0% | 33.4
3527 | 0 | 0 | 0 | 1.0074 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1133 | 32.3 | 0 | 82.1133 | 887.3976 | 69.63% | 0 | 0 | 0 | 0% | 32.3
3528 | 0 | 0 | 0 | 1.0074 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7617 | 31.8 | 0 | 80.7617 | 811.7156 | 63.69% | 0 | 0 | 0 | 0% | 31.8
3529 | 0 | 0 | 0 | 1.4104 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7778 | 31.8 | 0 | 80.7778 | 736.0224 | 57.75% | 0 | 0 | 0 | 0% | 31.8
3530 | 0 | 0 | 0 | 2.0149 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8666 | 32.3 | 0 | 81.8666 | 658.9037 | 51.7% | 0 | 0 | 0 | 0% | 32.3
3531 | 0 | 0 | 0 | 1.8134 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4483 | 34.6 | 0 | 87.4483 | 575.1607 | 45.13% | 0 | 0 | 0 | 0% | 34.6
3532 | 0 | 0 | 0 | 2.2164 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8033 | 38.1 | 0 | 95.8033 | 481.4983 | 37.78% | 0 | 0 | 0 | 0% | 38.1
3533 | 0 | 1 | 1 | 9.6714 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0034 | 41.1 | 0 | 103.0034 | 379.2472 | 29.76% | 0 | 0 | 0 | 0% | 41.1
3534 | 243 | 59 | 28 | 10.6788 | 16.8 | 122.3061 | 0 | 44.8362 | 0 | 1.3272 | 0 | 0 | 1.3272 | 0 | 0 | 0 | 103.48 | 41.2728 | 0 | 103.48 | 276.4809 | 21.69% | 0 | 0 | 0 | 0% | 42.6
3535 | 598 | 243 | 59 | 10.4773 | 18.2 | 300.9838 | 146.7135 | 0 | 115.0867 | 6.3922 | 0 | 0 | 6.3922 | 0 | 0 | 0 | 93.6936 | 37.1078 | 115.0867 | 93.6936 | 294.4666 | 23.1% | 0 | 0 | 0 | 0% | 43.5
3536 | 767 | 450 | 73 | 9.2684 | 20.4 | 386.0444 | 218.7162 | 0 | 183.0352 | 28.4809 | 0 | 0 | 28.4809 | 0 | 0 | 0 | 0 | 0 | 183.0352 | 0 | 467.8245 | 36.71% | 0 | 0 | 0 | 0% | 28.4809
3537 | 856 | 645 | 78 | 8.261 | 23.5 | 430.8397 | 262.5593 | 0 | 224.5255 | 56.4685 | 0 | 5.7342 | 50.7342 | 0 | 0 | 0 | 0 | 0 | 224.5255 | 0 | 680.4791 | 53.39% | 4.3982 | 0 | 4.4889 | 8.978% | 45
3538 | 907 | 812 | 83 | 7.858 | 25.7 | 456.5089 | 289.4454 | 0 | 250.153 | 89.2621 | 0 | 22.131 | 67.131 | 0 | 0 | 0 | 0 | 0 | 250.153 | 0 | 917.4062 | 71.98% | 16.9745 | 0 | 21.8134 | 43.63% | 45
3539 | 882 | 932 | 130 | 7.2535 | 27.4 | 443.9259 | 289.2565 | 0 | 250.3671 | 106 | 6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 250.3671 | 0 | 1154.5361 | 90.59% | 19.175 | 0 | 41.3839 | 82.77% | 44
3540 | 763 | 962 | 225 | 8.0595 | 28.6 | 384.0312 | 246.636 | 7.014 | 210.4698 | 107 | 20.9935 | 11.0065 | 75 | 0 | 0 | 0 | 0 | 0 | 210.4698 | 0 | 1274.5104 | 100% | 8.442 | 0 | 50 | 100% | 43
3541 | 767 | 924 | 179 | 11.2833 | 28.4 | 386.0444 | 0 | 253.5719 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
3542 | 806 | 904 | 158 | 11.6862 | 28.4 | 405.6738 | 0 | 260.7061 | 0 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
3543 | 492 | 671 | 250 | 11.8877 | 28 | 247.6322 | 0 | 153.5777 | 0 | 68.0262 | 12.9631 | 0 | 55.0631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
3544 | 327 | 439 | 205 | 10.6788 | 26.9 | 164.5848 | 0 | 96.5443 | 0 | 34.6552 | 0 | 0 | 34.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.0448 | 42.811 | 85.62% | 41.7
3545 | 225 | 279 | 162 | 10.2758 | 26.1 | 113.2464 | 0 | 59.7091 | 0 | 19.864 | 0 | 0 | 19.864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.336 | 20.0174 | 40.03% | 42.2
3546 | 382 | 247 | 107 | 8.6639 | 26.1 | 192.2672 | 0 | 81.8062 | 0 | 10.6878 | 0 | 0 | 10.6878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 19.616 | 0 | 0% | 30.3038
3547 | 308 | 111 | 59 | 8.0595 | 24.9 | 155.0218 | 0 | 0 | 0 | 3.222 | 0 | 0 | 3.222 | 0 | 0 | 0 | 95.9509 | 37.578 | 0 | 95.9509 | 1182.3413 | 92.77% | 0 | 0 | 0 | 0% | 40.8
3548 | 2 | 6 | 5 | 7.858 | 22.5 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0596 | 37.4 | 0 | 95.0596 | 1090.8227 | 85.59% | 0 | 0 | 0 | 0% | 37.4
3549 | 0 | 0 | 0 | 9.4699 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5804 | 35.3 | 0 | 89.5804 | 1005.1897 | 78.87% | 0 | 0 | 0 | 0% | 35.3
3550 | 0 | 0 | 0 | 11.2833 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2583 | 33.6 | 0 | 85.2583 | 924.4384 | 72.53% | 0 | 0 | 0 | 0% | 33.6
3551 | 0 | 0 | 0 | 9.6714 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.431 | 32.5 | 0 | 82.431 | 846.8192 | 66.44% | 0 | 0 | 0 | 0% | 32.5
3552 | 0 | 0 | 0 | 8.261 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2437 | 32 | 0 | 81.2437 | 770.6046 | 60.46% | 0 | 0 | 0 | 0% | 32
3553 | 0 | 0 | 0 | 7.2535 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7778 | 31.8 | 0 | 80.7778 | 694.9424 | 54.53% | 0 | 0 | 0 | 0% | 31.8
3554 | 0 | 0 | 0 | 9.4699 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9988 | 32.3 | 0 | 81.9988 | 617.8551 | 48.48% | 0 | 0 | 0 | 0% | 32.3
3555 | 0 | 0 | 0 | 9.2684 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6701 | 34.7 | 0 | 87.6701 | 533.8545 | 41.89% | 0 | 0 | 0 | 0% | 34.7
3556 | 0 | 0 | 0 | 10.4773 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2264 | 38.3 | 0 | 96.2264 | 439.6587 | 34.5% | 0 | 0 | 0 | 0% | 38.3
3557 | 0 | 1 | 1 | 8.0595 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3421 | 41.3 | 0 | 103.3421 | 336.882 | 26.43% | 0 | 0 | 0 | 0% | 41.3
3558 | 292 | 66 | 29 | 6.0446 | 16.1 | 146.9687 | 0 | 54.0605 | 0 | 1.4041 | 0 | 0 | 1.4041 | 0 | 0 | 0 | 103.3932 | 41.2959 | 0 | 103.3932 | 234.0884 | 18.37% | 0 | 0 | 0 | 0% | 42.7
3559 | 650 | 254 | 55 | 9.6714 | 18.8 | 327.1563 | 159.7272 | 0 | 127.5678 | 6.5124 | 0 | 0 | 6.5124 | 0 | 0 | 0 | 93.037 | 36.7876 | 127.5678 | 93.037 | 265.3332 | 20.82% | 0 | 0 | 0 | 0% | 43.3
3560 | 767 | 458 | 82 | 12.6937 | 19.8 | 386.0444 | 218.853 | 0 | 181.0764 | 29.3032 | 0 | 0 | 29.3032 | 0 | 0 | 0 | 0 | 0 | 181.0764 | 0 | 437.4804 | 34.33% | 0 | 0 | 0 | 0% | 29.3032
3561 | 859 | 649 | 81 | 12.0892 | 20.8 | 432.3496 | 263.4788 | 0 | 222.986 | 59.141 | 0 | 7.2705 | 51.8705 | 0 | 0 | 0 | 0 | 0 | 222.986 | 0 | 649.4706 | 50.96% | 5.5765 | 0 | 5.6923 | 11.38% | 44.6
3562 | 899 | 810 | 88 | 12.4922 | 21.5 | 452.4823 | 286.8979 | 0 | 244.8328 | 92.431 | 0 | 23.7655 | 68.6655 | 0 | 0 | 0 | 0 | 0 | 244.8328 | 0 | 882.2302 | 69.22% | 18.2281 | 0 | 24.299 | 48.6% | 44.9
3563 | 924 | 930 | 92 | 11.0818 | 21.9 | 465.0653 | 303.0251 | 0 | 260.7691 | 106.4 | 6.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 260.7691 | 0 | 1130.1402 | 88.67% | 19.175 | 0 | 43.8723 | 87.74% | 43.6
3564 | 931 | 992 | 96 | 12.0892 | 22.8 | 468.5885 | 230.2488 | 79.2534 | 198.0298 | 107.2 | 24.3735 | 7.8265 | 75 | 0 | 0 | 0 | 0 | 0 | 198.0298 | 0 | 1274.5104 | 100% | 6.003 | 0 | 50 | 100% | 42.8
3565 | 926 | 997 | 99 | 12.8952 | 23.2 | 466.0719 | 0 | 306.1173 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
3566 | 916 | 946 | 99 | 12.6937 | 23.8 | 461.0387 | 0 | 296.2352 | 0 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
3567 | 884 | 838 | 101 | 13.0966 | 23.6 | 444.9326 | 0 | 275.8943 | 0 | 99.8874 | 28.9937 | 0 | 70.8937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.9
3568 | 837 | 683 | 96 | 13.4996 | 22.9 | 421.2767 | 0 | 247.105 | 0 | 68.3954 | 13.3477 | 0 | 55.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
3569 | 768 | 498 | 85 | 13.4996 | 22 | 386.5478 | 0 | 203.8386 | 0 | 33.9195 | 0 | 0 | 33.9195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.9805 | 41.8549 | 83.71% | 41.9
3570 | 629 | 293 | 70 | 12.8952 | 20.5 | 316.5866 | 0 | 134.8219 | 0 | 10.6294 | 0 | 0 | 10.6294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.3391 | 32.68% | 35.6294
3571 | 348 | 100 | 40 | 12.8952 | 18.5 | 175.1545 | 0 | 0 | 0 | 2.1262 | 0 | 0 | 2.1262 | 0 | 0 | 0 | 59.3649 | 22.3646 | 0 | 59.3649 | 1220.3967 | 95.75% | 0 | 16.0092 | 2.7756e-15 | 5.551e-15% | 40.5
3572 | 3 | 4 | 4 | 11.0818 | 17 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4917 | 37.1 | 0 | 93.4917 | 1129.7403 | 88.64% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.1
3573 | 0 | 0 | 0 | 8.6639 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5217 | 35.1 | 0 | 88.5217 | 1044.676 | 81.97% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.1
3574 | 0 | 0 | 0 | 5.2387 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3853 | 33.4 | 0 | 84.3853 | 964.511 | 75.68% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.4
3575 | 0 | 0 | 0 | 5.4401 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9052 | 32 | 0 | 80.9052 | 888.3187 | 69.7% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32
3576 | 0 | 0 | 0 | 4.4327 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3772 | 31.4 | 0 | 79.3772 | 813.8035 | 63.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.4
3577 | 0 | 0 | 0 | 5.4401 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3694 | 31.4 | 0 | 79.3694 | 739.2772 | 58% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.4
3578 | 0 | 0 | 0 | 5.8431 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5214 | 31.9 | 0 | 80.5214 | 663.3331 | 52.05% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.9
3579 | 0 | 0 | 0 | 2.4178 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2345 | 34.3 | 0 | 86.2345 | 580.5101 | 45.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.3
3580 | 0 | 0 | 0 | 1.6119 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.133 | 37.6 | 0 | 94.133 | 488.3259 | 38.31% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.6
3581 | 0 | 1 | 1 | 1.8134 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.314 | 40.6 | 0 | 101.314 | 387.5458 | 30.41% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 40.6
3582 | 356 | 69 | 24 | 1.2089 | 13.2 | 179.181 | 66.1289 | 0 | 43.9324 | 1.0649 | 0 | 0 | 1.0649 | 0 | 0 | 0 | 102.3848 | 41.0351 | 43.9324 | 102.3848 | 326.9334 | 25.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42.1
3583 | 705 | 262 | 46 | 4.6342 | 16.6 | 354.8388 | 173.5169 | 0 | 143.488 | 6.034 | 0 | 0 | 6.034 | 0 | 0 | 0 | 92.6135 | 36.766 | 143.488 | 92.6135 | 372.7769 | 29.25% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42.8
3584 | 846 | 472 | 57 | 7.858 | 19.3 | 425.8065 | 241.545 | 0 | 205.1778 | 29.5128 | 0 | 0 | 29.5128 | 0 | 0 | 0 | 0 | 0 | 205.1778 | 0 | 566.9896 | 44.49% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 29.5128
3585 | 922 | 671 | 62 | 12.4922 | 21 | 464.0586 | 282.8042 | 0 | 240.9324 | 62.3299 | 0 | 8.915 | 53.415 | 0 | 0 | 0 | 0 | 0 | 240.9324 | 0 | 795.0461 | 62.38% | 6.8378 | 0 | 6.9808 | 13.96% | 44.5
3586 | 959 | 835 | 67 | 13.2981 | 21.6 | 482.6814 | 306.0533 | 0 | 262.2189 | 96.9087 | 1.0544 | 25 | 70.8544 | 0 | 0 | 0 | 0 | 0 | 262.2189 | 0 | 1043.2515 | 81.86% | 19.175 | 0 | 26.5569 | 53.11% | 44.8
3587 | 962 | 948 | 78 | 12.0892 | 22 | 484.1913 | 315.483 | 0 | 271.7341 | 106.5 | 6.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 271.7341 | 0 | 1274.5104 | 100% | 19.175 | 0 | 46.133 | 92.27% | 43.5
3588 | 980 | 1016 | 74 | 14.7085 | 22.5 | 493.251 | 0 | 325.7947 | 0 | 107.2 | 27.2616 | 4.9384 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 3.7878 | 0 | 50 | 100% | 42.8
3589 | 986 | 1023 | 70 | 15.5145 | 23.4 | 496.2709 | 0 | 325.9302 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
3590 | 978 | 970 | 69 | 16.119 | 23.9 | 492.2444 | 0 | 316.2316 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
3591 | 961 | 865 | 66 | 15.5145 | 23.9 | 483.688 | 0 | 299.875 | 0 | 104.9369 | 31.4685 | 0 | 73.4685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42
3592 | 916 | 707 | 66 | 15.5145 | 23.5 | 461.0387 | 0 | 270.4101 | 0 | 72.0444 | 15.1222 | 0 | 56.9222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
3593 | 850 | 516 | 61 | 15.5145 | 22.7 | 427.8198 | 0 | 225.6298 | 0 | 34.8861 | 0 | 0 | 34.8861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.8139 | 43.0446 | 86.09% | 41.7
3594 | 736 | 310 | 50 | 13.9026 | 21.5 | 370.4416 | 0 | 157.8834 | 0 | 10.2782 | 0 | 0 | 10.2782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.5251 | 35.05% | 35.2782
3595 | 474 | 111 | 30 | 12.6937 | 19.7 | 238.5724 | 0 | 0 | 0 | 1.5672 | 0 | 0 | 1.5672 | 0 | 0 | 0 | 58.3509 | 21.864 | 0 | 58.3509 | 1221.3667 | 95.83% | 0 | 17.1688 | 0 | 0% | 40.6
3596 | 6 | 3 | 3 | 11.2833 | 17.6 | 3.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2991 | 37.4 | 0 | 94.2991 | 1129.8449 | 88.65% | 0 | 0 | 0 | 0% | 37.4
3597 | 0 | 0 | 0 | 9.2684 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6851 | 35.6 | 0 | 89.6851 | 1043.3727 | 81.86% | 0 | 0 | 0 | 0% | 35.6
3598 | 0 | 0 | 0 | 7.858 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3076 | 33.8 | 0 | 85.3076 | 962.043 | 75.48% | 0 | 0 | 0 | 0% | 33.8
3599 | 0 | 0 | 0 | 3.2238 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8159 | 32.4 | 0 | 81.8159 | 884.7052 | 69.42% | 0 | 0 | 0 | 0% | 32.4
3600 | 0 | 0 | 0 | 2.6193 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3295 | 31.8 | 0 | 80.3295 | 809.0525 | 63.48% | 0 | 0 | 0 | 0% | 31.8
3601 | 0 | 0 | 0 | 3.2238 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8496 | 31.6 | 0 | 79.8496 | 733.9513 | 57.59% | 0 | 0 | 0 | 0% | 31.6
3602 | 0 | 0 | 0 | 2.8208 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2401 | 32.2 | 0 | 81.2401 | 657.1457 | 51.56% | 0 | 0 | 0 | 0% | 32.2
3603 | 0 | 0 | 0 | 4.0297 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.243 | 34.3 | 0 | 86.243 | 574.3074 | 45.06% | 0 | 0 | 0 | 0% | 34.3
3604 | 0 | 0 | 0 | 3.6268 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.3724 | 37.7 | 0 | 94.3724 | 481.8216 | 37.8% | 0 | 0 | 0 | 0% | 37.7
3605 | 0 | 1 | 1 | 4.4327 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.589 | 40.3 | 0 | 100.589 | 381.8664 | 29.96% | 0 | 0 | 0 | 0% | 40.3
3606 | 389 | 72 | 22 | 2.8208 | 13.6 | 195.7905 | 72.4946 | 0 | 49.1009 | 1.0477 | 0 | 0 | 1.0477 | 0 | 0 | 0 | 102.2249 | 40.9523 | 49.1009 | 102.2249 | 326.3745 | 25.61% | 0 | 0 | 0 | 0% | 42
3607 | 732 | 266 | 41 | 3.8283 | 17.5 | 368.4283 | 180.4434 | 0 | 150.2393 | 5.9866 | 0 | 0 | 5.9866 | 0 | 0 | 0 | 94.3172 | 37.4134 | 150.2393 | 94.3172 | 376.8477 | 29.57% | 0 | 0 | 0 | 0% | 43.4
3608 | 854 | 474 | 52 | 9.0669 | 20.7 | 429.833 | 243.9806 | 0 | 206.7208 | 29.1386 | 0 | 0 | 29.1386 | 0 | 0 | 0 | 0 | 0 | 206.7208 | 0 | 572.6854 | 44.93% | 0 | 0 | 0 | 0% | 29.1386
3609 | 919 | 669 | 59 | 10.8803 | 22.2 | 462.5487 | 281.888 | 0 | 241.0802 | 60.0331 | 0 | 7.4666 | 52.5666 | 0 | 0 | 0 | 0 | 0 | 241.0802 | 0 | 801.0736 | 62.85% | 5.7269 | 0 | 5.8475 | 11.69% | 45.1
3610 | 960 | 836 | 62 | 13.2981 | 23.6 | 483.1847 | 306.3817 | 0 | 262.5893 | 94.5548 | 0 | 24.6274 | 69.9274 | 0 | 0 | 0 | 0 | 0 | 262.5893 | 0 | 1049.8384 | 82.37% | 18.8892 | 0 | 25.1346 | 50.27% | 45.3
3611 | 975 | 952 | 66 | 13.0966 | 24.2 | 490.7345 | 319.7434 | 0 | 275.1653 | 105.8 | 5.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 275.1653 | 0 | 1274.5104 | 100% | 19.175 | 0 | 44.7135 | 89.43% | 44.2
3612 | 980 | 1014 | 70 | 14.1041 | 24.7 | 493.251 | 0 | 325.7979 | 0 | 106.9 | 25.1498 | 6.7502 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 5.1774 | 0 | 50 | 100% | 43.1
3613 | 984 | 1022 | 69 | 15.313 | 25.3 | 495.2643 | 0 | 325.2469 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
3614 | 977 | 971 | 67 | 15.1115 | 25.4 | 491.7411 | 0 | 315.8541 | 0 | 107.6 | 32.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
3615 | 952 | 863 | 68 | 13.7011 | 25.7 | 479.1582 | 0 | 297.0156 | 0 | 102.7483 | 30.4242 | 0 | 72.3242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.9
3616 | 914 | 708 | 65 | 14.5071 | 25.6 | 460.0321 | 0 | 269.7985 | 0 | 70.8757 | 14.6378 | 0 | 56.2378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
3617 | 849 | 518 | 61 | 15.1115 | 24.7 | 427.3165 | 0 | 225.3842 | 0 | 34.6083 | 0 | 0 | 34.6083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.6917 | 43.1684 | 86.34% | 41.3
3618 | 734 | 312 | 50 | 13.4996 | 23.6 | 369.435 | 0 | 157.5675 | 0 | 10.2059 | 0 | 0 | 10.2059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.6452 | 35.29% | 35.2059
3619 | 474 | 113 | 31 | 12.2907 | 21.5 | 238.5724 | 0 | 0 | 0 | 1.6251 | 0 | 0 | 1.6251 | 0 | 0 | 0 | 57.0361 | 21.1909 | 0 | 57.0361 | 1222.6357 | 95.93% | 0 | 17.284 | 0 | 0% | 40.1
3620 | 9 | 4 | 3 | 10.0743 | 18.6 | 4.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4681 | 37.4 | 0 | 94.4681 | 1131.1131 | 88.75% | 0 | 0 | 0 | 0% | 37.4
3621 | 0 | 0 | 0 | 9.2684 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0617 | 36.1 | 0 | 91.0617 | 1043.2419 | 81.85% | 0 | 0 | 0 | 0% | 36.1
3622 | 0 | 0 | 0 | 10.6788 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0937 | 34.1 | 0 | 86.0937 | 961.0452 | 75.41% | 0 | 0 | 0 | 0% | 34.1
3623 | 0 | 0 | 0 | 6.8506 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2714 | 32.5 | 0 | 82.2714 | 883.4231 | 69.31% | 0 | 0 | 0 | 0% | 32.5
3624 | 0 | 0 | 0 | 5.2387 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1579 | 31.6 | 0 | 80.1579 | 808.3325 | 63.42% | 0 | 0 | 0 | 0% | 31.6
3625 | 0 | 0 | 0 | 4.4327 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6641 | 31 | 0 | 78.6641 | 734.9114 | 57.66% | 0 | 0 | 0 | 0% | 31
3626 | 0 | 0 | 0 | 6.0446 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6151 | 30.6 | 0 | 77.6151 | 662.593 | 51.99% | 0 | 0 | 0 | 0% | 30.6
3627 | 0 | 0 | 0 | 4.4327 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3276 | 30.5 | 0 | 77.3276 | 590.5405 | 46.33% | 0 | 0 | 0 | 0% | 30.5
3628 | 0 | 0 | 0 | 2.0149 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8967 | 31.2 | 0 | 78.8967 | 516.5234 | 40.53% | 0 | 0 | 0 | 0% | 31.2
3629 | 0 | 1 | 1 | 2.4178 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2995 | 33.9 | 0 | 85.2995 | 434.8117 | 34.12% | 0 | 0 | 0 | 0% | 33.9
3630 | 373 | 73 | 23 | 2.4178 | 14 | 187.7374 | 69.7347 | 0 | 46.7202 | 1.1211 | 0 | 0 | 1.1211 | 0 | 0 | 0 | 90.5805 | 36.0789 | 46.7202 | 90.5805 | 390.5699 | 30.64% | 0 | 0 | 0 | 0% | 37.2
3631 | 718 | 266 | 43 | 6.4476 | 18.1 | 361.3819 | 177.2642 | 0 | 146.0258 | 6.0345 | 0 | 0 | 6.0345 | 0 | 0 | 0 | 83.733 | 32.9655 | 146.0258 | 83.733 | 448.3655 | 35.18% | 0 | 0 | 0 | 0% | 39
3632 | 855 | 476 | 52 | 12.4922 | 21.2 | 430.3364 | 244.4174 | 0 | 205.0618 | 29.1269 | 0 | 0 | 29.1269 | 0 | 0 | 0 | 0 | 0 | 205.0618 | 0 | 640.5087 | 50.26% | 0 | 0 | 0 | 0% | 29.1269
3633 | 930 | 676 | 55 | 12.8952 | 22.8 | 468.0852 | 285.2684 | 0 | 243.0817 | 65.284 | 0 | 12.542 | 52.742 | 0 | 0 | 0 | 0 | 0 | 243.0817 | 0 | 868.2765 | 68.13% | 9.6197 | 0 | 9.8237 | 19.65% | 40.2
3634 | 968 | 841 | 59 | 13.4996 | 24.1 | 487.2112 | 308.946 | 0 | 264.864 | 99.3045 | 4.3023 | 25 | 70.0023 | 0 | 0 | 0 | 0 | 0 | 264.864 | 0 | 1116.4544 | 87.6% | 19.175 | 0 | 29.4055 | 58.81% | 40.7
3635 | 989 | 961 | 61 | 14.7085 | 25.3 | 497.7809 | 260.1795 | 64.1537 | 223.4281 | 110.3 | 10.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 223.4281 | 0 | 1274.5104 | 100% | 19.175 | 0 | 48.9872 | 97.97% | 39.7
3636 | 997 | 1026 | 63 | 15.5145 | 25.7 | 501.8074 | 0 | 331.453 | 0 | 111.8 | 36.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9872 | 97.97% | 38.2
3637 | 996 | 1030 | 63 | 16.7234 | 25.9 | 501.3041 | 0 | 329.1905 | 0 | 112.8 | 37.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9872 | 97.97% | 37.2
3638 | 988 | 979 | 63 | 17.5294 | 26.2 | 497.2776 | 0 | 319.3558 | 0 | 113.2 | 38.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9872 | 97.97% | 36.8
3639 | 968 | 871 | 62 | 17.1264 | 25.9 | 487.2112 | 0 | 301.9549 | 0 | 109.6828 | 36.4914 | 0 | 73.1914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9872 | 97.97% | 36.7
3640 | 936 | 718 | 58 | 16.5219 | 25.6 | 471.1051 | 0 | 276.2673 | 0 | 76.9205 | 19.9603 | 0 | 56.9603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9872 | 97.97% | 37
3641 | 878 | 528 | 53 | 16.9249 | 24.8 | 441.9127 | 0 | 233.0958 | 0 | 34.9877 | 0 | 0 | 34.9877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.9872 | 97.97% | 34.9877
3642 | 773 | 320 | 44 | 15.716 | 23.5 | 389.0643 | 0 | 166.0447 | 0 | 10.4187 | 0 | 0 | 10.4187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.4607 | 46.92% | 35.4187
3643 | 531 | 119 | 27 | 12.6937 | 22.1 | 267.2615 | 0 | 0 | 0 | 1.3197 | 0 | 0 | 1.3197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.9768 | 0 | 0% | 24.2965
3644 | 14 | 4 | 3 | 9.8729 | 19.6 | 7.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0365 | 35.5 | 0 | 90.0365 | 1188.3101 | 93.24% | 0 | 0 | 0 | 0% | 35.5
3645 | 0 | 0 | 0 | 9.6714 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7272 | 33.4 | 0 | 84.7272 | 1108.1247 | 86.95% | 0 | 0 | 0 | 0% | 33.4
3646 | 0 | 0 | 0 | 4.6342 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7604 | 31.4 | 0 | 79.7604 | 1033.602 | 81.1% | 0 | 0 | 0 | 0% | 31.4
3647 | 0 | 0 | 0 | 4.2312 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3713 | 30 | 0 | 76.3713 | 962.9636 | 75.56% | 0 | 0 | 0 | 0% | 30
3648 | 0 | 0 | 0 | 2.4178 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2679 | 29.1 | 0 | 74.2679 | 894.4369 | 70.18% | 0 | 0 | 0 | 0% | 29.1
3649 | 0 | 0 | 0 | 2.6193 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3211 | 28.7 | 0 | 73.3211 | 826.8121 | 64.87% | 0 | 0 | 0 | 0% | 28.7
3650 | 0 | 0 | 0 | 4.4327 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.645 | 28.4 | 0 | 72.645 | 759.8293 | 59.62% | 0 | 0 | 0 | 0% | 28.4
3651 | 0 | 0 | 0 | 3.8283 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4664 | 27.9 | 0 | 71.4664 | 693.969 | 54.45% | 0 | 0 | 0 | 0% | 27.9
3652 | 0 | 0 | 0 | 2.8208 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.348 | 27.9 | 0 | 71.348 | 628.2074 | 49.29% | 0 | 0 | 0 | 0% | 27.9
3653 | 0 | 1 | 1 | 4.8357 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1121 | 29.6 | 0 | 75.1121 | 558.4869 | 43.82% | 0 | 0 | 0 | 0% | 29.6
3654 | 420 | 77 | 21 | 4.0297 | 15.4 | 211.3933 | 78.7666 | 0 | 54.6258 | 0.9632 | 0 | 0 | 0.9632 | 0 | 0 | 0 | 79.2052 | 31.2368 | 54.6258 | 79.2052 | 534.9662 | 41.97% | 0 | 0 | 0 | 0% | 32.2
3655 | 760 | 275 | 39 | 2.2164 | 19.1 | 382.5212 | 187.9171 | 0 | 157.7587 | 5.8122 | 0 | 0 | 5.8122 | 0 | 0 | 0 | 73.3813 | 28.4878 | 157.7587 | 73.3813 | 613.509 | 48.14% | 0 | 0 | 0 | 0% | 34.3
3656 | 883 | 487 | 48 | 3.6268 | 21.5 | 444.4293 | 252.5771 | 0 | 217.6425 | 29.0509 | 0 | 0 | 29.0509 | 0 | 0 | 0 | 0 | 0 | 217.6425 | 0 | 815.1073 | 63.95% | 0 | 0 | 0 | 0% | 29.0509
3657 | 946 | 686 | 54 | 6.8506 | 23.8 | 476.1382 | 290.185 | 0 | 251.4225 | 69.297 | 0 | 16.7485 | 52.5485 | 0 | 0 | 0 | 0 | 0 | 251.4225 | 0 | 1047.9953 | 82.23% | 12.8461 | 0 | 13.1204 | 26.24% | 35.8
3658 | 978 | 850 | 58 | 10.8803 | 25.2 | 492.2444 | 312.1504 | 0 | 269.4556 | 103.0808 | 8.2404 | 25 | 69.8404 | 0 | 0 | 0 | 0 | 0 | 269.4556 | 0 | 1274.5104 | 100% | 19.175 | 0 | 32.7049 | 65.41% | 36.6
3659 | 993 | 967 | 61 | 10.4773 | 26.4 | 499.7942 | 0 | 325.645 | 0 | 113.4 | 16.3226 | 22.0774 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 16.9334 | 0 | 50 | 100% | 36.6
3660 | 1001 | 1031 | 63 | 8.8654 | 27.1 | 503.8207 | 0 | 332.7865 | 0 | 114.7 | 39.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.3
3661 | 1001 | 1037 | 63 | 9.0669 | 27.9 | 503.8207 | 0 | 330.8199 | 0 | 115.4 | 40.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.6
3662 | 991 | 985 | 64 | 9.6714 | 28.6 | 498.7875 | 0 | 320.2712 | 0 | 115.7 | 40.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.3
3663 | 967 | 874 | 63 | 10.6788 | 28.7 | 486.7079 | 0 | 301.5901 | 0 | 108.7897 | 37.1448 | 0 | 71.6448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.5
3664 | 931 | 718 | 60 | 10.2758 | 27.9 | 468.5885 | 0 | 274.7631 | 0 | 76.7846 | 20.8923 | 0 | 55.8923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35
3665 | 871 | 528 | 55 | 9.6714 | 27.8 | 438.3894 | 0 | 231.243 | 0 | 34.3294 | 0 | 0 | 34.3294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.3294
3666 | 760 | 320 | 46 | 9.8729 | 26.6 | 382.5212 | 0 | 163.342 | 0 | 10.3444 | 0 | 0 | 10.3444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.4699 | 48.94% | 35.3444
3667 | 485 | 115 | 30 | 9.8729 | 24.6 | 244.1089 | 0 | 0 | 0 | 1.518 | 0 | 0 | 1.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.9618 | 5.5511e-15 | 1.11e-14% | 25.4798
3668 | 15 | 5 | 4 | 7.2535 | 22 | 7.5498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3199 | 35.9 | 0 | 91.3199 | 1187.1474 | 93.15% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 35.9
3669 | 0 | 0 | 0 | 4.0297 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5205 | 33.6 | 0 | 85.5205 | 1106.3461 | 86.81% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 33.6
3670 | 0 | 0 | 0 | 3.0223 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8669 | 31.7 | 0 | 80.8669 | 1030.8839 | 80.88% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 31.7
3671 | 0 | 0 | 0 | 2.6193 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7918 | 30.5 | 0 | 77.7918 | 958.7824 | 75.23% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 30.5
3672 | 0 | 0 | 0 | 2.0149 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1063 | 29.9 | 0 | 76.1063 | 888.3446 | 69.7% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 29.9
3673 | 0 | 0 | 0 | 1.2089 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0534 | 29.9 | 0 | 76.0534 | 817.897 | 64.17% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 29.9
3674 | 0 | 0 | 0 | 2.0149 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8707 | 30.7 | 0 | 77.8707 | 745.2523 | 58.47% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 30.7
3675 | 0 | 0 | 0 | 3.4253 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.339 | 33.8 | 0 | 85.339 | 663.8062 | 52.08% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 33.8
3676 | 0 | 0 | 0 | 1.2089 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6555 | 37.7 | 0 | 94.6555 | 571.2588 | 44.82% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 37.7
3677 | 0 | 2 | 2 | 3.4253 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4881 | 40.6 | 0 | 101.4881 | 470.3939 | 36.91% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 40.6
3678 | 347 | 76 | 28 | 2.6193 | 17.2 | 174.6511 | 65.2744 | 0 | 42.6837 | 1.3221 | 0 | 0 | 1.3221 | 0 | 0 | 0 | 102.8351 | 40.9779 | 42.6837 | 102.8351 | 408.5205 | 32.05% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 42.3
3679 | 694 | 267 | 51 | 1.2089 | 21.8 | 349.3023 | 171.853 | 0 | 143.1389 | 6.0464 | 0 | 0 | 6.0464 | 0 | 0 | 0 | 95.5507 | 37.6536 | 143.1389 | 95.5507 | 450.9917 | 35.39% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 43.7
3680 | 813 | 476 | 71 | 1.8134 | 23.7 | 409.197 | 232.6963 | 0 | 199.8634 | 28.2693 | 0 | 0 | 28.2693 | 0 | 0 | 0 | 0 | 0 | 199.8634 | 0 | 639.6965 | 50.19% | 0 | 0 | 5.5511e-15 | 1.11e-14% | 28.2693
3681 | 811 | 652 | 114 | 3.0223 | 25.4 | 408.1904 | 248.7833 | 0 | 214.3613 | 53.439 | 0 | 3.8695 | 49.5695 | 0 | 0 | 0 | 0 | 0 | 214.3613 | 0 | 842.0896 | 66.07% | 2.9679 | 0 | 3.0317 | 6.063% | 45.7
3682 | 874 | 819 | 115 | 3.4253 | 26.8 | 439.8994 | 278.9695 | 0 | 242.4766 | 84.1005 | 0 | 18.9002 | 65.2002 | 0 | 0 | 0 | 0 | 0 | 242.4766 | 0 | 1071.0283 | 84.03% | 14.4965 | 0 | 17.8399 | 35.68% | 46.3
3683 | 933 | 942 | 96 | 3.2238 | 28.8 | 469.5951 | 305.9701 | 0 | 267.8683 | 104.6 | 4.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 267.8683 | 0 | 1274.5104 | 100% | 19.175 | 0 | 37.4273 | 74.85% | 45.4
3684 | 948 | 1012 | 99 | 4.2312 | 30.2 | 477.1449 | 0 | 315.1703 | 0 | 105 | 13.9531 | 16.0469 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 12.308 | 0 | 50 | 100% | 45
3685 | 914 | 1013 | 125 | 7.858 | 30.1 | 460.0321 | 0 | 302.046 | 0 | 105.1 | 30.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.9
3686 | 577 | 844 | 300 | 7.455 | 30.2 | 290.4141 | 0 | 186.4434 | 0 | 93.1641 | 24.032 | 0 | 69.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.1
3687 | 162 | 585 | 441 | 10.0743 | 29 | 81.5374 | 0 | 50.516 | 0 | 46.0435 | 0.87176 | 0 | 45.1718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.3
3688 | 249 | 522 | 339 | 8.6639 | 29.1 | 125.326 | 0 | 73.4781 | 0 | 39.0844 | 0 | 0 | 39.0844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 4.5156 | 45.388 | 90.78% | 43.6
3689 | 644 | 499 | 152 | 8.261 | 29 | 324.1364 | 0 | 170.9753 | 0 | 33.721 | 0 | 0 | 33.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.679 | 35.5023 | 71% | 43.4
3690 | 499 | 266 | 92 | 8.4625 | 28.2 | 251.1554 | 0 | 107.297 | 0 | 10.8608 | 0 | 0 | 10.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 9.9678 | 19.94% | 35.8608
3691 | 376 | 110 | 43 | 7.6565 | 26.8 | 189.2473 | 0 | 0 | 0 | 2.2337 | 0 | 0 | 2.2337 | 0 | 0 | 0 | 77.5602 | 29.8066 | 0 | 77.5602 | 1202.9078 | 94.38% | 0 | 9.7598 | 0 | 0% | 41.8
3692 | 11 | 5 | 5 | 3.6268 | 24.1 | 5.5365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.7963 | 38.4 | 0 | 97.7963 | 1108.5045 | 86.97% | 0 | 0 | 0 | 0% | 38.4
3693 | 0 | 0 | 0 | 2.8208 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4072 | 36.8 | 0 | 93.4072 | 1018.632 | 79.92% | 0 | 0 | 0 | 0% | 36.8
3694 | 0 | 0 | 0 | 1.2089 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4706 | 34.8 | 0 | 88.4706 | 934.3705 | 73.31% | 0 | 0 | 0 | 0% | 34.8
3695 | 0 | 0 | 0 | 2.0149 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1708 | 33.5 | 0 | 85.1708 | 853.8624 | 67% | 0 | 0 | 0 | 0% | 33.5
3696 | 0 | 0 | 0 | 1.0074 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.235 | 32.8 | 0 | 83.235 | 775.3465 | 60.83% | 0 | 0 | 0 | 0% | 32.8
3697 | 0 | 0 | 0 | 1.2089 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1264 | 32.8 | 0 | 83.1264 | 696.8187 | 54.67% | 0 | 0 | 0 | 0% | 32.8
3698 | 0 | 0 | 0 | 0.40297 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5079 | 33.4 | 0 | 84.5079 | 616.5609 | 48.38% | 0 | 0 | 0 | 0% | 33.4
3699 | 0 | 0 | 0 | 0.80595 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0064 | 35.7 | 0 | 90.0064 | 529.6968 | 41.56% | 0 | 0 | 0 | 0% | 35.7
3700 | 0 | 0 | 0 | 0.40297 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0759 | 39.1 | 0 | 98.0759 | 433.1657 | 33.99% | 0 | 0 | 0 | 0% | 39.1
3701 | 0 | 1 | 1 | 2.0149 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5316 | 41.8 | 0 | 104.5316 | 328.9268 | 25.81% | 0 | 0 | 0 | 0% | 41.8
3702 | 369 | 75 | 26 | 1.2089 | 17 | 185.7241 | 69.619 | 0 | 47.0733 | 1.181 | 0 | 0 | 1.181 | 0 | 0 | 0 | 105.5551 | 42.119 | 47.0733 | 105.5551 | 268.4128 | 21.06% | 0 | 0 | 0 | 0% | 43.3
3703 | 711 | 271 | 50 | 1.8134 | 20.8 | 357.8587 | 176.3197 | 0 | 147.16 | 6.0209 | 0 | 0 | 6.0209 | 0 | 0 | 0 | 97.3894 | 38.4791 | 147.16 | 97.3894 | 313.6471 | 24.61% | 0 | 0 | 0 | 0% | 44.5
3704 | 831 | 478 | 68 | 2.4178 | 21.8 | 418.2567 | 237.9929 | 0 | 204.5632 | 28.8752 | 0 | 0 | 28.8752 | 0 | 0 | 0 | 0 | 0 | 204.5632 | 0 | 508.4549 | 39.89% | 0 | 0 | 0 | 0% | 28.8752
3705 | 905 | 675 | 76 | 3.4253 | 24.8 | 455.5022 | 277.6316 | 0 | 241.1962 | 56.0715 | 0 | 4.8358 | 51.2358 | 0 | 0 | 0 | 0 | 0 | 241.1962 | 0 | 738.1488 | 57.92% | 3.709 | 0 | 3.7893 | 7.579% | 46.4
3706 | 941 | 839 | 83 | 4.6342 | 25.8 | 473.6217 | 300.3706 | 0 | 262.1779 | 88.6727 | 0 | 21.0864 | 67.5864 | 0 | 0 | 0 | 0 | 0 | 262.1779 | 0 | 987.8238 | 77.51% | 16.1732 | 0 | 20.3127 | 40.63% | 46.5
3707 | 958 | 955 | 87 | 4.6342 | 27.7 | 482.1781 | 314.1715 | 0 | 275.0333 | 104.5 | 4.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 275.0333 | 0 | 1249.7411 | 98.06% | 19.175 | 0 | 39.9029 | 79.81% | 45.5
3708 | 962 | 1017 | 90 | 8.0595 | 29.7 | 484.1913 | 0 | 319.8153 | 0 | 105.1 | 17.2147 | 12.8853 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.7411 | 98.06% | 9.8831 | 0 | 50 | 100% | 44.9
3709 | 954 | 1019 | 94 | 9.8729 | 30.1 | 480.1648 | 0 | 315.2422 | 0 | 105.2 | 30.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.7411 | 98.06% | 0 | 0 | 50 | 100% | 44.8
3710 | 933 | 961 | 96 | 11.2833 | 30.8 | 469.5951 | 0 | 301.4257 | 0 | 105.2 | 30.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.7411 | 98.06% | 0 | 0 | 50 | 100% | 44.8
3711 | 897 | 856 | 104 | 10.2758 | 30.9 | 451.4757 | 0 | 279.659 | 0 | 95.2301 | 25.665 | 0 | 69.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.7411 | 98.06% | 0 | 0 | 50 | 100% | 43.9
3712 | 823 | 701 | 118 | 10.4773 | 30.2 | 414.2302 | 0 | 242.8289 | 0 | 65.5521 | 11.1261 | 0 | 54.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.7411 | 98.06% | 0 | 0 | 50 | 100% | 43.3
3713 | 722 | 506 | 112 | 8.4625 | 29.6 | 363.3952 | 0 | 191.6763 | 0 | 33.2773 | 0 | 0 | 33.2773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.7411 | 98.06% | 0 | 9.8227 | 39.9661 | 79.93% | 43.1
3714 | 571 | 301 | 93 | 8.6639 | 26.6 | 287.3942 | 0 | 122.8262 | 0 | 11.7146 | 0 | 0 | 11.7146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.7411 | 98.06% | 0 | 25 | 14.4281 | 28.86% | 36.7146
3715 | 255 | 103 | 52 | 7.2535 | 23.9 | 128.3459 | 0 | 0 | 0 | 2.7742 | 0 | 0 | 2.7742 | 0 | 0 | 0 | 65.4906 | 24.701 | 0 | 65.4906 | 1189.7459 | 93.35% | 0 | 14.1247 | 0 | 0% | 41.6
3716 | 3 | 4 | 4 | 5.4401 | 21.4 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0495 | 38.3 | 0 | 97.0495 | 1095.669 | 85.97% | 0 | 0 | 0 | 0% | 38.3
3717 | 0 | 0 | 0 | 3.8283 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9503 | 36.7 | 0 | 92.9503 | 1006.1168 | 78.94% | 0 | 0 | 0 | 0% | 36.7
3718 | 0 | 0 | 0 | 2.4178 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2576 | 34.8 | 0 | 88.2576 | 921.8911 | 72.33% | 0 | 0 | 0 | 0% | 34.8
3719 | 0 | 0 | 0 | 2.2164 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3263 | 33.6 | 0 | 85.3263 | 841.1293 | 66% | 0 | 0 | 0 | 0% | 33.6
3720 | 0 | 0 | 0 | 2.0149 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0841 | 33 | 0 | 84.0841 | 762.0755 | 59.79% | 0 | 0 | 0 | 0% | 33
3721 | 0 | 0 | 0 | 1.8134 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6698 | 32.8 | 0 | 83.6698 | 683.5222 | 53.63% | 0 | 0 | 0 | 0% | 32.8
3722 | 0 | 0 | 0 | 3.4253 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9972 | 33.4 | 0 | 84.9972 | 603.2978 | 47.34% | 0 | 0 | 0 | 0% | 33.4
3723 | 0 | 0 | 0 | 7.858 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7813 | 35.7 | 0 | 90.7813 | 516.4702 | 40.52% | 0 | 0 | 0 | 0% | 35.7
3724 | 0 | 0 | 0 | 9.2684 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8665 | 39.1 | 0 | 98.8665 | 419.9801 | 32.95% | 0 | 0 | 0 | 0% | 39.1
3725 | 0 | 1 | 1 | 9.2684 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9466 | 41.6 | 0 | 104.9466 | 316.3532 | 24.82% | 0 | 0 | 0 | 0% | 41.6
3726 | 119 | 54 | 38 | 15.716 | 21.4 | 59.8948 | 0 | 22.5166 | 0 | 1.9786 | 0 | 0 | 1.9786 | 0 | 0 | 0 | 103.1412 | 40.8214 | 0 | 103.1412 | 214.8996 | 16.86% | 0 | 0 | 0 | 0% | 42.8
3727 | 509 | 237 | 75 | 17.1264 | 22 | 256.1886 | 126.4068 | 0 | 92.1264 | 6.8208 | 0 | 0 | 6.8208 | 0 | 0 | 0 | 60.9591 | 22.8357 | 92.1264 | 60.9591 | 246.7637 | 19.36% | 0 | 0 | 0 | 0% | 29.6565
3728 | 685 | 453 | 115 | 18.3353 | 22.8 | 344.7724 | 196.2978 | 0 | 156.8412 | 28.5726 | 0 | 0 | 28.5726 | 0 | 0 | 0 | 0 | 0 | 156.8412 | 0 | 395.5781 | 31.04% | 0 | 0 | 0 | 0% | 28.5726
3729 | 882 | 678 | 91 | 20.3502 | 24 | 443.9259 | 270.5903 | 0 | 224.9471 | 61.2763 | 0 | 8.1882 | 53.0882 | 0 | 0 | 0 | 0 | 0 | 224.9471 | 0 | 609.0128 | 47.78% | 6.2803 | 0 | 6.4172 | 12.83% | 44.9
3730 | 858 | 855 | 165 | 21.5591 | 25.3 | 431.8463 | 273.8924 | 0 | 227.4301 | 97.8158 | 1.2079 | 25 | 71.6079 | 0 | 0 | 0 | 0 | 0 | 227.4301 | 0 | 824.8035 | 64.72% | 19.175 | 0 | 26.0102 | 52.02% | 45.4
3731 | 481 | 811 | 369 | 20.7532 | 26.1 | 242.0957 | 157.7438 | 0 | 119.5847 | 92.5646 | 0 | 24.2323 | 68.3323 | 0 | 0 | 0 | 0 | 0 | 119.5847 | 0 | 938.268 | 73.62% | 18.5862 | 0 | 45.0015 | 90% | 44.1
3732 | 778 | 1045 | 288 | 13.9026 | 27.6 | 391.5809 | 258.6216 | 0 | 217.5814 | 107.1 | 25.7222 | 6.3778 | 75 | 0 | 0 | 0 | 0 | 0 | 217.5814 | 0 | 1144.714 | 89.82% | 4.8918 | 0 | 50 | 100% | 42.9
3733 | 947 | 1051 | 129 | 7.052 | 28 | 476.6416 | 270.977 | 41.9296 | 235.9996 | 107.2 | 32.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 235.9996 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.8
3734 | 935 | 980 | 109 | 4.8357 | 28.5 | 470.6018 | 0 | 302.0219 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
3735 | 740 | 841 | 213 | 9.6714 | 28.5 | 372.4549 | 0 | 230.6696 | 0 | 95.1386 | 26.6693 | 0 | 68.4693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
3736 | 376 | 586 | 309 | 11.6862 | 27.5 | 189.2473 | 0 | 110.9229 | 0 | 47.7892 | 3.1946 | 0 | 44.5946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.4
3737 | 296 | 409 | 244 | 8.8654 | 26.6 | 148.9819 | 0 | 78.5767 | 0 | 28.3297 | 0 | 0 | 28.3297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 13.4703 | 36.2381 | 72.48% | 41.8
3738 | 27 | 154 | 142 | 6.8506 | 25.4 | 13.5896 | 0 | 5.8097 | 0 | 9.9487 | 0 | 0 | 9.9487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.6962 | 21.39% | 34.9487
3739 | 37 | 67 | 59 | 4.2312 | 24.4 | 18.6227 | 0 | 0 | 0 | 3.5309 | 0 | 0 | 3.5309 | 0 | 0 | 0 | 70.1397 | 26.699 | 0 | 70.1397 | 1210.077 | 94.94% | 0 | 10.4701 | 0 | 0% | 40.7
3740 | 2 | 6 | 6 | 3.2238 | 23.1 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4165 | 37.5 | 0 | 95.4165 | 1118.2943 | 87.74% | 0 | 0 | 0 | 0% | 37.5
3741 | 0 | 0 | 0 | 3.8283 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0027 | 35.8 | 0 | 91.0027 | 1031.2848 | 80.92% | 0 | 0 | 0 | 0% | 35.8
3742 | 0 | 0 | 0 | 2.0149 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5075 | 34 | 0 | 86.5075 | 949.3977 | 74.49% | 0 | 0 | 0 | 0% | 34
3743 | 0 | 0 | 0 | 3.6268 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6045 | 32.8 | 0 | 83.6045 | 870.9419 | 68.34% | 0 | 0 | 0 | 0% | 32.8
3744 | 0 | 0 | 0 | 3.4253 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9703 | 32.2 | 0 | 81.9703 | 794.1783 | 62.31% | 0 | 0 | 0 | 0% | 32.2
3745 | 0 | 0 | 0 | 3.2238 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8885 | 32.2 | 0 | 81.8885 | 717.4032 | 56.29% | 0 | 0 | 0 | 0% | 32.2
3746 | 0 | 0 | 0 | 4.2312 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.546 | 32.5 | 0 | 82.546 | 639.7655 | 50.2% | 0 | 0 | 0 | 0% | 32.5
3747 | 0 | 0 | 0 | 3.0223 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.763 | 34.8 | 0 | 87.763 | 555.4923 | 43.58% | 0 | 0 | 0 | 0% | 34.8
3748 | 0 | 0 | 0 | 1.6119 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2811 | 38 | 0 | 95.2811 | 462.1748 | 36.26% | 0 | 0 | 0 | 0% | 38
3749 | 0 | 1 | 1 | 1.4104 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.867 | 40.8 | 0 | 101.867 | 360.8358 | 28.31% | 0 | 0 | 0 | 0% | 40.8
3750 | 303 | 73 | 30 | 1.4104 | 15.6 | 152.5052 | 0 | 57.4937 | 0 | 1.4764 | 0 | 0 | 1.4764 | 0 | 0 | 0 | 101.4768 | 40.5236 | 0 | 101.4768 | 260.249 | 20.42% | 0 | 0 | 0 | 0% | 42
3751 | 642 | 260 | 61 | 0.40297 | 20.3 | 323.1298 | 159.6603 | 0 | 131.9448 | 6.2307 | 0 | 0 | 6.2307 | 0 | 0 | 0 | 92.9593 | 36.6693 | 131.9448 | 92.9593 | 295.674 | 23.2% | 0 | 0 | 0 | 0% | 42.9
3752 | 791 | 469 | 78 | 2.2164 | 22.5 | 398.1241 | 226.8094 | 0 | 194.1743 | 28.1228 | 0 | 0 | 28.1228 | 0 | 0 | 0 | 0 | 0 | 194.1743 | 0 | 479.8122 | 37.65% | 0 | 0 | 0 | 0% | 28.1228
3753 | 872 | 665 | 87 | 6.6491 | 23.7 | 438.8928 | 267.5388 | 0 | 230.1652 | 58.3117 | 0 | 7.1058 | 51.2058 | 0 | 0 | 0 | 0 | 0 | 230.1652 | 0 | 698.081 | 54.77% | 5.4502 | 0 | 5.5698 | 11.14% | 44.1
3754 | 926 | 833 | 88 | 7.455 | 24.5 | 466.0719 | 295.618 | 0 | 256.1647 | 91.7311 | 0 | 23.6655 | 68.0655 | 0 | 0 | 0 | 0 | 0 | 256.1647 | 0 | 941.0055 | 73.83% | 18.1515 | 0 | 24.1196 | 48.24% | 44.4
3755 | 951 | 951 | 88 | 6.0446 | 25.6 | 478.6548 | 311.8858 | 0 | 272.1264 | 106.8 | 6.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 272.1264 | 0 | 1199.0668 | 94.08% | 19.175 | 0 | 43.7154 | 87.43% | 43.2
3756 | 944 | 1013 | 102 | 7.2535 | 26.4 | 475.1316 | 144.6724 | 169.1043 | 125.9529 | 107.5 | 24.4823 | 8.0177 | 75 | 0 | 0 | 0 | 0 | 0 | 125.9529 | 0 | 1274.5104 | 100% | 6.1496 | 0 | 50 | 100% | 42.5
3757 | 946 | 1019 | 99 | 8.6639 | 26.7 | 476.1382 | 0 | 312.5536 | 0 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
3758 | 950 | 974 | 93 | 10.4773 | 26.4 | 478.1515 | 0 | 306.8171 | 0 | 107.7 | 32.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
3759 | 937 | 872 | 87 | 9.8729 | 26.9 | 471.6084 | 0 | 292.025 | 0 | 101.6138 | 29.8569 | 0 | 71.7569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.9
3760 | 915 | 724 | 77 | 11.4848 | 26.7 | 460.5354 | 0 | 269.8875 | 0 | 71.8441 | 15.0721 | 0 | 56.7721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
3761 | 850 | 533 | 69 | 12.8952 | 26.1 | 427.8198 | 0 | 225.6208 | 0 | 35.195 | 0 | 0 | 35.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.705 | 43.1489 | 86.3% | 41.9
3762 | 732 | 323 | 57 | 11.4848 | 25.4 | 368.4283 | 0 | 157.5422 | 0 | 10.8899 | 0 | 0 | 10.8899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.6037 | 35.21% | 35.8899
3763 | 479 | 121 | 34 | 8.4625 | 24.5 | 241.089 | 0 | 0 | 0 | 1.8049 | 0 | 0 | 1.8049 | 0 | 0 | 0 | 59.1265 | 21.8667 | 0 | 59.1265 | 1220.6672 | 95.78% | 0 | 17.2284 | 0 | 0% | 40.9
3764 | 17 | 5 | 4 | 4.8357 | 22.4 | 8.5564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7686 | 37.7 | 0 | 95.7686 | 1128.3075 | 88.53% | 0 | 0 | 0 | 0% | 37.7
3765 | 0 | 0 | 0 | 2.2164 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6463 | 36.1 | 0 | 91.6463 | 1040.4496 | 81.64% | 0 | 0 | 0 | 0% | 36.1
3766 | 0 | 0 | 0 | 2.6193 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0241 | 34.3 | 0 | 87.0241 | 957.6861 | 75.14% | 0 | 0 | 0 | 0% | 34.3
3767 | 0 | 0 | 0 | 1.0074 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8187 | 33.1 | 0 | 83.8187 | 878.3663 | 68.92% | 0 | 0 | 0 | 0% | 33.1
3768 | 0 | 0 | 0 | 1.6119 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2836 | 32.5 | 0 | 82.2836 | 800.7447 | 62.83% | 0 | 0 | 0 | 0% | 32.5
3769 | 0 | 0 | 0 | 2.0149 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8159 | 32.4 | 0 | 81.8159 | 723.3953 | 56.76% | 0 | 0 | 0 | 0% | 32.4
3770 | 0 | 0 | 0 | 1.4104 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9717 | 32.9 | 0 | 82.9717 | 644.6109 | 50.58% | 0 | 0 | 0 | 0% | 32.9
3771 | 0 | 0 | 0 | 3.0223 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4309 | 35.2 | 0 | 88.4309 | 559.1884 | 43.87% | 0 | 0 | 0 | 0% | 35.2
3772 | 0 | 0 | 0 | 2.6193 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8013 | 38.3 | 0 | 95.8013 | 465.0049 | 36.48% | 0 | 0 | 0 | 0% | 38.3
3773 | 0 | 1 | 1 | 3.8283 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.0786 | 40.9 | 0 | 102.0786 | 363.373 | 28.51% | 0 | 0 | 0 | 0% | 40.9
3774 | 185 | 66 | 38 | 3.4253 | 16.2 | 93.1137 | 0 | 35.1994 | 0 | 1.9444 | 0 | 0 | 1.9444 | 0 | 0 | 0 | 101.3928 | 40.4556 | 0 | 101.3928 | 262.9675 | 20.63% | 0 | 0 | 0 | 0% | 42.4
3775 | 455 | 220 | 77 | 1.6119 | 18.6 | 229.0094 | 113.3105 | 0 | 88.2101 | 6.7199 | 0 | 0 | 6.7199 | 0 | 0 | 0 | 92.022 | 36.3801 | 88.2101 | 92.022 | 257.8126 | 20.23% | 0 | 0 | 0 | 0% | 43.1
3776 | 731 | 457 | 93 | 1.8134 | 21.6 | 367.925 | 209.7293 | 0 | 178.3584 | 27.6055 | 0 | 0 | 27.6055 | 0 | 0 | 0 | 0 | 0 | 178.3584 | 0 | 427.0437 | 33.51% | 0 | 0 | 0 | 0% | 27.6055
3777 | 829 | 654 | 103 | 3.0223 | 23.2 | 417.2501 | 254.3633 | 0 | 219.5268 | 54.7881 | 0 | 5.1441 | 49.6441 | 0 | 0 | 0 | 0 | 0 | 219.5268 | 0 | 635.3366 | 49.85% | 3.9455 | 0 | 4.0326 | 8.065% | 44.5
3778 | 877 | 817 | 110 | 3.8283 | 25.1 | 441.4093 | 279.9941 | 0 | 243.2931 | 85.9602 | 0 | 20.6801 | 65.2801 | 0 | 0 | 0 | 0 | 0 | 243.2931 | 0 | 866.1795 | 67.96% | 15.8616 | 0 | 20.2447 | 40.49% | 44.6
3779 | 908 | 936 | 112 | 4.8357 | 26.5 | 457.0122 | 297.7903 | 0 | 259.7297 | 106.8 | 6.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 259.7297 | 0 | 1112.618 | 87.3% | 19.175 | 0 | 39.8434 | 79.69% | 43.2
3780 | 908 | 997 | 120 | 9.4699 | 27 | 457.0122 | 246.26 | 55.527 | 212.753 | 107.8 | 19.8443 | 12.9557 | 75 | 0 | 0 | 0 | 0 | 0 | 212.753 | 0 | 1274.5104 | 100% | 9.937 | 0 | 50 | 100% | 42.2
3781 | 899 | 1000 | 124 | 7.2535 | 27.5 | 452.4823 | 0 | 297.0035 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42
3782 | 890 | 949 | 119 | 4.6342 | 28.1 | 447.9525 | 0 | 287.3929 | 0 | 108.2 | 33.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
3783 | 864 | 845 | 117 | 6.2461 | 28.4 | 434.8662 | 0 | 269.2254 | 0 | 94.656 | 26.678 | 0 | 67.978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.3
3784 | 813 | 690 | 111 | 5.0372 | 29 | 409.197 | 0 | 239.7601 | 0 | 64.5758 | 11.8379 | 0 | 52.7379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.9
3785 | 733 | 502 | 100 | 7.858 | 28.7 | 368.9316 | 0 | 194.5404 | 0 | 33.0206 | 0 | 0 | 33.0206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.6794 | 42.1521 | 84.3% | 40.7
3786 | 596 | 298 | 79 | 9.2684 | 27.9 | 299.9772 | 0 | 128.2911 | 0 | 10.9385 | 0 | 0 | 10.9385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.6032 | 33.21% | 35.9385
3787 | 358 | 112 | 46 | 8.261 | 26.6 | 180.1876 | 0 | 0 | 0 | 2.4355 | 0 | 0 | 2.4355 | 0 | 0 | 0 | 57.0828 | 20.8175 | 0 | 57.0828 | 1222.6406 | 95.93% | 0 | 16.247 | 0 | 0% | 39.5
3788 | 15 | 7 | 6 | 8.261 | 23.9 | 7.5498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6202 | 36.7 | 0 | 93.6202 | 1133.0406 | 88.9% | 0 | 0 | 0 | 0% | 36.7
3789 | 0 | 0 | 0 | 6.8506 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0146 | 35.4 | 0 | 90.0146 | 1047.1384 | 82.16% | 0 | 0 | 0 | 0% | 35.4
3790 | 0 | 0 | 0 | 7.455 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.455 | 33.6 | 0 | 85.455 | 966.3961 | 75.82% | 0 | 0 | 0 | 0% | 33.6
3791 | 0 | 0 | 0 | 6.8506 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5524 | 32 | 0 | 81.5524 | 890.2011 | 69.85% | 0 | 0 | 0 | 0% | 32
3792 | 0 | 0 | 0 | 8.8654 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3094 | 31.1 | 0 | 79.3094 | 816.4904 | 64.06% | 0 | 0 | 0 | 0% | 31.1
3793 | 0 | 0 | 0 | 9.6714 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8475 | 30.6 | 0 | 77.8475 | 744.1943 | 58.39% | 0 | 0 | 0 | 0% | 30.6
3794 | 0 | 0 | 0 | 7.6565 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.804 | 30.6 | 0 | 77.804 | 671.8872 | 52.72% | 0 | 0 | 0 | 0% | 30.6
3795 | 0 | 0 | 0 | 7.6565 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5544 | 30.5 | 0 | 77.5544 | 599.8459 | 47.06% | 0 | 0 | 0 | 0% | 30.5
3796 | 0 | 0 | 0 | 2.8208 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4258 | 31.3 | 0 | 79.4258 | 525.5606 | 41.24% | 0 | 0 | 0 | 0% | 31.3
3797 | 0 | 1 | 1 | 2.6193 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3915 | 33.8 | 0 | 85.3915 | 444.1512 | 34.85% | 0 | 0 | 0 | 0% | 33.8
3798 | 264 | 70 | 32 | 2.8208 | 17 | 132.8758 | 0 | 50.3639 | 0 | 1.613 | 0 | 0 | 1.613 | 0 | 0 | 0 | 88.6307 | 35.087 | 0 | 88.6307 | 358.9935 | 28.17% | 0 | 0 | 0 | 0% | 36.7
3799 | 589 | 252 | 67 | 4.0297 | 20.2 | 296.4539 | 146.8783 | 0 | 118.8867 | 6.4172 | 0 | 0 | 6.4172 | 0 | 0 | 0 | 82.3869 | 32.2828 | 118.8867 | 82.3869 | 392.9843 | 30.83% | 0 | 0 | 0 | 0% | 38.7
3800 | 740 | 457 | 88 | 11.2833 | 23.1 | 372.4549 | 212.4359 | 0 | 176.0522 | 27.7718 | 0 | 0 | 27.7718 | 0 | 0 | 0 | 0 | 0 | 176.0522 | 0 | 557.6092 | 43.75% | 0 | 0 | 0 | 0% | 27.7718
3801 | 815 | 647 | 103 | 14.3056 | 24.2 | 410.2037 | 250.0866 | 0 | 209.3015 | 60.6064 | 0 | 10.4532 | 50.1532 | 0 | 0 | 0 | 0 | 0 | 209.3015 | 0 | 753.3252 | 59.11% | 8.0176 | 0 | 8.1959 | 16.39% | 39.7
3802 | 850 | 807 | 118 | 13.9026 | 24.9 | 427.8198 | 271.3937 | 0 | 229.4364 | 92.7069 | 1.4035 | 25 | 66.3035 | 0 | 0 | 0 | 0 | 0 | 229.4364 | 0 | 967.8692 | 75.94% | 19.175 | 0 | 27.7974 | 55.59% | 39.9
3803 | 870 | 924 | 130 | 14.3056 | 25.1 | 437.8861 | 285.3354 | 0 | 242.3732 | 111.2 | 11.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 242.3732 | 0 | 1194.5103 | 93.72% | 19.175 | 0 | 47.3989 | 94.8% | 38.8
3804 | 875 | 989 | 140 | 14.5071 | 25.6 | 440.4027 | 156.6071 | 134.1909 | 133.2726 | 112.7 | 34.3825 | 3.3175 | 75 | 0 | 0 | 0 | 0 | 0 | 133.2726 | 0 | 1274.5104 | 100% | 2.5445 | 0 | 50 | 100% | 37.3
3805 | 851 | 990 | 158 | 15.5145 | 25.8 | 428.3231 | 0 | 281.1252 | 0 | 113.5 | 38.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.5
3806 | 846 | 947 | 157 | 15.9175 | 25.9 | 425.8065 | 0 | 273.1413 | 0 | 113.9 | 38.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.1
3807 | 817 | 837 | 147 | 16.9249 | 25.6 | 411.2103 | 0 | 254.5342 | 0 | 104.1831 | 34.2415 | 0 | 69.9415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.7
3808 | 769 | 686 | 136 | 16.7234 | 25.3 | 387.0511 | 0 | 226.7428 | 0 | 72.7992 | 18.4996 | 0 | 54.2996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.8
3809 | 681 | 500 | 124 | 16.119 | 24.4 | 342.7591 | 0 | 180.7118 | 0 | 33.7613 | 0 | 0 | 33.7613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.7613
3810 | 519 | 295 | 101 | 14.7085 | 22.7 | 261.2217 | 0 | 111.7245 | 0 | 12.157 | 0 | 0 | 12.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.4478 | 48.9% | 37.157
3811 | 211 | 100 | 56 | 13.2981 | 20.8 | 106.2 | 0 | 0 | 0 | 3.072 | 0 | 0 | 3.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.9195 | 0 | 0% | 26.9915
3812 | 2 | 5 | 4 | 11.2833 | 19.1 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7807 | 35 | 0 | 88.7807 | 1189.7057 | 93.35% | 0 | 0 | 0 | 0% | 35
3813 | 0 | 0 | 0 | 10.0743 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9024 | 32.6 | 0 | 82.9024 | 1111.8088 | 87.23% | 0 | 0 | 0 | 0% | 32.6
3814 | 0 | 0 | 0 | 8.8654 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7458 | 30.9 | 0 | 78.7458 | 1038.6874 | 81.5% | 0 | 0 | 0 | 0% | 30.9
3815 | 0 | 0 | 0 | 6.4476 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.6416 | 29.6 | 0 | 75.6416 | 968.8572 | 76.02% | 0 | 0 | 0 | 0% | 29.6
3816 | 0 | 0 | 0 | 3.8283 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7926 | 28.8 | 0 | 73.7926 | 900.801 | 70.68% | 0 | 0 | 0 | 0% | 28.8
3817 | 0 | 0 | 0 | 2.8208 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.879 | 28.4 | 0 | 72.879 | 833.6155 | 65.41% | 0 | 0 | 0 | 0% | 28.4
3818 | 0 | 0 | 0 | 2.2164 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2038 | 28.1 | 0 | 72.2038 | 767.0708 | 60.19% | 0 | 0 | 0 | 0% | 28.1
3819 | 0 | 0 | 0 | 2.2164 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1837 | 28.1 | 0 | 72.1837 | 700.5345 | 54.96% | 0 | 0 | 0 | 0% | 28.1
3820 | 0 | 0 | 0 | 2.0149 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0783 | 28.1 | 0 | 72.0783 | 634.0849 | 49.75% | 0 | 0 | 0 | 0% | 28.1
3821 | 0 | 1 | 1 | 1.2089 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.615 | 29.7 | 0 | 75.615 | 564.1231 | 44.26% | 0 | 0 | 0 | 0% | 29.7
3822 | 3 | 34 | 33 | 0.80595 | 15.4 | 1.51 | 0 | 0.57379 | 0 | 1.8959 | 0 | 0 | 1.8959 | 0 | 0 | 0 | 76.0172 | 29.9041 | 0 | 76.0172 | 493.6478 | 38.73% | 0 | 0 | 0 | 0% | 31.8
3823 | 169 | 198 | 141 | 4.0297 | 18 | 85.0606 | 0 | 42.1987 | 0 | 9.9885 | 0 | 0 | 9.9885 | 0 | 0 | 0 | 62.8788 | 23.9115 | 0 | 62.8788 | 436.0276 | 34.21% | 0 | 0 | 0 | 0% | 33.9
3824 | 72 | 342 | 303 | 4.2312 | 19.7 | 36.2389 | 0 | 20.6814 | 0 | 23.8704 | 0 | 0 | 23.8704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.0276 | 34.21% | 0 | 0 | 0 | 0% | 23.8704
3825 | 28 | 342 | 319 | 3.8283 | 20.7 | 14.0929 | 0 | 8.5926 | 0 | 25.0089 | 0 | 0 | 25.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.0276 | 34.21% | 0 | 0 | 0 | 0% | 25.0089
3826 | 165 | 454 | 311 | 3.4253 | 22 | 83.0474 | 0 | 52.6864 | 0 | 34.9505 | 0 | 0 | 34.9505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.0276 | 34.21% | 0 | 0 | 0 | 0% | 34.9505
3827 | 441 | 731 | 315 | 2.4178 | 24.4 | 221.963 | 144.64 | 0 | 117.3371 | 81.0995 | 0 | 22.6497 | 58.4497 | 0 | 0 | 0 | 0 | 0 | 117.3371 | 0 | 544.5092 | 42.72% | 17.3723 | 0 | 17.7613 | 35.52% | 35.8
3828 | 516 | 855 | 344 | 4.4327 | 26.6 | 259.7118 | 171.4763 | 0 | 141.7462 | 105.0019 | 10.451 | 25 | 69.551 | 0 | 0 | 0 | 0 | 0 | 141.7462 | 0 | 675.5578 | 53.01% | 19.175 | 0 | 37.3657 | 74.73% | 34.1
3829 | 750 | 978 | 242 | 8.0595 | 27.4 | 377.488 | 247.7421 | 0 | 210.9513 | 116.8 | 25.6884 | 16.1116 | 75 | 0 | 0 | 0 | 0 | 0 | 210.9513 | 0 | 870.5885 | 68.31% | 12.3576 | 0 | 50 | 100% | 33.2
3830 | 768 | 916 | 195 | 8.8654 | 28.3 | 386.5478 | 247.9193 | 0 | 210.6582 | 117.1 | 42.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 210.6582 | 0 | 1065.3482 | 83.59% | 0 | 0 | 50 | 100% | 32.9
3831 | 763 | 838 | 188 | 10.2758 | 28.3 | 384.0312 | 237.6679 | 0 | 200.3765 | 103.608 | 35.404 | 0 | 68.204 | 0 | 0 | 0 | 0 | 0 | 200.3765 | 0 | 1250.6022 | 98.12% | 0 | 0 | 50 | 100% | 32.8
3832 | 715 | 677 | 164 | 10.4773 | 28.1 | 359.8719 | 0 | 210.7804 | 0 | 71.8897 | 19.2949 | 0 | 52.5949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.6022 | 98.12% | 0 | 0 | 50 | 100% | 33.3
3833 | 647 | 495 | 134 | 10.8803 | 27.4 | 325.6463 | 0 | 171.6586 | 0 | 32.8776 | 0 | 0 | 32.8776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.6022 | 98.12% | 0 | 0 | 50 | 100% | 32.8776
3834 | 468 | 284 | 108 | 11.0818 | 25.7 | 235.5525 | 0 | 100.7454 | 0 | 11.8497 | 0 | 0 | 11.8497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.6022 | 98.12% | 0 | 24.3503 | 25.1082 | 50.22% | 36.2
3835 | 169 | 90 | 53 | 9.8729 | 23.3 | 85.0606 | 0 | 0 | 0 | 2.9905 | 0 | 0 | 2.9905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.6022 | 98.12% | 0 | 24.5621 | 0 | 0% | 27.5527
3836 | 6 | 5 | 5 | 6.0446 | 21.1 | 3.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3261 | 34.7 | 0 | 88.3261 | 1166.6325 | 91.54% | 0 | 0 | 0 | 0% | 34.7
3837 | 0 | 0 | 0 | 3.6268 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5564 | 32.8 | 0 | 83.5564 | 1088.1291 | 85.38% | 0 | 0 | 0 | 0% | 32.8
3838 | 0 | 0 | 0 | 1.4104 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1146 | 31 | 0 | 79.1146 | 1014.6059 | 79.61% | 0 | 0 | 0 | 0% | 31
3839 | 0 | 0 | 0 | 1.0074 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.4052 | 29.9 | 0 | 76.4052 | 944.008 | 74.07% | 0 | 0 | 0 | 0% | 29.9
3840 | 0 | 0 | 0 | 2.0149 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3239 | 29.4 | 0 | 75.3239 | 874.4486 | 68.61% | 0 | 0 | 0 | 0% | 29.4
3841 | 0 | 0 | 0 | 1.6119 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.0284 | 29.3 | 0 | 75.0284 | 805.1619 | 63.17% | 0 | 0 | 0 | 0% | 29.3
3842 | 0 | 0 | 0 | 2.4178 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.79 | 30.1 | 0 | 76.79 | 734.128 | 57.6% | 0 | 0 | 0 | 0% | 30.1
3843 | 0 | 0 | 0 | 2.4178 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0441 | 32.7 | 0 | 83.0441 | 655.8436 | 51.46% | 0 | 0 | 0 | 0% | 32.7
3844 | 0 | 0 | 0 | 1.2089 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8202 | 36 | 0 | 90.8202 | 568.107 | 44.57% | 0 | 0 | 0 | 0% | 36
3845 | 0 | 1 | 1 | 2.8208 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5908 | 38.8 | 0 | 97.5908 | 472.4038 | 37.07% | 0 | 0 | 0 | 0% | 38.8
3846 | 44 | 51 | 45 | 2.6193 | 17.7 | 22.146 | 0 | 8.4365 | 0 | 2.4945 | 0 | 0 | 2.4945 | 0 | 0 | 0 | 95.7633 | 38.0055 | 0 | 95.7633 | 378.9558 | 29.73% | 0 | 0 | 0 | 0% | 40.5
3847 | 514 | 240 | 70 | 1.4104 | 21.3 | 258.7051 | 128.5084 | 0 | 102.4372 | 6.2299 | 0 | 0 | 6.2299 | 0 | 0 | 0 | 90.2039 | 35.4701 | 102.4372 | 90.2039 | 388.6337 | 30.49% | 0 | 0 | 0 | 0% | 41.7
3848 | 809 | 472 | 71 | 1.2089 | 24.6 | 407.1838 | 232.5115 | 0 | 199.8941 | 27.3574 | 0 | 0 | 27.3574 | 0 | 0 | 0 | 0 | 0 | 199.8941 | 0 | 576.1782 | 45.21% | 0 | 0 | 0 | 0% | 27.3574
3849 | 873 | 662 | 83 | 6.0446 | 25.6 | 439.3961 | 267.9304 | 0 | 230.9299 | 57.2618 | 0 | 7.0809 | 50.1809 | 0 | 0 | 0 | 0 | 0 | 230.9299 | 0 | 792.841 | 62.21% | 5.4311 | 0 | 5.5534 | 11.11% | 43.1
3850 | 916 | 827 | 88 | 9.6714 | 26.9 | 461.0387 | 292.5136 | 0 | 252.0208 | 90.5219 | 0 | 23.511 | 67.011 | 0 | 0 | 0 | 0 | 0 | 252.0208 | 0 | 1029.2918 | 80.76% | 18.0329 | 0 | 23.9927 | 47.99% | 43.5
3851 | 950 | 951 | 88 | 8.0595 | 27.5 | 478.1515 | 311.5937 | 0 | 270.6839 | 107.5 | 7.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 270.6839 | 0 | 1274.5104 | 100% | 19.175 | 0 | 43.5999 | 87.2% | 42.5
3852 | 953 | 1013 | 92 | 5.0372 | 28.2 | 479.6615 | 0 | 316.6804 | 0 | 108.4 | 25.2395 | 8.1605 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 6.2591 | 0 | 50 | 100% | 41.6
3853 | 934 | 1016 | 106 | 7.858 | 28.7 | 470.0984 | 0 | 308.4989 | 0 | 108.6 | 33.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.4
3854 | 911 | 965 | 116 | 10.2758 | 28.7 | 458.5221 | 0 | 294.0362 | 0 | 108.9 | 33.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
3855 | 887 | 853 | 105 | 8.6639 | 28.8 | 446.4425 | 0 | 276.2432 | 0 | 97.682 | 28.591 | 0 | 69.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.5
3856 | 854 | 705 | 95 | 10.6788 | 28.7 | 429.833 | 0 | 251.7074 | 0 | 68.8962 | 14.3981 | 0 | 54.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.1
3857 | 801 | 522 | 80 | 12.0892 | 28.1 | 403.1572 | 0 | 212.4731 | 0 | 34.1338 | 0 | 0 | 34.1338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.5662 | 43.2868 | 86.57% | 40.7
3858 | 644 | 316 | 76 | 11.6862 | 27.6 | 324.1364 | 0 | 138.6216 | 0 | 11.3315 | 0 | 0 | 11.3315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.7269 | 35.45% | 36.3315
3859 | 418 | 127 | 49 | 9.2684 | 26.4 | 210.3867 | 0 | 0 | 0 | 2.6458 | 0 | 0 | 2.6458 | 0 | 0 | 0 | 55.6043 | 20.2152 | 0 | 55.6043 | 1224.0179 | 96.04% | 0 | 17.339 | 0 | 0% | 40.2
3860 | 25 | 9 | 7 | 5.6416 | 24.5 | 12.5829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9769 | 36.8 | 0 | 93.9769 | 1133.9845 | 88.97% | 0 | 0 | 0 | 0% | 36.8
3861 | 0 | 0 | 0 | 3.8283 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8118 | 35.2 | 0 | 89.8118 | 1048.5058 | 82.27% | 0 | 0 | 0 | 0% | 35.2
3862 | 0 | 0 | 0 | 2.6193 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5646 | 33.6 | 0 | 85.5646 | 967.7156 | 75.93% | 0 | 0 | 0 | 0% | 33.6
3863 | 0 | 0 | 0 | 1.8134 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3788 | 32.3 | 0 | 82.3788 | 890.5846 | 69.88% | 0 | 0 | 0 | 0% | 32.3
3864 | 0 | 0 | 0 | 2.0149 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8803 | 31.7 | 0 | 80.8803 | 815.109 | 63.95% | 0 | 0 | 0 | 0% | 31.7
3865 | 0 | 0 | 0 | 3.6268 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6252 | 31.6 | 0 | 80.6252 | 739.9039 | 58.05% | 0 | 0 | 0 | 0% | 31.6
3866 | 0 | 0 | 0 | 1.8134 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6798 | 32.1 | 0 | 81.6798 | 663.3478 | 52.05% | 0 | 0 | 0 | 0% | 32.1
3867 | 0 | 0 | 0 | 3.6268 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4515 | 34.5 | 0 | 87.4515 | 579.8917 | 45.5% | 0 | 0 | 0 | 0% | 34.5
3868 | 0 | 0 | 0 | 1.2089 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4974 | 37.9 | 0 | 95.4974 | 486.7953 | 38.19% | 0 | 0 | 0 | 0% | 37.9
3869 | 0 | 1 | 1 | 1.6119 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.6709 | 40.9 | 0 | 102.6709 | 385.1044 | 30.22% | 0 | 0 | 0 | 0% | 40.9
3870 | 339 | 75 | 26 | 1.4104 | 18.7 | 170.6246 | 65.1557 | 0 | 43.0177 | 1.1691 | 0 | 0 | 1.1691 | 0 | 0 | 0 | 103.1885 | 41.0309 | 43.0177 | 103.1885 | 323.5732 | 25.39% | 0 | 0 | 0 | 0% | 42.2
3871 | 689 | 265 | 49 | 2.2164 | 22.2 | 346.7857 | 172.4764 | 0 | 143.3907 | 5.4937 | 0 | 0 | 5.4937 | 0 | 0 | 0 | 95.5032 | 37.6063 | 143.3907 | 95.5032 | 366.8832 | 28.79% | 0 | 0 | 0 | 0% | 43.1
3872 | 831 | 473 | 60 | 6.2461 | 24.4 | 418.2567 | 238.9347 | 0 | 203.84 | 27.6437 | 0 | 0 | 27.6437 | 0 | 0 | 0 | 0 | 0 | 203.84 | 0 | 559.8842 | 43.93% | 0 | 0 | 0 | 0% | 27.6437
3873 | 905 | 666 | 66 | 6.8506 | 26.4 | 455.5022 | 277.7781 | 0 | 239.7221 | 56.467 | 0 | 6.1835 | 50.2835 | 0 | 0 | 0 | 0 | 0 | 239.7221 | 0 | 786.8593 | 61.74% | 4.7427 | 0 | 4.8503 | 9.701% | 44.1
3874 | 948 | 831 | 68 | 5.4401 | 27.2 | 477.1449 | 302.7588 | 0 | 264.03 | 88.5203 | 0 | 22.2601 | 66.2601 | 0 | 0 | 0 | 0 | 0 | 264.03 | 0 | 1036.8497 | 81.35% | 17.0735 | 0 | 22.3111 | 44.62% | 44
3875 | 956 | 943 | 75 | 6.2461 | 28.5 | 481.1714 | 313.574 | 0 | 273.6274 | 107.4 | 7.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 273.6274 | 0 | 1274.5104 | 100% | 19.175 | 0 | 41.9211 | 83.84% | 42.6
3876 | 955 | 1005 | 83 | 9.4699 | 28.9 | 480.6681 | 0 | 317.3278 | 0 | 108.1 | 22.8005 | 10.2995 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 7.8997 | 0 | 50 | 100% | 41.9
3877 | 950 | 1014 | 90 | 9.8729 | 29.4 | 478.1515 | 0 | 313.7608 | 0 | 108.3 | 33.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
3878 | 935 | 962 | 90 | 6.2461 | 29.7 | 470.6018 | 0 | 301.7371 | 0 | 108.4 | 33.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
3879 | 909 | 857 | 90 | 7.858 | 30.2 | 457.5155 | 0 | 283.0442 | 0 | 96.5308 | 27.6654 | 0 | 68.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
3880 | 768 | 691 | 140 | 9.4699 | 30.5 | 386.5478 | 0 | 226.3132 | 0 | 64.9124 | 11.8562 | 0 | 53.0562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
3881 | 720 | 519 | 122 | 9.4699 | 30 | 362.3885 | 0 | 190.9426 | 0 | 34.1739 | 0 | 0 | 34.1739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.4261 | 42.4066 | 84.81% | 41.6
3882 | 657 | 315 | 69 | 8.6639 | 28.9 | 330.6795 | 0 | 141.3983 | 0 | 10.9067 | 0 | 0 | 10.9067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.843 | 33.69% | 35.9067
3883 | 310 | 108 | 52 | 8.261 | 24.9 | 156.0284 | 0 | 0 | 0 | 2.7541 | 0 | 0 | 2.7541 | 0 | 0 | 0 | 57.8154 | 21.2739 | 0 | 57.8154 | 1221.9133 | 95.87% | 0 | 16.472 | 0 | 0% | 40.5
3884 | 9 | 7 | 6 | 11.6862 | 20.4 | 4.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7392 | 37.4 | 0 | 94.7392 | 1130.3821 | 88.69% | 0 | 0 | 0 | 0% | 37.4
3885 | 0 | 0 | 0 | 15.9175 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5918 | 35.8 | 0 | 90.5918 | 1043.3425 | 81.86% | 0 | 0 | 0 | 0% | 35.8
3886 | 0 | 0 | 0 | 16.119 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.441 | 34.1 | 0 | 86.441 | 961.1383 | 75.41% | 0 | 0 | 0 | 0% | 34.1
3887 | 0 | 0 | 0 | 14.91 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9944 | 32.7 | 0 | 82.9944 | 882.9405 | 69.28% | 0 | 0 | 0 | 0% | 32.7
3888 | 0 | 0 | 0 | 13.9026 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9379 | 32.3 | 0 | 81.9379 | 805.8678 | 63.23% | 0 | 0 | 0 | 0% | 32.3
3889 | 0 | 0 | 0 | 13.2981 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6506 | 32.2 | 0 | 81.6506 | 729.0668 | 57.2% | 0 | 0 | 0 | 0% | 32.2
3890 | 0 | 0 | 0 | 10.2758 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2747 | 32.9 | 0 | 83.2747 | 650.2637 | 51.02% | 0 | 0 | 0 | 0% | 32.9
3891 | 0 | 0 | 0 | 9.4699 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4867 | 35.1 | 0 | 88.4867 | 565.0992 | 44.34% | 0 | 0 | 0 | 0% | 35.1
3892 | 0 | 0 | 0 | 10.6788 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5918 | 38.5 | 0 | 96.5918 | 470.3209 | 36.9% | 0 | 0 | 0 | 0% | 38.5
3893 | 0 | 1 | 1 | 8.261 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.5037 | 41.4 | 0 | 103.5037 | 367.2507 | 28.82% | 0 | 0 | 0 | 0% | 41.4
3894 | 9 | 42 | 41 | 7.052 | 15.5 | 4.5299 | 0 | 1.7338 | 0 | 2.3943 | 0 | 0 | 2.3943 | 0 | 0 | 0 | 100.702 | 40.2057 | 0 | 100.702 | 267.5246 | 20.99% | 0 | 0 | 0 | 0% | 42.6
3895 | 495 | 258 | 100 | 9.4699 | 17 | 249.1421 | 124.0631 | 0 | 94.3408 | 8.2913 | 0 | 0 | 8.2913 | 0 | 0 | 0 | 69.7265 | 26.9858 | 94.3408 | 69.7265 | 292.7111 | 22.97% | 0 | 0 | 0 | 0% | 35.2771
3896 | 495 | 443 | 203 | 10.4773 | 18 | 249.1421 | 142.365 | 0 | 110.9022 | 29.3944 | 0 | 0 | 29.3944 | 0 | 0 | 0 | 0 | 0 | 110.9022 | 0 | 397.6092 | 31.2% | 0 | 0 | 0 | 0% | 29.3944
3897 | 358 | 499 | 256 | 10.6788 | 18.9 | 180.1876 | 109.8948 | 0 | 80.3044 | 38.5447 | 0 | 0 | 38.5447 | 0 | 0 | 0 | 0 | 0 | 80.3044 | 0 | 473.566 | 37.16% | 0 | 0 | 0 | 0% | 38.5447
3898 | 708 | 752 | 175 | 10.2758 | 20.2 | 356.3487 | 226.1319 | 0 | 189.3689 | 80.2337 | 0 | 17.8668 | 62.3668 | 0 | 0 | 0 | 0 | 0 | 189.3689 | 0 | 652.6828 | 51.21% | 13.7039 | 0 | 14.0167 | 28.03% | 44.5
3899 | 924 | 938 | 106 | 10.2758 | 21.2 | 465.0653 | 303.0909 | 0 | 261.3014 | 107 | 7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 261.3014 | 0 | 899.8378 | 70.6% | 19.175 | 0 | 33.6295 | 67.26% | 43
3900 | 943 | 999 | 99 | 11.4848 | 21.8 | 474.6283 | 313.3253 | 0 | 270.087 | 107.7 | 11.833 | 20.867 | 75 | 0 | 0 | 0 | 0 | 0 | 270.087 | 0 | 1155.3027 | 90.65% | 16.005 | 0 | 50 | 100% | 42.3
3901 | 942 | 1006 | 101 | 12.2907 | 22.7 | 474.125 | 311.096 | 0 | 267.5492 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 267.5492 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
3902 | 930 | 956 | 102 | 13.0966 | 23.2 | 468.0852 | 0 | 300.0794 | 0 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
3903 | 900 | 858 | 100 | 12.0892 | 23.7 | 452.9856 | 0 | 280.192 | 0 | 101.3347 | 29.9174 | 0 | 71.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.5
3904 | 850 | 705 | 97 | 12.8952 | 23.2 | 427.8198 | 0 | 250.4235 | 0 | 70.0363 | 14.3182 | 0 | 55.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.4
3905 | 784 | 518 | 84 | 12.6937 | 22.5 | 394.6008 | 0 | 207.8616 | 0 | 34.6426 | 0 | 0 | 34.6426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.9574 | 42.8849 | 85.77% | 41.6
3906 | 653 | 312 | 68 | 13.4996 | 21.5 | 328.6663 | 0 | 140.5058 | 0 | 11.1781 | 0 | 0 | 11.1781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.3175 | 34.64% | 36.1781
3907 | 373 | 115 | 42 | 13.7011 | 19.8 | 187.7374 | 0 | 0 | 0 | 2.1976 | 0 | 0 | 2.1976 | 0 | 0 | 0 | 58.1423 | 21.7687 | 0 | 58.1423 | 1221.5753 | 95.85% | 0 | 16.9337 | 0 | 0% | 40.9
3908 | 13 | 6 | 5 | 12.8952 | 17.9 | 6.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8203 | 37.6 | 0 | 94.8203 | 1129.5015 | 88.62% | 0 | 0 | 0 | 0% | 37.6
3909 | 0 | 0 | 0 | 10.6788 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8868 | 36 | 0 | 90.8868 | 1041.9255 | 81.75% | 0 | 0 | 0 | 0% | 36
3910 | 0 | 0 | 0 | 8.0595 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.629 | 34.2 | 0 | 86.629 | 959.4533 | 75.28% | 0 | 0 | 0 | 0% | 34.2
3911 | 0 | 0 | 0 | 7.052 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7159 | 33 | 0 | 83.7159 | 880.4207 | 69.08% | 0 | 0 | 0 | 0% | 33
3912 | 0 | 0 | 0 | 6.2461 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3941 | 32.5 | 0 | 82.3941 | 802.8006 | 62.99% | 0 | 0 | 0 | 0% | 32.5
3913 | 0 | 0 | 0 | 7.2535 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8903 | 32.3 | 0 | 81.8903 | 725.7363 | 56.94% | 0 | 0 | 0 | 0% | 32.3
3914 | 0 | 0 | 0 | 3.0223 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2616 | 32.9 | 0 | 83.2616 | 646.9536 | 50.76% | 0 | 0 | 0 | 0% | 32.9
3915 | 0 | 0 | 0 | 3.0223 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4342 | 35.1 | 0 | 88.4342 | 561.8112 | 44.08% | 0 | 0 | 0 | 0% | 35.1
3916 | 0 | 0 | 0 | 4.0297 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6109 | 38.5 | 0 | 96.6109 | 467.0579 | 36.65% | 0 | 0 | 0 | 0% | 38.5
3917 | 0 | 1 | 1 | 3.4253 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3015 | 41.3 | 0 | 103.3015 | 364.2983 | 28.58% | 0 | 0 | 0 | 0% | 41.3
3918 | 7 | 37 | 36 | 2.8208 | 15.5 | 3.5232 | 0 | 1.3515 | 0 | 2.0871 | 0 | 0 | 2.0871 | 0 | 0 | 0 | 100.9602 | 40.3129 | 0 | 100.9602 | 264.2967 | 20.74% | 0 | 0 | 0 | 0% | 42.4
3919 | 117 | 147 | 109 | 4.2312 | 18.1 | 58.8881 | 0 | 29.3586 | 0 | 7.7328 | 0 | 0 | 7.7328 | 0 | 0 | 0 | 89.7378 | 35.4672 | 0 | 89.7378 | 178.0466 | 13.97% | 0 | 0 | 0 | 0% | 43.2
3920 | 479 | 424 | 182 | 10.6788 | 20.7 | 241.089 | 137.8016 | 0 | 106.4985 | 27.0721 | 0 | 0 | 27.0721 | 0 | 0 | 0 | 0 | 0 | 106.4985 | 0 | 279.047 | 21.89% | 0 | 0 | 0 | 0% | 27.0721
3921 | 695 | 630 | 164 | 12.6937 | 21.9 | 349.8056 | 213.3665 | 0 | 176.0363 | 53.0567 | 0 | 4.2284 | 48.8284 | 0 | 0 | 0 | 0 | 0 | 176.0363 | 0 | 445.9952 | 34.99% | 3.2432 | 0 | 3.3177 | 6.635% | 44.6
3922 | 741 | 796 | 194 | 13.7011 | 23.5 | 372.9582 | 236.6948 | 0 | 197.3142 | 86.4031 | 0 | 20.8016 | 65.6016 | 0 | 0 | 0 | 0 | 0 | 197.3142 | 0 | 633.1228 | 49.68% | 15.9548 | 0 | 19.6391 | 39.28% | 44.8
3923 | 828 | 918 | 162 | 13.7011 | 25 | 416.7468 | 271.6138 | 0 | 229.768 | 106.5 | 6.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 229.768 | 0 | 851.0287 | 66.77% | 19.175 | 0 | 39.2547 | 78.51% | 43.5
3924 | 845 | 982 | 162 | 13.7011 | 25.9 | 425.3032 | 280.7515 | 0 | 238.4174 | 107.2 | 18.5052 | 13.6948 | 75 | 0 | 0 | 0 | 0 | 0 | 238.4174 | 0 | 1077.1375 | 84.51% | 10.5039 | 0 | 50 | 100% | 42.8
3925 | 848 | 989 | 159 | 14.3056 | 25.4 | 426.8131 | 280.0321 | 0 | 237.3571 | 107.3 | 32.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 237.3571 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.7
3926 | 856 | 944 | 143 | 13.9026 | 25.4 | 430.8397 | 0 | 276.1624 | 0 | 107.3 | 32.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.7
3927 | 810 | 839 | 152 | 12.0892 | 25.2 | 407.6871 | 0 | 252.1284 | 0 | 96.5073 | 27.1036 | 0 | 69.4036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
3928 | 715 | 685 | 170 | 11.4848 | 25.1 | 359.8719 | 0 | 210.6042 | 0 | 65.4078 | 11.6539 | 0 | 53.7539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
3929 | 545 | 475 | 167 | 11.6862 | 24.1 | 274.308 | 0 | 144.4548 | 0 | 32.0943 | 0 | 0 | 32.0943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 10.2057 | 39.5614 | 79.12% | 42.3
3930 | 306 | 245 | 121 | 10.4773 | 22.7 | 154.0151 | 0 | 65.8225 | 0 | 11.4223 | 0 | 0 | 11.4223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 13.9902 | 27.98% | 36.4223
3931 | 1 | 41 | 41 | 10.8803 | 20.6 | 0.50332 | 0 | 0 | 0 | 2.5647 | 0 | 0 | 2.5647 | 0 | 0 | 0 | 64.9073 | 24.6569 | 0 | 64.9073 | 1215.0616 | 95.34% | 0 | 13.6783 | 0 | 0% | 40.9
3932 | 0 | 3 | 3 | 9.4699 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.575 | 37.8 | 0 | 95.575 | 1122.4195 | 88.07% | 0 | 0 | 0 | 0% | 37.8
3933 | 0 | 0 | 0 | 8.4625 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.644 | 36.2 | 0 | 91.644 | 1034.2826 | 81.15% | 0 | 0 | 0 | 0% | 36.2
3934 | 0 | 0 | 0 | 6.2461 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4863 | 34.5 | 0 | 87.4863 | 950.9399 | 74.61% | 0 | 0 | 0 | 0% | 34.5
3935 | 0 | 0 | 0 | 4.4327 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.297 | 33.2 | 0 | 84.297 | 871.3351 | 68.37% | 0 | 0 | 0 | 0% | 33.2
3936 | 0 | 0 | 0 | 6.6491 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1103 | 32.7 | 0 | 83.1103 | 793.1461 | 62.23% | 0 | 0 | 0 | 0% | 32.7
3937 | 0 | 0 | 0 | 6.2461 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8198 | 32.6 | 0 | 82.8198 | 715.2298 | 56.12% | 0 | 0 | 0 | 0% | 32.6
3938 | 0 | 0 | 0 | 7.052 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0231 | 33.1 | 0 | 84.0231 | 635.8751 | 49.89% | 0 | 0 | 0 | 0% | 33.1
3939 | 0 | 0 | 0 | 6.4476 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2543 | 35.2 | 0 | 89.2543 | 550.4538 | 43.19% | 0 | 0 | 0 | 0% | 35.2
3940 | 0 | 0 | 0 | 4.6342 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0216 | 38.5 | 0 | 97.0216 | 455.6996 | 35.75% | 0 | 0 | 0 | 0% | 38.5
3941 | 0 | 1 | 1 | 4.8357 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2287 | 41.1 | 0 | 103.2287 | 353.5042 | 27.74% | 0 | 0 | 0 | 0% | 41.1
3942 | 83 | 50 | 36 | 5.4401 | 17.6 | 41.7753 | 0 | 16.0594 | 0 | 1.8995 | 0 | 0 | 1.8995 | 0 | 0 | 0 | 102.2117 | 40.7005 | 0 | 102.2117 | 252.4096 | 19.8% | 0 | 0 | 0 | 0% | 42.6
3943 | 455 | 233 | 88 | 4.4327 | 18.9 | 229.0094 | 114.3028 | 0 | 88.1965 | 7.154 | 0 | 0 | 7.154 | 0 | 0 | 0 | 92.2352 | 36.446 | 88.1965 | 92.2352 | 247.1315 | 19.39% | 0 | 0 | 0 | 0% | 43.6
3944 | 672 | 443 | 108 | 5.2387 | 20.7 | 338.2293 | 193.3787 | 0 | 161.7697 | 26.7654 | 0 | 0 | 26.7654 | 0 | 0 | 0 | 0 | 0 | 161.7697 | 0 | 400.7525 | 31.44% | 0 | 0 | 0 | 0% | 26.7654
3945 | 804 | 644 | 109 | 3.8283 | 23.3 | 404.6672 | 246.858 | 0 | 212.2857 | 52.2721 | 0 | 3.6861 | 48.5861 | 0 | 0 | 0 | 0 | 0 | 212.2857 | 0 | 602.3449 | 47.26% | 2.8272 | 0 | 2.8926 | 5.785% | 44.9
3946 | 876 | 814 | 108 | 8.0595 | 24.9 | 440.906 | 279.8456 | 0 | 240.9188 | 87.0102 | 0 | 21.1051 | 65.9051 | 0 | 0 | 0 | 0 | 0 | 240.9188 | 0 | 831.1281 | 65.21% | 16.1876 | 0 | 19.4545 | 38.91% | 44.8
3947 | 918 | 938 | 105 | 6.0446 | 26.4 | 462.0454 | 301.1524 | 0 | 262.1669 | 106.5 | 6.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 262.1669 | 0 | 1080.0891 | 84.75% | 19.175 | 0 | 39.073 | 78.15% | 43.5
3948 | 935 | 1006 | 103 | 10.4773 | 27.5 | 470.6018 | 306.0883 | 4.5544 | 264.4223 | 107.6 | 18.6756 | 13.9244 | 75 | 0 | 0 | 0 | 0 | 0 | 264.4223 | 0 | 1274.5104 | 100% | 10.68 | 0 | 50 | 100% | 42.4
3949 | 934 | 1014 | 104 | 10.6788 | 28.4 | 470.0984 | 0 | 308.4094 | 0 | 107.8 | 32.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.2
3950 | 920 | 961 | 103 | 12.0892 | 28.9 | 463.052 | 0 | 296.7685 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42
3951 | 913 | 867 | 94 | 8.6639 | 29.2 | 459.5288 | 0 | 284.1395 | 0 | 98.2585 | 28.3793 | 0 | 69.8793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.5
3952 | 869 | 715 | 92 | 11.2833 | 28.8 | 437.3828 | 0 | 255.9074 | 0 | 69.3046 | 14.1023 | 0 | 55.2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
3953 | 745 | 518 | 100 | 10.6788 | 28 | 374.9715 | 0 | 197.4052 | 0 | 33.923 | 0 | 0 | 33.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.777 | 43.0673 | 86.13% | 40.7
3954 | 585 | 309 | 90 | 10.6788 | 26.6 | 294.4407 | 0 | 125.7911 | 0 | 12.0188 | 0 | 0 | 12.0188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.4926 | 34.99% | 37.0188
3955 | 288 | 102 | 45 | 8.4625 | 25.5 | 144.9554 | 0 | 0 | 0 | 2.3008 | 0 | 0 | 2.3008 | 0 | 0 | 0 | 55.8583 | 20.3993 | 0 | 55.8583 | 1223.7998 | 96.02% | 0 | 17.0999 | 0 | 0% | 39.8
3956 | 19 | 9 | 8 | 7.455 | 23.4 | 9.563 | 0 | 0 | 0 | 0.03373 | 0 | 0 | 0.03373 | 0 | 0 | 0 | 94.6619 | 37.1663 | 0 | 94.6619 | 1132.9578 | 88.89% | 0 | 0 | 0 | 0% | 37.2
3957 | 0 | 0 | 0 | 3.4253 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2554 | 35.9 | 0 | 91.2554 | 1045.665 | 82.04% | 0 | 0 | 0 | 0% | 35.9
3958 | 0 | 0 | 0 | 1.8134 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.695 | 33.7 | 0 | 85.695 | 964.6397 | 75.69% | 0 | 0 | 0 | 0% | 33.7
3959 | 0 | 0 | 0 | 0.60446 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9866 | 32.2 | 0 | 81.9866 | 887.8839 | 69.66% | 0 | 0 | 0 | 0% | 32.2
3960 | 0 | 0 | 0 | 1.6119 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5362 | 31.6 | 0 | 80.5362 | 812.8091 | 63.77% | 0 | 0 | 0 | 0% | 31.6
3961 | 0 | 0 | 0 | 3.8283 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3412 | 31.1 | 0 | 79.3412 | 739.0623 | 57.99% | 0 | 0 | 0 | 0% | 31.1
3962 | 0 | 0 | 0 | 3.8283 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.183 | 30.7 | 0 | 78.183 | 666.4812 | 52.29% | 0 | 0 | 0 | 0% | 30.7
3963 | 0 | 0 | 0 | 3.6268 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8214 | 30.6 | 0 | 77.8214 | 594.1662 | 46.62% | 0 | 0 | 0 | 0% | 30.6
3964 | 0 | 0 | 0 | 3.2238 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9185 | 31.5 | 0 | 79.9185 | 519.3239 | 40.75% | 0 | 0 | 0 | 0% | 31.5
3965 | 0 | 1 | 1 | 3.6268 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8358 | 34 | 0 | 85.8358 | 437.3411 | 34.31% | 0 | 0 | 0 | 0% | 34
3966 | 384 | 78 | 25 | 2.6193 | 16 | 193.2739 | 74.4508 | 0 | 51.0217 | 1.26 | 0 | 0 | 1.26 | 0 | 0 | 0 | 89.5492 | 35.54 | 51.0217 | 89.5492 | 398.6419 | 31.28% | 0 | 0 | 0 | 0% | 36.8
3967 | 729 | 272 | 45 | 1.2089 | 19.9 | 366.9184 | 183.3382 | 0 | 153.8539 | 5.4865 | 0 | 0 | 5.4865 | 0 | 0 | 0 | 85.0631 | 33.4135 | 153.8539 | 85.0631 | 462.4494 | 36.28% | 0 | 0 | 0 | 0% | 38.9
3968 | 860 | 482 | 56 | 2.0149 | 22.4 | 432.853 | 247.5476 | 0 | 213.5371 | 27.6063 | 0 | 0 | 27.6063 | 0 | 0 | 0 | 0 | 0 | 213.5371 | 0 | 662.5099 | 51.98% | 0 | 0 | 0 | 0% | 27.6063
3969 | 926 | 678 | 62 | 2.8208 | 24.3 | 466.0719 | 284.3509 | 0 | 247.7412 | 60.2119 | 0 | 10.056 | 50.156 | 0 | 0 | 0 | 0 | 0 | 247.7412 | 0 | 894.6158 | 70.19% | 7.7129 | 0 | 7.8924 | 15.78% | 40.1
3970 | 962 | 842 | 66 | 4.8357 | 26.6 | 484.1913 | 307.3513 | 0 | 268.6033 | 92.9978 | 1.3989 | 25 | 66.5989 | 0 | 0 | 0 | 0 | 0 | 268.6033 | 0 | 1146.2672 | 89.94% | 19.175 | 0 | 27.5137 | 55.03% | 40.2
3971 | 970 | 957 | 75 | 10.2758 | 27.7 | 488.2179 | 213.2867 | 104.942 | 184.6816 | 110.9 | 10.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 184.6816 | 0 | 1274.5104 | 100% | 19.175 | 0 | 47.135 | 94.27% | 39.1
3972 | 965 | 1025 | 90 | 10.0743 | 27.9 | 485.7013 | 0 | 320.6001 | 0 | 112.7 | 34.0496 | 3.6504 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 2.7999 | 0 | 50 | 100% | 37.3
3973 | 963 | 1028 | 87 | 8.4625 | 28.4 | 484.6946 | 0 | 317.9625 | 0 | 113.7 | 38.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.3
3974 | 950 | 975 | 86 | 6.2461 | 28.8 | 478.1515 | 0 | 306.404 | 0 | 114 | 39 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36
3975 | 927 | 869 | 82 | 8.4625 | 28.4 | 466.5752 | 0 | 288.4467 | 0 | 104.1849 | 34.1424 | 0 | 70.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.9
3976 | 889 | 718 | 78 | 6.8506 | 28.6 | 447.4492 | 0 | 261.7366 | 0 | 73.3185 | 18.6592 | 0 | 54.6592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36
3977 | 826 | 532 | 71 | 8.6639 | 28.3 | 415.7402 | 0 | 218.7959 | 0 | 34.474 | 0 | 0 | 34.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.474
3978 | 710 | 327 | 59 | 8.4625 | 27.1 | 357.3553 | 0 | 152.6033 | 0 | 11.201 | 0 | 0 | 11.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.422 | 48.84% | 36.201
3979 | 440 | 125 | 39 | 7.052 | 25.8 | 221.4597 | 0 | 0 | 0 | 1.9149 | 0 | 0 | 1.9149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.8701 | 0 | 0% | 25.785
3980 | 26 | 8 | 6 | 4.6342 | 23.2 | 13.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8297 | 35.2 | 0 | 89.8297 | 1189.0499 | 93.29% | 0 | 0 | 0 | 0% | 35.2
3981 | 0 | 0 | 0 | 3.4253 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7251 | 33.2 | 0 | 84.7251 | 1109.3492 | 87.04% | 0 | 0 | 0 | 0% | 33.2
3982 | 0 | 0 | 0 | 6.4476 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1968 | 31.4 | 0 | 80.1968 | 1034.6829 | 81.18% | 0 | 0 | 0 | 0% | 31.4
3983 | 0 | 0 | 0 | 4.2312 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5579 | 29.9 | 0 | 76.5579 | 963.9766 | 75.64% | 0 | 0 | 0 | 0% | 29.9
3984 | 0 | 0 | 0 | 3.6268 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.4427 | 29 | 0 | 74.4427 | 895.3012 | 70.25% | 0 | 0 | 0 | 0% | 29
3985 | 0 | 0 | 0 | 4.8357 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.573 | 28.6 | 0 | 73.573 | 827.4565 | 64.92% | 0 | 0 | 0 | 0% | 28.6
3986 | 0 | 0 | 0 | 5.4401 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.6995 | 28.2 | 0 | 72.6995 | 760.4451 | 59.67% | 0 | 0 | 0 | 0% | 28.2
3987 | 0 | 0 | 0 | 5.0372 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.3744 | 28.1 | 0 | 72.3744 | 693.7325 | 54.43% | 0 | 0 | 0 | 0% | 28.1
3988 | 0 | 0 | 0 | 6.8506 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8564 | 27.9 | 0 | 71.8564 | 627.5054 | 49.24% | 0 | 0 | 0 | 0% | 27.9
3989 | 0 | 1 | 1 | 3.6268 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4634 | 29.6 | 0 | 75.4634 | 557.7769 | 43.76% | 0 | 0 | 0 | 0% | 29.6
3990 | 255 | 87 | 56 | 4.2312 | 17.5 | 128.3459 | 0 | 49.5365 | 0 | 3.1124 | 0 | 0 | 3.1124 | 0 | 0 | 0 | 74.2509 | 28.9876 | 0 | 74.2509 | 489.2148 | 38.38% | 0 | 0 | 0 | 0% | 32.1
3991 | 349 | 235 | 118 | 4.8357 | 20.1 | 175.6578 | 87.8647 | 0 | 63.5351 | 8.7763 | 0 | 0 | 8.7763 | 0 | 0 | 0 | 66.0977 | 25.2237 | 63.5351 | 66.0977 | 487.3269 | 38.24% | 0 | 0 | 0 | 0% | 34
3992 | 331 | 378 | 215 | 8.0595 | 22.4 | 166.5981 | 95.3035 | 0 | 68.3436 | 24.848 | 0 | 0 | 24.848 | 0 | 0 | 0 | 0 | 0 | 68.3436 | 0 | 550.5634 | 43.2% | 0 | 0 | 0 | 0% | 24.848
3993 | 572 | 653 | 266 | 10.2758 | 24.4 | 287.8975 | 175.6688 | 0 | 142.4123 | 62.8008 | 0 | 13.4504 | 49.3504 | 0 | 0 | 0 | 0 | 0 | 142.4123 | 0 | 682.3337 | 53.54% | 10.3165 | 0 | 10.5581 | 21.12% | 35.9
3994 | 265 | 590 | 366 | 11.6862 | 24.7 | 133.3791 | 84.6746 | 0 | 56.3434 | 56.6681 | 0 | 10.234 | 46.434 | 0 | 0 | 0 | 0 | 0 | 56.3434 | 0 | 734.4668 | 57.63% | 7.8495 | 0 | 18.5914 | 37.18% | 36.2
3995 | 126 | 568 | 445 | 9.2684 | 25.3 | 63.418 | 0 | 41.3393 | 0 | 53.3165 | 0 | 8.7083 | 44.6083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734.4668 | 57.63% | 6.6792 | 0 | 25.4271 | 50.85% | 35.9
3996 | 2 | 283 | 275 | 10.6788 | 24.4 | 1.0066 | 0 | 0.66444 | 0 | 20.4115 | 0 | 0 | 20.4115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734.4668 | 57.63% | 0 | 13.9885 | 11.1133 | 22.23% | 34.4
3997 | 135 | 477 | 336 | 10.4773 | 24.4 | 67.9478 | 0 | 44.571 | 0 | 43.1615 | 0 | 4.8808 | 38.2808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734.4668 | 57.63% | 3.7435 | 0 | 14.9447 | 29.89% | 33.4
3998 | 566 | 816 | 277 | 11.2833 | 26.1 | 284.8776 | 182.5282 | 0 | 148.1793 | 103.0344 | 9.9172 | 25 | 68.1172 | 0 | 0 | 0 | 0 | 0 | 148.1793 | 0 | 871.5731 | 68.38% | 19.175 | 0 | 34.5695 | 69.14% | 33.2
3999 | 250 | 587 | 372 | 12.4922 | 25.6 | 125.8293 | 77.7771 | 0 | 48.9849 | 61.1188 | 0 | 13.9594 | 47.1594 | 0 | 0 | 0 | 0 | 0 | 48.9849 | 0 | 916.8975 | 71.94% | 10.7069 | 0 | 45.5275 | 91.06% | 33.2
4000 | 785 | 718 | 151 | 12.6937 | 25.5 | 395.1041 | 231.0626 | 0 | 192.7231 | 78.6111 | 16.7081 | 5.6975 | 56.2056 | 0 | 0 | 0 | 0 | 0 | 192.7231 | 0 | 1095.2191 | 85.93% | 4.37 | 0 | 50 | 100% | 33.8
4001 | 468 | 406 | 146 | 12.0892 | 24.7 | 235.5525 | 123.9231 | 0 | 92.8585 | 27.8008 | 0 | 0 | 27.8008 | 0 | 0 | 0 | 0 | 0 | 92.8585 | 0 | 1181.1386 | 92.67% | 0 | 7.0992 | 42.7355 | 85.47% | 34.9
4002 | 311 | 214 | 87 | 10.8803 | 23.8 | 156.5317 | 66.811 | 0 | 39.7639 | 9.0259 | 0 | 0 | 9.0259 | 0 | 0 | 0 | 0 | 0 | 39.7639 | 0 | 1217.9311 | 95.56% | 0 | 25 | 17.1526 | 34.31% | 34.0259
4003 | 221 | 117 | 68 | 9.8729 | 22.8 | 111.2331 | 0 | 0 | 0 | 3.9138 | 0 | 0 | 3.9138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1217.9311 | 95.56% | 0 | 16.7623 | 0 | 0% | 20.6761
4004 | 5 | 10 | 9 | 6.8506 | 21.5 | 2.5166 | 0 | 0 | 0 | 0.090082 | 0 | 0 | 0.090082 | 0 | 0 | 0 | 89.592 | 35.2099 | 0 | 89.592 | 1132.5034 | 88.86% | 0 | 0 | 0 | 0% | 35.3
4005 | 0 | 0 | 0 | 4.8357 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1244 | 33 | 0 | 84.1244 | 1053.4242 | 82.65% | 0 | 0 | 0 | 0% | 33
4006 | 0 | 0 | 0 | 2.6193 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9135 | 31.3 | 0 | 79.9135 | 979.0311 | 76.82% | 0 | 0 | 0 | 0% | 31.3
4007 | 0 | 0 | 0 | 2.2164 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6546 | 30 | 0 | 76.6546 | 908.1938 | 71.26% | 0 | 0 | 0 | 0% | 30
4008 | 0 | 0 | 0 | 2.0149 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.7634 | 29.2 | 0 | 74.7634 | 839.1719 | 65.84% | 0 | 0 | 0 | 0% | 29.2
4009 | 0 | 0 | 0 | 2.2164 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6584 | 29.2 | 0 | 74.6584 | 770.2371 | 60.43% | 0 | 0 | 0 | 0% | 29.2
4010 | 0 | 0 | 0 | 1.6119 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7953 | 30.6 | 0 | 77.7953 | 697.8766 | 54.76% | 0 | 0 | 0 | 0% | 30.6
4011 | 0 | 0 | 0 | 0.80595 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3411 | 33.4 | 0 | 84.3411 | 617.5888 | 48.46% | 0 | 0 | 0 | 0% | 33.4
4012 | 0 | 0 | 0 | 0.20149 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.437 | 37.2 | 0 | 93.437 | 526.4679 | 41.31% | 0 | 0 | 0 | 0% | 37.2
4013 | 0 | 1 | 1 | 1.8134 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1298 | 40.4 | 0 | 101.1298 | 426.1724 | 33.44% | 0 | 0 | 0 | 0% | 40.4
4014 | 308 | 74 | 30 | 0.60446 | 16.1 | 155.0218 | 59.9435 | 0 | 38.806 | 1.4713 | 0 | 0 | 1.4713 | 0 | 0 | 0 | 102.7512 | 41.0287 | 38.806 | 102.7512 | 360.4256 | 28.28% | 0 | 0 | 0 | 0% | 42.5
4015 | 652 | 261 | 58 | 0.40297 | 21.2 | 328.1629 | 164.3173 | 0 | 136.3017 | 5.7901 | 0 | 0 | 5.7901 | 0 | 0 | 0 | 96.0799 | 37.9099 | 136.3017 | 96.0799 | 395.4095 | 31.02% | 0 | 0 | 0 | 0% | 43.7
4016 | 795 | 465 | 72 | 2.2164 | 23 | 400.1373 | 228.9648 | 0 | 196.2051 | 26.7626 | 0 | 0 | 26.7626 | 0 | 0 | 0 | 0 | 0 | 196.2051 | 0 | 580.251 | 45.53% | 0 | 0 | 0 | 0% | 26.7626
4017 | 882 | 662 | 77 | 3.8283 | 24.3 | 443.9259 | 270.9096 | 0 | 234.7303 | 53.827 | 0 | 4.4135 | 49.4135 | 0 | 0 | 0 | 0 | 0 | 234.7303 | 0 | 801.3864 | 62.88% | 3.3852 | 0 | 3.465 | 6.93% | 45
4018 | 928 | 827 | 80 | 2.8208 | 26.9 | 467.0785 | 296.5546 | 0 | 259.2481 | 83.7636 | 0 | 19.2318 | 64.5318 | 0 | 0 | 0 | 0 | 0 | 259.2481 | 0 | 1045.6198 | 82.04% | 14.7508 | 0 | 18.5639 | 37.13% | 45.3
4019 | 942 | 942 | 86 | 4.6342 | 28.6 | 474.125 | 309.08 | 0 | 270.3035 | 105.7 | 5.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 270.3035 | 0 | 1274.5104 | 100% | 19.175 | 0 | 38.1915 | 76.38% | 44.3
4020 | 943 | 1004 | 92 | 7.858 | 29.4 | 474.6283 | 0 | 313.2778 | 0 | 106.7 | 16.6593 | 15.0407 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 11.5362 | 0 | 50 | 100% | 43.3
4021 | 945 | 1016 | 94 | 9.8729 | 29.6 | 475.6349 | 0 | 311.9753 | 0 | 106.8 | 31.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.2
4022 | 930 | 963 | 93 | 7.2535 | 30.3 | 468.0852 | 0 | 299.8755 | 0 | 106.9 | 31.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.1
4023 | 924 | 867 | 84 | 9.8729 | 30.7 | 465.0653 | 0 | 287.4159 | 0 | 96.9449 | 27.1725 | 0 | 69.7725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
4024 | 896 | 721 | 76 | 10.4773 | 30.2 | 450.9724 | 0 | 263.6716 | 0 | 67.7832 | 12.6416 | 0 | 55.1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
4025 | 832 | 534 | 69 | 7.455 | 29.9 | 418.7601 | 0 | 220.2254 | 0 | 34.3712 | 0 | 0 | 34.3712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.2288 | 41.5783 | 83.16% | 42.6
4026 | 709 | 328 | 60 | 6.0446 | 29.4 | 356.852 | 0 | 152.2254 | 0 | 11.2621 | 0 | 0 | 11.2621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.9917 | 31.98% | 36.2621
4027 | 470 | 131 | 39 | 3.2238 | 27.6 | 236.5592 | 0 | 0 | 0 | 1.891 | 0 | 0 | 1.891 | 0 | 0 | 0 | 63.9996 | 23.6834 | 0 | 63.9996 | 1215.9881 | 95.41% | 0 | 15.6256 | 0 | 0% | 41.2
4028 | 36 | 9 | 6 | 3.2238 | 24.7 | 18.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9403 | 38 | 0 | 96.9403 | 1122.6641 | 88.09% | 0 | 0 | 0 | 0% | 38
4029 | 0 | 0 | 0 | 4.8357 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5364 | 36.4 | 0 | 92.5364 | 1033.9297 | 81.12% | 0 | 0 | 0 | 0% | 36.4
4030 | 0 | 0 | 0 | 1.6119 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.992 | 34.6 | 0 | 87.992 | 950.2625 | 74.56% | 0 | 0 | 0 | 0% | 34.6
4031 | 0 | 0 | 0 | 2.0149 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4943 | 33.2 | 0 | 84.4943 | 870.6258 | 68.31% | 0 | 0 | 0 | 0% | 33.2
4032 | 0 | 0 | 0 | 3.4253 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0606 | 32.7 | 0 | 83.0606 | 792.4056 | 62.17% | 0 | 0 | 0 | 0% | 32.7
4033 | 0 | 0 | 0 | 2.0149 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6283 | 32.5 | 0 | 82.6283 | 714.7425 | 56.08% | 0 | 0 | 0 | 0% | 32.5
4034 | 0 | 0 | 0 | 1.6119 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9729 | 33.1 | 0 | 83.9729 | 635.3561 | 49.85% | 0 | 0 | 0 | 0% | 33.1
4035 | 0 | 0 | 0 | 1.4104 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8161 | 35.2 | 0 | 88.8161 | 549.9002 | 43.15% | 0 | 0 | 0 | 0% | 35.2
4036 | 0 | 0 | 0 | 0.80595 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1412 | 38.3 | 0 | 96.1412 | 455.6793 | 35.75% | 0 | 0 | 0 | 0% | 38.3
4037 | 0 | 1 | 1 | 1.2089 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4233 | 41.3 | 0 | 103.4233 | 352.8754 | 27.69% | 0 | 0 | 0 | 0% | 41.3
4038 | 341 | 75 | 27 | 0.80595 | 17.8 | 171.6312 | 66.483 | 0 | 44.4029 | 1.2449 | 0 | 0 | 1.2449 | 0 | 0 | 0 | 105.5187 | 42.0551 | 44.4029 | 105.5187 | 289.9403 | 22.75% | 0 | 0 | 0 | 0% | 43.3
4039 | 681 | 262 | 50 | 1.8134 | 22 | 342.7591 | 171.7955 | 0 | 142.8798 | 5.2189 | 0 | 0 | 5.2189 | 0 | 0 | 0 | 99.5177 | 39.2811 | 142.8798 | 99.5177 | 328.5527 | 25.78% | 0 | 0 | 0 | 0% | 44.5
4040 | 825 | 469 | 62 | 4.0297 | 23.9 | 415.2368 | 237.6708 | 0 | 203.737 | 26.9515 | 0 | 0 | 26.9515 | 0 | 0 | 0 | 0 | 0 | 203.737 | 0 | 522.3171 | 40.98% | 0 | 0 | 0 | 0% | 26.9515
4041 | 880 | 657 | 75 | 6.4476 | 23.7 | 442.9193 | 270.3322 | 0 | 232.9079 | 53.5079 | 0 | 3.8039 | 49.7039 | 0 | 0 | 0 | 0 | 0 | 232.9079 | 0 | 743.8245 | 58.36% | 2.9176 | 0 | 2.9869 | 5.974% | 45.9
4042 | 909 | 817 | 86 | 5.2387 | 25.7 | 457.5155 | 290.5169 | 0 | 252.7345 | 84.1272 | 0 | 19.0136 | 65.1136 | 0 | 0 | 0 | 0 | 0 | 252.7345 | 0 | 984.188 | 77.22% | 14.5834 | 0 | 17.9166 | 35.83% | 46.1
4043 | 922 | 932 | 95 | 6.0446 | 27.4 | 464.0586 | 302.5376 | 0 | 263.4681 | 105 | 5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 263.4681 | 0 | 1234.7598 | 96.88% | 19.175 | 0 | 37.547 | 75.09% | 45
4044 | 916 | 992 | 105 | 6.8506 | 28.9 | 461.0387 | 0 | 304.3043 | 0 | 105.9 | 15.0407 | 15.8593 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.7598 | 96.88% | 12.1641 | 0 | 50 | 100% | 44.1
4045 | 916 | 1001 | 106 | 6.0446 | 30.4 | 461.0387 | 0 | 302.3805 | 0 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.7598 | 96.88% | 0 | 0 | 50 | 100% | 43.9
4046 | 899 | 949 | 109 | 12.8952 | 31.1 | 452.4823 | 0 | 289.8439 | 0 | 106.2 | 31.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.7598 | 96.88% | 0 | 0 | 50 | 100% | 43.8
4047 | 870 | 845 | 107 | 12.4922 | 30 | 437.8861 | 0 | 270.5742 | 0 | 93.8598 | 25.2799 | 0 | 68.5799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.7598 | 96.88% | 0 | 0 | 50 | 100% | 43.3
4048 | 828 | 697 | 100 | 12.0892 | 29.6 | 416.7468 | 0 | 243.6011 | 0 | 64.5561 | 10.878 | 0 | 53.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.7598 | 96.88% | 0 | 0 | 50 | 100% | 42.8
4049 | 769 | 517 | 86 | 9.0669 | 29.4 | 387.0511 | 0 | 203.4693 | 0 | 33.626 | 0 | 0 | 33.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.7598 | 96.88% | 0 | 9.174 | 40.6096 | 81.22% | 42.8
4050 | 680 | 323 | 66 | 7.858 | 29 | 342.2558 | 0 | 145.9066 | 0 | 11.522 | 0 | 0 | 11.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.7598 | 96.88% | 0 | 25 | 15.0193 | 30.04% | 36.522
4051 | 455 | 130 | 39 | 9.0669 | 27 | 229.0094 | 0 | 0 | 0 | 1.8973 | 0 | 0 | 1.8973 | 0 | 0 | 0 | 66.4161 | 24.8294 | 0 | 66.4161 | 1173.8974 | 92.11% | 0 | 14.6733 | 0 | 0% | 41.4
4052 | 26 | 8 | 6 | 6.6491 | 21.7 | 13.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6147 | 38.1 | 0 | 96.6147 | 1080.3859 | 84.77% | 0 | 0 | 0 | 0% | 38.1
4053 | 0 | 0 | 0 | 3.8283 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8761 | 36.7 | 0 | 92.8761 | 990.8287 | 77.74% | 0 | 0 | 0 | 0% | 36.7
4054 | 0 | 0 | 0 | 1.6119 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9305 | 34.7 | 0 | 87.9305 | 906.8898 | 71.16% | 0 | 0 | 0 | 0% | 34.7
4055 | 0 | 0 | 0 | 1.0074 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9674 | 33.5 | 0 | 84.9674 | 826.4109 | 64.84% | 0 | 0 | 0 | 0% | 33.5
4056 | 0 | 0 | 0 | 0.60446 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6659 | 33 | 0 | 83.6659 | 747.3526 | 58.64% | 0 | 0 | 0 | 0% | 33
4057 | 0 | 0 | 0 | 1.6119 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.062 | 32.8 | 0 | 83.062 | 668.8527 | 52.48% | 0 | 0 | 0 | 0% | 32.8
4058 | 0 | 0 | 0 | 1.0074 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.169 | 33.3 | 0 | 84.169 | 588.9101 | 46.21% | 0 | 0 | 0 | 0% | 33.3
4059 | 0 | 0 | 0 | 1.8134 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6142 | 35.6 | 0 | 89.6142 | 502.356 | 39.42% | 0 | 0 | 0 | 0% | 35.6
4060 | 0 | 0 | 0 | 2.4178 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5685 | 38.9 | 0 | 97.5685 | 406.4337 | 31.89% | 0 | 0 | 0 | 0% | 38.9
4061 | 0 | 1 | 1 | 2.4178 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2815 | 41.7 | 0 | 104.2815 | 302.5143 | 23.74% | 0 | 0 | 0 | 0% | 41.7
4062 | 253 | 70 | 33 | 3.0223 | 19.1 | 127.3393 | 0 | 49.4082 | 0 | 1.671 | 0 | 0 | 1.671 | 0 | 0 | 0 | 104.448 | 41.5216 | 0 | 104.448 | 199.0698 | 15.62% | 0 | 0 | 0 | 0% | 43.1926
4063 | 626 | 259 | 64 | 1.8134 | 22.9 | 315.0767 | 158.0703 | 0 | 129.9871 | 5.7604 | 0 | 0 | 5.7604 | 0 | 0 | 0 | 0 | 0 | 129.9871 | 0 | 322.6765 | 25.32% | 0 | 0 | 0 | 0% | 5.7604
4064 | 741 | 458 | 91 | 1.6119 | 25.4 | 372.9582 | 213.5304 | 0 | 181.9722 | 26.377 | 0 | 0 | 26.377 | 0 | 0 | 0 | 0 | 0 | 181.9722 | 0 | 495.7168 | 38.89% | 0 | 0 | 0 | 0% | 26.377
4065 | 873 | 669 | 90 | 3.6268 | 27.8 | 439.3961 | 268.2199 | 0 | 232.3092 | 51.9928 | 0 | 2.7964 | 49.1964 | 0 | 0 | 0 | 0 | 0 | 232.3092 | 0 | 716.6234 | 56.23% | 2.1448 | 0 | 2.1961 | 4.392% | 46.4
4066 | 927 | 835 | 89 | 6.4476 | 28.9 | 466.5752 | 296.3054 | 0 | 257.4811 | 85.5068 | 0 | 19.5034 | 66.0034 | 0 | 0 | 0 | 0 | 0 | 257.4811 | 0 | 961.4663 | 75.44% | 14.9591 | 0 | 17.5126 | 35.03% | 46.5
4067 | 958 | 958 | 89 | 7.455 | 30.1 | 482.1781 | 314.3721 | 0 | 273.6839 | 104.8 | 4.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 273.6839 | 0 | 1221.7167 | 95.86% | 19.175 | 0 | 37.1458 | 74.29% | 45.2
4068 | 917 | 1051 | 164 | 9.0669 | 31.2 | 461.542 | 229.9117 | 74.723 | 199.0202 | 105.6 | 14.2321 | 16.3679 | 75 | 0 | 0 | 0 | 0 | 0 | 199.0202 | 0 | 1274.5104 | 100% | 12.5542 | 0 | 50 | 100% | 44.4
4069 | 962 | 1041 | 103 | 10.4773 | 32.1 | 484.1913 | 0 | 317.5438 | 0 | 105.8 | 30.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.2
4070 | 942 | 983 | 101 | 12.0892 | 32.5 | 474.125 | 0 | 303.6714 | 0 | 105.9 | 30.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.1
4071 | 862 | 899 | 161 | 11.8877 | 33.2 | 433.8596 | 0 | 268.0427 | 0 | 99.653 | 28.0265 | 0 | 71.6265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.6
4072 | 272 | 527 | 318 | 11.6862 | 32.4 | 136.9023 | 0 | 80.0036 | 0 | 38.9195 | 0 | 0 | 38.9195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 4.3805 | 45.5155 | 91.03% | 43.3
4073 | 353 | 440 | 246 | 9.6714 | 31.9 | 177.671 | 0 | 93.3614 | 0 | 30.1577 | 0 | 0 | 30.1577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 12.8423 | 32.3682 | 64.74% | 43
4074 | 627 | 355 | 117 | 7.858 | 31.7 | 315.58 | 0 | 134.4408 | 0 | 14.4625 | 0 | 0 | 14.4625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 6.7737 | 13.55% | 39.4625
4075 | 416 | 143 | 64 | 5.6416 | 30.5 | 209.38 | 0 | 0 | 0 | 3.4267 | 0 | 0 | 3.4267 | 0 | 0 | 0 | 82.4323 | 31.4561 | 0 | 82.4323 | 1197.7839 | 93.98% | 0 | 6.6172 | 0 | 0% | 41.5
4076 | 41 | 15 | 12 | 5.6416 | 25.2 | 20.636 | 0 | 0 | 0 | 0.23942 | 0 | 0 | 0.23942 | 0 | 0 | 0 | 96.9493 | 37.9606 | 0 | 96.9493 | 1104.4973 | 86.66% | 0 | 0 | 0 | 0% | 38.2
4077 | 0 | 0 | 0 | 3.6268 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0317 | 37 | 0 | 94.0317 | 1014.1018 | 79.57% | 0 | 0 | 0 | 0% | 37
4078 | 0 | 0 | 0 | 1.0074 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0732 | 35 | 0 | 89.0732 | 929.2949 | 72.91% | 0 | 0 | 0 | 0% | 35
4079 | 0 | 0 | 0 | 1.0074 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6235 | 33.6 | 0 | 85.6235 | 848.5357 | 66.58% | 0 | 0 | 0 | 0% | 33.6
4080 | 0 | 0 | 0 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3121 | 33.1 | 0 | 84.3121 | 769.1989 | 60.35% | 0 | 0 | 0 | 0% | 33.1
4081 | 0 | 0 | 0 | 1.0074 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7968 | 32.9 | 0 | 83.7968 | 690.4213 | 54.17% | 0 | 0 | 0 | 0% | 32.9
4082 | 0 | 0 | 0 | 2.4178 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.746 | 33.3 | 0 | 84.746 | 610.4866 | 47.9% | 0 | 0 | 0 | 0% | 33.3
4083 | 0 | 0 | 0 | 1.6119 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.282 | 35.2 | 0 | 89.282 | 525.0572 | 41.2% | 0 | 0 | 0 | 0% | 35.2
4084 | 0 | 0 | 0 | 1.6119 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.745 | 38.3 | 0 | 96.745 | 430.8653 | 33.81% | 0 | 0 | 0 | 0% | 38.3
4085 | 0 | 1 | 1 | 2.4178 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2393 | 40.9 | 0 | 103.2393 | 329.2235 | 25.83% | 0 | 0 | 0 | 0% | 40.9
4086 | 241 | 83 | 48 | 3.0223 | 22.4 | 121.2995 | 0 | 47.1384 | 0 | 2.5222 | 0 | 0 | 2.5222 | 0 | 0 | 0 | 102.2559 | 40.3778 | 0 | 102.2559 | 229.0253 | 17.97% | 0 | 0 | 0 | 0% | 42.9
4087 | 610 | 255 | 65 | 2.0149 | 24.5 | 307.0236 | 154.1695 | 0 | 126.3088 | 5.7073 | 0 | 0 | 5.7073 | 0 | 0 | 0 | 97.6136 | 38.2927 | 126.3088 | 97.6136 | 254.8719 | 20% | 0 | 0 | 0 | 0% | 44
4088 | 779 | 459 | 74 | 1.6119 | 26.5 | 392.0842 | 224.5421 | 0 | 192.2649 | 25.8668 | 0 | 0 | 25.8668 | 0 | 0 | 0 | 0 | 0 | 192.2649 | 0 | 437.8679 | 34.36% | 0 | 0 | 0 | 0% | 25.8668
4089 | 858 | 653 | 84 | 3.0223 | 28.4 | 431.8463 | 263.6498 | 0 | 228.2316 | 49.7582 | 2.0291 | 0 | 47.7291 | 0 | 0 | 0 | 0 | 0 | 228.2316 | 0 | 655.0966 | 51.4% | 0 | 0 | 0 | 0% | 45.7
4090 | 902 | 817 | 92 | 4.2312 | 29.9 | 453.9923 | 288.3502 | 0 | 251.1232 | 81.6273 | 0 | 17.9136 | 63.7136 | 0 | 0 | 0 | 0 | 0 | 251.1232 | 0 | 894.1133 | 70.15% | 13.7398 | 0 | 14.0701 | 28.14% | 45.8
4091 | 925 | 934 | 93 | 4.0297 | 31.3 | 465.5686 | 303.5649 | 0 | 265.4027 | 103.5316 | 4.4658 | 25 | 74.0658 | 0 | 0 | 0 | 0 | 0 | 265.4027 | 0 | 1146.7212 | 89.97% | 19.175 | 0 | 33.7061 | 67.41% | 44.6
4092 | 939 | 1004 | 94 | 6.6491 | 32.1 | 472.615 | 214.2543 | 97.6889 | 186.7742 | 106.4 | 10.6552 | 20.7448 | 75 | 0 | 0 | 0 | 0 | 0 | 186.7742 | 0 | 1274.5104 | 100% | 15.9113 | 0 | 50 | 100% | 43.6
4093 | 970 | 1031 | 85 | 10.6788 | 32.8 | 488.2179 | 0 | 320.163 | 0 | 106.7 | 31.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.3
4094 | 975 | 988 | 77 | 12.6937 | 32.8 | 490.7345 | 0 | 314.2738 | 0 | 106.9 | 31.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.1
4095 | 967 | 890 | 70 | 12.2907 | 32.9 | 486.7079 | 0 | 300.6451 | 0 | 100.4965 | 29.0482 | 0 | 71.4482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
4096 | 945 | 745 | 64 | 13.0966 | 32.9 | 475.6349 | 0 | 277.8835 | 0 | 71.1087 | 14.4544 | 0 | 56.6544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.2
4097 | 871 | 550 | 62 | 12.0892 | 31.8 | 438.3894 | 0 | 230.2619 | 0 | 35.3648 | 0 | 0 | 35.3648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.6352 | 43.2063 | 86.41% | 42
4098 | 734 | 336 | 56 | 8.4625 | 31.5 | 369.435 | 0 | 157.2643 | 0 | 11.3299 | 0 | 0 | 11.3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.6087 | 35.22% | 36.3299
4099 | 455 | 130 | 39 | 6.0446 | 30.6 | 229.0094 | 0 | 0 | 0 | 1.8582 | 0 | 0 | 1.8582 | 0 | 0 | 0 | 60.5371 | 21.8437 | 0 | 60.5371 | 1219.3904 | 95.68% | 0 | 17.198 | 2.7756e-15 | 5.551e-15% | 40.9
4100 | 31 | 9 | 6 | 4.2312 | 28.2 | 15.6028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4286 | 37.9 | 0 | 97.4286 | 1125.6824 | 88.32% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.9
4101 | 0 | 0 | 0 | 6.0446 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9957 | 36.8 | 0 | 93.9957 | 1035.6828 | 81.26% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.8
4102 | 0 | 0 | 0 | 4.6342 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8789 | 34.9 | 0 | 88.8789 | 951.1824 | 74.63% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.9
4103 | 0 | 0 | 0 | 6.0446 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1707 | 33.4 | 0 | 85.1707 | 870.98 | 68.34% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.4
4104 | 0 | 0 | 0 | 7.6565 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8708 | 32.9 | 0 | 83.8708 | 792.2204 | 62.16% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.9
4105 | 0 | 0 | 0 | 6.2461 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.416 | 32.7 | 0 | 83.416 | 713.9674 | 56.02% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.7
4106 | 0 | 0 | 0 | 4.4327 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4316 | 33.2 | 0 | 84.4316 | 634.3335 | 49.77% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.2
4107 | 0 | 0 | 0 | 3.2238 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3177 | 35.3 | 0 | 89.3177 | 548.6414 | 43.05% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.3
4108 | 0 | 0 | 0 | 2.4178 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9583 | 38.5 | 0 | 96.9583 | 453.8957 | 35.61% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38.5
4109 | 0 | 1 | 1 | 2.2164 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2831 | 41.1 | 0 | 103.2831 | 351.7096 | 27.6% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.1
4110 | 57 | 41 | 32 | 1.8134 | 18.9 | 28.6891 | 0 | 11.1653 | 0 | 1.7186 | 0 | 0 | 1.7186 | 0 | 0 | 0 | 104.0714 | 41.3814 | 0 | 104.0714 | 248.7002 | 19.51% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.1
4111 | 524 | 234 | 63 | 4.0297 | 21.3 | 263.7383 | 132.5482 | 0 | 105.3019 | 5.3531 | 0 | 0 | 5.3531 | 0 | 0 | 0 | 98.5873 | 38.9469 | 105.3019 | 98.5873 | 252.6353 | 19.82% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 44.3
4112 | 763 | 453 | 74 | 2.2164 | 24.1 | 384.0312 | 219.9899 | 0 | 187.7894 | 25.6746 | 0 | 0 | 25.6746 | 0 | 0 | 0 | 0 | 0 | 187.7894 | 0 | 431.2761 | 33.84% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 25.6746
4113 | 847 | 646 | 82 | 4.8357 | 25.8 | 426.3098 | 260.3089 | 0 | 224.4847 | 50.1472 | 2.2736 | 0 | 47.8736 | 0 | 0 | 0 | 0 | 0 | 224.4847 | 0 | 644.8246 | 50.59% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 45.6
4114 | 881 | 809 | 97 | 5.8431 | 27.3 | 443.4226 | 281.6727 | 0 | 244.0169 | 82.156 | 0 | 18.228 | 63.928 | 0 | 0 | 0 | 0 | 0 | 244.0169 | 0 | 876.9536 | 68.81% | 13.9809 | 0 | 14.3191 | 28.64% | 45.7
4115 | 769 | 865 | 158 | 7.052 | 27.8 | 387.0511 | 252.3881 | 0 | 215.8643 | 96.9972 | 1.3486 | 25 | 70.6486 | 0 | 0 | 0 | 0 | 0 | 215.8643 | 0 | 1082.3016 | 84.92% | 19.175 | 0 | 33.958 | 67.92% | 44.3
4116 | 586 | 788 | 210 | 10.4773 | 28.3 | 294.944 | 194.675 | 0 | 160.0347 | 89.0741 | 2.5158 | 20.4213 | 66.137 | 0 | 0 | 0 | 0 | 0 | 160.0347 | 0 | 1234.5399 | 96.86% | 15.6631 | 0 | 50 | 100% | 43.2
4117 | 878 | 995 | 131 | 9.8729 | 29 | 441.9127 | 0 | 289.7779 | 0 | 107.2 | 32.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.5399 | 96.86% | 0 | 0 | 50 | 100% | 42.8
4118 | 852 | 943 | 140 | 9.6714 | 29.6 | 428.8264 | 0 | 274.5971 | 0 | 107.3 | 32.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.5399 | 96.86% | 0 | 0 | 50 | 100% | 42.7
4119 | 821 | 841 | 138 | 9.6714 | 29.5 | 413.2236 | 0 | 255.2134 | 0 | 93.5627 | 25.7313 | 0 | 67.8313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.5399 | 96.86% | 0 | 0 | 50 | 100% | 42.1
4120 | 757 | 655 | 136 | 9.2684 | 29.2 | 381.0113 | 0 | 222.544 | 0 | 63.4894 | 10.7947 | 0 | 52.6947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.5399 | 96.86% | 0 | 0 | 50 | 100% | 41.9
4121 | 698 | 509 | 114 | 10.8803 | 28.4 | 351.3155 | 0 | 184.4432 | 0 | 33.5496 | 0 | 0 | 33.5496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.5399 | 96.86% | 0 | 7.8504 | 41.9609 | 83.92% | 41.4
4122 | 582 | 312 | 88 | 10.6788 | 27.1 | 292.9307 | 0 | 124.595 | 0 | 12.1664 | 0 | 0 | 12.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.5399 | 96.86% | 0 | 25 | 16.3596 | 32.72% | 37.1664
4123 | 327 | 119 | 52 | 9.4699 | 25.6 | 164.5848 | 0 | 0 | 0 | 2.7369 | 0 | 0 | 2.7369 | 0 | 0 | 0 | 57.9769 | 21.2874 | 0 | 57.9769 | 1181.8066 | 92.73% | 0 | 15.9758 | 2.7756e-15 | 5.551e-15% | 40
4124 | 3 | 5 | 5 | 7.6565 | 23.8 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3067 | 37.4 | 0 | 95.3067 | 1090.2977 | 85.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.4
4125 | 0 | 0 | 0 | 6.2461 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6287 | 36.4 | 0 | 92.6287 | 1001.5979 | 78.59% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.4
4126 | 0 | 0 | 0 | 5.4401 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0595 | 34.6 | 0 | 88.0595 | 917.9628 | 72.02% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.6
4127 | 0 | 0 | 0 | 5.8431 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3004 | 33.1 | 0 | 84.3004 | 838.6423 | 65.8% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.1
4128 | 0 | 0 | 0 | 7.2535 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0194 | 32.2 | 0 | 82.0194 | 761.8703 | 59.78% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.2
4129 | 0 | 0 | 0 | 7.052 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.762 | 31.7 | 0 | 80.762 | 686.4975 | 53.86% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.7
4130 | 0 | 0 | 0 | 6.4476 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2139 | 31.5 | 0 | 80.2139 | 611.6746 | 47.99% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.5
4131 | 0 | 0 | 0 | 6.2461 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8923 | 31.4 | 0 | 79.8923 | 537.1193 | 42.14% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.4
4132 | 0 | 0 | 0 | 3.6268 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4684 | 32.1 | 0 | 81.4684 | 460.5781 | 36.14% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.1
4133 | 0 | 1 | 1 | 3.2238 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.415 | 34.6 | 0 | 87.415 | 376.8435 | 29.57% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.6
4134 | 214 | 64 | 33 | 2.6193 | 18 | 107.7099 | 0 | 41.9758 | 0 | 1.6049 | 0 | 0 | 1.6049 | 0 | 0 | 0 | 90.7483 | 35.8951 | 0 | 90.7483 | 289.4211 | 22.71% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.5
4135 | 521 | 238 | 74 | 2.6193 | 20.6 | 262.2284 | 131.8969 | 0 | 105.1719 | 6.1313 | 0 | 0 | 6.1313 | 0 | 0 | 0 | 86.0141 | 33.7687 | 105.1719 | 86.0141 | 306.9219 | 24.08% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.9
4136 | 698 | 442 | 94 | 5.8431 | 22.9 | 351.3155 | 201.3031 | 0 | 168.9057 | 25.6347 | 0 | 0 | 25.6347 | 0 | 0 | 0 | 0 | 0 | 168.9057 | 0 | 465.7252 | 36.54% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 25.6347
4137 | 788 | 632 | 105 | 9.0669 | 24.8 | 396.6141 | 242.2139 | 0 | 205.1878 | 54.0093 | 0 | 6.4547 | 47.5547 | 0 | 0 | 0 | 0 | 0 | 205.1878 | 0 | 658.6405 | 51.68% | 4.9507 | 0 | 5.0712 | 10.14% | 41.1
4138 | 842 | 794 | 111 | 11.6862 | 25.8 | 423.7932 | 269.2387 | 0 | 228.7739 | 86.4338 | 0 | 22.4669 | 63.9669 | 0 | 0 | 0 | 0 | 0 | 228.7739 | 0 | 873.7312 | 68.55% | 17.2321 | 0 | 22.7227 | 45.45% | 41.5
4139 | 867 | 910 | 116 | 10.8803 | 27 | 436.3762 | 284.5743 | 0 | 243.7574 | 109.3 | 9.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 243.7574 | 0 | 1102.9093 | 86.54% | 19.175 | 0 | 42.3644 | 84.73% | 40.7
4140 | 881 | 978 | 119 | 10.4773 | 27.7 | 443.4226 | 292.6804 | 0 | 251.7229 | 111 | 26.2814 | 9.7186 | 75 | 0 | 0 | 0 | 0 | 0 | 251.7229 | 0 | 1274.5104 | 100% | 7.4541 | 0 | 50 | 100% | 39
4141 | 890 | 991 | 115 | 11.4848 | 28.5 | 447.9525 | 0 | 293.7194 | 0 | 112.1 | 37.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.9
4142 | 891 | 948 | 108 | 12.0892 | 29.2 | 448.4558 | 0 | 287.137 | 0 | 112.2 | 37.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.8
4143 | 874 | 850 | 102 | 13.0966 | 29 | 439.8994 | 0 | 271.6477 | 0 | 100.3325 | 31.4163 | 0 | 68.9163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.5
4144 | 825 | 701 | 100 | 13.7011 | 28.5 | 415.2368 | 0 | 242.4722 | 0 | 70.4595 | 16.4298 | 0 | 54.0298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.6
4145 | 749 | 520 | 94 | 14.91 | 27.3 | 376.9847 | 0 | 197.8265 | 0 | 34.2795 | 0 | 0 | 34.2795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 3.5205 | 46.3943 | 92.79% | 37.8
4146 | 613 | 318 | 81 | 14.1041 | 25.9 | 308.5336 | 0 | 131.1161 | 0 | 12.1028 | 0 | 0 | 12.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 20.7895 | 41.58% | 37.1028
4147 | 345 | 123 | 52 | 11.6862 | 24.1 | 173.6445 | 0 | 0 | 0 | 2.7561 | 0 | 0 | 2.7561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 20.2986 | 2.7756e-15 | 5.551e-15% | 23.0547
4148 | 14 | 9 | 8 | 9.2684 | 22 | 7.0464 | 0 | 0 | 0 | 0.036411 | 0 | 0 | 0.036411 | 0 | 0 | 0 | 91.9614 | 36.1636 | 0 | 91.9614 | 1186.4794 | 93.09% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.2
4149 | 0 | 0 | 0 | 7.6565 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5542 | 34 | 0 | 86.5542 | 1104.5895 | 86.67% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34
4150 | 0 | 0 | 0 | 5.0372 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1254 | 32.2 | 0 | 82.1254 | 1027.791 | 80.64% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.2
4151 | 0 | 0 | 0 | 2.6193 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2479 | 30.6 | 0 | 78.2479 | 955.2817 | 74.95% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.6
4152 | 0 | 0 | 0 | 2.6193 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1326 | 29.7 | 0 | 76.1326 | 884.995 | 69.44% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 29.7
4153 | 0 | 0 | 0 | 3.0223 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.0553 | 29.2 | 0 | 75.0553 | 815.7416 | 64% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 29.2
4154 | 0 | 0 | 0 | 2.8208 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5162 | 29 | 0 | 74.5162 | 746.9948 | 58.61% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 29
4155 | 0 | 0 | 0 | 3.0223 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0008 | 28.8 | 0 | 74.0008 | 678.7321 | 53.25% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 28.8
4156 | 0 | 0 | 0 | 3.4253 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5136 | 28.6 | 0 | 73.5136 | 610.9269 | 47.93% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 28.6
4157 | 0 | 1 | 1 | 3.0223 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8074 | 30.5 | 0 | 77.8074 | 538.8019 | 42.28% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.5
4158 | 249 | 68 | 33 | 1.6119 | 17.8 | 125.326 | 0 | 48.9025 | 0 | 1.6046 | 0 | 0 | 1.6046 | 0 | 0 | 0 | 79.4136 | 31.1954 | 0 | 79.4136 | 464.7817 | 36.47% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.8
4159 | 569 | 247 | 69 | 1.2089 | 20.6 | 286.3876 | 144.1597 | 0 | 117.2671 | 5.8515 | 0 | 0 | 5.8515 | 0 | 0 | 0 | 75.0296 | 29.1485 | 117.2671 | 75.0296 | 504.4249 | 39.58% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35
4160 | 732 | 451 | 86 | 2.6193 | 23.2 | 368.4283 | 211.1648 | 0 | 179.4253 | 25.8003 | 0 | 0 | 25.8003 | 0 | 0 | 0 | 0 | 0 | 179.4253 | 0 | 670.9715 | 52.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 25.8003
4161 | 822 | 646 | 95 | 8.0595 | 26 | 413.7269 | 252.7049 | 0 | 215.522 | 59.1415 | 0 | 11.1208 | 48.0208 | 0 | 0 | 0 | 0 | 0 | 215.522 | 0 | 871.0239 | 68.34% | 8.5296 | 0 | 8.7385 | 17.48% | 36.9
4162 | 857 | 806 | 109 | 11.6862 | 27.2 | 431.343 | 274.0715 | 0 | 233.3579 | 91.0242 | 1.6121 | 25 | 64.4121 | 0 | 0 | 0 | 0 | 0 | 233.3579 | 0 | 1087.632 | 85.34% | 19.175 | 0 | 28.383 | 56.77% | 37.8
4163 | 890 | 927 | 111 | 12.0892 | 28.6 | 447.9525 | 292.1472 | 0 | 250.2882 | 112.1 | 12.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 250.2882 | 0 | 1274.5104 | 100% | 19.175 | 0 | 48.0275 | 96.06% | 37.9
4164 | 905 | 995 | 112 | 12.8952 | 29.6 | 455.5022 | 0 | 300.6589 | 0 | 113.5 | 35.9898 | 2.5102 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 1.9253 | 0 | 50 | 100% | 36.5
4165 | 901 | 1006 | 118 | 12.2907 | 30.4 | 453.489 | 0 | 297.3308 | 0 | 114.2 | 39.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.8
4166 | 872 | 955 | 132 | 12.0892 | 30.9 | 438.8928 | 0 | 280.9864 | 0 | 114.4 | 39.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.6
4167 | 822 | 848 | 142 | 12.6937 | 30.4 | 413.7269 | 0 | 255.4479 | 0 | 101.5637 | 33.0319 | 0 | 68.5319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.5
4168 | 776 | 703 | 136 | 12.8952 | 30.1 | 390.5743 | 0 | 228.0115 | 0 | 72.1895 | 18.1948 | 0 | 53.9948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.8
4169 | 668 | 518 | 136 | 12.8952 | 29.5 | 336.216 | 0 | 176.3466 | 0 | 34.249 | 0 | 0 | 34.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.249
4170 | 473 | 309 | 123 | 13.4996 | 27.9 | 238.0691 | 0 | 101.0762 | 0 | 13.4433 | 0 | 0 | 13.4433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.7567 | 25.6652 | 51.33% | 37.2
4171 | 219 | 119 | 72 | 12.6937 | 25.1 | 110.2265 | 0 | 0 | 0 | 4.1223 | 0 | 0 | 4.1223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 0.055539 | 0.1111% | 29.1223
4172 | 2 | 6 | 5 | 9.2684 | 22.5 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8983 | 36.1 | 0 | 91.8983 | 1186.6091 | 93.1% | 0 | 0 | 0.055539 | 0.1111% | 36.1
4173 | 0 | 0 | 0 | 8.0595 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.873 | 34.1 | 0 | 86.873 | 1104.3853 | 86.65% | 0 | 0 | 0.055539 | 0.1111% | 34.1
4174 | 0 | 0 | 0 | 4.0297 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3408 | 32.3 | 0 | 82.3408 | 1027.299 | 80.6% | 0 | 0 | 0.055539 | 0.1111% | 32.3
4175 | 0 | 0 | 0 | 2.2164 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1732 | 31 | 0 | 79.1732 | 953.7238 | 74.83% | 0 | 0 | 0.055539 | 0.1111% | 31
4176 | 0 | 0 | 0 | 2.8208 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2632 | 30.2 | 0 | 77.2632 | 882.2435 | 69.22% | 0 | 0 | 0.055539 | 0.1111% | 30.2
4177 | 0 | 0 | 0 | 2.6193 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.4512 | 29.9 | 0 | 76.4512 | 811.5954 | 63.68% | 0 | 0 | 0.055539 | 0.1111% | 29.9
4178 | 0 | 0 | 0 | 2.0149 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1983 | 30.3 | 0 | 77.1983 | 740.0794 | 58.07% | 0 | 0 | 0.055539 | 0.1111% | 30.3
4179 | 0 | 0 | 0 | 0.40297 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2437 | 32 | 0 | 81.2437 | 663.7948 | 52.08% | 0 | 0 | 0.055539 | 0.1111% | 32
4180 | 0 | 0 | 0 | 1.8134 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4455 | 34.2 | 0 | 86.4455 | 581.1978 | 45.6% | 0 | 0 | 0.055539 | 0.1111% | 34.2
4181 | 0 | 1 | 1 | 2.2164 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5263 | 36.3 | 0 | 91.5263 | 492.6176 | 38.65% | 0 | 0 | 0.055539 | 0.1111% | 36.3
4182 | 123 | 56 | 37 | 2.8208 | 18.5 | 61.908 | 0 | 24.1845 | 0 | 1.9311 | 0 | 0 | 1.9311 | 0 | 0 | 0 | 93.4165 | 36.9689 | 0 | 93.4165 | 402.132 | 31.55% | 0 | 0 | 0.055539 | 0.1111% | 38.9
4183 | 473 | 237 | 87 | 2.2164 | 21.4 | 238.0691 | 119.9243 | 0 | 94.2786 | 6.7215 | 0 | 0 | 6.7215 | 0 | 0 | 0 | 85.6598 | 33.5785 | 94.2786 | 85.6598 | 409.5769 | 32.14% | 0 | 0 | 0.055539 | 0.1111% | 40.3
4184 | 656 | 442 | 112 | 6.4476 | 23.9 | 330.1762 | 189.2902 | 0 | 157.2735 | 25.7357 | 0 | 0 | 25.7357 | 0 | 0 | 0 | 0 | 0 | 157.2735 | 0 | 557.0207 | 43.7% | 0 | 0 | 0.055539 | 0.1111% | 25.7357
4185 | 766 | 633 | 125 | 6.0446 | 25.3 | 385.5411 | 235.5272 | 0 | 200.8393 | 52.9508 | 0 | 5.4254 | 47.5254 | 0 | 0 | 0 | 0 | 0 | 200.8393 | 0 | 745.3075 | 58.48% | 4.1613 | 0 | 4.3193 | 8.639% | 42.1
4186 | 828 | 800 | 133 | 5.0372 | 26.8 | 416.7468 | 264.833 | 0 | 228.6509 | 84.1679 | 0 | 20.734 | 63.434 | 0 | 0 | 0 | 0 | 0 | 228.6509 | 0 | 959.6676 | 75.3% | 15.903 | 0 | 20.614 | 41.23% | 42.7
4187 | 875 | 921 | 124 | 5.8431 | 28.2 | 440.4027 | 287.2474 | 0 | 249.3101 | 106.8305 | 7.3653 | 25 | 74.4653 | 0 | 0 | 0 | 0 | 0 | 249.3101 | 0 | 1193.3957 | 93.64% | 19.175 | 0 | 40.2614 | 80.52% | 42.1
4188 | 884 | 985 | 128 | 4.8357 | 29.6 | 444.9326 | 178.6113 | 115.078 | 155.6757 | 109.1 | 21.71 | 12.39 | 75 | 0 | 0 | 0 | 0 | 0 | 155.6757 | 0 | 1274.5104 | 100% | 9.5032 | 0 | 49.9987 | 100% | 40.9
4189 | 864 | 986 | 141 | 5.0372 | 29.9 | 434.8662 | 0 | 285.1032 | 0 | 109.6 | 34.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9987 | 100% | 40.4
4190 | 863 | 957 | 146 | 4.4327 | 31 | 434.3629 | 0 | 278.0607 | 0 | 109.5 | 34.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9987 | 100% | 40.5
4191 | 789 | 832 | 156 | 4.6342 | 31.1 | 397.1174 | 0 | 245.1577 | 0 | 90.6228 | 25.1614 | 0 | 65.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9987 | 100% | 40.3
4192 | 771 | 689 | 130 | 6.4476 | 30.3 | 388.0577 | 0 | 226.483 | 0 | 64.649 | 12.1245 | 0 | 52.5245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9987 | 100% | 40.4
4193 | 723 | 517 | 107 | 8.261 | 29.8 | 363.8985 | 0 | 190.7699 | 0 | 33.7945 | 0 | 0 | 33.7945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.7055 | 43.1291 | 86.26% | 40.5
4194 | 539 | 299 | 91 | 7.858 | 28.7 | 271.2881 | 0 | 115.0651 | 0 | 11.9872 | 0 | 0 | 11.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.5167 | 35.03% | 36.9872
4195 | 199 | 90 | 46 | 7.455 | 26.9 | 100.1602 | 0 | 0 | 0 | 2.3412 | 0 | 0 | 2.3412 | 0 | 0 | 0 | 57.9601 | 21.1593 | 0 | 57.9601 | 1221.7802 | 95.86% | 0 | 17.0995 | 2.7756e-15 | 5.551e-15% | 40.6
4196 | 15 | 9 | 8 | 4.6342 | 24.6 | 7.5498 | 0 | 0 | 0 | 0.031394 | 0 | 0 | 0.031394 | 0 | 0 | 0 | 96.3575 | 37.7686 | 0 | 96.3575 | 1129.0959 | 88.59% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.8
4197 | 0 | 0 | 0 | 4.6342 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9649 | 36.5 | 0 | 92.9649 | 1040.0689 | 81.61% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.5
4198 | 0 | 0 | 0 | 2.0149 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7635 | 34.4 | 0 | 87.7635 | 956.8994 | 75.08% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.4
4199 | 0 | 0 | 0 | 1.0074 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2751 | 33.4 | 0 | 85.2751 | 876.5495 | 68.78% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.4
4200 | 0 | 0 | 0 | 0.60446 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5177 | 32.7 | 0 | 83.5177 | 798.1651 | 62.63% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.7
4201 | 0 | 0 | 0 | 2.4178 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1753 | 32.6 | 0 | 83.1753 | 720.1359 | 56.5% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.6
4202 | 0 | 0 | 0 | 2.8208 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5402 | 33.2 | 0 | 84.5402 | 640.4535 | 50.25% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.2
4203 | 0 | 0 | 0 | 2.4178 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8046 | 35.8 | 0 | 90.8046 | 553.3119 | 43.41% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.8
4204 | 0 | 0 | 0 | 2.0149 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5095 | 39 | 0 | 98.5095 | 457.072 | 35.86% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39
4205 | 0 | 1 | 1 | 1.2089 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3229 | 41.9 | 0 | 105.3229 | 352.5535 | 27.66% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.9
4206 | 188 | 62 | 35 | 1.2089 | 20 | 94.6237 | 0 | 37.0037 | 0 | 1.709 | 0 | 0 | 1.709 | 0 | 0 | 0 | 108.1797 | 42.991 | 0 | 108.1797 | 244.8931 | 19.21% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 44.7
4207 | 506 | 233 | 76 | 3.6268 | 22.5 | 254.6786 | 128.3778 | 0 | 101.5699 | 6.1016 | 0 | 0 | 6.1016 | 0 | 0 | 0 | 101.3488 | 39.9984 | 101.5699 | 101.3488 | 242.1866 | 19% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 46.1
4208 | 670 | 431 | 101 | 5.6416 | 25.3 | 337.2226 | 193.3799 | 0 | 161.6012 | 25.032 | 0 | 0 | 25.032 | 0 | 0 | 0 | 59.2805 | 21.868 | 161.6012 | 59.2805 | 341.9291 | 26.83% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 46.9
4209 | 767 | 623 | 115 | 4.2312 | 27.1 | 386.0444 | 235.8737 | 0 | 202.0528 | 46.1582 | 0 | 0 | 46.1582 | 0 | 0 | 0 | 0 | 0 | 202.0528 | 0 | 533.7259 | 41.88% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 46.1582
4210 | 831 | 788 | 120 | 4.2312 | 28.6 | 418.2567 | 265.8291 | 0 | 229.8809 | 74.995 | 0 | 13.3475 | 61.6475 | 0 | 0 | 0 | 0 | 0 | 229.8809 | 0 | 751.9382 | 59% | 10.2375 | 0 | 10.4912 | 20.98% | 48.3
4211 | 872 | 911 | 119 | 4.0297 | 30.2 | 438.8928 | 286.2873 | 0 | 249.2348 | 97.4365 | 0 | 24.9183 | 72.5183 | 0 | 0 | 0 | 0 | 0 | 249.2348 | 0 | 988.522 | 77.56% | 19.1123 | 0 | 30.0772 | 60.15% | 47.6
4212 | 888 | 980 | 120 | 6.4476 | 31.1 | 446.9458 | 295.027 | 0 | 256.3369 | 103 | 3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 256.3369 | 0 | 1231.8475 | 96.65% | 19.175 | 0 | 49.7275 | 99.45% | 47
4213 | 898 | 995 | 117 | 7.6565 | 31 | 451.979 | 0 | 296.3047 | 0 | 103 | 28 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.8475 | 96.65% | 0 | 0 | 49.7275 | 99.45% | 47
4214 | 889 | 949 | 115 | 9.6714 | 31.5 | 447.4492 | 0 | 286.4131 | 0 | 102.9 | 27.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.8475 | 96.65% | 0 | 0 | 49.7275 | 99.45% | 47.1
4215 | 868 | 851 | 111 | 11.4848 | 30.5 | 436.8795 | 0 | 269.6672 | 0 | 91.1928 | 22.4464 | 0 | 68.7464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.8475 | 96.65% | 0 | 0 | 49.7275 | 99.45% | 46.3
4216 | 835 | 706 | 102 | 10.2758 | 30.5 | 420.27 | 0 | 245.2187 | 0 | 62.5225 | 8.3113 | 0 | 54.2113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.8475 | 96.65% | 0 | 0 | 49.7275 | 99.45% | 45.9
4217 | 777 | 526 | 87 | 9.0669 | 30.4 | 391.0776 | 0 | 204.9116 | 0 | 34.3379 | 0 | 0 | 34.3379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.8475 | 96.65% | 0 | 10.9621 | 38.4955 | 76.99% | 45.3
4218 | 658 | 325 | 72 | 9.0669 | 29.7 | 331.1828 | 0 | 140.3213 | 0 | 11.8965 | 0 | 0 | 11.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.8475 | 96.65% | 0 | 25 | 12.8791 | 25.76% | 36.8965
4219 | 387 | 130 | 50 | 6.6491 | 26.3 | 194.7838 | 0 | 0 | 0 | 2.6713 | 0 | 0 | 2.6713 | 0 | 0 | 0 | 74.4721 | 28.4589 | 0 | 74.4721 | 1163.2653 | 91.27% | 0 | 12.5698 | 0 | 0% | 43.7
4220 | 22 | 10 | 8 | 5.8431 | 22.9 | 11.073 | 0 | 0 | 0 | 0.034649 | 0 | 0 | 0.034649 | 0 | 0 | 0 | 103.0538 | 40.6654 | 0 | 103.0538 | 1062.4514 | 83.36% | 0 | 0 | 0 | 0% | 40.7
4221 | 0 | 0 | 0 | 2.2164 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3379 | 38.8 | 0 | 98.3379 | 966.9493 | 75.87% | 0 | 0 | 0 | 0% | 38.8
4222 | 0 | 0 | 0 | 6.0446 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1908 | 36.7 | 0 | 93.1908 | 877.4009 | 68.84% | 0 | 0 | 0 | 0% | 36.7
4223 | 0 | 0 | 0 | 4.4327 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6938 | 35.3 | 0 | 89.6938 | 791.76 | 62.12% | 0 | 0 | 0 | 0% | 35.3
4224 | 0 | 0 | 0 | 3.8283 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8358 | 34.5 | 0 | 87.8358 | 708.3978 | 55.58% | 0 | 0 | 0 | 0% | 34.5
4225 | 0 | 0 | 0 | 1.8134 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.431 | 34.4 | 0 | 87.431 | 625.3128 | 49.06% | 0 | 0 | 0 | 0% | 34.4
4226 | 0 | 0 | 0 | 2.6193 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3293 | 34.8 | 0 | 88.3293 | 541.0489 | 42.45% | 0 | 0 | 0 | 0% | 34.8
4227 | 0 | 0 | 0 | 3.8283 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3439 | 36.9 | 0 | 93.3439 | 450.8622 | 35.38% | 0 | 0 | 0 | 0% | 36.9
4228 | 0 | 0 | 0 | 7.455 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0936 | 40.1 | 0 | 101.0936 | 351.5035 | 27.58% | 0 | 0 | 0 | 0% | 40.1
4229 | 0 | 0 | 0 | 5.8431 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.6402 | 43.2 | 0 | 108.6402 | 243.3243 | 19.09% | 0 | 0 | 0 | 0% | 43.2
4230 | 0 | 17 | 17 | 4.6342 | 20.2 | 0 | 0 | 0 | 0 | 0.75325 | 0 | 0 | 0.75325 | 0 | 0 | 0 | 95.925 | 37.903 | 0 | 95.925 | 150.2158 | 11.79% | 0 | 0 | 0 | 0% | 38.6563
4231 | 0 | 66 | 66 | 2.8208 | 20.9 | 0 | 0 | 0 | 0 | 4.4881 | 0 | 0 | 4.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.2158 | 11.79% | 0 | 0 | 0 | 0% | 4.4881
4232 | 0 | 154 | 152 | 5.6416 | 22.1 | 0 | 0 | 0 | 0 | 10.8845 | 0 | 0 | 10.8845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.2158 | 11.79% | 0 | 0 | 0 | 0% | 10.8845
4233 | 126 | 437 | 342 | 7.455 | 23.7 | 63.418 | 0 | 38.755 | 0 | 31.6777 | 0 | 0 | 31.6777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.2158 | 11.79% | 0 | 0 | 0 | 0% | 31.6777
4234 | 798 | 798 | 158 | 8.4625 | 25.6 | 401.6473 | 255.3083 | 0 | 217.6913 | 79.0664 | 0 | 14.5332 | 64.5332 | 0 | 0 | 0 | 0 | 0 | 217.6913 | 0 | 358.2145 | 28.11% | 11.147 | 0 | 11.4248 | 22.85% | 50
4235 | 849 | 913 | 143 | 7.858 | 27.3 | 427.3165 | 278.7608 | 0 | 240.0655 | 100.3418 | 0.47091 | 25 | 74.8709 | 0 | 0 | 0 | 0 | 0 | 240.0655 | 0 | 587.5911 | 46.1% | 19.175 | 0 | 31.0779 | 62.16% | 49.4
4236 | 853 | 980 | 153 | 6.2461 | 28.8 | 429.3297 | 283.4088 | 0 | 245.4448 | 101.4 | 2.3299 | 24.0701 | 75 | 0 | 0 | 0 | 0 | 0 | 245.4448 | 0 | 822.1075 | 64.5% | 18.4618 | 0 | 50 | 100% | 48.6
4237 | 854 | 990 | 154 | 8.0595 | 29.8 | 429.833 | 281.77 | 0 | 242.8419 | 101.4 | 26.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 242.8419 | 0 | 1054.1369 | 82.71% | 0 | 0 | 50 | 100% | 48.6
4238 | 856 | 949 | 144 | 7.858 | 30.9 | 430.8397 | 275.7591 | 0 | 237.3094 | 101.4 | 26.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 237.3094 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.6
4239 | 500 | 667 | 239 | 8.8654 | 30.7 | 251.6587 | 0 | 155.3175 | 0 | 59.8136 | 6.0068 | 0 | 53.8068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.8
4240 | 772 | 718 | 156 | 11.6862 | 30.5 | 388.561 | 0 | 226.6573 | 0 | 63.3056 | 8.0028 | 0 | 55.3028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.3
4241 | 627 | 516 | 161 | 13.7011 | 28.9 | 315.58 | 0 | 165.2649 | 0 | 34.9746 | 0 | 0 | 34.9746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 11.5254 | 38.1891 | 76.38% | 46.5
4242 | 455 | 309 | 132 | 13.4996 | 27.6 | 229.0094 | 0 | 96.9232 | 0 | 14.0382 | 0 | 0 | 14.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 12.569 | 25.14% | 39.0382
4243 | 142 | 100 | 65 | 10.8803 | 26.7 | 71.4711 | 0 | 0 | 0 | 3.684 | 0 | 0 | 3.684 | 0 | 0 | 0 | 75.6533 | 28.9505 | 0 | 75.6533 | 1204.782 | 94.53% | 0 | 12.2655 | 0 | 0% | 44.9
4244 | 4 | 5 | 5 | 8.4625 | 24.5 | 2.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8844 | 41.7 | 0 | 105.8844 | 1101.0307 | 86.39% | 0 | 0 | 0 | 0% | 41.7
4245 | 0 | 0 | 0 | 4.2312 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9498 | 39.7 | 0 | 100.9498 | 1002.9235 | 78.69% | 0 | 0 | 0 | 0% | 39.7
4246 | 0 | 0 | 0 | 3.0223 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0443 | 37.3 | 0 | 95.0443 | 911.6672 | 71.53% | 0 | 0 | 0 | 0% | 37.3
4247 | 0 | 0 | 0 | 3.6268 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8433 | 35.6 | 0 | 90.8433 | 825.0837 | 64.74% | 0 | 0 | 0 | 0% | 35.6
4248 | 0 | 0 | 0 | 3.4253 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4457 | 34.7 | 0 | 88.4457 | 741.1276 | 58.15% | 0 | 0 | 0 | 0% | 34.7
4249 | 0 | 0 | 0 | 3.6268 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7635 | 34.4 | 0 | 87.7635 | 657.9578 | 51.62% | 0 | 0 | 0 | 0% | 34.4
4250 | 0 | 0 | 0 | 5.6416 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.959 | 34.9 | 0 | 88.959 | 573.3907 | 44.99% | 0 | 0 | 0 | 0% | 34.9
4251 | 0 | 0 | 0 | 5.0372 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1837 | 37.1 | 0 | 94.1837 | 482.6273 | 37.87% | 0 | 0 | 0 | 0% | 37.1
4252 | 0 | 0 | 0 | 2.2164 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6996 | 40.3 | 0 | 101.6996 | 382.6953 | 30.03% | 0 | 0 | 0 | 0% | 40.3
4253 | 0 | 1 | 1 | 4.6342 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.4238 | 43.5 | 0 | 109.4238 | 273.6443 | 21.47% | 0 | 0 | 0 | 0% | 43.5
4254 | 19 | 49 | 46 | 9.4699 | 20.9 | 9.563 | 0 | 3.7463 | 0 | 2.5037 | 0 | 0 | 2.5037 | 0 | 0 | 0 | 87.7259 | 34.4612 | 0 | 87.7259 | 190.2774 | 14.93% | 0 | 0 | 0 | 0% | 36.9649
4255 | 88 | 161 | 133 | 12.2907 | 23.1 | 44.2919 | 0 | 22.3535 | 0 | 8.9472 | 0 | 0 | 8.9472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.2774 | 14.93% | 0 | 0 | 0 | 0% | 8.9472
4256 | 252 | 359 | 226 | 12.0892 | 24.8 | 126.836 | 72.7705 | 0 | 44.4463 | 22.9214 | 0 | 0 | 22.9214 | 0 | 0 | 0 | 0 | 0 | 44.4463 | 0 | 232.773 | 18.26% | 0 | 0 | 0 | 0% | 22.9214
4257 | 391 | 549 | 277 | 13.4996 | 27.2 | 196.7971 | 120.2841 | 0 | 88.8123 | 40.3373 | 0 | 0 | 40.3373 | 0 | 0 | 0 | 0 | 0 | 88.8123 | 0 | 317.6875 | 24.93% | 0 | 0 | 0 | 0% | 40.3373
4258 | 570 | 811 | 345 | 15.1115 | 29.2 | 286.8909 | 182.3888 | 0 | 145.9147 | 78.0321 | 0 | 14.016 | 64.016 | 0 | 0 | 0 | 0 | 0 | 145.9147 | 0 | 457.1982 | 35.87% | 10.7503 | 0 | 11.0199 | 22.04% | 50
4259 | 347 | 697 | 372 | 14.7085 | 30.3 | 174.6511 | 113.9444 | 0 | 82.2344 | 61.6611 | 0 | 5.8306 | 55.8306 | 0 | 0 | 0 | 0 | 0 | 82.2344 | 0 | 535.8234 | 42.04% | 4.472 | 0 | 15.6041 | 31.21% | 50
4260 | 570 | 939 | 374 | 14.5071 | 31 | 286.8909 | 189.3901 | 0 | 152.8247 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 152.8247 | 0 | 681.9409 | 53.51% | 19.175 | 0 | 35.26 | 70.52% | 50
4261 | 552 | 949 | 394 | 14.91 | 31.8 | 277.8312 | 182.1174 | 0 | 145.8722 | 100 | 6.2526 | 18.7474 | 75 | 0 | 0 | 0 | 0 | 0 | 145.8722 | 0 | 821.411 | 64.45% | 14.3793 | 0 | 50 | 100% | 50
4262 | 439 | 831 | 409 | 16.119 | 31.1 | 220.9563 | 141.4126 | 0 | 107.1276 | 85.198 | 17.599 | 0 | 67.599 | 0 | 0 | 0 | 0 | 0 | 107.1276 | 0 | 923.837 | 72.49% | 0 | 0 | 50 | 100% | 50
4263 | 658 | 825 | 255 | 16.9249 | 31.5 | 331.1828 | 204.3716 | 0 | 165.6327 | 83.372 | 16.836 | 0 | 66.536 | 0 | 0 | 0 | 0 | 0 | 165.6327 | 0 | 1082.2004 | 84.91% | 0 | 0 | 50 | 100% | 49.7
4264 | 624 | 677 | 217 | 16.7234 | 32.2 | 314.0701 | 183.1564 | 0 | 145.8575 | 54.7923 | 2.8961 | 0 | 51.8961 | 0 | 0 | 0 | 0 | 0 | 145.8575 | 0 | 1221.6565 | 95.85% | 0 | 0 | 50 | 100% | 49
4265 | 536 | 496 | 188 | 15.313 | 30.6 | 269.7781 | 141.2015 | 0 | 107.3442 | 33.3544 | 0 | 0 | 33.3544 | 0 | 0 | 0 | 0 | 0 | 107.3442 | 0 | 1274.5104 | 100% | 0 | 14.6456 | 34.9894 | 69.98% | 48
4266 | 313 | 282 | 155 | 14.1041 | 28.7 | 157.5383 | 0 | 66.5973 | 0 | 14.0057 | 0 | 0 | 14.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 9.3655 | 18.73% | 39.0057
4267 | 77 | 102 | 84 | 11.6862 | 27.1 | 38.7554 | 0 | 0 | 0 | 4.847 | 0 | 0 | 4.847 | 0 | 0 | 0 | 83.4365 | 32.2147 | 0 | 83.4365 | 1196.5246 | 93.88% | 0 | 9.1383 | 1.3878e-15 | 2.776e-15% | 46.2
4268 | 2 | 9 | 9 | 10.2758 | 25.3 | 1.0066 | 0 | 0 | 0 | 0.082067 | 0 | 0 | 0.082067 | 0 | 0 | 0 | 108.7509 | 42.8179 | 0 | 108.7509 | 1089.6192 | 85.49% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 42.9
4269 | 0 | 0 | 0 | 7.6565 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0779 | 40.6 | 0 | 103.0779 | 988.9833 | 77.6% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 40.6
4270 | 0 | 0 | 0 | 6.8506 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8434 | 38 | 0 | 96.8434 | 895.7607 | 70.28% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 38
4271 | 0 | 0 | 0 | 7.052 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9925 | 36.2 | 0 | 92.9925 | 806.9259 | 63.31% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 36.2
4272 | 0 | 0 | 0 | 5.6416 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7043 | 35.3 | 0 | 90.7043 | 720.5898 | 56.54% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 35.3
4273 | 0 | 0 | 0 | 4.6342 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4662 | 35 | 0 | 89.4662 | 635.5254 | 49.86% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 35
4274 | 0 | 0 | 0 | 4.2312 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.02 | 35.3 | 0 | 90.02 | 549.8123 | 43.14% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 35.3
4275 | 0 | 0 | 0 | 2.6193 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1648 | 37.5 | 0 | 95.1648 | 457.9354 | 35.93% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 37.5
4276 | 0 | 0 | 0 | 3.4253 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9463 | 40.7 | 0 | 102.9463 | 356.8989 | 28% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 40.7
4277 | 0 | 1 | 1 | 2.2164 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.0919 | 43.6 | 0 | 110.0919 | 247.5826 | 19.43% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 43.6
4278 | 79 | 55 | 43 | 3.4253 | 22.4 | 39.7621 | 0 | 15.5881 | 0 | 2.2712 | 0 | 0 | 2.2712 | 0 | 0 | 0 | 65.6523 | 24.8657 | 0 | 65.6523 | 187.3173 | 14.7% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 27.1369
4279 | 350 | 220 | 110 | 1.4104 | 26 | 176.1611 | 88.9526 | 0 | 65.6819 | 7.7025 | 0 | 0 | 7.7025 | 0 | 0 | 0 | 0 | 0 | 65.6819 | 0 | 250.1967 | 19.63% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 7.7025
4280 | 539 | 421 | 155 | 6.2461 | 28.3 | 271.2881 | 155.686 | 0 | 126.0487 | 25.0827 | 0 | 0 | 25.0827 | 0 | 0 | 0 | 62.5315 | 22.9596 | 126.0487 | 62.5315 | 313.7055 | 24.61% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 48.0423
4281 | 656 | 616 | 181 | 10.0743 | 31.4 | 330.1762 | 201.8417 | 0 | 167.1132 | 45.7632 | 0 | 0 | 45.7632 | 0 | 0 | 0 | 0 | 0 | 167.1132 | 0 | 473.2256 | 37.13% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 45.7632
4282 | 731 | 784 | 195 | 12.0892 | 33.3 | 367.925 | 233.9391 | 0 | 196.0366 | 74.2274 | 0 | 12.1137 | 62.1137 | 0 | 0 | 0 | 0 | 0 | 196.0366 | 0 | 660.3548 | 51.81% | 9.2912 | 0 | 9.5256 | 19.05% | 50
4283 | 771 | 909 | 206 | 13.2981 | 34.1 | 388.0577 | 253.1968 | 0 | 213.1147 | 98.5011 | 0 | 24.2506 | 74.2506 | 0 | 0 | 0 | 0 | 0 | 213.1147 | 0 | 863.7862 | 67.77% | 18.6002 | 0 | 28.595 | 57.19% | 50
4284 | 789 | 979 | 211 | 14.3056 | 34.6 | 397.1174 | 262.1683 | 0 | 220.8952 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 220.8952 | 0 | 1074.6445 | 84.32% | 19.175 | 0 | 48.2538 | 96.51% | 50
4285 | 798 | 992 | 206 | 14.7085 | 34.6 | 401.6473 | 263.2641 | 0 | 221.6847 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 221.6847 | 0 | 1274.5104 | 100% | 0 | 0 | 48.2538 | 96.51% | 50
4286 | 800 | 951 | 196 | 15.716 | 34.5 | 402.6539 | 0 | 257.6819 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.2538 | 96.51% | 50
4287 | 789 | 857 | 181 | 18.1338 | 34.2 | 397.1174 | 0 | 245.0295 | 0 | 88.239 | 19.1195 | 0 | 69.1195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.2538 | 96.51% | 50
4288 | 733 | 704 | 168 | 16.5219 | 33.8 | 368.9316 | 0 | 215.0932 | 0 | 58.2904 | 4.3452 | 0 | 53.9452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.2538 | 96.51% | 49.6
4289 | 636 | 516 | 153 | 14.91 | 32.8 | 320.1099 | 0 | 167.4508 | 0 | 34.3839 | 0 | 0 | 34.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 14.1161 | 33.7838 | 67.57% | 48.5
4290 | 478 | 312 | 126 | 13.7011 | 31.6 | 240.5857 | 0 | 101.5811 | 0 | 13.763 | 0 | 0 | 13.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 8.1562 | 16.31% | 38.763
4291 | 221 | 120 | 73 | 14.91 | 29.4 | 111.2331 | 0 | 0 | 0 | 4.1082 | 0 | 0 | 4.1082 | 0 | 0 | 0 | 87.8818 | 33.8346 | 0 | 87.8818 | 1191.591 | 93.49% | 0 | 7.9572 | 0 | 0% | 45.9
4292 | 8 | 10 | 9 | 12.2907 | 26.9 | 4.0265 | 0 | 0 | 0 | 0.078685 | 0 | 0 | 0.078685 | 0 | 0 | 0 | 109.3366 | 42.9213 | 0 | 109.3366 | 1084.3694 | 85.08% | 0 | 0 | 0 | 0% | 43
4293 | 0 | 0 | 0 | 13.0966 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.4873 | 41.4 | 0 | 105.4873 | 981.4777 | 77.01% | 0 | 0 | 0 | 0% | 41.4
4294 | 0 | 0 | 0 | 10.2758 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0565 | 38.8 | 0 | 99.0565 | 885.8203 | 69.5% | 0 | 0 | 0 | 0% | 38.8
4295 | 0 | 0 | 0 | 8.8654 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7516 | 36.7 | 0 | 93.7516 | 796.072 | 62.46% | 0 | 0 | 0 | 0% | 36.7
4296 | 0 | 0 | 0 | 6.0446 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3184 | 35.4 | 0 | 90.3184 | 710.067 | 55.71% | 0 | 0 | 0 | 0% | 35.4
4297 | 0 | 0 | 0 | 3.8283 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2773 | 34.6 | 0 | 88.2773 | 626.33 | 49.14% | 0 | 0 | 0 | 0% | 34.6
4298 | 0 | 0 | 0 | 2.2164 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0627 | 34.1 | 0 | 87.0627 | 543.9733 | 42.68% | 0 | 0 | 0 | 0% | 34.1
4299 | 0 | 0 | 0 | 2.2164 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7445 | 33.6 | 0 | 85.7445 | 463.0855 | 36.33% | 0 | 0 | 0 | 0% | 33.6
4300 | 0 | 0 | 0 | 3.0223 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1441 | 34.2 | 0 | 87.1441 | 380.5397 | 29.86% | 0 | 0 | 0 | 0% | 34.2
4301 | 0 | 1 | 1 | 5.0372 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8262 | 36.9 | 0 | 93.8262 | 290.3189 | 22.78% | 0 | 0 | 0 | 0% | 36.9
4302 | 102 | 60 | 44 | 6.0446 | 23.3 | 51.3384 | 0 | 20.1385 | 0 | 2.2632 | 0 | 0 | 2.2632 | 0 | 0 | 0 | 62.0586 | 23.2263 | 0 | 62.0586 | 233.5486 | 18.32% | 0 | 0 | 0 | 0% | 25.4894
4303 | 363 | 229 | 116 | 3.6268 | 26 | 182.7042 | 92.3002 | 0 | 67.9523 | 8.1418 | 0 | 0 | 8.1418 | 0 | 0 | 0 | 0 | 0 | 67.9523 | 0 | 298.25 | 23.4% | 0 | 0 | 0 | 0% | 8.1418
4304 | 541 | 428 | 160 | 6.8506 | 28.5 | 272.2947 | 156.3009 | 0 | 126.2697 | 25.4651 | 0 | 0 | 25.4651 | 0 | 0 | 0 | 0 | 0 | 126.2697 | 0 | 418.4788 | 32.83% | 0 | 0 | 0 | 0% | 25.4651
4305 | 666 | 622 | 179 | 10.4773 | 30.4 | 335.2094 | 204.9546 | 0 | 169.8113 | 46.519 | 0.25952 | 0 | 46.2595 | 0 | 0 | 0 | 0 | 0 | 169.8113 | 0 | 580.1661 | 45.52% | 0 | 0 | 0 | 0% | 46
4306 | 734 | 787 | 194 | 11.6862 | 32.5 | 369.435 | 234.933 | 0 | 197.1641 | 77.7791 | 0 | 15.4395 | 62.3395 | 0 | 0 | 0 | 0 | 0 | 197.1641 | 0 | 767.8976 | 60.25% | 11.8421 | 0 | 12.1426 | 24.29% | 46.9
4307 | 774 | 911 | 204 | 12.4922 | 34 | 389.5677 | 254.2061 | 0 | 214.5155 | 101.74 | 2.52 | 25 | 74.22 | 0 | 0 | 0 | 0 | 0 | 214.5155 | 0 | 972.1505 | 76.28% | 19.175 | 0 | 31.8041 | 63.61% | 46.7
4308 | 785 | 979 | 213 | 13.4996 | 34.5 | 395.1041 | 260.8531 | 0 | 220.1322 | 104.2 | 6.0636 | 23.1364 | 75 | 0 | 0 | 0 | 0 | 0 | 220.1322 | 0 | 1181.7513 | 92.72% | 17.7456 | 0 | 50 | 100% | 45.8
4309 | 789 | 994 | 215 | 14.5071 | 34.8 | 397.1174 | 260.2813 | 0 | 219.0252 | 105.2 | 30.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 219.0252 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.8
4310 | 779 | 949 | 211 | 14.7085 | 35.2 | 392.0842 | 0 | 250.9022 | 0 | 105.4 | 30.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.6
4311 | 744 | 847 | 206 | 13.7011 | 35.5 | 374.4681 | 0 | 231.0273 | 0 | 90.7225 | 23.1612 | 0 | 67.5612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.4
4312 | 695 | 699 | 189 | 14.3056 | 35 | 349.8056 | 0 | 203.8886 | 0 | 62.1091 | 8.9546 | 0 | 53.1546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.2
4313 | 614 | 513 | 162 | 13.9026 | 34.1 | 309.0369 | 0 | 161.5655 | 0 | 34.1478 | 0 | 0 | 34.1478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.6522 | 40.1044 | 80.21% | 43.8
4314 | 462 | 308 | 128 | 13.4996 | 32.6 | 232.5326 | 0 | 98.0423 | 0 | 13.7164 | 0 | 0 | 13.7164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 14.4735 | 28.95% | 38.7164
4315 | 229 | 122 | 73 | 11.2833 | 30.5 | 115.2597 | 0 | 0 | 0 | 4.0863 | 0 | 0 | 4.0863 | 0 | 0 | 0 | 67.712 | 24.9959 | 0 | 67.712 | 1212.4462 | 95.13% | 0 | 14.1177 | 0 | 0% | 43.2
4316 | 10 | 11 | 10 | 11.6862 | 28.1 | 5.0332 | 0 | 0 | 0 | 0.12766 | 0 | 0 | 0.12766 | 0 | 0 | 0 | 104.6373 | 40.8723 | 0 | 104.6373 | 1110.5907 | 87.14% | 0 | 0 | 0 | 0% | 41
4317 | 0 | 0 | 0 | 6.2461 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3189 | 38.4 | 0 | 98.3189 | 1015.8019 | 79.7% | 0 | 0 | 0 | 0% | 38.4
4318 | 0 | 0 | 0 | 2.2164 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.922 | 35.9 | 0 | 91.922 | 928.0967 | 72.82% | 0 | 0 | 0 | 0% | 35.9
4319 | 0 | 0 | 0 | 2.2164 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9973 | 34 | 0 | 86.9973 | 845.8754 | 66.37% | 0 | 0 | 0 | 0% | 34
4320 | 0 | 0 | 0 | 4.4327 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2353 | 32.8 | 0 | 84.2353 | 766.8094 | 60.17% | 0 | 0 | 0 | 0% | 32.8
4321 | 0 | 0 | 0 | 3.0223 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.77 | 31.9 | 0 | 81.77 | 690.4457 | 54.17% | 0 | 0 | 0 | 0% | 31.9
4322 | 0 | 0 | 0 | 4.2312 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0777 | 31.6 | 0 | 81.0777 | 614.8478 | 48.24% | 0 | 0 | 0 | 0% | 31.6
4323 | 0 | 0 | 0 | 3.6268 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0449 | 31.2 | 0 | 80.0449 | 540.3723 | 42.4% | 0 | 0 | 0 | 0% | 31.2
4324 | 0 | 0 | 0 | 3.0223 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6691 | 31.1 | 0 | 79.6691 | 466.2755 | 36.58% | 0 | 0 | 0 | 0% | 31.1
4325 | 0 | 1 | 0 | 2.2164 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3903 | 32.7 | 0 | 83.3903 | 387.979 | 30.44% | 0 | 0 | 0 | 0% | 32.7
4326 | 177 | 62 | 36 | 0.80595 | 21.6 | 89.0872 | 0 | 34.9633 | 0 | 1.7435 | 0 | 0 | 1.7435 | 0 | 0 | 0 | 85.3886 | 33.4565 | 0 | 85.3886 | 307.4323 | 24.12% | 0 | 0 | 0 | 0% | 35.2
4327 | 524 | 241 | 80 | 2.8208 | 25.5 | 263.7383 | 133.2936 | 0 | 106.4467 | 6.2265 | 0 | 0 | 6.2265 | 0 | 0 | 0 | 81.0571 | 31.3735 | 106.4467 | 81.0571 | 332.029 | 26.05% | 0 | 0 | 0 | 0% | 37.6
4328 | 692 | 443 | 103 | 2.2164 | 27.8 | 348.2956 | 199.9728 | 0 | 169.1192 | 25.0275 | 0 | 0 | 25.0275 | 0 | 0 | 0 | 0 | 0 | 169.1192 | 0 | 490.9955 | 38.52% | 0 | 0 | 0 | 0% | 25.0275
4329 | 781 | 637 | 120 | 5.6416 | 30.4 | 393.0909 | 240.3874 | 0 | 205.6347 | 52.7694 | 0 | 6.0347 | 46.7347 | 0 | 0 | 0 | 0 | 0 | 205.6347 | 0 | 684.2853 | 53.69% | 4.6286 | 0 | 4.7467 | 9.493% | 40.7
4330 | 832 | 801 | 131 | 8.8654 | 32.6 | 418.7601 | 266.3387 | 0 | 227.9058 | 84.1838 | 0 | 21.1419 | 63.0419 | 0 | 0 | 0 | 0 | 0 | 227.9058 | 0 | 898.5092 | 70.5% | 16.2158 | 0 | 21.3764 | 42.75% | 41.9
4331 | 856 | 921 | 140 | 10.6788 | 34.1 | 430.8397 | 281.1646 | 0 | 240.8404 | 105.4943 | 6.4471 | 25 | 74.0471 | 0 | 0 | 0 | 0 | 0 | 240.8404 | 0 | 1124.8912 | 88.26% | 19.175 | 0 | 41.0408 | 82.08% | 42.6
4332 | 854 | 987 | 154 | 11.2833 | 35 | 429.833 | 283.7984 | 0 | 243.0091 | 108 | 21.6098 | 11.3902 | 75 | 0 | 0 | 0 | 0 | 0 | 243.0091 | 0 | 1274.5104 | 100% | 8.7363 | 0 | 50 | 100% | 42
4333 | 842 | 1000 | 169 | 12.2907 | 35.7 | 423.7932 | 0 | 277.7514 | 0 | 108.7 | 33.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.3
4334 | 752 | 928 | 213 | 12.6937 | 35.6 | 378.4947 | 0 | 242.1925 | 0 | 108.8 | 33.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.2
4335 | 713 | 834 | 219 | 11.2833 | 35.4 | 358.8653 | 0 | 221.3764 | 0 | 91.1574 | 24.9287 | 0 | 66.2287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.3
4336 | 723 | 696 | 166 | 11.0818 | 34.6 | 363.8985 | 0 | 212.047 | 0 | 64.0599 | 11.2299 | 0 | 52.8299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
4337 | 648 | 516 | 145 | 11.0818 | 34.1 | 326.1497 | 0 | 170.412 | 0 | 34.0633 | 0 | 0 | 34.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.0367 | 41.7594 | 83.52% | 42.1
4338 | 491 | 311 | 119 | 11.0818 | 33.1 | 247.1288 | 0 | 104.0051 | 0 | 13.4245 | 0 | 0 | 13.4245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.1248 | 32.25% | 38.4245
4339 | 215 | 118 | 71 | 10.2758 | 31.1 | 108.2132 | 0 | 0 | 0 | 3.9602 | 0 | 0 | 3.9602 | 0 | 0 | 0 | 66.1255 | 24.2137 | 0 | 66.1255 | 1213.9939 | 95.25% | 0 | 15.7261 | 0 | 0% | 43.9
4340 | 10 | 10 | 9 | 8.4625 | 28.8 | 5.0332 | 0 | 0 | 0 | 0.074579 | 0 | 0 | 0.074579 | 0 | 0 | 0 | 106.1435 | 41.4254 | 0 | 106.1435 | 1110.4694 | 87.13% | 0 | 0 | 0 | 0% | 41.5
4341 | 0 | 0 | 0 | 4.2312 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3387 | 38.4 | 0 | 98.3387 | 1015.6538 | 79.69% | 0 | 0 | 0 | 0% | 38.4
4342 | 0 | 0 | 0 | 3.8283 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1925 | 36 | 0 | 92.1925 | 927.6464 | 72.78% | 0 | 0 | 0 | 0% | 36
4343 | 0 | 0 | 0 | 1.2089 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3251 | 34.1 | 0 | 87.3251 | 845.0603 | 66.3% | 0 | 0 | 0 | 0% | 34.1
4344 | 0 | 0 | 0 | 1.2089 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5033 | 33.4 | 0 | 85.5033 | 764.5163 | 59.99% | 0 | 0 | 0 | 0% | 33.4
4345 | 0 | 0 | 0 | 2.8208 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7812 | 33.1 | 0 | 84.7812 | 684.78 | 53.73% | 0 | 0 | 0 | 0% | 33.1
4346 | 0 | 0 | 0 | 2.4178 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.069 | 33.7 | 0 | 86.069 | 603.535 | 47.35% | 0 | 0 | 0 | 0% | 33.7
4347 | 0 | 0 | 0 | 2.4178 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6714 | 36.5 | 0 | 92.6714 | 514.4632 | 40.37% | 0 | 0 | 0 | 0% | 36.5
4348 | 0 | 0 | 0 | 3.6268 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0913 | 39.9 | 0 | 101.0913 | 415.6627 | 32.61% | 0 | 0 | 0 | 0% | 39.9
4349 | 1 | 1 | 0 | 2.6193 | 21.9 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.0533 | 43.2 | 0 | 109.0533 | 307.4733 | 24.12% | 0 | 0 | 0 | 0% | 43.2
4350 | 154 | 53 | 31 | 3.8283 | 22.2 | 77.5109 | 0 | 30.4314 | 0 | 1.4273 | 0 | 0 | 1.4273 | 0 | 0 | 0 | 111.7138 | 44.2727 | 0 | 111.7138 | 196.1648 | 15.39% | 0 | 0 | 0 | 0% | 45.7
4351 | 540 | 235 | 71 | 2.4178 | 26 | 271.7914 | 137.4137 | 0 | 110.4608 | 5.5604 | 0 | 0 | 5.5604 | 0 | 0 | 0 | 65.0305 | 24.3092 | 110.4608 | 65.0305 | 242.005 | 18.99% | 0 | 0 | 0 | 0% | 29.8696
4352 | 715 | 439 | 91 | 3.2238 | 29.2 | 359.8719 | 206.6659 | 0 | 175.1048 | 24.6155 | 0 | 0 | 24.6155 | 0 | 0 | 0 | 65.7494 | 24.2845 | 175.1048 | 65.7494 | 348.5803 | 27.35% | 0 | 0 | 0 | 0% | 48.9
4353 | 817 | 635 | 100 | 3.4253 | 30.5 | 411.2103 | 251.513 | 0 | 216.8082 | 46.3899 | 0 | 0 | 46.3899 | 0 | 0 | 0 | 0 | 0 | 216.8082 | 0 | 554.5756 | 43.51% | 0 | 0 | 0 | 0% | 46.3899
4354 | 876 | 802 | 102 | 4.0297 | 32.3 | 440.906 | 280.4648 | 0 | 243.751 | 74.0044 | 0 | 12.0022 | 62.0022 | 0 | 0 | 0 | 0 | 0 | 243.751 | 0 | 786.1698 | 61.68% | 9.2057 | 0 | 9.442 | 18.88% | 50
4355 | 905 | 923 | 104 | 4.4327 | 33.8 | 455.5022 | 297.2885 | 0 | 259.4873 | 95.8852 | 0 | 22.9426 | 72.9426 | 0 | 0 | 0 | 0 | 0 | 259.4873 | 0 | 1032.7156 | 81.03% | 17.597 | 0 | 27.4907 | 54.98% | 50
4356 | 924 | 996 | 104 | 9.6714 | 34.2 | 465.0653 | 307.0805 | 0 | 265.6928 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 265.6928 | 0 | 1274.5104 | 100% | 19.175 | 0 | 47.1579 | 94.32% | 50
4357 | 940 | 1015 | 97 | 11.4848 | 34.7 | 473.1183 | 0 | 310.0639 | 0 | 100 | 21.3873 | 3.6127 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 2.7709 | 0 | 50 | 100% | 50
4358 | 921 | 965 | 100 | 13.9026 | 34.7 | 463.5553 | 0 | 296.6069 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4359 | 881 | 861 | 108 | 14.5071 | 34.4 | 443.4226 | 0 | 273.5091 | 0 | 88.9663 | 19.7832 | 0 | 69.1832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.4
4360 | 739 | 670 | 133 | 13.9026 | 34 | 371.9515 | 0 | 216.6828 | 0 | 54.5659 | 2.9829 | 0 | 51.5829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.6
4361 | 703 | 514 | 114 | 13.4996 | 33.9 | 353.8321 | 0 | 184.7654 | 0 | 33.8585 | 0 | 0 | 33.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 13.8415 | 35.8053 | 71.61% | 47.7
4362 | 537 | 304 | 95 | 11.6862 | 33 | 270.2814 | 0 | 113.5316 | 0 | 12.4638 | 0 | 0 | 12.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.1667 | 20.33% | 37.4638
4363 | 245 | 110 | 56 | 7.455 | 31.5 | 123.3128 | 0 | 0 | 0 | 2.9064 | 0 | 0 | 2.9064 | 0 | 0 | 0 | 85.4435 | 32.5793 | 0 | 85.4435 | 1194.484 | 93.72% | 0 | 9.9143 | 0 | 0% | 45.4
4364 | 1 | 7 | 7 | 7.2535 | 28.1 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.6475 | 42.1 | 0 | 107.6475 | 1089.286 | 85.47% | 0 | 0 | 0 | 0% | 42.1
4365 | 0 | 0 | 0 | 9.8729 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6165 | 39.9 | 0 | 101.6165 | 990.6292 | 77.73% | 0 | 0 | 0 | 0% | 39.9
4366 | 0 | 0 | 0 | 7.6565 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7168 | 37.6 | 0 | 95.7168 | 898.5488 | 70.5% | 0 | 0 | 0 | 0% | 37.6
4367 | 0 | 0 | 0 | 5.0372 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6125 | 35.9 | 0 | 91.6125 | 811.1472 | 63.64% | 0 | 0 | 0 | 0% | 35.9
4368 | 0 | 0 | 0 | 7.858 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4778 | 35.1 | 0 | 89.4778 | 726.0545 | 56.97% | 0 | 0 | 0 | 0% | 35.1
4369 | 0 | 0 | 0 | 8.0595 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5847 | 34.8 | 0 | 88.5847 | 641.8171 | 50.36% | 0 | 0 | 0 | 0% | 34.8
4370 | 0 | 0 | 0 | 6.4476 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4515 | 35.2 | 0 | 89.4515 | 556.425 | 43.66% | 0 | 0 | 0 | 0% | 35.2
4371 | 0 | 0 | 0 | 4.8357 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9946 | 37.5 | 0 | 94.9946 | 464.5533 | 36.45% | 0 | 0 | 0 | 0% | 37.5
4372 | 0 | 0 | 0 | 4.2312 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7047 | 40.7 | 0 | 102.7047 | 363.5229 | 28.52% | 0 | 0 | 0 | 0% | 40.7
4373 | 0 | 1 | 1 | 5.2387 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.1723 | 43.9 | 0 | 110.1723 | 253.3506 | 19.88% | 0 | 0 | 0 | 0% | 43.9
4374 | 118 | 51 | 34 | 6.6491 | 18.8 | 59.3915 | 0 | 23.3235 | 0 | 1.7088 | 0 | 0 | 1.7088 | 0 | 0 | 0 | 87.0912 | 34.3135 | 0 | 87.0912 | 170.4326 | 13.37% | 0 | 0 | 0 | 0% | 36.0223
4375 | 391 | 213 | 94 | 8.6639 | 20.8 | 196.7971 | 99.5284 | 0 | 71.8027 | 6.8342 | 0 | 0 | 6.8342 | 0 | 0 | 0 | 0 | 0 | 71.8027 | 0 | 239.2109 | 18.77% | 0 | 0 | 0 | 0% | 6.8342
4376 | 621 | 421 | 119 | 12.4922 | 23.4 | 312.5601 | 179.535 | 0 | 144.6233 | 25.2006 | 0 | 0 | 25.2006 | 0 | 0 | 0 | 64.7409 | 24.3994 | 144.6233 | 64.7409 | 318.3916 | 24.98% | 0 | 0 | 0 | 0% | 49.6
4377 | 749 | 621 | 130 | 13.0966 | 25.2 | 376.9847 | 230.6209 | 0 | 192.0576 | 47.4462 | 0 | 0 | 47.4462 | 0 | 0 | 0 | 0 | 0 | 192.0576 | 0 | 501.8328 | 39.37% | 0 | 0 | 0 | 0% | 47.4462
4378 | 814 | 786 | 135 | 12.2907 | 26.8 | 409.7004 | 260.6526 | 0 | 220.4093 | 78.026 | 0 | 14.013 | 64.013 | 0 | 0 | 0 | 0 | 0 | 220.4093 | 0 | 712.3537 | 55.89% | 10.748 | 0 | 11.0254 | 22.05% | 50
4379 | 830 | 904 | 151 | 10.8803 | 28.1 | 417.7534 | 272.6784 | 0 | 232.5529 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 232.5529 | 0 | 934.4734 | 73.32% | 19.175 | 0 | 30.6955 | 61.39% | 50
4380 | 839 | 974 | 161 | 9.0669 | 29.2 | 422.2833 | 278.8514 | 0 | 239.475 | 100 | 0.46465 | 24.5353 | 75 | 0 | 0 | 0 | 0 | 0 | 239.475 | 0 | 1163.2046 | 91.27% | 18.8186 | 0 | 50 | 100% | 50
4381 | 865 | 993 | 145 | 6.8506 | 30.4 | 435.3695 | 279.1366 | 6.1752 | 241.5745 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 241.5745 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4382 | 845 | 948 | 152 | 8.8654 | 31.3 | 425.3032 | 0 | 272.1197 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4383 | 808 | 845 | 154 | 10.6788 | 31 | 406.6804 | 0 | 250.821 | 0 | 88.0179 | 19.459 | 0 | 68.559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.1
4384 | 772 | 699 | 138 | 9.8729 | 30.9 | 388.561 | 0 | 226.2997 | 0 | 59.6975 | 5.6488 | 0 | 54.0488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.4
4385 | 613 | 479 | 127 | 10.0743 | 30.3 | 308.5336 | 0 | 161.0132 | 0 | 31.9947 | 0 | 0 | 31.9947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 15.6053 | 33.9943 | 67.99% | 47.6
4386 | 524 | 302 | 99 | 10.4773 | 28.7 | 263.7383 | 0 | 110.5633 | 0 | 12.8695 | 0 | 0 | 12.8695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 8.3519 | 16.7% | 37.8695
4387 | 236 | 106 | 56 | 10.2758 | 26.7 | 118.7829 | 0 | 0 | 0 | 2.9735 | 0 | 0 | 2.9735 | 0 | 0 | 0 | 89.7817 | 34.8829 | 0 | 89.7817 | 1189.2853 | 93.31% | 0 | 8.1435 | 0 | 0% | 46
4388 | 6 | 7 | 6 | 8.8654 | 25 | 3.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3836 | 42.7 | 0 | 108.3836 | 1082.7289 | 84.95% | 0 | 0 | 0 | 0% | 42.7
4389 | 0 | 0 | 0 | 8.8654 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4681 | 40.4 | 0 | 102.4681 | 982.6667 | 77.1% | 0 | 0 | 0 | 0% | 40.4
4390 | 0 | 0 | 0 | 9.0669 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4039 | 38 | 0 | 96.4039 | 889.4549 | 69.79% | 0 | 0 | 0 | 0% | 38
4391 | 0 | 0 | 0 | 5.4401 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9817 | 36.2 | 0 | 91.9817 | 801.3158 | 62.87% | 0 | 0 | 0 | 0% | 36.2
4392 | 0 | 0 | 0 | 3.2238 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.034 | 35.4 | 0 | 90.034 | 715.3997 | 56.13% | 0 | 0 | 0 | 0% | 35.4
4393 | 0 | 0 | 0 | 5.4401 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2267 | 35.1 | 0 | 89.2267 | 630.3048 | 49.45% | 0 | 0 | 0 | 0% | 35.1
4394 | 0 | 0 | 0 | 5.6416 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2763 | 35.5 | 0 | 90.2763 | 544.0812 | 42.69% | 0 | 0 | 0 | 0% | 35.5
4395 | 0 | 0 | 0 | 6.2461 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8157 | 37.8 | 0 | 95.8157 | 451.3617 | 35.41% | 0 | 0 | 0 | 0% | 37.8
4396 | 0 | 0 | 0 | 4.4327 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.1911 | 40.9 | 0 | 103.1911 | 349.7719 | 27.44% | 0 | 0 | 0 | 0% | 40.9
4397 | 0 | 1 | 1 | 2.6193 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.0893 | 44.2 | 0 | 111.0893 | 238.7391 | 18.73% | 0 | 0 | 0 | 0% | 44.2
4398 | 160 | 54 | 31 | 3.0223 | 20.4 | 80.5308 | 0 | 31.6293 | 0 | 1.4314 | 0 | 0 | 1.4314 | 0 | 0 | 0 | 114.2375 | 45.4686 | 0 | 114.2375 | 124.001 | 9.729% | 0 | 0 | 0 | 0% | 46.9
4399 | 522 | 228 | 71 | 3.6268 | 22.2 | 262.7317 | 132.9076 | 0 | 105.7857 | 5.5649 | 0 | 0 | 5.5649 | 0 | 0 | 0 | 0 | 0 | 105.7857 | 0 | 225.9352 | 17.73% | 0 | 0 | 0 | 0% | 5.5649
4400 | 684 | 428 | 98 | 6.4476 | 24 | 344.2691 | 197.7903 | 0 | 165.2475 | 24.9377 | 0 | 0 | 24.9377 | 0 | 0 | 0 | 65.1931 | 24.5623 | 165.2475 | 65.1931 | 325.4036 | 25.53% | 0 | 0 | 0 | 0% | 49.5
4401 | 758 | 616 | 120 | 9.2684 | 25.5 | 381.5146 | 233.4344 | 0 | 196.9922 | 46.8303 | 0 | 0 | 46.8303 | 0 | 0 | 0 | 0 | 0 | 196.9922 | 0 | 514.6053 | 40.38% | 0 | 0 | 0 | 0% | 46.8303
4402 | 805 | 777 | 135 | 9.4699 | 26.7 | 405.1705 | 257.8084 | 0 | 219.4409 | 76.1826 | 0 | 13.0913 | 63.0913 | 0 | 0 | 0 | 0 | 0 | 219.4409 | 0 | 725.3678 | 56.91% | 10.041 | 0 | 10.3018 | 20.6% | 50
4403 | 846 | 902 | 137 | 8.4625 | 28.3 | 425.8065 | 277.9628 | 0 | 238.974 | 98.3754 | 0 | 24.1877 | 74.1877 | 0 | 0 | 0 | 0 | 0 | 238.974 | 0 | 954.891 | 74.92% | 18.552 | 0 | 29.3355 | 58.67% | 50
4404 | 828 | 961 | 159 | 7.858 | 29.7 | 416.7468 | 275.2165 | 0 | 236.7732 | 100.1 | 0.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 236.7732 | 0 | 1182.3004 | 92.77% | 19.175 | 0 | 49.0084 | 98.02% | 49.9
4405 | 833 | 975 | 159 | 9.0669 | 30.5 | 419.2634 | 172.3298 | 102.4153 | 147.7975 | 100.3 | 25.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 147.7975 | 0 | 1274.5104 | 100% | 0 | 0 | 49.0084 | 98.02% | 49.7
4406 | 816 | 927 | 161 | 10.4773 | 31.1 | 410.707 | 0 | 262.7714 | 0 | 100.5 | 25.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.0084 | 98.02% | 49.5
4407 | 770 | 823 | 165 | 12.8952 | 30.9 | 387.5544 | 0 | 239.0027 | 0 | 86.0982 | 18.8491 | 0 | 67.2491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.0084 | 98.02% | 48.4
4408 | 733 | 682 | 149 | 12.2907 | 30.6 | 368.9316 | 0 | 214.8119 | 0 | 58.3796 | 5.2398 | 0 | 53.1398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.0084 | 98.02% | 47.9
4409 | 653 | 499 | 129 | 11.2833 | 30 | 328.6663 | 0 | 171.4137 | 0 | 33.7564 | 0 | 0 | 33.7564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 13.4436 | 35.2178 | 70.44% | 47.2
4410 | 530 | 304 | 99 | 10.4773 | 28.9 | 266.7582 | 0 | 111.5994 | 0 | 12.984 | 0 | 0 | 12.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 9.5718 | 19.14% | 37.984
4411 | 289 | 117 | 56 | 9.0669 | 27.5 | 145.4587 | 0 | 0 | 0 | 2.9623 | 0 | 0 | 2.9623 | 0 | 0 | 0 | 86.1527 | 33.3063 | 0 | 86.1527 | 1193.4853 | 93.64% | 0 | 9.3314 | 0 | 0% | 45.6
4412 | 14 | 9 | 8 | 6.6491 | 25.8 | 7.0464 | 0 | 0 | 0 | 0.029158 | 0 | 0 | 0.029158 | 0 | 0 | 0 | 107.3165 | 42.1708 | 0 | 107.3165 | 1088.4388 | 85.4% | 0 | 0 | 0 | 0% | 42.2
4413 | 0 | 0 | 0 | 8.0595 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8998 | 40.1 | 0 | 101.8998 | 989.2219 | 77.62% | 0 | 0 | 0 | 0% | 40.1
4414 | 0 | 0 | 0 | 9.6714 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7114 | 37.7 | 0 | 95.7114 | 896.8665 | 70.37% | 0 | 0 | 0 | 0% | 37.7
4415 | 0 | 0 | 0 | 7.052 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7508 | 36.1 | 0 | 91.7508 | 809.0111 | 63.48% | 0 | 0 | 0 | 0% | 36.1
4416 | 0 | 0 | 0 | 3.8283 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8487 | 35.3 | 0 | 89.8487 | 723.3769 | 56.76% | 0 | 0 | 0 | 0% | 35.3
4417 | 0 | 0 | 0 | 2.0149 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2887 | 35.1 | 0 | 89.2887 | 638.2853 | 50.08% | 0 | 0 | 0 | 0% | 35.1
4418 | 0 | 0 | 0 | 3.0223 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9532 | 35.4 | 0 | 89.9532 | 552.3442 | 43.34% | 0 | 0 | 0 | 0% | 35.4
4419 | 0 | 0 | 0 | 1.0074 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9804 | 37.5 | 0 | 94.9804 | 460.481 | 36.13% | 0 | 0 | 0 | 0% | 37.5
4420 | 0 | 0 | 0 | 3.2238 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4161 | 40.6 | 0 | 102.4161 | 359.7414 | 28.23% | 0 | 0 | 0 | 0% | 40.6
4421 | 0 | 0 | 0 | 3.6268 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.111 | 43.9 | 0 | 110.111 | 249.5791 | 19.58% | 0 | 0 | 0 | 0% | 43.9
4422 | 54 | 46 | 37 | 3.2238 | 19.2 | 27.1791 | 0 | 10.675 | 0 | 1.9138 | 0 | 0 | 1.9138 | 0 | 0 | 0 | 112.5601 | 44.8862 | 0 | 112.5601 | 136.5283 | 10.71% | 0 | 0 | 0 | 0% | 46.8
4423 | 336 | 207 | 104 | 5.2387 | 21.4 | 169.1146 | 85.5663 | 0 | 60.9949 | 7.3252 | 0 | 0 | 7.3252 | 0 | 0 | 0 | 0 | 0 | 60.9949 | 0 | 195.23 | 15.32% | 0 | 0 | 0 | 0% | 7.3252
4424 | 502 | 397 | 152 | 3.0223 | 24.3 | 252.6653 | 145.1913 | 0 | 117.6659 | 23.9041 | 0 | 0 | 23.9041 | 0 | 0 | 0 | 66.6869 | 25.1959 | 117.6659 | 66.6869 | 247.2426 | 19.4% | 0 | 0 | 0 | 0% | 49.1
4425 | 597 | 584 | 192 | 5.8431 | 26.4 | 300.4805 | 183.8862 | 0 | 152.6457 | 44.0381 | 0 | 0 | 44.0381 | 0 | 0 | 0 | 0 | 0 | 152.6457 | 0 | 393.7162 | 30.89% | 0 | 0 | 0 | 0% | 44.0381
4426 | 631 | 739 | 231 | 8.8654 | 27.4 | 317.5933 | 202.1129 | 0 | 167.9756 | 68.7714 | 0 | 9.3857 | 59.3857 | 0 | 0 | 0 | 0 | 0 | 167.9756 | 0 | 554.9001 | 43.54% | 7.1988 | 0 | 7.3868 | 14.77% | 50
4427 | 700 | 867 | 229 | 9.6714 | 28.4 | 352.3222 | 230.0162 | 0 | 193.5953 | 93.5754 | 0 | 21.7877 | 71.7877 | 0 | 0 | 0 | 0 | 0 | 193.5953 | 0 | 740.6676 | 58.11% | 16.7112 | 0 | 24.5344 | 49.07% | 50
4428 | 726 | 939 | 233 | 11.6862 | 29.5 | 365.4084 | 241.3327 | 0 | 202.9517 | 100.3 | 0.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 202.9517 | 0 | 935.4133 | 73.39% | 19.175 | 0 | 44.2101 | 88.42% | 49.7
4429 | 738 | 956 | 228 | 11.0818 | 30.2 | 371.4482 | 243.4017 | 0 | 205.2309 | 100.4 | 18.0434 | 7.3566 | 75 | 0 | 0 | 0 | 0 | 0 | 205.2309 | 0 | 1132.346 | 88.85% | 5.6425 | 0 | 50 | 100% | 49.6
4430 | 744 | 916 | 213 | 10.4773 | 30.5 | 374.4681 | 237.2052 | 2.3737 | 200.0706 | 100.4 | 25.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 200.0706 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.6
4431 | 750 | 825 | 183 | 9.2684 | 31 | 377.488 | 0 | 232.7747 | 0 | 85.0504 | 18.0752 | 0 | 66.9752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.9
4432 | 757 | 691 | 140 | 11.2833 | 30.7 | 381.0113 | 0 | 221.7884 | 0 | 59.0227 | 5.3113 | 0 | 53.7113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.4
4433 | 703 | 515 | 115 | 10.2758 | 30.4 | 353.8321 | 0 | 184.423 | 0 | 34.4791 | 0 | 0 | 34.4791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 13.1209 | 36.5385 | 73.08% | 47.6
4434 | 579 | 316 | 91 | 11.2833 | 29.4 | 291.4208 | 0 | 121.6578 | 0 | 12.9952 | 0 | 0 | 12.9952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.8889 | 21.78% | 37.9952
4435 | 361 | 131 | 57 | 11.2833 | 27.4 | 181.6976 | 0 | 0 | 0 | 3.0285 | 0 | 0 | 3.0285 | 0 | 0 | 0 | 83.6053 | 32.2577 | 0 | 83.6053 | 1196.3662 | 93.87% | 0 | 10.6138 | 2.7756e-15 | 5.551e-15% | 45.9
4436 | 19 | 11 | 9 | 11.0818 | 24.8 | 9.563 | 0 | 0 | 0 | 0.083142 | 0 | 0 | 0.083142 | 0 | 0 | 0 | 108.3928 | 42.7169 | 0 | 108.3928 | 1089.7761 | 85.51% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42.8
4437 | 0 | 0 | 0 | 8.8654 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4415 | 40.8 | 0 | 103.4415 | 988.6027 | 77.57% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 40.8
4438 | 0 | 0 | 0 | 6.6491 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6597 | 38.4 | 0 | 97.6597 | 894.2627 | 70.17% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38.4
4439 | 0 | 0 | 0 | 2.8208 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9463 | 36.5 | 0 | 92.9463 | 805.2931 | 63.18% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.5
4440 | 0 | 0 | 0 | 2.2164 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1128 | 35.8 | 0 | 91.1128 | 718.2724 | 56.36% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.8
4441 | 0 | 0 | 0 | 1.8134 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8297 | 35.3 | 0 | 89.8297 | 632.6325 | 49.64% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.3
4442 | 0 | 0 | 0 | 2.0149 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7813 | 35.7 | 0 | 90.7813 | 545.8622 | 42.83% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.7
4443 | 0 | 0 | 0 | 2.6193 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3272 | 38 | 0 | 96.3272 | 452.586 | 35.51% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38
4444 | 0 | 0 | 0 | 2.6193 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4341 | 41 | 0 | 103.4341 | 350.7281 | 27.52% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41
4445 | 0 | 0 | 0 | 2.2164 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.8489 | 44.1 | 0 | 110.8489 | 239.9992 | 18.83% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 44.1
4446 | 36 | 45 | 40 | 3.2238 | 20 | 18.1194 | 0 | 7.1159 | 0 | 2.0916 | 0 | 0 | 2.0916 | 0 | 0 | 0 | 113.2758 | 45.1084 | 0 | 113.2758 | 126.3151 | 9.911% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 47.2
4447 | 220 | 189 | 121 | 3.4253 | 22.6 | 110.7298 | 0 | 56.033 | 0 | 8.1965 | 0 | 0 | 8.1965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.3151 | 9.911% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 8.1965
4448 | 387 | 380 | 190 | 5.6416 | 24.6 | 194.7838 | 111.9521 | 0 | 85.4207 | 23.6829 | 0 | 0 | 23.6829 | 0 | 0 | 0 | 0 | 0 | 85.4207 | 0 | 208.6031 | 16.37% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 23.6829
4449 | 537 | 576 | 222 | 5.4401 | 26 | 270.2814 | 165.4354 | 0 | 135.5848 | 43.1611 | 0 | 0 | 43.1611 | 0 | 0 | 0 | 0 | 0 | 135.5848 | 0 | 339.2154 | 26.62% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.1611
4450 | 634 | 745 | 237 | 4.0297 | 27.7 | 319.1032 | 203.1033 | 0 | 171.4944 | 67.6333 | 0 | 8.8167 | 58.8167 | 0 | 0 | 0 | 0 | 0 | 171.4944 | 0 | 504.4204 | 39.58% | 6.7624 | 0 | 6.94 | 13.88% | 50
4451 | 668 | 866 | 258 | 4.0297 | 29.4 | 336.216 | 219.5237 | 0 | 186.8051 | 89.0922 | 0 | 19.5461 | 69.5461 | 0 | 0 | 0 | 0 | 0 | 186.8051 | 0 | 684.3746 | 53.7% | 14.9919 | 0 | 22.3255 | 44.65% | 50
4452 | 691 | 936 | 264 | 7.2535 | 30.5 | 347.7923 | 229.7183 | 0 | 194.7708 | 100.5 | 0.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 194.7708 | 0 | 872.0023 | 68.42% | 19.175 | 0 | 42.0041 | 84.01% | 49.5
4453 | 698 | 948 | 261 | 6.8506 | 31.2 | 351.3155 | 230.2005 | 0 | 195.4725 | 100.8 | 15.6419 | 10.1581 | 75 | 0 | 0 | 0 | 0 | 0 | 195.4725 | 0 | 1060.306 | 83.19% | 7.7912 | 0 | 50 | 100% | 49.2
4454 | 683 | 910 | 262 | 6.4476 | 32.7 | 343.7658 | 219.9313 | 0 | 186.0902 | 98.0775 | 24.5388 | 0 | 73.5388 | 0 | 0 | 0 | 0 | 0 | 186.0902 | 0 | 1239.5715 | 97.26% | 0 | 0 | 50 | 100% | 49
4455 | 647 | 811 | 254 | 9.4699 | 32.9 | 325.6463 | 0 | 200.791 | 0 | 81.7524 | 16.7762 | 0 | 64.9762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1239.5715 | 97.26% | 0 | 0 | 50 | 100% | 48.2
4456 | 589 | 656 | 224 | 9.6714 | 31.9 | 296.4539 | 0 | 172.5234 | 0 | 52.997 | 2.6985 | 0 | 50.2985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1239.5715 | 97.26% | 0 | 0 | 50 | 100% | 47.6
4457 | 535 | 491 | 183 | 9.2684 | 32.4 | 269.2748 | 0 | 140.2612 | 0 | 33.0314 | 0 | 0 | 33.0314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1239.5715 | 97.26% | 0 | 13.5686 | 36.0772 | 72.15% | 46.6
4458 | 58 | 154 | 127 | 9.2684 | 30.2 | 29.1924 | 0 | 12.16 | 0 | 9.3007 | 0 | 0 | 9.3007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1239.5715 | 97.26% | 0 | 25 | 10.4238 | 20.85% | 34.3007
4459 | 19 | 52 | 49 | 9.4699 | 26.9 | 9.563 | 0 | 0 | 0 | 2.9889 | 0 | 0 | 2.9889 | 0 | 0 | 0 | 81.301 | 31.3521 | 0 | 81.301 | 1163.9616 | 91.33% | 0 | 10.1591 | 1.3878e-15 | 2.776e-15% | 44.5
4460 | 4 | 9 | 9 | 10.2758 | 25.2 | 2.0133 | 0 | 0 | 0 | 0.08228 | 0 | 0 | 0.08228 | 0 | 0 | 0 | 106.0644 | 41.7177 | 0 | 106.0644 | 1060.1869 | 83.18% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 41.8
4461 | 0 | 0 | 0 | 7.858 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2437 | 40.2 | 0 | 102.2437 | 960.6766 | 75.38% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 40.2
4462 | 0 | 0 | 0 | 3.6268 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0478 | 38.1 | 0 | 97.0478 | 867.1711 | 68.04% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 38.1
4463 | 0 | 0 | 0 | 4.8357 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4222 | 36.3 | 0 | 92.4222 | 778.7431 | 61.1% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 36.3
4464 | 0 | 0 | 0 | 3.6268 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9919 | 35.2 | 0 | 89.9919 | 693.1221 | 54.38% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 35.2
4465 | 0 | 0 | 0 | 2.2164 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2501 | 34.5 | 0 | 88.2501 | 609.4614 | 47.82% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 34.5
4466 | 0 | 0 | 0 | 2.0149 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.104 | 34 | 0 | 87.104 | 527.115 | 41.36% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 34
4467 | 0 | 0 | 0 | 0.80595 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9275 | 34 | 0 | 86.9275 | 444.9196 | 34.91% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 34
4468 | 0 | 0 | 0 | 3.0223 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0381 | 34.5 | 0 | 88.0381 | 361.4112 | 28.36% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 34.5
4469 | 0 | 0 | 0 | 1.8134 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2033 | 36.7 | 0 | 93.2033 | 271.7544 | 21.32% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 36.7
4470 | 42 | 46 | 39 | 2.8208 | 21.3 | 21.1393 | 0 | 8.2999 | 0 | 1.969 | 0 | 0 | 1.969 | 0 | 0 | 0 | 95.4235 | 37.631 | 0 | 95.4235 | 179.4324 | 14.08% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 39.6
4471 | 246 | 197 | 121 | 1.4104 | 24.4 | 123.8161 | 62.6597 | 0 | 40.8646 | 8.1596 | 0 | 0 | 8.1596 | 0 | 0 | 0 | 0 | 0 | 40.8646 | 0 | 218.4015 | 17.14% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 8.1596
4472 | 421 | 391 | 184 | 1.8134 | 27.8 | 211.8966 | 121.8103 | 0 | 96.1632 | 23.7165 | 0 | 0 | 23.7165 | 0 | 0 | 0 | 0 | 0 | 96.1632 | 0 | 310.1042 | 24.33% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 23.7165
4473 | 511 | 576 | 237 | 6.0446 | 34.1 | 257.1952 | 157.4542 | 0 | 127.9038 | 41.8707 | 0 | 0 | 41.8707 | 0 | 0 | 0 | 0 | 0 | 127.9038 | 0 | 432.0753 | 33.9% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 41.8707
4474 | 521 | 735 | 312 | 9.8729 | 35.8 | 262.2284 | 166.9277 | 0 | 134.6266 | 67.946 | 0 | 11.223 | 56.723 | 0 | 0 | 0 | 0 | 0 | 134.6266 | 0 | 560.4573 | 43.97% | 8.608 | 0 | 8.8353 | 17.67% | 45.5
4475 | 212 | 625 | 426 | 11.8877 | 35.9 | 106.7033 | 69.6764 | 0 | 42.0769 | 51.2225 | 0 | 3.1113 | 48.1113 | 0 | 0 | 0 | 0 | 0 | 42.0769 | 0 | 600.5825 | 47.12% | 2.3863 | 0 | 11.2847 | 22.57% | 45
4476 | 332 | 752 | 421 | 5.4401 | 36.6 | 167.1014 | 110.3814 | 0 | 84.2112 | 72.9577 | 0 | 14.5288 | 58.4288 | 0 | 0 | 0 | 0 | 0 | 84.2112 | 0 | 680.8877 | 53.42% | 11.1436 | 0 | 22.7226 | 45.45% | 43.9
4477 | 273 | 703 | 424 | 8.8654 | 37.5 | 137.4056 | 90.0323 | 0 | 63.5027 | 66.8467 | 0 | 11.7733 | 55.0733 | 0 | 0 | 0 | 0 | 0 | 63.5027 | 0 | 741.4448 | 58.17% | 9.0301 | 0 | 31.9913 | 63.98% | 43.3
4478 | 3 | 232 | 226 | 13.2981 | 35.7 | 1.51 | 0 | 0.96601 | 0 | 16.0318 | 0 | 0 | 16.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741.4448 | 58.17% | 0 | 25 | 6.3351 | 12.67% | 41.0318
4479 | 17 | 336 | 318 | 17.9323 | 36.5 | 8.5564 | 0 | 5.2754 | 0 | 23.8349 | 0 | 0 | 23.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741.4448 | 58.17% | 0 | 6.1731 | 0 | 0% | 30.008
4480 | 165 | 433 | 310 | 14.91 | 37.7 | 83.0474 | 0 | 48.3179 | 0 | 31.8727 | 0 | 0 | 31.8727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741.4448 | 58.17% | 0 | 0 | 0 | 0% | 31.8727
4481 | 63 | 204 | 172 | 9.2684 | 37.7 | 31.709 | 0 | 16.5061 | 0 | 14.1056 | 0 | 0 | 14.1056 | 0 | 0 | 0 | 77.1279 | 28.0944 | 0 | 77.1279 | 670.4063 | 52.6% | 0 | 0 | 0 | 0% | 42.2
4482 | 35 | 149 | 134 | 11.2833 | 36.6 | 17.6161 | 0 | 7.3214 | 0 | 9.2732 | 0 | 0 | 9.2732 | 0 | 0 | 0 | 88.6164 | 33.1268 | 0 | 88.6164 | 587.0641 | 46.06% | 0 | 0 | 0 | 0% | 42.4
4483 | 1 | 43 | 43 | 12.8952 | 29.3 | 0.50332 | 0 | 0 | 0 | 2.6141 | 0 | 0 | 2.6141 | 0 | 0 | 0 | 100.5723 | 39.0859 | 0 | 100.5723 | 489.7557 | 38.43% | 0 | 0 | 0 | 0% | 41.7
4484 | 0 | 6 | 6 | 8.4625 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1618 | 39.5 | 0 | 101.1618 | 391.6844 | 30.73% | 0 | 0 | 0 | 0% | 39.5
4485 | 0 | 0 | 0 | 3.0223 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.612 | 37.3 | 0 | 95.612 | 299.8314 | 23.53% | 0 | 0 | 0 | 0% | 37.3
4486 | 0 | 0 | 0 | 7.455 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0442 | 35.1 | 0 | 90.0442 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 35.1
4487 | 0 | 0 | 0 | 4.8357 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 0
4488 | 0 | 0 | 0 | 1.6119 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 0
4489 | 0 | 0 | 0 | 2.8208 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 0
4490 | 0 | 0 | 0 | 2.2164 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 0
4491 | 0 | 0 | 0 | 3.8283 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 0
4492 | 0 | 0 | 0 | 7.858 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 0
4493 | 0 | 0 | 0 | 3.8283 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 0
4494 | 0 | 18 | 18 | 2.8208 | 24 | 0 | 0 | 0 | 0 | 0.75999 | 0 | 0 | 0.75999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 0.75999
4495 | 34 | 97 | 85 | 2.2164 | 26.1 | 17.1128 | 0 | 8.6604 | 0 | 5.655 | 0 | 0 | 5.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.0976 | 16.8% | 0 | 0 | 0 | 0% | 5.655
4496 | 242 | 328 | 210 | 6.8506 | 30.9 | 121.8028 | 70.0315 | 0 | 45.1971 | 20.8196 | 0 | 0 | 20.8196 | 0 | 0 | 0 | 0 | 0 | 45.1971 | 0 | 257.1288 | 20.17% | 0 | 0 | 0 | 0% | 20.8196
4497 | 262 | 463 | 279 | 7.6565 | 32 | 131.8692 | 80.7447 | 0 | 54.9137 | 33.3176 | 0 | 0 | 33.3176 | 0 | 0 | 0 | 0 | 0 | 54.9137 | 0 | 309.4111 | 24.28% | 0 | 0 | 0 | 0% | 33.3176
4498 | 455 | 695 | 332 | 10.8803 | 34.5 | 229.0094 | 145.8023 | 0 | 114.4248 | 67.875 | 0 | 13.3875 | 54.4875 | 0 | 0 | 0 | 0 | 0 | 114.4248 | 0 | 418.3526 | 32.82% | 10.2682 | 0 | 10.5405 | 21.08% | 41.1
4499 | 70 | 483 | 411 | 13.2981 | 34.7 | 35.2322 | 0 | 23.0087 | 0 | 35.928 | 0 | 0 | 35.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418.3526 | 32.82% | 0 | 5.772 | 4.6164 | 9.233% | 41.7
4500 | 299 | 788 | 484 | 10.4773 | 35.9 | 150.4919 | 99.4196 | 0 | 71.0187 | 82.5664 | 0 | 20.8832 | 61.6832 | 0 | 0 | 0 | 0 | 0 | 71.0187 | 0 | 485.968 | 38.13% | 16.0174 | 0 | 21.0588 | 42.12% | 40.8
4501 | 121 | 593 | 462 | 10.2758 | 35.8 | 60.9014 | 0 | 39.9031 | 0 | 51.0115 | 0 | 5.5557 | 45.4557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485.968 | 38.13% | 4.2613 | 0 | 25.4332 | 50.87% | 39.9
4502 | 33 | 423 | 383 | 10.8803 | 35.4 | 16.6095 | 0 | 10.626 | 0 | 31.033 | 0 | 0 | 31.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485.968 | 38.13% | 0 | 8.467 | 16.7429 | 33.49% | 39.5
4503 | 88 | 464 | 384 | 8.261 | 35.3 | 44.2919 | 0 | 27.3063 | 0 | 34.2889 | 0 | 0 | 34.2889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485.968 | 38.13% | 0 | 5.1111 | 11.4968 | 22.99% | 39.4
4504 | 411 | 657 | 353 | 8.4625 | 36.6 | 206.8634 | 120.3256 | 0 | 91.9819 | 57.7556 | 0 | 9.0778 | 48.6778 | 0 | 0 | 0 | 0 | 0 | 91.9819 | 0 | 573.5421 | 45% | 6.9627 | 0 | 18.6445 | 37.29% | 39.6
4505 | 239 | 432 | 291 | 10.8803 | 36.5 | 120.2929 | 62.5778 | 0 | 36.4763 | 29.2362 | 0 | 0 | 29.2362 | 0 | 0 | 0 | 0 | 0 | 36.4763 | 0 | 608.2705 | 47.73% | 0 | 10.9638 | 7.3912 | 14.78% | 40.2
4506 | 79 | 178 | 145 | 7.858 | 34.4 | 39.7621 | 0 | 16.4869 | 0 | 10.5931 | 0 | 0 | 10.5931 | 0 | 0 | 0 | 65.3103 | 23.406 | 0 | 65.3103 | 548.4664 | 43.03% | 0 | 7.2008 | 1.2594e-05 | 2.519e-05% | 41.2
4507 | 37 | 78 | 69 | 10.0743 | 32.1 | 18.6227 | 0 | 0 | 0 | 4.0619 | 0 | 0 | 4.0619 | 0 | 0 | 0 | 99.1297 | 38.1381 | 0 | 99.1297 | 452.7743 | 35.53% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 42.2
4508 | 1 | 2 | 2 | 9.6714 | 28.2 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2729 | 39.9 | 0 | 102.2729 | 353.2838 | 27.72% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 39.9
4509 | 0 | 0 | 0 | 3.2238 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0867 | 37.4 | 0 | 96.0867 | 260.7749 | 20.46% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 37.4
4510 | 0 | 0 | 0 | 1.4104 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.0967 | 23.3509 | 0 | 63.0967 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 23.3509
4511 | 0 | 0 | 0 | 2.0149 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 0
4512 | 0 | 0 | 0 | 1.8134 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 0
4513 | 0 | 0 | 0 | 2.6193 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 0
4514 | 0 | 0 | 0 | 3.6268 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 0
4515 | 0 | 0 | 0 | 5.8431 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 0
4516 | 0 | 0 | 0 | 3.6268 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 0
4517 | 0 | 0 | 0 | 1.4104 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 0
4518 | 0 | 23 | 23 | 1.4104 | 19.7 | 0 | 0 | 0 | 0 | 1.1075 | 0 | 0 | 1.1075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 1.1075
4519 | 2 | 99 | 98 | 1.8134 | 21.6 | 1.0066 | 0 | 0.50941 | 0 | 6.6372 | 0 | 0 | 6.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 6.6372
4520 | 140 | 262 | 190 | 3.4253 | 24.2 | 70.4644 | 0 | 40.5209 | 0 | 17.2074 | 0 | 0 | 17.2074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.9504 | 15.92% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 17.2074
4521 | 257 | 392 | 215 | 5.2387 | 27.6 | 129.3526 | 79.2182 | 0 | 54.7502 | 28.6743 | 0 | 0 | 28.6743 | 0 | 0 | 0 | 0 | 0 | 54.7502 | 0 | 254.9741 | 20.01% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 28.6743
4522 | 389 | 617 | 297 | 5.4401 | 30.3 | 195.7905 | 124.6707 | 0 | 97.5457 | 47.9875 | 0 | 0 | 47.9875 | 0 | 0 | 0 | 0 | 0 | 97.5457 | 0 | 347.6623 | 27.28% | 0 | 0 | 1.2594e-05 | 2.519e-05% | 47.9875
4523 | 577 | 833 | 306 | 6.0446 | 32.6 | 290.4141 | 189.6773 | 0 | 158.0207 | 84.5891 | 0 | 17.9445 | 66.6445 | 0 | 0 | 0 | 0 | 0 | 158.0207 | 0 | 497.814 | 39.06% | 13.7635 | 0 | 14.1302 | 28.26% | 48.7
4524 | 542 | 872 | 340 | 6.0446 | 33.9 | 272.798 | 180.2374 | 0 | 149.2754 | 92.5966 | 0 | 22.5483 | 70.0483 | 0 | 0 | 0 | 0 | 0 | 149.2754 | 0 | 639.6558 | 50.19% | 17.2946 | 0 | 31.8856 | 63.77% | 47.5
4525 | 661 | 958 | 306 | 11.2833 | 34.2 | 332.6928 | 217.9768 | 0 | 181.5204 | 103 | 4.9958 | 23.0042 | 75 | 0 | 0 | 0 | 0 | 0 | 181.5204 | 0 | 812.1369 | 63.72% | 17.6442 | 0 | 50 | 100% | 47
4526 | 833 | 961 | 177 | 11.4848 | 34.2 | 419.2634 | 268.2268 | 0 | 228.1894 | 103.3 | 28.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 228.1894 | 0 | 1028.963 | 80.73% | 0 | 0 | 50 | 100% | 46.7
4527 | 887 | 880 | 124 | 14.5071 | 34.2 | 446.4425 | 275.2186 | 0 | 233.0054 | 96.7738 | 25.4369 | 0 | 71.3369 | 0 | 0 | 0 | 0 | 0 | 233.0054 | 0 | 1250.3653 | 98.11% | 0 | 0 | 50 | 100% | 45.9
4528 | 903 | 742 | 89 | 9.8729 | 34.5 | 454.4956 | 0 | 264.3005 | 0 | 68.5515 | 11.5758 | 0 | 56.9758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.3653 | 98.11% | 0 | 0 | 50 | 100% | 45.4
4529 | 860 | 561 | 75 | 10.8803 | 34.3 | 432.853 | 0 | 225.0277 | 0 | 37.1387 | 0 | 0 | 37.1387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.3653 | 98.11% | 0 | 7.7613 | 42.0331 | 84.07% | 44.9
4530 | 713 | 342 | 67 | 8.6639 | 33.2 | 358.8653 | 0 | 148.4435 | 0 | 13.0522 | 0 | 0 | 13.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.3653 | 98.11% | 0 | 25 | 16.3705 | 32.74% | 38.0522
4531 | 426 | 129 | 42 | 8.0595 | 31.8 | 214.4132 | 0 | 0 | 0 | 2.0477 | 0 | 0 | 2.0477 | 0 | 0 | 0 | 69.0252 | 25.4041 | 0 | 69.0252 | 1187.0045 | 93.13% | 0 | 15.9482 | 0 | 0% | 43.4
4532 | 32 | 9 | 6 | 4.4327 | 29.5 | 16.1062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8349 | 40 | 0 | 102.8349 | 1087.1036 | 85.3% | 0 | 0 | 0 | 0% | 40
4533 | 0 | 0 | 0 | 3.4253 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0906 | 38.2 | 0 | 98.0906 | 992.5257 | 77.88% | 0 | 0 | 0 | 0% | 38.2
4534 | 0 | 0 | 0 | 7.858 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8422 | 36.1 | 0 | 92.8422 | 903.785 | 70.91% | 0 | 0 | 0 | 0% | 36.1
4535 | 0 | 0 | 0 | 9.2684 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6676 | 34.9 | 0 | 89.6676 | 818.5109 | 64.22% | 0 | 0 | 0 | 0% | 34.9
4536 | 0 | 0 | 0 | 7.455 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4591 | 34.1 | 0 | 87.4591 | 735.7156 | 57.73% | 0 | 0 | 0 | 0% | 34.1
4537 | 0 | 0 | 0 | 6.0446 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9973 | 34 | 0 | 86.9973 | 653.393 | 51.27% | 0 | 0 | 0 | 0% | 34
4538 | 0 | 0 | 0 | 7.052 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0557 | 34.5 | 0 | 88.0557 | 569.8096 | 44.71% | 0 | 0 | 0 | 0% | 34.5
4539 | 0 | 0 | 0 | 5.8431 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0225 | 36.6 | 0 | 93.0225 | 480.3779 | 37.69% | 0 | 0 | 0 | 0% | 36.6
4540 | 0 | 0 | 0 | 2.6193 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.8031 | 39.5 | 0 | 99.8031 | 382.6469 | 30.02% | 0 | 0 | 0 | 0% | 39.5
4541 | 0 | 0 | 0 | 2.6193 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8217 | 42.1 | 0 | 105.8217 | 277.5027 | 21.77% | 0 | 0 | 0 | 0% | 42.1
4542 | 296 | 57 | 21 | 4.6342 | 19.8 | 148.9819 | 58.4089 | 0 | 26.967 | 0.79982 | 0 | 0 | 0.79982 | 0 | 0 | 0 | 0 | 0 | 26.967 | 0 | 303.2063 | 23.79% | 0 | 0 | 0 | 0% | 0.79982
4543 | 674 | 240 | 47 | 2.4178 | 23 | 339.2359 | 171.6507 | 0 | 142.5436 | 4.2363 | 0 | 0 | 4.2363 | 0 | 0 | 0 | 61.456 | 22.9839 | 142.5436 | 61.456 | 382.8282 | 30.04% | 0 | 0 | 0 | 0% | 27.2202
4544 | 827 | 449 | 57 | 1.6119 | 25.3 | 416.2435 | 239.3999 | 0 | 206.1498 | 25.0498 | 0 | 0 | 25.0498 | 0 | 0 | 0 | 59.9377 | 22.1502 | 206.1498 | 59.9377 | 524.0782 | 41.12% | 0 | 0 | 0 | 0% | 47.2
4545 | 907 | 647 | 62 | 2.8208 | 26.8 | 456.5089 | 279.626 | 0 | 243.2947 | 47.9286 | 0 | 0 | 47.9286 | 0 | 0 | 0 | 0 | 0 | 243.2947 | 0 | 754.6111 | 59.21% | 0 | 0 | 0 | 0% | 47.9286
4546 | 940 | 813 | 70 | 4.2312 | 28.4 | 473.1183 | 301.3033 | 0 | 263.2066 | 80.1143 | 0 | 15.7072 | 64.4072 | 0 | 0 | 0 | 0 | 0 | 263.2066 | 0 | 1004.0114 | 78.78% | 12.0474 | 0 | 12.3702 | 24.74% | 48.7
4547 | 960 | 936 | 75 | 4.2312 | 29.8 | 483.1847 | 315.6137 | 0 | 276.5345 | 102.2 | 2.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 276.5345 | 0 | 1266.0405 | 99.34% | 19.175 | 0 | 32.0589 | 64.12% | 47.8
4548 | 966 | 1005 | 78 | 5.8431 | 30.6 | 486.2046 | 0 | 321.2699 | 0 | 103.5 | 5.7192 | 22.7808 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0405 | 99.34% | 17.4729 | 0 | 50 | 100% | 46.5
4549 | 978 | 1025 | 77 | 10.6788 | 30.8 | 492.2444 | 0 | 322.5048 | 0 | 103.7 | 28.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0405 | 99.34% | 0 | 0 | 50 | 100% | 46.3
4550 | 968 | 979 | 76 | 12.2907 | 30.3 | 487.2112 | 0 | 311.6993 | 0 | 103.9 | 28.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0405 | 99.34% | 0 | 0 | 50 | 100% | 46.1
4551 | 934 | 873 | 80 | 12.0892 | 30.1 | 470.0984 | 0 | 289.787 | 0 | 98.3891 | 26.4445 | 0 | 71.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0405 | 99.34% | 0 | 0 | 50 | 100% | 45.5
4552 | 881 | 719 | 82 | 12.4922 | 29.3 | 443.4226 | 0 | 257.7994 | 0 | 68.1799 | 11.5399 | 0 | 56.6399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0405 | 99.34% | 0 | 0 | 50 | 100% | 45.1
4553 | 804 | 531 | 79 | 9.4699 | 29.8 | 404.6672 | 0 | 210.2357 | 0 | 35.9249 | 0 | 0 | 35.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0405 | 99.34% | 0 | 8.7751 | 40.9912 | 81.98% | 44.7
4554 | 680 | 327 | 67 | 10.2758 | 28.5 | 342.2558 | 0 | 141.2256 | 0 | 12.9617 | 0 | 0 | 12.9617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0405 | 99.34% | 0 | 25 | 15.3247 | 30.65% | 37.9617
4555 | 428 | 129 | 43 | 8.6639 | 27.2 | 215.4198 | 0 | 0 | 0 | 2.167 | 0 | 0 | 2.167 | 0 | 0 | 0 | 70.5257 | 26.6057 | 0 | 70.5257 | 1201.2325 | 94.25% | 0 | 14.9273 | 0 | 0% | 43.7
4556 | 30 | 8 | 6 | 4.0297 | 25.4 | 15.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4001 | 40.6 | 0 | 103.4001 | 1100.5577 | 86.35% | 0 | 0 | 0 | 0% | 40.6
4557 | 0 | 0 | 0 | 1.0074 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2625 | 38.6 | 0 | 98.2625 | 1005.5868 | 78.9% | 0 | 0 | 0 | 0% | 38.6
4558 | 0 | 0 | 0 | 2.8208 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2643 | 36.6 | 0 | 93.2643 | 916.2815 | 71.89% | 0 | 0 | 0 | 0% | 36.6
4559 | 0 | 0 | 0 | 2.0149 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6212 | 35.1 | 0 | 89.6212 | 831.0175 | 65.2% | 0 | 0 | 0 | 0% | 35.1
4560 | 0 | 0 | 0 | 1.6119 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5417 | 34.3 | 0 | 87.5417 | 748.0969 | 58.7% | 0 | 0 | 0 | 0% | 34.3
4561 | 0 | 0 | 0 | 2.8208 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4755 | 33.9 | 0 | 86.4755 | 666.3657 | 52.28% | 0 | 0 | 0 | 0% | 33.9
4562 | 0 | 0 | 0 | 2.0149 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3744 | 34.3 | 0 | 87.3744 | 583.523 | 45.78% | 0 | 0 | 0 | 0% | 34.3
4563 | 0 | 0 | 0 | 3.4253 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1257 | 36.7 | 0 | 93.1257 | 493.8647 | 38.75% | 0 | 0 | 0 | 0% | 36.7
4564 | 0 | 0 | 0 | 2.6193 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0536 | 39.6 | 0 | 100.0536 | 395.9063 | 31.06% | 0 | 0 | 0 | 0% | 39.6
4565 | 0 | 0 | 0 | 3.4253 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.0593 | 42.4 | 0 | 107.0593 | 289.9746 | 22.75% | 0 | 0 | 0 | 0% | 42.4
4566 | 223 | 51 | 24 | 3.6268 | 22.5 | 112.2398 | 0 | 43.971 | 0 | 0.97562 | 0 | 0 | 0.97562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.9746 | 22.75% | 0 | 0 | 0 | 0% | 0.97562
4567 | 597 | 228 | 57 | 5.4401 | 24.4 | 300.4805 | 152.0133 | 0 | 123.0654 | 4.5314 | 0 | 0 | 4.5314 | 0 | 0 | 0 | 0 | 0 | 123.0654 | 0 | 407.3539 | 31.96% | 0 | 0 | 0 | 0% | 4.5314
4568 | 728 | 428 | 83 | 10.6788 | 25.9 | 366.4151 | 210.7721 | 0 | 174.9462 | 24.8599 | 0 | 0 | 24.8599 | 0 | 0 | 0 | 61.4204 | 22.7401 | 174.9462 | 61.4204 | 518.0961 | 40.65% | 0 | 0 | 0 | 0% | 47.6
4569 | 811 | 624 | 100 | 11.8877 | 27.8 | 408.1904 | 250.0745 | 0 | 210.8505 | 47.5867 | 0 | 0 | 47.5867 | 0 | 0 | 0 | 0 | 0 | 210.8505 | 0 | 718.5349 | 56.38% | 0 | 0 | 0 | 0% | 47.5867
4570 | 840 | 785 | 120 | 12.8952 | 28.7 | 422.7866 | 269.2871 | 0 | 228.187 | 77.9333 | 0 | 14.0166 | 63.9166 | 0 | 0 | 0 | 0 | 0 | 228.187 | 0 | 935.4541 | 73.4% | 10.7508 | 0 | 11.0404 | 22.08% | 49.9
4571 | 864 | 907 | 129 | 13.9026 | 29.5 | 434.8662 | 284.0818 | 0 | 241.576 | 100.8 | 0.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 241.576 | 0 | 1165.1012 | 91.42% | 19.175 | 0 | 30.732 | 61.46% | 49.2
4572 | 862 | 974 | 143 | 13.9026 | 30.1 | 433.8596 | 286.7146 | 0 | 244.0966 | 101.5 | 2.0379 | 24.4621 | 75 | 0 | 0 | 0 | 0 | 0 | 244.0966 | 0 | 1274.5104 | 100% | 18.7624 | 0 | 50 | 100% | 48.5
4573 | 863 | 990 | 147 | 14.7085 | 30.6 | 434.3629 | 0 | 284.5758 | 0 | 101.7 | 26.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.3
4574 | 858 | 948 | 143 | 14.7085 | 31.2 | 431.8463 | 0 | 276.2831 | 0 | 101.9 | 26.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.1
4575 | 831 | 848 | 139 | 14.7085 | 31.7 | 418.2567 | 0 | 257.8185 | 0 | 92.4321 | 22.466 | 0 | 69.966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.5
4576 | 784 | 701 | 131 | 14.7085 | 31.2 | 394.6008 | 0 | 229.361 | 0 | 63.3088 | 8.1544 | 0 | 55.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47
4577 | 711 | 516 | 114 | 14.7085 | 30.6 | 357.8587 | 0 | 185.7937 | 0 | 35.3142 | 0 | 0 | 35.3142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 10.8858 | 38.8226 | 77.65% | 46.2
4578 | 620 | 321 | 83 | 13.4996 | 29.7 | 312.0568 | 0 | 128.4406 | 0 | 13.2253 | 0 | 0 | 13.2253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 13.1524 | 26.3% | 38.2253
4579 | 376 | 126 | 50 | 12.2907 | 27.7 | 189.2473 | 0 | 0 | 0 | 2.6677 | 0 | 0 | 2.6677 | 0 | 0 | 0 | 76.7172 | 29.3228 | 0 | 76.7172 | 1203.754 | 94.45% | 0 | 12.8096 | 0 | 0% | 44.8
4580 | 23 | 10 | 8 | 9.6714 | 25.4 | 11.5763 | 0 | 0 | 0 | 0.029963 | 0 | 0 | 0.029963 | 0 | 0 | 0 | 105.9983 | 41.67 | 0 | 105.9983 | 1100.071 | 86.31% | 0 | 0 | 0 | 0% | 41.7
4581 | 0 | 0 | 0 | 5.8431 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9095 | 39.7 | 0 | 100.9095 | 1001.9484 | 78.61% | 0 | 0 | 0 | 0% | 39.7
4582 | 0 | 0 | 0 | 4.0297 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4356 | 37.5 | 0 | 95.4356 | 910.1109 | 71.41% | 0 | 0 | 0 | 0% | 37.5
4583 | 0 | 0 | 0 | 3.8283 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5025 | 35.9 | 0 | 91.5025 | 822.7689 | 64.56% | 0 | 0 | 0 | 0% | 35.9
4584 | 0 | 0 | 0 | 4.2312 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7758 | 35.2 | 0 | 89.7758 | 737.3198 | 57.85% | 0 | 0 | 0 | 0% | 35.2
4585 | 0 | 0 | 0 | 2.4178 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4104 | 34.7 | 0 | 88.4104 | 653.3374 | 51.26% | 0 | 0 | 0 | 0% | 34.7
4586 | 0 | 0 | 0 | 4.8357 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2693 | 35 | 0 | 89.2693 | 568.4136 | 44.6% | 0 | 0 | 0 | 0% | 35
4587 | 0 | 0 | 0 | 3.4253 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4661 | 37.2 | 0 | 94.4661 | 477.3527 | 37.45% | 0 | 0 | 0 | 0% | 37.2
4588 | 0 | 0 | 0 | 2.0149 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.255 | 40.1 | 0 | 101.255 | 377.9663 | 29.66% | 0 | 0 | 0 | 0% | 40.1
4589 | 0 | 0 | 0 | 1.8134 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.9775 | 43.3 | 0 | 108.9775 | 269.4713 | 21.14% | 0 | 0 | 0 | 0% | 43.3
4590 | 66 | 44 | 35 | 2.4178 | 21.2 | 33.2189 | 0 | 13.0023 | 0 | 1.6552 | 0 | 0 | 1.6552 | 0 | 0 | 0 | 60.663 | 22.7615 | 0 | 60.663 | 214.0108 | 16.79% | 0 | 0 | 0 | 0% | 24.4167
4591 | 340 | 202 | 102 | 2.0149 | 24.3 | 171.1279 | 86.5523 | 0 | 63.1708 | 7.0118 | 0 | 0 | 7.0118 | 0 | 0 | 0 | 0 | 0 | 63.1708 | 0 | 274.3184 | 21.52% | 0 | 0 | 0 | 0% | 7.0118
4592 | 535 | 401 | 146 | 4.2312 | 27.5 | 269.2748 | 154.9152 | 0 | 126.298 | 23.9971 | 0 | 0 | 23.9971 | 0 | 0 | 0 | 60.1404 | 22.0178 | 126.298 | 60.1404 | 340.0062 | 26.68% | 0 | 0 | 0 | 0% | 46.0149
4593 | 643 | 594 | 176 | 6.0446 | 29.4 | 323.6331 | 198.3066 | 0 | 166.064 | 44.618 | 0 | 0 | 44.618 | 0 | 0 | 0 | 0 | 0 | 166.064 | 0 | 498.0985 | 39.08% | 0 | 0 | 0 | 0% | 44.618
4594 | 719 | 762 | 191 | 9.2684 | 31.4 | 361.8852 | 230.5284 | 0 | 194.3861 | 72.5028 | 0 | 11.2514 | 61.2514 | 0 | 0 | 0 | 0 | 0 | 194.3861 | 0 | 683.1532 | 53.6% | 8.6298 | 0 | 8.8636 | 17.73% | 50
4595 | 734 | 880 | 217 | 10.6788 | 32.3 | 369.435 | 241.363 | 0 | 203.6453 | 95.6415 | 0 | 22.8207 | 72.8207 | 0 | 0 | 0 | 0 | 0 | 203.6453 | 0 | 877.0227 | 68.81% | 17.5035 | 0 | 26.8413 | 53.68% | 50
4596 | 734 | 952 | 241 | 12.0892 | 32.7 | 369.435 | 244.1689 | 0 | 205.4239 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 205.4239 | 0 | 1072.5854 | 84.16% | 19.175 | 0 | 46.5358 | 93.07% | 50
4597 | 730 | 967 | 250 | 11.8877 | 33.2 | 367.4217 | 240.714 | 0 | 202.3743 | 100 | 20.6026 | 4.3974 | 75 | 0 | 0 | 0 | 0 | 0 | 202.3743 | 0 | 1265.2449 | 99.27% | 3.3728 | 0 | 50 | 100% | 50
4598 | 689 | 917 | 266 | 12.2907 | 33.5 | 346.7857 | 0 | 221.8687 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.2449 | 99.27% | 0 | 0 | 50 | 100% | 50
4599 | 641 | 816 | 264 | 13.7011 | 33.8 | 322.6264 | 0 | 198.8637 | 0 | 82.2196 | 16.1098 | 0 | 66.1098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.2449 | 99.27% | 0 | 0 | 50 | 100% | 50
4600 | 555 | 662 | 255 | 14.5071 | 33.6 | 279.3412 | 0 | 162.329 | 0 | 52.7789 | 1.5894 | 0 | 51.1894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.2449 | 99.27% | 0 | 0 | 50 | 100% | 49.6
4601 | 445 | 478 | 222 | 14.3056 | 32.9 | 223.9762 | 0 | 116.2066 | 0 | 33.0603 | 0 | 0 | 33.0603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.2449 | 99.27% | 0 | 15.4397 | 34.1445 | 68.29% | 48.5
4602 | 274 | 279 | 170 | 13.2981 | 32 | 137.909 | 0 | 56.6163 | 0 | 14.8426 | 0 | 0 | 14.8426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.2449 | 99.27% | 0 | 25 | 8.4702 | 16.94% | 39.8426
4603 | 75 | 100 | 83 | 12.4922 | 29.8 | 37.7488 | 0 | 0 | 0 | 4.7147 | 0 | 0 | 4.7147 | 0 | 0 | 0 | 88.0026 | 33.8366 | 0 | 88.0026 | 1182.1968 | 92.76% | 0 | 8.2487 | 0 | 0% | 46.8
4604 | 1 | 8 | 8 | 9.2684 | 27.5 | 0.50332 | 0 | 0 | 0 | 0.025963 | 0 | 0 | 0.025963 | 0 | 0 | 0 | 111.0787 | 43.574 | 0 | 111.0787 | 1073.0728 | 84.19% | 0 | 0 | 0 | 0% | 43.6
4605 | 0 | 0 | 0 | 10.0743 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.9266 | 41.6 | 0 | 105.9266 | 969.5974 | 76.08% | 0 | 0 | 0 | 0% | 41.6
4606 | 0 | 0 | 0 | 9.0669 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4118 | 39 | 0 | 99.4118 | 873.499 | 68.54% | 0 | 0 | 0 | 0% | 39
4607 | 0 | 0 | 0 | 6.6491 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1266 | 36.9 | 0 | 94.1266 | 783.3004 | 61.46% | 0 | 0 | 0 | 0% | 36.9
4608 | 0 | 0 | 0 | 4.2312 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9902 | 36.1 | 0 | 91.9902 | 695.4032 | 54.56% | 0 | 0 | 0 | 0% | 36.1
4609 | 0 | 0 | 0 | 3.8283 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9782 | 35.7 | 0 | 90.9782 | 608.6113 | 47.75% | 0 | 0 | 0 | 0% | 35.7
4610 | 0 | 0 | 0 | 3.2238 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3746 | 35.9 | 0 | 91.3746 | 521.2446 | 40.9% | 0 | 0 | 0 | 0% | 35.9
4611 | 0 | 0 | 0 | 3.4253 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8878 | 38.2 | 0 | 96.8878 | 427.3572 | 33.53% | 0 | 0 | 0 | 0% | 38.2
4612 | 0 | 0 | 0 | 4.4327 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4556 | 41.2 | 0 | 104.4556 | 324.8883 | 25.49% | 0 | 0 | 0 | 0% | 41.2
4613 | 0 | 0 | 0 | 4.4327 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.2502 | 27.2196 | 0 | 71.2502 | 259.2715 | 20.34% | 0 | 0 | 0 | 0% | 27.2196
4614 | 7 | 41 | 39 | 2.4178 | 23.5 | 3.5232 | 0 | 1.3776 | 0 | 1.8662 | 0 | 0 | 1.8662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.2715 | 20.34% | 0 | 0 | 0 | 0% | 1.8662
4615 | 104 | 156 | 122 | 2.4178 | 26.9 | 52.345 | 0 | 26.4665 | 0 | 7.8849 | 0 | 0 | 7.8849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.2715 | 20.34% | 0 | 0 | 0 | 0% | 7.8849
4616 | 314 | 373 | 221 | 3.6268 | 30 | 158.0417 | 90.9334 | 0 | 66.7695 | 23.4317 | 0 | 0 | 23.4317 | 0 | 0 | 0 | 0 | 0 | 66.7695 | 0 | 323.2182 | 25.36% | 0 | 0 | 0 | 0% | 23.4317
4617 | 432 | 564 | 280 | 5.4401 | 32.1 | 217.4331 | 133.256 | 0 | 105.5361 | 41.2174 | 0 | 0 | 41.2174 | 0 | 0 | 0 | 0 | 0 | 105.5361 | 0 | 424.2925 | 33.29% | 0 | 0 | 0 | 0% | 41.2174
4618 | 531 | 731 | 305 | 7.858 | 34.8 | 267.2615 | 170.274 | 0 | 138.9141 | 63.7999 | 0 | 6.8999 | 56.8999 | 0 | 0 | 0 | 0 | 0 | 138.9141 | 0 | 557.3336 | 43.73% | 5.2922 | 0 | 5.4364 | 10.87% | 50
4619 | 491 | 849 | 397 | 9.2684 | 35.6 | 247.1288 | 161.4734 | 0 | 129.8432 | 84.4207 | 0 | 17.2103 | 67.2103 | 0 | 0 | 0 | 0 | 0 | 129.8432 | 0 | 681.6874 | 53.49% | 13.2003 | 0 | 18.9963 | 37.99% | 50
4620 | 505 | 895 | 400 | 8.8654 | 36.6 | 254.1753 | 168.0077 | 0 | 136.2365 | 93.5716 | 0 | 21.7858 | 71.7858 | 0 | 0 | 0 | 0 | 0 | 136.2365 | 0 | 812.1642 | 63.72% | 16.7097 | 0 | 36.1612 | 72.32% | 50
4621 | 357 | 862 | 500 | 11.4848 | 36.5 | 179.6843 | 117.717 | 0 | 87.9376 | 86.3696 | 0.62057 | 17.5642 | 68.1848 | 0 | 0 | 0 | 0 | 0 | 87.9376 | 0 | 896.3841 | 70.33% | 13.4718 | 0 | 50 | 100% | 50
4622 | 226 | 698 | 474 | 13.0966 | 36.2 | 113.7497 | 72.7777 | 0 | 44.2276 | 58.1489 | 4.0744 | 0 | 54.0744 | 0 | 0 | 0 | 0 | 0 | 44.2276 | 0 | 938.7419 | 73.66% | 0 | 0 | 50 | 100% | 50
4623 | 19 | 416 | 393 | 12.0892 | 35.2 | 9.563 | 0 | 5.8944 | 0 | 29.6894 | 0 | 0 | 29.6894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 938.7419 | 73.66% | 0 | 19.5106 | 29.961 | 59.92% | 49.2
4624 | 16 | 356 | 341 | 11.8877 | 34.4 | 8.0531 | 0 | 4.6787 | 0 | 25.3493 | 0 | 0 | 25.3493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 938.7419 | 73.66% | 0 | 23.3507 | 5.977 | 11.95% | 48.7
4625 | 3 | 177 | 174 | 12.0892 | 32.8 | 1.51 | 0 | 0.78289 | 0 | 12.2507 | 0 | 0 | 12.2507 | 0 | 0 | 0 | 79.0012 | 29.7291 | 0 | 79.0012 | 865.8157 | 67.93% | 0 | 5.8202 | 0 | 0% | 47.8
4626 | 5 | 146 | 143 | 11.2833 | 31.3 | 2.5166 | 0 | 1.0304 | 0 | 9.8083 | 0 | 0 | 9.8083 | 0 | 0 | 0 | 96.0907 | 36.9917 | 0 | 96.0907 | 773.6864 | 60.7% | 0 | 0 | 0 | 0% | 46.8
4627 | 3 | 73 | 72 | 12.2907 | 29.7 | 1.51 | 0 | 0 | 0 | 4.3637 | 0 | 0 | 4.3637 | 0 | 0 | 0 | 105.4373 | 41.0363 | 0 | 105.4373 | 670.9232 | 52.64% | 0 | 0 | 0 | 0% | 45.4
4628 | 0 | 5 | 5 | 6.6491 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.4037 | 42.4 | 0 | 108.4037 | 564.7595 | 44.31% | 0 | 0 | 0 | 0% | 42.4
4629 | 0 | 0 | 0 | 3.6268 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.3482 | 40.8 | 0 | 104.3482 | 463.1032 | 36.34% | 0 | 0 | 0 | 0% | 40.8
4630 | 0 | 0 | 0 | 2.8208 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2794 | 38.4 | 0 | 98.2794 | 368.2455 | 28.89% | 0 | 0 | 0 | 0% | 38.4
4631 | 0 | 0 | 0 | 1.4104 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8536 | 32.4755 | 0 | 83.8536 | 289.6126 | 22.72% | 0 | 0 | 0 | 0% | 32.4755
4632 | 0 | 0 | 0 | 4.6342 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.6126 | 22.72% | 0 | 0 | 0 | 0% | 0
4633 | 0 | 0 | 0 | 5.0372 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.6126 | 22.72% | 0 | 0 | 0 | 0% | 0
4634 | 0 | 0 | 0 | 4.0297 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.6126 | 22.72% | 0 | 0 | 0 | 0% | 0
4635 | 0 | 0 | 0 | 3.0223 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.6126 | 22.72% | 0 | 0 | 0 | 0% | 0
4636 | 0 | 0 | 0 | 2.2164 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.6126 | 22.72% | 0 | 0 | 0 | 0% | 0
4637 | 0 | 0 | 0 | 3.0223 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.6126 | 22.72% | 0 | 0 | 0 | 0% | 0
4638 | 1 | 30 | 30 | 2.8208 | 23.3 | 0.50332 | 0 | 0.19658 | 0 | 1.3804 | 0 | 0 | 1.3804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.6126 | 22.72% | 0 | 0 | 0 | 0% | 1.3804
4639 | 103 | 158 | 126 | 2.0149 | 26.6 | 51.8417 | 0 | 26.202 | 0 | 8.1082 | 0 | 0 | 8.1082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289.6126 | 22.72% | 0 | 0 | 0 | 0% | 8.1082
4640 | 285 | 351 | 210 | 3.0223 | 28.9 | 143.4455 | 82.5443 | 0 | 58.827 | 22.0131 | 0 | 0 | 22.0131 | 0 | 0 | 0 | 0 | 0 | 58.827 | 0 | 345.9625 | 27.14% | 0 | 0 | 0 | 0% | 22.0131
4641 | 432 | 544 | 260 | 4.8357 | 32.1 | 217.4331 | 133.2793 | 0 | 105.8619 | 40.0652 | 0 | 0 | 40.0652 | 0 | 0 | 0 | 0 | 0 | 105.8619 | 0 | 447.3667 | 35.1% | 0 | 0 | 0 | 0% | 40.0652
4642 | 529 | 707 | 290 | 4.4327 | 33.9 | 266.2549 | 169.6549 | 0 | 140.1122 | 64.6562 | 0 | 9.4781 | 55.1781 | 0 | 0 | 0 | 0 | 0 | 140.1122 | 0 | 581.5789 | 45.63% | 7.2697 | 0 | 7.4688 | 14.94% | 45.7
4643 | 593 | 828 | 303 | 4.8357 | 35.4 | 298.4672 | 195.0377 | 0 | 163.7318 | 87.872 | 0 | 21.236 | 66.636 | 0 | 0 | 0 | 0 | 0 | 163.7318 | 0 | 738.4162 | 57.94% | 16.288 | 0 | 24.2029 | 48.41% | 45.4
4644 | 635 | 920 | 307 | 5.2387 | 36.4 | 319.6065 | 211.2592 | 0 | 178.764 | 103.2973 | 4.4486 | 25 | 73.8486 | 0 | 0 | 0 | 0 | 0 | 178.764 | 0 | 909.6528 | 71.37% | 19.175 | 0 | 43.9031 | 87.81% | 44.4
4645 | 621 | 939 | 328 | 7.052 | 37 | 312.5601 | 204.7655 | 0 | 171.7355 | 106.5 | 23.763 | 7.737 | 75 | 0 | 0 | 0 | 0 | 0 | 171.7355 | 0 | 1074.1567 | 84.28% | 5.9343 | 0 | 50 | 100% | 43.5
4646 | 666 | 897 | 273 | 6.4476 | 36.9 | 335.2094 | 214.4768 | 0 | 181.0773 | 102.152 | 29.626 | 0 | 72.526 | 0 | 0 | 0 | 0 | 0 | 181.0773 | 0 | 1247.6091 | 97.89% | 0 | 0 | 50 | 100% | 42.9
4647 | 524 | 701 | 249 | 9.6714 | 36.5 | 263.7383 | 0 | 162.5578 | 0 | 69.4981 | 13.449 | 0 | 56.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.6091 | 97.89% | 0 | 0 | 50 | 100% | 42.6
4648 | 515 | 612 | 235 | 12.0892 | 36.1 | 259.2085 | 0 | 150.5622 | 0 | 51.9031 | 4.8516 | 0 | 47.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.6091 | 97.89% | 0 | 0 | 50 | 100% | 42.2
4649 | 406 | 437 | 201 | 11.6862 | 35.5 | 204.3469 | 0 | 105.8794 | 0 | 29.849 | 0 | 0 | 29.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.6091 | 97.89% | 0 | 11.951 | 37.7235 | 75.45% | 41.8
4650 | 331 | 282 | 154 | 7.858 | 34.9 | 166.5981 | 0 | 68.0306 | 0 | 14.3224 | 0 | 0 | 14.3224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.6091 | 97.89% | 0 | 25 | 12.042 | 24.08% | 39.3224
4651 | 132 | 105 | 77 | 5.0372 | 32.1 | 66.4379 | 0 | 0 | 0 | 4.343 | 0 | 0 | 4.343 | 0 | 0 | 0 | 68.7229 | 25.2339 | 0 | 68.7229 | 1184.5501 | 92.94% | 0 | 11.7231 | 0 | 0% | 41.3
4652 | 2 | 8 | 8 | 4.0297 | 29.5 | 1.0066 | 0 | 0 | 0 | 0.022052 | 0 | 0 | 0.022052 | 0 | 0 | 0 | 100.3729 | 38.9779 | 0 | 100.3729 | 1087.4795 | 85.33% | 0 | 0 | 0 | 0% | 39
4653 | 0 | 0 | 0 | 4.0297 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5109 | 36.8 | 0 | 94.5109 | 996.9039 | 78.22% | 0 | 0 | 0 | 0% | 36.8
4654 | 0 | 0 | 0 | 5.2387 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6272 | 34.5 | 0 | 88.6272 | 912.8423 | 71.62% | 0 | 0 | 0 | 0% | 34.5
4655 | 0 | 0 | 0 | 5.2387 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7995 | 33 | 0 | 84.7995 | 833.1038 | 65.37% | 0 | 0 | 0 | 0% | 33
4656 | 0 | 0 | 0 | 3.4253 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2265 | 32 | 0 | 82.2265 | 756.2219 | 59.33% | 0 | 0 | 0 | 0% | 32
4657 | 0 | 0 | 0 | 1.4104 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3193 | 31.3 | 0 | 80.3193 | 681.4156 | 53.46% | 0 | 0 | 0 | 0% | 31.3
4658 | 0 | 0 | 0 | 3.2238 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1558 | 30.8 | 0 | 79.1558 | 607.8932 | 47.7% | 0 | 0 | 0 | 0% | 30.8
4659 | 0 | 0 | 0 | 2.2164 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5752 | 30.6 | 0 | 78.5752 | 534.9815 | 41.98% | 0 | 0 | 0 | 0% | 30.6
4660 | 0 | 0 | 0 | 2.4178 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6357 | 30.2 | 0 | 77.6357 | 463.0936 | 36.34% | 0 | 0 | 0 | 0% | 30.2
4661 | 0 | 0 | 0 | 2.6193 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4629 | 31.8 | 0 | 81.4629 | 386.9467 | 30.36% | 0 | 0 | 0 | 0% | 31.8
4662 | 230 | 48 | 20 | 2.8208 | 22.2 | 115.763 | 0 | 45.1541 | 0 | 0.67548 | 0 | 0 | 0.67548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386.9467 | 30.36% | 0 | 0 | 0 | 0% | 0.67548
4663 | 645 | 230 | 47 | 3.2238 | 25.9 | 324.6397 | 164.0058 | 0 | 135.0828 | 4.0531 | 0 | 0 | 4.0531 | 0 | 0 | 0 | 0 | 0 | 135.0828 | 0 | 513.5888 | 40.3% | 0 | 0 | 0 | 0% | 4.0531
4664 | 780 | 435 | 66 | 4.4327 | 28.3 | 392.5876 | 225.9332 | 0 | 192.6689 | 24.3188 | 0 | 0 | 24.3188 | 0 | 0 | 0 | 0 | 0 | 192.6689 | 0 | 694.2189 | 54.47% | 0 | 0 | 0 | 0% | 24.3188
4665 | 851 | 627 | 79 | 4.0297 | 30.5 | 428.3231 | 262.5934 | 0 | 226.9404 | 53.9899 | 0 | 7.545 | 46.445 | 0 | 0 | 0 | 0 | 0 | 226.9404 | 0 | 906.9789 | 71.16% | 5.787 | 0 | 5.9463 | 11.89% | 38.9
4666 | 884 | 779 | 91 | 10.2758 | 31.5 | 444.9326 | 283.5427 | 0 | 243.2574 | 87.437 | 0 | 23.8185 | 63.6185 | 0 | 0 | 0 | 0 | 0 | 243.2574 | 0 | 1135.0364 | 89.06% | 18.2688 | 0 | 24.7182 | 49.44% | 39.8
4667 | 894 | 888 | 105 | 6.8506 | 31.8 | 449.9657 | 294.0665 | 0 | 255.2263 | 108.4102 | 9.1051 | 25 | 74.3051 | 0 | 0 | 0 | 0 | 0 | 255.2263 | 0 | 1274.5104 | 100% | 19.175 | 0 | 44.4212 | 88.84% | 40.2
4668 | 892 | 964 | 115 | 5.8431 | 33.2 | 448.9591 | 0 | 296.7634 | 0 | 110.8 | 28.7214 | 7.0786 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 5.4293 | 0 | 50 | 100% | 39.2
4669 | 885 | 981 | 122 | 6.2461 | 34.1 | 445.4359 | 0 | 291.8125 | 0 | 111.6 | 36.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.4
4670 | 865 | 930 | 126 | 6.4476 | 34.8 | 435.3695 | 0 | 278.5749 | 0 | 111.8 | 36.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.2
4671 | 824 | 835 | 131 | 8.4625 | 35.3 | 414.7335 | 0 | 255.6221 | 0 | 95.5472 | 28.6236 | 0 | 66.9236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.3
4672 | 767 | 684 | 127 | 9.4699 | 35 | 386.0444 | 0 | 224.1869 | 0 | 67.4727 | 14.4364 | 0 | 53.0364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.6
4673 | 693 | 508 | 112 | 8.261 | 34.5 | 348.7989 | 0 | 180.6028 | 0 | 34.054 | 0 | 0 | 34.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 4.946 | 44.9186 | 89.84% | 39
4674 | 576 | 304 | 86 | 4.0297 | 34 | 289.9108 | 0 | 118.0607 | 0 | 12.791 | 0 | 0 | 12.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 19.2337 | 38.47% | 37.791
4675 | 335 | 116 | 50 | 5.8431 | 30.9 | 168.6113 | 0 | 0 | 0 | 2.5479 | 0 | 0 | 2.5479 | 0 | 0 | 0 | 56.7987 | 20.2309 | 0 | 56.7987 | 1222.9202 | 95.95% | 0 | 18.7212 | 2.7756e-15 | 5.551e-15% | 41.5
4676 | 22 | 8 | 7 | 3.2238 | 27.6 | 11.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9402 | 39.4 | 0 | 100.9402 | 1125.1234 | 88.28% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.4
4677 | 0 | 0 | 0 | 1.2089 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.659 | 36.9 | 0 | 94.659 | 1034.3657 | 81.16% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.9
4678 | 0 | 0 | 0 | 2.6193 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6197 | 34.8 | 0 | 89.6197 | 949.2107 | 74.48% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.8
4679 | 0 | 0 | 0 | 1.6119 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3473 | 33.1 | 0 | 85.3473 | 868.909 | 68.18% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.1
4680 | 0 | 0 | 0 | 2.2164 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3022 | 32.3 | 0 | 83.3022 | 790.8847 | 62.05% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.3
4681 | 0 | 0 | 0 | 2.4178 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5761 | 32 | 0 | 82.5761 | 713.6637 | 56% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32
4682 | 0 | 0 | 0 | 1.4104 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3805 | 32.8 | 0 | 84.3805 | 634.375 | 49.77% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.8
4683 | 0 | 0 | 0 | 1.8134 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7226 | 35.9 | 0 | 91.7226 | 546.723 | 42.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.9
4684 | 0 | 0 | 0 | 2.6193 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.8178 | 39.2 | 0 | 99.8178 | 449.8769 | 35.3% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.2
4685 | 0 | 0 | 0 | 2.8208 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5 | 42.8 | 0 | 108.5 | 342.7581 | 26.89% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 42.8
4686 | 141 | 41 | 25 | 2.6193 | 24.7 | 70.9678 | 0 | 27.6417 | 0 | 0.90197 | 0 | 0 | 0.90197 | 0 | 0 | 0 | 60.6639 | 22.5133 | 0 | 60.6639 | 287.3013 | 22.54% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 23.4152
4687 | 479 | 204 | 69 | 1.6119 | 28.2 | 241.089 | 121.7327 | 0 | 96.1582 | 5.0298 | 0 | 0 | 5.0298 | 0 | 0 | 0 | 0 | 0 | 96.1582 | 0 | 378.2331 | 29.68% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 5.0298
4688 | 661 | 405 | 96 | 3.2238 | 31 | 332.6928 | 191.4805 | 0 | 160.8396 | 23.2291 | 0 | 0 | 23.2291 | 0 | 0 | 0 | 69.3989 | 25.6709 | 160.8396 | 69.3989 | 466.5333 | 36.6% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 48.9
4689 | 764 | 601 | 111 | 4.8357 | 33.2 | 384.5345 | 235.7879 | 0 | 201.8621 | 44.6917 | 0 | 0 | 44.6917 | 0 | 0 | 0 | 0 | 0 | 201.8621 | 0 | 656.9578 | 51.55% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 44.6917
4690 | 807 | 772 | 136 | 5.8431 | 34.6 | 406.1771 | 258.8771 | 0 | 222.7328 | 72.1835 | 0 | 11.0918 | 61.0918 | 0 | 0 | 0 | 0 | 0 | 222.7328 | 0 | 867.0703 | 68.03% | 8.5074 | 0 | 8.7429 | 17.49% | 50
4691 | 841 | 915 | 159 | 6.2461 | 35.5 | 423.2899 | 276.6609 | 0 | 239.1866 | 97.8144 | 0 | 23.9072 | 73.9072 | 0 | 0 | 0 | 0 | 0 | 239.1866 | 0 | 1092.7045 | 85.74% | 18.3368 | 0 | 27.5874 | 55.17% | 50
4692 | 847 | 1020 | 204 | 7.052 | 36.4 | 426.3098 | 281.7941 | 0 | 243.5839 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 243.5839 | 0 | 1274.5104 | 100% | 19.175 | 0 | 47.2933 | 94.59% | 50
4693 | 831 | 1041 | 231 | 15.1115 | 36.7 | 418.2567 | 0 | 274.005 | 0 | 100 | 21.5662 | 3.4338 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 2.6337 | 0 | 50 | 100% | 50
4694 | 822 | 948 | 178 | 15.1115 | 36.6 | 413.7269 | 0 | 264.7406 | 0 | 100.1 | 25.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.9
4695 | 808 | 847 | 156 | 14.3056 | 36.2 | 406.6804 | 0 | 250.6576 | 0 | 89 | 20 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49
4696 | 759 | 690 | 139 | 14.91 | 35.8 | 382.0179 | 0 | 221.802 | 0 | 59.5444 | 5.6222 | 0 | 53.9222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.3
4697 | 633 | 488 | 128 | 13.0966 | 35.8 | 318.5999 | 0 | 164.8543 | 0 | 33.2003 | 0 | 0 | 33.2003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 14.1997 | 35.4094 | 70.82% | 47.4
4698 | 503 | 288 | 98 | 11.4848 | 35 | 253.1686 | 0 | 102.8097 | 0 | 12.8684 | 0 | 0 | 12.8684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 9.7203 | 19.44% | 37.8684
4699 | 256 | 108 | 59 | 9.0669 | 33.5 | 128.8493 | 0 | 0 | 0 | 3.0762 | 0 | 0 | 3.0762 | 0 | 0 | 0 | 87.7886 | 33.2634 | 0 | 87.7886 | 1191.9156 | 93.52% | 0 | 9.4604 | 0 | 0% | 45.8
4700 | 16 | 8 | 7 | 4.8357 | 30.9 | 8.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1503 | 42.4 | 0 | 109.1503 | 1085.0809 | 85.14% | 0 | 0 | 0 | 0% | 42.4
4701 | 0 | 0 | 0 | 3.4253 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.1039 | 40.3 | 0 | 103.1039 | 984.8689 | 77.27% | 0 | 0 | 0 | 0% | 40.3
4702 | 0 | 0 | 0 | 1.4104 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2089 | 38 | 0 | 97.2089 | 891.2678 | 69.93% | 0 | 0 | 0 | 0% | 38
4703 | 0 | 0 | 0 | 1.0074 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8099 | 36.2 | 0 | 92.8099 | 802.5646 | 62.97% | 0 | 0 | 0 | 0% | 36.2
4704 | 0 | 0 | 0 | 2.2164 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6408 | 35.3 | 0 | 90.6408 | 716.2475 | 56.2% | 0 | 0 | 0 | 0% | 35.3
4705 | 0 | 0 | 0 | 5.6416 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4795 | 34.9 | 0 | 89.4795 | 631.1798 | 49.52% | 0 | 0 | 0 | 0% | 34.9
4706 | 0 | 0 | 0 | 10.6788 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9017 | 35.2 | 0 | 89.9017 | 545.5739 | 42.81% | 0 | 0 | 0 | 0% | 35.2
4707 | 0 | 0 | 0 | 10.2758 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4355 | 37.6 | 0 | 95.4355 | 453.3682 | 35.57% | 0 | 0 | 0 | 0% | 37.6
4708 | 0 | 0 | 0 | 11.0818 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6211 | 40.2 | 0 | 101.6211 | 353.689 | 27.75% | 0 | 0 | 0 | 0% | 40.2
4709 | 0 | 0 | 0 | 8.6639 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9353 | 32.0406 | 0 | 81.9353 | 277.0224 | 21.74% | 0 | 0 | 0 | 0% | 32.0406
4710 | 75 | 37 | 27 | 6.4476 | 21.5 | 37.7488 | 0 | 14.6798 | 0 | 1.0471 | 0 | 0 | 1.0471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277.0224 | 21.74% | 0 | 0 | 0 | 0% | 1.0471
4711 | 432 | 199 | 76 | 9.2684 | 23.9 | 217.4331 | 109.7227 | 0 | 81.1109 | 5.4425 | 0 | 0 | 5.4425 | 0 | 0 | 0 | 0 | 0 | 81.1109 | 0 | 354.483 | 27.81% | 0 | 0 | 0 | 0% | 5.4425
4712 | 629 | 399 | 105 | 13.2981 | 26.6 | 316.5866 | 182.2241 | 0 | 146.7286 | 23.8515 | 0 | 0 | 23.8515 | 0 | 0 | 0 | 67.7458 | 25.4485 | 146.7286 | 67.7458 | 432.3592 | 33.92% | 0 | 0 | 0 | 0% | 49.3
4713 | 737 | 595 | 123 | 14.1041 | 28 | 370.9449 | 227.4933 | 0 | 188.607 | 46.0204 | 0 | 0 | 46.0204 | 0 | 0 | 0 | 0 | 0 | 188.607 | 0 | 611.9327 | 48.01% | 0 | 0 | 0 | 0% | 46.0204
4714 | 803 | 763 | 131 | 13.7011 | 29.9 | 404.1639 | 257.625 | 0 | 216.8519 | 75.7131 | 0 | 12.8566 | 62.8566 | 0 | 0 | 0 | 0 | 0 | 216.8519 | 0 | 818.3984 | 64.21% | 9.861 | 0 | 10.1354 | 20.27% | 50
4715 | 833 | 887 | 141 | 14.7085 | 30.7 | 419.2634 | 274.0565 | 0 | 231.6665 | 99.2773 | 0 | 24.6387 | 74.6387 | 0 | 0 | 0 | 0 | 0 | 231.6665 | 0 | 1038.9692 | 81.52% | 18.8979 | 0 | 29.5593 | 59.12% | 50
4716 | 855 | 963 | 142 | 14.5071 | 30.7 | 430.3364 | 284.4574 | 0 | 241.6185 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 241.6185 | 0 | 1269.0152 | 99.57% | 19.175 | 0 | 49.2681 | 98.54% | 50
4717 | 874 | 985 | 132 | 12.6937 | 31.5 | 439.8994 | 0 | 288.1824 | 0 | 100.1 | 25.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.0152 | 99.57% | 0 | 0 | 49.2681 | 98.54% | 49.9
4718 | 867 | 941 | 129 | 11.6862 | 32 | 436.3762 | 0 | 279.2506 | 0 | 100.4 | 25.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.0152 | 99.57% | 0 | 0 | 49.2681 | 98.54% | 49.6
4719 | 832 | 837 | 127 | 12.0892 | 32.2 | 418.7601 | 0 | 258.104 | 0 | 88.9808 | 20.2404 | 0 | 68.7404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.0152 | 99.57% | 0 | 0 | 49.2681 | 98.54% | 48.5
4720 | 756 | 681 | 133 | 12.8952 | 31.7 | 380.5079 | 0 | 220.8801 | 0 | 60.3304 | 6.3152 | 0 | 54.0152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.0152 | 99.57% | 0 | 0 | 49.2681 | 98.54% | 47.7
4721 | 656 | 493 | 124 | 13.4996 | 30.7 | 330.1762 | 0 | 170.7284 | 0 | 34.4567 | 0 | 0 | 34.4567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.0152 | 99.57% | 0 | 12.3433 | 36.5831 | 73.17% | 46.8
4722 | 523 | 296 | 96 | 13.2981 | 29 | 263.235 | 0 | 106.5928 | 0 | 13.3267 | 0 | 0 | 13.3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.0152 | 99.57% | 0 | 25 | 10.8904 | 21.78% | 38.3267
4723 | 305 | 114 | 53 | 12.2907 | 27.1 | 153.5118 | 0 | 0 | 0 | 2.7893 | 0 | 0 | 2.7893 | 0 | 0 | 0 | 81.7374 | 31.5133 | 0 | 81.7374 | 1192.8942 | 93.6% | 0 | 10.5974 | 1.3878e-15 | 2.776e-15% | 44.9
4724 | 12 | 8 | 7 | 11.2833 | 24.7 | 6.0398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.6451 | 42 | 0 | 106.6451 | 1088.2695 | 85.39% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 42
4725 | 0 | 0 | 0 | 9.8729 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9905 | 39.8 | 0 | 100.9905 | 989.8522 | 77.67% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 39.8
4726 | 0 | 0 | 0 | 7.455 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2454 | 37.5 | 0 | 95.2454 | 898.0095 | 70.46% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 37.5
4727 | 0 | 0 | 0 | 5.8431 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0448 | 35.8 | 0 | 91.0448 | 810.9422 | 63.63% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 35.8
4728 | 0 | 0 | 0 | 5.6416 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2796 | 35.1 | 0 | 89.2796 | 725.8141 | 56.95% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 35.1
4729 | 0 | 0 | 0 | 4.2312 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0257 | 34.6 | 0 | 88.0257 | 642.1179 | 50.38% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 34.6
4730 | 0 | 0 | 0 | 1.6119 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9312 | 35 | 0 | 88.9312 | 557.2397 | 43.72% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 35
4731 | 0 | 0 | 0 | 2.6193 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9238 | 37.5 | 0 | 94.9238 | 465.322 | 36.51% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 37.5
4732 | 0 | 0 | 0 | 2.8208 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9423 | 40.4 | 0 | 101.9423 | 365.0852 | 28.65% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 40.4
4733 | 0 | 0 | 0 | 4.4327 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.0852 | 28.65% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
4734 | 168 | 45 | 26 | 2.8208 | 21.6 | 84.5573 | 0 | 32.8263 | 0 | 0.96177 | 0 | 0 | 0.96177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.0852 | 28.65% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0.96177
4735 | 245 | 172 | 112 | 1.4104 | 24.1 | 123.3128 | 62.1853 | 0 | 40.4555 | 7.5134 | 0 | 0 | 7.5134 | 0 | 0 | 0 | 0 | 0 | 40.4555 | 0 | 403.7496 | 31.68% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 7.5134
4736 | 171 | 281 | 192 | 2.6193 | 25.1 | 86.0673 | 0 | 49.5425 | 0 | 18.076 | 0 | 0 | 18.076 | 0 | 0 | 0 | 79.6518 | 30.824 | 0 | 79.6518 | 329.7223 | 25.87% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 48.9
4737 | 641 | 675 | 259 | 3.0223 | 28.1 | 322.6264 | 197.8931 | 0 | 166.9001 | 49.9357 | 0 | 0 | 49.9357 | 0 | 0 | 0 | 0 | 0 | 166.9001 | 0 | 488.8474 | 38.36% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 49.9357
4738 | 557 | 676 | 234 | 2.4178 | 29.8 | 280.3478 | 178.7221 | 0 | 149.225 | 56.3521 | 0 | 3.176 | 53.176 | 0 | 0 | 0 | 0 | 0 | 149.225 | 0 | 631.1208 | 49.52% | 2.436 | 0 | 2.5042 | 5.008% | 50
4739 | 842 | 958 | 206 | 7.6565 | 30.6 | 423.7932 | 277.0447 | 0 | 238.6336 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 238.6336 | 0 | 858.6378 | 67.37% | 19.175 | 0 | 22.2158 | 44.43% | 50
4740 | 812 | 995 | 216 | 7.858 | 31.3 | 408.6937 | 270.1526 | 0 | 232.0445 | 100.8 | 0.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 232.0445 | 0 | 1079.8726 | 84.73% | 19.175 | 0 | 41.9274 | 83.85% | 49.2
4741 | 913 | 994 | 111 | 7.858 | 31.9 | 459.5288 | 301.0417 | 0 | 261.0954 | 101.1 | 15.8616 | 10.2384 | 75 | 0 | 0 | 0 | 0 | 0 | 261.0954 | 0 | 1274.5104 | 100% | 7.8528 | 0 | 50 | 100% | 48.9
4742 | 905 | 950 | 108 | 8.8654 | 32.5 | 455.5022 | 0 | 291.5099 | 0 | 101.4 | 26.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.6
4743 | 852 | 840 | 119 | 11.6862 | 32.1 | 428.8264 | 0 | 264.3117 | 0 | 91.5171 | 21.9586 | 0 | 69.5586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.6
4744 | 801 | 690 | 115 | 12.2907 | 30.9 | 403.1572 | 0 | 233.9814 | 0 | 63.9083 | 8.6042 | 0 | 55.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.7
4745 | 712 | 508 | 111 | 12.2907 | 28.8 | 358.362 | 0 | 185.1339 | 0 | 35.8185 | 0 | 0 | 35.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.9815 | 39.7407 | 79.48% | 45.8
4746 | 443 | 282 | 111 | 9.8729 | 27.4 | 222.9696 | 0 | 90.0261 | 0 | 13.3181 | 0 | 0 | 13.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 14.0445 | 28.09% | 38.3181
4747 | 137 | 77 | 44 | 5.4401 | 26.1 | 68.9545 | 0 | 0 | 0 | 2.4056 | 0 | 0 | 2.4056 | 0 | 0 | 0 | 73.4725 | 28.0299 | 0 | 73.4725 | 1206.8586 | 94.69% | 0 | 13.6645 | 0 | 0% | 44.1
4748 | 1 | 6 | 6 | 8.8654 | 24.8 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0008 | 40.9 | 0 | 104.0008 | 1105.3356 | 86.73% | 0 | 0 | 0 | 0% | 40.9
4749 | 0 | 0 | 0 | 7.455 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3567 | 39.1 | 0 | 99.3567 | 1008.9271 | 79.16% | 0 | 0 | 0 | 0% | 39.1
4750 | 0 | 0 | 0 | 4.6342 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1443 | 37 | 0 | 94.1443 | 918.4909 | 72.07% | 0 | 0 | 0 | 0% | 37
4751 | 0 | 0 | 0 | 2.4178 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3637 | 35.5 | 0 | 90.3637 | 832.2533 | 65.3% | 0 | 0 | 0 | 0% | 35.5
4752 | 0 | 0 | 0 | 1.4104 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3916 | 34.7 | 0 | 88.3916 | 748.2714 | 58.71% | 0 | 0 | 0 | 0% | 34.7
4753 | 0 | 0 | 0 | 1.4104 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3944 | 34.3 | 0 | 87.3944 | 665.4398 | 52.21% | 0 | 0 | 0 | 0% | 34.3
4754 | 0 | 0 | 0 | 2.6193 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5052 | 34.8 | 0 | 88.5052 | 581.1389 | 45.6% | 0 | 0 | 0 | 0% | 34.8
4755 | 0 | 0 | 0 | 1.8134 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0447 | 37.1 | 0 | 94.0447 | 490.3476 | 38.47% | 0 | 0 | 0 | 0% | 37.1
4756 | 0 | 0 | 0 | 2.0149 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9613 | 40 | 0 | 100.9613 | 391.2273 | 30.7% | 0 | 0 | 0 | 0% | 40
4757 | 0 | 0 | 0 | 4.6342 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7824 | 32.4114 | 0 | 82.7824 | 313.6001 | 24.61% | 0 | 0 | 0 | 0% | 32.4114
4758 | 150 | 39 | 23 | 3.2238 | 21.7 | 75.4976 | 0 | 29.2545 | 0 | 0.7708 | 0 | 0 | 0.7708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313.6001 | 24.61% | 0 | 0 | 0 | 0% | 0.7708
4759 | 515 | 204 | 62 | 2.8208 | 23.6 | 259.2085 | 130.6189 | 0 | 103.9333 | 4.6791 | 0 | 0 | 4.6791 | 0 | 0 | 0 | 0 | 0 | 103.9333 | 0 | 412.5318 | 32.37% | 0 | 0 | 0 | 0% | 4.6791
4760 | 704 | 408 | 83 | 4.0297 | 26.3 | 354.3354 | 203.9739 | 0 | 172.3039 | 23.9666 | 0 | 0 | 23.9666 | 0 | 0 | 0 | 66.5019 | 24.9334 | 172.3039 | 66.5019 | 515.4925 | 40.45% | 0 | 0 | 0 | 0% | 48.9
4761 | 789 | 601 | 100 | 7.052 | 26.8 | 397.1174 | 243.6239 | 0 | 207.7293 | 46.4646 | 0 | 0 | 46.4646 | 0 | 0 | 0 | 0 | 0 | 207.7293 | 0 | 712.6159 | 55.91% | 0 | 0 | 0 | 0% | 46.4646
4762 | 831 | 762 | 115 | 8.261 | 28 | 418.2567 | 266.6693 | 0 | 228.4688 | 75.6548 | 0 | 12.8274 | 62.8274 | 0 | 0 | 0 | 0 | 0 | 228.4688 | 0 | 929.4199 | 72.92% | 9.8386 | 0 | 10.1154 | 20.23% | 50
4763 | 874 | 893 | 116 | 11.2833 | 29.4 | 439.8994 | 287.6016 | 0 | 246.4596 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 246.4596 | 0 | 1163.2962 | 91.27% | 19.175 | 0 | 29.8298 | 59.66% | 50
4764 | 905 | 974 | 110 | 11.4848 | 30.9 | 455.5022 | 301.0949 | 0 | 258.996 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 258.996 | 0 | 1274.5104 | 100% | 19.175 | 0 | 49.5443 | 99.09% | 50
4765 | 919 | 994 | 104 | 11.6862 | 31.8 | 462.5487 | 0 | 303.0211 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.5443 | 99.09% | 50
4766 | 928 | 960 | 95 | 12.0892 | 32.3 | 467.0785 | 0 | 298.9411 | 0 | 100.4 | 25.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.5443 | 99.09% | 49.6
4767 | 919 | 864 | 87 | 11.4848 | 32.7 | 462.5487 | 0 | 285.1028 | 0 | 94.4198 | 22.8599 | 0 | 71.5599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.5443 | 99.09% | 48.7
4768 | 887 | 716 | 81 | 12.0892 | 32.7 | 446.4425 | 0 | 259.0516 | 0 | 65.6951 | 8.7476 | 0 | 56.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.5443 | 99.09% | 48.2
4769 | 821 | 529 | 73 | 11.4848 | 32.4 | 413.2236 | 0 | 213.1711 | 0 | 36.658 | 0 | 0 | 36.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 10.542 | 38.7074 | 77.41% | 47.2
4770 | 695 | 321 | 61 | 11.2833 | 30.8 | 349.8056 | 0 | 140.8206 | 0 | 13.038 | 0 | 0 | 13.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 13.0074 | 26.01% | 38.038
4771 | 442 | 121 | 38 | 8.0595 | 29.3 | 222.4663 | 0 | 0 | 0 | 1.8257 | 0 | 0 | 1.8257 | 0 | 0 | 0 | 81.7567 | 31.3207 | 0 | 81.7567 | 1198.4574 | 94.03% | 0 | 12.6536 | 0 | 0% | 45.8
4772 | 23 | 6 | 4 | 7.052 | 27 | 11.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8171 | 42.7 | 0 | 108.8171 | 1091.8212 | 85.67% | 0 | 0 | 0 | 0% | 42.7
4773 | 0 | 0 | 0 | 6.6491 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0313 | 40.5 | 0 | 103.0313 | 991.4236 | 77.79% | 0 | 0 | 0 | 0% | 40.5
4774 | 0 | 0 | 0 | 5.6416 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6888 | 38 | 0 | 96.6888 | 898.1617 | 70.47% | 0 | 0 | 0 | 0% | 38
4775 | 0 | 0 | 0 | 3.6268 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.33 | 36.3 | 0 | 92.33 | 809.695 | 63.53% | 0 | 0 | 0 | 0% | 36.3
4776 | 0 | 0 | 0 | 4.6342 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3457 | 35.5 | 0 | 90.3457 | 723.4546 | 56.76% | 0 | 0 | 0 | 0% | 35.5
4777 | 0 | 0 | 0 | 4.0297 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3229 | 35 | 0 | 89.3229 | 638.4909 | 50.1% | 0 | 0 | 0 | 0% | 35
4778 | 0 | 0 | 0 | 3.4253 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8941 | 35.3 | 0 | 89.8941 | 552.7797 | 43.37% | 0 | 0 | 0 | 0% | 35.3
4779 | 0 | 0 | 0 | 5.8431 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5751 | 37.7 | 0 | 95.5751 | 460.2956 | 36.12% | 0 | 0 | 0 | 0% | 37.7
4780 | 0 | 0 | 0 | 6.4476 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2405 | 40.5 | 0 | 102.2405 | 359.7794 | 28.23% | 0 | 0 | 0 | 0% | 40.5
4781 | 0 | 0 | 0 | 7.052 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.9623 | 43.7 | 0 | 109.9623 | 250.1284 | 19.63% | 0 | 0 | 0 | 0% | 43.7
4782 | 152 | 41 | 25 | 5.4401 | 20.5 | 76.5042 | 0 | 29.5848 | 0 | 0.84646 | 0 | 0 | 0.84646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250.1284 | 19.63% | 0 | 0 | 0 | 0% | 0.84646
4783 | 501 | 204 | 67 | 4.2312 | 22.4 | 252.162 | 126.9641 | 0 | 100.0564 | 5.0557 | 0 | 0 | 5.0557 | 0 | 0 | 0 | 0 | 0 | 100.0564 | 0 | 346.1026 | 27.16% | 0 | 0 | 0 | 0% | 5.0557
4784 | 658 | 404 | 100 | 6.2461 | 26.3 | 331.1828 | 190.6524 | 0 | 158.7071 | 24.0856 | 0 | 0 | 24.0856 | 0 | 0 | 0 | 68.7474 | 25.9144 | 158.7071 | 68.7474 | 435.1379 | 34.14% | 0 | 0 | 0 | 0% | 50
4785 | 758 | 603 | 119 | 8.8654 | 29.8 | 381.5146 | 234.0888 | 0 | 197.9484 | 46.2416 | 0 | 0 | 46.2416 | 0 | 0 | 0 | 0 | 0 | 197.9484 | 0 | 624.3721 | 48.99% | 0 | 0 | 0 | 0% | 46.2416
4786 | 830 | 774 | 125 | 12.0892 | 31.9 | 417.7534 | 266.377 | 0 | 226.0346 | 77.2667 | 0 | 13.6334 | 63.6334 | 0 | 0 | 0 | 0 | 0 | 226.0346 | 0 | 840.4562 | 65.94% | 10.4568 | 0 | 10.7525 | 21.51% | 50
4787 | 843 | 894 | 143 | 13.4996 | 32.8 | 424.2966 | 277.4201 | 0 | 235.6203 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 235.6203 | 0 | 1065.7039 | 83.62% | 19.175 | 0 | 30.4698 | 60.94% | 50
4788 | 837 | 961 | 159 | 16.7234 | 32.7 | 421.2767 | 278.4719 | 0 | 234.7817 | 100 | 0.23724 | 24.7628 | 75 | 0 | 0 | 0 | 0 | 0 | 234.7817 | 0 | 1274.5104 | 100% | 18.993 | 0 | 50 | 100% | 50
4789 | 828 | 975 | 168 | 17.5294 | 32.7 | 416.7468 | 0 | 273.0177 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4790 | 784 | 921 | 186 | 15.9175 | 33 | 394.6008 | 0 | 252.5748 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4791 | 660 | 806 | 240 | 14.91 | 33.1 | 332.1895 | 0 | 204.7588 | 0 | 84.1241 | 17.462 | 0 | 66.662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.2
4792 | 493 | 634 | 274 | 14.91 | 32.7 | 248.1355 | 0 | 143.9518 | 0 | 51.2281 | 1.3641 | 0 | 49.8641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.5
4793 | 349 | 446 | 246 | 15.5145 | 31.9 | 175.6578 | 0 | 90.4864 | 0 | 31.5392 | 0 | 0 | 31.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 16.0608 | 33.4875 | 66.98% | 47.6
4794 | 174 | 248 | 178 | 14.3056 | 30.8 | 87.5772 | 0 | 35.1501 | 0 | 14.3177 | 0 | 0 | 14.3177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 7.7835 | 15.57% | 39.3177
4795 | 28 | 81 | 74 | 14.7085 | 29.6 | 14.0929 | 0 | 0 | 0 | 4.2923 | 0 | 0 | 4.2923 | 0 | 0 | 0 | 87.2211 | 33.5365 | 0 | 87.2211 | 1192.3309 | 93.55% | 0 | 7.5712 | 0 | 0% | 45.4
4796 | 0 | 5 | 5 | 12.0892 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8932 | 42.6 | 0 | 108.8932 | 1085.6917 | 85.19% | 0 | 0 | 0 | 0% | 42.6
4797 | 0 | 0 | 0 | 11.4848 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4869 | 41 | 0 | 104.4869 | 983.8951 | 77.2% | 0 | 0 | 0 | 0% | 41
4798 | 0 | 0 | 0 | 9.8729 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0393 | 38.5 | 0 | 98.0393 | 889.2142 | 69.77% | 0 | 0 | 0 | 0% | 38.5
4799 | 0 | 0 | 0 | 8.6639 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8512 | 36.4 | 0 | 92.8512 | 800.4104 | 62.8% | 0 | 0 | 0 | 0% | 36.4
4800 | 0 | 0 | 0 | 7.455 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5853 | 35.1 | 0 | 89.5853 | 715.1824 | 56.11% | 0 | 0 | 0 | 0% | 35.1
4801 | 0 | 0 | 0 | 2.8208 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3481 | 34.6 | 0 | 88.3481 | 631.3509 | 49.54% | 0 | 0 | 0 | 0% | 34.6
4802 | 0 | 0 | 0 | 1.4104 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1849 | 34.1 | 0 | 87.1849 | 548.8518 | 43.06% | 0 | 0 | 0 | 0% | 34.1
4803 | 0 | 0 | 0 | 2.0149 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3722 | 34.2 | 0 | 87.3722 | 466.1113 | 36.57% | 0 | 0 | 0 | 0% | 34.2
4804 | 0 | 0 | 0 | 2.4178 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8691 | 34.4 | 0 | 87.8691 | 382.7849 | 30.03% | 0 | 0 | 0 | 0% | 34.4
4805 | 0 | 0 | 0 | 2.2164 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2457 | 36.6 | 0 | 93.2457 | 293.3815 | 23.02% | 0 | 0 | 0 | 0% | 36.6
4806 | 9 | 29 | 28 | 2.0149 | 22.8 | 4.5299 | 0 | 1.7479 | 0 | 1.1102 | 0 | 0 | 1.1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.3815 | 23.02% | 0 | 0 | 0 | 0% | 1.1102
4807 | 103 | 148 | 117 | 1.8134 | 26.7 | 51.8417 | 0 | 26.079 | 0 | 7.537 | 0 | 0 | 7.537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.3815 | 23.02% | 0 | 0 | 0 | 0% | 7.537
4808 | 141 | 290 | 221 | 1.2089 | 29.6 | 70.9678 | 0 | 40.8549 | 0 | 18.9818 | 0 | 0 | 18.9818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.3815 | 23.02% | 0 | 0 | 0 | 0% | 18.9818
4809 | 294 | 509 | 311 | 3.6268 | 31.6 | 147.9753 | 90.8084 | 0 | 66.6741 | 37.0853 | 0 | 0 | 37.0853 | 0 | 0 | 0 | 0 | 0 | 66.6741 | 0 | 356.9975 | 28.01% | 0 | 0 | 0 | 0% | 37.0853
4810 | 511 | 719 | 311 | 9.6714 | 33.3 | 257.1952 | 164.0153 | 0 | 131.938 | 68.1653 | 0 | 11.0826 | 57.0826 | 0 | 0 | 0 | 0 | 0 | 131.938 | 0 | 482.884 | 37.89% | 8.5004 | 0 | 8.742 | 17.48% | 46
4811 | 612 | 840 | 288 | 10.8803 | 34 | 308.0302 | 201.4097 | 0 | 166.3101 | 92.8608 | 0 | 23.4804 | 69.3804 | 0 | 0 | 0 | 0 | 0 | 166.3101 | 0 | 641.5661 | 50.34% | 18.0095 | 0 | 27.2635 | 54.53% | 45.9
4812 | 656 | 915 | 280 | 9.4699 | 33.9 | 330.1762 | 218.2531 | 0 | 182.8099 | 105 | 5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 182.8099 | 0 | 815.9911 | 64.02% | 19.175 | 0 | 46.9837 | 93.97% | 45
4813 | 673 | 933 | 271 | 11.4848 | 33.7 | 338.7326 | 221.9116 | 0 | 185.0675 | 105.8 | 26.9761 | 3.8239 | 75 | 0 | 0 | 0 | 0 | 0 | 185.0675 | 0 | 992.5702 | 77.88% | 2.9329 | 0 | 50 | 100% | 44.2
4814 | 662 | 888 | 263 | 12.0892 | 33.4 | 333.1961 | 213.2736 | 0 | 176.6589 | 105.229 | 30.7145 | 0 | 74.5145 | 0 | 0 | 0 | 0 | 0 | 176.6589 | 0 | 1161.1264 | 91.1% | 0 | 0 | 50 | 100% | 43.8
4815 | 614 | 783 | 257 | 12.6937 | 32.7 | 309.0369 | 190.495 | 0 | 154.96 | 86.0553 | 21.3777 | 0 | 64.6777 | 0 | 0 | 0 | 0 | 0 | 154.96 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.3
4816 | 536 | 633 | 243 | 13.7011 | 31.4 | 269.7781 | 0 | 156.4748 | 0 | 57.25 | 7.025 | 0 | 50.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.2
4817 | 418 | 450 | 212 | 14.1041 | 30.7 | 210.3867 | 0 | 108.2185 | 0 | 32.0991 | 0 | 0 | 32.0991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 11.0009 | 38.6881 | 77.38% | 43.1
4818 | 268 | 258 | 153 | 13.2981 | 30.2 | 134.8891 | 0 | 53.9744 | 0 | 13.9601 | 0 | 0 | 13.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 12.9806 | 25.96% | 38.9601
4819 | 71 | 84 | 68 | 12.4922 | 28.1 | 35.7355 | 0 | 0 | 0 | 3.9022 | 0 | 0 | 3.9022 | 0 | 0 | 0 | 70.0106 | 26.2738 | 0 | 70.0106 | 1210.209 | 94.95% | 0 | 12.624 | 0 | 0% | 42.8
4820 | 1 | 5 | 5 | 11.0818 | 25.5 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.6917 | 40.3 | 0 | 102.6917 | 1110.3833 | 87.12% | 0 | 0 | 0 | 0% | 40.3
4821 | 0 | 0 | 0 | 9.8729 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9598 | 38 | 0 | 96.9598 | 1017.0379 | 79.8% | 0 | 0 | 0 | 0% | 38
4822 | 0 | 0 | 0 | 4.2312 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2153 | 35.7 | 0 | 91.2153 | 930.0567 | 72.97% | 0 | 0 | 0 | 0% | 35.7
4823 | 0 | 0 | 0 | 2.4178 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1811 | 34 | 0 | 87.1811 | 847.6401 | 66.51% | 0 | 0 | 0 | 0% | 34
4824 | 0 | 0 | 0 | 1.8134 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1609 | 32.7 | 0 | 84.1609 | 768.6691 | 60.31% | 0 | 0 | 0 | 0% | 32.7
4825 | 0 | 0 | 0 | 1.8134 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.213 | 31.9 | 0 | 82.213 | 691.8719 | 54.29% | 0 | 0 | 0 | 0% | 31.9
4826 | 0 | 0 | 0 | 2.0149 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1757 | 31.6 | 0 | 81.1757 | 616.1631 | 48.35% | 0 | 0 | 0 | 0% | 31.6
4827 | 0 | 0 | 0 | 2.0149 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.61 | 31.4 | 0 | 80.61 | 541.0559 | 42.45% | 0 | 0 | 0 | 0% | 31.4
4828 | 0 | 0 | 0 | 4.0297 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5446 | 31 | 0 | 79.5446 | 467.0984 | 36.65% | 0 | 0 | 0 | 0% | 31
4829 | 0 | 0 | 0 | 5.2387 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8187 | 32.3 | 0 | 82.8187 | 389.4993 | 30.56% | 0 | 0 | 0 | 0% | 32.3
4830 | 35 | 33 | 28 | 7.2535 | 23.7 | 17.6161 | 0 | 6.7818 | 0 | 1.0233 | 0 | 0 | 1.0233 | 0 | 0 | 0 | 86.7359 | 33.8767 | 0 | 86.7359 | 307.459 | 24.12% | 0 | 0 | 0 | 0% | 34.9
4831 | 274 | 177 | 99 | 6.8506 | 24.6 | 137.909 | 69.3078 | 0 | 44.421 | 6.7595 | 0 | 0 | 6.7595 | 0 | 0 | 0 | 0 | 0 | 44.421 | 0 | 349.2451 | 27.4% | 0 | 0 | 0 | 0% | 6.7595
4832 | 476 | 374 | 151 | 7.2535 | 27.4 | 239.5791 | 137.9219 | 0 | 108.7973 | 23.137 | 0 | 0 | 23.137 | 0 | 0 | 0 | 0 | 0 | 108.7973 | 0 | 451.5888 | 35.43% | 0 | 0 | 0 | 0% | 23.137
4833 | 593 | 567 | 184 | 12.2907 | 29.2 | 298.4672 | 183.1886 | 0 | 148.2917 | 47.2989 | 0 | 3.5494 | 43.7494 | 0 | 0 | 0 | 0 | 0 | 148.2917 | 0 | 591.0843 | 46.38% | 2.7224 | 0 | 2.8002 | 5.6% | 40.2
4834 | 679 | 735 | 199 | 14.91 | 31 | 341.7525 | 217.9594 | 0 | 179.3097 | 79.777 | 0 | 19.1385 | 60.6385 | 0 | 0 | 0 | 0 | 0 | 179.3097 | 0 | 759.7579 | 59.61% | 14.6792 | 0 | 17.8989 | 35.8% | 41.5
4835 | 704 | 853 | 220 | 14.91 | 31.4 | 354.3354 | 231.6965 | 0 | 192.2249 | 102.5091 | 5.0545 | 25 | 72.4545 | 0 | 0 | 0 | 0 | 0 | 192.2249 | 0 | 940.5806 | 73.8% | 19.175 | 0 | 37.6219 | 75.24% | 42.4
4836 | 695 | 926 | 254 | 16.3204 | 32.3 | 349.8056 | 231.2286 | 0 | 191.0423 | 108.2 | 17.5102 | 15.6898 | 75 | 0 | 0 | 0 | 0 | 0 | 191.0423 | 0 | 1120.2908 | 87.9% | 12.0341 | 0 | 50 | 100% | 41.8
4837 | 617 | 909 | 300 | 17.1264 | 32.1 | 310.5468 | 203.4494 | 0 | 164.6681 | 108.9 | 33.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 164.6681 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
4838 | 534 | 892 | 385 | 18.7383 | 31.5 | 268.7715 | 0 | 172.0382 | 0 | 109.0823 | 34.1411 | 0 | 74.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.8
4839 | 619 | 788 | 258 | 18.1338 | 31 | 311.5535 | 0 | 192.0552 | 0 | 91.6559 | 25.578 | 0 | 66.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.5
4840 | 554 | 636 | 233 | 16.5219 | 30.6 | 278.8378 | 0 | 161.6967 | 0 | 61.0318 | 10.1659 | 0 | 50.8659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.7
4841 | 454 | 459 | 201 | 16.9249 | 29.9 | 228.5061 | 0 | 117.366 | 0 | 32.8768 | 0 | 0 | 32.8768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.2232 | 41.5431 | 83.09% | 41.1
4842 | 128 | 173 | 118 | 16.3204 | 28.2 | 64.4246 | 0 | 25.6992 | 0 | 9.813 | 0 | 0 | 9.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.832 | 31.66% | 34.813
4843 | 27 | 71 | 65 | 14.91 | 25.9 | 13.5896 | 0 | 0 | 0 | 3.8656 | 0 | 0 | 3.8656 | 0 | 0 | 0 | 64.8526 | 24.2397 | 0 | 64.8526 | 1215.1367 | 95.34% | 0 | 15.3947 | 0 | 0% | 43.5
4844 | 0 | 6 | 6 | 10.8803 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8783 | 41.3 | 0 | 104.8783 | 1112.4782 | 87.29% | 0 | 0 | 0 | 0% | 41.3
4845 | 0 | 0 | 0 | 11.0818 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4659 | 38.7 | 0 | 98.4659 | 1017.2119 | 79.81% | 0 | 0 | 0 | 0% | 38.7
4846 | 0 | 0 | 0 | 9.2684 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8141 | 36.4 | 0 | 92.8141 | 928.4326 | 72.85% | 0 | 0 | 0 | 0% | 36.4
4847 | 0 | 0 | 0 | 4.6342 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7118 | 34.7 | 0 | 88.7118 | 844.2104 | 66.24% | 0 | 0 | 0 | 0% | 34.7
4848 | 0 | 0 | 0 | 3.0223 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2764 | 33.7 | 0 | 86.2764 | 762.7682 | 59.85% | 0 | 0 | 0 | 0% | 33.7
4849 | 0 | 0 | 0 | 4.8357 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3656 | 33.3 | 0 | 85.3656 | 682.3619 | 53.54% | 0 | 0 | 0 | 0% | 33.3
4850 | 0 | 0 | 0 | 5.4401 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2072 | 33.7 | 0 | 86.2072 | 600.9593 | 47.15% | 0 | 0 | 0 | 0% | 33.7
4851 | 0 | 0 | 0 | 4.8357 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8636 | 36.9 | 0 | 93.8636 | 510.7292 | 40.07% | 0 | 0 | 0 | 0% | 36.9
4852 | 0 | 0 | 0 | 4.6342 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.3326 | 40 | 0 | 101.3326 | 411.6047 | 32.3% | 0 | 0 | 0 | 0% | 40
4853 | 0 | 0 | 0 | 2.6193 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5098 | 40.0479 | 0 | 101.5098 | 312.3227 | 24.51% | 0 | 0 | 0 | 0% | 40.0479
4854 | 51 | 31 | 24 | 2.0149 | 22.4 | 25.6692 | 0 | 9.8577 | 0 | 0.87008 | 0 | 0 | 0.87008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.3227 | 24.51% | 0 | 0 | 0 | 0% | 0.87008
4855 | 369 | 187 | 86 | 4.2312 | 25.6 | 185.7241 | 93.2398 | 0 | 68.5956 | 5.9491 | 0 | 0 | 5.9491 | 0 | 0 | 0 | 0 | 0 | 68.5956 | 0 | 377.6256 | 29.63% | 0 | 0 | 0 | 0% | 5.9491
4856 | 535 | 381 | 135 | 9.4699 | 27.7 | 269.2748 | 155.0156 | 0 | 123.5351 | 23.4969 | 0 | 0 | 23.4969 | 0 | 0 | 0 | 65.3298 | 24.2581 | 123.5351 | 65.3298 | 435.3232 | 34.16% | 0 | 0 | 0 | 0% | 47.755
4857 | 631 | 573 | 172 | 14.1041 | 30.5 | 317.5933 | 194.956 | 0 | 158.2531 | 44.6159 | 0 | 0 | 44.6159 | 0 | 0 | 0 | 0 | 0 | 158.2531 | 0 | 585.5494 | 45.94% | 0 | 0 | 0 | 0% | 44.6159
4858 | 680 | 734 | 204 | 15.5145 | 31.5 | 342.2558 | 218.3005 | 0 | 179.3119 | 72.1937 | 0 | 11.0968 | 61.0968 | 0 | 0 | 0 | 0 | 0 | 179.3119 | 0 | 755.7663 | 59.3% | 8.5113 | 0 | 8.7558 | 17.51% | 50
4859 | 691 | 849 | 233 | 15.313 | 32.5 | 347.7923 | 227.4271 | 0 | 188.0123 | 94.6686 | 0 | 22.3343 | 72.3343 | 0 | 0 | 0 | 0 | 0 | 188.0123 | 0 | 934.2423 | 73.3% | 17.1304 | 0 | 26.3783 | 52.76% | 50
4860 | 723 | 927 | 233 | 15.5145 | 33.6 | 363.8985 | 240.5441 | 0 | 200.1552 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 200.1552 | 0 | 1124.2453 | 88.21% | 19.175 | 0 | 46.1042 | 92.21% | 50
4861 | 734 | 944 | 227 | 16.7234 | 34.2 | 369.435 | 242.0333 | 0 | 200.886 | 100 | 20.0626 | 4.9374 | 75 | 0 | 0 | 0 | 0 | 0 | 200.886 | 0 | 1274.5104 | 100% | 3.787 | 0 | 50 | 100% | 50
4862 | 717 | 900 | 227 | 18.5368 | 34.2 | 360.8786 | 0 | 230.9988 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4863 | 668 | 793 | 225 | 16.119 | 33.7 | 336.216 | 0 | 207.2697 | 0 | 82.7184 | 16.3592 | 0 | 66.3592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4864 | 586 | 640 | 217 | 16.5219 | 32.4 | 294.944 | 0 | 171.0027 | 0 | 52.4467 | 1.2233 | 0 | 51.2233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4865 | 490 | 462 | 187 | 15.313 | 32.1 | 246.6255 | 0 | 126.485 | 0 | 32.9747 | 0 | 0 | 32.9747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 17.0253 | 32.4883 | 64.98% | 50
4866 | 321 | 266 | 144 | 15.716 | 30.3 | 161.5649 | 0 | 64.2468 | 0 | 14.0803 | 0 | 0 | 14.0803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 6.773 | 13.55% | 39.0803
4867 | 93 | 90 | 70 | 13.9026 | 27.9 | 46.8085 | 0 | 0 | 0 | 3.9944 | 0 | 0 | 3.9944 | 0 | 0 | 0 | 96.4371 | 37.52 | 0 | 96.4371 | 1181.8796 | 92.73% | 0 | 6.5856 | 0 | 0% | 48.1
4868 | 0 | 5 | 5 | 11.0818 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.5332 | 44.7 | 0 | 113.5332 | 1069.514 | 83.92% | 0 | 0 | 0 | 0% | 44.7
4869 | 0 | 0 | 0 | 8.6639 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3351 | 42.2 | 0 | 107.3351 | 964.3066 | 75.66% | 0 | 0 | 0 | 0% | 42.2
4870 | 0 | 0 | 0 | 6.8506 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2356 | 39.7 | 0 | 101.2356 | 866.126 | 67.96% | 0 | 0 | 0 | 0% | 39.7
4871 | 0 | 0 | 0 | 2.4178 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7356 | 37.9 | 0 | 96.7356 | 773.0097 | 60.65% | 0 | 0 | 0 | 0% | 37.9
4872 | 0 | 0 | 0 | 2.4178 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1643 | 36.9 | 0 | 94.1643 | 682.736 | 53.57% | 0 | 0 | 0 | 0% | 36.9
4873 | 0 | 0 | 0 | 4.0297 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6258 | 36.3 | 0 | 92.6258 | 594.1464 | 46.62% | 0 | 0 | 0 | 0% | 36.3
4874 | 0 | 0 | 0 | 6.0446 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5079 | 36.7 | 0 | 93.5079 | 504.507 | 39.58% | 0 | 0 | 0 | 0% | 36.7
4875 | 0 | 0 | 0 | 4.8357 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.075 | 39 | 0 | 99.075 | 408.2998 | 32.04% | 0 | 0 | 0 | 0% | 39
4876 | 0 | 0 | 0 | 5.4401 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.0723 | 41.4623 | 0 | 105.0723 | 305.0577 | 23.94% | 0 | 0 | 0 | 0% | 41.4623
4877 | 0 | 0 | 0 | 5.0372 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305.0577 | 23.94% | 0 | 0 | 0 | 0% | 0
4878 | 58 | 34 | 27 | 4.6342 | 22.7 | 29.1924 | 0 | 11.1814 | 0 | 0.94924 | 0 | 0 | 0.94924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305.0577 | 23.94% | 0 | 0 | 0 | 0% | 0.94924
4879 | 324 | 181 | 92 | 5.2387 | 25.2 | 163.0748 | 81.7765 | 0 | 57.233 | 6.2937 | 0 | 0 | 6.2937 | 0 | 0 | 0 | 0 | 0 | 57.233 | 0 | 360.2377 | 28.26% | 0 | 0 | 0 | 0% | 6.2937
4880 | 536 | 381 | 135 | 5.4401 | 29 | 269.7781 | 155.3011 | 0 | 126.1728 | 23.3096 | 0 | 0 | 23.3096 | 0 | 0 | 0 | 0 | 0 | 126.1728 | 0 | 481.8846 | 37.81% | 0 | 0 | 0 | 0% | 23.3096
4881 | 661 | 579 | 162 | 8.261 | 31.7 | 332.6928 | 204.2539 | 0 | 170.4541 | 44.7561 | 0 | 0 | 44.7561 | 0 | 0 | 0 | 0 | 0 | 170.4541 | 0 | 646.2245 | 50.7% | 0 | 0 | 0 | 0% | 44.7561
4882 | 731 | 749 | 179 | 10.6788 | 33.3 | 367.925 | 234.6934 | 0 | 197.5463 | 73.161 | 0 | 11.5805 | 61.5805 | 0 | 0 | 0 | 0 | 0 | 197.5463 | 0 | 836.6847 | 65.65% | 8.8822 | 0 | 9.1387 | 18.28% | 50
4883 | 772 | 875 | 188 | 11.0818 | 34.6 | 388.561 | 254.0963 | 0 | 215.2486 | 96.7206 | 0 | 23.3603 | 73.3603 | 0 | 0 | 0 | 0 | 0 | 215.2486 | 0 | 1044.2123 | 81.93% | 17.9174 | 0 | 27.5735 | 55.15% | 50
4884 | 783 | 947 | 199 | 13.9026 | 35.3 | 394.0975 | 260.5057 | 0 | 219.602 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 219.602 | 0 | 1255.9371 | 98.54% | 19.175 | 0 | 47.3023 | 94.6% | 50
4885 | 799 | 968 | 192 | 16.119 | 35.6 | 402.1506 | 0 | 263.4725 | 0 | 100 | 21.5815 | 3.4185 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.9371 | 98.54% | 2.622 | 0 | 50 | 100% | 50
4886 | 790 | 936 | 198 | 15.716 | 35.9 | 397.6207 | 0 | 254.5229 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.9371 | 98.54% | 0 | 0 | 50 | 100% | 50
4887 | 699 | 819 | 223 | 15.1115 | 35.9 | 351.8189 | 0 | 216.9023 | 0 | 85.6291 | 17.8146 | 0 | 67.8146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.9371 | 98.54% | 0 | 0 | 50 | 100% | 50
4888 | 160 | 417 | 298 | 14.3056 | 35 | 80.5308 | 0 | 46.6811 | 0 | 31.546 | 0 | 0 | 31.546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.9371 | 98.54% | 0 | 18.454 | 31.016 | 62.03% | 50
4889 | 149 | 280 | 203 | 12.6937 | 34.1 | 74.9943 | 0 | 38.4043 | 0 | 20.3742 | 0 | 0 | 20.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.9371 | 98.54% | 0 | 25 | 5.297 | 10.59% | 45.3742
4890 | 461 | 288 | 116 | 13.2981 | 34 | 232.0293 | 0 | 91.9742 | 0 | 13.7911 | 0 | 0 | 13.7911 | 0 | 0 | 0 | 81.8579 | 30.759 | 0 | 81.8579 | 1180.0223 | 92.59% | 0 | 5.15 | 0 | 0% | 49.7
4891 | 183 | 99 | 62 | 12.2907 | 32.1 | 92.1071 | 0 | 0 | 0 | 3.3846 | 0 | 0 | 3.3846 | 0 | 0 | 0 | 115.4502 | 44.8154 | 0 | 115.4502 | 1066.0687 | 83.65% | 0 | 0 | 0 | 0% | 48.2
4892 | 2 | 5 | 5 | 9.2684 | 28.6 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.6246 | 44.5 | 0 | 113.6246 | 954.0238 | 74.85% | 0 | 0 | 0 | 0% | 44.5
4893 | 0 | 0 | 0 | 8.0595 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0094 | 42.4 | 0 | 108.0094 | 848.206 | 66.55% | 0 | 0 | 0 | 0% | 42.4
4894 | 0 | 0 | 0 | 5.2387 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4981 | 39.8 | 0 | 101.4981 | 749.6986 | 58.82% | 0 | 0 | 0 | 0% | 39.8
4895 | 0 | 0 | 0 | 2.8208 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2227 | 38.1 | 0 | 97.2227 | 656.0046 | 51.47% | 0 | 0 | 0 | 0% | 38.1
4896 | 0 | 0 | 0 | 2.0149 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.652 | 37.1 | 0 | 94.652 | 565.1568 | 44.34% | 0 | 0 | 0 | 0% | 37.1
4897 | 0 | 0 | 0 | 3.2238 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.339 | 36.6 | 0 | 93.339 | 475.7411 | 37.33% | 0 | 0 | 0 | 0% | 36.6
4898 | 0 | 0 | 0 | 3.8283 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6577 | 36.7 | 0 | 93.6577 | 385.9635 | 30.28% | 0 | 0 | 0 | 0% | 36.7
4899 | 0 | 0 | 0 | 4.8357 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385.9635 | 30.28% | 0 | 0 | 0 | 0% | 0
4900 | 0 | 0 | 0 | 4.8357 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385.9635 | 30.28% | 0 | 0 | 0 | 0% | 0
4901 | 0 | 0 | 0 | 5.0372 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385.9635 | 30.28% | 0 | 0 | 0 | 0% | 0
4902 | 55 | 30 | 23 | 4.6342 | 23.8 | 27.6825 | 0 | 10.5736 | 0 | 0.69586 | 0 | 0 | 0.69586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385.9635 | 30.28% | 0 | 0 | 0 | 0% | 0.69586
4903 | 412 | 188 | 77 | 5.2387 | 26.5 | 207.3668 | 103.8616 | 0 | 77.9791 | 5.4115 | 0 | 0 | 5.4115 | 0 | 0 | 0 | 0 | 0 | 77.9791 | 0 | 461.1286 | 36.18% | 0 | 0 | 0 | 0% | 5.4115
4904 | 618 | 391 | 110 | 7.052 | 29.6 | 311.0501 | 179.0314 | 0 | 147.506 | 23.7525 | 0 | 0 | 23.7525 | 0 | 0 | 0 | 70.3093 | 26.2475 | 147.506 | 70.3093 | 538.6099 | 42.26% | 0 | 0 | 0 | 0% | 50
4905 | 738 | 592 | 128 | 9.4699 | 32.3 | 371.4482 | 228.0788 | 0 | 191.9818 | 45.8567 | 0 | 0 | 45.8567 | 0 | 0 | 0 | 0 | 0 | 191.9818 | 0 | 722.8734 | 56.72% | 0 | 0 | 0 | 0% | 45.8567
4906 | 790 | 759 | 144 | 10.0743 | 33.3 | 397.6207 | 253.6564 | 0 | 215.3896 | 74.8161 | 0 | 12.4081 | 62.4081 | 0 | 0 | 0 | 0 | 0 | 215.3896 | 0 | 929.6035 | 72.94% | 9.517 | 0 | 9.7932 | 19.59% | 50
4907 | 814 | 882 | 159 | 12.0892 | 34 | 409.7004 | 267.9302 | 0 | 227.5538 | 99.376 | 0 | 24.688 | 74.688 | 0 | 0 | 0 | 0 | 0 | 227.5538 | 0 | 1148.0088 | 90.07% | 18.9357 | 0 | 29.2786 | 58.56% | 50
4908 | 830 | 955 | 163 | 12.6937 | 34.6 | 417.7534 | 276.1419 | 0 | 234.9421 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 234.9421 | 0 | 1274.5104 | 100% | 19.175 | 0 | 49.0102 | 98.02% | 50
4909 | 849 | 976 | 155 | 13.7011 | 35 | 427.3165 | 0 | 279.9673 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.0102 | 98.02% | 50
4910 | 849 | 934 | 145 | 13.2981 | 35.1 | 427.3165 | 0 | 273.5389 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.0102 | 98.02% | 50
4911 | 822 | 833 | 139 | 11.6862 | 35.2 | 413.7269 | 0 | 255.0882 | 0 | 88.8253 | 19.4126 | 0 | 69.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.0102 | 98.02% | 50
4912 | 780 | 686 | 129 | 12.8952 | 34.8 | 392.5876 | 0 | 227.5279 | 0 | 60.2111 | 5.1056 | 0 | 55.1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.0102 | 98.02% | 50
4913 | 712 | 504 | 111 | 12.0892 | 34.5 | 358.362 | 0 | 183.2401 | 0 | 35.5901 | 0 | 0 | 35.5901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 14.4099 | 34.1843 | 68.37% | 50
4914 | 568 | 298 | 88 | 12.2907 | 33.3 | 285.8843 | 0 | 112.9573 | 0 | 13.3681 | 0 | 0 | 13.3681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 8.4617 | 16.92% | 38.3681
4915 | 262 | 100 | 50 | 9.0669 | 31.5 | 131.8692 | 0 | 0 | 0 | 2.5543 | 0 | 0 | 2.5543 | 0 | 0 | 0 | 97.4411 | 37.521 | 0 | 97.4411 | 1180.8868 | 92.65% | 0 | 8.2248 | 0 | 0% | 48.3
4916 | 4 | 4 | 4 | 7.455 | 28.8 | 2.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.6459 | 44.9 | 0 | 114.6459 | 1067.6779 | 83.77% | 0 | 0 | 0 | 0% | 44.9
4917 | 0 | 0 | 0 | 5.8431 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5753 | 42.6 | 0 | 108.5753 | 961.2785 | 75.42% | 0 | 0 | 0 | 0% | 42.6
4918 | 0 | 0 | 0 | 3.0223 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8424 | 39.9 | 0 | 101.8424 | 862.3954 | 67.66% | 0 | 0 | 0 | 0% | 39.9
4919 | 0 | 0 | 0 | 4.4327 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.724 | 37.8 | 0 | 96.724 | 769.3017 | 60.36% | 0 | 0 | 0 | 0% | 37.8
4920 | 0 | 0 | 0 | 6.2461 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2958 | 36.8 | 0 | 94.2958 | 678.9131 | 53.27% | 0 | 0 | 0 | 0% | 36.8
4921 | 0 | 0 | 0 | 4.0297 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3225 | 36.1 | 0 | 92.3225 | 590.6613 | 46.34% | 0 | 0 | 0 | 0% | 36.1
4922 | 0 | 0 | 0 | 5.0372 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6556 | 36.2 | 0 | 92.6556 | 502.0381 | 39.39% | 0 | 0 | 0 | 0% | 36.2
4923 | 0 | 0 | 0 | 4.6342 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4077 | 38.2 | 0 | 97.4077 | 408.0616 | 32.02% | 0 | 0 | 0 | 0% | 38.2
4924 | 0 | 0 | 0 | 4.2312 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7101 | 40.4 | 0 | 102.7101 | 307.7887 | 24.15% | 0 | 0 | 0 | 0% | 40.4
4925 | 0 | 0 | 0 | 5.4401 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307.7887 | 24.15% | 0 | 0 | 0 | 0% | 0
4926 | 57 | 29 | 23 | 5.8431 | 24.4 | 28.6891 | 0 | 10.9259 | 0 | 0.69365 | 0 | 0 | 0.69365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307.7887 | 24.15% | 0 | 0 | 0 | 0% | 0.69365
4927 | 409 | 186 | 76 | 2.8208 | 27.2 | 205.8568 | 102.9721 | 0 | 78.0048 | 5.3191 | 0 | 0 | 5.3191 | 0 | 0 | 0 | 0 | 0 | 78.0048 | 0 | 383.0017 | 30.05% | 0 | 0 | 0 | 0% | 5.3191
4928 | 634 | 391 | 105 | 4.0297 | 30.1 | 319.1032 | 183.5799 | 0 | 153.2163 | 23.621 | 0 | 0 | 23.621 | 0 | 0 | 0 | 70.7536 | 26.379 | 153.2163 | 70.7536 | 465.6186 | 36.53% | 0 | 0 | 0 | 0% | 50
4929 | 766 | 594 | 114 | 7.6565 | 31.8 | 385.5411 | 236.7636 | 0 | 201.1528 | 46.1016 | 0 | 0 | 46.1016 | 0 | 0 | 0 | 0 | 0 | 201.1528 | 0 | 658.8073 | 51.69% | 0 | 0 | 0 | 0% | 46.1016
4930 | 844 | 770 | 117 | 9.6714 | 32.6 | 424.7999 | 271.0152 | 0 | 231.8209 | 77.0099 | 0 | 13.5049 | 63.5049 | 0 | 0 | 0 | 0 | 0 | 231.8209 | 0 | 881.45 | 69.16% | 10.3583 | 0 | 10.6605 | 21.32% | 50
4931 | 890 | 902 | 116 | 10.2758 | 33.5 | 447.9525 | 292.9564 | 0 | 252.2507 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 252.2507 | 0 | 1123.7136 | 88.17% | 19.175 | 0 | 30.3949 | 60.79% | 50
4932 | 903 | 973 | 117 | 9.8729 | 34.3 | 454.4956 | 300.4278 | 0 | 259.4097 | 100 | 0.16386 | 24.8361 | 75 | 0 | 0 | 0 | 0 | 0 | 259.4097 | 0 | 1274.5104 | 100% | 19.0493 | 0 | 50 | 100% | 50
4933 | 902 | 985 | 116 | 10.2758 | 34.8 | 453.9923 | 0 | 297.4533 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4934 | 898 | 943 | 112 | 11.0818 | 34.9 | 451.979 | 0 | 289.3355 | 0 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4935 | 865 | 838 | 112 | 12.0892 | 35 | 435.3695 | 0 | 268.454 | 0 | 90.0384 | 20.0192 | 0 | 70.0192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
4936 | 780 | 677 | 122 | 10.4773 | 34.1 | 392.5876 | 0 | 227.4864 | 0 | 59.495 | 4.9475 | 0 | 54.5475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.6
4937 | 685 | 488 | 111 | 8.4625 | 33.6 | 344.7724 | 0 | 176.0244 | 0 | 34.5791 | 0 | 0 | 34.5791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 13.7209 | 35.8809 | 71.76% | 48.3
4938 | 517 | 283 | 93 | 7.6565 | 32.8 | 260.2151 | 0 | 102.4803 | 0 | 13.1041 | 0 | 0 | 13.1041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.1547 | 20.31% | 38.1041
4939 | 248 | 98 | 52 | 8.0595 | 30.8 | 124.8227 | 0 | 0 | 0 | 2.6888 | 0 | 0 | 2.6888 | 0 | 0 | 0 | 88.7727 | 34.0424 | 0 | 88.7727 | 1190.6085 | 93.42% | 0 | 9.8688 | 0 | 0% | 46.6
4940 | 5 | 5 | 5 | 6.2461 | 28.4 | 2.5166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3824 | 43.6 | 0 | 111.3824 | 1081.1413 | 84.83% | 0 | 0 | 0 | 0% | 43.6
4941 | 0 | 0 | 0 | 4.6342 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6689 | 41.4 | 0 | 105.6689 | 978.0522 | 76.74% | 0 | 0 | 0 | 0% | 41.4
4942 | 0 | 0 | 0 | 2.6193 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1455 | 38.8 | 0 | 99.1455 | 882.2624 | 69.22% | 0 | 0 | 0 | 0% | 38.8
4943 | 0 | 0 | 0 | 3.2238 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6899 | 37.1 | 0 | 94.6899 | 791.4193 | 62.1% | 0 | 0 | 0 | 0% | 37.1
4944 | 0 | 0 | 0 | 3.2238 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9902 | 36.1 | 0 | 91.9902 | 703.4949 | 55.2% | 0 | 0 | 0 | 0% | 36.1
4945 | 0 | 0 | 0 | 2.0149 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5893 | 35.6 | 0 | 90.5893 | 616.9557 | 48.41% | 0 | 0 | 0 | 0% | 35.6
4946 | 0 | 0 | 0 | 1.4104 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7606 | 35.7 | 0 | 90.7606 | 530.1218 | 41.59% | 0 | 0 | 0 | 0% | 35.7
4947 | 0 | 0 | 0 | 0.60446 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7195 | 38.2 | 0 | 96.7195 | 436.2055 | 34.23% | 0 | 0 | 0 | 0% | 38.2
4948 | 0 | 0 | 0 | 2.8208 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9597 | 40.8 | 0 | 102.9597 | 334.8349 | 26.27% | 0 | 0 | 0 | 0% | 40.8
4949 | 0 | 0 | 0 | 1.6119 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4374 | 35.2604 | 0 | 89.4374 | 249.1692 | 19.55% | 0 | 0 | 0 | 0% | 35.2604
4950 | 144 | 35 | 18 | 1.0074 | 20.4 | 72.4777 | 0 | 27.5167 | 0 | 0.43236 | 0 | 0 | 0.43236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249.1692 | 19.55% | 0 | 0 | 0 | 0% | 0.43236
4951 | 561 | 200 | 55 | 1.4104 | 24.3 | 282.3611 | 141.0464 | 0 | 114.2336 | 4.2698 | 0 | 0 | 4.2698 | 0 | 0 | 0 | 0 | 0 | 114.2336 | 0 | 358.8296 | 28.15% | 0 | 0 | 0 | 0% | 4.2698
4952 | 731 | 407 | 81 | 2.6193 | 27.4 | 367.925 | 211.5592 | 0 | 179.8203 | 24.5164 | 0 | 0 | 24.5164 | 0 | 0 | 0 | 67.793 | 25.3836 | 179.8203 | 67.793 | 469.1797 | 36.81% | 0 | 0 | 0 | 0% | 49.9
4953 | 778 | 616 | 134 | 7.455 | 29.6 | 391.5809 | 240.5035 | 0 | 204.6679 | 48.5889 | 0 | 0 | 48.5889 | 0 | 0 | 0 | 0 | 0 | 204.6679 | 0 | 664.9542 | 52.17% | 0 | 0 | 0 | 0% | 48.5889
4954 | 446 | 663 | 313 | 8.0595 | 30.8 | 224.4796 | 143.224 | 0 | 113.4564 | 57.7244 | 0 | 3.8622 | 53.8622 | 0 | 0 | 0 | 0 | 0 | 113.4564 | 0 | 773.4806 | 60.69% | 2.9623 | 0 | 3.0492 | 6.098% | 50
4955 | 353 | 704 | 391 | 8.261 | 31.8 | 177.671 | 116.1991 | 0 | 88.1878 | 65.7534 | 0 | 7.8767 | 57.8767 | 0 | 0 | 0 | 0 | 0 | 88.1878 | 0 | 857.8364 | 67.31% | 6.0414 | 0 | 9.2678 | 18.54% | 50
4956 | 326 | 678 | 362 | 6.4476 | 32.9 | 164.0815 | 108.4595 | 0 | 81.7342 | 61.908 | 0 | 6.204 | 55.704 | 0 | 0 | 0 | 0 | 0 | 81.7342 | 0 | 936.0191 | 73.44% | 4.7585 | 0 | 14.1658 | 28.33% | 49.5
4957 | 779 | 927 | 176 | 5.8431 | 34.4 | 392.0842 | 256.9 | 0 | 220.8869 | 101 | 1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 220.8869 | 0 | 1147.3078 | 90.02% | 19.175 | 0 | 33.9031 | 67.81% | 49
4958 | 875 | 937 | 128 | 8.261 | 35.5 | 440.4027 | 281.9354 | 0 | 243.0028 | 101.5 | 6.1112 | 20.3888 | 75 | 0 | 0 | 0 | 0 | 0 | 243.0028 | 0 | 1274.5104 | 100% | 15.6382 | 0 | 50 | 100% | 48.5
4959 | 850 | 839 | 127 | 8.8654 | 36.1 | 427.8198 | 0 | 263.8224 | 0 | 91.1718 | 21.8359 | 0 | 69.3359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.5
4960 | 805 | 691 | 120 | 9.8729 | 35.8 | 405.1705 | 0 | 234.7362 | 0 | 64.396 | 8.948 | 0 | 55.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.5
4961 | 719 | 516 | 121 | 11.2833 | 35.7 | 361.8852 | 0 | 184.4799 | 0 | 36.5733 | 0 | 0 | 36.5733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.9267 | 40.813 | 81.63% | 45.5
4962 | 240 | 199 | 101 | 7.455 | 35.1 | 120.7962 | 0 | 47.4163 | 0 | 9.8121 | 0 | 0 | 9.8121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.0833 | 30.17% | 34.8121
4963 | 340 | 135 | 75 | 12.0892 | 33.7 | 171.1279 | 0 | 0 | 0 | 4.1088 | 0 | 0 | 4.1088 | 0 | 0 | 0 | 67.6201 | 24.5351 | 0 | 67.6201 | 1212.5893 | 95.14% | 0 | 14.656 | 0 | 0% | 43.3
4964 | 8 | 6 | 5 | 9.4699 | 32 | 4.0265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.0961 | 40.6 | 0 | 105.0961 | 1110.3811 | 87.12% | 0 | 0 | 0 | 0% | 40.6
4965 | 0 | 0 | 0 | 5.6416 | 30.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.7604 | 39.4 | 0 | 101.7604 | 1011.857 | 79.39% | 0 | 0 | 0 | 0% | 39.4
4966 | 0 | 0 | 0 | 8.261 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3425 | 37.3 | 0 | 96.3425 | 919.3917 | 72.14% | 0 | 0 | 0 | 0% | 37.3
4967 | 0 | 0 | 0 | 6.4476 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0162 | 35.3 | 0 | 91.0162 | 832.7562 | 65.34% | 0 | 0 | 0 | 0% | 35.3
4968 | 0 | 0 | 0 | 4.4327 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6795 | 34.4 | 0 | 88.6795 | 748.7357 | 58.75% | 0 | 0 | 0 | 0% | 34.4
4969 | 0 | 0 | 0 | 3.8283 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5577 | 33.6 | 0 | 86.5577 | 667.0968 | 52.34% | 0 | 0 | 0 | 0% | 33.6
4970 | 0 | 0 | 0 | 2.6193 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9381 | 33.1 | 0 | 84.9381 | 587.2061 | 46.07% | 0 | 0 | 0 | 0% | 33.1
4971 | 0 | 0 | 0 | 4.2312 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8127 | 33.5 | 0 | 85.8127 | 506.2895 | 39.72% | 0 | 0 | 0 | 0% | 33.5
4972 | 0 | 0 | 0 | 4.2312 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2072 | 33.7 | 0 | 86.2072 | 424.8897 | 33.34% | 0 | 0 | 0 | 0% | 33.7
4973 | 0 | 0 | 0 | 2.6193 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5691 | 35.6 | 0 | 90.5691 | 338.3111 | 26.54% | 0 | 0 | 0 | 0% | 35.6
4974 | 161 | 32 | 15 | 4.2312 | 21.8 | 81.0341 | 0 | 30.665 | 0 | 0.28463 | 0 | 0 | 0.28463 | 0 | 0 | 0 | 96.9091 | 38.2154 | 0 | 96.9091 | 244.3175 | 19.17% | 0 | 0 | 0 | 0% | 38.5
4975 | 613 | 199 | 41 | 2.2164 | 25 | 308.5336 | 153.8956 | 0 | 125.9915 | 3.5516 | 0 | 0 | 3.5516 | 0 | 0 | 0 | 0 | 0 | 125.9915 | 0 | 363.9113 | 28.55% | 0 | 0 | 0 | 0% | 3.5516
4976 | 786 | 406 | 55 | 2.0149 | 27.9 | 395.6075 | 227.3521 | 0 | 194.7793 | 23.8855 | 0 | 0 | 23.8855 | 0 | 0 | 0 | 0 | 0 | 194.7793 | 0 | 548.8002 | 43.06% | 0 | 0 | 0 | 0% | 23.8855
4977 | 864 | 602 | 65 | 3.0223 | 29.9 | 434.8662 | 267.1214 | 0 | 231.4938 | 50.9686 | 0 | 4.5843 | 46.3843 | 0 | 0 | 0 | 0 | 0 | 231.4938 | 0 | 768.5392 | 60.3% | 3.5161 | 0 | 3.6198 | 7.24% | 41.8
4978 | 905 | 770 | 73 | 5.2387 | 31.5 | 455.5022 | 290.6407 | 0 | 252.9375 | 84.0998 | 0 | 20.8499 | 63.2499 | 0 | 0 | 0 | 0 | 0 | 252.9375 | 0 | 1008.633 | 79.14% | 15.9919 | 0 | 20.0829 | 40.17% | 42.4
4979 | 927 | 895 | 79 | 9.2684 | 32.6 | 466.5752 | 305.1563 | 0 | 264.1023 | 108.1 | 8.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 264.1023 | 0 | 1259.3248 | 98.81% | 19.175 | 0 | 39.8231 | 79.65% | 41.9
4980 | 931 | 963 | 84 | 8.0595 | 32.7 | 468.5885 | 0 | 309.7399 | 0 | 109.2 | 21.3114 | 12.8886 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.3248 | 98.81% | 9.8855 | 0 | 50 | 100% | 40.8
4981 | 925 | 978 | 90 | 5.0372 | 32.5 | 465.5686 | 0 | 305.0595 | 0 | 110.1 | 35.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.3248 | 98.81% | 0 | 0 | 50 | 100% | 39.9
4982 | 920 | 934 | 84 | 7.6565 | 33.9 | 463.052 | 0 | 296.4475 | 0 | 110.6 | 35.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.3248 | 98.81% | 0 | 0 | 50 | 100% | 39.4
4983 | 882 | 828 | 87 | 17.9323 | 34.7 | 443.9259 | 0 | 273.7816 | 0 | 101.3622 | 31.1811 | 0 | 70.1811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.3248 | 98.81% | 0 | 0 | 50 | 100% | 39
4984 | 817 | 679 | 97 | 12.6937 | 35.5 | 411.2103 | 0 | 238.1946 | 0 | 69.896 | 15.348 | 0 | 54.548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.3248 | 98.81% | 0 | 0 | 50 | 100% | 39.2
4985 | 770 | 504 | 83 | 8.6639 | 34.2 | 387.5544 | 0 | 197.2626 | 0 | 35.7288 | 0 | 0 | 35.7288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.3248 | 98.81% | 0 | 3.5712 | 46.3241 | 92.65% | 39.3
4986 | 663 | 309 | 69 | 12.2907 | 32.5 | 333.6994 | 0 | 130.5513 | 0 | 13.2709 | 0 | 0 | 13.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.3248 | 98.81% | 0 | 25 | 20.591 | 41.18% | 38.2709
4987 | 430 | 116 | 41 | 10.0743 | 30.4 | 216.4265 | 0 | 0 | 0 | 2.0678 | 0 | 0 | 2.0678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.3248 | 98.81% | 0 | 20.0046 | 0 | 0% | 22.0724
4988 | 7 | 4 | 4 | 7.455 | 29 | 3.5232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9248 | 37.2 | 0 | 95.9248 | 1167.2952 | 91.59% | 0 | 0 | 0 | 0% | 37.2
4989 | 0 | 0 | 0 | 8.261 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5991 | 35.1 | 0 | 90.5991 | 1081.1264 | 84.83% | 0 | 0 | 0 | 0% | 35.1
4990 | 0 | 0 | 0 | 8.4625 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8559 | 33.2 | 0 | 85.8559 | 1000.3501 | 78.49% | 0 | 0 | 0 | 0% | 33.2
4991 | 0 | 0 | 0 | 5.6416 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5707 | 31.5 | 0 | 81.5707 | 924.3494 | 72.53% | 0 | 0 | 0 | 0% | 31.5
4992 | 0 | 0 | 0 | 3.8283 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1766 | 30.6 | 0 | 79.1766 | 850.951 | 66.77% | 0 | 0 | 0 | 0% | 30.6
4993 | 0 | 0 | 0 | 2.6193 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4465 | 30 | 0 | 77.4465 | 779.3932 | 61.15% | 0 | 0 | 0 | 0% | 30
4994 | 0 | 0 | 0 | 3.0223 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.4758 | 29.6 | 0 | 76.4758 | 708.7612 | 55.61% | 0 | 0 | 0 | 0% | 29.6
4995 | 0 | 0 | 0 | 3.4253 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6487 | 29.7 | 0 | 76.6487 | 637.9487 | 50.05% | 0 | 0 | 0 | 0% | 29.7
4996 | 0 | 0 | 0 | 3.2238 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3507 | 29.2 | 0 | 75.3507 | 568.3723 | 44.6% | 0 | 0 | 0 | 0% | 29.2
4997 | 0 | 0 | 0 | 4.2312 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2711 | 30.5 | 0 | 78.2711 | 495.7976 | 38.9% | 0 | 0 | 0 | 0% | 30.5
4998 | 136 | 30 | 16 | 3.8283 | 22.7 | 68.4512 | 0 | 25.8147 | 0 | 0.33573 | 0 | 0 | 0.33573 | 0 | 0 | 0 | 82.9238 | 32.3643 | 0 | 82.9238 | 418.0604 | 32.8% | 0 | 0 | 0 | 0% | 32.7
4999 | 563 | 194 | 48 | 4.0297 | 25.1 | 283.3677 | 141.1251 | 0 | 113.4462 | 3.785 | 0 | 0 | 3.785 | 0 | 0 | 0 | 79.8724 | 30.915 | 113.4462 | 79.8724 | 449.6227 | 35.28% | 0 | 0 | 0 | 0% | 34.7
5000 | 747 | 398 | 65 | 4.0297 | 26.5 | 375.9781 | 215.9444 | 0 | 183.4318 | 23.9068 | 0 | 0 | 23.9068 | 0 | 0 | 0 | 0 | 0 | 183.4318 | 0 | 620.6331 | 48.7% | 0 | 0 | 0 | 0% | 23.9068
5001 | 843 | 597 | 71 | 7.6565 | 28 | 424.2966 | 260.6595 | 0 | 223.2091 | 57.1858 | 0 | 10.0929 | 47.0929 | 0 | 0 | 0 | 0 | 0 | 223.2091 | 0 | 828.7272 | 65.02% | 7.7413 | 0 | 7.9705 | 15.94% | 37
5002 | 842 | 733 | 85 | 7.858 | 28.7 | 423.7932 | 270.4233 | 0 | 232.2444 | 85.6407 | 0 | 23.9203 | 61.7203 | 0 | 0 | 0 | 0 | 0 | 232.2444 | 0 | 1045.2448 | 82.01% | 18.3469 | 0 | 26.8609 | 53.72% | 37.8
5003 | 850 | 874 | 121 | 8.261 | 29.5 | 427.8198 | 279.8179 | 0 | 240.8712 | 111.0978 | 11.4989 | 25 | 74.5989 | 0 | 0 | 0 | 0 | 0 | 240.8712 | 0 | 1269.8049 | 99.63% | 19.175 | 0 | 46.6039 | 93.21% | 38.1
5004 | 902 | 959 | 106 | 9.0669 | 29.8 | 453.9923 | 0 | 300.0895 | 0 | 112.8 | 33.4997 | 4.3003 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.8049 | 99.63% | 3.2984 | 0 | 50 | 100% | 37.2
5005 | 922 | 980 | 93 | 11.2833 | 30.3 | 464.0586 | 0 | 304.0825 | 0 | 113.5 | 38.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.8049 | 99.63% | 0 | 0 | 50 | 100% | 36.5
5006 | 907 | 933 | 93 | 10.4773 | 30.2 | 456.5089 | 0 | 292.2726 | 0 | 113.8 | 38.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.8049 | 99.63% | 0 | 0 | 50 | 100% | 36.2
5007 | 886 | 831 | 89 | 10.2758 | 30.3 | 445.9392 | 0 | 275.0527 | 0 | 105.6737 | 34.8369 | 0 | 70.8369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.8049 | 99.63% | 0 | 0 | 50 | 100% | 36
5008 | 851 | 684 | 81 | 9.8729 | 30.1 | 428.3231 | 0 | 248.0662 | 0 | 75.7618 | 19.7309 | 0 | 56.0309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.8049 | 99.63% | 0 | 0 | 50 | 100% | 36.3
5009 | 788 | 501 | 72 | 9.2684 | 29.8 | 396.6141 | 0 | 201.5627 | 0 | 36.2252 | 0 | 0 | 36.2252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.8049 | 99.63% | 0 | 0 | 50 | 100% | 36.2252
5010 | 664 | 298 | 59 | 7.2535 | 29.4 | 334.2027 | 0 | 130.308 | 0 | 12.8335 | 0 | 0 | 12.8335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.8049 | 99.63% | 0 | 25 | 24.2633 | 48.53% | 37.8335
5011 | 379 | 103 | 35 | 6.8506 | 28.2 | 190.7573 | 0 | 0 | 0 | 1.6717 | 0 | 0 | 1.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.8049 | 99.63% | 0 | 23.5688 | 0 | 0% | 25.2405
5012 | 3 | 3 | 3 | 3.6268 | 26.6 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.107 | 37.9 | 0 | 97.107 | 1176.3374 | 92.3% | 0 | 0 | 0 | 0% | 37.9
5013 | 0 | 0 | 0 | 3.2238 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9962 | 35.5 | 0 | 90.9962 | 1089.6203 | 85.49% | 0 | 0 | 0 | 0% | 35.5
5014 | 0 | 0 | 0 | 5.8431 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.572 | 33.4 | 0 | 85.572 | 1008.9932 | 79.17% | 0 | 0 | 0 | 0% | 33.4
5015 | 0 | 0 | 0 | 3.8283 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.77 | 31.9 | 0 | 81.77 | 932.6079 | 73.17% | 0 | 0 | 0 | 0% | 31.9
5016 | 0 | 0 | 0 | 1.6119 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0611 | 31.2 | 0 | 80.0611 | 858.111 | 67.33% | 0 | 0 | 0 | 0% | 31.2
5017 | 0 | 0 | 0 | 1.4104 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4407 | 31 | 0 | 79.4407 | 784.2661 | 61.53% | 0 | 0 | 0 | 0% | 31
5018 | 0 | 0 | 0 | 1.2089 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0372 | 31.7 | 0 | 81.0372 | 708.6208 | 55.6% | 0 | 0 | 0 | 0% | 31.7
5019 | 0 | 0 | 0 | 0.80595 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.992 | 34.6 | 0 | 87.992 | 624.8735 | 49.03% | 0 | 0 | 0 | 0% | 34.6
5020 | 0 | 0 | 0 | 1.4104 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8955 | 37.5 | 0 | 94.8955 | 532.9161 | 41.81% | 0 | 0 | 0 | 0% | 37.5
5021 | 0 | 0 | 0 | 1.6119 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5454 | 40.7 | 0 | 102.5454 | 431.792 | 33.88% | 0 | 0 | 0 | 0% | 40.7
5022 | 135 | 30 | 16 | 2.2164 | 19.3 | 67.9478 | 0 | 25.5329 | 0 | 0.34969 | 0 | 0 | 0.34969 | 0 | 0 | 0 | 109.3755 | 43.5503 | 0 | 109.3755 | 322.5265 | 25.31% | 0 | 0 | 0 | 0% | 43.9
5023 | 550 | 190 | 51 | 1.4104 | 23.2 | 276.8246 | 137.6423 | 0 | 110.9985 | 4.0163 | 0 | 0 | 4.0163 | 0 | 0 | 0 | 0 | 0 | 110.9985 | 0 | 427.7407 | 33.56% | 0 | 0 | 0 | 0% | 4.0163
5024 | 729 | 393 | 72 | 1.2089 | 26.5 | 366.9184 | 210.6089 | 0 | 179.3932 | 23.8361 | 0 | 0 | 23.8361 | 0 | 0 | 0 | 62.7574 | 23.2639 | 179.3932 | 62.7574 | 540.3715 | 42.4% | 0 | 0 | 0 | 0% | 47.1
5025 | 812 | 589 | 87 | 3.4253 | 28 | 408.6937 | 251.1023 | 0 | 216.4033 | 46.2763 | 0 | 0 | 46.2763 | 0 | 0 | 0 | 0 | 0 | 216.4033 | 0 | 744.8947 | 58.45% | 0 | 0 | 0 | 0% | 46.2763
5026 | 869 | 759 | 95 | 4.8357 | 29.3 | 437.3828 | 279.1084 | 0 | 242.1785 | 77.3462 | 0 | 14.0231 | 63.3231 | 0 | 0 | 0 | 0 | 0 | 242.1785 | 0 | 973.7781 | 76.4% | 10.7557 | 0 | 11.0759 | 22.15% | 49.3
5027 | 902 | 887 | 98 | 5.2387 | 30.6 | 453.9923 | 296.9453 | 0 | 258.8115 | 101.5 | 1.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 258.8115 | 0 | 1218.3813 | 95.6% | 19.175 | 0 | 30.8218 | 61.64% | 48.5
5028 | 918 | 963 | 100 | 9.6714 | 31.2 | 462.0454 | 305.41 | 0 | 264.0679 | 102.7 | 3.4188 | 24.2812 | 75 | 0 | 0 | 0 | 0 | 0 | 264.0679 | 0 | 1274.5104 | 100% | 18.6237 | 0 | 50 | 100% | 47.3
5029 | 908 | 973 | 106 | 10.4773 | 32 | 457.0122 | 0 | 299.4786 | 0 | 102.9 | 27.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.1
5030 | 899 | 929 | 104 | 10.0743 | 32.7 | 452.4823 | 0 | 289.7099 | 0 | 103 | 28 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47
5031 | 873 | 825 | 100 | 10.2758 | 32.8 | 439.3961 | 0 | 271.0484 | 0 | 94.2551 | 23.9776 | 0 | 70.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.3
5032 | 830 | 677 | 94 | 11.2833 | 32.7 | 417.7534 | 0 | 241.9061 | 0 | 65.7172 | 10.1086 | 0 | 55.6086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.5
5033 | 752 | 491 | 85 | 11.4848 | 32 | 378.4947 | 0 | 192.0562 | 0 | 35.754 | 0 | 0 | 35.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.046 | 40.6861 | 81.37% | 44.8
5034 | 617 | 288 | 69 | 9.4699 | 31.1 | 310.5468 | 0 | 120.6677 | 0 | 12.7628 | 0 | 0 | 12.7628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 14.9452 | 29.89% | 37.7628
5035 | 328 | 96 | 39 | 7.052 | 29.5 | 165.0881 | 0 | 0 | 0 | 1.9455 | 0 | 0 | 1.9455 | 0 | 0 | 0 | 72.0635 | 27.0389 | 0 | 72.0635 | 1208.2555 | 94.8% | 0 | 14.5155 | 0 | 0% | 43.5
5036 | 2 | 3 | 3 | 4.0297 | 26.4 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8774 | 40.3 | 0 | 102.8774 | 1108.2853 | 86.96% | 0 | 0 | 0 | 0% | 40.3
5037 | 0 | 0 | 0 | 1.0074 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0181 | 38.4 | 0 | 98.0181 | 1013.7649 | 79.54% | 0 | 0 | 0 | 0% | 38.4
5038 | 0 | 0 | 0 | 1.6119 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3225 | 36.1 | 0 | 92.3225 | 925.5836 | 72.62% | 0 | 0 | 0 | 0% | 36.1
5039 | 0 | 0 | 0 | 2.2164 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5254 | 34.6 | 0 | 88.5254 | 841.6038 | 66.03% | 0 | 0 | 0 | 0% | 34.6
5040 | 0 | 0 | 0 | 3.0223 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9219 | 33.9 | 0 | 86.9219 | 759.4716 | 59.59% | 0 | 0 | 0 | 0% | 33.9
5041 | 0 | 0 | 0 | 3.2238 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8299 | 33.5 | 0 | 85.8299 | 678.5484 | 53.24% | 0 | 0 | 0 | 0% | 33.5
5042 | 0 | 0 | 0 | 2.0149 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4438 | 33.9 | 0 | 86.4438 | 596.8421 | 46.83% | 0 | 0 | 0 | 0% | 33.9
5043 | 0 | 0 | 0 | 1.6119 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5497 | 36.5 | 0 | 92.5497 | 507.7569 | 39.84% | 0 | 0 | 0 | 0% | 36.5
5044 | 0 | 0 | 0 | 2.8208 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5563 | 39 | 0 | 98.5563 | 411.5396 | 32.29% | 0 | 0 | 0 | 0% | 39
5045 | 0 | 0 | 0 | 3.8283 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.1903 | 41.7 | 0 | 105.1903 | 307.6123 | 24.14% | 0 | 0 | 0 | 0% | 41.7
5046 | 104 | 28 | 17 | 2.6193 | 22.1 | 52.345 | 0 | 19.596 | 0 | 0.38149 | 0 | 0 | 0.38149 | 0 | 0 | 0 | 111.5693 | 44.2185 | 0 | 111.5693 | 196.4426 | 15.41% | 0 | 0 | 0 | 0% | 44.6
5047 | 503 | 183 | 56 | 2.8208 | 23.9 | 253.1686 | 125.6647 | 0 | 99.3466 | 4.3083 | 0 | 0 | 4.3083 | 0 | 0 | 0 | 56.6777 | 20.8673 | 99.3466 | 56.6777 | 239.6759 | 18.81% | 0 | 0 | 0 | 0% | 25.1756
5048 | 705 | 388 | 78 | 2.4178 | 28 | 354.8388 | 203.5395 | 0 | 172.4294 | 23.7695 | 0 | 0 | 23.7695 | 0 | 0 | 0 | 63.9953 | 23.6305 | 172.4294 | 63.9953 | 345.3453 | 27.1% | 0 | 0 | 0 | 0% | 47.4
5049 | 790 | 583 | 96 | 3.0223 | 30.9 | 397.6207 | 244.325 | 0 | 210.2762 | 45.5244 | 0 | 0 | 45.5244 | 0 | 0 | 0 | 0 | 0 | 210.2762 | 0 | 545.098 | 42.77% | 0 | 0 | 0 | 0% | 45.5244
5050 | 824 | 749 | 117 | 6.4476 | 32.7 | 414.7335 | 264.6661 | 0 | 227.756 | 75.7791 | 0 | 13.3896 | 62.3896 | 0 | 0 | 0 | 0 | 0 | 227.756 | 0 | 761.4558 | 59.74% | 10.2698 | 0 | 10.5771 | 21.15% | 49
5051 | 841 | 875 | 136 | 9.0669 | 33.7 | 423.2899 | 276.8718 | 0 | 237.7127 | 100.6126 | 1.2563 | 25 | 74.3563 | 0 | 0 | 0 | 0 | 0 | 237.7127 | 0 | 987.272 | 77.46% | 19.175 | 0 | 30.3258 | 60.65% | 48.1
5052 | 866 | 953 | 135 | 9.8729 | 34.5 | 435.8729 | 288.1074 | 0 | 247.8996 | 102.9 | 2.9945 | 24.9055 | 75 | 0 | 0 | 0 | 0 | 0 | 247.8996 | 0 | 1222.7653 | 95.94% | 19.1025 | 0 | 50 | 100% | 47.1
5053 | 859 | 964 | 140 | 11.4848 | 34.7 | 432.3496 | 170.9886 | 112.3425 | 146.3119 | 103.1 | 28.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 146.3119 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.9
5054 | 847 | 919 | 139 | 12.6937 | 34.6 | 426.3098 | 0 | 272.9683 | 0 | 103.4 | 28.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.6
5055 | 826 | 821 | 133 | 12.4922 | 34.2 | 415.7402 | 0 | 256.4878 | 0 | 94.6613 | 24.4806 | 0 | 70.1806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.7
5056 | 761 | 669 | 133 | 13.4996 | 33 | 383.0245 | 0 | 221.7616 | 0 | 65.3519 | 10.1259 | 0 | 55.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.1
5057 | 667 | 489 | 128 | 13.4996 | 31.5 | 335.7127 | 0 | 170.0825 | 0 | 36.0233 | 0 | 0 | 36.0233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.2767 | 41.4769 | 82.95% | 44.3
5058 | 502 | 279 | 100 | 13.2981 | 30.3 | 252.6653 | 0 | 97.834 | 0 | 13.5219 | 0 | 0 | 13.5219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.7323 | 31.46% | 38.5219
5059 | 217 | 90 | 51 | 12.8952 | 28.3 | 109.2199 | 0 | 0 | 0 | 2.6652 | 0 | 0 | 2.6652 | 0 | 0 | 0 | 67.9623 | 25.357 | 0 | 67.9623 | 1212.202 | 95.11% | 0 | 15.2778 | 0 | 0% | 43.3
5060 | 1 | 3 | 3 | 9.8729 | 26.4 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.389 | 40.1 | 0 | 102.389 | 1112.8238 | 87.31% | 0 | 0 | 0 | 0% | 40.1
5061 | 0 | 0 | 0 | 10.8803 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.69 | 38.3 | 0 | 97.69 | 1018.7076 | 79.93% | 0 | 0 | 0 | 0% | 38.3
5062 | 0 | 0 | 0 | 10.8803 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5941 | 35.9 | 0 | 91.5941 | 931.3395 | 73.07% | 0 | 0 | 0 | 0% | 35.9
5063 | 0 | 0 | 0 | 9.6714 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5242 | 34.3 | 0 | 87.5242 | 848.4973 | 66.57% | 0 | 0 | 0 | 0% | 34.3
5064 | 0 | 0 | 0 | 6.6491 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7555 | 33.6 | 0 | 85.7555 | 767.6498 | 60.23% | 0 | 0 | 0 | 0% | 33.6
5065 | 0 | 0 | 0 | 4.6342 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5422 | 33.1 | 0 | 84.5422 | 688.1664 | 53.99% | 0 | 0 | 0 | 0% | 33.1
5066 | 0 | 0 | 0 | 3.4253 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5042 | 33.5 | 0 | 85.5042 | 607.5775 | 47.67% | 0 | 0 | 0 | 0% | 33.5
5067 | 0 | 0 | 0 | 6.4476 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3746 | 35.9 | 0 | 91.3746 | 520.2215 | 40.82% | 0 | 0 | 0 | 0% | 35.9
5068 | 0 | 0 | 0 | 12.0892 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2132 | 38.2 | 0 | 97.2132 | 426.3458 | 33.45% | 0 | 0 | 0 | 0% | 38.2
5069 | 0 | 0 | 0 | 8.6639 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9139 | 40.6 | 0 | 102.9139 | 325.5828 | 25.55% | 0 | 0 | 0 | 0% | 40.6
5070 | 0 | 15 | 15 | 9.8729 | 22.8 | 0 | 0 | 0 | 0 | 0.37471 | 0 | 0 | 0.37471 | 0 | 0 | 0 | 108.5267 | 42.9253 | 0 | 108.5267 | 218.1904 | 17.12% | 0 | 0 | 0 | 0% | 43.3
5071 | 0 | 32 | 32 | 9.0669 | 23.3 | 0 | 0 | 0 | 0 | 1.9026 | 0 | 0 | 1.9026 | 0 | 0 | 0 | 109.2809 | 43.1974 | 0 | 109.2809 | 109.9767 | 8.629% | 0 | 0 | 0 | 0% | 45.1
5072 | 0 | 55 | 55 | 9.4699 | 23.9 | 0 | 0 | 0 | 0 | 3.6064 | 0 | 0 | 3.6064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.9767 | 8.629% | 0 | 0 | 0 | 0% | 3.6064
5073 | 56 | 221 | 180 | 12.6937 | 24.4 | 28.1858 | 0 | 17.321 | 0 | 16.1803 | 0 | 0 | 16.1803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.9767 | 8.629% | 0 | 0 | 0 | 0% | 16.1803
5074 | 461 | 628 | 268 | 11.6862 | 26.6 | 232.0293 | 148.0768 | 0 | 115.8452 | 58.1215 | 0 | 5.0608 | 53.0608 | 0 | 0 | 0 | 0 | 0 | 115.8452 | 0 | 220.6457 | 17.31% | 3.8816 | 0 | 3.9983 | 7.997% | 48
5075 | 320 | 684 | 394 | 15.1115 | 27.5 | 161.0616 | 105.3525 | 0 | 73.6076 | 68.1634 | 0 | 10.5317 | 57.6317 | 0 | 0 | 0 | 0 | 0 | 73.6076 | 0 | 290.9644 | 22.83% | 8.0778 | 0 | 12.3191 | 24.64% | 47.1
5076 | 114 | 510 | 392 | 15.5145 | 28 | 57.3782 | 0 | 37.926 | 0 | 41.5359 | 0 | 0 | 41.5359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290.9644 | 22.83% | 0 | 4.6641 | 7.5154 | 15.03% | 46.2
5077 | 253 | 696 | 442 | 13.9026 | 29.2 | 127.3393 | 83.4535 | 0 | 53.9366 | 71.0542 | 0 | 12.4771 | 58.5771 | 0 | 0 | 0 | 0 | 0 | 53.9366 | 0 | 342.491 | 26.87% | 9.5699 | 0 | 17.3733 | 34.75% | 46.1
5078 | 291 | 682 | 401 | 15.9175 | 30 | 146.4654 | 93.7884 | 0 | 62.6421 | 68.1161 | 0 | 11.058 | 57.058 | 0 | 0 | 0 | 0 | 0 | 62.6421 | 0 | 402.3341 | 31.57% | 8.4815 | 0 | 26.11 | 52.22% | 46
5079 | 462 | 723 | 337 | 16.119 | 30.4 | 232.5326 | 143.4784 | 0 | 109.0906 | 77.9088 | 0 | 16.2544 | 61.6544 | 0 | 0 | 0 | 0 | 0 | 109.0906 | 0 | 506.5503 | 39.74% | 12.4671 | 0 | 38.9522 | 77.9% | 45.4
5080 | 662 | 649 | 180 | 13.2981 | 31.2 | 333.1961 | 192.8836 | 0 | 156.7982 | 62.7807 | 0 | 9.0404 | 53.7404 | 0 | 0 | 0 | 0 | 0 | 156.7982 | 0 | 656.3425 | 51.5% | 6.934 | 0 | 46.0948 | 92.19% | 44.7
5081 | 564 | 462 | 156 | 14.5071 | 30 | 283.871 | 143.5929 | 0 | 110.0783 | 34.1983 | 0 | 0 | 34.1983 | 0 | 0 | 0 | 0 | 0 | 110.0783 | 0 | 761.5023 | 59.75% | 0 | 9.8017 | 35.9999 | 72% | 44
5082 | 420 | 266 | 114 | 14.91 | 28.3 | 211.3933 | 81.5642 | 0 | 51.3952 | 13.5966 | 0 | 0 | 13.5966 | 0 | 0 | 0 | 0 | 0 | 51.3952 | 0 | 810.601 | 63.6% | 0 | 25 | 10.2511 | 20.5% | 38.5966
5083 | 152 | 83 | 55 | 13.9026 | 26.4 | 76.5042 | 0 | 0 | 0 | 3.0192 | 0 | 0 | 3.0192 | 0 | 0 | 0 | 77.7294 | 29.9273 | 0 | 77.7294 | 738.8528 | 57.97% | 0 | 9.9535 | 0 | 0% | 42.9
5084 | 1 | 3 | 3 | 13.9026 | 24 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1718 | 39.8 | 0 | 101.1718 | 640.4532 | 50.25% | 0 | 0 | 0 | 0% | 39.8
5085 | 0 | 0 | 0 | 13.2981 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3394 | 38.3 | 0 | 97.3394 | 546.3469 | 42.87% | 0 | 0 | 0 | 0% | 38.3
5086 | 0 | 0 | 0 | 10.8803 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4038 | 36.3 | 0 | 92.4038 | 457.8864 | 35.93% | 0 | 0 | 0 | 0% | 36.3
5087 | 0 | 0 | 0 | 6.8506 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.242 | 34.6 | 0 | 88.242 | 374.1622 | 29.36% | 0 | 0 | 0 | 0% | 34.6
5088 | 0 | 0 | 0 | 5.6416 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2915 | 33.8 | 0 | 86.2915 | 292.6524 | 22.96% | 0 | 0 | 0 | 0% | 33.8
5089 | 0 | 0 | 0 | 4.8357 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2413 | 33.4 | 0 | 85.2413 | 212.2993 | 16.66% | 0 | 0 | 0 | 0% | 33.4
5090 | 0 | 0 | 0 | 4.2312 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8377 | 27.2669 | 0 | 70.8377 | 147.0498 | 11.54% | 0 | 0 | 0 | 0% | 27.2669
5091 | 0 | 0 | 0 | 3.6268 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.0498 | 11.54% | 0 | 0 | 0 | 0% | 0
5092 | 0 | 0 | 0 | 2.6193 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.0498 | 11.54% | 0 | 0 | 0 | 0% | 0
5093 | 0 | 0 | 0 | 3.2238 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.0498 | 11.54% | 0 | 0 | 0 | 0% | 0
5094 | 3 | 17 | 17 | 2.4178 | 19.7 | 1.51 | 0 | 0.56074 | 0 | 0.48996 | 0 | 0 | 0.48996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.0498 | 11.54% | 0 | 0 | 0 | 0% | 0.48996
5095 | 56 | 105 | 90 | 2.2164 | 21.3 | 28.1858 | 0 | 13.939 | 0 | 6.017 | 0 | 0 | 6.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.0498 | 11.54% | 0 | 0 | 0 | 0% | 6.017
5096 | 55 | 198 | 170 | 2.0149 | 23.6 | 27.6825 | 0 | 15.8559 | 0 | 13.6911 | 0 | 0 | 13.6911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.0498 | 11.54% | 0 | 0 | 0 | 0% | 13.6911
5097 | 153 | 385 | 283 | 4.2312 | 25.1 | 77.0076 | 0 | 47.3279 | 0 | 29.2339 | 0 | 0 | 29.2339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.0498 | 11.54% | 0 | 0 | 0 | 0% | 29.2339
5098 | 377 | 572 | 274 | 8.8654 | 27.3 | 189.7507 | 121.0986 | 0 | 92.2435 | 47.7502 | 0 | 0 | 47.7502 | 0 | 0 | 0 | 0 | 0 | 92.2435 | 0 | 234.6469 | 18.41% | 0 | 0 | 0 | 0% | 47.7502
5099 | 695 | 847 | 234 | 5.2387 | 29.2 | 349.8056 | 228.8186 | 0 | 195.0742 | 95.2082 | 0 | 22.8541 | 72.3541 | 0 | 0 | 0 | 0 | 0 | 195.0742 | 0 | 419.895 | 32.95% | 17.5291 | 0 | 18.0589 | 36.12% | 49.5
5100 | 680 | 908 | 263 | 3.6268 | 30.7 | 342.2558 | 226.2226 | 0 | 193.2245 | 101.5 | 1.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 193.2245 | 0 | 603.3867 | 47.34% | 19.175 | 0 | 37.8135 | 75.63% | 48.5
5101 | 709 | 930 | 248 | 5.6416 | 32 | 356.852 | 233.8809 | 0 | 199.6614 | 101.8 | 11.3776 | 15.4224 | 75 | 0 | 0 | 0 | 0 | 0 | 199.6614 | 0 | 792.991 | 62.22% | 11.829 | 0 | 50 | 100% | 48.2
5102 | 671 | 882 | 262 | 7.052 | 32.6 | 337.726 | 216.2758 | 0 | 182.3283 | 101.9 | 26.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 182.3283 | 0 | 966.1352 | 75.8% | 0 | 0 | 50 | 100% | 48.1
5103 | 643 | 782 | 244 | 6.8506 | 33.6 | 323.6331 | 199.718 | 0 | 167.0048 | 83.6091 | 18.0545 | 0 | 65.5545 | 0 | 0 | 0 | 0 | 0 | 167.0048 | 0 | 1124.7278 | 88.25% | 0 | 0 | 50 | 100% | 47.5
5104 | 583 | 634 | 224 | 11.6862 | 31.6 | 293.434 | 169.8415 | 0 | 136.232 | 57.8093 | 5.6546 | 0 | 52.1546 | 0 | 0 | 0 | 0 | 0 | 136.232 | 0 | 1254.0977 | 98.4% | 0 | 0 | 50 | 100% | 46.5
5105 | 535 | 456 | 167 | 10.4773 | 30.3 | 269.2748 | 0 | 135.9956 | 0 | 33.798 | 0 | 0 | 33.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.0977 | 98.4% | 0 | 11.902 | 37.7401 | 75.48% | 45.7
5106 | 386 | 258 | 120 | 8.8654 | 29.1 | 194.2805 | 0 | 74.6941 | 0 | 13.5184 | 0 | 0 | 13.5184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.0977 | 98.4% | 0 | 25 | 11.9878 | 23.98% | 38.5184
5107 | 134 | 78 | 53 | 7.2535 | 26.7 | 67.4445 | 0 | 0 | 0 | 2.8881 | 0 | 0 | 2.8881 | 0 | 0 | 0 | 77.0258 | 29.5736 | 0 | 77.0258 | 1183.0314 | 92.82% | 0 | 11.6382 | 1.3878e-15 | 2.776e-15% | 44.1
5108 | 1 | 3 | 3 | 7.858 | 24.2 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6171 | 41.2 | 0 | 104.6171 | 1080.6771 | 84.79% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 41.2
5109 | 0 | 0 | 0 | 5.8431 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0275 | 38.6 | 0 | 98.0275 | 985.717 | 77.34% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 38.6
5110 | 0 | 0 | 0 | 3.4253 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6287 | 36.4 | 0 | 92.6287 | 896.9841 | 70.38% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 36.4
5111 | 0 | 0 | 0 | 1.2089 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6669 | 34.8 | 0 | 88.6669 | 812.7346 | 63.77% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 34.8
5112 | 0 | 0 | 0 | 2.4178 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4966 | 33.9 | 0 | 86.4966 | 731.0047 | 57.36% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 33.9
5113 | 0 | 0 | 0 | 2.0149 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5265 | 33.5 | 0 | 85.5265 | 650.3679 | 51.03% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 33.5
5114 | 0 | 0 | 0 | 2.6193 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4543 | 33.9 | 0 | 86.4543 | 568.6513 | 44.62% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 33.9
5115 | 0 | 0 | 0 | 2.2164 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9817 | 36.2 | 0 | 91.9817 | 480.4088 | 37.69% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 36.2
5116 | 0 | 0 | 0 | 1.2089 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4522 | 38.5 | 0 | 97.4522 | 385.6249 | 30.26% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 38.5
5117 | 0 | 0 | 0 | 3.4253 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5108 | 41.8 | 0 | 105.5108 | 281.4109 | 22.08% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 41.8
5118 | 33 | 22 | 18 | 3.6268 | 21.1 | 16.6095 | 0 | 6.1418 | 0 | 0.51062 | 0 | 0 | 0.51062 | 0 | 0 | 0 | 95.3977 | 37.6323 | 0 | 95.3977 | 189.0516 | 14.83% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 38.1429
5119 | 331 | 162 | 78 | 1.6119 | 23 | 166.5981 | 82.2271 | 0 | 58.9397 | 5.4967 | 0 | 0 | 5.4967 | 0 | 0 | 0 | 0 | 0 | 58.9397 | 0 | 245.2331 | 19.24% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 5.4967
5120 | 559 | 363 | 117 | 2.6193 | 26.2 | 281.3544 | 161.0262 | 0 | 132.4934 | 23.3374 | 0 | 0 | 23.3374 | 0 | 0 | 0 | 56.1375 | 20.4589 | 132.4934 | 56.1375 | 320.457 | 25.14% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 43.7963
5121 | 666 | 555 | 146 | 5.0372 | 28.9 | 335.2094 | 206.034 | 0 | 173.9303 | 44.548 | 0 | 0 | 44.548 | 0 | 0 | 0 | 0 | 0 | 173.9303 | 0 | 485.8077 | 38.12% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 44.548
5122 | 723 | 720 | 170 | 6.0446 | 30.1 | 363.8985 | 232.2441 | 0 | 197.8499 | 72.3411 | 0 | 11.1705 | 61.1705 | 0 | 0 | 0 | 0 | 0 | 197.8499 | 0 | 673.8982 | 52.88% | 8.5678 | 0 | 8.828 | 17.66% | 50
5123 | 764 | 850 | 181 | 10.0743 | 30.6 | 384.5345 | 251.5423 | 0 | 213.3582 | 98.8784 | 0 | 24.6892 | 74.1892 | 0 | 0 | 0 | 0 | 0 | 213.3582 | 0 | 876.7318 | 68.79% | 18.9366 | 0 | 28.3398 | 56.68% | 49.5
5124 | 758 | 921 | 205 | 11.0818 | 31.2 | 381.5146 | 252.1686 | 0 | 213.3643 | 101.7 | 1.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 213.3643 | 0 | 1079.5713 | 84.7% | 19.175 | 0 | 48.0972 | 96.19% | 48.3
5125 | 713 | 928 | 243 | 11.2833 | 31.3 | 358.8653 | 235.2146 | 0 | 197.6203 | 102.2 | 27.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 197.6203 | 0 | 1267.4435 | 99.45% | 0 | 0 | 48.0972 | 96.19% | 47.8
5126 | 686 | 883 | 249 | 9.0669 | 32 | 345.2757 | 0 | 221.1266 | 0 | 102.5 | 27.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.4435 | 99.45% | 0 | 0 | 48.0972 | 96.19% | 47.5
5127 | 626 | 775 | 253 | 6.0446 | 33 | 315.0767 | 0 | 194.467 | 0 | 83.1946 | 18.1473 | 0 | 65.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.4435 | 99.45% | 0 | 0 | 48.0972 | 96.19% | 46.9
5128 | 616 | 633 | 202 | 7.2535 | 33.9 | 310.0435 | 0 | 179.4301 | 0 | 57.5558 | 5.7779 | 0 | 51.7779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.4435 | 99.45% | 0 | 0 | 48.0972 | 96.19% | 46
5129 | 528 | 448 | 165 | 9.2684 | 33.3 | 265.7516 | 0 | 134.0045 | 0 | 33.0088 | 0 | 0 | 33.0088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.4435 | 99.45% | 0 | 11.9912 | 35.7437 | 71.49% | 45
5130 | 364 | 250 | 122 | 7.455 | 32.4 | 183.2075 | 0 | 70.1833 | 0 | 13.2043 | 0 | 0 | 13.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.4435 | 99.45% | 0 | 25 | 9.9876 | 19.98% | 38.2043
5131 | 134 | 78 | 53 | 6.6491 | 29.7 | 67.4445 | 0 | 0 | 0 | 2.8401 | 0 | 0 | 2.8401 | 0 | 0 | 0 | 80.7712 | 30.8649 | 0 | 80.7712 | 1192.5274 | 93.57% | 0 | 9.695 | 0 | 0% | 43.4
5132 | 1 | 2 | 2 | 6.6491 | 25.9 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2653 | 40.5 | 0 | 103.2653 | 1092.146 | 85.69% | 0 | 0 | 0 | 0% | 40.5
5133 | 0 | 0 | 0 | 4.6342 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6705 | 38.3 | 0 | 97.6705 | 998.0298 | 78.31% | 0 | 0 | 0 | 0% | 38.3
5134 | 0 | 0 | 0 | 2.4178 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.193 | 36.1 | 0 | 92.193 | 909.9991 | 71.4% | 0 | 0 | 0 | 0% | 36.1
5135 | 0 | 0 | 0 | 1.4104 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5653 | 34.2 | 0 | 87.5653 | 827.1501 | 64.9% | 0 | 0 | 0 | 0% | 34.2
5136 | 0 | 0 | 0 | 2.0149 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7983 | 33.1 | 0 | 84.7983 | 747.4221 | 58.64% | 0 | 0 | 0 | 0% | 33.1
5137 | 0 | 0 | 0 | 1.4104 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0267 | 32.4 | 0 | 83.0267 | 669.6652 | 52.54% | 0 | 0 | 0 | 0% | 32.4
5138 | 0 | 0 | 0 | 2.6193 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.028 | 32 | 0 | 82.028 | 593.0091 | 46.53% | 0 | 0 | 0 | 0% | 32
5139 | 0 | 0 | 0 | 1.4104 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9766 | 32.4 | 0 | 82.9766 | 515.2726 | 40.43% | 0 | 0 | 0 | 0% | 32.4
5140 | 0 | 0 | 0 | 2.8208 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.313 | 32.6 | 0 | 83.313 | 437.115 | 34.3% | 0 | 0 | 0 | 0% | 32.6
5141 | 0 | 0 | 0 | 1.8134 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0953 | 34.6 | 0 | 88.0953 | 353.3838 | 27.73% | 0 | 0 | 0 | 0% | 34.6
5142 | 23 | 22 | 19 | 1.6119 | 20.9 | 11.5763 | 0 | 4.2613 | 0 | 0.5537 | 0 | 0 | 0.5537 | 0 | 0 | 0 | 93.9597 | 37.0463 | 0 | 93.9597 | 262.7227 | 20.61% | 0 | 0 | 0 | 0% | 37.6
5143 | 287 | 160 | 86 | 1.8134 | 23.4 | 144.4521 | 71.1497 | 0 | 48.2825 | 5.9728 | 0 | 0 | 5.9728 | 0 | 0 | 0 | 0 | 0 | 48.2825 | 0 | 308.3602 | 24.19% | 0 | 0 | 0 | 0% | 5.9728
5144 | 509 | 361 | 136 | 6.4476 | 25.3 | 256.1886 | 146.5014 | 0 | 117.436 | 23.5958 | 0 | 0 | 23.5958 | 0 | 0 | 0 | 0 | 0 | 117.436 | 0 | 419.3628 | 32.9% | 0 | 0 | 0 | 0% | 23.5958
5145 | 591 | 557 | 192 | 8.4625 | 26.4 | 297.4606 | 182.8472 | 0 | 150.1419 | 47.3958 | 2.3479 | 0 | 45.0479 | 0 | 0 | 0 | 0 | 0 | 150.1419 | 0 | 561.2796 | 44.04% | 0 | 0 | 0 | 0% | 42.7
5146 | 262 | 565 | 362 | 6.6491 | 27.5 | 131.8692 | 84.1614 | 0 | 58.8364 | 49.1387 | 0 | 2.8694 | 46.2694 | 0 | 0 | 0 | 0 | 0 | 58.8364 | 0 | 616.8928 | 48.4% | 2.2008 | 0 | 2.268 | 4.536% | 43.4
5147 | 611 | 809 | 267 | 4.0297 | 29.3 | 307.5269 | 201.1729 | 0 | 169.6852 | 93.288 | 0 | 24.894 | 68.394 | 0 | 0 | 0 | 0 | 0 | 169.6852 | 0 | 777.2824 | 60.99% | 19.0937 | 0 | 21.9444 | 43.89% | 43.5
5148 | 727 | 913 | 227 | 3.0223 | 31.6 | 365.9117 | 241.8524 | 0 | 207.9961 | 107.4 | 7.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 207.9961 | 0 | 973.884 | 76.41% | 19.175 | 0 | 41.7046 | 83.41% | 42.6
5149 | 688 | 918 | 258 | 5.8431 | 33.2 | 346.2824 | 226.9819 | 0 | 193.0578 | 108.2 | 22.705 | 10.495 | 75 | 0 | 0 | 0 | 0 | 0 | 193.0578 | 0 | 1156.3656 | 90.73% | 8.0497 | 0 | 50 | 100% | 41.8
5150 | 665 | 869 | 256 | 7.455 | 33.4 | 334.7061 | 214.3739 | 0 | 180.3414 | 107.8181 | 33.2091 | 0 | 74.6091 | 0 | 0 | 0 | 0 | 0 | 180.3414 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.4
5151 | 664 | 776 | 225 | 9.2684 | 32.8 | 334.2027 | 0 | 206.3044 | 0 | 92.069 | 25.5345 | 0 | 66.5345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41
5152 | 653 | 637 | 182 | 9.4699 | 32 | 328.6663 | 0 | 190.0934 | 0 | 65.3844 | 12.2922 | 0 | 53.0922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.8
5153 | 528 | 447 | 165 | 4.6342 | 31.7 | 265.7516 | 0 | 133.7923 | 0 | 32.9243 | 0 | 0 | 32.9243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.6757 | 42.0913 | 84.18% | 40.6
5154 | 361 | 246 | 119 | 5.4401 | 30.5 | 181.6976 | 0 | 69.3519 | 0 | 13.0317 | 0 | 0 | 13.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.3318 | 32.66% | 38.0317
5155 | 105 | 72 | 52 | 5.4401 | 28.5 | 52.8483 | 0 | 0 | 0 | 2.8674 | 0 | 0 | 2.8674 | 0 | 0 | 0 | 60.3224 | 21.9819 | 0 | 60.3224 | 1219.5583 | 95.69% | 0 | 15.8507 | 0 | 0% | 40.7
5156 | 0 | 2 | 2 | 6.0446 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9356 | 38.3 | 0 | 97.9356 | 1125.1814 | 88.28% | 0 | 0 | 0 | 0% | 38.3
5157 | 0 | 0 | 0 | 5.0372 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2854 | 36.1 | 0 | 92.2854 | 1037.0583 | 81.37% | 0 | 0 | 0 | 0% | 36.1
5158 | 0 | 0 | 0 | 4.2312 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0497 | 34 | 0 | 87.0497 | 954.7907 | 74.91% | 0 | 0 | 0 | 0% | 34
5159 | 0 | 0 | 0 | 4.6342 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.852 | 32.3 | 0 | 82.852 | 877.2523 | 68.83% | 0 | 0 | 0 | 0% | 32.3
5160 | 0 | 0 | 0 | 4.6342 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4326 | 31.3 | 0 | 80.4326 | 802.4019 | 62.96% | 0 | 0 | 0 | 0% | 31.3
5161 | 0 | 0 | 0 | 5.0372 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5225 | 30.5 | 0 | 78.5225 | 729.6542 | 57.25% | 0 | 0 | 0 | 0% | 30.5
5162 | 0 | 0 | 0 | 3.0223 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9887 | 30.3 | 0 | 77.9887 | 657.4729 | 51.59% | 0 | 0 | 0 | 0% | 30.3
5163 | 0 | 0 | 0 | 2.2164 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2003 | 30.4 | 0 | 78.2003 | 585.0424 | 45.9% | 0 | 0 | 0 | 0% | 30.4
5164 | 0 | 0 | 0 | 2.6193 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7591 | 29.8 | 0 | 76.7591 | 514.1169 | 40.34% | 0 | 0 | 0 | 0% | 29.8
5165 | 0 | 0 | 0 | 2.4178 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9155 | 31.1 | 0 | 79.9155 | 439.7715 | 34.51% | 0 | 0 | 0 | 0% | 31.1
5166 | 12 | 19 | 17 | 2.4178 | 23 | 6.0398 | 0 | 2.2128 | 0 | 0.47689 | 0 | 0 | 0.47689 | 0 | 0 | 0 | 84.0803 | 32.8231 | 0 | 84.0803 | 360.7492 | 28.3% | 0 | 0 | 0 | 0% | 33.3
5167 | 218 | 147 | 90 | 2.4178 | 24.1 | 109.7232 | 0 | 53.9278 | 0 | 6.142 | 0 | 0 | 6.142 | 0 | 0 | 0 | 76.2334 | 29.458 | 0 | 76.2334 | 290.2974 | 22.78% | 0 | 0 | 0 | 0% | 35.6
5168 | 439 | 343 | 148 | 2.6193 | 25.6 | 220.9563 | 126.2437 | 0 | 99.9594 | 22.5358 | 0 | 0 | 22.5358 | 0 | 0 | 0 | 0 | 0 | 99.9594 | 0 | 383.5186 | 30.09% | 0 | 0 | 0 | 0% | 22.5358
5169 | 559 | 537 | 191 | 2.4178 | 27.3 | 281.3544 | 172.9602 | 0 | 143.8146 | 46.3992 | 0 | 3.9496 | 42.4496 | 0 | 0 | 0 | 0 | 0 | 143.8146 | 0 | 517.6385 | 40.61% | 3.0294 | 0 | 3.1222 | 6.244% | 38.5
5170 | 629 | 701 | 220 | 2.4178 | 29.7 | 316.5866 | 202.0525 | 0 | 171.0319 | 76.5796 | 0 | 18.4898 | 58.0898 | 0 | 0 | 0 | 0 | 0 | 171.0319 | 0 | 677.1411 | 53.13% | 14.1817 | 0 | 17.7388 | 35.48% | 39.6
5171 | 678 | 828 | 233 | 4.4327 | 32.2 | 341.2492 | 223.2378 | 0 | 190.1886 | 100.1942 | 4.8971 | 25 | 70.2971 | 0 | 0 | 0 | 0 | 0 | 190.1886 | 0 | 854.509 | 67.05% | 19.175 | 0 | 37.5019 | 75% | 40.4
5172 | 691 | 899 | 248 | 5.4401 | 33.9 | 347.7923 | 229.873 | 0 | 196.0225 | 110.3 | 19.4901 | 15.8099 | 75 | 0 | 0 | 0 | 0 | 0 | 196.0225 | 0 | 1037.3176 | 81.39% | 12.1262 | 0 | 50 | 100% | 39.7
5173 | 672 | 908 | 265 | 6.0446 | 34.6 | 338.2293 | 221.7184 | 0 | 188.0262 | 111 | 36 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 188.0262 | 0 | 1212.6689 | 95.15% | 0 | 0 | 50 | 100% | 39
5174 | 645 | 862 | 268 | 9.2684 | 34.1 | 324.6397 | 207.9435 | 0 | 173.3562 | 110.0664 | 35.6832 | 0 | 74.3832 | 0 | 0 | 0 | 0 | 0 | 173.3562 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.7
5175 | 601 | 760 | 260 | 10.2758 | 33.1 | 302.4938 | 0 | 186.7616 | 0 | 91.4645 | 26.5323 | 0 | 64.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.4
5176 | 543 | 613 | 233 | 8.4625 | 33.3 | 273.3013 | 0 | 157.9767 | 0 | 61.7714 | 11.6357 | 0 | 50.1357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.5
5177 | 439 | 431 | 195 | 8.0595 | 32.9 | 220.9563 | 0 | 111.0634 | 0 | 31.9292 | 0 | 0 | 31.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 6.9708 | 42.8165 | 85.63% | 38.9
5178 | 304 | 240 | 133 | 8.0595 | 32.5 | 153.0085 | 0 | 58.1874 | 0 | 13.1298 | 0 | 0 | 13.1298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.0533 | 34.11% | 38.1298
5179 | 108 | 72 | 52 | 7.455 | 31 | 54.3583 | 0 | 0 | 0 | 2.7491 | 0 | 0 | 2.7491 | 0 | 0 | 0 | 60.3114 | 21.7024 | 0 | 60.3114 | 1219.5975 | 95.69% | 0 | 16.5485 | 0 | 0% | 41
5180 | 1 | 2 | 2 | 4.8357 | 28.5 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1957 | 38.6 | 0 | 99.1957 | 1123.8805 | 88.18% | 0 | 0 | 0 | 0% | 38.6
5181 | 0 | 0 | 0 | 4.0297 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6739 | 36.1 | 0 | 92.6739 | 1035.3825 | 81.24% | 0 | 0 | 0 | 0% | 36.1
5182 | 0 | 0 | 0 | 4.8357 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.185 | 33.9 | 0 | 87.185 | 953.0317 | 74.78% | 0 | 0 | 0 | 0% | 33.9
5183 | 0 | 0 | 0 | 2.4178 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.156 | 32.3 | 0 | 83.156 | 875.2055 | 68.67% | 0 | 0 | 0 | 0% | 32.3
5184 | 0 | 0 | 0 | 2.4178 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3785 | 31.6 | 0 | 81.3785 | 799.3404 | 62.72% | 0 | 0 | 0 | 0% | 31.6
5185 | 0 | 0 | 0 | 1.4104 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5626 | 31.3 | 0 | 80.5626 | 724.3549 | 56.83% | 0 | 0 | 0 | 0% | 31.3
5186 | 0 | 0 | 0 | 2.2164 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4343 | 31.7 | 0 | 81.4343 | 648.371 | 50.87% | 0 | 0 | 0 | 0% | 31.7
5187 | 0 | 0 | 0 | 2.2164 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6646 | 34.3 | 0 | 87.6646 | 565.3101 | 44.36% | 0 | 0 | 0 | 0% | 34.3
5188 | 0 | 0 | 0 | 2.6193 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3586 | 36.7 | 0 | 93.3586 | 475.6546 | 37.32% | 0 | 0 | 0 | 0% | 36.7
5189 | 0 | 0 | 0 | 1.8134 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.637 | 40.1 | 0 | 101.637 | 376.2598 | 29.52% | 0 | 0 | 0 | 0% | 40.1
5190 | 14 | 18 | 16 | 2.4178 | 21.6 | 7.0464 | 0 | 2.569 | 0 | 0.43334 | 0 | 0 | 0.43334 | 0 | 0 | 0 | 108.6637 | 43.0667 | 0 | 108.6637 | 268.4245 | 21.06% | 0 | 0 | 0 | 0% | 43.5
5191 | 255 | 150 | 86 | 1.4104 | 23.6 | 128.3459 | 62.9395 | 0 | 41.1034 | 5.9715 | 0 | 0 | 5.9715 | 0 | 0 | 0 | 83.3273 | 32.4691 | 41.1034 | 83.3273 | 229.1205 | 17.98% | 0 | 0 | 0 | 0% | 38.4406
5192 | 472 | 345 | 139 | 2.6193 | 26.5 | 237.5658 | 135.6095 | 0 | 108.6957 | 22.7002 | 0 | 0 | 22.7002 | 0 | 0 | 0 | 0 | 0 | 108.6957 | 0 | 331.8475 | 26.04% | 0 | 0 | 0 | 0% | 22.7002
5193 | 606 | 543 | 172 | 5.6416 | 29.3 | 305.0103 | 187.5159 | 0 | 156.1844 | 43.9557 | 0 | 0 | 43.9557 | 0 | 0 | 0 | 0 | 0 | 156.1844 | 0 | 479.4554 | 37.62% | 0 | 0 | 0 | 0% | 43.9557
5194 | 668 | 707 | 199 | 5.6416 | 31.5 | 336.216 | 214.5797 | 0 | 181.544 | 69.7397 | 0 | 9.8699 | 59.8699 | 0 | 0 | 0 | 0 | 0 | 181.544 | 0 | 651.0304 | 51.08% | 7.5702 | 0 | 7.8035 | 15.61% | 50
5195 | 694 | 831 | 224 | 5.6416 | 32.9 | 349.3023 | 228.5109 | 0 | 194.6078 | 92.5903 | 0 | 21.3452 | 71.2452 | 0 | 0 | 0 | 0 | 0 | 194.6078 | 0 | 834.9518 | 65.51% | 16.3717 | 0 | 24.6798 | 49.36% | 49.9
5196 | 684 | 897 | 253 | 7.052 | 33.9 | 344.2691 | 227.5409 | 0 | 192.9015 | 101.1 | 1.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 192.9015 | 0 | 1017.2606 | 79.82% | 19.175 | 0 | 44.4457 | 88.89% | 48.9
5197 | 658 | 905 | 275 | 8.8654 | 34.8 | 331.1828 | 217.1149 | 0 | 182.1158 | 101.4 | 19.375 | 7.025 | 75 | 0 | 0 | 0 | 0 | 0 | 182.1158 | 0 | 1189.376 | 93.32% | 5.3882 | 0 | 50 | 100% | 48.6
5198 | 650 | 862 | 265 | 8.261 | 35 | 327.1563 | 209.5735 | 0 | 175.4588 | 99.8958 | 25.7479 | 0 | 74.1479 | 0 | 0 | 0 | 0 | 0 | 175.4588 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.4
5199 | 622 | 758 | 241 | 11.4848 | 34.7 | 313.0634 | 0 | 193.3214 | 0 | 82.0335 | 17.1168 | 0 | 64.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.8
5200 | 567 | 617 | 221 | 9.2684 | 34.7 | 285.381 | 0 | 164.86 | 0 | 54.2835 | 3.7918 | 0 | 50.4918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.7
5201 | 496 | 441 | 178 | 9.8729 | 34.8 | 249.6454 | 0 | 125.2838 | 0 | 32.7443 | 0 | 0 | 32.7443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 13.1557 | 36.4409 | 72.88% | 45.9
5202 | 336 | 242 | 126 | 7.6565 | 34 | 169.1146 | 0 | 64.0744 | 0 | 12.9781 | 0 | 0 | 12.9781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.6736 | 21.35% | 37.9781
5203 | 108 | 71 | 52 | 7.6565 | 30.9 | 54.3583 | 0 | 0 | 0 | 2.7405 | 0 | 0 | 2.7405 | 0 | 0 | 0 | 83.6222 | 31.903 | 0 | 83.6222 | 1196.4872 | 93.88% | 0 | 10.3565 | 0 | 0% | 45
5204 | 0 | 2 | 2 | 4.8357 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7103 | 41.7 | 0 | 106.7103 | 1092.3343 | 85.71% | 0 | 0 | 0 | 0% | 41.7
5205 | 0 | 0 | 0 | 4.8357 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4892 | 38.9 | 0 | 99.4892 | 996.2256 | 78.17% | 0 | 0 | 0 | 0% | 38.9
5206 | 0 | 0 | 0 | 4.2312 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6258 | 36.3 | 0 | 92.6258 | 907.7111 | 71.22% | 0 | 0 | 0 | 0% | 36.3
5207 | 0 | 0 | 0 | 0.60446 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6052 | 34.7 | 0 | 88.6052 | 823.6349 | 64.62% | 0 | 0 | 0 | 0% | 34.7
5208 | 0 | 0 | 0 | 1.6119 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2245 | 33.7 | 0 | 86.2245 | 742.2846 | 58.24% | 0 | 0 | 0 | 0% | 33.7
5209 | 0 | 0 | 0 | 2.6193 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2113 | 33.3 | 0 | 85.2113 | 662.0656 | 51.95% | 0 | 0 | 0 | 0% | 33.3
5210 | 0 | 0 | 0 | 1.8134 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.378 | 33.8 | 0 | 86.378 | 580.4965 | 45.55% | 0 | 0 | 0 | 0% | 33.8
5211 | 0 | 0 | 0 | 1.4104 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5633 | 36 | 0 | 91.5633 | 492.8452 | 38.67% | 0 | 0 | 0 | 0% | 36
5212 | 0 | 0 | 0 | 1.0074 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8404 | 38.2 | 0 | 96.8404 | 398.9524 | 31.3% | 0 | 0 | 0 | 0% | 38.2
5213 | 0 | 0 | 0 | 2.2164 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9771 | 41.5 | 0 | 104.9771 | 295.627 | 23.2% | 0 | 0 | 0 | 0% | 41.5
5214 | 16 | 19 | 17 | 2.4178 | 21.9 | 8.0531 | 0 | 2.9211 | 0 | 0.47896 | 0 | 0 | 0.47896 | 0 | 0 | 0 | 111.2972 | 44.121 | 0 | 111.2972 | 184.7751 | 14.5% | 0 | 0 | 0 | 0% | 44.6
5215 | 264 | 150 | 84 | 2.0149 | 23.1 | 132.8758 | 65.0091 | 0 | 42.6987 | 5.8892 | 0 | 0 | 5.8892 | 0 | 0 | 0 | 0 | 0 | 42.6987 | 0 | 225.579 | 17.7% | 0 | 0 | 0 | 0% | 5.8892
5216 | 514 | 351 | 128 | 1.6119 | 26.5 | 258.7051 | 147.5352 | 0 | 120.3439 | 22.9331 | 0 | 0 | 22.9331 | 0 | 0 | 0 | 67.3077 | 25.2669 | 120.3439 | 67.3077 | 278.755 | 21.87% | 0 | 0 | 0 | 0% | 48.2
5217 | 658 | 550 | 151 | 1.6119 | 31 | 331.1828 | 203.6196 | 0 | 172.7754 | 43.764 | 0 | 0 | 43.764 | 0 | 0 | 0 | 0 | 0 | 172.7754 | 0 | 443.4304 | 34.79% | 0 | 0 | 0 | 0% | 43.764
5218 | 716 | 715 | 174 | 4.8357 | 32.6 | 360.3752 | 229.9961 | 0 | 196.4227 | 71.1783 | 0 | 10.5892 | 60.5892 | 0 | 0 | 0 | 0 | 0 | 196.4227 | 0 | 630.6444 | 49.48% | 8.1219 | 0 | 8.3734 | 16.75% | 50
5219 | 743 | 844 | 199 | 9.6714 | 34.7 | 373.9648 | 244.65 | 0 | 207.3197 | 97.5239 | 0 | 23.762 | 73.762 | 0 | 0 | 0 | 0 | 0 | 207.3197 | 0 | 828.2445 | 64.99% | 18.2254 | 0 | 27.1632 | 54.33% | 50
5220 | 758 | 920 | 210 | 8.8654 | 36.1 | 381.5146 | 252.1539 | 0 | 214.7625 | 100.4 | 0.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 214.7625 | 0 | 1032.9386 | 81.05% | 19.175 | 0 | 46.9321 | 93.86% | 49.6
5221 | 736 | 928 | 227 | 6.6491 | 37.6 | 370.4416 | 242.8705 | 0 | 207.4683 | 100.6 | 21.7203 | 3.8797 | 75 | 0 | 0 | 0 | 0 | 0 | 207.4683 | 0 | 1230.6804 | 96.56% | 2.9757 | 0 | 50 | 100% | 49.4
5222 | 721 | 887 | 229 | 6.6491 | 38.5 | 362.8918 | 0 | 232.4758 | 0 | 101.1 | 26.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.6804 | 96.56% | 0 | 0 | 50 | 100% | 48.9
5223 | 673 | 782 | 226 | 7.052 | 39.2 | 338.7326 | 0 | 209.1995 | 0 | 82.8813 | 17.4407 | 0 | 65.4407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.6804 | 96.56% | 0 | 0 | 50 | 100% | 48
5224 | 600 | 632 | 216 | 7.6565 | 39.4 | 301.9904 | 0 | 174.3501 | 0 | 54.7793 | 3.8396 | 0 | 50.9396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.6804 | 96.56% | 0 | 0 | 50 | 100% | 47.1
5225 | 491 | 443 | 185 | 8.4625 | 38.7 | 247.1288 | 0 | 123.8224 | 0 | 32.5744 | 0 | 0 | 32.5744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.6804 | 96.56% | 0 | 13.7256 | 35.8514 | 71.7% | 46.3
5226 | 293 | 236 | 133 | 10.4773 | 34 | 147.472 | 0 | 55.6659 | 0 | 12.95 | 0 | 0 | 12.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.6804 | 96.56% | 0 | 25 | 10.0804 | 20.16% | 37.95
5227 | 66 | 67 | 55 | 9.0669 | 30.3 | 33.2189 | 0 | 0 | 0 | 2.9509 | 0 | 0 | 2.9509 | 0 | 0 | 0 | 85.0835 | 32.5696 | 0 | 85.0835 | 1150.9903 | 90.31% | 0 | 9.7795 | 0 | 0% | 45.3
5228 | 0 | 1 | 1 | 8.8654 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.977 | 41.8 | 0 | 106.977 | 1046.5467 | 82.11% | 0 | 0 | 0 | 0% | 41.8
5229 | 0 | 0 | 0 | 5.8431 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3919 | 39 | 0 | 99.3919 | 950.4764 | 74.58% | 0 | 0 | 0 | 0% | 39
5230 | 0 | 0 | 0 | 5.4401 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4512 | 36.6 | 0 | 93.4512 | 861.0643 | 67.56% | 0 | 0 | 0 | 0% | 36.6
5231 | 0 | 0 | 0 | 2.0149 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4483 | 35 | 0 | 89.4483 | 776.0411 | 60.89% | 0 | 0 | 0 | 0% | 35
5232 | 0 | 0 | 0 | 1.8134 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2724 | 34.1 | 0 | 87.2724 | 693.5116 | 54.41% | 0 | 0 | 0 | 0% | 34.1
5233 | 0 | 0 | 0 | 1.2089 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6623 | 33.8 | 0 | 86.6623 | 611.6898 | 47.99% | 0 | 0 | 0 | 0% | 33.8
5234 | 0 | 0 | 0 | 2.0149 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.716 | 34.1 | 0 | 87.716 | 528.7129 | 41.48% | 0 | 0 | 0 | 0% | 34.1
5235 | 0 | 0 | 0 | 3.0223 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7558 | 36.3 | 0 | 92.7558 | 440.0042 | 34.52% | 0 | 0 | 0 | 0% | 36.3
5236 | 0 | 0 | 0 | 3.4253 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5708 | 38.8 | 0 | 98.5708 | 344.393 | 27.02% | 0 | 0 | 0 | 0% | 38.8
5237 | 0 | 0 | 0 | 2.0149 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5519 | 41.7 | 0 | 105.5519 | 240.4969 | 18.87% | 0 | 0 | 0 | 0% | 41.7
5238 | 6 | 16 | 16 | 1.8134 | 22.8 | 3.0199 | 0 | 1.0897 | 0 | 0.42697 | 0 | 0 | 0.42697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.4969 | 18.87% | 0 | 0 | 0 | 0% | 0.42697
5239 | 148 | 137 | 99 | 3.4253 | 25 | 74.491 | 0 | 36.3563 | 0 | 6.6088 | 0 | 0 | 6.6088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.4969 | 18.87% | 0 | 0 | 0 | 0% | 6.6088
5240 | 399 | 356 | 183 | 3.0223 | 30.2 | 200.8236 | 114.412 | 0 | 88.886 | 23.6846 | 0 | 0 | 23.6846 | 0 | 0 | 0 | 0 | 0 | 88.886 | 0 | 325.3673 | 25.53% | 0 | 0 | 0 | 0% | 23.6846
5241 | 468 | 510 | 225 | 4.2312 | 34.2 | 235.5525 | 144.7893 | 0 | 116.9976 | 40.2436 | 0 | 0 | 40.2436 | 0 | 0 | 0 | 0 | 0 | 116.9976 | 0 | 437.0793 | 34.29% | 0 | 0 | 0 | 0% | 40.2436
5242 | 573 | 705 | 270 | 6.2461 | 36.3 | 288.4009 | 184.0576 | 0 | 152.7381 | 66.5475 | 0 | 8.2738 | 58.2738 | 0 | 0 | 0 | 0 | 0 | 152.7381 | 0 | 582.9171 | 45.74% | 6.346 | 0 | 6.5434 | 13.09% | 50
5243 | 608 | 823 | 292 | 6.8506 | 38.5 | 306.017 | 200.2019 | 0 | 167.5527 | 88.874 | 0 | 19.837 | 69.037 | 0 | 0 | 0 | 0 | 0 | 167.5527 | 0 | 742.9002 | 58.29% | 15.215 | 0 | 22.2319 | 44.46% | 49.2
5244 | 721 | 970 | 293 | 8.0595 | 40.1 | 362.8918 | 239.8416 | 0 | 203.9274 | 102.1 | 2.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 203.9274 | 0 | 937.6148 | 73.57% | 19.175 | 0 | 42.0036 | 84.01% | 47.9
5245 | 301 | 817 | 521 | 8.0595 | 40.1 | 151.4985 | 99.3341 | 0 | 72.4017 | 84.2327 | 8.2055 | 10.1109 | 65.9163 | 0 | 0 | 0 | 0 | 0 | 72.4017 | 0 | 1006.7456 | 78.99% | 7.755 | 0 | 50 | 100% | 47.6
5246 | 126 | 569 | 447 | 7.2535 | 39 | 63.418 | 0 | 40.6278 | 0 | 44.589 | 0 | 0 | 44.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006.7456 | 78.99% | 0 | 2.511 | 47.4113 | 94.82% | 47.1
5247 | 282 | 630 | 396 | 11.6862 | 37.4 | 141.9355 | 87.6698 | 0 | 59.8378 | 56.6971 | 1.8753 | 3.2732 | 51.5485 | 0 | 0 | 0 | 0 | 0 | 59.8378 | 0 | 1063.8801 | 83.47% | 2.5106 | 0 | 50 | 100% | 46.4
5248 | 266 | 547 | 355 | 11.2833 | 37.4 | 133.8824 | 77.2487 | 0 | 49.5401 | 42.1945 | 0 | 0 | 42.1945 | 0 | 0 | 0 | 0 | 0 | 49.5401 | 0 | 1111.1821 | 87.19% | 0 | 3.5055 | 46.3859 | 92.77% | 45.7
5249 | 36 | 257 | 235 | 11.8877 | 36 | 18.1194 | 0 | 9.0641 | 0 | 18.313 | 0 | 0 | 18.313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1111.1821 | 87.19% | 0 | 25 | 20.6116 | 41.22% | 43.313
5250 | 1 | 105 | 105 | 8.0595 | 34.8 | 0.50332 | 0 | 0.18927 | 0 | 7.028 | 0 | 0 | 7.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1111.1821 | 87.19% | 0 | 19.9925 | 0 | 0% | 27.0205
5251 | 0 | 28 | 28 | 5.8431 | 33.5 | 0 | 0 | 0 | 0 | 1.4521 | 0 | 0 | 1.4521 | 0 | 0 | 0 | 111.6443 | 43.0479 | 0 | 111.6443 | 1001.6734 | 78.59% | 0 | 0 | 0 | 0% | 44.5
5252 | 0 | 0 | 0 | 2.4178 | 31.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9324 | 41.4 | 0 | 106.9324 | 897.3599 | 70.41% | 0 | 0 | 0 | 0% | 41.4
5253 | 0 | 0 | 0 | 2.0149 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0344 | 38.8 | 0 | 100.0344 | 800.7182 | 62.83% | 0 | 0 | 0 | 0% | 38.8
5254 | 0 | 0 | 0 | 2.0149 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0979 | 36.5 | 0 | 94.0979 | 710.6765 | 55.76% | 0 | 0 | 0 | 0% | 36.5
5255 | 0 | 0 | 0 | 2.8208 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7991 | 34.7 | 0 | 89.7991 | 625.4236 | 49.07% | 0 | 0 | 0 | 0% | 34.7
5256 | 0 | 0 | 0 | 3.4253 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3972 | 33.8 | 0 | 87.3972 | 542.8742 | 42.59% | 0 | 0 | 0 | 0% | 33.8
5257 | 0 | 0 | 0 | 4.0297 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4162 | 33.5 | 0 | 86.4162 | 461.3795 | 36.2% | 0 | 0 | 0 | 0% | 33.5
5258 | 0 | 0 | 0 | 2.4178 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7995 | 33.7 | 0 | 86.7995 | 379.4104 | 29.77% | 0 | 0 | 0 | 0% | 33.7
5259 | 0 | 0 | 0 | 3.8283 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6774 | 35.8 | 0 | 91.6774 | 291.8567 | 22.9% | 0 | 0 | 0 | 0% | 35.8
5260 | 0 | 0 | 0 | 5.8431 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.0519 | 21.6938 | 0 | 59.0519 | 237.9949 | 18.67% | 0 | 0 | 0 | 0% | 21.6938
5261 | 0 | 0 | 0 | 1.4104 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237.9949 | 18.67% | 0 | 0 | 0 | 0% | 0
5262 | 5 | 16 | 15 | 2.8208 | 23.6 | 2.5166 | 0 | 0.9031 | 0 | 0.37586 | 0 | 0 | 0.37586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237.9949 | 18.67% | 0 | 0 | 0 | 0% | 0.37586
5263 | 164 | 141 | 100 | 3.0223 | 26.5 | 82.5441 | 0 | 40.1855 | 0 | 6.6641 | 0 | 0 | 6.6641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237.9949 | 18.67% | 0 | 0 | 0 | 0% | 6.6641
5264 | 371 | 337 | 177 | 1.2089 | 29.7 | 186.7308 | 106.2723 | 0 | 81.6387 | 22.4831 | 0 | 0 | 22.4831 | 0 | 0 | 0 | 0 | 0 | 81.6387 | 0 | 315.79 | 24.78% | 0 | 0 | 0 | 0% | 22.4831
5265 | 499 | 535 | 231 | 1.8134 | 32.1 | 251.1554 | 154.3273 | 0 | 126.5557 | 41.9832 | 0 | 0 | 41.9832 | 0 | 0 | 0 | 0 | 0 | 126.5557 | 0 | 436.3873 | 34.24% | 0 | 0 | 0 | 0% | 41.9832
5266 | 593 | 712 | 261 | 2.2164 | 34.2 | 298.4672 | 190.4769 | 0 | 160.2338 | 65.8539 | 0 | 7.9269 | 57.9269 | 0 | 0 | 0 | 0 | 0 | 160.2338 | 0 | 589.0771 | 46.22% | 6.08 | 0 | 6.2701 | 12.54% | 50
5267 | 670 | 850 | 267 | 3.4253 | 35.4 | 337.2226 | 220.6211 | 0 | 188.0803 | 92.2408 | 0 | 21.1204 | 71.1204 | 0 | 0 | 0 | 0 | 0 | 188.0803 | 0 | 768.3023 | 60.28% | 16.1994 | 0 | 22.9761 | 45.95% | 50
5268 | 713 | 925 | 259 | 5.0372 | 36.3 | 358.8653 | 237.1763 | 0 | 203.1135 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 203.1135 | 0 | 961.8529 | 75.47% | 19.175 | 0 | 42.7508 | 85.5% | 50
5269 | 734 | 943 | 248 | 6.8506 | 36.6 | 369.435 | 242.2503 | 0 | 206.7627 | 100.2 | 16.0353 | 9.1647 | 75 | 0 | 0 | 0 | 0 | 0 | 206.7627 | 0 | 1158.881 | 90.93% | 7.0294 | 0 | 50 | 100% | 49.8
5270 | 718 | 894 | 243 | 11.2833 | 36.4 | 361.3819 | 231.5204 | 0 | 194.2982 | 100.5 | 25.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 194.2982 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.5
5271 | 665 | 785 | 240 | 13.4996 | 35.9 | 334.7061 | 0 | 206.7664 | 0 | 87.4312 | 19.3656 | 0 | 68.0656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.7
5272 | 556 | 622 | 238 | 12.6937 | 35.3 | 279.8445 | 0 | 161.3699 | 0 | 55.4988 | 3.9494 | 0 | 51.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.6
5273 | 445 | 433 | 200 | 9.4699 | 35 | 223.9762 | 0 | 111.8614 | 0 | 32.507 | 0 | 0 | 32.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 14.093 | 35.4685 | 70.94% | 46.6
5274 | 299 | 234 | 133 | 8.0595 | 34 | 150.4919 | 0 | 56.3773 | 0 | 13.0188 | 0 | 0 | 13.0188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 9.6898 | 19.38% | 38.0188
5275 | 99 | 67 | 50 | 5.8431 | 31.5 | 49.8284 | 0 | 0 | 0 | 2.6336 | 0 | 0 | 2.6336 | 0 | 0 | 0 | 88.3139 | 33.7685 | 0 | 88.3139 | 1191.1825 | 93.46% | 0 | 9.3979 | 0 | 0% | 45.8
5276 | 1 | 1 | 1 | 4.0297 | 28.6 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.9806 | 42.6 | 0 | 108.9806 | 1084.4501 | 85.09% | 0 | 0 | 0 | 0% | 42.6
5277 | 0 | 0 | 0 | 1.6119 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4823 | 39.7 | 0 | 101.4823 | 986.0482 | 77.37% | 0 | 0 | 0 | 0% | 39.7
5278 | 0 | 0 | 0 | 0.60446 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2189 | 37.2 | 0 | 95.2189 | 894.6796 | 70.2% | 0 | 0 | 0 | 0% | 37.2
5279 | 0 | 0 | 0 | 1.0074 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3999 | 35.3 | 0 | 90.3999 | 808.6117 | 63.44% | 0 | 0 | 0 | 0% | 35.3
5280 | 0 | 0 | 0 | 0.60446 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1018 | 34.4 | 0 | 88.1018 | 725.1199 | 56.89% | 0 | 0 | 0 | 0% | 34.4
5281 | 0 | 0 | 0 | 2.0149 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8268 | 33.9 | 0 | 86.8268 | 643.0647 | 50.46% | 0 | 0 | 0 | 0% | 33.9
5282 | 0 | 0 | 0 | 0.60446 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.29 | 34.1 | 0 | 87.29 | 560.4609 | 43.97% | 0 | 0 | 0 | 0% | 34.1
5283 | 0 | 0 | 0 | 1.0074 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3632 | 36.2 | 0 | 92.3632 | 472.133 | 37.04% | 0 | 0 | 0 | 0% | 36.2
5284 | 0 | 0 | 0 | 0.60446 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2231 | 38.3 | 0 | 97.2231 | 377.9206 | 29.65% | 0 | 0 | 0 | 0% | 38.3
5285 | 0 | 0 | 0 | 2.6193 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6363 | 41.3 | 0 | 104.6363 | 275.1232 | 21.59% | 0 | 0 | 0 | 0% | 41.3
5286 | 13 | 16 | 15 | 2.8208 | 23.5 | 6.5431 | 0 | 2.3348 | 0 | 0.37688 | 0 | 0 | 0.37688 | 0 | 0 | 0 | 64.1408 | 24.1275 | 0 | 64.1408 | 216.3158 | 16.97% | 0 | 0 | 0 | 0% | 24.5044
5287 | 282 | 155 | 87 | 1.2089 | 25.9 | 141.9355 | 68.9197 | 0 | 46.4639 | 6.0937 | 0 | 0 | 6.0937 | 0 | 0 | 0 | 0 | 0 | 46.4639 | 0 | 260.6248 | 20.45% | 0 | 0 | 0 | 0% | 6.0937
5288 | 535 | 363 | 137 | 1.8134 | 30.2 | 269.2748 | 153.0838 | 0 | 125.3978 | 24.072 | 0 | 0 | 24.072 | 0 | 0 | 0 | 0 | 0 | 125.3978 | 0 | 380.2072 | 29.83% | 0 | 0 | 0 | 0% | 24.072
5289 | 651 | 566 | 175 | 4.6342 | 34.2 | 327.6596 | 201.264 | 0 | 169.6442 | 45.7514 | 0 | 0 | 45.7514 | 0 | 0 | 0 | 0 | 0 | 169.6442 | 0 | 541.9839 | 42.52% | 0 | 0 | 0 | 0% | 45.7514
5290 | 739 | 747 | 191 | 6.0446 | 36.4 | 371.9515 | 237.3651 | 0 | 202.7159 | 76.2197 | 0 | 13.1099 | 63.1099 | 0 | 0 | 0 | 0 | 0 | 202.7159 | 0 | 735.2985 | 57.69% | 10.0553 | 0 | 10.3712 | 20.74% | 50
5291 | 772 | 875 | 207 | 8.0595 | 37.9 | 388.561 | 254.2124 | 0 | 217.1763 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 217.1763 | 0 | 942.403 | 73.94% | 19.175 | 0 | 30.1488 | 60.3% | 50
5292 | 764 | 941 | 230 | 10.2758 | 38.9 | 384.5345 | 254.1366 | 0 | 215.8655 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 215.8655 | 0 | 1148.2575 | 90.09% | 19.175 | 0 | 49.9264 | 99.85% | 50
5293 | 750 | 956 | 247 | 11.8877 | 39.8 | 377.488 | 247.5528 | 0 | 208.8757 | 100.4 | 25.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 208.8757 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9264 | 99.85% | 49.6
5294 | 705 | 901 | 260 | 13.7011 | 40.3 | 354.8388 | 0 | 227.3358 | 0 | 100.9 | 25.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9264 | 99.85% | 49.1
5295 | 654 | 792 | 254 | 14.7085 | 40.4 | 329.1696 | 0 | 203.3744 | 0 | 86.695 | 19.2475 | 0 | 67.4475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9264 | 99.85% | 48.2
5296 | 556 | 632 | 247 | 12.6937 | 40.6 | 279.8445 | 0 | 161.2726 | 0 | 55.4919 | 4.1959 | 0 | 51.2959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9264 | 99.85% | 47.1
5297 | 415 | 436 | 217 | 11.4848 | 40.2 | 208.8767 | 0 | 104.1517 | 0 | 31.7715 | 0 | 0 | 31.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 14.3285 | 35.1499 | 70.3% | 46.1
5298 | 244 | 233 | 150 | 7.858 | 38.1 | 122.8094 | 0 | 45.831 | 0 | 13.2924 | 0 | 0 | 13.2924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 9.3674 | 18.73% | 38.2924
5299 | 51 | 65 | 56 | 3.8283 | 35 | 25.6692 | 0 | 0 | 0 | 2.8958 | 0 | 0 | 2.8958 | 0 | 0 | 0 | 87.0135 | 32.7204 | 0 | 87.0135 | 1192.9222 | 93.6% | 0 | 9.0838 | 0 | 0% | 44.7
5300 | 1 | 1 | 1 | 2.2164 | 30.4 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.5211 | 41.8 | 0 | 107.5211 | 1087.9222 | 85.36% | 0 | 0 | 0 | 0% | 41.8
5301 | 0 | 0 | 0 | 2.4178 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6007 | 39.5 | 0 | 101.6007 | 989.5047 | 77.64% | 0 | 0 | 0 | 0% | 39.5
5302 | 0 | 0 | 0 | 1.2089 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2895 | 37 | 0 | 95.2895 | 898.1595 | 70.47% | 0 | 0 | 0 | 0% | 37
5303 | 0 | 0 | 0 | 1.8134 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9846 | 35.1 | 0 | 90.9846 | 811.6206 | 63.68% | 0 | 0 | 0 | 0% | 35.1
5304 | 0 | 0 | 0 | 1.4104 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7115 | 33.8 | 0 | 87.7115 | 728.8037 | 57.18% | 0 | 0 | 0 | 0% | 33.8
5305 | 0 | 0 | 0 | 1.4104 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3473 | 32.9 | 0 | 85.3473 | 648.6292 | 50.89% | 0 | 0 | 0 | 0% | 32.9
5306 | 0 | 0 | 0 | 1.4104 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5593 | 32.6 | 0 | 84.5593 | 569.3205 | 44.67% | 0 | 0 | 0 | 0% | 32.6
5307 | 0 | 0 | 0 | 1.8134 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0917 | 32.9 | 0 | 85.0917 | 489.3585 | 38.4% | 0 | 0 | 0 | 0% | 32.9
5308 | 0 | 0 | 0 | 2.4178 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7328 | 33.2 | 0 | 85.7328 | 408.6368 | 32.06% | 0 | 0 | 0 | 0% | 33.2
5309 | 0 | 0 | 0 | 1.4104 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9352 | 35 | 0 | 89.9352 | 323.039 | 25.35% | 0 | 0 | 0 | 0% | 35
5310 | 5 | 14 | 14 | 2.6193 | 26.3 | 2.5166 | 0 | 0.89276 | 0 | 0.31939 | 0 | 0 | 0.31939 | 0 | 0 | 0 | 97.4862 | 38.0806 | 0 | 97.4862 | 229.0187 | 17.97% | 0 | 0 | 0 | 0% | 38.4
5311 | 166 | 138 | 96 | 4.4327 | 28.3 | 83.5507 | 0 | 40.4604 | 0 | 6.4033 | 0 | 0 | 6.4033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0187 | 17.97% | 0 | 0 | 0 | 0% | 6.4033
5312 | 383 | 334 | 170 | 4.2312 | 31.5 | 192.7706 | 109.4674 | 0 | 83.7461 | 22.4896 | 0 | 0 | 22.4896 | 0 | 0 | 0 | 0 | 0 | 83.7461 | 0 | 308.5176 | 24.21% | 0 | 0 | 0 | 0% | 22.4896
5313 | 467 | 528 | 244 | 8.261 | 33.7 | 235.0492 | 144.321 | 0 | 114.4581 | 42.4122 | 0 | 0 | 42.4122 | 0 | 0 | 0 | 0 | 0 | 114.4581 | 0 | 417.1709 | 32.73% | 0 | 0 | 0 | 0% | 42.4122
5314 | 527 | 669 | 271 | 6.4476 | 34.6 | 265.2483 | 169.264 | 0 | 138.7563 | 67.8702 | 0 | 11.6351 | 56.2351 | 0 | 0 | 0 | 0 | 0 | 138.7563 | 0 | 548.8901 | 43.07% | 8.9241 | 0 | 9.2059 | 18.41% | 44.6
5315 | 653 | 832 | 261 | 4.4327 | 36.1 | 328.6663 | 215.0301 | 0 | 182.5693 | 95.8878 | 0.6939 | 25 | 70.1939 | 0 | 0 | 0 | 0 | 0 | 182.5693 | 0 | 722.2003 | 56.66% | 19.175 | 0 | 28.9863 | 57.97% | 44.5
5316 | 715 | 910 | 240 | 5.4401 | 37.4 | 359.8719 | 237.8327 | 0 | 203.5057 | 106.6 | 6.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 203.5057 | 0 | 915.3851 | 71.82% | 19.175 | 0 | 48.7668 | 97.53% | 43.4
5317 | 561 | 897 | 360 | 9.0669 | 38.4 | 282.3611 | 185.1865 | 0 | 152.2365 | 107.3 | 32.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 152.2365 | 0 | 1059.9008 | 83.16% | 0 | 0 | 48.7668 | 97.53% | 42.7
5318 | 737 | 892 | 223 | 12.0892 | 38.9 | 370.9449 | 237.663 | 0 | 199.6268 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 199.6268 | 0 | 1249.4034 | 98.03% | 0 | 0 | 48.7668 | 97.53% | 42.1
5319 | 699 | 791 | 218 | 12.8952 | 39.2 | 351.8189 | 0 | 217.3993 | 0 | 94.5642 | 26.4821 | 0 | 68.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.4034 | 98.03% | 0 | 0 | 48.7668 | 97.53% | 41.6
5320 | 605 | 625 | 209 | 11.8877 | 39.1 | 304.507 | 0 | 175.3794 | 0 | 61.6472 | 10.1736 | 0 | 51.4736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.4034 | 98.03% | 0 | 0 | 48.7668 | 97.53% | 41.3
5321 | 488 | 434 | 179 | 9.2684 | 38.9 | 245.6189 | 0 | 122.274 | 0 | 32.1766 | 0 | 0 | 32.1766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.4034 | 98.03% | 0 | 8.7234 | 39.7693 | 79.54% | 40.9
5322 | 318 | 232 | 125 | 10.0743 | 36.5 | 160.0549 | 0 | 59.5004 | 0 | 12.5946 | 0 | 0 | 12.5946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.4034 | 98.03% | 0 | 25 | 13.9834 | 27.97% | 37.5946
5323 | 72 | 59 | 46 | 11.2833 | 32.8 | 36.2389 | 0 | 0 | 0 | 2.3687 | 0 | 0 | 2.3687 | 0 | 0 | 0 | 68.3311 | 24.9737 | 0 | 68.3311 | 1186.7675 | 93.12% | 0 | 13.5576 | 0 | 0% | 40.9
5324 | 0 | 1 | 1 | 8.8654 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2179 | 38.4 | 0 | 99.2179 | 1091.1129 | 85.61% | 0 | 0 | 0 | 0% | 38.4
5325 | 0 | 0 | 0 | 6.0446 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0487 | 36.2 | 0 | 93.0487 | 1002.2222 | 78.64% | 0 | 0 | 0 | 0% | 36.2
5326 | 0 | 0 | 0 | 2.2164 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2199 | 34.1 | 0 | 87.2199 | 919.7438 | 72.16% | 0 | 0 | 0 | 0% | 34.1
5327 | 0 | 0 | 0 | 1.8134 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9021 | 32.3 | 0 | 82.9021 | 842.1569 | 66.08% | 0 | 0 | 0 | 0% | 32.3
5328 | 0 | 0 | 0 | 1.8134 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6518 | 31.3 | 0 | 80.6518 | 767.1008 | 60.19% | 0 | 0 | 0 | 0% | 31.3
5329 | 0 | 0 | 0 | 3.4253 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8134 | 30.6 | 0 | 78.8134 | 694.0396 | 54.46% | 0 | 0 | 0 | 0% | 30.6
5330 | 0 | 0 | 0 | 2.4178 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2471 | 30.3 | 0 | 78.2471 | 621.6169 | 48.77% | 0 | 0 | 0 | 0% | 30.3
5331 | 0 | 0 | 0 | 2.2164 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6178 | 30.5 | 0 | 78.6178 | 548.7551 | 43.06% | 0 | 0 | 0 | 0% | 30.5
5332 | 0 | 0 | 0 | 1.8134 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1649 | 29.9 | 0 | 77.1649 | 477.4416 | 37.46% | 0 | 0 | 0 | 0% | 29.9
5333 | 0 | 0 | 0 | 2.2164 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3478 | 30.8 | 0 | 79.3478 | 403.7479 | 31.68% | 0 | 0 | 0 | 0% | 30.8
5334 | 1 | 9 | 9 | 2.4178 | 24.6 | 0.50332 | 0 | 0.17747 | 0 | 0.063448 | 0 | 0 | 0.063448 | 0 | 0 | 0 | 84.6468 | 32.9366 | 0 | 84.6468 | 324.1351 | 25.43% | 0 | 0 | 0 | 0% | 33
5335 | 148 | 141 | 103 | 3.8283 | 25.9 | 74.491 | 0 | 35.9726 | 0 | 6.8516 | 0 | 0 | 6.8516 | 0 | 0 | 0 | 66.0343 | 24.7627 | 0 | 66.0343 | 263.5114 | 20.68% | 0 | 0 | 0 | 0% | 31.6143
5336 | 320 | 292 | 150 | 10.0743 | 27.3 | 161.0616 | 91.354 | 0 | 63.7387 | 19.8775 | 0 | 0 | 19.8775 | 0 | 0 | 0 | 0 | 0 | 63.7387 | 0 | 323.0056 | 25.34% | 0 | 0 | 0 | 0% | 19.8775
5337 | 549 | 522 | 189 | 10.4773 | 29.2 | 276.3212 | 169.5833 | 0 | 136.6199 | 48.3865 | 0 | 5.1433 | 43.2433 | 0 | 0 | 0 | 0 | 0 | 136.6199 | 0 | 450.5276 | 35.35% | 3.9449 | 0 | 4.07 | 8.14% | 38.1
5338 | 658 | 703 | 206 | 6.0446 | 31.7 | 331.1828 | 211.3284 | 0 | 178.2929 | 81.8656 | 0 | 21.3328 | 60.5328 | 0 | 0 | 0 | 0 | 0 | 178.2929 | 0 | 616.9474 | 48.41% | 16.3623 | 0 | 20.9513 | 41.9% | 39.2
5339 | 692 | 832 | 231 | 4.2312 | 33.5 | 348.2956 | 227.8758 | 0 | 194.6227 | 103.4765 | 6.9383 | 25 | 71.5383 | 0 | 0 | 0 | 0 | 0 | 194.6227 | 0 | 798.6096 | 62.66% | 19.175 | 0 | 40.7345 | 81.47% | 39.6
5340 | 654 | 859 | 247 | 4.2312 | 34.9 | 329.1696 | 217.5378 | 0 | 184.9523 | 109.3393 | 23.6109 | 11.7087 | 74.0196 | 0 | 0 | 0 | 0 | 0 | 184.9523 | 0 | 971.2455 | 76.21% | 8.9806 | 0 | 50 | 100% | 38.7
5341 | 709 | 901 | 230 | 8.8654 | 35.4 | 356.852 | 234.0638 | 0 | 198.053 | 112.1 | 37.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 198.053 | 0 | 1156.1096 | 90.71% | 0 | 0 | 50 | 100% | 37.9
5342 | 143 | 536 | 396 | 10.6788 | 33.4 | 71.9744 | 0 | 46.1155 | 0 | 49.3675 | 5.9837 | 0 | 43.3837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.1096 | 90.71% | 0 | 0 | 50 | 100% | 37.4
5343 | 164 | 473 | 335 | 8.4625 | 32.8 | 82.5441 | 0 | 51.0141 | 0 | 39.3271 | 1.0636 | 0 | 38.2636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.1096 | 90.71% | 0 | 0 | 50 | 100% | 37.2
5344 | 82 | 377 | 314 | 7.455 | 33 | 41.272 | 0 | 23.756 | 0 | 28.3563 | 0 | 0 | 28.3563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.1096 | 90.71% | 0 | 8.7437 | 40.9804 | 81.96% | 37.1
5345 | 43 | 260 | 233 | 6.8506 | 31.2 | 21.6426 | 0 | 10.7566 | 0 | 18.7827 | 0 | 0 | 18.7827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.1096 | 90.71% | 0 | 18.5173 | 21.8782 | 43.76% | 37.3
5346 | 207 | 237 | 172 | 6.0446 | 30.5 | 104.1867 | 0 | 38.5811 | 0 | 14.5474 | 0 | 0 | 14.5474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.1096 | 90.71% | 0 | 21.2088 | 0 | 0% | 35.7562
5347 | 55 | 63 | 53 | 4.0297 | 29.6 | 27.6825 | 0 | 0 | 0 | 2.7232 | 0 | 0 | 2.7232 | 0 | 0 | 0 | 95.0717 | 36.7768 | 0 | 95.0717 | 1065.0636 | 83.57% | 0 | 0 | 0 | 0% | 39.5
5348 | 0 | 0 | 0 | 2.6193 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.6191 | 37.2 | 0 | 95.6191 | 973.3185 | 76.37% | 0 | 0 | 0 | 0% | 37.2
5349 | 0 | 0 | 0 | 1.6119 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5459 | 34.8 | 0 | 89.5459 | 888.2782 | 69.7% | 0 | 0 | 0 | 0% | 34.8
5350 | 0 | 0 | 0 | 1.2089 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5795 | 32.9 | 0 | 84.5795 | 808.8324 | 63.46% | 0 | 0 | 0 | 0% | 32.9
5351 | 0 | 0 | 0 | 1.4104 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8497 | 31.4 | 0 | 80.8497 | 733.5369 | 57.55% | 0 | 0 | 0 | 0% | 31.4
5352 | 0 | 0 | 0 | 0.80595 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8134 | 30.6 | 0 | 78.8134 | 660.4641 | 51.82% | 0 | 0 | 0 | 0% | 30.6
5353 | 0 | 0 | 0 | 1.2089 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8398 | 30.2 | 0 | 77.8398 | 588.4477 | 46.17% | 0 | 0 | 0 | 0% | 30.2
5354 | 0 | 0 | 0 | 1.0074 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6703 | 30.6 | 0 | 78.6703 | 515.4828 | 40.45% | 0 | 0 | 0 | 0% | 30.6
5355 | 0 | 0 | 0 | 1.4104 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6098 | 32.6 | 0 | 83.6098 | 437.0192 | 34.29% | 0 | 0 | 0 | 0% | 32.6
5356 | 0 | 0 | 0 | 1.8134 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.552 | 34.7 | 0 | 88.552 | 352.8707 | 27.69% | 0 | 0 | 0 | 0% | 34.7
5357 | 0 | 0 | 0 | 2.8208 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.2328 | 21.2178 | 0 | 57.2328 | 300.7146 | 23.59% | 0 | 0 | 0 | 0% | 21.2178
5358 | 23 | 14 | 11 | 3.0223 | 22 | 11.5763 | 0 | 4.0565 | 0 | 0.17363 | 0 | 0 | 0.17363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300.7146 | 23.59% | 0 | 0 | 0 | 0% | 0.17363
5359 | 374 | 151 | 65 | 2.2164 | 24.6 | 188.2407 | 90.6421 | 0 | 66.9176 | 4.8897 | 0 | 0 | 4.8897 | 0 | 0 | 0 | 0 | 0 | 66.9176 | 0 | 363.3523 | 28.51% | 0 | 0 | 0 | 0% | 4.8897
5360 | 605 | 356 | 104 | 1.0074 | 28.2 | 304.507 | 172.5069 | 0 | 143.84 | 23.9944 | 0 | 0 | 23.9944 | 0 | 0 | 0 | 0 | 0 | 143.84 | 0 | 497.9924 | 39.07% | 0 | 0 | 0 | 0% | 23.9944
5361 | 708 | 571 | 150 | 2.8208 | 29.8 | 356.3487 | 218.5917 | 0 | 186.3225 | 50.0717 | 0 | 2.8358 | 47.2358 | 0 | 0 | 0 | 0 | 0 | 186.3225 | 0 | 672.3978 | 52.76% | 2.1751 | 0 | 2.2444 | 4.489% | 44.4
5362 | 734 | 756 | 207 | 5.2387 | 31.5 | 369.435 | 235.7154 | 0 | 201.5824 | 85.4672 | 0 | 20.2336 | 65.2336 | 0 | 0 | 0 | 0 | 0 | 201.5824 | 0 | 861.0871 | 67.56% | 15.5192 | 0 | 18.2582 | 36.52% | 45
5363 | 815 | 938 | 237 | 9.0669 | 32.5 | 410.2037 | 268.3831 | 0 | 229.7016 | 105.5 | 5.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 229.7016 | 0 | 1076.0972 | 84.43% | 19.175 | 0 | 38.0443 | 76.09% | 44.5
5364 | 447 | 806 | 390 | 10.4773 | 32.5 | 224.9829 | 148.6811 | 0 | 117.2569 | 98.256 | 12.2719 | 15.1061 | 70.878 | 0 | 0 | 0 | 0 | 0 | 117.2569 | 0 | 1185.8544 | 93.04% | 11.5864 | 0 | 50 | 100% | 43.5
5365 | 234 | 642 | 415 | 11.4848 | 32.4 | 117.7763 | 77.2587 | 0 | 49.2864 | 66.8901 | 11.9451 | 0 | 54.9451 | 0 | 0 | 0 | 0 | 0 | 49.2864 | 0 | 1231.9885 | 96.66% | 0 | 0 | 50 | 100% | 43
5366 | 30 | 398 | 364 | 11.8877 | 31 | 15.0995 | 0 | 9.675 | 0 | 30.6993 | 0 | 0 | 30.6993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.9885 | 96.66% | 0 | 11.8007 | 37.8251 | 75.65% | 42.5
5367 | 93 | 440 | 363 | 11.4848 | 30.6 | 46.8085 | 0 | 28.9332 | 0 | 34.9194 | 0 | 0 | 34.9194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.9885 | 96.66% | 0 | 7.1806 | 30.4167 | 60.83% | 42.1
5368 | 264 | 508 | 321 | 10.2758 | 30.2 | 132.8758 | 0 | 76.4364 | 0 | 41.3732 | 0 | 0 | 41.3732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.9885 | 96.66% | 0 | 0 | 30.4167 | 60.83% | 41.3732
5369 | 512 | 434 | 175 | 10.0743 | 29.6 | 257.6985 | 0 | 127.8705 | 0 | 34.0105 | 0 | 0 | 34.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.9885 | 96.66% | 0 | 6.9895 | 23.2052 | 46.41% | 41
5370 | 566 | 258 | 77 | 9.6714 | 28.8 | 284.8776 | 0 | 105.0797 | 0 | 12.9109 | 0 | 0 | 12.9109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.9885 | 96.66% | 0 | 22.4912 | 0 | 0% | 35.4021
5371 | 201 | 61 | 31 | 9.2684 | 27.1 | 101.1668 | 0 | 0 | 0 | 1.401 | 0 | 0 | 1.401 | 0 | 0 | 0 | 101.3198 | 39.599 | 0 | 101.3198 | 1133.7728 | 88.96% | 0 | 0 | 0 | 0% | 41
5372 | 0 | 0 | 0 | 9.6714 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.755 | 37.9 | 0 | 96.755 | 1040.6439 | 81.65% | 0 | 0 | 0 | 0% | 37.9
5373 | 0 | 0 | 0 | 8.0595 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6353 | 35.5 | 0 | 90.6353 | 954.2697 | 74.87% | 0 | 0 | 0 | 0% | 35.5
5374 | 0 | 0 | 0 | 5.8431 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4861 | 33.4 | 0 | 85.4861 | 873.722 | 68.55% | 0 | 0 | 0 | 0% | 33.4
5375 | 0 | 0 | 0 | 5.2387 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0775 | 32 | 0 | 82.0775 | 797.0026 | 62.53% | 0 | 0 | 0 | 0% | 32
5376 | 0 | 0 | 0 | 3.4253 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0933 | 31.2 | 0 | 80.0933 | 722.4725 | 56.69% | 0 | 0 | 0 | 0% | 31.2
5377 | 0 | 0 | 0 | 2.4178 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.227 | 30.9 | 0 | 79.227 | 648.8646 | 50.91% | 0 | 0 | 0 | 0% | 30.9
5378 | 0 | 0 | 0 | 2.2164 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9825 | 31.2 | 0 | 79.9825 | 574.4136 | 45.07% | 0 | 0 | 0 | 0% | 31.2
5379 | 0 | 0 | 0 | 2.0149 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5305 | 33.1 | 0 | 84.5305 | 494.8423 | 38.83% | 0 | 0 | 0 | 0% | 33.1
5380 | 0 | 0 | 0 | 3.0223 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5755 | 34.8 | 0 | 88.5755 | 410.4862 | 32.21% | 0 | 0 | 0 | 0% | 34.8
5381 | 0 | 0 | 0 | 3.0223 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4704 | 30.6382 | 0 | 78.4704 | 337.635 | 26.49% | 0 | 0 | 0 | 0% | 30.6382
5382 | 0 | 7 | 7 | 1.4104 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337.635 | 26.49% | 0 | 0 | 0 | 0% | 0
5383 | 20 | 78 | 72 | 1.4104 | 22.1 | 10.0663 | 0 | 4.8328 | 0 | 4.7472 | 0 | 0 | 4.7472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337.635 | 26.49% | 0 | 0 | 0 | 0% | 4.7472
5384 | 362 | 337 | 181 | 6.4476 | 24.9 | 182.2009 | 103.0894 | 0 | 76.5149 | 23.6379 | 0 | 0 | 23.6379 | 0 | 0 | 0 | 0 | 0 | 76.5149 | 0 | 409.5832 | 32.14% | 0 | 0 | 0 | 0% | 23.6379
5385 | 523 | 492 | 181 | 7.858 | 26.4 | 263.235 | 161.3925 | 0 | 130.3771 | 41.7394 | 0 | 0 | 41.7394 | 0 | 0 | 0 | 0 | 0 | 130.3771 | 0 | 532.179 | 41.76% | 0 | 0 | 0 | 0% | 41.7394
5386 | 800 | 734 | 140 | 10.2758 | 27.6 | 402.6539 | 256.8798 | 0 | 218.1189 | 87.7211 | 0 | 21.4105 | 66.3105 | 0 | 0 | 0 | 0 | 0 | 218.1189 | 0 | 737.2797 | 57.85% | 16.4219 | 0 | 16.9477 | 33.9% | 44.9
5387 | 828 | 863 | 156 | 11.6862 | 28.8 | 416.7468 | 272.6672 | 0 | 232.0834 | 105.7 | 5.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 232.0834 | 0 | 955.5116 | 74.97% | 19.175 | 0 | 36.7367 | 73.47% | 44.3
5388 | 762 | 900 | 196 | 13.7011 | 29.1 | 383.5278 | 253.451 | 0 | 212.9473 | 106.7 | 14.9442 | 16.7558 | 75 | 0 | 0 | 0 | 0 | 0 | 212.9473 | 0 | 1155.7494 | 90.68% | 12.8517 | 0 | 50 | 100% | 43.3
5389 | 689 | 970 | 323 | 14.7085 | 29.5 | 346.7857 | 227.5074 | 0 | 188.3194 | 107 | 32 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 188.3194 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43
5390 | 323 | 701 | 405 | 14.3056 | 29 | 162.5715 | 0 | 104.1725 | 0 | 79.7409 | 18.5704 | 0 | 61.1704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
5391 | 607 | 788 | 296 | 13.7011 | 29.1 | 305.5137 | 0 | 188.8737 | 0 | 98.0112 | 27.9056 | 0 | 70.1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.2
5392 | 520 | 625 | 271 | 12.4922 | 28.5 | 261.725 | 0 | 150.465 | 0 | 65.4336 | 11.9168 | 0 | 53.5168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.6
5393 | 371 | 373 | 193 | 12.0892 | 27.4 | 186.7308 | 0 | 92.5048 | 0 | 29.8065 | 0 | 0 | 29.8065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 11.3935 | 38.2434 | 76.49% | 41.2
5394 | 318 | 212 | 110 | 10.8803 | 26.5 | 160.0549 | 0 | 58.8052 | 0 | 11.9833 | 0 | 0 | 11.9833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 12.4462 | 24.89% | 36.9833
5395 | 55 | 43 | 34 | 9.2684 | 25 | 27.6825 | 0 | 0 | 0 | 1.7303 | 0 | 0 | 1.7303 | 0 | 0 | 0 | 71.6468 | 27.3076 | 0 | 71.6468 | 1208.5908 | 94.83% | 0 | 12.0622 | 1.3878e-15 | 2.776e-15% | 41.1
5396 | 0 | 0 | 0 | 8.4625 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.009 | 38.1 | 0 | 97.009 | 1115.0347 | 87.49% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 38.1
5397 | 0 | 0 | 0 | 7.858 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2403 | 35.8 | 0 | 91.2403 | 1027.9622 | 80.66% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 35.8
5398 | 0 | 0 | 0 | 6.8506 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8119 | 33.6 | 0 | 85.8119 | 947.0145 | 74.3% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 33.6
5399 | 0 | 0 | 0 | 6.8506 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1443 | 32.1 | 0 | 82.1443 | 870.1903 | 68.28% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 32.1
5400 | 0 | 0 | 0 | 5.8431 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2104 | 31.3 | 0 | 80.2104 | 795.5106 | 62.42% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 31.3
5401 | 0 | 0 | 0 | 5.6416 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9698 | 30.8 | 0 | 78.9698 | 722.1868 | 56.66% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 30.8
5402 | 0 | 0 | 0 | 5.4401 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9117 | 31.2 | 0 | 79.9117 | 647.8056 | 50.83% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 31.2
5403 | 0 | 0 | 0 | 4.2312 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2188 | 33 | 0 | 84.2188 | 568.5791 | 44.61% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 33
5404 | 0 | 0 | 0 | 3.6268 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7448 | 34.9 | 0 | 88.7448 | 483.9377 | 37.97% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 34.9
5405 | 0 | 0 | 0 | 1.4104 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4979 | 37.3 | 0 | 94.4979 | 392.5249 | 30.8% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 37.3
5406 | 19 | 13 | 11 | 2.8208 | 20 | 9.563 | 0 | 0 | 0 | 0.17777 | 0 | 0 | 0.17777 | 0 | 0 | 0 | 73.1559 | 28.3365 | 0 | 73.1559 | 325.0048 | 25.5% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 28.5142
5407 | 344 | 142 | 64 | 2.0149 | 22.1 | 173.1412 | 82.869 | 0 | 59.4375 | 4.8636 | 0 | 0 | 4.8636 | 0 | 0 | 0 | 0 | 0 | 59.4375 | 0 | 380.7723 | 29.88% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 4.8636
5408 | 597 | 345 | 99 | 2.2164 | 23.8 | 300.4805 | 169.7915 | 0 | 140.854 | 24.1128 | 0 | 0 | 24.1128 | 0 | 0 | 0 | 0 | 0 | 140.854 | 0 | 512.9296 | 40.25% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 24.1128
5409 | 744 | 550 | 110 | 3.4253 | 25.7 | 374.4681 | 229.4707 | 0 | 196.2971 | 49.0896 | 2.1448 | 0 | 46.9448 | 0 | 0 | 0 | 0 | 0 | 196.2971 | 0 | 697.1067 | 54.7% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 44.8
5410 | 820 | 726 | 116 | 3.4253 | 27.8 | 412.7203 | 263.2687 | 0 | 227.7387 | 81.9047 | 0 | 18.0024 | 63.9024 | 0 | 0 | 0 | 0 | 0 | 227.7387 | 0 | 910.784 | 71.46% | 13.8078 | 0 | 14.252 | 28.5% | 45.9
5411 | 842 | 854 | 134 | 3.6268 | 29.3 | 423.7932 | 277.2803 | 0 | 240.8423 | 104.4 | 4.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 240.8423 | 0 | 1136.7559 | 89.19% | 19.175 | 0 | 34.0439 | 68.09% | 45.6
5412 | 778 | 903 | 185 | 4.0297 | 30.6 | 391.5809 | 258.7672 | 0 | 223.3691 | 105.3 | 10.1452 | 20.1548 | 75 | 0 | 0 | 0 | 0 | 0 | 223.3691 | 0 | 1274.5104 | 100% | 15.4587 | 0 | 50 | 100% | 44.7
5413 | 362 | 593 | 251 | 5.6416 | 31.1 | 182.2009 | 0 | 119.545 | 0 | 62.5094 | 9.1547 | 0 | 53.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.2
5414 | 851 | 940 | 181 | 8.261 | 32.2 | 428.3231 | 0 | 274.4745 | 0 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.9
5415 | 809 | 795 | 147 | 9.2684 | 32.3 | 407.1838 | 0 | 251.7694 | 0 | 99.3079 | 27.954 | 0 | 71.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.4
5416 | 767 | 634 | 121 | 11.6862 | 32.5 | 386.0444 | 0 | 221.8004 | 0 | 68.2418 | 12.7209 | 0 | 55.5209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.8
5417 | 680 | 443 | 102 | 12.6937 | 31.9 | 342.2558 | 0 | 169.2728 | 0 | 34.9229 | 0 | 0 | 34.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 7.1771 | 42.5931 | 85.19% | 42.1
5418 | 522 | 237 | 74 | 11.2833 | 30.6 | 262.7317 | 0 | 96.1464 | 0 | 12.0076 | 0 | 0 | 12.0076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 16.7923 | 33.58% | 37.0076
5419 | 191 | 57 | 30 | 5.4401 | 29.1 | 96.1336 | 0 | 0 | 0 | 1.3031 | 0 | 0 | 1.3031 | 0 | 0 | 0 | 65.1386 | 24.0254 | 0 | 65.1386 | 1214.8951 | 95.32% | 0 | 16.2715 | 0 | 0% | 41.6
5420 | 0 | 0 | 0 | 7.2535 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8813 | 38.7 | 0 | 98.8813 | 1119.4045 | 87.83% | 0 | 0 | 0 | 0% | 38.7
5421 | 0 | 0 | 0 | 5.6416 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2257 | 36.5 | 0 | 93.2257 | 1030.1963 | 80.83% | 0 | 0 | 0 | 0% | 36.5
5422 | 0 | 0 | 0 | 1.6119 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.735 | 34.3 | 0 | 87.735 | 947.1 | 74.31% | 0 | 0 | 0 | 0% | 34.3
5423 | 0 | 0 | 0 | 1.4104 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5425 | 32.6 | 0 | 83.5425 | 868.7463 | 68.16% | 0 | 0 | 0 | 0% | 32.6
5424 | 0 | 0 | 0 | 0.60446 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0777 | 31.6 | 0 | 81.0777 | 793.1334 | 62.23% | 0 | 0 | 0 | 0% | 31.6
5425 | 0 | 0 | 0 | 1.6119 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3823 | 30.9 | 0 | 79.3823 | 719.3892 | 56.44% | 0 | 0 | 0 | 0% | 30.9
5426 | 0 | 0 | 0 | 2.0149 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6975 | 30.7 | 0 | 78.6975 | 646.3539 | 50.71% | 0 | 0 | 0 | 0% | 30.7
5427 | 0 | 0 | 0 | 1.8134 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1835 | 30.9 | 0 | 79.1835 | 572.7707 | 44.94% | 0 | 0 | 0 | 0% | 30.9
5428 | 0 | 0 | 0 | 2.8208 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8454 | 30.8 | 0 | 78.8454 | 499.5307 | 39.19% | 0 | 0 | 0 | 0% | 30.8
5429 | 0 | 0 | 0 | 2.4178 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0481 | 31.7 | 0 | 81.0481 | 423.8374 | 33.25% | 0 | 0 | 0 | 0% | 31.7
5430 | 39 | 14 | 10 | 1.6119 | 20.5 | 19.6294 | 0 | 0 | 0 | 0.10247 | 0 | 0 | 0.10247 | 0 | 0 | 0 | 86.0684 | 33.7975 | 0 | 86.0684 | 342.371 | 26.86% | 0 | 0 | 0 | 0% | 33.9
5431 | 461 | 150 | 49 | 2.6193 | 22.5 | 232.0293 | 110.7035 | 0 | 85.3679 | 4.1946 | 0 | 0 | 4.1946 | 0 | 0 | 0 | 0 | 0 | 85.3679 | 0 | 422.2365 | 33.13% | 0 | 0 | 0 | 0% | 4.1946
5432 | 690 | 356 | 73 | 3.6268 | 26.3 | 347.289 | 195.9784 | 0 | 164.8852 | 24.6154 | 0 | 0 | 24.6154 | 0 | 0 | 0 | 0 | 0 | 164.8852 | 0 | 576.4941 | 45.23% | 0 | 0 | 0 | 0% | 24.6154
5433 | 795 | 558 | 89 | 4.2312 | 29.1 | 400.1373 | 245.0676 | 0 | 210.5607 | 55.9188 | 0 | 8.4594 | 47.4594 | 0 | 0 | 0 | 0 | 0 | 210.5607 | 0 | 773.4832 | 60.69% | 6.4884 | 0 | 6.6981 | 13.4% | 39
5434 | 846 | 728 | 100 | 2.8208 | 31.4 | 425.8065 | 271.5803 | 0 | 235.753 | 85.6975 | 0 | 22.7987 | 62.8987 | 0 | 0 | 0 | 0 | 0 | 235.753 | 0 | 994.0407 | 77.99% | 17.4866 | 0 | 24.7499 | 49.5% | 40.1
5435 | 876 | 854 | 107 | 3.2238 | 32.9 | 440.906 | 288.4795 | 0 | 251.591 | 108.5258 | 9.1129 | 25 | 74.4129 | 0 | 0 | 0 | 0 | 0 | 251.591 | 0 | 1229.4154 | 96.46% | 19.175 | 0 | 44.5447 | 89.09% | 40.3
5436 | 892 | 928 | 110 | 5.8431 | 34 | 448.9591 | 0 | 296.6777 | 0 | 110.4 | 28.5101 | 6.8899 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.4154 | 96.46% | 5.2845 | 0 | 50 | 100% | 39.6
5437 | 891 | 940 | 112 | 10.6788 | 34.1 | 448.4558 | 0 | 294.272 | 0 | 111.1 | 36.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.4154 | 96.46% | 0 | 0 | 50 | 100% | 38.9
5438 | 873 | 890 | 113 | 11.4848 | 33.8 | 439.3961 | 0 | 281.5855 | 0 | 111.5 | 36.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.4154 | 96.46% | 0 | 0 | 50 | 100% | 38.5
5439 | 840 | 784 | 111 | 10.8803 | 34.3 | 422.7866 | 0 | 261.4095 | 0 | 101.9049 | 31.8525 | 0 | 70.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.4154 | 96.46% | 0 | 0 | 50 | 100% | 38.2
5440 | 788 | 629 | 103 | 10.8803 | 33.6 | 396.6141 | 0 | 227.7336 | 0 | 72.2076 | 17.2038 | 0 | 55.0038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.4154 | 96.46% | 0 | 0 | 50 | 100% | 37.8
5441 | 705 | 441 | 90 | 10.2758 | 33.4 | 354.8388 | 0 | 175.2076 | 0 | 34.6213 | 0 | 0 | 34.6213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.4154 | 96.46% | 0 | 3.3787 | 46.5126 | 93.03% | 38
5442 | 549 | 236 | 66 | 8.0595 | 32 | 276.3212 | 0 | 100.7155 | 0 | 11.6126 | 0 | 0 | 11.6126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.4154 | 96.46% | 0 | 25 | 20.7083 | 41.42% | 36.6126
5443 | 206 | 56 | 27 | 3.2238 | 30.1 | 103.6834 | 0 | 0 | 0 | 1.1038 | 0 | 0 | 1.1038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.4154 | 96.46% | 0 | 20.063 | 0 | 0% | 21.1668
5444 | 0 | 0 | 0 | 1.8134 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3494 | 37.5 | 0 | 96.3494 | 1136.819 | 89.2% | 0 | 0 | 0 | 0% | 37.5
5445 | 0 | 0 | 0 | 5.8431 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8049 | 35.4 | 0 | 90.8049 | 1050.3067 | 82.41% | 0 | 0 | 0 | 0% | 35.4
5446 | 0 | 0 | 0 | 3.8283 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6064 | 33.4 | 0 | 85.6064 | 969.6345 | 76.08% | 0 | 0 | 0 | 0% | 33.4
5447 | 0 | 0 | 0 | 1.8134 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9018 | 31.9 | 0 | 81.9018 | 893.1138 | 70.08% | 0 | 0 | 0 | 0% | 31.9
5448 | 0 | 0 | 0 | 3.2238 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6569 | 31 | 0 | 79.6569 | 819.0664 | 64.27% | 0 | 0 | 0 | 0% | 31
5449 | 0 | 0 | 0 | 2.2164 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7179 | 30.6 | 0 | 78.7179 | 746.0496 | 58.54% | 0 | 0 | 0 | 0% | 30.6
5450 | 0 | 0 | 0 | 2.2164 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3504 | 30.9 | 0 | 79.3504 | 672.3077 | 52.75% | 0 | 0 | 0 | 0% | 30.9
5451 | 0 | 0 | 0 | 4.2312 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1102 | 32.4 | 0 | 83.1102 | 594.3856 | 46.64% | 0 | 0 | 0 | 0% | 32.4
5452 | 0 | 0 | 0 | 3.8283 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4016 | 33.9 | 0 | 86.4016 | 512.6406 | 40.22% | 0 | 0 | 0 | 0% | 33.9
5453 | 0 | 0 | 0 | 4.2312 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8433 | 36.1 | 0 | 91.8433 | 424.6029 | 33.31% | 0 | 0 | 0 | 0% | 36.1
5454 | 35 | 12 | 9 | 3.6268 | 21.5 | 17.6161 | 0 | 0 | 0 | 0.053616 | 0 | 0 | 0.053616 | 0 | 0 | 0 | 92.3527 | 36.3485 | 0 | 92.3527 | 335.8464 | 26.35% | 0 | 0 | 0 | 0% | 36.4021
5455 | 423 | 144 | 51 | 3.8283 | 23.2 | 212.9033 | 101.2482 | 0 | 76.0273 | 4.2889 | 0 | 0 | 4.2889 | 0 | 0 | 0 | 0 | 0 | 76.0273 | 0 | 407.3109 | 31.96% | 0 | 0 | 0 | 0% | 4.2889
5456 | 657 | 347 | 79 | 7.052 | 26.1 | 330.6795 | 186.3475 | 0 | 154.2143 | 24.3973 | 0 | 0 | 24.3973 | 0 | 0 | 0 | 0 | 0 | 154.2143 | 0 | 552.2699 | 43.33% | 0 | 0 | 0 | 0% | 24.3973
5457 | 782 | 550 | 93 | 8.0595 | 28.3 | 393.5942 | 240.9249 | 0 | 204.6748 | 52.3269 | 0 | 4.3135 | 48.0135 | 0 | 0 | 0 | 0 | 0 | 204.6748 | 0 | 744.661 | 58.43% | 3.3084 | 0 | 3.4158 | 6.832% | 43.7
5458 | 846 | 725 | 102 | 7.6565 | 30.2 | 425.8065 | 271.5426 | 0 | 233.4461 | 85.2253 | 0 | 20.0627 | 65.1627 | 0 | 0 | 0 | 0 | 0 | 233.4461 | 0 | 964.0967 | 75.64% | 15.3881 | 0 | 19.3036 | 38.61% | 45.1
5459 | 877 | 853 | 109 | 5.6416 | 31.8 | 441.4093 | 288.811 | 0 | 250.9693 | 104.7 | 4.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 250.9693 | 0 | 1200.0039 | 94.15% | 19.175 | 0 | 39.1012 | 78.2% | 45.3
5460 | 889 | 927 | 115 | 5.0372 | 33.1 | 447.4492 | 295.6731 | 0 | 257.7876 | 105.3 | 16.5374 | 13.7626 | 75 | 0 | 0 | 0 | 0 | 0 | 257.7876 | 0 | 1274.5104 | 100% | 10.556 | 0 | 50 | 100% | 44.7
5461 | 887 | 937 | 116 | 6.6491 | 34.1 | 446.4425 | 0 | 292.9845 | 0 | 105.6 | 30.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.4
5462 | 871 | 887 | 116 | 9.0669 | 34.7 | 438.3894 | 0 | 280.9566 | 0 | 106 | 31 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44
5463 | 845 | 782 | 110 | 9.2684 | 34.6 | 425.3032 | 0 | 262.9231 | 0 | 96.6037 | 26.6019 | 0 | 70.0019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.4
5464 | 798 | 629 | 101 | 8.6639 | 34.5 | 401.6473 | 0 | 230.4818 | 0 | 67.0988 | 12.0994 | 0 | 54.9994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.9
5465 | 701 | 435 | 90 | 7.2535 | 33.8 | 352.8255 | 0 | 173.9263 | 0 | 34.2583 | 0 | 0 | 34.2583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.1417 | 41.5952 | 83.19% | 42.4
5466 | 538 | 231 | 67 | 8.261 | 33.4 | 270.7848 | 0 | 98.3006 | 0 | 11.4731 | 0 | 0 | 11.4731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.7868 | 31.57% | 36.4731
5467 | 176 | 51 | 27 | 6.2461 | 31.1 | 88.5839 | 0 | 0 | 0 | 1.0781 | 0 | 0 | 1.0781 | 0 | 0 | 0 | 69.1053 | 25.5292 | 0 | 69.1053 | 1211.0936 | 95.02% | 0 | 15.2928 | 0 | 0% | 41.9
5468 | 1 | 0 | 0 | 6.8506 | 27.4 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6577 | 39.3 | 0 | 100.6577 | 1113.6452 | 87.38% | 0 | 0 | 0 | 0% | 39.3
5469 | 0 | 0 | 0 | 6.4476 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.609 | 37 | 0 | 94.609 | 1022.928 | 80.26% | 0 | 0 | 0 | 0% | 37
5470 | 0 | 0 | 0 | 3.8283 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7474 | 34.7 | 0 | 88.7474 | 938.6795 | 73.65% | 0 | 0 | 0 | 0% | 34.7
5471 | 0 | 0 | 0 | 3.4253 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2825 | 32.9 | 0 | 84.2825 | 859.498 | 67.44% | 0 | 0 | 0 | 0% | 32.9
5472 | 0 | 0 | 0 | 2.4178 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0777 | 31.6 | 0 | 81.0777 | 783.8892 | 61.51% | 0 | 0 | 0 | 0% | 31.6
5473 | 0 | 0 | 0 | 0.60446 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3504 | 30.9 | 0 | 79.3504 | 710.1786 | 55.72% | 0 | 0 | 0 | 0% | 30.9
5474 | 0 | 0 | 0 | 0.60446 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0136 | 30.8 | 0 | 79.0136 | 636.8115 | 49.97% | 0 | 0 | 0 | 0% | 30.8
5475 | 0 | 0 | 0 | 1.4104 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4108 | 31.4 | 0 | 80.4108 | 561.8758 | 44.09% | 0 | 0 | 0 | 0% | 31.4
5476 | 0 | 0 | 0 | 1.4104 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3969 | 31.4 | 0 | 80.3969 | 486.9393 | 38.21% | 0 | 0 | 0 | 0% | 31.4
5477 | 0 | 0 | 0 | 2.0149 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9504 | 32.9 | 0 | 83.9504 | 407.9903 | 32.01% | 0 | 0 | 0 | 0% | 32.9
5478 | 33 | 12 | 8 | 2.2164 | 21.2 | 16.6095 | 0 | 0 | 0 | 0.037761 | 0 | 0 | 0.037761 | 0 | 0 | 0 | 91.6261 | 36.0622 | 0 | 91.6261 | 320.0605 | 25.11% | 0 | 0 | 0 | 0% | 36.1
5479 | 438 | 143 | 49 | 2.6193 | 24.8 | 220.453 | 104.4882 | 0 | 79.4746 | 4.1822 | 0 | 0 | 4.1822 | 0 | 0 | 0 | 88.4773 | 34.5178 | 79.4746 | 88.4773 | 310.6009 | 24.37% | 0 | 0 | 0 | 0% | 38.7
5480 | 674 | 347 | 75 | 2.6193 | 27.7 | 339.2359 | 190.8968 | 0 | 160.4596 | 24.2555 | 0 | 0 | 24.2555 | 0 | 0 | 0 | 0 | 0 | 160.4596 | 0 | 461.2767 | 36.19% | 0 | 0 | 0 | 0% | 24.2555
5481 | 787 | 550 | 91 | 2.2164 | 30.9 | 396.1108 | 242.3246 | 0 | 208.6803 | 51.3832 | 0 | 4.7416 | 46.6416 | 0 | 0 | 0 | 0 | 0 | 208.6803 | 0 | 657.2329 | 51.57% | 3.6368 | 0 | 3.7555 | 7.511% | 41.9
5482 | 857 | 727 | 97 | 2.6193 | 33.1 | 431.343 | 275.0333 | 0 | 239.0749 | 83.0616 | 0 | 19.9808 | 63.0808 | 0 | 0 | 0 | 0 | 0 | 239.0749 | 0 | 881.7305 | 69.18% | 15.3253 | 0 | 19.5807 | 39.16% | 43.1
5483 | 889 | 853 | 100 | 3.4253 | 34.8 | 447.4492 | 292.7647 | 0 | 255.6156 | 106.1339 | 6.4669 | 25 | 74.6669 | 0 | 0 | 0 | 0 | 0 | 255.6156 | 0 | 1121.7603 | 88.01% | 19.175 | 0 | 39.3812 | 78.76% | 43.2
5484 | 903 | 925 | 101 | 3.6268 | 36.2 | 454.4956 | 300.3224 | 0 | 262.5684 | 107.5 | 19.0928 | 13.4072 | 75 | 0 | 0 | 0 | 0 | 0 | 262.5684 | 0 | 1274.5104 | 100% | 10.2833 | 0 | 50 | 100% | 42.5
5485 | 907 | 939 | 101 | 5.2387 | 37 | 456.5089 | 0 | 299.6262 | 0 | 108.2 | 33.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
5486 | 906 | 896 | 96 | 9.6714 | 37.3 | 456.0056 | 0 | 292.2644 | 0 | 108.6 | 33.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.4
5487 | 884 | 792 | 91 | 10.8803 | 37.4 | 444.9326 | 0 | 275.0139 | 0 | 100.8151 | 29.9575 | 0 | 70.8575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.9
5488 | 832 | 634 | 86 | 11.2833 | 36.8 | 418.7601 | 0 | 240.1534 | 0 | 70.3038 | 14.9519 | 0 | 55.3519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.4
5489 | 744 | 441 | 77 | 11.2833 | 36.1 | 374.4681 | 0 | 184.2898 | 0 | 34.8271 | 0 | 0 | 34.8271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.4729 | 44.3494 | 88.7% | 40.3
5490 | 576 | 233 | 59 | 9.4699 | 34.6 | 289.9108 | 0 | 104.8175 | 0 | 11.2459 | 0 | 0 | 11.2459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.5374 | 37.07% | 36.2459
5491 | 215 | 53 | 24 | 6.4476 | 33 | 108.2132 | 0 | 0 | 0 | 0.92132 | 0 | 0 | 0.92132 | 0 | 0 | 0 | 60.5131 | 21.5241 | 0 | 60.5131 | 1219.4331 | 95.68% | 0 | 17.9546 | 0 | 0% | 40.4
5492 | 0 | 0 | 0 | 4.2312 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5845 | 37.8 | 0 | 97.5845 | 1125.5871 | 88.32% | 0 | 0 | 0 | 0% | 37.8
5493 | 0 | 0 | 0 | 1.8134 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7322 | 35.6 | 0 | 91.7322 | 1038.17 | 81.46% | 0 | 0 | 0 | 0% | 35.6
5494 | 0 | 0 | 0 | 3.4253 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1142 | 33.4 | 0 | 86.1142 | 957.0667 | 75.09% | 0 | 0 | 0 | 0% | 33.4
5495 | 0 | 0 | 0 | 1.2089 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9936 | 31.8 | 0 | 81.9936 | 880.5491 | 69.09% | 0 | 0 | 0 | 0% | 31.8
5496 | 0 | 0 | 0 | 0.40297 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1732 | 30.7 | 0 | 79.1732 | 807.1207 | 63.33% | 0 | 0 | 0 | 0% | 30.7
5497 | 0 | 0 | 0 | 1.0074 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.824 | 30.2 | 0 | 77.824 | 735.1399 | 57.68% | 0 | 0 | 0 | 0% | 30.2
5498 | 0 | 0 | 0 | 2.4178 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3681 | 30 | 0 | 77.3681 | 663.6519 | 52.07% | 0 | 0 | 0 | 0% | 30
5499 | 0 | 0 | 0 | 2.2164 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0868 | 29.9 | 0 | 77.0868 | 592.4223 | 46.48% | 0 | 0 | 0 | 0% | 29.9
5500 | 0 | 0 | 0 | 2.2164 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0053 | 29.4 | 0 | 76.0053 | 522.2287 | 40.97% | 0 | 0 | 0 | 0% | 29.4
5501 | 0 | 0 | 0 | 2.4178 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.036 | 30.3 | 0 | 78.036 | 449.9615 | 35.3% | 0 | 0 | 0 | 0% | 30.3
5502 | 44 | 12 | 8 | 3.4253 | 23 | 22.146 | 0 | 0 | 0 | 0.034395 | 0 | 0 | 0.034395 | 0 | 0 | 0 | 83.2184 | 32.4656 | 0 | 83.2184 | 371.9081 | 29.18% | 0 | 0 | 0 | 0% | 32.5
5503 | 504 | 148 | 42 | 2.0149 | 26.5 | 253.672 | 119.82 | 0 | 94.278 | 3.832 | 0 | 0 | 3.832 | 0 | 0 | 0 | 80.2756 | 30.968 | 94.278 | 80.2756 | 385.029 | 30.21% | 0 | 0 | 0 | 0% | 34.8
5504 | 707 | 354 | 71 | 2.6193 | 30.4 | 355.8454 | 199.9496 | 0 | 168.9851 | 24.8045 | 0 | 0 | 24.8045 | 0 | 0 | 0 | 0 | 0 | 168.9851 | 0 | 542.3067 | 42.55% | 0 | 0 | 0 | 0% | 24.8045
5505 | 800 | 556 | 90 | 6.2461 | 29.7 | 402.6539 | 246.1799 | 0 | 210.6203 | 58.5871 | 0 | 10.1435 | 48.4435 | 0 | 0 | 0 | 0 | 0 | 210.6203 | 0 | 738.335 | 57.93% | 7.7801 | 0 | 8.035 | 16.07% | 38.3
5506 | 848 | 726 | 104 | 6.8506 | 30.7 | 426.8131 | 272.1038 | 0 | 234.4587 | 91.3245 | 0.91223 | 25 | 65.4122 | 0 | 0 | 0 | 0 | 0 | 234.4587 | 0 | 956.5501 | 75.05% | 19.175 | 0 | 27.8384 | 55.68% | 39.5
5507 | 887 | 856 | 106 | 6.2461 | 33.2 | 446.4425 | 292.1076 | 0 | 253.7731 | 109.7 | 9.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 253.7731 | 0 | 1192.7415 | 93.58% | 19.175 | 0 | 47.6419 | 95.28% | 40.3
5508 | 913 | 931 | 100 | 7.6565 | 34.8 | 459.5288 | 214.5931 | 89.0478 | 186.3527 | 110.5 | 32.5231 | 2.9769 | 75 | 0 | 0 | 0 | 0 | 0 | 186.3527 | 0 | 1274.5104 | 100% | 2.2833 | 0 | 50 | 100% | 39.5
5509 | 924 | 946 | 96 | 10.6788 | 35.9 | 465.0653 | 0 | 305.2794 | 0 | 111.1 | 36.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.9
5510 | 924 | 906 | 92 | 14.1041 | 36.6 | 465.0653 | 0 | 298.0902 | 0 | 111.6 | 36.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.4
5511 | 896 | 799 | 90 | 12.8952 | 36.6 | 450.9724 | 0 | 278.7026 | 0 | 106.3085 | 34.1043 | 0 | 72.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.1
5512 | 799 | 626 | 101 | 13.9026 | 36.2 | 402.1506 | 0 | 230.485 | 0 | 72.8026 | 17.4513 | 0 | 55.3513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.9
5513 | 701 | 430 | 89 | 13.2981 | 35.3 | 352.8255 | 0 | 173.3505 | 0 | 34.287 | 0 | 0 | 34.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 3.813 | 46.0626 | 92.13% | 38.1
5514 | 525 | 222 | 64 | 10.8803 | 33.9 | 264.2416 | 0 | 95.1473 | 0 | 11.027 | 0 | 0 | 11.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 20.247 | 40.49% | 36.027
5515 | 177 | 48 | 25 | 9.6714 | 31.4 | 89.0872 | 0 | 0 | 0 | 0.9551 | 0 | 0 | 0.9551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 19.6075 | 0 | 0% | 20.5626
5516 | 0 | 0 | 0 | 6.0446 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4365 | 37.8 | 0 | 97.4365 | 1180.7962 | 92.65% | 0 | 0 | 0 | 0% | 37.8
5517 | 0 | 0 | 0 | 2.2164 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5471 | 35.6 | 0 | 91.5471 | 1093.5459 | 85.8% | 0 | 0 | 0 | 0% | 35.6
5518 | 0 | 0 | 0 | 1.6119 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6934 | 33.3 | 0 | 85.6934 | 1012.8777 | 79.47% | 0 | 0 | 0 | 0% | 33.3
5519 | 0 | 0 | 0 | 1.0074 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9498 | 31.8 | 0 | 81.9498 | 936.3933 | 73.47% | 0 | 0 | 0 | 0% | 31.8
5520 | 0 | 0 | 0 | 1.4104 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7373 | 31 | 0 | 79.7373 | 862.3068 | 67.66% | 0 | 0 | 0 | 0% | 31
5521 | 0 | 0 | 0 | 0.20149 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8972 | 30.7 | 0 | 78.8972 | 789.1171 | 61.92% | 0 | 0 | 0 | 0% | 30.7
5522 | 0 | 0 | 0 | 2.0149 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9966 | 31.2 | 0 | 79.9966 | 714.6825 | 56.08% | 0 | 0 | 0 | 0% | 31.2
5523 | 0 | 0 | 0 | 2.6193 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1207 | 33.7 | 0 | 86.1207 | 633.3638 | 49.69% | 0 | 0 | 0 | 0% | 33.7
5524 | 0 | 0 | 0 | 2.2164 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9167 | 36.1 | 0 | 91.9167 | 545.3891 | 42.79% | 0 | 0 | 0 | 0% | 36.1
5525 | 0 | 0 | 0 | 2.8208 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1985 | 39.1 | 0 | 99.1985 | 448.8698 | 35.22% | 0 | 0 | 0 | 0% | 39.1
5526 | 39 | 10 | 7 | 4.2312 | 23.7 | 19.6294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9484 | 42.2 | 0 | 106.9484 | 343.5068 | 26.95% | 0 | 0 | 0 | 0% | 42.2
5527 | 474 | 142 | 43 | 4.0297 | 26 | 238.5724 | 112.2903 | 0 | 86.463 | 3.8926 | 0 | 0 | 3.8926 | 0 | 0 | 0 | 103.0603 | 40.4074 | 86.463 | 103.0603 | 324.8626 | 25.49% | 0 | 0 | 0 | 0% | 44.3
5528 | 720 | 350 | 64 | 1.8134 | 29.2 | 362.3885 | 203.3188 | 0 | 172.4198 | 24.7253 | 0 | 0 | 24.7253 | 0 | 0 | 0 | 58.1373 | 20.9747 | 172.4198 | 58.1373 | 435.3288 | 34.16% | 0 | 0 | 0 | 0% | 45.7
5529 | 834 | 556 | 74 | 1.4104 | 32.8 | 419.7667 | 256.4842 | 0 | 222.0789 | 46.9844 | 0 | 0 | 46.9844 | 0 | 0 | 0 | 0 | 0 | 222.0789 | 0 | 645.2138 | 50.62% | 0 | 0 | 0 | 0% | 46.9844
5530 | 885 | 729 | 83 | 3.8283 | 34.6 | 445.4359 | 283.9316 | 0 | 247.1147 | 80.2777 | 0 | 16.0388 | 64.2388 | 0 | 0 | 0 | 0 | 0 | 247.1147 | 0 | 878.76 | 68.95% | 12.3018 | 0 | 12.7068 | 25.41% | 48.2
5531 | 905 | 851 | 90 | 4.6342 | 35.6 | 455.5022 | 298.0366 | 0 | 260.1424 | 102 | 2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 260.1424 | 0 | 1124.6186 | 88.24% | 19.175 | 0 | 32.5131 | 65.03% | 48
5532 | 906 | 917 | 95 | 7.455 | 36.1 | 456.0056 | 241.7418 | 59.5638 | 209.9323 | 103 | 5.9277 | 22.0723 | 75 | 0 | 0 | 0 | 0 | 0 | 209.9323 | 0 | 1274.5104 | 100% | 16.9295 | 0 | 50 | 100% | 47
5533 | 944 | 952 | 87 | 10.2758 | 36.5 | 475.1316 | 0 | 311.9265 | 0 | 103.6 | 28.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.4
5534 | 955 | 912 | 77 | 10.8803 | 37.1 | 480.6681 | 0 | 308.112 | 0 | 104.1 | 29.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.9
5535 | 940 | 809 | 72 | 10.6788 | 37.4 | 473.1183 | 0 | 292.3424 | 0 | 101.5541 | 28.327 | 0 | 73.227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.9
5536 | 908 | 656 | 66 | 10.8803 | 35.9 | 457.0122 | 0 | 261.7645 | 0 | 72.2294 | 14.0647 | 0 | 58.1647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.1
5537 | 768 | 439 | 70 | 10.8803 | 33.8 | 386.5478 | 0 | 189.6026 | 0 | 35.4191 | 0 | 0 | 35.4191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.3809 | 41.3445 | 82.69% | 43.8
5538 | 578 | 224 | 55 | 10.4773 | 32.2 | 290.9175 | 0 | 104.3225 | 0 | 11.0072 | 0 | 0 | 11.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.5248 | 31.05% | 36.0072
5539 | 189 | 46 | 22 | 10.0743 | 29.1 | 95.127 | 0 | 0 | 0 | 0.79358 | 0 | 0 | 0.79358 | 0 | 0 | 0 | 72.2453 | 27.1739 | 0 | 72.2453 | 1208.0874 | 94.79% | 0 | 15.0325 | 0 | 0% | 43
5540 | 0 | 0 | 0 | 8.4625 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.0058 | 39.9 | 0 | 102.0058 | 1109.1236 | 87.02% | 0 | 0 | 0 | 0% | 39.9
5541 | 0 | 0 | 0 | 10.0743 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4021 | 37.4 | 0 | 95.4021 | 1017.5302 | 79.84% | 0 | 0 | 0 | 0% | 37.4
5542 | 0 | 0 | 0 | 8.6639 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5674 | 35.1 | 0 | 89.5674 | 932.3529 | 73.15% | 0 | 0 | 0 | 0% | 35.1
5543 | 0 | 0 | 0 | 8.261 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8635 | 33.6 | 0 | 85.8635 | 851.3892 | 66.8% | 0 | 0 | 0 | 0% | 33.6
5544 | 0 | 0 | 0 | 4.4327 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0726 | 32.9 | 0 | 84.0726 | 772.4261 | 60.61% | 0 | 0 | 0 | 0% | 32.9
5545 | 0 | 0 | 0 | 4.8357 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0841 | 32.5 | 0 | 83.0841 | 694.561 | 54.5% | 0 | 0 | 0 | 0% | 32.5
5546 | 0 | 0 | 0 | 4.6342 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5177 | 32.7 | 0 | 83.5177 | 616.186 | 48.35% | 0 | 0 | 0 | 0% | 32.7
5547 | 0 | 0 | 0 | 3.6268 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6573 | 34.9 | 0 | 88.6573 | 531.6051 | 41.71% | 0 | 0 | 0 | 0% | 34.9
5548 | 0 | 0 | 0 | 3.2238 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1846 | 37.2 | 0 | 94.1846 | 440.5428 | 34.57% | 0 | 0 | 0 | 0% | 37.2
5549 | 0 | 0 | 0 | 3.6268 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.8185 | 39.6 | 0 | 99.8185 | 342.5926 | 26.88% | 0 | 0 | 0 | 0% | 39.6
5550 | 40 | 10 | 7 | 4.0297 | 20 | 20.1327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7547 | 42.4 | 0 | 106.7547 | 236.6669 | 18.57% | 0 | 0 | 0 | 0% | 42.4
5551 | 450 | 140 | 48 | 3.4253 | 22 | 226.4928 | 106.2189 | 0 | 80.8121 | 4.3297 | 0 | 0 | 4.3297 | 0 | 0 | 0 | 101.1806 | 39.9703 | 80.8121 | 101.1806 | 214.3583 | 16.82% | 0 | 0 | 0 | 0% | 44.3
5552 | 658 | 345 | 85 | 6.8506 | 24.1 | 331.1828 | 185.5227 | 0 | 153.5292 | 25.5923 | 0 | 0 | 25.5923 | 0 | 0 | 0 | 0 | 0 | 153.5292 | 0 | 360.4636 | 28.28% | 0 | 0 | 0 | 0% | 25.5923
5553 | 785 | 551 | 99 | 8.0595 | 25.6 | 395.1041 | 241.2616 | 0 | 204.9278 | 52.6444 | 0 | 2.9722 | 49.6722 | 0 | 0 | 0 | 0 | 0 | 204.9278 | 0 | 555.4821 | 43.58% | 2.2797 | 0 | 2.3551 | 4.71% | 46.7
5554 | 864 | 727 | 100 | 7.455 | 27.4 | 434.8662 | 277.149 | 0 | 238.7869 | 87.2578 | 0 | 19.9289 | 67.3289 | 0 | 0 | 0 | 0 | 0 | 238.7869 | 0 | 782.7225 | 61.41% | 15.2855 | 0 | 18.1461 | 36.29% | 47.4
5555 | 898 | 857 | 103 | 7.2535 | 29.2 | 451.979 | 295.7322 | 0 | 256.4814 | 103.4 | 3.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 256.4814 | 0 | 1026.8017 | 80.56% | 19.175 | 0 | 37.9553 | 75.91% | 46.6
5556 | 905 | 932 | 114 | 6.4476 | 30.8 | 455.5022 | 300.9655 | 0 | 261.83 | 104.7 | 14.4991 | 15.2009 | 75 | 0 | 0 | 0 | 0 | 0 | 261.83 | 0 | 1274.5104 | 100% | 11.6591 | 0 | 50 | 100% | 45.3
5557 | 862 | 946 | 156 | 8.0595 | 31.8 | 433.8596 | 0 | 284.868 | 0 | 105.3 | 30.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.7
5558 | 752 | 903 | 242 | 9.8729 | 32.2 | 378.4947 | 0 | 242.6353 | 0 | 105.7 | 30.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.3
5559 | 469 | 636 | 259 | 13.4996 | 31 | 236.0559 | 0 | 145.837 | 0 | 71.3658 | 13.9829 | 0 | 57.3829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.4
5560 | 514 | 618 | 282 | 12.2907 | 30.6 | 258.7051 | 0 | 148.0865 | 0 | 65.3286 | 11.3643 | 0 | 53.9643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
5561 | 281 | 302 | 154 | 12.6937 | 29.5 | 141.4322 | 0 | 69.2569 | 0 | 23.0823 | 0 | 0 | 23.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 19.4177 | 29.9431 | 59.89% | 42.5
5562 | 161 | 143 | 99 | 12.2907 | 28 | 81.0341 | 0 | 28.9386 | 0 | 9.0731 | 0 | 0 | 9.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 4.1191 | 8.238% | 34.0731
5563 | 88 | 39 | 27 | 12.6937 | 26.5 | 44.2919 | 0 | 0 | 0 | 1.1209 | 0 | 0 | 1.1209 | 0 | 0 | 0 | 93.9056 | 36.5904 | 0 | 93.9056 | 1184.6972 | 92.95% | 0 | 3.9888 | 6.9389e-16 | 1.388e-15% | 41.7
5564 | 0 | 0 | 0 | 11.0818 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9677 | 38.8 | 0 | 98.9677 | 1089.1444 | 85.46% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 38.8
5565 | 0 | 0 | 0 | 10.4773 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0188 | 36.4 | 0 | 93.0188 | 1000.2282 | 78.48% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 36.4
5566 | 0 | 0 | 0 | 8.8654 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8999 | 34.3 | 0 | 87.8999 | 917.0281 | 71.95% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 34.3
5567 | 0 | 0 | 0 | 8.8654 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2146 | 32.8 | 0 | 84.2146 | 838.0013 | 65.75% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 32.8
5568 | 0 | 0 | 0 | 7.6565 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7104 | 32.2 | 0 | 82.7104 | 760.645 | 59.68% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 32.2
5569 | 0 | 0 | 0 | 6.2461 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1768 | 32 | 0 | 82.1768 | 683.8652 | 53.66% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 32
5570 | 0 | 0 | 0 | 6.2461 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1437 | 32.4 | 0 | 83.1437 | 605.989 | 47.55% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 32.4
5571 | 0 | 0 | 0 | 6.0446 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.091 | 34.5 | 0 | 88.091 | 522.4451 | 40.99% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 34.5
5572 | 0 | 0 | 0 | 6.6491 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7515 | 36.8 | 0 | 93.7515 | 432.5274 | 33.94% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 36.8
5573 | 0 | 0 | 0 | 6.4476 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9369 | 39 | 0 | 98.9369 | 336.3221 | 26.39% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 39
5574 | 1 | 7 | 7 | 5.4401 | 22.2 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.4476 | 41.7 | 0 | 105.4476 | 232.4041 | 18.23% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 41.7
5575 | 132 | 96 | 63 | 7.6565 | 23.2 | 66.4379 | 0 | 31.0419 | 0 | 4.4418 | 0 | 0 | 4.4418 | 0 | 0 | 0 | 73.6607 | 28.3602 | 0 | 73.6607 | 164.4338 | 12.9% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 32.802
5576 | 418 | 306 | 144 | 10.0743 | 25.4 | 210.3867 | 117.6672 | 0 | 88.3963 | 23.3927 | 0 | 0 | 23.3927 | 0 | 0 | 0 | 0 | 0 | 88.3963 | 0 | 248.2677 | 19.48% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 23.3927
5577 | 479 | 499 | 222 | 13.2981 | 26.2 | 241.089 | 147.1195 | 0 | 114.0226 | 44.0087 | 0 | 0 | 44.0087 | 0 | 0 | 0 | 0 | 0 | 114.0226 | 0 | 356.4052 | 27.96% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 44.0087
5578 | 727 | 724 | 194 | 13.9026 | 27.2 | 365.9117 | 233.1635 | 0 | 194.0537 | 88.7838 | 0 | 20.9919 | 67.7919 | 0 | 0 | 0 | 0 | 0 | 194.0537 | 0 | 540.4431 | 42.4% | 16.1008 | 0 | 16.6357 | 33.27% | 46.8
5579 | 664 | 821 | 260 | 17.1264 | 27.2 | 334.2027 | 218.671 | 0 | 178.6011 | 103.4 | 3.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 178.6011 | 0 | 709.8259 | 55.69% | 19.175 | 0 | 36.4478 | 72.9% | 46.6
5580 | 638 | 856 | 273 | 16.9249 | 27.4 | 321.1165 | 212.167 | 0 | 172.6765 | 104.3 | 12.1991 | 17.1009 | 75 | 0 | 0 | 0 | 0 | 0 | 172.6765 | 0 | 873.5899 | 68.54% | 13.1164 | 0 | 50 | 100% | 45.7
5581 | 760 | 913 | 212 | 17.5294 | 27.7 | 382.5212 | 251.1726 | 0 | 208.6018 | 104.6 | 29.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 208.6018 | 0 | 1071.425 | 84.07% | 0 | 0 | 50 | 100% | 45.4
5582 | 753 | 869 | 207 | 17.1264 | 28.2 | 378.998 | 242.9759 | 0 | 201.2907 | 105.1 | 30.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 201.2907 | 0 | 1262.3264 | 99.04% | 0 | 0 | 50 | 100% | 44.9
5583 | 689 | 747 | 204 | 17.5294 | 28 | 346.7857 | 0 | 214.2127 | 0 | 96.5252 | 26.1126 | 0 | 70.4126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.3264 | 99.04% | 0 | 0 | 50 | 100% | 44.3
5584 | 639 | 599 | 184 | 17.5294 | 27.2 | 321.6198 | 0 | 183.9835 | 0 | 66.489 | 11.4945 | 0 | 54.9945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.3264 | 99.04% | 0 | 0 | 50 | 100% | 43.5
5585 | 558 | 410 | 142 | 17.3279 | 26.2 | 280.8511 | 0 | 137.297 | 0 | 33.9699 | 0 | 0 | 33.9699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.3264 | 99.04% | 0 | 9.1301 | 40.568 | 81.14% | 43.1
5586 | 210 | 174 | 107 | 15.5145 | 24.8 | 105.6967 | 0 | 37.5889 | 0 | 10.4157 | 0 | 0 | 10.4157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.3264 | 99.04% | 0 | 25 | 14.7407 | 29.48% | 35.4157
5587 | 0 | 18 | 18 | 13.7011 | 23.5 | 0 | 0 | 0 | 0 | 0.70273 | 0 | 0 | 0.70273 | 0 | 0 | 0 | 70.7242 | 27.0282 | 0 | 70.7242 | 1197.3257 | 93.94% | 0 | 14.2691 | 0 | 0% | 42
5588 | 0 | 0 | 0 | 12.6937 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7814 | 39.3 | 0 | 99.7814 | 1100.4009 | 86.34% | 0 | 0 | 0 | 0% | 39.3
5589 | 0 | 0 | 0 | 8.8654 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6205 | 36.8 | 0 | 93.6205 | 1010.584 | 79.29% | 0 | 0 | 0 | 0% | 36.8
5590 | 0 | 0 | 0 | 7.052 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6669 | 34.8 | 0 | 88.6669 | 926.3743 | 72.68% | 0 | 0 | 0 | 0% | 34.8
5591 | 0 | 0 | 0 | 5.6416 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7828 | 33.2 | 0 | 84.7828 | 846.6292 | 66.43% | 0 | 0 | 0 | 0% | 33.2
5592 | 0 | 0 | 0 | 6.6491 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7548 | 32.4 | 0 | 82.7548 | 769.1421 | 60.35% | 0 | 0 | 0 | 0% | 32.4
5593 | 0 | 0 | 0 | 7.455 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7862 | 32 | 0 | 81.7862 | 692.7277 | 54.35% | 0 | 0 | 0 | 0% | 32
5594 | 0 | 0 | 0 | 7.6565 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6935 | 32.4 | 0 | 82.6935 | 615.2738 | 48.28% | 0 | 0 | 0 | 0% | 32.4
5595 | 0 | 0 | 0 | 3.0223 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.431 | 34.4 | 0 | 87.431 | 532.1632 | 41.75% | 0 | 0 | 0 | 0% | 34.4
5596 | 0 | 0 | 0 | 1.6119 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4908 | 36.5 | 0 | 92.4908 | 443.0919 | 34.77% | 0 | 0 | 0 | 0% | 36.5
5597 | 0 | 0 | 0 | 2.0149 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4392 | 39 | 0 | 98.4392 | 346.8877 | 27.22% | 0 | 0 | 0 | 0% | 39
5598 | 26 | 9 | 7 | 3.2238 | 19.3 | 13.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8843 | 42.1 | 0 | 105.8843 | 241.8347 | 18.97% | 0 | 0 | 0 | 0% | 42.1
5599 | 382 | 129 | 50 | 3.6268 | 21 | 192.2672 | 89.4916 | 0 | 65.3945 | 4.4108 | 0 | 0 | 4.4108 | 0 | 0 | 0 | 0 | 0 | 65.3945 | 0 | 303.8481 | 23.84% | 0 | 0 | 0 | 0% | 4.4108
5600 | 645 | 332 | 80 | 6.2461 | 23.6 | 324.6397 | 181.2713 | 0 | 149.9387 | 25.0816 | 0 | 0 | 25.0816 | 0 | 0 | 0 | 55.5655 | 20.4184 | 149.9387 | 55.5655 | 395.5075 | 31.03% | 0 | 0 | 0 | 0% | 45.5
5601 | 775 | 535 | 94 | 11.2833 | 25.5 | 390.071 | 237.8729 | 0 | 199.8945 | 51.8804 | 0 | 2.5402 | 49.3402 | 0 | 0 | 0 | 0 | 0 | 199.8945 | 0 | 584.5832 | 45.87% | 1.9483 | 0 | 2.0134 | 4.027% | 46.8
5602 | 839 | 708 | 103 | 11.2833 | 26.6 | 422.2833 | 269.0372 | 0 | 228.8495 | 86.3582 | 0 | 19.2291 | 67.1291 | 0 | 0 | 0 | 0 | 0 | 228.8495 | 0 | 801.0467 | 62.85% | 14.7487 | 0 | 17.2543 | 34.51% | 47.9
5603 | 860 | 835 | 117 | 11.0818 | 27.7 | 432.853 | 283.2187 | 0 | 242.3721 | 102.7 | 2.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 242.3721 | 0 | 1030.301 | 80.84% | 19.175 | 0 | 37.0693 | 74.14% | 47.3
5604 | 873 | 911 | 126 | 13.0966 | 28 | 439.3961 | 290.3089 | 0 | 247.9223 | 103.8 | 12.4857 | 16.3143 | 75 | 0 | 0 | 0 | 0 | 0 | 247.9223 | 0 | 1264.8051 | 99.24% | 12.513 | 0 | 50 | 100% | 46.2
5605 | 892 | 925 | 112 | 14.3056 | 28.7 | 448.9591 | 0 | 294.8121 | 0 | 104.3 | 29.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.8051 | 99.24% | 0 | 0 | 50 | 100% | 45.7
5606 | 884 | 877 | 109 | 14.5071 | 29.1 | 444.9326 | 0 | 285.2687 | 0 | 104.8 | 29.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.8051 | 99.24% | 0 | 0 | 50 | 100% | 45.2
5607 | 850 | 769 | 108 | 15.716 | 29.1 | 427.8198 | 0 | 264.2263 | 0 | 101.2859 | 28.343 | 0 | 72.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.8051 | 99.24% | 0 | 0 | 50 | 100% | 44.6
5608 | 798 | 612 | 102 | 15.5145 | 28.5 | 401.6473 | 0 | 229.6173 | 0 | 70.4994 | 13.3497 | 0 | 57.1497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.8051 | 99.24% | 0 | 0 | 50 | 100% | 43.8
5609 | 708 | 420 | 88 | 15.5145 | 27.5 | 356.3487 | 0 | 173.8943 | 0 | 35.4984 | 0 | 0 | 35.4984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.8051 | 99.24% | 0 | 7.9016 | 41.836 | 83.67% | 43.4
5610 | 529 | 212 | 63 | 14.5071 | 26.4 | 266.2549 | 0 | 94.2914 | 0 | 11.2246 | 0 | 0 | 11.2246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.8051 | 99.24% | 0 | 25 | 16.005 | 32.01% | 36.2246
5611 | 134 | 38 | 22 | 12.6937 | 24.9 | 67.4445 | 0 | 0 | 0 | 0.74135 | 0 | 0 | 0.74135 | 0 | 0 | 0 | 69.2685 | 26.268 | 0 | 69.2685 | 1201.1977 | 94.25% | 0 | 15.4906 | 0 | 0% | 42.5
5612 | 0 | 0 | 0 | 10.2758 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5271 | 39.6 | 0 | 100.5271 | 1103.3895 | 86.57% | 0 | 0 | 0 | 0% | 39.6
5613 | 0 | 0 | 0 | 9.0669 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4661 | 37.2 | 0 | 94.4661 | 1012.4261 | 79.44% | 0 | 0 | 0 | 0% | 37.2
5614 | 0 | 0 | 0 | 7.455 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8155 | 34.9 | 0 | 88.8155 | 927.9086 | 72.81% | 0 | 0 | 0 | 0% | 34.9
5615 | 0 | 0 | 0 | 6.4476 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9436 | 33.3 | 0 | 84.9436 | 847.9506 | 66.53% | 0 | 0 | 0 | 0% | 33.3
5616 | 0 | 0 | 0 | 5.6416 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8597 | 32.5 | 0 | 82.8597 | 770.3056 | 60.44% | 0 | 0 | 0 | 0% | 32.5
5617 | 0 | 0 | 0 | 3.4253 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5785 | 32 | 0 | 81.5785 | 694.0711 | 54.46% | 0 | 0 | 0 | 0% | 32
5618 | 0 | 0 | 0 | 2.0149 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.544 | 32.4 | 0 | 82.544 | 616.7012 | 48.39% | 0 | 0 | 0 | 0% | 32.4
5619 | 0 | 0 | 0 | 2.6193 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3161 | 34.4 | 0 | 87.3161 | 533.5749 | 41.87% | 0 | 0 | 0 | 0% | 34.4
5620 | 0 | 0 | 0 | 2.2164 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0699 | 36.4 | 0 | 92.0699 | 444.7679 | 34.9% | 0 | 0 | 0 | 0% | 36.4
5621 | 0 | 0 | 0 | 3.8283 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4358 | 38.7 | 0 | 97.4358 | 349.4068 | 27.41% | 0 | 0 | 0 | 0% | 38.7
5622 | 43 | 9 | 6 | 3.2238 | 18.3 | 21.6426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5027 | 37.856 | 0 | 95.5027 | 256.4338 | 20.12% | 0 | 0 | 0 | 0% | 37.856
5623 | 493 | 137 | 39 | 3.8283 | 20.7 | 248.1355 | 115.0459 | 0 | 89.1511 | 3.9348 | 0 | 0 | 3.9348 | 0 | 0 | 0 | 0 | 0 | 89.1511 | 0 | 340.8391 | 26.74% | 0 | 0 | 0 | 0% | 3.9348
5624 | 727 | 343 | 62 | 7.2535 | 24.1 | 365.9117 | 203.9747 | 0 | 170.6215 | 26.1042 | 0 | 0 | 26.1042 | 0 | 0 | 0 | 0 | 0 | 170.6215 | 0 | 502.3779 | 39.42% | 0 | 0 | 0 | 0% | 26.1042
5625 | 833 | 547 | 75 | 11.6862 | 26.1 | 419.2634 | 255.499 | 0 | 215.9516 | 54.1972 | 0 | 3.5986 | 50.5986 | 0 | 0 | 0 | 0 | 0 | 215.9516 | 0 | 706.8338 | 55.46% | 2.7601 | 0 | 2.8527 | 5.705% | 47
5626 | 892 | 722 | 81 | 12.0892 | 27.3 | 448.9591 | 285.9808 | 0 | 244.3814 | 89.8187 | 0 | 20.9093 | 68.9093 | 0 | 0 | 0 | 0 | 0 | 244.3814 | 0 | 938.2061 | 73.61% | 16.0375 | 0 | 19.4278 | 38.86% | 48
5627 | 917 | 851 | 88 | 11.4848 | 28.3 | 461.542 | 301.9901 | 0 | 259.7499 | 102.6 | 2.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 259.7499 | 0 | 1184.1289 | 92.91% | 19.175 | 0 | 39.2456 | 78.49% | 47.4
5628 | 924 | 923 | 95 | 12.8952 | 28.9 | 465.0653 | 307.2605 | 0 | 263.8179 | 103.9 | 15.3335 | 13.5665 | 75 | 0 | 0 | 0 | 0 | 0 | 263.8179 | 0 | 1274.5104 | 100% | 10.4055 | 0 | 50 | 100% | 46.1
5629 | 927 | 936 | 95 | 13.4996 | 29.5 | 466.5752 | 0 | 306.3962 | 0 | 104.4 | 29.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.6
5630 | 915 | 885 | 94 | 13.4996 | 29.8 | 460.5354 | 0 | 295.2961 | 0 | 104.7 | 29.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.3
5631 | 882 | 774 | 92 | 13.4996 | 30 | 443.9259 | 0 | 274.13 | 0 | 102.4396 | 28.9698 | 0 | 73.4698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.5
5632 | 811 | 609 | 92 | 14.7085 | 29.1 | 408.1904 | 0 | 233.2084 | 0 | 70.0969 | 13.1984 | 0 | 56.8984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.7
5633 | 697 | 412 | 87 | 14.91 | 28.2 | 350.8122 | 0 | 170.8688 | 0 | 34.8673 | 0 | 0 | 34.8673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.3327 | 41.3893 | 82.78% | 43.2
5634 | 501 | 203 | 64 | 15.5145 | 26.8 | 252.162 | 0 | 88.9237 | 0 | 10.914 | 0 | 0 | 10.914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 15.5545 | 31.11% | 35.914
5635 | 132 | 37 | 21 | 11.2833 | 25.4 | 66.4379 | 0 | 0 | 0 | 0.6744 | 0 | 0 | 0.6744 | 0 | 0 | 0 | 69.1529 | 26.1732 | 0 | 69.1529 | 1211.014 | 95.02% | 0 | 15.0525 | 0 | 0% | 41.9
5636 | 0 | 0 | 0 | 7.858 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1738 | 39 | 0 | 99.1738 | 1114.9274 | 87.48% | 0 | 0 | 0 | 0% | 39
5637 | 0 | 0 | 0 | 7.455 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0692 | 37 | 0 | 94.0692 | 1024.524 | 80.39% | 0 | 0 | 0 | 0% | 37
5638 | 0 | 0 | 0 | 7.6565 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.325 | 35.1 | 0 | 89.325 | 939.4317 | 73.71% | 0 | 0 | 0 | 0% | 35.1
5639 | 0 | 0 | 0 | 6.0446 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9294 | 33.3 | 0 | 84.9294 | 859.4827 | 67.44% | 0 | 0 | 0 | 0% | 33.3
5640 | 0 | 0 | 0 | 2.8208 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2232 | 32.2 | 0 | 82.2232 | 782.5641 | 61.4% | 0 | 0 | 0 | 0% | 32.2
5641 | 0 | 0 | 0 | 2.0149 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2588 | 31.4 | 0 | 80.2588 | 707.8188 | 55.54% | 0 | 0 | 0 | 0% | 31.4
5642 | 0 | 0 | 0 | 2.4178 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9454 | 30.9 | 0 | 78.9454 | 634.4968 | 49.78% | 0 | 0 | 0 | 0% | 30.9
5643 | 0 | 0 | 0 | 2.2164 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1277 | 31.4 | 0 | 80.1277 | 559.8492 | 43.93% | 0 | 0 | 0 | 0% | 31.4
5644 | 0 | 0 | 0 | 4.8357 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9476 | 31.7 | 0 | 80.9476 | 484.2929 | 38% | 0 | 0 | 0 | 0% | 31.7
5645 | 0 | 0 | 0 | 3.4253 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2307 | 33.1 | 0 | 84.2307 | 404.8802 | 31.77% | 0 | 0 | 0 | 0% | 33.1
5646 | 36 | 9 | 6 | 3.4253 | 18.8 | 18.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6258 | 36.2 | 0 | 91.6258 | 316.5926 | 24.84% | 0 | 0 | 0 | 0% | 36.2
5647 | 443 | 132 | 45 | 3.8283 | 20.3 | 222.9696 | 102.9659 | 0 | 77.5962 | 4.3153 | 0 | 0 | 4.3153 | 0 | 0 | 0 | 87.9216 | 34.5847 | 77.5962 | 87.9216 | 305.7739 | 23.99% | 0 | 0 | 0 | 0% | 38.9
5648 | 680 | 336 | 73 | 8.6639 | 23 | 342.2558 | 190.461 | 0 | 157.028 | 25.8967 | 0 | 0 | 25.8967 | 0 | 0 | 0 | 0 | 0 | 157.028 | 0 | 453.427 | 35.58% | 0 | 0 | 0 | 0% | 25.8967
5649 | 794 | 538 | 88 | 10.0743 | 25 | 399.634 | 243.3652 | 0 | 205.653 | 58.5619 | 0 | 8.4809 | 50.0809 | 0 | 0 | 0 | 0 | 0 | 205.653 | 0 | 646.8021 | 50.75% | 6.5049 | 0 | 6.7239 | 13.45% | 41.6
5650 | 861 | 715 | 96 | 13.4996 | 26.8 | 433.3563 | 275.9908 | 0 | 234.0708 | 94.5113 | 0.95567 | 25 | 68.5557 | 0 | 0 | 0 | 0 | 0 | 234.0708 | 0 | 866.8984 | 68.02% | 19.175 | 0 | 26.5447 | 53.09% | 42.6
5651 | 894 | 845 | 101 | 13.0966 | 27.9 | 449.9657 | 294.4152 | 0 | 251.7831 | 107.5 | 7.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 251.7831 | 0 | 1103.6496 | 86.59% | 19.175 | 0 | 46.3654 | 92.73% | 42.5
5652 | 906 | 917 | 105 | 12.2907 | 28.4 | 456.0056 | 301.267 | 0 | 258.6059 | 108.4 | 28.8157 | 4.5843 | 75 | 0 | 0 | 0 | 0 | 0 | 258.6059 | 0 | 1274.5104 | 100% | 3.5162 | 0 | 50 | 100% | 41.6
5653 | 910 | 929 | 103 | 12.2907 | 29.4 | 458.0188 | 0 | 300.7943 | 0 | 109.3 | 34.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.7
5654 | 891 | 874 | 103 | 11.2833 | 29.7 | 448.4558 | 0 | 287.5745 | 0 | 109.8 | 34.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.2
5655 | 850 | 762 | 106 | 11.4848 | 29.8 | 427.8198 | 0 | 264.142 | 0 | 104.5068 | 32.3534 | 0 | 72.1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.8
5656 | 780 | 600 | 104 | 12.4922 | 29.3 | 392.5876 | 0 | 224.1493 | 0 | 72.2726 | 16.3363 | 0 | 55.9363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.6
5657 | 672 | 404 | 92 | 11.6862 | 28.3 | 338.2293 | 0 | 164.4274 | 0 | 34.1995 | 0 | 0 | 34.1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.6005 | 44.2118 | 88.42% | 39.8
5658 | 482 | 196 | 64 | 11.0818 | 27.3 | 242.599 | 0 | 85.1878 | 0 | 10.6107 | 0 | 0 | 10.6107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.3735 | 36.75% | 35.6107
5659 | 112 | 33 | 19 | 9.8729 | 25.7 | 56.3715 | 0 | 0 | 0 | 0.55682 | 0 | 0 | 0.55682 | 0 | 0 | 0 | 57.4728 | 21.0655 | 0 | 57.4728 | 1222.252 | 95.9% | 0 | 17.7777 | 0 | 0% | 39.4
5660 | 0 | 0 | 0 | 7.6565 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8198 | 37.2 | 0 | 94.8198 | 1131.2955 | 88.76% | 0 | 0 | 0 | 0% | 37.2
5661 | 0 | 0 | 0 | 8.0595 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4957 | 35.1 | 0 | 89.4957 | 1046.1913 | 82.09% | 0 | 0 | 0 | 0% | 35.1
5662 | 0 | 0 | 0 | 5.2387 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3251 | 33 | 0 | 84.3251 | 966.9614 | 75.87% | 0 | 0 | 0 | 0% | 33
5663 | 0 | 0 | 0 | 3.6268 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6668 | 31.5 | 0 | 80.6668 | 891.8154 | 69.97% | 0 | 0 | 0 | 0% | 31.5
5664 | 0 | 0 | 0 | 2.8208 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3775 | 30.6 | 0 | 78.3775 | 819.1695 | 64.27% | 0 | 0 | 0 | 0% | 30.6
5665 | 0 | 0 | 0 | 3.8283 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.463 | 29.8 | 0 | 76.463 | 748.5512 | 58.73% | 0 | 0 | 0 | 0% | 29.8
5666 | 0 | 0 | 0 | 4.4327 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7491 | 29.5 | 0 | 75.7491 | 678.6109 | 53.24% | 0 | 0 | 0 | 0% | 29.5
5667 | 0 | 0 | 0 | 4.4327 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3831 | 29.8 | 0 | 76.3831 | 608.0443 | 47.71% | 0 | 0 | 0 | 0% | 29.8
5668 | 0 | 0 | 0 | 3.4253 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4701 | 29.4 | 0 | 75.4701 | 538.3481 | 42.24% | 0 | 0 | 0 | 0% | 29.4
5669 | 0 | 0 | 0 | 3.4253 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7469 | 30 | 0 | 76.7469 | 467.4 | 36.67% | 0 | 0 | 0 | 0% | 30
5670 | 33 | 8 | 5 | 4.6342 | 19.1 | 16.6095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2901 | 32.3 | 0 | 82.2901 | 390.2549 | 30.62% | 0 | 0 | 0 | 0% | 32.3
5671 | 456 | 129 | 41 | 2.6193 | 20.9 | 229.5127 | 105.5555 | 0 | 80.4522 | 4.0824 | 0 | 0 | 4.0824 | 0 | 0 | 0 | 78.1856 | 30.5176 | 80.4522 | 78.1856 | 392.55 | 30.8% | 0 | 0 | 0 | 0% | 34.6
5672 | 695 | 334 | 67 | 4.8357 | 23 | 349.8056 | 194.3211 | 0 | 162.8862 | 25.8865 | 0 | 0 | 25.8865 | 0 | 0 | 0 | 0 | 0 | 162.8862 | 0 | 543.956 | 42.68% | 0 | 0 | 0 | 0% | 25.8865
5673 | 809 | 538 | 81 | 9.4699 | 25.2 | 407.1838 | 247.7838 | 0 | 210.0998 | 63.0008 | 0 | 12.7004 | 50.3004 | 0 | 0 | 0 | 0 | 0 | 210.0998 | 0 | 739.2479 | 58% | 9.7412 | 0 | 10.0707 | 20.14% | 37.6
5674 | 865 | 711 | 91 | 11.4848 | 26.8 | 435.3695 | 277.2202 | 0 | 236.4345 | 97.7874 | 4.4937 | 25 | 68.2937 | 0 | 0 | 0 | 0 | 0 | 236.4345 | 0 | 959.0185 | 75.25% | 19.175 | 0 | 29.8943 | 59.79% | 38.8
5675 | 886 | 838 | 101 | 12.8952 | 27.9 | 445.9392 | 291.7621 | 0 | 249.4234 | 110.7 | 10.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 249.4234 | 0 | 1190.8625 | 93.44% | 19.175 | 0 | 49.718 | 99.44% | 39.3
5676 | 883 | 906 | 114 | 12.4922 | 28.7 | 444.4293 | 167.5699 | 126.0412 | 143.4928 | 111.5 | 36.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 143.4928 | 0 | 1274.5104 | 100% | 0 | 0 | 49.718 | 99.44% | 38.5
5677 | 876 | 915 | 120 | 11.6862 | 28.9 | 440.906 | 0 | 289.5731 | 0 | 112.3 | 37.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.718 | 99.44% | 37.7
5678 | 849 | 860 | 126 | 12.4922 | 29.3 | 427.3165 | 0 | 274.0423 | 0 | 112.8 | 37.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.718 | 99.44% | 37.2
5679 | 771 | 745 | 149 | 14.5071 | 28.8 | 388.0577 | 0 | 239.5539 | 0 | 105.8079 | 34.504 | 0 | 71.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.718 | 99.44% | 36.8
5680 | 668 | 582 | 158 | 13.0966 | 28.5 | 336.216 | 0 | 191.8387 | 0 | 71.8774 | 17.6387 | 0 | 54.2387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.718 | 99.44% | 36.6
5681 | 548 | 383 | 128 | 13.4996 | 27.8 | 275.8179 | 0 | 133.8311 | 0 | 32.1439 | 0 | 0 | 32.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.2561 | 44.2849 | 88.57% | 37.4
5682 | 387 | 192 | 86 | 13.7011 | 26.2 | 194.7838 | 0 | 0 | 0 | 11.0246 | 0 | 0 | 11.0246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.4428 | 36.89% | 36.0246
5683 | 78 | 41 | 31 | 11.8877 | 24.5 | 39.2588 | 0 | 0 | 0 | 1.1165 | 0 | 0 | 1.1165 | 0 | 0 | 0 | 55.5415 | 20.3414 | 0 | 55.5415 | 1224.0705 | 96.04% | 0 | 17.8421 | 0 | 0% | 39.3
5684 | 0 | 0 | 0 | 9.2684 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2007 | 37 | 0 | 94.2007 | 1133.6546 | 88.95% | 0 | 0 | 0 | 0% | 37
5685 | 0 | 0 | 0 | 6.8506 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7201 | 34.8 | 0 | 88.7201 | 1049.3999 | 82.34% | 0 | 0 | 0 | 0% | 34.8
5686 | 0 | 0 | 0 | 5.4401 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.337 | 33 | 0 | 84.337 | 970.1378 | 76.12% | 0 | 0 | 0 | 0% | 33
5687 | 0 | 0 | 0 | 5.6416 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3929 | 31.8 | 0 | 81.3929 | 894.1638 | 70.16% | 0 | 0 | 0 | 0% | 31.8
5688 | 0 | 0 | 0 | 6.2461 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2104 | 31.3 | 0 | 80.2104 | 819.4993 | 64.3% | 0 | 0 | 0 | 0% | 31.3
5689 | 0 | 0 | 0 | 6.0446 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4263 | 31 | 0 | 79.4263 | 745.6817 | 58.51% | 0 | 0 | 0 | 0% | 31
5690 | 0 | 0 | 0 | 6.8506 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0699 | 31.7 | 0 | 81.0699 | 670.0199 | 52.57% | 0 | 0 | 0 | 0% | 31.7
5691 | 0 | 0 | 0 | 5.0372 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7692 | 34.5 | 0 | 87.7692 | 586.5792 | 46.02% | 0 | 0 | 0 | 0% | 34.5
5692 | 0 | 0 | 0 | 5.2387 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.6194 | 37.8 | 0 | 95.6194 | 493.7851 | 38.74% | 0 | 0 | 0 | 0% | 37.8
5693 | 0 | 0 | 0 | 6.4476 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9243 | 40.8 | 0 | 102.9243 | 392.3963 | 30.79% | 0 | 0 | 0 | 0% | 40.8
5694 | 1 | 5 | 5 | 7.858 | 20.6 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.0001 | 43.7 | 0 | 110.0001 | 282.7173 | 22.18% | 0 | 0 | 0 | 0% | 43.7
5695 | 44 | 87 | 78 | 6.4476 | 21.5 | 22.146 | 0 | 10.1427 | 0 | 5.2504 | 0 | 0 | 5.2504 | 0 | 0 | 0 | 102.4968 | 40.5496 | 0 | 102.4968 | 181.9782 | 14.28% | 0 | 0 | 0 | 0% | 45.8
5696 | 123 | 232 | 188 | 9.2684 | 23.5 | 61.908 | 0 | 34.329 | 0 | 18.2258 | 0 | 0 | 18.2258 | 0 | 0 | 0 | 69.6299 | 26.5438 | 0 | 69.6299 | 117.8403 | 9.246% | 0 | 0 | 0 | 0% | 44.7695
5697 | 115 | 344 | 275 | 10.6788 | 24.5 | 57.8815 | 0 | 35.1967 | 0 | 27.8615 | 0 | 0 | 27.8615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.8403 | 9.246% | 0 | 0 | 0 | 0% | 27.8615
5698 | 49 | 371 | 331 | 11.6862 | 25.2 | 24.6626 | 0 | 15.7007 | 0 | 29.8787 | 0 | 0 | 29.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.8403 | 9.246% | 0 | 0 | 0 | 0% | 29.8787
5699 | 344 | 731 | 438 | 12.0892 | 26.7 | 173.1412 | 113.254 | 0 | 82.9545 | 83.4779 | 0 | 17.7389 | 65.7389 | 0 | 0 | 0 | 0 | 0 | 82.9545 | 0 | 196.2705 | 15.4% | 13.6058 | 0 | 14.0681 | 28.14% | 48
5700 | 301 | 699 | 422 | 12.8952 | 27.5 | 151.4985 | 100.0844 | 0 | 69.9877 | 79.9886 | 0 | 16.6443 | 63.3443 | 0 | 0 | 0 | 0 | 0 | 69.9877 | 0 | 262.441 | 20.59% | 12.7662 | 0 | 27.268 | 54.54% | 46.7
5701 | 434 | 813 | 415 | 12.6937 | 28.6 | 218.4397 | 143.4733 | 0 | 110.9641 | 102.5854 | 3.1927 | 25 | 74.3927 | 0 | 0 | 0 | 0 | 0 | 110.9641 | 0 | 367.3532 | 28.82% | 19.175 | 0 | 47.0946 | 94.19% | 46.2
5702 | 364 | 710 | 390 | 15.5145 | 28.6 | 183.2075 | 117.5032 | 0 | 85.2201 | 83.3185 | 14.9958 | 3.6635 | 64.6592 | 0 | 0 | 0 | 0 | 0 | 85.2201 | 0 | 447.9253 | 35.14% | 2.8099 | 0 | 50 | 100% | 46
5703 | 249 | 552 | 356 | 14.91 | 28.2 | 125.326 | 77.3531 | 0 | 47.2247 | 53.3172 | 4.1586 | 0 | 49.1586 | 0 | 0 | 0 | 0 | 0 | 47.2247 | 0 | 492.5744 | 38.65% | 0 | 0 | 50 | 100% | 45
5704 | 29 | 279 | 259 | 15.313 | 27.1 | 14.5962 | 0 | 8.3228 | 0 | 21.2277 | 0 | 0 | 21.2277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 492.5744 | 38.65% | 0 | 22.8723 | 26.3542 | 52.71% | 44.1
5705 | 160 | 306 | 226 | 14.5071 | 26.4 | 80.5308 | 0 | 39 | 0 | 24.1471 | 0 | 0 | 24.1471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 492.5744 | 38.65% | 0 | 20.0529 | 5.6221 | 11.24% | 44.2
5706 | 20 | 104 | 98 | 13.9026 | 25.1 | 10.0663 | 0 | 0 | 0 | 7.0416 | 0 | 0 | 7.0416 | 0 | 0 | 0 | 85.1908 | 33.1194 | 0 | 85.1908 | 412.4133 | 32.36% | 0 | 5.439 | 0 | 0% | 45.6
5707 | 4 | 30 | 30 | 11.8877 | 24.1 | 2.0133 | 0 | 0 | 0 | 1.1063 | 0 | 0 | 1.1063 | 0 | 0 | 0 | 105.556 | 41.5937 | 0 | 105.556 | 308.8205 | 24.23% | 0 | 0 | 0 | 0% | 42.7
5708 | 0 | 0 | 0 | 9.4699 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.3252 | 39.5 | 0 | 100.3252 | 211.1415 | 16.57% | 0 | 0 | 0 | 0% | 39.5
5709 | 0 | 0 | 0 | 9.2684 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2555 | 33.7129 | 0 | 86.2555 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 33.7129
5710 | 0 | 0 | 0 | 8.6639 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 0
5711 | 0 | 0 | 0 | 3.4253 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 0
5712 | 0 | 0 | 0 | 2.0149 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 0
5713 | 0 | 0 | 0 | 2.6193 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 0
5714 | 0 | 0 | 0 | 2.2164 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 0
5715 | 0 | 0 | 0 | 2.8208 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 0
5716 | 0 | 0 | 0 | 2.8208 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 0
5717 | 0 | 0 | 0 | 1.4104 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 0
5718 | 0 | 6 | 6 | 1.0074 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 0
5719 | 48 | 85 | 78 | 1.4104 | 20.8 | 24.1592 | 0 | 11.0177 | 0 | 5.2659 | 0 | 0 | 5.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 5.2659
5720 | 159 | 241 | 177 | 1.8134 | 22.9 | 80.0275 | 0 | 44.2953 | 0 | 18.2928 | 0 | 0 | 18.2928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.624 | 10.17% | 0 | 0 | 0 | 0% | 18.2928
5721 | 574 | 500 | 177 | 2.4178 | 25.4 | 288.9042 | 175.5449 | 0 | 146.2646 | 44.9172 | 0 | 0 | 44.9172 | 0 | 0 | 0 | 0 | 0 | 146.2646 | 0 | 268.3793 | 21.06% | 0 | 0 | 0 | 0% | 44.9172
5722 | 699 | 687 | 187 | 3.4253 | 27 | 351.8189 | 223.9309 | 0 | 191.1016 | 80.0695 | 0 | 16.0848 | 63.9848 | 0 | 0 | 0 | 0 | 0 | 191.1016 | 0 | 449.6696 | 35.28% | 12.337 | 0 | 12.758 | 25.52% | 47.9
5723 | 803 | 846 | 183 | 5.2387 | 28.8 | 404.1639 | 264.3071 | 0 | 228.0683 | 103.3 | 3.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 228.0683 | 0 | 666.0288 | 52.26% | 19.175 | 0 | 32.5875 | 65.17% | 46.7
5724 | 796 | 919 | 211 | 10.6788 | 29.4 | 400.6406 | 264.6678 | 0 | 225.194 | 104.6 | 7.6472 | 21.9528 | 75 | 0 | 0 | 0 | 0 | 0 | 225.194 | 0 | 879.6613 | 69.02% | 16.8378 | 0 | 50 | 100% | 45.4
5725 | 638 | 859 | 283 | 9.4699 | 29.5 | 321.1165 | 210.9263 | 0 | 175.8897 | 105.1 | 30.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 175.8897 | 0 | 1046.5207 | 82.11% | 0 | 0 | 50 | 100% | 44.9
5726 | 248 | 587 | 370 | 7.6565 | 29.6 | 124.8227 | 80.0644 | 0 | 54.192 | 60.5167 | 8.1083 | 0 | 52.4083 | 0 | 0 | 0 | 0 | 0 | 54.192 | 0 | 1097.9304 | 86.15% | 0 | 0 | 50 | 100% | 44.3
5727 | 707 | 759 | 220 | 7.858 | 30.2 | 355.8454 | 219.5974 | 0 | 184.9131 | 98.9577 | 27.6288 | 0 | 71.3288 | 0 | 0 | 0 | 0 | 0 | 184.9131 | 0 | 1273.35 | 99.91% | 0 | 0 | 50 | 100% | 43.7
5728 | 501 | 501 | 185 | 10.4773 | 29.7 | 252.162 | 0 | 143.6888 | 0 | 48.5924 | 2.6962 | 0 | 45.8962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.35 | 99.91% | 0 | 0 | 50 | 100% | 43.2
5729 | 157 | 225 | 154 | 6.2461 | 28.7 | 79.0208 | 0 | 38.1952 | 0 | 17.8712 | 0 | 0 | 17.8712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.35 | 99.91% | 0 | 25 | 24.1507 | 48.3% | 42.8712
5730 | 4 | 70 | 69 | 3.8283 | 27.6 | 2.0133 | 0 | 0 | 0 | 4.6309 | 0 | 0 | 4.6309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.35 | 99.91% | 0 | 23.3573 | 0 | 0% | 27.9882
5731 | 19 | 16 | 14 | 8.8654 | 26.5 | 9.563 | 0 | 0 | 0 | 0.31236 | 0 | 0 | 0.31236 | 0 | 0 | 0 | 106.5211 | 41.7876 | 0 | 106.5211 | 1169.2753 | 91.74% | 0 | 0 | 0 | 0% | 42.1
5732 | 0 | 0 | 0 | 11.8877 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0158 | 39 | 0 | 99.0158 | 1073.1256 | 84.2% | 0 | 0 | 0 | 0% | 39
5733 | 0 | 0 | 0 | 6.8506 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4891 | 36.4 | 0 | 92.4891 | 984.3543 | 77.23% | 0 | 0 | 0 | 0% | 36.4
5734 | 0 | 0 | 0 | 2.8208 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6148 | 34.4 | 0 | 87.6148 | 901.234 | 70.71% | 0 | 0 | 0 | 0% | 34.4
5735 | 0 | 0 | 0 | 2.6193 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.977 | 32.9 | 0 | 83.977 | 822.3147 | 64.52% | 0 | 0 | 0 | 0% | 32.9
5736 | 0 | 0 | 0 | 1.2089 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4886 | 32.3 | 0 | 82.4886 | 745.0531 | 58.46% | 0 | 0 | 0 | 0% | 32.3
5737 | 0 | 0 | 0 | 4.8357 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9818 | 32.1 | 0 | 81.9818 | 668.3434 | 52.44% | 0 | 0 | 0 | 0% | 32.1
5738 | 0 | 0 | 0 | 3.0223 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1124 | 32.6 | 0 | 83.1124 | 590.3367 | 46.32% | 0 | 0 | 0 | 0% | 32.6
5739 | 0 | 0 | 0 | 1.2089 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9954 | 35.1 | 0 | 88.9954 | 505.1214 | 39.63% | 0 | 0 | 0 | 0% | 35.1
5740 | 0 | 0 | 0 | 0.60446 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8279 | 38 | 0 | 95.8279 | 411.7143 | 32.3% | 0 | 0 | 0 | 0% | 38
5741 | 0 | 0 | 0 | 2.0149 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2448 | 40.7 | 0 | 102.2448 | 310.5574 | 24.37% | 0 | 0 | 0 | 0% | 40.7
5742 | 13 | 5 | 5 | 1.4104 | 18.2 | 6.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5617 | 43.7 | 0 | 109.5617 | 200.8181 | 15.76% | 0 | 0 | 0 | 0% | 43.7
5743 | 340 | 114 | 48 | 0.80595 | 20.5 | 171.1279 | 77.7032 | 0 | 54.788 | 4.4131 | 0 | 0 | 4.4131 | 0 | 0 | 0 | 0 | 0 | 54.788 | 0 | 253.088 | 19.86% | 0 | 0 | 0 | 0% | 4.4131
5744 | 617 | 315 | 82 | 1.2089 | 23.6 | 310.5468 | 171.5668 | 0 | 142.8719 | 24.8767 | 0 | 0 | 24.8767 | 0 | 0 | 0 | 59.7951 | 22.2233 | 142.8719 | 59.7951 | 334.7728 | 26.27% | 0 | 0 | 0 | 0% | 47.1
5745 | 752 | 520 | 100 | 1.6119 | 27.1 | 378.4947 | 229.8052 | 0 | 197.2159 | 47.5672 | 0 | 0 | 47.5672 | 0 | 0 | 0 | 0 | 0 | 197.2159 | 0 | 522.4136 | 40.99% | 0 | 0 | 0 | 0% | 47.5672
5746 | 822 | 697 | 114 | 3.0223 | 29.4 | 413.7269 | 263.2811 | 0 | 227.8948 | 81.5911 | 0 | 16.3455 | 65.2455 | 0 | 0 | 0 | 0 | 0 | 227.8948 | 0 | 739.2439 | 58% | 12.537 | 0 | 12.9668 | 25.93% | 48.9
5747 | 852 | 826 | 126 | 3.4253 | 30.7 | 428.8264 | 280.3685 | 0 | 243.8332 | 101.6 | 1.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 243.8332 | 0 | 971.2388 | 76.2% | 19.175 | 0 | 32.7991 | 65.6% | 48.4
5748 | 768 | 842 | 163 | 5.2387 | 31.6 | 386.5478 | 255.3509 | 0 | 219.7528 | 102.9 | 6.2171 | 21.6829 | 75 | 0 | 0 | 0 | 0 | 0 | 219.7528 | 0 | 1180.3224 | 92.61% | 16.6308 | 0 | 50 | 100% | 47.1
5749 | 857 | 940 | 175 | 11.6862 | 31.5 | 431.343 | 251.8647 | 31.4837 | 215.3304 | 103.2 | 28.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 215.3304 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.8
5750 | 854 | 865 | 140 | 10.6788 | 31.8 | 429.833 | 0 | 275.7313 | 0 | 103.8 | 28.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.2
5751 | 819 | 748 | 129 | 12.4922 | 31.5 | 412.2169 | 0 | 254.3432 | 0 | 99.0416 | 26.7208 | 0 | 72.3208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.6
5752 | 758 | 583 | 114 | 12.4922 | 31.2 | 381.5146 | 0 | 217.2515 | 0 | 65.8224 | 10.6112 | 0 | 55.2112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.6
5753 | 660 | 387 | 92 | 10.8803 | 30.6 | 332.1895 | 0 | 160.2557 | 0 | 33.36 | 0 | 0 | 33.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 11.14 | 38.4799 | 76.96% | 44.5
5754 | 463 | 180 | 61 | 10.4773 | 29.3 | 233.036 | 0 | 0 | 0 | 9.9139 | 0 | 0 | 9.9139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 12.6261 | 25.25% | 34.9139
5755 | 99 | 25 | 15 | 7.858 | 27.7 | 49.8284 | 0 | 0 | 0 | 0.27199 | 0 | 0 | 0.27199 | 0 | 0 | 0 | 79.4593 | 30.5181 | 0 | 79.4593 | 1200.9559 | 94.23% | 0 | 12.2099 | 0 | 0% | 43
5756 | 0 | 0 | 0 | 3.2238 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9036 | 39.9 | 0 | 101.9036 | 1102.1016 | 86.47% | 0 | 0 | 0 | 0% | 39.9
5757 | 0 | 0 | 0 | 3.2238 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9852 | 37.6 | 0 | 95.9852 | 1009.8801 | 79.24% | 0 | 0 | 0 | 0% | 37.6
5758 | 0 | 0 | 0 | 1.8134 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.599 | 35.5 | 0 | 90.599 | 923.5864 | 72.47% | 0 | 0 | 0 | 0% | 35.5
5759 | 0 | 0 | 0 | 2.4178 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5832 | 33.9 | 0 | 86.5832 | 841.8087 | 66.05% | 0 | 0 | 0 | 0% | 33.9
5760 | 0 | 0 | 0 | 1.6119 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8855 | 33.2 | 0 | 84.8855 | 761.9504 | 59.78% | 0 | 0 | 0 | 0% | 33.2
5761 | 0 | 0 | 0 | 3.2238 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0009 | 32.9 | 0 | 84.0009 | 683.0505 | 53.59% | 0 | 0 | 0 | 0% | 32.9
5762 | 0 | 0 | 0 | 3.8283 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6187 | 33.2 | 0 | 84.6187 | 603.4098 | 47.34% | 0 | 0 | 0 | 0% | 33.2
5763 | 0 | 0 | 0 | 3.2238 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.612 | 35.7 | 0 | 90.612 | 516.5935 | 40.53% | 0 | 0 | 0 | 0% | 35.7
5764 | 0 | 0 | 0 | 3.0223 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8046 | 38.7 | 0 | 97.8046 | 421.2652 | 33.05% | 0 | 0 | 0 | 0% | 38.7
5765 | 0 | 0 | 0 | 2.2164 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9543 | 41.3 | 0 | 103.9543 | 318.502 | 24.99% | 0 | 0 | 0 | 0% | 41.3
5766 | 19 | 8 | 7 | 3.4253 | 20 | 9.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.5699 | 44.4 | 0 | 111.5699 | 206.8418 | 16.23% | 0 | 0 | 0 | 0% | 44.4
5767 | 329 | 115 | 50 | 1.8134 | 22.5 | 165.5914 | 74.856 | 0 | 51.7296 | 4.4065 | 0 | 0 | 4.4065 | 0 | 0 | 0 | 101.33 | 39.9906 | 51.7296 | 101.33 | 157.0269 | 12.32% | 0 | 0 | 0 | 0% | 44.3971
5768 | 602 | 317 | 90 | 2.8208 | 24.9 | 302.9971 | 167.0768 | 0 | 138.096 | 25.2907 | 0 | 0 | 25.2907 | 0 | 0 | 0 | 0 | 0 | 138.096 | 0 | 288.8768 | 22.67% | 0 | 0 | 0 | 0% | 25.2907
5769 | 704 | 552 | 160 | 8.4625 | 27.6 | 354.3354 | 214.968 | 0 | 180.1874 | 53.6189 | 2.0594 | 0 | 51.5594 | 0 | 0 | 0 | 0 | 0 | 180.1874 | 0 | 460.9142 | 36.16% | 0 | 0 | 0 | 0% | 49.5
5770 | 719 | 687 | 177 | 10.8803 | 28.6 | 361.8852 | 230.2427 | 0 | 193.1067 | 82.8196 | 0 | 16.4098 | 66.4098 | 0 | 0 | 0 | 0 | 0 | 193.1067 | 0 | 645.2865 | 50.63% | 12.5863 | 0 | 13.0196 | 26.04% | 50
5771 | 643 | 782 | 244 | 11.2833 | 29.7 | 323.6331 | 211.5413 | 0 | 175.4098 | 99.4997 | 0 | 24.9998 | 74.4998 | 0 | 0 | 0 | 0 | 0 | 175.4098 | 0 | 812.7624 | 63.77% | 19.1749 | 0 | 32.8547 | 65.71% | 49.5
5772 | 768 | 871 | 190 | 9.4699 | 31 | 386.5478 | 255.3438 | 0 | 217.2529 | 101.9 | 5.2904 | 21.6096 | 75 | 0 | 0 | 0 | 0 | 0 | 217.2529 | 0 | 1020.1887 | 80.05% | 16.5745 | 0 | 50 | 100% | 48.1
5773 | 230 | 625 | 409 | 9.8729 | 31.2 | 115.763 | 76.05 | 0 | 49.0342 | 63.745 | 8.1225 | 0 | 55.6225 | 0 | 0 | 0 | 0 | 0 | 49.0342 | 0 | 1067.0051 | 83.72% | 0 | 0 | 50 | 100% | 47.5
5774 | 431 | 718 | 350 | 10.2758 | 30.6 | 216.9298 | 139.1704 | 0 | 108.2996 | 86.9363 | 19.8681 | 0 | 67.0681 | 0 | 0 | 0 | 0 | 0 | 108.2996 | 0 | 1170.4062 | 91.83% | 0 | 0 | 50 | 100% | 47.2
5775 | 415 | 601 | 283 | 10.8803 | 30.8 | 208.8767 | 128.8582 | 0 | 98.2756 | 65.0537 | 9.3268 | 0 | 55.7268 | 0 | 0 | 0 | 0 | 0 | 98.2756 | 0 | 1264.2367 | 99.19% | 0 | 0 | 50 | 100% | 46.4
5776 | 119 | 357 | 286 | 9.0669 | 29.1 | 59.8948 | 0 | 34.0836 | 0 | 29.4499 | 0 | 0 | 29.4499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.2367 | 99.19% | 0 | 16.3501 | 33.0895 | 66.18% | 45.8
5777 | 422 | 352 | 170 | 5.6416 | 29.6 | 212.3999 | 0 | 102.2676 | 0 | 30.1256 | 0 | 0 | 30.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.2367 | 99.19% | 0 | 15.4744 | 17.0842 | 34.17% | 45.6
5778 | 334 | 159 | 70 | 4.0297 | 28.7 | 168.108 | 0 | 0 | 0 | 8.8949 | 0 | 0 | 8.8949 | 0 | 0 | 0 | 58.7483 | 21.287 | 0 | 58.7483 | 1210.8215 | 95% | 0 | 16.5181 | 2.7756e-15 | 5.551e-15% | 46.7
5779 | 1 | 11 | 11 | 5.2387 | 27 | 0.50332 | 0 | 0 | 0 | 0.15803 | 0 | 0 | 0.15803 | 0 | 0 | 0 | 111.3333 | 43.742 | 0 | 111.3333 | 1101.2669 | 86.41% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.9
5780 | 0 | 0 | 0 | 5.2387 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7916 | 41.1 | 0 | 104.7916 | 999.2191 | 78.4% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.1
5781 | 0 | 0 | 0 | 2.2164 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1177 | 38.5 | 0 | 98.1177 | 904.5924 | 70.98% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38.5
5782 | 0 | 0 | 0 | 2.4178 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6258 | 36.3 | 0 | 92.6258 | 816.0916 | 64.03% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.3
5783 | 0 | 0 | 0 | 1.8134 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3304 | 34.6 | 0 | 88.3304 | 732.3377 | 57.46% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.6
5784 | 0 | 0 | 0 | 2.4178 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2463 | 33.8 | 0 | 86.2463 | 650.9301 | 51.07% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.8
5785 | 0 | 0 | 0 | 1.8134 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9777 | 33.3 | 0 | 84.9777 | 570.9406 | 44.8% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.3
5786 | 0 | 0 | 0 | 2.4178 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6529 | 33.6 | 0 | 85.6529 | 490.1593 | 38.46% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.6
5787 | 0 | 0 | 0 | 2.6193 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5216 | 36.1 | 0 | 91.5216 | 402.2351 | 31.56% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.1
5788 | 0 | 0 | 0 | 1.8134 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4919 | 39 | 0 | 98.4919 | 306.0552 | 24.01% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39
5789 | 0 | 0 | 0 | 1.8134 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0777 | 41.3 | 0 | 104.0777 | 203.296 | 15.95% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.3
5790 | 19 | 5 | 5 | 3.6268 | 19.8 | 9.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.296 | 15.95% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
5791 | 368 | 113 | 45 | 1.6119 | 22.4 | 185.2208 | 83.3433 | 0 | 60.0501 | 4.3488 | 0 | 0 | 4.3488 | 0 | 0 | 0 | 0 | 0 | 60.0501 | 0 | 260.6251 | 20.45% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 4.3488
5792 | 627 | 312 | 79 | 2.0149 | 25.3 | 315.58 | 173.6772 | 0 | 144.6163 | 25.1202 | 0 | 0 | 25.1202 | 0 | 0 | 0 | 63.0019 | 23.4798 | 144.6163 | 63.0019 | 341.0267 | 26.76% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 48.6
5793 | 750 | 513 | 99 | 2.6193 | 27.7 | 377.488 | 228.8312 | 0 | 195.9745 | 47.9178 | 0 | 0 | 47.9178 | 0 | 0 | 0 | 0 | 0 | 195.9745 | 0 | 527.6043 | 41.4% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 47.9178
5794 | 813 | 685 | 114 | 2.6193 | 29.6 | 409.197 | 260.2883 | 0 | 225.2296 | 79.3835 | 0 | 14.6918 | 64.6918 | 0 | 0 | 0 | 0 | 0 | 225.2296 | 0 | 742.0344 | 58.22% | 11.2686 | 0 | 11.6583 | 23.32% | 50
5795 | 854 | 815 | 119 | 5.4401 | 30.4 | 429.833 | 280.8891 | 0 | 243.5638 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 243.5638 | 0 | 973.9194 | 76.42% | 19.175 | 0 | 31.4964 | 62.99% | 50
5796 | 873 | 889 | 122 | 6.8506 | 31.5 | 439.3961 | 290.2459 | 0 | 251.6215 | 101 | 2.6817 | 23.3183 | 75 | 0 | 0 | 0 | 0 | 0 | 251.6215 | 0 | 1213.4759 | 95.21% | 17.8851 | 0 | 50 | 100% | 49
5797 | 861 | 895 | 131 | 8.8654 | 32 | 433.3563 | 196.0445 | 88.6352 | 168.8376 | 101.4 | 26.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 168.8376 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.6
5798 | 684 | 755 | 174 | 6.0446 | 32 | 344.2691 | 0 | 220.886 | 0 | 96.5222 | 24.2111 | 0 | 72.3111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.1
5799 | 556 | 671 | 244 | 9.6714 | 31.4 | 279.8445 | 0 | 172.6098 | 0 | 78.0328 | 15.5164 | 0 | 62.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47
5800 | 470 | 477 | 197 | 11.4848 | 30.5 | 236.5592 | 0 | 134.5235 | 0 | 45.095 | 0 | 0 | 45.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.095
5801 | 272 | 278 | 155 | 9.6714 | 29.6 | 136.9023 | 0 | 65.788 | 0 | 22.8629 | 0 | 0 | 22.8629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.6371 | 26.5837 | 53.17% | 45.5
5802 | 48 | 71 | 55 | 7.052 | 28.4 | 24.1592 | 0 | 0 | 0 | 4.2465 | 0 | 0 | 4.2465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 0.72176 | 1.444% | 29.2465
5803 | 11 | 12 | 11 | 8.8654 | 26.8 | 5.5365 | 0 | 0 | 0 | 0.17005 | 0 | 0 | 0.17005 | 0 | 0 | 0 | 109.584 | 43.0299 | 0 | 109.584 | 1166.9915 | 91.56% | 0 | 0 | 0.72176 | 1.444% | 43.2
5804 | 0 | 0 | 0 | 6.6491 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9352 | 40.4 | 0 | 102.9352 | 1066.9284 | 83.71% | 0 | 0 | 0.72176 | 1.444% | 40.4
5805 | 0 | 0 | 0 | 5.6416 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0478 | 38.1 | 0 | 97.0478 | 973.4314 | 76.38% | 0 | 0 | 0.72176 | 1.444% | 38.1
5806 | 0 | 0 | 0 | 3.8283 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2403 | 35.8 | 0 | 91.2403 | 886.4125 | 69.55% | 0 | 0 | 0.72176 | 1.444% | 35.8
5807 | 0 | 0 | 0 | 3.6268 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3022 | 34.2 | 0 | 87.3022 | 803.8186 | 63.07% | 0 | 0 | 0.72176 | 1.444% | 34.2
5808 | 0 | 0 | 0 | 2.6193 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1259 | 33.3 | 0 | 85.1259 | 723.6948 | 56.78% | 0 | 0 | 0.72176 | 1.444% | 33.3
5809 | 0 | 0 | 0 | 2.6193 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4251 | 32.6 | 0 | 83.4251 | 645.4792 | 50.65% | 0 | 0 | 0.72176 | 1.444% | 32.6
5810 | 0 | 0 | 0 | 2.0149 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6348 | 31.9 | 0 | 81.6348 | 569.2396 | 44.66% | 0 | 0 | 0.72176 | 1.444% | 31.9
5811 | 0 | 0 | 0 | 2.8208 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0662 | 32.1 | 0 | 82.0662 | 492.4944 | 38.64% | 0 | 0 | 0.72176 | 1.444% | 32.1
5812 | 0 | 0 | 0 | 3.6268 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0846 | 32.9 | 0 | 84.0846 | 413.4791 | 32.44% | 0 | 0 | 0.72176 | 1.444% | 32.9
5813 | 0 | 0 | 0 | 2.2164 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8572 | 34.1 | 0 | 86.8572 | 331.2038 | 25.99% | 0 | 0 | 0.72176 | 1.444% | 34.1
5814 | 15 | 5 | 5 | 1.6119 | 20.3 | 7.5498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4834 | 37.3 | 0 | 94.4834 | 239.827 | 18.82% | 0 | 0 | 0.72176 | 1.444% | 37.3
5815 | 246 | 104 | 57 | 0.80595 | 22.2 | 123.8161 | 0 | 55.4504 | 0 | 4.7139 | 0 | 0 | 4.7139 | 0 | 0 | 0 | 89.8601 | 35.2861 | 0 | 89.8601 | 154.0822 | 12.09% | 0 | 0 | 0.72176 | 1.444% | 40
5816 | 522 | 292 | 98 | 1.6119 | 24.3 | 262.7317 | 144.3064 | 0 | 117.2837 | 23.8118 | 0 | 0 | 23.8118 | 0 | 0 | 0 | 0 | 0 | 117.2837 | 0 | 265.4422 | 20.83% | 0 | 0 | 0.72176 | 1.444% | 23.8118
5817 | 627 | 491 | 143 | 2.0149 | 26.4 | 315.58 | 191.1473 | 0 | 160.8827 | 48.1383 | 0 | 2.6192 | 45.5192 | 0 | 0 | 0 | 0 | 0 | 160.8827 | 0 | 418.199 | 32.81% | 2.0089 | 0 | 2.8004 | 5.601% | 42.9
5818 | 723 | 667 | 158 | 2.2164 | 28.7 | 363.8985 | 231.4238 | 0 | 198.5539 | 81.8137 | 0 | 19.0069 | 62.8069 | 0 | 0 | 0 | 0 | 0 | 198.5539 | 0 | 606.7245 | 47.6% | 14.5783 | 0 | 17.885 | 35.77% | 43.8
5819 | 792 | 791 | 145 | 3.0223 | 30.2 | 398.6274 | 260.4314 | 0 | 225.2388 | 105.6149 | 5.9575 | 25 | 74.6575 | 0 | 0 | 0 | 0 | 0 | 225.2388 | 0 | 820.587 | 64.38% | 19.175 | 0 | 37.726 | 75.45% | 43.7
5820 | 823 | 876 | 154 | 6.0446 | 31.6 | 414.2302 | 273.6147 | 0 | 236.3694 | 107.2 | 16.7361 | 15.4639 | 75 | 0 | 0 | 0 | 0 | 0 | 236.3694 | 0 | 1045.018 | 81.99% | 11.8608 | 0 | 49.9987 | 100% | 42.8
5821 | 812 | 924 | 205 | 10.6788 | 31.7 | 408.6937 | 268.4449 | 0 | 228.7945 | 108.3 | 33.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 228.7945 | 0 | 1262.2566 | 99.04% | 0 | 0 | 49.9987 | 100% | 41.7
5822 | 715 | 862 | 257 | 12.4922 | 31.7 | 359.8719 | 0 | 230.92 | 0 | 108.8 | 33.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.2566 | 99.04% | 0 | 0 | 49.9987 | 100% | 41.2
5823 | 590 | 649 | 212 | 11.6862 | 30.8 | 296.9573 | 0 | 183.1337 | 0 | 85.7828 | 22.5414 | 0 | 63.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.2566 | 99.04% | 0 | 0 | 49.9987 | 100% | 40.7
5824 | 691 | 585 | 165 | 12.2907 | 31.3 | 347.7923 | 0 | 197.6405 | 0 | 71.0524 | 15.3762 | 0 | 55.6762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.2566 | 99.04% | 0 | 0 | 49.9987 | 100% | 40.3
5825 | 575 | 395 | 147 | 9.0669 | 31 | 289.4075 | 0 | 138.801 | 0 | 34.1188 | 0 | 0 | 34.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.2566 | 99.04% | 0 | 6.6812 | 43.0865 | 86.17% | 40.8
5826 | 184 | 119 | 64 | 9.0669 | 29 | 92.6104 | 0 | 0 | 0 | 6.5401 | 0 | 0 | 6.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.2566 | 99.04% | 0 | 25 | 17.2218 | 34.44% | 31.5401
5827 | 41 | 15 | 12 | 6.8506 | 27.3 | 20.636 | 0 | 0 | 0 | 0.18093 | 0 | 0 | 0.18093 | 0 | 0 | 0 | 63.2018 | 23.3715 | 0 | 63.2018 | 1204.5266 | 94.51% | 0 | 16.6476 | 0 | 0% | 40.2
5828 | 0 | 0 | 0 | 4.2312 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5441 | 37.7 | 0 | 96.5441 | 1111.7445 | 87.23% | 0 | 0 | 0 | 0% | 37.7
5829 | 0 | 0 | 0 | 3.8283 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1169 | 35.6 | 0 | 91.1169 | 1024.9361 | 80.42% | 0 | 0 | 0 | 0% | 35.6
5830 | 0 | 0 | 0 | 1.0074 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3656 | 33.3 | 0 | 85.3656 | 944.6051 | 74.12% | 0 | 0 | 0 | 0% | 33.3
5831 | 0 | 0 | 0 | 1.6119 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3851 | 31.7 | 0 | 81.3851 | 868.7182 | 68.16% | 0 | 0 | 0 | 0% | 31.7
5832 | 0 | 0 | 0 | 1.4104 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1238 | 30.8 | 0 | 79.1238 | 795.3114 | 62.4% | 0 | 0 | 0 | 0% | 30.8
5833 | 0 | 0 | 0 | 2.2164 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4239 | 30.1 | 0 | 77.4239 | 723.7592 | 56.79% | 0 | 0 | 0 | 0% | 30.1
5834 | 0 | 0 | 0 | 1.6119 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6198 | 29.8 | 0 | 76.6198 | 652.9995 | 51.24% | 0 | 0 | 0 | 0% | 29.8
5835 | 0 | 0 | 0 | 1.2089 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1129 | 30.1 | 0 | 77.1129 | 581.712 | 45.64% | 0 | 0 | 0 | 0% | 30.1
5836 | 0 | 0 | 0 | 1.6119 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.8858 | 30 | 0 | 76.8858 | 510.6625 | 40.07% | 0 | 0 | 0 | 0% | 30
5837 | 0 | 0 | 0 | 2.4178 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7334 | 30.4 | 0 | 77.7334 | 438.651 | 34.42% | 0 | 0 | 0 | 0% | 30.4
5838 | 19 | 5 | 4 | 2.6193 | 19.7 | 9.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3282 | 32.7 | 0 | 83.3282 | 360.3826 | 28.28% | 0 | 0 | 0 | 0% | 32.7
5839 | 382 | 110 | 41 | 2.2164 | 21.2 | 192.2672 | 85.6928 | 0 | 62.2096 | 4.2215 | 0 | 0 | 4.2215 | 0 | 0 | 0 | 78.859 | 30.7785 | 62.2096 | 78.859 | 345.1257 | 27.08% | 0 | 0 | 0 | 0% | 35
5840 | 638 | 308 | 73 | 1.8134 | 25.2 | 321.1165 | 176.0194 | 0 | 146.9028 | 25.1948 | 0 | 0 | 25.1948 | 0 | 0 | 0 | 0 | 0 | 146.9028 | 0 | 481.9896 | 37.82% | 0 | 0 | 0 | 0% | 25.1948
5841 | 764 | 510 | 90 | 1.6119 | 28.3 | 384.5345 | 232.7206 | 0 | 199.9701 | 57.1858 | 0 | 9.4929 | 47.6929 | 0 | 0 | 0 | 0 | 0 | 199.9701 | 0 | 668.2943 | 52.44% | 7.2811 | 0 | 7.535 | 15.07% | 38.2
5842 | 834 | 683 | 100 | 3.6268 | 30.1 | 419.7667 | 266.8945 | 0 | 231.0899 | 90.6571 | 0.47853 | 25 | 65.1785 | 0 | 0 | 0 | 0 | 0 | 231.0899 | 0 | 883.5922 | 69.33% | 19.175 | 0 | 27.3789 | 54.76% | 39.7
5843 | 869 | 816 | 112 | 5.8431 | 31.4 | 437.3828 | 285.6786 | 0 | 247.8745 | 109.7 | 9.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 247.8745 | 0 | 1114.5277 | 87.45% | 19.175 | 0 | 47.2227 | 94.45% | 40.3
5844 | 775 | 857 | 181 | 7.455 | 32.7 | 390.071 | 257.6493 | 0 | 220.6161 | 110.6 | 32.1011 | 3.4989 | 75 | 0 | 0 | 0 | 0 | 0 | 220.6161 | 0 | 1274.5104 | 100% | 2.6837 | 0 | 50 | 100% | 39.4
5845 | 794 | 893 | 192 | 12.2907 | 33.1 | 399.634 | 0 | 262.461 | 0 | 111.5 | 36.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.5
5846 | 467 | 657 | 255 | 12.0892 | 32.7 | 235.0492 | 0 | 150.84 | 0 | 86.737 | 24.3185 | 0 | 62.4185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.1
5847 | 119 | 459 | 368 | 11.8877 | 31.3 | 59.8948 | 0 | 36.9307 | 0 | 38.3792 | 0.18959 | 0 | 38.1896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38
5848 | 273 | 451 | 291 | 11.0818 | 30.5 | 137.4056 | 0 | 78.0287 | 0 | 43.172 | 2.636 | 0 | 40.536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.9
5849 | 577 | 386 | 138 | 9.4699 | 30.6 | 290.4141 | 0 | 139.0089 | 0 | 33.516 | 0 | 0 | 33.516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.684 | 44.1187 | 88.24% | 39.2
5850 | 311 | 153 | 76 | 7.455 | 29.3 | 156.5317 | 0 | 0 | 0 | 9.0242 | 0 | 0 | 9.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.2502 | 36.5% | 34.0242
5851 | 4 | 10 | 9 | 5.0372 | 26.6 | 2.0133 | 0 | 0 | 0 | 0.06857 | 0 | 0 | 0.06857 | 0 | 0 | 0 | 61.6986 | 22.7936 | 0 | 61.6986 | 1218.2029 | 95.58% | 0 | 17.6378 | 0 | 0% | 40.5
5852 | 0 | 0 | 0 | 2.4178 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1643 | 38.1 | 0 | 97.1643 | 1124.6356 | 88.24% | 0 | 0 | 0 | 0% | 38.1
5853 | 0 | 0 | 0 | 2.0149 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9343 | 35.6 | 0 | 90.9343 | 1037.9725 | 81.44% | 0 | 0 | 0 | 0% | 35.6
5854 | 0 | 0 | 0 | 2.2164 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8299 | 33.5 | 0 | 85.8299 | 957.0838 | 75.09% | 0 | 0 | 0 | 0% | 33.5
5855 | 0 | 0 | 0 | 2.0149 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5939 | 32.2 | 0 | 82.5939 | 879.8215 | 69.03% | 0 | 0 | 0 | 0% | 32.2
5856 | 0 | 0 | 0 | 2.4178 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5613 | 31.4 | 0 | 80.5613 | 804.7982 | 63.15% | 0 | 0 | 0 | 0% | 31.4
5857 | 0 | 0 | 0 | 2.2164 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9542 | 31.2 | 0 | 79.9542 | 730.4153 | 57.31% | 0 | 0 | 0 | 0% | 31.2
5858 | 0 | 0 | 0 | 2.4178 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8502 | 32 | 0 | 81.8502 | 653.9035 | 51.31% | 0 | 0 | 0 | 0% | 32
5859 | 0 | 0 | 0 | 0.60446 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5214 | 35.2 | 0 | 89.5214 | 568.4595 | 44.6% | 0 | 0 | 0 | 0% | 35.2
5860 | 0 | 0 | 0 | 2.2164 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.375 | 38.9 | 0 | 98.375 | 472.5328 | 37.08% | 0 | 0 | 0 | 0% | 38.9
5861 | 0 | 0 | 0 | 3.6268 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5343 | 41.4 | 0 | 104.5343 | 369.462 | 28.99% | 0 | 0 | 0 | 0% | 41.4
5862 | 2 | 2 | 2 | 4.8357 | 21.2 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.092 | 44.1 | 0 | 111.092 | 258.6448 | 20.29% | 0 | 0 | 0 | 0% | 44.1
5863 | 57 | 54 | 40 | 10.6788 | 21 | 28.6891 | 0 | 12.7243 | 0 | 2.7604 | 0 | 0 | 2.7604 | 0 | 0 | 0 | 95.3986 | 37.6387 | 0 | 95.3986 | 166.2496 | 13.04% | 0 | 0 | 0 | 0% | 40.3991
5864 | 527 | 292 | 96 | 12.2907 | 23.6 | 265.2483 | 145.0976 | 0 | 112.6146 | 24.5618 | 0 | 0 | 24.5618 | 0 | 0 | 0 | 0 | 0 | 112.6146 | 0 | 273.0507 | 21.42% | 0 | 0 | 0 | 0% | 24.5618
5865 | 695 | 499 | 116 | 13.0966 | 25.9 | 349.8056 | 211.5248 | 0 | 174.2168 | 49.3676 | 0.63382 | 0 | 48.7338 | 0 | 0 | 0 | 0 | 0 | 174.2168 | 0 | 438.2738 | 34.39% | 0 | 0 | 0 | 0% | 48.1
5866 | 802 | 675 | 115 | 12.2907 | 27.5 | 403.6605 | 256.5963 | 0 | 216.6532 | 86.2597 | 0 | 18.5799 | 67.6799 | 0 | 0 | 0 | 0 | 0 | 216.6532 | 0 | 643.7426 | 50.51% | 14.2507 | 0 | 14.75 | 29.5% | 49.1
5867 | 839 | 804 | 125 | 14.3056 | 28.4 | 422.2833 | 275.7452 | 0 | 233.4141 | 101.3 | 1.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 233.4141 | 0 | 865.1071 | 67.88% | 19.175 | 0 | 34.5968 | 69.19% | 48.7
5868 | 867 | 880 | 123 | 15.5145 | 28.7 | 436.3762 | 288.2266 | 0 | 244.5518 | 101.8 | 7.3973 | 19.4027 | 75 | 0 | 0 | 0 | 0 | 0 | 244.5518 | 0 | 1097.0342 | 86.07% | 14.8819 | 0 | 50 | 100% | 48.2
5869 | 873 | 888 | 119 | 15.313 | 29 | 439.3961 | 288.5379 | 0 | 244.9716 | 101.8 | 26.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 244.9716 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.2
5870 | 863 | 838 | 115 | 16.3204 | 29.2 | 434.3629 | 0 | 278.7761 | 0 | 102.3 | 27.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.7
5871 | 847 | 732 | 105 | 15.9175 | 29.4 | 426.3098 | 0 | 262.8134 | 0 | 99.2357 | 26.3179 | 0 | 72.9179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.6
5872 | 780 | 570 | 100 | 13.0966 | 29.6 | 392.5876 | 0 | 222.7799 | 0 | 65.6923 | 9.9961 | 0 | 55.6961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.7
5873 | 660 | 369 | 86 | 12.0892 | 29.3 | 332.1895 | 0 | 158.6892 | 0 | 32.8872 | 0 | 0 | 32.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 12.8128 | 36.7403 | 73.48% | 45.7
5874 | 395 | 146 | 53 | 12.2907 | 27.9 | 198.8104 | 0 | 0 | 0 | 8.3493 | 0 | 0 | 8.3493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.8677 | 21.74% | 33.3493
5875 | 22 | 10 | 8 | 9.2684 | 26.1 | 11.073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8475 | 33.2981 | 0 | 85.8475 | 1193.7546 | 93.66% | 0 | 10.5019 | 0 | 0% | 43.8
5876 | 0 | 0 | 0 | 5.2387 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2544 | 40.6 | 0 | 103.2544 | 1093.1195 | 85.77% | 0 | 0 | 0 | 0% | 40.6
5877 | 0 | 0 | 0 | 6.6491 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9219 | 38.5 | 0 | 97.9219 | 998.4717 | 78.34% | 0 | 0 | 0 | 0% | 38.5
5878 | 0 | 0 | 0 | 7.052 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.798 | 36.5 | 0 | 92.798 | 909.4822 | 71.36% | 0 | 0 | 0 | 0% | 36.5
5879 | 0 | 0 | 0 | 5.4401 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3341 | 35.1 | 0 | 89.3341 | 824.3941 | 64.68% | 0 | 0 | 0 | 0% | 35.1
5880 | 0 | 0 | 0 | 6.4476 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6148 | 34.4 | 0 | 87.6148 | 741.3194 | 58.17% | 0 | 0 | 0 | 0% | 34.4
5881 | 0 | 0 | 0 | 7.455 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6424 | 34 | 0 | 86.6424 | 659.3904 | 51.74% | 0 | 0 | 0 | 0% | 34
5882 | 0 | 0 | 0 | 3.6268 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3221 | 34.3 | 0 | 87.3221 | 576.579 | 45.24% | 0 | 0 | 0 | 0% | 34.3
5883 | 0 | 0 | 0 | 2.8208 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5472 | 36.9 | 0 | 93.5472 | 486.3906 | 38.16% | 0 | 0 | 0 | 0% | 36.9
5884 | 0 | 0 | 0 | 3.2238 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1336 | 40.1 | 0 | 101.1336 | 387.0312 | 30.37% | 0 | 0 | 0 | 0% | 40.1
5885 | 0 | 0 | 0 | 2.2164 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.1882 | 42.2 | 0 | 106.1882 | 281.7099 | 22.1% | 0 | 0 | 0 | 0% | 42.2
5886 | 8 | 4 | 3 | 2.4178 | 19.6 | 4.0265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.9218 | 45 | 0 | 112.9218 | 168.305 | 13.21% | 0 | 0 | 0 | 0% | 45
5887 | 303 | 100 | 45 | 2.4178 | 21.7 | 152.5052 | 67.1811 | 0 | 44.4728 | 4.197 | 0 | 0 | 4.197 | 0 | 0 | 0 | 0 | 0 | 44.4728 | 0 | 210.9212 | 16.55% | 0 | 0 | 0 | 0% | 4.197
5888 | 585 | 295 | 82 | 3.0223 | 23.9 | 294.4407 | 160.7313 | 0 | 132.0669 | 24.8957 | 0 | 0 | 24.8957 | 0 | 0 | 0 | 63.24 | 23.7043 | 132.0669 | 63.24 | 279.5592 | 21.93% | 0 | 0 | 0 | 0% | 48.6
5889 | 725 | 498 | 104 | 6.8506 | 26.3 | 364.9051 | 220.4672 | 0 | 186.2402 | 48.7898 | 0 | 0 | 48.7898 | 0 | 0 | 0 | 0 | 0 | 186.2402 | 0 | 457.5247 | 35.9% | 0 | 0 | 0 | 0% | 48.7898
5890 | 798 | 671 | 118 | 7.6565 | 28.2 | 401.6473 | 255.2583 | 0 | 218.1808 | 83.6805 | 0 | 16.8403 | 66.8403 | 0 | 0 | 0 | 0 | 0 | 218.1808 | 0 | 666.0118 | 52.26% | 12.9165 | 0 | 13.3709 | 26.74% | 50
5891 | 832 | 797 | 128 | 7.2535 | 29.6 | 418.7601 | 273.3733 | 0 | 235.3936 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 235.3936 | 0 | 890.9469 | 69.91% | 19.175 | 0 | 33.2206 | 66.44% | 50
5892 | 853 | 870 | 131 | 6.0446 | 30.7 | 429.3297 | 283.5643 | 0 | 245.7427 | 100 | 3.8669 | 21.1331 | 75 | 0 | 0 | 0 | 0 | 0 | 245.7427 | 0 | 1125.7713 | 88.33% | 16.2091 | 0 | 50 | 100% | 50
5893 | 855 | 880 | 131 | 6.6491 | 31.5 | 430.3364 | 282.552 | 0 | 244.4441 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 244.4441 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 50
5894 | 839 | 826 | 130 | 9.6714 | 31.5 | 422.2833 | 0 | 271.0519 | 0 | 100.3 | 25.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.7
5895 | 797 | 712 | 127 | 9.4699 | 31.2 | 401.144 | 0 | 247.2545 | 0 | 92.3909 | 21.9954 | 0 | 70.3954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.4
5896 | 718 | 549 | 122 | 12.0892 | 30.1 | 361.3819 | 0 | 204.9231 | 0 | 60.8361 | 6.9181 | 0 | 53.9181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47
5897 | 391 | 267 | 90 | 10.8803 | 28.6 | 196.7971 | 0 | 93.8234 | 0 | 22.576 | 0 | 0 | 22.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.324 | 24.824 | 49.65% | 46.9
5898 | 0 | 34 | 33 | 8.0595 | 27 | 0 | 0 | 0 | 0 | 1.934 | 0 | 0 | 1.934 | 0 | 0 | 0 | 60.1423 | 22.0821 | 0 | 60.1423 | 1219.737 | 95.7% | 0 | 23.9839 | 0 | 0% | 48
5899 | 0 | 6 | 6 | 5.2387 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.9053 | 44.5 | 0 | 112.9053 | 1108.0291 | 86.94% | 0 | 0 | 0 | 0% | 44.5
5900 | 0 | 0 | 0 | 6.2461 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.3555 | 41.1 | 0 | 104.3555 | 1006.007 | 78.93% | 0 | 0 | 0 | 0% | 41.1
5901 | 0 | 0 | 0 | 7.6565 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4799 | 39.2 | 0 | 99.4799 | 909.3716 | 71.35% | 0 | 0 | 0 | 0% | 39.2
5902 | 0 | 0 | 0 | 7.2535 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4797 | 37.2 | 0 | 94.4797 | 818.4258 | 64.21% | 0 | 0 | 0 | 0% | 37.2
5903 | 0 | 0 | 0 | 4.6342 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0237 | 35.8 | 0 | 91.0237 | 731.4026 | 57.39% | 0 | 0 | 0 | 0% | 35.8
5904 | 0 | 0 | 0 | 5.6416 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0732 | 35 | 0 | 89.0732 | 646.5946 | 50.73% | 0 | 0 | 0 | 0% | 35
5905 | 0 | 0 | 0 | 5.6416 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8192 | 34.5 | 0 | 87.8192 | 563.2297 | 44.19% | 0 | 0 | 0 | 0% | 34.5
5906 | 0 | 0 | 0 | 4.0297 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7273 | 34.9 | 0 | 88.7273 | 478.6837 | 37.56% | 0 | 0 | 0 | 0% | 34.9
5907 | 0 | 0 | 0 | 4.4327 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0087 | 37.5 | 0 | 95.0087 | 386.8078 | 30.35% | 0 | 0 | 0 | 0% | 37.5
5908 | 0 | 0 | 0 | 2.8208 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7047 | 40.7 | 0 | 102.7047 | 285.7696 | 22.42% | 0 | 0 | 0 | 0% | 40.7
5909 | 0 | 0 | 0 | 3.2238 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7691 | 42.8 | 0 | 107.7691 | 178.7389 | 14.02% | 0 | 0 | 0 | 0% | 42.8
5910 | 3 | 3 | 3 | 3.2238 | 20.1 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1555 | 26.9989 | 0 | 70.1555 | 114.132 | 8.955% | 0 | 0 | 0 | 0% | 26.9989
5911 | 235 | 95 | 53 | 2.2164 | 21.2 | 118.2796 | 0 | 51.7175 | 0 | 4.576 | 0 | 0 | 4.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.132 | 8.955% | 0 | 0 | 0 | 0% | 4.576
5912 | 497 | 287 | 107 | 5.0372 | 23 | 250.1487 | 136.2642 | 0 | 108.4624 | 24.3519 | 0 | 0 | 24.3519 | 0 | 0 | 0 | 0 | 0 | 108.4624 | 0 | 217.8728 | 17.09% | 0 | 0 | 0 | 0% | 24.3519
5913 | 641 | 483 | 137 | 5.2387 | 24.5 | 322.6264 | 194.7548 | 0 | 163.1179 | 47.37 | 0 | 0 | 47.37 | 0 | 0 | 0 | 0 | 0 | 163.1179 | 0 | 373.8898 | 29.34% | 0 | 0 | 0 | 0% | 47.37
5914 | 716 | 659 | 163 | 2.6193 | 27 | 360.3752 | 228.9758 | 0 | 196.1059 | 77.8643 | 0 | 13.9322 | 63.9322 | 0 | 0 | 0 | 0 | 0 | 196.1059 | 0 | 561.4588 | 44.05% | 10.686 | 0 | 11.0636 | 22.13% | 50
5915 | 755 | 782 | 175 | 3.4253 | 28.6 | 380.0046 | 248.0077 | 0 | 213.5378 | 100 | 0 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 213.5378 | 0 | 765.701 | 60.08% | 19.175 | 0 | 30.9161 | 61.83% | 50
5916 | 770 | 863 | 196 | 5.0372 | 30.1 | 387.5544 | 255.9651 | 0 | 220.4208 | 100 | 0.96805 | 24.032 | 75 | 0 | 0 | 0 | 0 | 0 | 220.4208 | 0 | 976.5264 | 76.62% | 18.4325 | 0 | 50 | 100% | 50
5917 | 719 | 873 | 244 | 10.2758 | 30.4 | 361.8852 | 237.5768 | 0 | 200.3476 | 100 | 25 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 200.3476 | 0 | 1168.1524 | 91.65% | 0 | 0 | 50 | 100% | 50
5918 | 461 | 653 | 268 | 11.2833 | 29.5 | 232.0293 | 148.9491 | 0 | 116.9574 | 78.1229 | 14.3114 | 0 | 63.8114 | 0 | 0 | 0 | 0 | 0 | 116.9574 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 49.5
5919 | 643 | 732 | 258 | 12.4922 | 29.1 | 323.6331 | 0 | 199.4422 | 0 | 93.6902 | 22.6451 | 0 | 71.0451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 48.4
5920 | 629 | 564 | 192 | 11.4848 | 28.6 | 316.5866 | 0 | 179.3898 | 0 | 61.6909 | 7.2955 | 0 | 54.3955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.1
5921 | 122 | 165 | 108 | 9.8729 | 26.6 | 61.4047 | 0 | 29.2159 | 0 | 12.9592 | 0 | 0 | 12.9592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.1205 | 48.24% | 37.9592
5922 | 0 | 16 | 16 | 9.4699 | 25.2 | 0 | 0 | 0 | 0 | 0.71842 | 0 | 0 | 0.71842 | 0 | 0 | 0 | 64.5763 | 24.1807 | 0 | 64.5763 | 1215.4372 | 95.37% | 0 | 23.3009 | 0 | 0% | 48.2
5923 | 0 | 4 | 4 | 4.2312 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.0482 | 44.7 | 0 | 113.0482 | 1103.1401 | 86.55% | 0 | 0 | 0 | 0% | 44.7
5924 | 0 | 0 | 0 | 0.80595 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7821 | 41.3 | 0 | 104.7821 | 1000.5429 | 78.5% | 0 | 0 | 0 | 0% | 41.3
5925 | 0 | 0 | 0 | 2.8208 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.163 | 39.4 | 0 | 100.163 | 903.3218 | 70.88% | 0 | 0 | 0 | 0% | 39.4
5926 | 0 | 0 | 0 | 2.0149 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6494 | 37.2 | 0 | 94.6494 | 812.3667 | 63.74% | 0 | 0 | 0 | 0% | 37.2
5927 | 0 | 0 | 0 | 3.0223 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8692 | 35.7 | 0 | 90.8692 | 725.614 | 56.93% | 0 | 0 | 0 | 0% | 35.7
5928 | 0 | 0 | 0 | 2.2164 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8336 | 34.9 | 0 | 88.8336 | 641.0894 | 50.3% | 0 | 0 | 0 | 0% | 34.9
5929 | 0 | 0 | 0 | 1.6119 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0953 | 34.6 | 0 | 88.0953 | 557.425 | 43.74% | 0 | 0 | 0 | 0% | 34.6
5930 | 0 | 0 | 0 | 2.8208 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8427 | 34.9 | 0 | 88.8427 | 472.8701 | 37.1% | 0 | 0 | 0 | 0% | 34.9
5931 | 0 | 0 | 0 | 2.0149 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9089 | 37.4 | 0 | 94.9089 | 381.268 | 29.91% | 0 | 0 | 0 | 0% | 37.4
5932 | 0 | 0 | 0 | 2.8208 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4363 | 40.5 | 0 | 102.4363 | 280.7819 | 22.03% | 0 | 0 | 0 | 0% | 40.5
5933 | 0 | 0 | 0 | 3.4253 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.1552 | 42.4 | 0 | 107.1552 | 174.881 | 13.72% | 0 | 0 | 0 | 0% | 42.4
5934 | 0 | 2 | 1 | 3.0223 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174.881 | 13.72% | 0 | 0 | 0 | 0% | 0
5935 | 0 | 31 | 31 | 2.8208 | 22.6 | 0 | 0 | 0 | 0 | 1.7874 | 0 | 0 | 1.7874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174.881 | 13.72% | 0 | 0 | 0 | 0% | 1.7874
5936 | 256 | 271 | 173 | 4.0297 | 23.8 | 128.8493 | 70.0378 | 0 | 46.5117 | 21.9963 | 0 | 0 | 21.9963 | 0 | 0 | 0 | 0 | 0 | 46.5117 | 0 | 219.4811 | 17.22% | 0 | 0 | 0 | 0% | 21.9963
5937 | 399 | 473 | 253 | 5.0372 | 25.3 | 200.8236 | 121.1217 | 0 | 94.4597 | 42.9566 | 0 | 0 | 42.9566 | 0 | 0 | 0 | 0 | 0 | 94.4597 | 0 | 310.0586 | 24.33% | 0 | 0 | 0 | 0% | 42.9566
5938 | 450 | 555 | 241 | 5.4401 | 26.5 | 226.4928 | 143.8757 | 0 | 115.5206 | 57.7308 | 0 | 4.3654 | 53.3654 | 0 | 0 | 0 | 0 | 0 | 115.5206 | 0 | 420.8315 | 33.02% | 3.3483 | 0 | 3.4671 | 6.934% | 49
5939 | 591 | 762 | 284 | 5.6416 | 27.9 | 297.4606 | 194.0841 | 0 | 162.3031 | 98.239 | 0.06952 | 25 | 73.1695 | 0 | 0 | 0 | 0 | 0 | 162.3031 | 0 | 576.4641 | 45.23% | 19.175 | 0 | 23.3225 | 46.65% | 48.1
5940 | 230 | 603 | 399 | 9.2684 | 28.3 | 115.763 | 76.4505 | 0 | 49.7002 | 61.045 | 0 | 6.7725 | 54.2725 | 0 | 0 | 0 | 0 | 0 | 49.7002 | 0 | 624.1217 | 48.97% | 5.1945 | 0 | 28.7014 | 57.4% | 47.5
5941 | 196 | 570 | 391 | 10.4773 | 28.3 | 98.6502 | 64.755 | 0 | 38.3386 | 54.6155 | 0 | 3.7077 | 50.9077 | 0 | 0 | 0 | 0 | 0 | 38.3386 | 0 | 660.8846 | 51.85% | 2.8438 | 0 | 31.6462 | 63.29% | 47.2
5942 | 46 | 324 | 280 | 10.2758 | 27.9 | 23.1526 | 0 | 14.8642 | 0 | 26.0854 | 0 | 0 | 26.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660.8846 | 51.85% | 0 | 20.7146 | 10.1998 | 20.4% | 46.8
5943 | 1 | 122 | 120 | 10.4773 | 26.6 | 0.50332 | 0 | 0.31012 | 0 | 8.4477 | 0 | 0 | 8.4477 | 0 | 0 | 0 | 72.8499 | 27.7005 | 0 | 72.8499 | 593.8219 | 46.59% | 0 | 9.8518 | 0 | 0% | 46
5944 | 7 | 192 | 187 | 10.0743 | 26 | 3.5232 | 0 | 1.9949 | 0 | 14.244 | 0 | 0 | 14.244 | 0 | 0 | 0 | 79.6432 | 30.756 | 0 | 79.6432 | 519.9377 | 40.8% | 0 | 0 | 0 | 0% | 45
5945 | 149 | 203 | 136 | 10.0743 | 25.8 | 74.9943 | 0 | 35.6093 | 0 | 16.4035 | 0 | 0 | 16.4035 | 0 | 0 | 0 | 75.7789 | 29.0965 | 0 | 75.7789 | 450.0177 | 35.31% | 0 | 0 | 0 | 0% | 45.5
5946 | 77 | 105 | 90 | 9.6714 | 24.9 | 38.7554 | 0 | 0 | 0 | 7.2965 | 0 | 0 | 7.2965 | 0 | 0 | 0 | 100.3917 | 39.4035 | 0 | 100.3917 | 352.6792 | 27.67% | 0 | 0 | 0 | 0% | 46.7
5947 | 0 | 11 | 11 | 9.6714 | 23.9 | 0 | 0 | 0 | 0 | 0.16639 | 0 | 0 | 0.16639 | 0 | 0 | 0 | 108.5289 | 42.8336 | 0 | 108.5289 | 245.565 | 19.27% | 0 | 0 | 0 | 0% | 43
5948 | 0 | 0 | 0 | 9.2684 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.3974 | 25.6179 | 0 | 67.3974 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 25.6179
5949 | 0 | 0 | 0 | 7.052 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5950 | 0 | 0 | 0 | 4.8357 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5951 | 0 | 0 | 0 | 2.4178 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5952 | 0 | 0 | 0 | 2.0149 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5953 | 0 | 0 | 0 | 3.4253 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5954 | 0 | 0 | 0 | 3.2238 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5955 | 0 | 0 | 0 | 2.6193 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5956 | 0 | 0 | 0 | 1.4104 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5957 | 0 | 0 | 0 | 1.6119 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5958 | 4 | 3 | 3 | 3.2238 | 19 | 2.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 0
5959 | 261 | 92 | 46 | 3.4253 | 20 | 131.3658 | 0 | 56.5674 | 0 | 4.2765 | 0 | 0 | 4.2765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.6303 | 14.41% | 0 | 0 | 0 | 0% | 4.2765
5960 | 563 | 290 | 89 | 4.8357 | 22.2 | 283.3677 | 153.693 | 0 | 124.8986 | 25.4961 | 0 | 0 | 25.4961 | 0 | 0 | 0 | 0 | 0 | 124.8986 | 0 | 302.4715 | 23.73% | 0 | 0 | 0 | 0% | 25.4961
5961 | 546 | 423 | 133 | 8.0595 | 24.1 | 274.8113 | 165.5984 | 0 | 134.1542 | 42.6276 | 0 | 0 | 42.6276 | 0 | 0 | 0 | 0 | 0 | 134.1542 | 0 | 430.1196 | 33.75% | 0 | 0 | 0 | 0% | 42.6276
5962 | 658 | 612 | 155 | 9.0669 | 25.1 | 331.1828 | 210.3284 | 0 | 175.4673 | 76.883 | 0 | 14.7915 | 62.0915 | 0 | 0 | 0 | 0 | 0 | 175.4673 | 0 | 597.077 | 46.85% | 11.3451 | 0 | 11.7489 | 23.5% | 47.3
5963 | 800 | 818 | 179 | 8.6639 | 26.6 | 402.6539 | 262.6488 | 0 | 224.4356 | 103.7 | 3.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 224.4356 | 0 | 810.628 | 63.6% | 19.175 | 0 | 31.6065 | 63.21% | 46.3
5964 | 678 | 876 | 290 | 6.4476 | 27.7 | 341.2492 | 225.3007 | 0 | 191.0329 | 104.6 | 6.4434 | 23.1566 | 75 | 0 | 0 | 0 | 0 | 0 | 191.0329 | 0 | 992.3962 | 77.86% | 17.7611 | 0 | 50 | 100% | 45.4
5965 | 733 | 917 | 278 | 9.4699 | 28.2 | 368.9316 | 242.1378 | 0 | 204.96 | 104.9 | 29.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 204.96 | 0 | 1187.4161 | 93.17% | 0 | 0 | 50 | 100% | 45.1
5966 | 336 | 606 | 323 | 10.4773 | 28.3 | 169.1146 | 108.5853 | 0 | 79.4198 | 69.3318 | 12.2659 | 0 | 57.0659 | 0 | 0 | 0 | 0 | 0 | 79.4198 | 0 | 1262.9841 | 99.1% | 0 | 0 | 50 | 100% | 44.8
5967 | 271 | 426 | 237 | 9.4699 | 27.7 | 136.399 | 0 | 84.0255 | 0 | 41.0005 | 0 | 0 | 41.0005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.9841 | 99.1% | 0 | 2.7995 | 47.1013 | 94.2% | 43.8
5968 | 299 | 345 | 170 | 8.8654 | 28.1 | 150.4919 | 0 | 85.1454 | 0 | 32.1883 | 0 | 0 | 32.1883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.9841 | 99.1% | 0 | 10.9117 | 35.8029 | 71.61% | 43.1
5969 | 293 | 215 | 103 | 11.0818 | 27.2 | 147.472 | 0 | 69.8807 | 0 | 20.0391 | 0 | 0 | 20.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.9841 | 99.1% | 0 | 23.6609 | 11.3027 | 22.61% | 43.7
5970 | 267 | 122 | 62 | 11.2833 | 25.9 | 134.3857 | 0 | 0 | 0 | 7.4345 | 0 | 0 | 7.4345 | 0 | 0 | 0 | 69.4252 | 26.2493 | 0 | 69.4252 | 1199.1941 | 94.09% | 0 | 10.9162 | 0 | 0% | 44.6
5971 | 0 | 6 | 6 | 9.4699 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5596 | 41.2 | 0 | 104.5596 | 1096.7856 | 86.06% | 0 | 0 | 0 | 0% | 41.2
5972 | 0 | 0 | 0 | 10.4773 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3877 | 38.4 | 0 | 97.3877 | 1002.3481 | 78.65% | 0 | 0 | 0 | 0% | 38.4
5973 | 0 | 0 | 0 | 9.6714 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6869 | 36.9 | 0 | 93.6869 | 912.1604 | 71.57% | 0 | 0 | 0 | 0% | 36.9
5974 | 0 | 0 | 0 | 6.6491 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3159 | 35.1 | 0 | 89.3159 | 827.0051 | 64.89% | 0 | 0 | 0 | 0% | 35.1
5975 | 0 | 0 | 0 | 7.2535 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4486 | 33.5 | 0 | 85.4486 | 746.4134 | 58.56% | 0 | 0 | 0 | 0% | 33.5
5976 | 0 | 0 | 0 | 7.858 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0217 | 32.5 | 0 | 83.0217 | 668.554 | 52.46% | 0 | 0 | 0 | 0% | 32.5
5977 | 0 | 0 | 0 | 6.2461 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0792 | 32.1 | 0 | 82.0792 | 591.7445 | 46.43% | 0 | 0 | 0 | 0% | 32.1
5978 | 0 | 0 | 0 | 8.0595 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3393 | 31.8 | 0 | 81.3393 | 515.7462 | 40.47% | 0 | 0 | 0 | 0% | 31.8
5979 | 0 | 0 | 0 | 6.2461 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7633 | 32 | 0 | 81.7633 | 439.2484 | 34.46% | 0 | 0 | 0 | 0% | 32
5980 | 0 | 0 | 0 | 7.858 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8841 | 32.9 | 0 | 83.8841 | 360.3372 | 28.27% | 0 | 0 | 0 | 0% | 32.9
5981 | 0 | 0 | 0 | 7.455 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3911 | 33.9 | 0 | 86.3911 | 278.5503 | 21.86% | 0 | 0 | 0 | 0% | 33.9
5982 | 2 | 3 | 3 | 8.261 | 21.2 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278.5503 | 21.86% | 0 | 0 | 0 | 0% | 0
5983 | 266 | 96 | 48 | 8.4625 | 21.3 | 133.8824 | 0 | 57.2003 | 0 | 4.4855 | 0 | 0 | 4.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278.5503 | 21.86% | 0 | 0 | 0 | 0% | 4.4855
5984 | 494 | 280 | 107 | 8.4625 | 22.8 | 248.6388 | 134.5591 | 0 | 104.8138 | 24.779 | 0 | 0 | 24.779 | 0 | 0 | 0 | 0 | 0 | 104.8138 | 0 | 377.4513 | 29.62% | 0 | 0 | 0 | 0% | 24.779
5985 | 287 | 403 | 247 | 10.4773 | 23.5 | 144.4521 | 86.9671 | 0 | 59.4008 | 37.3125 | 0 | 0 | 37.3125 | 0 | 0 | 0 | 0 | 0 | 59.4008 | 0 | 433.5011 | 34.01% | 0 | 0 | 0 | 0% | 37.3125
5986 | 468 | 599 | 267 | 11.8877 | 24.6 | 235.5525 | 149.5595 | 0 | 117.0213 | 75.5238 | 0 | 17.2619 | 58.2619 | 0 | 0 | 0 | 0 | 0 | 117.0213 | 0 | 543.9209 | 42.68% | 13.2399 | 0 | 13.7132 | 27.43% | 41
5987 | 308 | 592 | 344 | 13.2981 | 25.3 | 155.0218 | 101.0923 | 0 | 70.6093 | 72.8565 | 0 | 16.1783 | 56.6783 | 0 | 0 | 0 | 0 | 0 | 70.6093 | 0 | 610.547 | 47.9% | 12.4087 | 0 | 26.5655 | 53.13% | 40.5
5988 | 128 | 595 | 475 | 13.2981 | 25.8 | 64.4246 | 0 | 42.5228 | 0 | 63.9775 | 0 | 12.4887 | 51.4887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610.547 | 47.9% | 9.5789 | 0 | 36.4868 | 72.97% | 39
5989 | 299 | 711 | 442 | 14.7085 | 26.2 | 150.4919 | 98.7576 | 0 | 67.6595 | 95.4836 | 11.5818 | 17.01 | 66.8918 | 0 | 0 | 0 | 0 | 0 | 67.6595 | 0 | 674.3896 | 52.91% | 13.0467 | 0 | 50 | 100% | 38.3
5990 | 240 | 609 | 405 | 14.91 | 26.1 | 120.7962 | 77.5696 | 0 | 47.3564 | 73.2698 | 17.6349 | 0 | 55.6349 | 0 | 0 | 0 | 0 | 0 | 47.3564 | 0 | 719.0745 | 56.42% | 0 | 0 | 50 | 100% | 38
5991 | 251 | 522 | 339 | 16.119 | 25.5 | 126.3327 | 77.8091 | 0 | 46.8834 | 58.4 | 10.35 | 0 | 48.05 | 0 | 0 | 0 | 0 | 0 | 46.8834 | 0 | 763.3131 | 59.89% | 0 | 0 | 50 | 100% | 37.7
5992 | 312 | 411 | 230 | 16.119 | 25.2 | 157.035 | 88.7785 | 0 | 57.9481 | 40.0753 | 1.2376 | 0 | 38.8376 | 0 | 0 | 0 | 0 | 0 | 57.9481 | 0 | 817.9921 | 64.18% | 0 | 0 | 50 | 100% | 37.6
5993 | 420 | 325 | 157 | 15.1115 | 25.2 | 211.3933 | 99.9639 | 0 | 68.4956 | 29.7269 | 0 | 0 | 29.7269 | 0 | 0 | 0 | 0 | 0 | 68.4956 | 0 | 882.6237 | 69.25% | 0 | 8.9731 | 40.7076 | 81.42% | 38.7
5994 | 270 | 125 | 66 | 15.5145 | 23.6 | 135.8957 | 0 | 0 | 0 | 7.835 | 0 | 0 | 7.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 882.6237 | 69.25% | 0 | 25 | 14.8172 | 29.63% | 32.835
5995 | 10 | 11 | 10 | 15.716 | 22 | 5.0332 | 0 | 0 | 0 | 0.13053 | 0 | 0 | 0.13053 | 0 | 0 | 0 | 63.0875 | 23.7613 | 0 | 63.0875 | 824.877 | 64.72% | 0 | 14.3082 | 0 | 0% | 38.2
5996 | 0 | 0 | 0 | 17.3279 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9922 | 35.8 | 0 | 90.9922 | 737.7558 | 57.89% | 0 | 0 | 0 | 0% | 35.8
5997 | 0 | 0 | 0 | 13.9026 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8256 | 34.1 | 0 | 86.8256 | 655.4729 | 51.43% | 0 | 0 | 0 | 0% | 34.1
5998 | 0 | 0 | 0 | 9.6714 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.235 | 32.2 | 0 | 82.235 | 578.4726 | 45.39% | 0 | 0 | 0 | 0% | 32.2
5999 | 0 | 0 | 0 | 7.6565 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0881 | 30.9 | 0 | 79.0881 | 504.9604 | 39.62% | 0 | 0 | 0 | 0% | 30.9
6000 | 0 | 0 | 0 | 8.0595 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9167 | 30 | 0 | 76.9167 | 433.8215 | 34.04% | 0 | 0 | 0 | 0% | 30
6001 | 0 | 0 | 0 | 4.4327 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7346 | 29.5 | 0 | 75.7346 | 363.8098 | 28.55% | 0 | 0 | 0 | 0% | 29.5
6002 | 0 | 0 | 0 | 3.8283 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.0274 | 29.2 | 0 | 75.0274 | 294.4639 | 23.1% | 0 | 0 | 0 | 0% | 29.2
6003 | 0 | 0 | 0 | 1.6119 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4639 | 23.1% | 0 | 0 | 0 | 0% | 0
6004 | 0 | 0 | 0 | 4.6342 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4639 | 23.1% | 0 | 0 | 0 | 0% | 0
6005 | 0 | 0 | 0 | 4.6342 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4639 | 23.1% | 0 | 0 | 0 | 0% | 0
6006 | 0 | 2 | 2 | 6.6491 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4639 | 23.1% | 0 | 0 | 0 | 0% | 0
6007 | 37 | 68 | 61 | 7.2535 | 19.7 | 18.6227 | 0 | 7.8932 | 0 | 4.2004 | 0 | 0 | 4.2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4639 | 23.1% | 0 | 0 | 0 | 0% | 4.2004
6008 | 208 | 234 | 168 | 10.2758 | 21.9 | 104.69 | 0 | 56.5298 | 0 | 20.2438 | 0 | 0 | 20.2438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4639 | 23.1% | 0 | 0 | 0 | 0% | 20.2438
6009 | 4 | 236 | 231 | 11.0818 | 22.5 | 2.0133 | 0 | 1.211 | 0 | 18.0492 | 0 | 0 | 18.0492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4639 | 23.1% | 0 | 0 | 0 | 0% | 18.0492
6010 | 89 | 434 | 363 | 11.8877 | 23.5 | 44.7952 | 0 | 28.435 | 0 | 36.6689 | 0 | 0 | 36.6689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.4639 | 23.1% | 0 | 0 | 0 | 0% | 36.6689
6011 | 473 | 741 | 352 | 12.4922 | 25.1 | 238.0691 | 155.2063 | 0 | 121.8656 | 106.4655 | 9.5328 | 25 | 71.9328 | 0 | 0 | 0 | 0 | 0 | 121.8656 | 0 | 408.476 | 32.05% | 19.175 | 0 | 19.8634 | 39.73% | 37.4
6012 | 115 | 659 | 547 | 12.4922 | 26 | 57.8815 | 0 | 38.1934 | 0 | 77.731 | 0 | 20.8155 | 56.9155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408.476 | 32.05% | 15.9655 | 0 | 36.4021 | 72.8% | 36.1
6013 | 266 | 728 | 486 | 12.8952 | 26.5 | 133.8824 | 87.8457 | 0 | 59.0097 | 96.9891 | 13.6304 | 17.1142 | 66.2445 | 0 | 0 | 0 | 0 | 0 | 59.0097 | 0 | 463.6829 | 36.38% | 13.1266 | 0 | 50 | 100% | 35.5
6014 | 158 | 500 | 363 | 13.0966 | 26.2 | 79.5241 | 0 | 51.0724 | 0 | 54.6493 | 9.8246 | 0 | 44.8246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463.6829 | 36.38% | 0 | 0 | 50 | 100% | 35
6015 | 340 | 524 | 287 | 12.0892 | 26.2 | 171.1279 | 105.3777 | 0 | 75.3614 | 67.1113 | 16.1057 | 0 | 51.0057 | 0 | 0 | 0 | 0 | 0 | 75.3614 | 0 | 534.1877 | 41.91% | 0 | 0 | 50 | 100% | 34.9
6016 | 692 | 544 | 145 | 11.2833 | 26.9 | 348.2956 | 196.7518 | 0 | 161.4773 | 74.6062 | 19.7031 | 0 | 54.9031 | 0 | 0 | 0 | 0 | 0 | 161.4773 | 0 | 685.2587 | 53.77% | 0 | 0 | 50 | 100% | 35.2
6017 | 479 | 319 | 122 | 8.261 | 26.5 | 241.089 | 113.7697 | 0 | 85.6877 | 28.7053 | 0 | 0 | 28.7053 | 0 | 0 | 0 | 0 | 0 | 85.6877 | 0 | 765.4244 | 60.06% | 0 | 8.2947 | 41.4088 | 82.82% | 37
6018 | 254 | 131 | 72 | 8.0595 | 25.6 | 127.8426 | 0 | 0 | 0 | 7.8432 | 0 | 0 | 7.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765.4244 | 60.06% | 0 | 25 | 15.5147 | 31.03% | 32.8432
6019 | 1 | 6 | 6 | 8.261 | 23.5 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.847 | 23.1205 | 0 | 61.847 | 708.8398 | 55.62% | 0 | 14.9795 | 0 | 0% | 38.1
6020 | 0 | 0 | 0 | 6.8506 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0764 | 35.8 | 0 | 91.0764 | 621.6394 | 48.77% | 0 | 0 | 0 | 0% | 35.8
6021 | 0 | 0 | 0 | 4.0297 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6786 | 33.6 | 0 | 85.6786 | 540.6967 | 42.42% | 0 | 0 | 0 | 0% | 33.6
6022 | 0 | 0 | 0 | 4.8357 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2232 | 32.2 | 0 | 82.2232 | 463.6359 | 36.38% | 0 | 0 | 0 | 0% | 32.2
6023 | 0 | 0 | 0 | 3.4253 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5439 | 31.1 | 0 | 79.5439 | 389.5443 | 30.56% | 0 | 0 | 0 | 0% | 31.1
6024 | 0 | 0 | 0 | 3.0223 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5757 | 30.7 | 0 | 78.5757 | 316.5061 | 24.83% | 0 | 0 | 0 | 0% | 30.7
6025 | 0 | 0 | 0 | 2.8208 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316.5061 | 24.83% | 0 | 0 | 0 | 0% | 0
6026 | 0 | 0 | 0 | 2.2164 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316.5061 | 24.83% | 0 | 0 | 0 | 0% | 0
6027 | 0 | 0 | 0 | 0.40297 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316.5061 | 24.83% | 0 | 0 | 0 | 0% | 0
6028 | 0 | 0 | 0 | 0.40297 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316.5061 | 24.83% | 0 | 0 | 0 | 0% | 0
6029 | 0 | 0 | 0 | 1.0074 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316.5061 | 24.83% | 0 | 0 | 0 | 0% | 0
6030 | 2 | 2 | 2 | 1.0074 | 17.9 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316.5061 | 24.83% | 0 | 0 | 0 | 0% | 0
6031 | 232 | 93 | 53 | 1.4104 | 18.7 | 116.7696 | 0 | 49.0926 | 0 | 4.8338 | 0 | 0 | 4.8338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316.5061 | 24.83% | 0 | 0 | 0 | 0% | 4.8338
6032 | 504 | 275 | 94 | 1.2089 | 22 | 253.672 | 136.5421 | 0 | 110.0238 | 24.1984 | 0 | 0 | 24.1984 | 0 | 0 | 0 | 0 | 0 | 110.0238 | 0 | 419.297 | 32.9% | 0 | 0 | 0 | 0% | 24.1984
6033 | 688 | 476 | 111 | 2.2164 | 23.8 | 346.2824 | 208.098 | 0 | 176.7206 | 50.1016 | 2.3508 | 0 | 47.7508 | 0 | 0 | 0 | 0 | 0 | 176.7206 | 0 | 584.4001 | 45.85% | 0 | 0 | 0 | 0% | 45.4
6034 | 799 | 661 | 118 | 3.2238 | 25.5 | 402.1506 | 255.2141 | 0 | 220.2699 | 87.7305 | 0 | 20.9153 | 66.8153 | 0 | 0 | 0 | 0 | 0 | 220.2699 | 0 | 790.1895 | 62% | 16.042 | 0 | 16.6203 | 33.24% | 45.9
6035 | 836 | 802 | 142 | 3.6268 | 26.9 | 420.7733 | 274.2423 | 0 | 237.9573 | 105 | 5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 237.9573 | 0 | 1012.5036 | 79.44% | 19.175 | 0 | 36.4867 | 72.97% | 45
6036 | 562 | 833 | 351 | 7.2535 | 28.3 | 282.8644 | 186.5965 | 0 | 154.3699 | 105.9 | 13.8947 | 17.0053 | 75 | 0 | 0 | 0 | 0 | 0 | 154.3699 | 0 | 1156.7253 | 90.76% | 13.0431 | 0 | 50 | 100% | 44.1
6037 | 57 | 413 | 357 | 7.455 | 27.5 | 28.6891 | 0 | 18.8214 | 0 | 34.088 | 0 | 0 | 34.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.7253 | 90.76% | 0 | 9.912 | 39.7323 | 79.46% | 44
6038 | 1 | 122 | 120 | 6.8506 | 25.5 | 0.50332 | 0 | 0.32326 | 0 | 8.454 | 0 | 0 | 8.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.7253 | 90.76% | 0 | 25 | 13.8345 | 27.67% | 33.454
6039 | 4 | 182 | 178 | 10.0743 | 24.4 | 2.0133 | 0 | 1.2395 | 0 | 13.3643 | 0 | 0 | 13.3643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.7253 | 90.76% | 0 | 13.3555 | 0 | 0% | 26.7199
6040 | 270 | 430 | 268 | 7.6565 | 25.6 | 135.8957 | 76.7063 | 0 | 50.8439 | 39.2382 | 0 | 0 | 39.2382 | 0 | 0 | 0 | 0 | 0 | 50.8439 | 0 | 1204.2268 | 94.49% | 0 | 0 | 0 | 0% | 39.2382
6041 | 56 | 186 | 163 | 4.2312 | 26.5 | 28.1858 | 0 | 13.273 | 0 | 14.628 | 0 | 0 | 14.628 | 0 | 0 | 0 | 76.7556 | 29.472 | 0 | 76.7556 | 1133.3502 | 88.92% | 0 | 0 | 0 | 0% | 44.1
6042 | 6 | 56 | 55 | 4.6342 | 26.2 | 3.0199 | 0 | 0 | 0 | 3.6084 | 0 | 0 | 3.6084 | 0 | 0 | 0 | 105.2592 | 41.2916 | 0 | 105.2592 | 1030.6223 | 80.86% | 0 | 0 | 0 | 0% | 44.9
6043 | 16 | 9 | 8 | 4.2312 | 25.7 | 8.0531 | 0 | 0 | 0 | 0.029293 | 0 | 0 | 0.029293 | 0 | 0 | 0 | 104.6132 | 41.0707 | 0 | 104.6132 | 928.5132 | 72.85% | 0 | 0 | 0 | 0% | 41.1
6044 | 0 | 0 | 0 | 6.8506 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8509 | 37.6 | 0 | 95.8509 | 836.2884 | 65.62% | 0 | 0 | 0 | 0% | 37.6
6045 | 0 | 0 | 0 | 5.6416 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1235 | 36.2 | 0 | 92.1235 | 748.0135 | 58.69% | 0 | 0 | 0 | 0% | 36.2
6046 | 0 | 0 | 0 | 6.0446 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1891 | 34.6 | 0 | 88.1891 | 664.2481 | 52.12% | 0 | 0 | 0 | 0% | 34.6
6047 | 0 | 0 | 0 | 4.4327 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9294 | 33.3 | 0 | 84.9294 | 584.185 | 45.84% | 0 | 0 | 0 | 0% | 33.3
6048 | 0 | 0 | 0 | 2.0149 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1244 | 33 | 0 | 84.1244 | 505.0055 | 39.62% | 0 | 0 | 0 | 0% | 33
6049 | 0 | 0 | 0 | 1.2089 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5942 | 32.4 | 0 | 82.5942 | 427.5222 | 33.54% | 0 | 0 | 0 | 0% | 32.4
6050 | 0 | 0 | 0 | 7.6565 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9403 | 32.8 | 0 | 83.9403 | 348.575 | 27.35% | 0 | 0 | 0 | 0% | 32.8
6051 | 0 | 0 | 0 | 4.6342 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.575 | 27.35% | 0 | 0 | 0 | 0% | 0
6052 | 0 | 0 | 0 | 5.0372 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.575 | 27.35% | 0 | 0 | 0 | 0% | 0
6053 | 0 | 0 | 0 | 7.6565 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.575 | 27.35% | 0 | 0 | 0 | 0% | 0
6054 | 5 | 2 | 2 | 4.4327 | 21.4 | 2.5166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.575 | 27.35% | 0 | 0 | 0 | 0% | 0
6055 | 231 | 99 | 69 | 5.6416 | 21.4 | 116.2663 | 0 | 48.4798 | 0 | 5.9223 | 0 | 0 | 5.9223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.575 | 27.35% | 0 | 0 | 0 | 0% | 5.9223
6056 | 71 | 164 | 137 | 9.2684 | 23.1 | 35.7355 | 0 | 19.1498 | 0 | 12.8208 | 0 | 0 | 12.8208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.575 | 27.35% | 0 | 0 | 0 | 0% | 12.8208
6057 | 216 | 384 | 266 | 15.9175 | 26.4 | 108.7166 | 65.2725 | 0 | 35.5558 | 34.406 | 0 | 0 | 34.406 | 0 | 0 | 0 | 0 | 0 | 35.5558 | 0 | 382.2244 | 29.99% | 0 | 0 | 0 | 0% | 34.406
6058 | 115 | 428 | 342 | 19.3427 | 27 | 57.8815 | 0 | 36.7239 | 0 | 36.5877 | 0 | 0 | 36.5877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382.2244 | 29.99% | 0 | 0 | 0 | 0% | 36.5877
6059 | 436 | 680 | 326 | 19.7457 | 28 | 219.4464 | 142.9861 | 0 | 106.5377 | 90.5202 | 0 | 23.4601 | 67.0601 | 0 | 0 | 0 | 0 | 0 | 106.5377 | 0 | 483.0499 | 37.9% | 17.9939 | 0 | 18.6454 | 37.29% | 43.6
6060 | 878 | 883 | 138 | 16.7234 | 28.4 | 441.9127 | 291.4324 | 0 | 246.9236 | 107.2 | 7.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 246.9236 | 0 | 716.7341 | 56.24% | 19.175 | 0 | 38.5146 | 77.03% | 42.8
6061 | 833 | 884 | 172 | 17.3279 | 27.1 | 419.2634 | 275.018 | 0 | 230.9583 | 107.5 | 18.0489 | 14.4511 | 75 | 0 | 0 | 0 | 0 | 0 | 230.9583 | 0 | 935.3091 | 73.39% | 11.084 | 0 | 50 | 100% | 42.5
6062 | 849 | 838 | 154 | 18.9398 | 26.7 | 427.3165 | 274.4601 | 0 | 229.5081 | 107.7 | 32.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 229.5081 | 0 | 1152.5117 | 90.43% | 0 | 0 | 50 | 100% | 42.3
6063 | 735 | 672 | 146 | 12.2907 | 26.4 | 369.9383 | 227.7072 | 0 | 189.8236 | 97.8671 | 28.1836 | 0 | 69.6836 | 0 | 0 | 0 | 0 | 0 | 189.8236 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.5
6064 | 313 | 346 | 170 | 9.4699 | 25.7 | 157.5383 | 0 | 88.8508 | 0 | 33.3953 | 0 | 0 | 33.3953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 8.0047 | 41.7067 | 83.41% | 41.4
6065 | 572 | 314 | 101 | 9.4699 | 25.9 | 287.8975 | 0 | 135.2873 | 0 | 30.7896 | 0 | 0 | 30.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 12.5104 | 28.7452 | 57.49% | 43.3
6066 | 485 | 141 | 45 | 9.8729 | 25.1 | 244.1089 | 0 | 0 | 0 | 8.3008 | 0 | 0 | 8.3008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 2.8428 | 5.686% | 33.3008
6067 | 36 | 9 | 6 | 5.4401 | 23.4 | 18.1194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1216 | 37.3552 | 0 | 95.1216 | 1183.0494 | 92.82% | 0 | 2.7448 | 0 | 0% | 40.1
6068 | 0 | 0 | 0 | 5.0372 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6018 | 36.8 | 0 | 93.6018 | 1093.1472 | 85.77% | 0 | 0 | 0 | 0% | 36.8
6069 | 0 | 0 | 0 | 5.0372 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5865 | 35.2 | 0 | 89.5865 | 1007.7178 | 79.07% | 0 | 0 | 0 | 0% | 35.2
6070 | 0 | 0 | 0 | 5.0372 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1278 | 33.4 | 0 | 85.1278 | 927.4717 | 72.77% | 0 | 0 | 0 | 0% | 33.4
6071 | 0 | 0 | 0 | 12.8952 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8349 | 32.5 | 0 | 82.8349 | 849.7859 | 66.68% | 0 | 0 | 0 | 0% | 32.5
6072 | 0 | 0 | 0 | 14.91 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.84 | 31.7 | 0 | 80.84 | 774.3188 | 60.75% | 0 | 0 | 0 | 0% | 31.7
6073 | 0 | 0 | 0 | 7.858 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5362 | 31.6 | 0 | 80.5362 | 699.1554 | 54.86% | 0 | 0 | 0 | 0% | 31.6
6074 | 0 | 0 | 0 | 9.8729 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5848 | 31.7 | 0 | 80.5848 | 623.6984 | 48.94% | 0 | 0 | 0 | 0% | 31.7
6075 | 0 | 0 | 0 | 7.6565 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3286 | 33.7 | 0 | 85.3286 | 542.5266 | 42.57% | 0 | 0 | 0 | 0% | 33.7
6076 | 0 | 0 | 0 | 8.0595 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.177 | 37 | 0 | 93.177 | 451.9474 | 35.46% | 0 | 0 | 0 | 0% | 37
6077 | 0 | 0 | 0 | 4.8357 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4473 | 38.4 | 0 | 96.4473 | 357.3618 | 28.04% | 0 | 0 | 0 | 0% | 38.4
6078 | 0 | 1 | 1 | 3.4253 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.8957 | 20.1405 | 0 | 53.8957 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 20.1405
6079 | 24 | 52 | 47 | 5.0372 | 16.8 | 12.0796 | 0 | 4.9949 | 0 | 3.1733 | 0 | 0 | 3.1733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 3.1733
6080 | 47 | 125 | 111 | 5.0372 | 17.8 | 23.6559 | 0 | 12.6197 | 0 | 10.0336 | 0 | 0 | 10.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 10.0336
6081 | 0 | 129 | 128 | 5.4401 | 18.8 | 0 | 0 | 0 | 0 | 9.408 | 0 | 0 | 9.408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 9.408
6082 | 0 | 92 | 91 | 3.4253 | 18.9 | 0 | 0 | 0 | 0 | 6.3489 | 0 | 0 | 6.3489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 6.3489
6083 | 0 | 123 | 121 | 6.4476 | 18.9 | 0 | 0 | 0 | 0 | 8.6697 | 0 | 0 | 8.6697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 8.6697
6084 | 0 | 133 | 132 | 6.2461 | 18.8 | 0 | 0 | 0 | 0 | 9.5234 | 0 | 0 | 9.5234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 9.5234
6085 | 0 | 177 | 175 | 3.4253 | 19.6 | 0 | 0 | 0 | 0 | 12.8793 | 0 | 0 | 12.8793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 12.8793
6086 | 0 | 195 | 193 | 5.8431 | 20.8 | 0 | 0 | 0 | 0 | 14.3389 | 0 | 0 | 14.3389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 14.3389
6087 | 16 | 183 | 169 | 10.4773 | 21.3 | 8.0531 | 0 | 4.9558 | 0 | 13.742 | 0 | 0 | 13.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 13.742
6088 | 109 | 240 | 176 | 12.8952 | 20.9 | 54.8616 | 0 | 30.9164 | 0 | 21.3465 | 0 | 0 | 21.3465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.325 | 24.19% | 0 | 0 | 0 | 0% | 21.3465
6089 | 430 | 281 | 102 | 13.4996 | 20.4 | 216.4265 | 101.4849 | 0 | 70.689 | 25.7144 | 0 | 0 | 25.7144 | 0 | 0 | 0 | 0 | 0 | 70.689 | 0 | 374.9812 | 29.42% | 0 | 0 | 0 | 0% | 25.7144
6090 | 0 | 23 | 23 | 6.8506 | 16 | 0 | 0 | 0 | 0 | 1.2687 | 0 | 0 | 1.2687 | 0 | 0 | 0 | 67.2977 | 25.9641 | 0 | 67.2977 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 27.2327
6091 | 0 | 1 | 1 | 5.2387 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6092 | 0 | 0 | 0 | 7.052 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6093 | 0 | 0 | 0 | 10.6788 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6094 | 0 | 0 | 0 | 10.0743 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6095 | 0 | 0 | 0 | 11.0818 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6096 | 0 | 0 | 0 | 8.8654 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6097 | 0 | 0 | 0 | 8.4625 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6098 | 0 | 0 | 0 | 7.2535 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6099 | 0 | 0 | 0 | 10.0743 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6100 | 0 | 0 | 0 | 7.2535 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6101 | 0 | 0 | 0 | 3.8283 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6102 | 0 | 1 | 1 | 5.0372 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 0
6103 | 1 | 40 | 40 | 4.6342 | 15.7 | 0.50332 | 0 | 0.20636 | 0 | 2.4964 | 0 | 0 | 2.4964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 2.4964
6104 | 1 | 49 | 48 | 4.6342 | 16.1 | 0.50332 | 0 | 0.26729 | 0 | 3.235 | 0 | 0 | 3.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 3.235
6105 | 15 | 137 | 123 | 4.4327 | 15.5 | 7.5498 | 0 | 4.5243 | 0 | 9.9795 | 0 | 0 | 9.9795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9228 | 24.55% | 0 | 0 | 0 | 0% | 9.9795
6106 | 343 | 565 | 307 | 3.2238 | 18.3 | 172.6379 | 109.4791 | 0 | 83.9509 | 59.7837 | 0 | 7.5918 | 52.1918 | 0 | 0 | 0 | 0 | 0 | 83.9509 | 0 | 391.9411 | 30.75% | 5.8229 | 0 | 6.0349 | 12.07% | 44.6
6107 | 85 | 374 | 302 | 9.4699 | 20.4 | 42.782 | 0 | 27.8601 | 0 | 32.2857 | 0 | 0 | 32.2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391.9411 | 30.75% | 0 | 5.8239 | 0 | 0% | 38.1096
6108 | 529 | 798 | 348 | 10.6788 | 22.4 | 266.2549 | 175.4884 | 0 | 141.948 | 107.3 | 7.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 141.948 | 0 | 525.549 | 41.24% | 19.175 | 0 | 19.8733 | 39.75% | 42.7
6109 | 335 | 650 | 361 | 12.0892 | 22.9 | 168.6113 | 110.5694 | 0 | 80.2259 | 85.49 | 0 | 21.545 | 63.945 | 0 | 0 | 0 | 0 | 0 | 80.2259 | 0 | 601.0613 | 47.16% | 16.525 | 0 | 37.0001 | 74% | 42.4
6110 | 186 | 492 | 335 | 12.8952 | 22.7 | 93.617 | 60.1334 | 0 | 32.8814 | 48.7464 | 0 | 3.2232 | 45.5232 | 0 | 0 | 0 | 0 | 0 | 32.8814 | 0 | 632.0108 | 49.59% | 2.4722 | 0 | 39.5623 | 79.12% | 42.3
6111 | 2 | 159 | 156 | 10.8803 | 21.8 | 1.0066 | 0 | 0.61933 | 0 | 11.5862 | 0 | 0 | 11.5862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 632.0108 | 49.59% | 0 | 25 | 13.656 | 27.31% | 36.5862
6112 | 1 | 156 | 154 | 10.8803 | 21 | 0.50332 | 0 | 0.2834 | 0 | 11.5201 | 0 | 0 | 11.5201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 632.0108 | 49.59% | 0 | 13.178 | 0 | 0% | 24.6981
6113 | 1 | 83 | 82 | 8.0595 | 20.3 | 0.50332 | 0 | 0.2355 | 0 | 5.8258 | 0 | 0 | 5.8258 | 0 | 0 | 0 | 95.3867 | 37.6742 | 0 | 95.3867 | 539.2471 | 42.31% | 0 | 0 | 0 | 0% | 43.5
6114 | 0 | 22 | 22 | 5.6416 | 19.8 | 0 | 0 | 0 | 0 | 1.1673 | 0 | 0 | 1.1673 | 0 | 0 | 0 | 107.0326 | 42.5327 | 0 | 107.0326 | 432.558 | 33.94% | 0 | 0 | 0 | 0% | 43.7
6115 | 0 | 0 | 0 | 4.2312 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.2758 | 39.8 | 0 | 100.2758 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 39.8
6116 | 0 | 0 | 0 | 5.8431 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6117 | 0 | 0 | 0 | 2.8208 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6118 | 0 | 0 | 0 | 5.6416 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6119 | 0 | 0 | 0 | 5.0372 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6120 | 0 | 0 | 0 | 7.455 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6121 | 0 | 0 | 0 | 6.6491 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6122 | 0 | 0 | 0 | 4.2312 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6123 | 0 | 0 | 0 | 6.4476 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6124 | 0 | 0 | 0 | 6.8506 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6125 | 0 | 0 | 0 | 7.455 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6126 | 0 | 0 | 0 | 3.8283 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 0
6127 | 16 | 37 | 33 | 3.8283 | 15 | 8.0531 | 0 | 3.2734 | 0 | 2.1055 | 0 | 0 | 2.1055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 2.1055
6128 | 118 | 166 | 112 | 2.6193 | 16.4 | 59.3915 | 0 | 31.395 | 0 | 12.9558 | 0 | 0 | 12.9558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6267 | 26.18% | 0 | 0 | 0 | 0% | 12.9558
6129 | 341 | 379 | 188 | 2.8208 | 19 | 171.6312 | 102.7263 | 0 | 77.7115 | 35.6989 | 0 | 0 | 35.6989 | 0 | 0 | 0 | 0 | 0 | 77.7115 | 0 | 407.3795 | 31.96% | 0 | 0 | 0 | 0% | 35.6989
6130 | 693 | 664 | 201 | 6.0446 | 21.5 | 348.7989 | 221.1377 | 0 | 187.263 | 94.5374 | 0.21869 | 25 | 69.3187 | 0 | 0 | 0 | 0 | 0 | 187.263 | 0 | 585.1033 | 45.91% | 19.175 | 0 | 19.8757 | 39.75% | 44.1
6131 | 638 | 717 | 223 | 13.2981 | 23.2 | 321.1165 | 209.0552 | 0 | 171.7252 | 107.4 | 7.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 171.7252 | 0 | 748.0807 | 58.7% | 19.175 | 0 | 39.7514 | 79.5% | 42.6
6132 | 62 | 441 | 383 | 12.8952 | 23 | 31.2057 | 0 | 20.5616 | 0 | 37.8939 | 0 | 0 | 37.8939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748.0807 | 58.7% | 0 | 3.3061 | 36.325 | 72.65% | 41.2
6133 | 14 | 114 | 102 | 14.3056 | 21 | 7.0464 | 0 | 4.6201 | 0 | 8.8887 | 0 | 0 | 8.8887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748.0807 | 58.7% | 0 | 25 | 10.4154 | 20.83% | 33.8887
6134 | 85 | 360 | 287 | 11.8877 | 21.1 | 42.782 | 0 | 27.4813 | 0 | 31.1302 | 0 | 0 | 31.1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748.0807 | 58.7% | 0 | 9.5698 | 0.49684 | 0.9937% | 40.7
6135 | 122 | 385 | 296 | 11.2833 | 22 | 61.4047 | 0 | 37.77 | 0 | 34.9681 | 0 | 0 | 34.9681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748.0807 | 58.7% | 0 | 0 | 0.49684 | 0.9937% | 34.9681
6136 | 72 | 319 | 276 | 12.2907 | 22.8 | 36.2389 | 0 | 20.3877 | 0 | 27.2148 | 0 | 0 | 27.2148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748.0807 | 58.7% | 0 | 0 | 0.49684 | 0.9937% | 27.2148
6137 | 6 | 122 | 118 | 10.6788 | 22.6 | 3.0199 | 0 | 1.4099 | 0 | 8.8929 | 0 | 0 | 8.8929 | 0 | 0 | 0 | 84.6961 | 33.1071 | 0 | 84.6961 | 668.1115 | 52.42% | 0 | 0 | 0.49684 | 0.9937% | 42
6138 | 10 | 51 | 50 | 10.4773 | 22.1 | 5.0332 | 0 | 0 | 0 | 3.3239 | 0 | 0 | 3.3239 | 0 | 0 | 0 | 99.5252 | 39.2761 | 0 | 99.5252 | 570.7628 | 44.78% | 0 | 0 | 0.49684 | 0.9937% | 42.6
6139 | 0 | 4 | 4 | 11.0818 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5271 | 38.9 | 0 | 98.5271 | 474.4828 | 37.23% | 0 | 0 | 0.49684 | 0.9937% | 38.9
6140 | 0 | 0 | 0 | 6.6491 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8067 | 36.1 | 0 | 91.8067 | 386.1682 | 30.3% | 0 | 0 | 0.49684 | 0.9937% | 36.1
6141 | 0 | 0 | 0 | 8.8654 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.2272 | 23.005 | 0 | 61.2272 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 23.005
6142 | 0 | 0 | 0 | 8.4625 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 0
6143 | 0 | 0 | 0 | 5.8431 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 0
6144 | 0 | 0 | 0 | 8.261 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 0
6145 | 0 | 0 | 0 | 6.4476 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 0
6146 | 0 | 0 | 0 | 6.8506 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 0
6147 | 0 | 0 | 0 | 6.2461 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 0
6148 | 0 | 0 | 0 | 7.052 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 0
6149 | 0 | 0 | 0 | 6.8506 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 0
6150 | 0 | 1 | 1 | 7.052 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 0
6151 | 0 | 31 | 31 | 8.0595 | 19 | 0 | 0 | 0 | 0 | 1.7908 | 0 | 0 | 1.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 1.7908
6152 | 0 | 57 | 57 | 10.4773 | 20 | 0 | 0 | 0 | 0 | 3.8463 | 0 | 0 | 3.8463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 3.8463
6153 | 0 | 116 | 116 | 7.455 | 19.5 | 0 | 0 | 0 | 0 | 8.4378 | 0 | 0 | 8.4378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 8.4378
6154 | 0 | 187 | 186 | 8.4625 | 21.5 | 0 | 0 | 0 | 0 | 13.9196 | 0 | 0 | 13.9196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 13.9196
6155 | 8 | 322 | 312 | 11.6862 | 22.6 | 4.0265 | 0 | 2.6206 | 0 | 25.019 | 0 | 0 | 25.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 25.019
6156 | 26 | 382 | 355 | 9.8729 | 23 | 13.0863 | 0 | 8.6201 | 0 | 30.2359 | 0 | 0 | 30.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.9766 | 25.89% | 0 | 0 | 0.49684 | 0.9937% | 30.2359
6157 | 310 | 693 | 423 | 11.6862 | 24.3 | 156.0284 | 102.2874 | 0 | 72.6434 | 98.4036 | 6.4518 | 25 | 66.9518 | 0 | 0 | 0 | 0 | 0 | 72.6434 | 0 | 398.9273 | 31.3% | 19.175 | 0 | 20.3751 | 40.75% | 35.5
6158 | 342 | 673 | 395 | 13.2981 | 24.9 | 172.1345 | 110.5755 | 0 | 79.5792 | 95.6244 | 5.2622 | 25 | 65.3622 | 0 | 0 | 0 | 0 | 0 | 79.5792 | 0 | 474.4611 | 37.23% | 19.175 | 0 | 40.2533 | 80.51% | 35.1
6159 | 351 | 580 | 336 | 12.6937 | 24.6 | 176.6644 | 108.6387 | 0 | 78.0595 | 78.593 | 9.5894 | 12.2571 | 56.7465 | 0 | 0 | 0 | 0 | 0 | 78.0595 | 0 | 548.5525 | 43.04% | 9.4012 | 0 | 49.9994 | 100% | 34.9
6160 | 456 | 468 | 215 | 12.0892 | 24.7 | 229.5127 | 129.0117 | 0 | 97.535 | 58.6814 | 11.6907 | 0 | 46.9907 | 0 | 0 | 0 | 0 | 0 | 97.535 | 0 | 641.1294 | 50.3% | 0 | 0 | 49.9994 | 100% | 35.3
6161 | 343 | 276 | 150 | 10.2758 | 24.7 | 172.6379 | 80.4242 | 0 | 52.8821 | 25.5584 | 0 | 0 | 25.5584 | 0 | 0 | 0 | 0 | 0 | 52.8821 | 0 | 691.3232 | 54.24% | 0 | 11.9416 | 37.6217 | 75.24% | 37.5
6162 | 125 | 97 | 71 | 11.8877 | 23.5 | 62.9147 | 0 | 0 | 0 | 6.279 | 0 | 0 | 6.279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.3232 | 54.24% | 0 | 25 | 11.7082 | 23.42% | 31.279
6163 | 1 | 4 | 4 | 9.6714 | 22.2 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3937 | 25.2032 | 0 | 66.3937 | 630.1609 | 49.44% | 0 | 11.2968 | 0 | 0% | 36.5
6164 | 0 | 0 | 0 | 9.4699 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1239 | 34.2 | 0 | 87.1239 | 547.2979 | 42.94% | 0 | 0 | 0 | 0% | 34.2
6165 | 0 | 0 | 0 | 8.4625 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3985 | 32.2 | 0 | 82.3985 | 469.8747 | 36.87% | 0 | 0 | 0 | 0% | 32.2
6166 | 0 | 0 | 0 | 6.4476 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8629 | 30.3 | 0 | 77.8629 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 30.3
6167 | 0 | 0 | 0 | 5.8431 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 0
6168 | 0 | 0 | 0 | 4.4327 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 0
6169 | 0 | 0 | 0 | 1.6119 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 0
6170 | 0 | 0 | 0 | 1.2089 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 0
6171 | 0 | 0 | 0 | 1.8134 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 0
6172 | 0 | 0 | 0 | 1.0074 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 0
6173 | 0 | 0 | 0 | 1.0074 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 0
6174 | 0 | 1 | 1 | 3.4253 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 0
6175 | 76 | 65 | 52 | 3.4253 | 20.4 | 38.2521 | 0 | 15.2773 | 0 | 3.915 | 0 | 0 | 3.915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.4994 | 31.19% | 0 | 0 | 0 | 0% | 3.915
6176 | 348 | 244 | 126 | 2.2164 | 22.3 | 175.1545 | 91.7282 | 0 | 67.8761 | 21.9125 | 0 | 0 | 21.9125 | 0 | 0 | 0 | 0 | 0 | 67.8761 | 0 | 461.4987 | 36.21% | 0 | 0 | 0 | 0% | 21.9125
6177 | 520 | 444 | 172 | 5.8431 | 24.5 | 261.725 | 155.9445 | 0 | 126.4609 | 54.0035 | 0 | 9.1018 | 44.9018 | 0 | 0 | 0 | 0 | 0 | 126.4609 | 0 | 580.7365 | 45.57% | 6.981 | 0 | 7.2381 | 14.48% | 35.8
6178 | 634 | 618 | 192 | 8.6639 | 26 | 319.1032 | 201.9475 | 0 | 167.9054 | 92.1869 | 2.7934 | 25 | 64.3934 | 0 | 0 | 0 | 0 | 0 | 167.9054 | 0 | 739.0517 | 57.99% | 19.175 | 0 | 27.1191 | 54.24% | 36.6
6179 | 702 | 744 | 199 | 8.4625 | 26.8 | 353.3288 | 229.8952 | 0 | 194.1537 | 113.6 | 13.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 194.1537 | 0 | 922.1159 | 72.35% | 19.175 | 0 | 47.0002 | 94% | 36.4
6180 | 734 | 816 | 200 | 9.0669 | 27.6 | 369.435 | 243.2803 | 0 | 206.2368 | 115.1 | 36.3278 | 3.7722 | 75 | 0 | 0 | 0 | 0 | 0 | 206.2368 | 0 | 1116.573 | 87.61% | 2.8933 | 0 | 50 | 100% | 34.9
6181 | 718 | 821 | 215 | 9.0669 | 27.9 | 361.3819 | 236.875 | 0 | 200.3479 | 116.1 | 41.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 200.3479 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.9
6182 | 661 | 748 | 222 | 11.4848 | 27.7 | 332.6928 | 0 | 213.7216 | 0 | 116.5 | 41.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.5
6183 | 653 | 644 | 193 | 11.4848 | 27.5 | 328.6663 | 0 | 202.0595 | 0 | 101.3829 | 33.9414 | 0 | 67.4414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.5
6184 | 560 | 477 | 170 | 12.0892 | 27.1 | 281.8577 | 0 | 158.2978 | 0 | 63.7707 | 14.8854 | 0 | 48.8854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34
6185 | 394 | 274 | 131 | 11.2833 | 26.2 | 198.3071 | 0 | 92.1768 | 0 | 26.2007 | 0 | 0 | 26.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 10.5993 | 39.0121 | 78.02% | 36.8
6186 | 104 | 83 | 59 | 9.8729 | 24.9 | 52.345 | 0 | 0 | 0 | 5.079 | 0 | 0 | 5.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 13.0948 | 26.19% | 30.079
6187 | 0 | 3 | 3 | 7.6565 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.6844 | 24.368 | 0 | 64.6844 | 1215.1576 | 95.34% | 0 | 12.632 | 0 | 0% | 37
6188 | 0 | 0 | 0 | 6.2461 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0557 | 34.5 | 0 | 88.0557 | 1131.5184 | 88.78% | 0 | 0 | 0 | 0% | 34.5
6189 | 0 | 0 | 0 | 4.2312 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.669 | 32.3 | 0 | 82.669 | 1053.9909 | 82.7% | 0 | 0 | 0 | 0% | 32.3
6190 | 0 | 0 | 0 | 3.8283 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6681 | 30.7 | 0 | 78.6681 | 980.8862 | 76.96% | 0 | 0 | 0 | 0% | 30.7
6191 | 0 | 0 | 0 | 2.0149 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0902 | 29.6 | 0 | 76.0902 | 910.4912 | 71.44% | 0 | 0 | 0 | 0% | 29.6
6192 | 0 | 0 | 0 | 2.6193 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1732 | 29.2 | 0 | 75.1732 | 840.9741 | 65.98% | 0 | 0 | 0 | 0% | 29.2
6193 | 0 | 0 | 0 | 3.2238 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3929 | 29.3 | 0 | 75.3929 | 771.2341 | 60.51% | 0 | 0 | 0 | 0% | 29.3
6194 | 0 | 0 | 0 | 1.4104 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4202 | 30.2 | 0 | 77.4202 | 699.4556 | 54.88% | 0 | 0 | 0 | 0% | 30.2
6195 | 0 | 0 | 0 | 1.6119 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3538 | 33.5 | 0 | 85.3538 | 618.7419 | 48.55% | 0 | 0 | 0 | 0% | 33.5
6196 | 0 | 0 | 0 | 2.2164 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8565 | 38.3 | 0 | 96.8565 | 524.3237 | 41.14% | 0 | 0 | 0 | 0% | 38.3
6197 | 0 | 0 | 0 | 1.8134 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7668 | 40.8 | 0 | 102.7668 | 422.721 | 33.17% | 0 | 0 | 0 | 0% | 40.8
6198 | 0 | 1 | 1 | 2.2164 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.2775 | 23.6104 | 0 | 62.2775 | 365.5725 | 28.68% | 0 | 0 | 0 | 0% | 23.6104
6199 | 155 | 71 | 43 | 2.6193 | 19.1 | 78.0142 | 0 | 30.879 | 0 | 3.8118 | 0 | 0 | 3.8118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.5725 | 28.68% | 0 | 0 | 0 | 0% | 3.8118
6200 | 532 | 266 | 88 | 4.0297 | 21.8 | 267.7649 | 139.5657 | 0 | 111.9239 | 25.7289 | 0 | 0 | 25.7289 | 0 | 0 | 0 | 0 | 0 | 111.9239 | 0 | 470.2023 | 36.89% | 0 | 0 | 0 | 0% | 25.7289
6201 | 728 | 475 | 103 | 3.4253 | 23.6 | 366.4151 | 217.8245 | 0 | 185.3561 | 55.2516 | 0 | 4.7258 | 50.5258 | 0 | 0 | 0 | 0 | 0 | 185.3561 | 0 | 643.4787 | 50.49% | 3.6247 | 0 | 3.7587 | 7.517% | 45.8
6202 | 815 | 651 | 113 | 3.8283 | 25.6 | 410.2037 | 259.3444 | 0 | 223.9181 | 91.2769 | 0 | 22.6385 | 68.6385 | 0 | 0 | 0 | 0 | 0 | 223.9181 | 0 | 852.8041 | 66.91% | 17.3637 | 0 | 21.7644 | 43.53% | 46
6203 | 540 | 607 | 195 | 3.6268 | 26.4 | 271.7914 | 176.7919 | 0 | 147.0311 | 82.0637 | 0 | 18.6319 | 63.4319 | 0 | 0 | 0 | 0 | 0 | 147.0311 | 0 | 990.2532 | 77.7% | 14.2906 | 0 | 36.5834 | 73.17% | 44.8
6204 | 825 | 873 | 189 | 8.6639 | 26.8 | 415.2368 | 273.3607 | 0 | 234.4839 | 105.8 | 13.9314 | 16.8686 | 75 | 0 | 0 | 0 | 0 | 0 | 234.4839 | 0 | 1209.4558 | 94.9% | 12.9382 | 0 | 50 | 100% | 44.2
6205 | 833 | 850 | 156 | 10.4773 | 26.5 | 419.2634 | 274.7723 | 0 | 234.7208 | 106 | 31 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 234.7208 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44
6206 | 806 | 788 | 157 | 9.2684 | 26.9 | 405.6738 | 0 | 260.6129 | 0 | 105.9 | 30.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.1
6207 | 753 | 709 | 194 | 8.261 | 27 | 378.998 | 0 | 232.942 | 0 | 104.9192 | 30.8096 | 0 | 74.1096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.3
6208 | 612 | 602 | 270 | 6.0446 | 27.2 | 308.0302 | 0 | 172.8442 | 0 | 75.1489 | 16.1244 | 0 | 59.0244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.9
6209 | 401 | 359 | 211 | 7.052 | 26.2 | 201.8303 | 0 | 93.6034 | 0 | 32.7125 | 0 | 0 | 32.7125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 12.1875 | 37.3638 | 74.73% | 44.9
6210 | 134 | 111 | 85 | 6.6491 | 24.5 | 67.4445 | 0 | 0 | 0 | 7.444 | 0 | 0 | 7.444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 11.4427 | 22.89% | 32.444
6211 | 0 | 2 | 2 | 5.0372 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.8166 | 29.3632 | 0 | 75.8166 | 1204.5229 | 94.51% | 0 | 11.0368 | 0 | 0% | 40.4
6212 | 0 | 0 | 0 | 2.8208 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2557 | 37.1 | 0 | 94.2557 | 1113.7638 | 87.39% | 0 | 0 | 0 | 0% | 37.1
6213 | 0 | 0 | 0 | 1.0074 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0534 | 35.4 | 0 | 90.0534 | 1027.7682 | 80.64% | 0 | 0 | 0 | 0% | 35.4
6214 | 0 | 0 | 0 | 0.60446 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1607 | 33.8 | 0 | 86.1607 | 946.3589 | 74.25% | 0 | 0 | 0 | 0% | 33.8
6215 | 0 | 0 | 0 | 1.6119 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2259 | 32.6 | 0 | 83.2259 | 868.2611 | 68.13% | 0 | 0 | 0 | 0% | 32.6
6216 | 0 | 0 | 0 | 2.8208 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6945 | 32 | 0 | 81.6945 | 791.8562 | 62.13% | 0 | 0 | 0 | 0% | 32
6217 | 0 | 0 | 0 | 2.2164 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6945 | 32 | 0 | 81.6945 | 715.44 | 56.13% | 0 | 0 | 0 | 0% | 32
6218 | 0 | 0 | 0 | 2.2164 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1124 | 32.6 | 0 | 83.1124 | 637.4136 | 50.01% | 0 | 0 | 0 | 0% | 32.6
6219 | 0 | 0 | 0 | 1.0074 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0365 | 35.5 | 0 | 90.0365 | 551.0614 | 43.24% | 0 | 0 | 0 | 0% | 35.5
6220 | 0 | 0 | 0 | 2.4178 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6714 | 39.9 | 0 | 100.6714 | 452.1647 | 35.48% | 0 | 0 | 0 | 0% | 39.9
6221 | 0 | 0 | 0 | 2.8208 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3065 | 41.8 | 0 | 105.3065 | 347.869 | 27.29% | 0 | 0 | 0 | 0% | 41.8
6222 | 0 | 0 | 0 | 3.6268 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3566 | 43.1 | 0 | 108.3566 | 239.8322 | 18.82% | 0 | 0 | 0 | 0% | 43.1
6223 | 123 | 79 | 55 | 2.4178 | 19.9 | 61.908 | 0 | 24.282 | 0 | 4.5938 | 0 | 0 | 4.5938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.8322 | 18.82% | 0 | 0 | 0 | 0% | 4.5938
6224 | 152 | 171 | 126 | 2.8208 | 21.8 | 76.5042 | 0 | 39.6859 | 0 | 15.2557 | 0 | 0 | 15.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.8322 | 18.82% | 0 | 0 | 0 | 0% | 15.2557
6225 | 57 | 185 | 152 | 4.6342 | 22.2 | 28.6891 | 0 | 17.0158 | 0 | 15.0848 | 0 | 0 | 15.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.8322 | 18.82% | 0 | 0 | 0 | 0% | 15.0848
6226 | 0 | 109 | 108 | 4.0297 | 23.3 | 0 | 0 | 0 | 0 | 7.5619 | 0 | 0 | 7.5619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.8322 | 18.82% | 0 | 0 | 0 | 0% | 7.5619
6227 | 54 | 280 | 236 | 7.6565 | 24 | 27.1791 | 0 | 17.6741 | 0 | 23.5252 | 0 | 0 | 23.5252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.8322 | 18.82% | 0 | 0 | 0 | 0% | 23.5252
6228 | 231 | 407 | 212 | 8.0595 | 24 | 116.2663 | 76.5182 | 0 | 50.3873 | 40.6803 | 0 | 0 | 40.6803 | 0 | 0 | 0 | 0 | 0 | 50.3873 | 0 | 287.641 | 22.57% | 0 | 0 | 0 | 0% | 40.6803
6229 | 819 | 908 | 231 | 8.261 | 25.8 | 412.2169 | 270.1122 | 0 | 231.65 | 105 | 5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 231.65 | 0 | 507.4365 | 39.81% | 19.175 | 0 | 19.887 | 39.77% | 45
6230 | 438 | 597 | 256 | 7.052 | 26.7 | 220.453 | 141.6277 | 0 | 112.4287 | 78.3483 | 0 | 16.8241 | 61.5241 | 0 | 0 | 0 | 0 | 0 | 112.4287 | 0 | 614.1117 | 48.18% | 12.9041 | 0 | 33.2702 | 66.54% | 44.7
6231 | 721 | 658 | 170 | 6.2461 | 27.5 | 362.8918 | 222.9836 | 0 | 188.9739 | 94.7665 | 4.4523 | 21.031 | 69.2833 | 0 | 0 | 0 | 0 | 0 | 188.9739 | 0 | 793.4151 | 62.25% | 16.1308 | 0 | 50 | 100% | 43.8
6232 | 598 | 460 | 139 | 4.8357 | 27.9 | 300.9838 | 168.7388 | 0 | 139.0399 | 52.2716 | 4.3858 | 0 | 47.8858 | 0 | 0 | 0 | 0 | 0 | 139.0399 | 0 | 925.3397 | 72.6% | 0 | 0 | 50 | 100% | 43.5
6233 | 272 | 213 | 112 | 4.8357 | 27.4 | 136.9023 | 63.3471 | 0 | 40.3601 | 19.1888 | 0 | 0 | 19.1888 | 0 | 0 | 0 | 0 | 0 | 40.3601 | 0 | 963.6344 | 75.61% | 0 | 25 | 24.0758 | 48.15% | 44.1888
6234 | 92 | 68 | 53 | 8.0595 | 25.1 | 46.3052 | 0 | 0 | 0 | 4.4673 | 0 | 0 | 4.4673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 963.6344 | 75.61% | 0 | 23.2175 | 0 | 0% | 27.6849
6235 | 1 | 2 | 2 | 7.858 | 23.3 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9485 | 41 | 0 | 103.9485 | 861.7818 | 67.62% | 0 | 0 | 0 | 0% | 41
6236 | 0 | 0 | 0 | 6.6491 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4689 | 37.6 | 0 | 95.4689 | 769.6144 | 60.39% | 0 | 0 | 0 | 0% | 37.6
6237 | 0 | 0 | 0 | 3.2238 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7606 | 35.7 | 0 | 90.7606 | 682.7873 | 53.57% | 0 | 0 | 0 | 0% | 35.7
6238 | 0 | 0 | 0 | 3.4253 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0591 | 33.8 | 0 | 86.0591 | 601.3846 | 47.19% | 0 | 0 | 0 | 0% | 33.8
6239 | 0 | 0 | 0 | 3.2238 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1626 | 32.6 | 0 | 83.1626 | 523.3458 | 41.06% | 0 | 0 | 0 | 0% | 32.6
6240 | 0 | 0 | 0 | 3.0223 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.465 | 31.9 | 0 | 81.465 | 447.1957 | 35.09% | 0 | 0 | 0 | 0% | 31.9
6241 | 0 | 0 | 0 | 2.2164 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6438 | 32 | 0 | 81.6438 | 370.8177 | 29.09% | 0 | 0 | 0 | 0% | 32
6242 | 0 | 0 | 0 | 2.0149 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5315 | 32.4 | 0 | 82.5315 | 293.3575 | 23.02% | 0 | 0 | 0 | 0% | 32.4
6243 | 0 | 0 | 0 | 1.4104 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.3575 | 23.02% | 0 | 0 | 0 | 0% | 0
6244 | 0 | 0 | 0 | 1.4104 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.3575 | 23.02% | 0 | 0 | 0 | 0% | 0
6245 | 0 | 0 | 0 | 2.0149 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.3575 | 23.02% | 0 | 0 | 0 | 0% | 0
6246 | 0 | 0 | 0 | 3.6268 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.3575 | 23.02% | 0 | 0 | 0 | 0% | 0
6247 | 165 | 64 | 37 | 5.2387 | 19.6 | 83.0474 | 0 | 32.2745 | 0 | 3.6093 | 0 | 0 | 3.6093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.3575 | 23.02% | 0 | 0 | 0 | 0% | 3.6093
6248 | 573 | 264 | 77 | 1.6119 | 22.6 | 288.4009 | 148.8863 | 0 | 121.5678 | 26.0911 | 0 | 0 | 26.0911 | 0 | 0 | 0 | 0 | 0 | 121.5678 | 0 | 408.4431 | 32.05% | 0 | 0 | 0 | 0% | 26.0911
6249 | 741 | 469 | 97 | 1.0074 | 25.1 | 372.9582 | 220.694 | 0 | 188.8553 | 53.0316 | 0 | 3.2658 | 49.7658 | 0 | 0 | 0 | 0 | 0 | 188.8553 | 0 | 587.2284 | 46.07% | 2.5049 | 0 | 2.5982 | 5.196% | 46.5
6250 | 721 | 612 | 143 | 2.4178 | 26 | 362.8918 | 228.9767 | 0 | 196.1663 | 82.2395 | 0 | 17.6698 | 64.5698 | 0 | 0 | 0 | 0 | 0 | 196.1663 | 0 | 772.9348 | 60.65% | 13.5527 | 0 | 16.6561 | 33.31% | 46.9
6251 | 713 | 746 | 201 | 2.6193 | 26.8 | 358.8653 | 233.297 | 0 | 200.1808 | 104.1 | 4.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 200.1808 | 0 | 962.4416 | 75.51% | 19.175 | 0 | 36.5459 | 73.09% | 45.9
6252 | 840 | 837 | 150 | 3.8283 | 27.7 | 422.7866 | 278.1646 | 0 | 241.5944 | 104.8 | 12.8893 | 16.9107 | 75 | 0 | 0 | 0 | 0 | 0 | 241.5944 | 0 | 1191.1538 | 93.46% | 12.9705 | 0 | 50 | 100% | 45.2
6253 | 802 | 818 | 158 | 3.8283 | 28.5 | 403.6605 | 264.4638 | 0 | 228.7324 | 105 | 30 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 228.7324 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45
6254 | 756 | 769 | 184 | 4.2312 | 29.3 | 380.5079 | 0 | 244.4603 | 0 | 105 | 30 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45
6255 | 625 | 618 | 200 | 4.6342 | 29.3 | 314.5734 | 0 | 193.2414 | 0 | 84.0338 | 19.9669 | 0 | 64.0669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.1
6256 | 532 | 449 | 167 | 8.4625 | 28.6 | 267.7649 | 0 | 149.9786 | 0 | 49.2905 | 2.8453 | 0 | 46.4453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.6
6257 | 360 | 249 | 126 | 8.261 | 27.1 | 181.1943 | 0 | 83.6487 | 0 | 24.282 | 0 | 0 | 24.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 21.318 | 27.8907 | 55.78% | 45.6
6258 | 242 | 93 | 52 | 5.2387 | 26 | 121.8028 | 0 | 0 | 0 | 6.0021 | 0 | 0 | 6.0021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 1.9614 | 3.923% | 31.0021
6259 | 1 | 2 | 2 | 3.6268 | 24.4 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9253 | 40.9 | 0 | 103.9253 | 1172.9747 | 92.03% | 0 | 0 | 1.9614 | 3.923% | 40.9
6260 | 0 | 0 | 0 | 0.60446 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.6404 | 37.6 | 0 | 95.6404 | 1080.8405 | 84.8% | 0 | 0 | 1.9614 | 3.923% | 37.6
6261 | 0 | 0 | 0 | 1.8134 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8329 | 35.7 | 0 | 90.8329 | 994.0466 | 77.99% | 0 | 0 | 1.9614 | 3.923% | 35.7
6262 | 0 | 0 | 0 | 0.80595 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1928 | 33.8 | 0 | 86.1928 | 912.6433 | 71.61% | 0 | 0 | 1.9614 | 3.923% | 33.8
6263 | 0 | 0 | 0 | 1.0074 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2386 | 32.6 | 0 | 83.2386 | 834.568 | 65.48% | 0 | 0 | 1.9614 | 3.923% | 32.6
6264 | 0 | 0 | 0 | 0.40297 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4283 | 32.3 | 0 | 82.4283 | 757.3763 | 59.42% | 0 | 0 | 1.9614 | 3.923% | 32.3
6265 | 0 | 0 | 0 | 1.2089 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8976 | 32.1 | 0 | 81.8976 | 680.7588 | 53.41% | 0 | 0 | 1.9614 | 3.923% | 32.1
6266 | 0 | 0 | 0 | 0.60446 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8101 | 32.5 | 0 | 82.8101 | 603.0637 | 47.32% | 0 | 0 | 1.9614 | 3.923% | 32.5
6267 | 0 | 0 | 0 | 1.4104 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9595 | 35.5 | 0 | 89.9595 | 516.7486 | 40.54% | 0 | 0 | 1.9614 | 3.923% | 35.5
6268 | 0 | 0 | 0 | 0.60446 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6722 | 40 | 0 | 100.6722 | 417.6043 | 32.77% | 0 | 0 | 1.9614 | 3.923% | 40
6269 | 0 | 0 | 0 | 3.4253 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.7064 | 42.1 | 0 | 105.7064 | 312.499 | 24.52% | 0 | 0 | 1.9614 | 3.923% | 42.1
6270 | 0 | 1 | 1 | 3.2238 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3888 | 43.6 | 0 | 109.3888 | 203.069 | 15.93% | 0 | 0 | 1.9614 | 3.923% | 43.6
6271 | 184 | 66 | 38 | 2.8208 | 19.8 | 92.6104 | 0 | 35.6567 | 0 | 3.8251 | 0 | 0 | 3.8251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.069 | 15.93% | 0 | 0 | 1.9614 | 3.923% | 3.8251
6272 | 493 | 248 | 89 | 1.6119 | 22.2 | 248.1355 | 127.479 | 0 | 101.4182 | 24.6598 | 0 | 0 | 24.6598 | 0 | 0 | 0 | 0 | 0 | 101.4182 | 0 | 299.8076 | 23.52% | 0 | 0 | 1.9614 | 3.923% | 24.6598
6273 | 653 | 449 | 121 | 1.8134 | 24.5 | 328.6663 | 194.0327 | 0 | 163.6437 | 48.8919 | 1.096 | 0 | 47.796 | 0 | 0 | 0 | 0 | 0 | 163.6437 | 0 | 455.9004 | 35.77% | 0 | 0 | 1.9614 | 3.923% | 46.7
6274 | 760 | 622 | 129 | 3.2238 | 25.6 | 382.5212 | 241.1219 | 0 | 207.2063 | 86.052 | 0 | 19.426 | 66.626 | 0 | 0 | 0 | 0 | 0 | 207.2063 | 0 | 653.5458 | 51.28% | 14.8997 | 0 | 17.4188 | 34.84% | 47.2
6275 | 798 | 746 | 143 | 3.6268 | 26.6 | 401.6473 | 261.0345 | 0 | 225.5729 | 103.9 | 3.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 225.5729 | 0 | 868.7105 | 68.16% | 19.175 | 0 | 37.3114 | 74.62% | 46.1
6276 | 752 | 810 | 197 | 4.6342 | 27 | 378.4947 | 248.9487 | 0 | 213.9983 | 104.5 | 13.5552 | 15.9448 | 75 | 0 | 0 | 0 | 0 | 0 | 213.9983 | 0 | 1072.8345 | 84.18% | 12.2297 | 0 | 49.9988 | 100% | 45.5
6277 | 716 | 785 | 199 | 7.6565 | 27.4 | 360.3752 | 236.0672 | 0 | 200.4235 | 104.9 | 29.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 200.4235 | 0 | 1264.0101 | 99.18% | 0 | 0 | 49.9988 | 100% | 45.1
6278 | 697 | 738 | 202 | 8.8654 | 27.6 | 350.8122 | 0 | 225.3883 | 0 | 104.9 | 29.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.0101 | 99.18% | 0 | 0 | 49.9988 | 100% | 45.1
6279 | 598 | 600 | 196 | 8.8654 | 27.6 | 300.9838 | 0 | 184.8425 | 0 | 82.4797 | 19.1399 | 0 | 63.3399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.0101 | 99.18% | 0 | 0 | 49.9988 | 100% | 44.2
6280 | 337 | 328 | 153 | 9.2684 | 26.8 | 169.618 | 0 | 94.9171 | 0 | 34.2305 | 0 | 0 | 34.2305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.0101 | 99.18% | 0 | 9.5695 | 40.0727 | 80.15% | 43.8
6281 | 304 | 220 | 114 | 9.6714 | 26 | 153.0085 | 0 | 70.472 | 0 | 20.7212 | 0 | 0 | 20.7212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.0101 | 99.18% | 0 | 24.9788 | 14.1624 | 28.32% | 45.7
6282 | 129 | 72 | 50 | 9.4699 | 24.5 | 64.9279 | 0 | 0 | 0 | 4.7021 | 0 | 0 | 4.7021 | 0 | 0 | 0 | 70.9395 | 27.0429 | 0 | 70.9395 | 1198.7952 | 94.06% | 0 | 13.655 | 0 | 0% | 45.4
6283 | 0 | 1 | 1 | 7.858 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.3543 | 41.2 | 0 | 104.3543 | 1096.4506 | 86.03% | 0 | 0 | 0 | 0% | 41.2
6284 | 0 | 0 | 0 | 6.0446 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1165 | 37.9 | 0 | 96.1165 | 1003.4971 | 78.74% | 0 | 0 | 0 | 0% | 37.9
6285 | 0 | 0 | 0 | 5.0372 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9544 | 35.8 | 0 | 90.9544 | 916.4542 | 71.91% | 0 | 0 | 0 | 0% | 35.8
6286 | 0 | 0 | 0 | 6.2461 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7625 | 34.1 | 0 | 86.7625 | 834.2463 | 65.46% | 0 | 0 | 0 | 0% | 34.1
6287 | 0 | 0 | 0 | 7.052 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8086 | 32.9 | 0 | 83.8086 | 755.4743 | 59.28% | 0 | 0 | 0 | 0% | 32.9
6288 | 0 | 0 | 0 | 4.0297 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6068 | 32.4 | 0 | 82.6068 | 678.0955 | 53.2% | 0 | 0 | 0 | 0% | 32.4
6289 | 0 | 0 | 0 | 4.8357 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1511 | 32.2 | 0 | 82.1511 | 601.2203 | 47.17% | 0 | 0 | 0 | 0% | 32.2
6290 | 0 | 0 | 0 | 6.2461 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3775 | 32.7 | 0 | 83.3775 | 522.9566 | 41.03% | 0 | 0 | 0 | 0% | 32.7
6291 | 0 | 0 | 0 | 6.0446 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2987 | 35.6 | 0 | 90.2987 | 436.3872 | 34.24% | 0 | 0 | 0 | 0% | 35.6
6292 | 0 | 0 | 0 | 5.0372 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.436 | 40.2 | 0 | 101.436 | 336.708 | 26.42% | 0 | 0 | 0 | 0% | 40.2
6293 | 0 | 0 | 0 | 4.4327 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.9471 | 42.1 | 0 | 105.9471 | 231.6271 | 18.17% | 0 | 0 | 0 | 0% | 42.1
6294 | 0 | 0 | 0 | 4.8357 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.6271 | 18.17% | 0 | 0 | 0 | 0% | 0
6295 | 13 | 46 | 44 | 5.0372 | 18.9 | 6.5431 | 0 | 2.4956 | 0 | 2.9065 | 0 | 0 | 2.9065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.6271 | 18.17% | 0 | 0 | 0 | 0% | 2.9065
6296 | 89 | 168 | 135 | 7.052 | 20 | 44.7952 | 0 | 22.9015 | 0 | 13.8404 | 0 | 0 | 13.8404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.6271 | 18.17% | 0 | 0 | 0 | 0% | 13.8404
6297 | 163 | 339 | 261 | 10.6788 | 22.4 | 82.0407 | 0 | 48.3207 | 0 | 32.2004 | 0 | 0 | 32.2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.6271 | 18.17% | 0 | 0 | 0 | 0% | 32.2004
6298 | 102 | 352 | 279 | 11.0818 | 22.6 | 51.3384 | 0 | 32.3288 | 0 | 30.8562 | 0 | 0 | 30.8562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.6271 | 18.17% | 0 | 0 | 0 | 0% | 30.8562
6299 | 51 | 349 | 307 | 8.6639 | 23.2 | 25.6692 | 0 | 16.6779 | 0 | 29.849 | 0 | 0 | 29.849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.6271 | 18.17% | 0 | 0 | 0 | 0% | 29.849
6300 | 19 | 406 | 384 | 9.6714 | 23.5 | 9.563 | 0 | 6.288 | 0 | 32.2857 | 0 | 0 | 32.2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.6271 | 18.17% | 0 | 0 | 0 | 0% | 32.2857
6301 | 165 | 655 | 511 | 11.0818 | 24.5 | 83.0474 | 0 | 54.3922 | 0 | 78.2379 | 0 | 17.319 | 60.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.6271 | 18.17% | 13.2836 | 0 | 13.7829 | 27.57% | 43.6
6302 | 257 | 661 | 455 | 12.0892 | 25 | 129.3526 | 83.108 | 0 | 54.51 | 82.0853 | 0 | 19.4926 | 62.5926 | 0 | 0 | 0 | 0 | 0 | 54.51 | 0 | 283.415 | 22.24% | 14.9508 | 0 | 29.2956 | 58.59% | 43.1
6303 | 336 | 546 | 326 | 12.0892 | 25 | 169.1146 | 103.8289 | 0 | 73.8664 | 67.3783 | 0 | 12.4392 | 54.9392 | 0 | 0 | 0 | 0 | 0 | 73.8664 | 0 | 353.5927 | 27.74% | 9.5408 | 0 | 39.195 | 78.39% | 42.5
6304 | 239 | 376 | 245 | 12.4922 | 24.7 | 120.2929 | 67.2516 | 0 | 39.2145 | 35.3542 | 0 | 0 | 35.3542 | 0 | 0 | 0 | 0 | 0 | 39.2145 | 0 | 390.849 | 30.67% | 0 | 6.9458 | 31.9893 | 63.98% | 42.3
6305 | 51 | 166 | 146 | 12.2907 | 23.7 | 25.6692 | 0 | 11.7947 | 0 | 13.525 | 0 | 0 | 13.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390.849 | 30.67% | 0 | 25 | 6.0534 | 12.11% | 38.525
6306 | 2 | 61 | 60 | 14.3056 | 22.5 | 1.0066 | 0 | 0 | 0 | 4.0389 | 0 | 0 | 4.0389 | 0 | 0 | 0 | 86.8847 | 34.0257 | 0 | 86.8847 | 308.4901 | 24.2% | 0 | 5.8354 | 0 | 0% | 43.9
6307 | 0 | 1 | 1 | 10.2758 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3229 | 33.004 | 0 | 84.3229 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 33.004
6308 | 0 | 0 | 0 | 9.4699 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6309 | 0 | 0 | 0 | 8.4625 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6310 | 0 | 0 | 0 | 4.8357 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6311 | 0 | 0 | 0 | 3.6268 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6312 | 0 | 0 | 0 | 3.6268 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6313 | 0 | 0 | 0 | 2.6193 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6314 | 0 | 0 | 0 | 3.2238 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6315 | 0 | 0 | 0 | 2.8208 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6316 | 0 | 0 | 0 | 2.0149 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6317 | 0 | 0 | 0 | 1.4104 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6318 | 0 | 0 | 0 | 2.0149 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 0
6319 | 1 | 32 | 32 | 1.6119 | 19.1 | 0.50332 | 0 | 0.19014 | 0 | 1.8286 | 0 | 0 | 1.8286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 1.8286
6320 | 2 | 112 | 110 | 2.2164 | 20.1 | 1.0066 | 0 | 0.51212 | 0 | 8.2442 | 0 | 0 | 8.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 8.2442
6321 | 29 | 283 | 266 | 1.0074 | 22.3 | 14.5962 | 0 | 8.5768 | 0 | 22.7192 | 0 | 0 | 22.7192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.0145 | 17.97% | 0 | 0 | 0 | 0% | 22.7192
6322 | 235 | 469 | 306 | 2.0149 | 23.9 | 118.2796 | 74.4087 | 0 | 51.246 | 45.386 | 2.293 | 0 | 43.093 | 0 | 0 | 0 | 0 | 0 | 51.246 | 0 | 277.6258 | 21.78% | 0 | 0 | 0 | 0% | 40.8
6323 | 278 | 636 | 416 | 4.2312 | 24.9 | 139.9222 | 90.8847 | 0 | 66.4761 | 78.7272 | 0 | 19.5136 | 59.2136 | 0 | 0 | 0 | 0 | 0 | 66.4761 | 0 | 340.6842 | 26.73% | 14.9669 | 0 | 15.5313 | 31.06% | 39.7
6324 | 401 | 786 | 454 | 6.8506 | 25.8 | 201.8303 | 132.6703 | 0 | 104.0589 | 112.2 | 12.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 104.0589 | 0 | 439.3932 | 34.48% | 19.175 | 0 | 35.4293 | 70.86% | 37.8
6325 | 210 | 602 | 424 | 7.6565 | 26 | 105.6967 | 69.2151 | 0 | 43.8834 | 76.1584 | 1.5225 | 18.3067 | 56.3292 | 0 | 0 | 0 | 0 | 0 | 43.8834 | 0 | 481.0205 | 37.74% | 14.0412 | 0 | 50 | 100% | 36.5
6326 | 35 | 398 | 366 | 7.858 | 25.6 | 17.6161 | 0 | 11.3185 | 0 | 33.6802 | 0 | 0 | 33.6802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481.0205 | 37.74% | 0 | 2.5198 | 47.3856 | 94.77% | 36.2
6327 | 71 | 348 | 295 | 9.8729 | 25.1 | 35.7355 | 0 | 21.9338 | 0 | 29.8422 | 0 | 0 | 29.8422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481.0205 | 37.74% | 0 | 6.0578 | 41.1003 | 82.2% | 35.9
6328 | 14 | 224 | 216 | 9.4699 | 24.3 | 7.0464 | 0 | 3.9356 | 0 | 17.5965 | 0 | 0 | 17.5965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481.0205 | 37.74% | 0 | 18.6035 | 21.7979 | 43.6% | 36.2
6329 | 2 | 92 | 91 | 8.0595 | 23.8 | 1.0066 | 0 | 0.46143 | 0 | 6.5647 | 0 | 0 | 6.5647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481.0205 | 37.74% | 0 | 21.0091 | 2.7756e-15 | 5.551e-15% | 27.5738
6330 | 10 | 52 | 50 | 6.4476 | 23.5 | 5.0332 | 0 | 0 | 0 | 3.2853 | 0 | 0 | 3.2853 | 0 | 0 | 0 | 92.3621 | 36.2147 | 0 | 92.3621 | 392.3505 | 30.78% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.5
6331 | 0 | 1 | 1 | 6.6491 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1631 | 37 | 0 | 94.1631 | 301.4845 | 23.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37
6332 | 0 | 0 | 0 | 3.4253 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3917 | 25.1784 | 0 | 66.3917 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 25.1784
6333 | 0 | 0 | 0 | 3.6268 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6334 | 0 | 0 | 0 | 3.4253 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6335 | 0 | 0 | 0 | 2.8208 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6336 | 0 | 0 | 0 | 1.2089 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6337 | 0 | 0 | 0 | 2.0149 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6338 | 0 | 0 | 0 | 2.4178 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6339 | 0 | 0 | 0 | 2.0149 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6340 | 0 | 0 | 0 | 1.8134 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6341 | 0 | 0 | 0 | 3.2238 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6342 | 0 | 0 | 0 | 1.4104 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
6343 | 0 | 27 | 27 | 1.0074 | 18.6 | 0 | 0 | 0 | 0 | 1.4501 | 0 | 0 | 1.4501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240.2778 | 18.85% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 1.4501
6344 | 415 | 240 | 91 | 2.0149 | 19.6 | 208.8767 | 105.7409 | 0 | 80.8288 | 22.5146 | 0 | 0 | 22.5146 | 0 | 0 | 0 | 0 | 0 | 80.8288 | 0 | 316.8723 | 24.86% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 22.5146
6345 | 749 | 456 | 87 | 2.6193 | 22.8 | 376.9847 | 220.9945 | 0 | 188.585 | 65.616 | 0 | 14.808 | 50.808 | 0 | 0 | 0 | 0 | 0 | 188.585 | 0 | 495.5779 | 38.88% | 11.3577 | 0 | 11.7877 | 23.58% | 36
6346 | 859 | 635 | 84 | 4.0297 | 25.2 | 432.3496 | 271.7162 | 0 | 235.4302 | 102.468 | 7.984 | 25 | 69.484 | 0 | 0 | 0 | 0 | 0 | 235.4302 | 0 | 718.6745 | 56.39% | 19.175 | 0 | 31.6886 | 63.38% | 36.5
6347 | 869 | 754 | 105 | 3.2238 | 26.9 | 437.3828 | 284.015 | 0 | 247.3105 | 113.8 | 15.7968 | 23.0032 | 75 | 0 | 0 | 0 | 0 | 0 | 247.3105 | 0 | 953.0291 | 74.78% | 17.6435 | 0 | 50 | 100% | 36.2
6348 | 852 | 812 | 126 | 3.2238 | 28.1 | 428.8264 | 281.7974 | 0 | 245.224 | 115.5 | 40.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 245.224 | 0 | 1185.4066 | 93.01% | 0 | 0 | 50 | 100% | 34.5
6349 | 792 | 790 | 150 | 2.4178 | 29.3 | 398.6274 | 260.9965 | 0 | 225.9537 | 116.6 | 41.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 225.9537 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.4
6350 | 755 | 740 | 167 | 4.0297 | 30.1 | 380.0046 | 0 | 244.1614 | 0 | 116.7 | 41.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.3
6351 | 614 | 584 | 181 | 6.0446 | 30.3 | 309.0369 | 0 | 189.6254 | 0 | 90.8414 | 28.7707 | 0 | 62.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.3
6352 | 597 | 425 | 112 | 5.6416 | 30.3 | 300.4805 | 0 | 167.6635 | 0 | 56.3551 | 11.1776 | 0 | 45.1776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34
6353 | 119 | 188 | 149 | 5.6416 | 29.3 | 59.8948 | 0 | 27.3888 | 0 | 16.4153 | 0 | 0 | 16.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 20.7847 | 28.4317 | 56.86% | 37.2
6354 | 255 | 94 | 54 | 4.8357 | 28.2 | 128.3459 | 0 | 0 | 0 | 6.0311 | 0 | 0 | 6.0311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 2.488 | 4.976% | 31.0311
6355 | 0 | 1 | 1 | 3.0223 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7841 | 36.6 | 0 | 93.7841 | 1184.6481 | 92.95% | 0 | 0 | 2.488 | 4.976% | 36.6
6356 | 0 | 0 | 0 | 3.8283 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7702 | 34.3 | 0 | 87.7702 | 1101.4441 | 86.42% | 0 | 0 | 2.488 | 4.976% | 34.3
6357 | 0 | 0 | 0 | 3.0223 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2695 | 32.1 | 0 | 82.2695 | 1024.4409 | 80.38% | 0 | 0 | 2.488 | 4.976% | 32.1
6358 | 0 | 0 | 0 | 1.4104 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5752 | 30.6 | 0 | 78.5752 | 951.5209 | 74.66% | 0 | 0 | 2.488 | 4.976% | 30.6
6359 | 0 | 0 | 0 | 2.2164 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7288 | 29.4 | 0 | 75.7288 | 881.5335 | 69.17% | 0 | 0 | 2.488 | 4.976% | 29.4
6360 | 0 | 0 | 0 | 3.0223 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5129 | 28.9 | 0 | 74.5129 | 812.7085 | 63.77% | 0 | 0 | 2.488 | 4.976% | 28.9
6361 | 0 | 0 | 0 | 2.4178 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6698 | 29 | 0 | 74.6698 | 743.7189 | 58.35% | 0 | 0 | 2.488 | 4.976% | 29
6362 | 0 | 0 | 0 | 2.2164 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3831 | 29.8 | 0 | 76.3831 | 673.0566 | 52.81% | 0 | 0 | 2.488 | 4.976% | 29.8
6363 | 0 | 0 | 0 | 2.6193 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2656 | 33.1 | 0 | 84.2656 | 593.5544 | 46.57% | 0 | 0 | 2.488 | 4.976% | 33.1
6364 | 0 | 0 | 0 | 3.4253 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8848 | 38 | 0 | 95.8848 | 500.0681 | 39.24% | 0 | 0 | 2.488 | 4.976% | 38
6365 | 0 | 0 | 0 | 4.0297 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.7319 | 40 | 0 | 100.7319 | 400.7997 | 31.45% | 0 | 0 | 2.488 | 4.976% | 40
6366 | 0 | 0 | 0 | 2.6193 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4434 | 41.6 | 0 | 104.4434 | 296.9846 | 23.3% | 0 | 0 | 2.488 | 4.976% | 41.6
6367 | 239 | 61 | 27 | 2.2164 | 19.3 | 120.2929 | 0 | 44.57 | 0 | 3.5311 | 0 | 0 | 3.5311 | 0 | 0 | 0 | 99.3039 | 39.3689 | 0 | 99.3039 | 199.4927 | 15.65% | 0 | 0 | 2.488 | 4.976% | 42.9
6368 | 611 | 267 | 79 | 3.4253 | 22 | 307.5269 | 154.9089 | 0 | 126.5001 | 28.4141 | 0 | 0 | 28.4141 | 0 | 0 | 0 | 0 | 0 | 126.5001 | 0 | 318.9378 | 25.02% | 0 | 0 | 2.488 | 4.976% | 28.4141
6369 | 617 | 433 | 130 | 5.8431 | 23 | 310.5468 | 181.6167 | 0 | 150.4877 | 52.2808 | 0 | 3.9904 | 48.2904 | 0 | 0 | 0 | 0 | 0 | 150.4877 | 0 | 461.0326 | 36.17% | 3.0606 | 0 | 5.665 | 11.33% | 44.3
6370 | 734 | 611 | 141 | 6.8506 | 24.2 | 369.435 | 231.945 | 0 | 196.9896 | 91.6994 | 0 | 23.6497 | 68.0497 | 0 | 0 | 0 | 0 | 0 | 196.9896 | 0 | 647.0359 | 50.77% | 18.1393 | 0 | 24.4936 | 48.99% | 44.4
6371 | 706 | 734 | 210 | 4.6342 | 25.4 | 355.3421 | 230.6759 | 0 | 197.0302 | 106.8 | 6.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 197.0302 | 0 | 833.0775 | 65.36% | 19.175 | 0 | 44.3974 | 88.79% | 43.2
6372 | 792 | 877 | 241 | 4.4327 | 26.2 | 398.6274 | 261.8727 | 0 | 226.0845 | 107.6 | 25.5643 | 7.0357 | 75 | 0 | 0 | 0 | 0 | 0 | 226.0845 | 0 | 1046.553 | 82.11% | 5.3964 | 0 | 49.9988 | 100% | 42.4
6373 | 681 | 777 | 229 | 7.052 | 26.5 | 342.7591 | 224.3799 | 0 | 189.7905 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 189.7905 | 0 | 1225.7586 | 96.17% | 0 | 0 | 49.9988 | 100% | 42.1
6374 | 662 | 694 | 197 | 7.858 | 26.8 | 333.1961 | 0 | 214.0903 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.7586 | 96.17% | 0 | 0 | 49.9988 | 100% | 42
6375 | 803 | 635 | 116 | 7.6565 | 27 | 404.1639 | 0 | 247.9217 | 0 | 99.6092 | 29.0046 | 0 | 70.6046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.7586 | 96.17% | 0 | 0 | 49.9988 | 100% | 41.6
6376 | 570 | 425 | 134 | 9.2684 | 26.1 | 286.8909 | 0 | 159.9218 | 0 | 51.7444 | 5.1222 | 0 | 46.6222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.7586 | 96.17% | 0 | 0 | 49.9988 | 100% | 41.5
6377 | 125 | 191 | 143 | 8.6639 | 24.6 | 62.9147 | 0 | 28.6992 | 0 | 16.4479 | 0 | 0 | 16.4479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.7586 | 96.17% | 0 | 25 | 24.0527 | 48.11% | 41.4479
6378 | 16 | 50 | 48 | 6.6491 | 23.4 | 8.0531 | 0 | 0 | 0 | 3.2929 | 0 | 0 | 3.2929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.7586 | 96.17% | 0 | 23.1767 | 0 | 0% | 26.4697
6379 | 0 | 1 | 1 | 5.4401 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5486 | 39.7 | 0 | 100.5486 | 1127.6358 | 88.48% | 0 | 0 | 0 | 0% | 39.7
6380 | 0 | 0 | 0 | 3.8283 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4302 | 36.4 | 0 | 92.4302 | 1038.9043 | 81.51% | 0 | 0 | 0 | 0% | 36.4
6381 | 0 | 0 | 0 | 1.4104 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.992 | 34.6 | 0 | 87.992 | 955.2398 | 74.95% | 0 | 0 | 0 | 0% | 34.6
6382 | 0 | 0 | 0 | 2.0149 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8443 | 32.9 | 0 | 83.8443 | 876.4633 | 68.77% | 0 | 0 | 0 | 0% | 32.9
6383 | 0 | 0 | 0 | 1.6119 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0952 | 31.8 | 0 | 81.0952 | 800.7608 | 62.83% | 0 | 0 | 0 | 0% | 31.8
6384 | 0 | 0 | 0 | 1.2089 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0521 | 31.4 | 0 | 80.0521 | 726.1937 | 56.98% | 0 | 0 | 0 | 0% | 31.4
6385 | 0 | 0 | 0 | 1.4104 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9881 | 31.4 | 0 | 79.9881 | 651.6269 | 51.13% | 0 | 0 | 0 | 0% | 31.4
6386 | 0 | 0 | 0 | 2.2164 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4709 | 32 | 0 | 81.4709 | 575.3581 | 45.14% | 0 | 0 | 0 | 0% | 32
6387 | 0 | 0 | 0 | 0.60446 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2606 | 34.5 | 0 | 87.2606 | 491.9058 | 38.6% | 0 | 0 | 0 | 0% | 34.5
6388 | 0 | 0 | 0 | 1.0074 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6266 | 38.8 | 0 | 97.6266 | 396.2367 | 31.09% | 0 | 0 | 0 | 0% | 38.8
6389 | 0 | 0 | 0 | 1.2089 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.3787 | 40.4 | 0 | 101.3787 | 295.9548 | 23.22% | 0 | 0 | 0 | 0% | 40.4
6390 | 0 | 0 | 0 | 0.60446 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2526 | 38.712 | 0 | 97.2526 | 200.4863 | 15.73% | 0 | 0 | 0 | 0% | 38.712
6391 | 323 | 67 | 23 | 2.0149 | 17.3 | 162.5715 | 59.6438 | 0 | 38.0606 | 3.7933 | 0 | 0 | 3.7933 | 0 | 0 | 0 | 0 | 0 | 38.0606 | 0 | 236.5677 | 18.56% | 0 | 0 | 0 | 0% | 3.7933
6392 | 691 | 259 | 48 | 1.2089 | 21.5 | 347.7923 | 174.3175 | 0 | 145.4809 | 28.1714 | 0 | 0 | 28.1714 | 0 | 0 | 0 | 0 | 0 | 145.4809 | 0 | 374.4831 | 29.38% | 0 | 0 | 0 | 0% | 28.1714
6393 | 829 | 460 | 60 | 1.6119 | 24.3 | 417.2501 | 243.4406 | 0 | 209.8792 | 58.8124 | 0 | 6.9062 | 51.9062 | 0 | 0 | 0 | 0 | 0 | 209.8792 | 0 | 573.4479 | 44.99% | 5.2971 | 0 | 5.4992 | 11% | 45
6394 | 905 | 635 | 65 | 3.0223 | 25.9 | 455.5022 | 285.6962 | 0 | 248.9597 | 95.0693 | 0 | 24.7347 | 70.3347 | 0 | 0 | 0 | 0 | 0 | 248.9597 | 0 | 809.4609 | 63.51% | 18.9715 | 0 | 25.1945 | 50.39% | 45.6
6395 | 939 | 760 | 69 | 4.0297 | 27.8 | 472.615 | 306.7182 | 0 | 268.2933 | 105.7 | 5.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 268.2933 | 0 | 1063.8021 | 83.47% | 19.175 | 0 | 45.1012 | 90.2% | 44.3
6396 | 934 | 816 | 76 | 5.6416 | 28.6 | 470.0984 | 308.7304 | 0 | 269.4793 | 106.3 | 25.1477 | 6.1523 | 75 | 0 | 0 | 0 | 0 | 0 | 269.4793 | 0 | 1274.5104 | 100% | 4.7188 | 0 | 50 | 100% | 43.7
6397 | 937 | 819 | 76 | 5.4401 | 29.5 | 471.6084 | 0 | 308.676 | 0 | 106.3 | 31.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.7
6398 | 918 | 755 | 74 | 7.052 | 30.1 | 462.0454 | 0 | 296.886 | 0 | 106.4 | 31.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.6
6399 | 883 | 634 | 71 | 9.2684 | 29.5 | 444.4293 | 0 | 272.5386 | 0 | 99.6266 | 28.2633 | 0 | 71.3633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.1
6400 | 815 | 465 | 64 | 8.8654 | 29.6 | 410.2037 | 0 | 228.429 | 0 | 63.2642 | 10.2321 | 0 | 53.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.8
6401 | 687 | 267 | 51 | 8.4625 | 28.2 | 345.779 | 0 | 157.3388 | 0 | 29.1869 | 0 | 0 | 29.1869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 16.1131 | 33.2747 | 66.55% | 45.3
6402 | 314 | 68 | 25 | 6.8506 | 24.6 | 158.0417 | 0 | 0 | 0 | 4.2739 | 0 | 0 | 4.2739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 7.3238 | 14.65% | 29.2739
6403 | 0 | 0 | 0 | 3.6268 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6595 | 33.5437 | 0 | 85.6595 | 1193.7961 | 93.67% | 0 | 7.0563 | 0 | 0% | 40.6
6404 | 0 | 0 | 0 | 0.80595 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0594 | 37.1 | 0 | 94.0594 | 1103.1165 | 86.55% | 0 | 0 | 0 | 0% | 37.1
6405 | 0 | 0 | 0 | 0.60446 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.127 | 35.5 | 0 | 90.127 | 1016.917 | 79.79% | 0 | 0 | 0 | 0% | 35.5
6406 | 0 | 0 | 0 | 1.4104 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8044 | 33.7 | 0 | 85.8044 | 935.8694 | 73.43% | 0 | 0 | 0 | 0% | 33.7
6407 | 0 | 0 | 0 | 1.8134 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0509 | 32.6 | 0 | 83.0509 | 857.9581 | 67.32% | 0 | 0 | 0 | 0% | 32.6
6408 | 0 | 0 | 0 | 1.2089 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5785 | 32 | 0 | 81.5785 | 781.7266 | 61.34% | 0 | 0 | 0 | 0% | 32
6409 | 0 | 0 | 0 | 3.2238 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9468 | 32.1 | 0 | 81.9468 | 705.095 | 55.32% | 0 | 0 | 0 | 0% | 32.1
6410 | 0 | 0 | 0 | 4.4327 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2132 | 32.6 | 0 | 83.2132 | 627.0403 | 49.2% | 0 | 0 | 0 | 0% | 32.6
6411 | 0 | 0 | 0 | 4.8357 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9188 | 35.4 | 0 | 89.9188 | 541.0416 | 42.45% | 0 | 0 | 0 | 0% | 35.4
6412 | 0 | 0 | 0 | 4.8357 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.255 | 40.1 | 0 | 101.255 | 441.661 | 34.65% | 0 | 0 | 0 | 0% | 40.1
6413 | 0 | 0 | 0 | 3.0223 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2233 | 41.8 | 0 | 105.2233 | 337.4571 | 26.48% | 0 | 0 | 0 | 0% | 41.8
6414 | 0 | 0 | 0 | 5.4401 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.9926 | 43.4 | 0 | 108.9926 | 228.6543 | 17.94% | 0 | 0 | 0 | 0% | 43.4
6415 | 346 | 66 | 22 | 5.0372 | 20.4 | 174.1478 | 63.258 | 0 | 40.1047 | 3.8449 | 0 | 0 | 3.8449 | 0 | 0 | 0 | 0 | 0 | 40.1047 | 0 | 266.7939 | 20.93% | 0 | 0 | 0 | 0% | 3.8449
6416 | 706 | 260 | 47 | 2.4178 | 22.6 | 355.3421 | 177.2082 | 0 | 147.7832 | 28.7582 | 0 | 0 | 28.7582 | 0 | 0 | 0 | 0 | 0 | 147.7832 | 0 | 407.3356 | 31.96% | 0 | 0 | 0 | 0% | 28.7582
6417 | 836 | 461 | 60 | 2.0149 | 26.7 | 420.7733 | 244.9118 | 0 | 211.1163 | 58.0293 | 0 | 5.9146 | 52.1146 | 0 | 0 | 0 | 0 | 0 | 211.1163 | 0 | 608.1071 | 47.71% | 4.5365 | 0 | 4.7103 | 9.421% | 46.2
6418 | 896 | 631 | 69 | 4.4327 | 28.3 | 450.9724 | 282.5737 | 0 | 245.5685 | 94.5863 | 0 | 24.2432 | 70.3432 | 0 | 0 | 0 | 0 | 0 | 245.5685 | 0 | 841.6426 | 66.04% | 18.5945 | 0 | 24.0171 | 48.03% | 46.1
6419 | 925 | 753 | 75 | 5.6416 | 29.4 | 465.5686 | 302.0596 | 0 | 263.2958 | 105 | 5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 263.2958 | 0 | 1092.0367 | 85.68% | 19.175 | 0 | 43.9266 | 87.85% | 45
6420 | 937 | 817 | 78 | 5.8431 | 30 | 471.6084 | 309.6273 | 0 | 270.2166 | 105.8 | 23.1738 | 7.6262 | 75 | 0 | 0 | 0 | 0 | 0 | 270.2166 | 0 | 1274.5104 | 100% | 5.8493 | 0 | 50 | 100% | 44.2
6421 | 930 | 815 | 81 | 7.858 | 30.1 | 468.0852 | 0 | 306.3175 | 0 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.9
6422 | 901 | 748 | 84 | 8.0595 | 30 | 453.489 | 0 | 291.3929 | 0 | 106.2 | 31.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.8
6423 | 850 | 622 | 83 | 7.052 | 30.1 | 427.8198 | 0 | 262.2721 | 0 | 95.7856 | 26.3428 | 0 | 69.4428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.1
6424 | 761 | 447 | 77 | 6.0446 | 30.1 | 383.0245 | 0 | 213.0746 | 0 | 58.8978 | 7.8989 | 0 | 50.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.1
6425 | 618 | 252 | 61 | 4.0297 | 29.9 | 311.0501 | 0 | 141.1798 | 0 | 27.2399 | 0 | 0 | 27.2399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 18.3601 | 30.9394 | 61.88% | 45.6
6426 | 270 | 64 | 28 | 5.0372 | 27 | 135.8957 | 0 | 0 | 0 | 4.077 | 0 | 0 | 4.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 4.9846 | 9.969% | 29.077
6427 | 0 | 0 | 0 | 4.2312 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2281 | 35.6977 | 0 | 91.2281 | 1187.5603 | 93.18% | 0 | 4.8023 | 0 | 0% | 40.5
6428 | 0 | 0 | 0 | 7.455 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4661 | 37.2 | 0 | 94.4661 | 1096.6004 | 86.04% | 0 | 0 | 0 | 0% | 37.2
6429 | 0 | 0 | 0 | 6.4476 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9705 | 35.4 | 0 | 89.9705 | 1010.682 | 79.3% | 0 | 0 | 0 | 0% | 35.4
6430 | 0 | 0 | 0 | 4.4327 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.879 | 33.7 | 0 | 85.879 | 929.6366 | 72.94% | 0 | 0 | 0 | 0% | 33.7
6431 | 0 | 0 | 0 | 4.6342 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2132 | 32.6 | 0 | 83.2132 | 851.6193 | 66.82% | 0 | 0 | 0 | 0% | 32.6
6432 | 0 | 0 | 0 | 5.0372 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1995 | 32.2 | 0 | 82.1995 | 774.7204 | 60.79% | 0 | 0 | 0 | 0% | 32.2
6433 | 0 | 0 | 0 | 5.2387 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6569 | 32 | 0 | 81.6569 | 698.4061 | 54.8% | 0 | 0 | 0 | 0% | 32
6434 | 0 | 0 | 0 | 4.8357 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7852 | 32.5 | 0 | 82.7852 | 620.7456 | 48.7% | 0 | 0 | 0 | 0% | 32.5
6435 | 0 | 0 | 0 | 5.6416 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4776 | 35.3 | 0 | 89.4776 | 535.0276 | 41.98% | 0 | 0 | 0 | 0% | 35.3
6436 | 0 | 0 | 0 | 4.4327 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1175 | 39.8 | 0 | 100.1175 | 436.5094 | 34.25% | 0 | 0 | 0 | 0% | 39.8
6437 | 0 | 0 | 0 | 3.6268 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7547 | 41.7 | 0 | 104.7547 | 332.5913 | 26.1% | 0 | 0 | 0 | 0% | 41.7
6438 | 0 | 0 | 0 | 4.6342 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.6421 | 42.9 | 0 | 107.6421 | 225.2236 | 17.67% | 0 | 0 | 0 | 0% | 42.9
6439 | 304 | 63 | 24 | 3.6268 | 19.4 | 153.0085 | 0 | 0 | 0 | 3.7703 | 0 | 0 | 3.7703 | 0 | 0 | 0 | 60.8889 | 22.9731 | 0 | 60.8889 | 169.5204 | 13.3% | 0 | 0 | 0 | 0% | 26.7435
6440 | 679 | 255 | 52 | 2.2164 | 22.2 | 341.7525 | 169.5723 | 0 | 140.6375 | 28.4651 | 0 | 0 | 28.4651 | 0 | 0 | 0 | 0 | 0 | 140.6375 | 0 | 303.062 | 23.78% | 0 | 0 | 0 | 0% | 28.4651
6441 | 824 | 458 | 65 | 4.0297 | 24.5 | 414.7335 | 240.8205 | 0 | 206.6483 | 60.6838 | 0 | 7.5419 | 53.1419 | 0 | 0 | 0 | 0 | 0 | 206.6483 | 0 | 499.2837 | 39.17% | 5.7846 | 0 | 6.0071 | 12.01% | 45.6
6442 | 894 | 630 | 72 | 8.4625 | 25.7 | 449.9657 | 281.663 | 0 | 242.4124 | 99.0411 | 1.4706 | 25 | 72.5706 | 0 | 0 | 0 | 0 | 0 | 242.4124 | 0 | 729.4651 | 57.23% | 19.175 | 0 | 25.9195 | 51.84% | 46.1
6443 | 929 | 754 | 77 | 10.6788 | 26.1 | 467.5819 | 303.2719 | 0 | 261.356 | 104.9 | 4.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 261.356 | 0 | 977.6343 | 76.71% | 19.175 | 0 | 45.832 | 91.66% | 45.1
6444 | 941 | 818 | 79 | 9.0669 | 26.8 | 473.6217 | 310.8539 | 0 | 269.3781 | 105.4 | 25.1671 | 5.2329 | 75 | 0 | 0 | 0 | 0 | 0 | 269.3781 | 0 | 1233.4209 | 96.78% | 4.0136 | 0 | 50 | 100% | 44.6
6445 | 933 | 816 | 82 | 6.8506 | 27.2 | 469.5951 | 0 | 307.2524 | 0 | 105.5 | 30.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.4209 | 96.78% | 0 | 0 | 50 | 100% | 44.5
6446 | 903 | 747 | 85 | 6.0446 | 27.9 | 454.4956 | 0 | 292.0439 | 0 | 105.6 | 30.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.4209 | 96.78% | 0 | 0 | 50 | 100% | 44.4
6447 | 859 | 623 | 83 | 7.455 | 28.1 | 432.3496 | 0 | 264.9655 | 0 | 97.6638 | 27.0319 | 0 | 70.6319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.4209 | 96.78% | 0 | 0 | 50 | 100% | 43.6
6448 | 770 | 447 | 76 | 7.6565 | 27.9 | 387.5544 | 0 | 215.369 | 0 | 60.7132 | 8.7066 | 0 | 52.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.4209 | 96.78% | 0 | 0 | 50 | 100% | 43.3
6449 | 600 | 244 | 61 | 7.6565 | 26.9 | 301.9904 | 0 | 136.5454 | 0 | 27.0382 | 0 | 0 | 27.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.4209 | 96.78% | 0 | 18.9618 | 30.3119 | 60.62% | 46
6450 | 225 | 58 | 27 | 7.455 | 24.6 | 113.2464 | 0 | 0 | 0 | 3.6446 | 0 | 0 | 3.6446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.4209 | 96.78% | 0 | 25 | 4.3532 | 8.706% | 28.6446
6451 | 0 | 0 | 0 | 6.2461 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8419 | 36.9065 | 0 | 93.8419 | 1143.3041 | 89.71% | 0 | 4.1935 | 0 | 0% | 41.1
6452 | 0 | 0 | 0 | 4.6342 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3201 | 37.6 | 0 | 95.3201 | 1051.2137 | 82.48% | 0 | 0 | 0 | 0% | 37.6
6453 | 0 | 0 | 0 | 4.0297 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0968 | 35.9 | 0 | 91.0968 | 963.9015 | 75.63% | 0 | 0 | 0 | 0% | 35.9
6454 | 0 | 0 | 0 | 2.8208 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1925 | 34.3 | 0 | 87.1925 | 881.1243 | 69.13% | 0 | 0 | 0 | 0% | 34.3
6455 | 0 | 0 | 0 | 2.6193 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.037 | 33 | 0 | 84.037 | 802.0766 | 62.93% | 0 | 0 | 0 | 0% | 33
6456 | 0 | 0 | 0 | 1.8134 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8225 | 32.5 | 0 | 82.8225 | 724.4413 | 56.84% | 0 | 0 | 0 | 0% | 32.5
6457 | 0 | 0 | 0 | 0.20149 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7614 | 32.1 | 0 | 81.7614 | 647.9274 | 50.84% | 0 | 0 | 0 | 0% | 32.1
6458 | 0 | 0 | 0 | 0.40297 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8033 | 32.6 | 0 | 82.8033 | 569.9825 | 44.72% | 0 | 0 | 0 | 0% | 32.6
6459 | 0 | 0 | 0 | 1.6119 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5242 | 35.4 | 0 | 89.5242 | 483.9847 | 37.97% | 0 | 0 | 0 | 0% | 35.4
6460 | 0 | 0 | 0 | 1.0074 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0267 | 39.8 | 0 | 100.0267 | 385.4639 | 30.24% | 0 | 0 | 0 | 0% | 39.8
6461 | 0 | 0 | 0 | 0.80595 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0673 | 41.5 | 0 | 104.0673 | 282.1081 | 22.13% | 0 | 0 | 0 | 0% | 41.5
6462 | 0 | 0 | 0 | 1.0074 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.162 | 28.9974 | 0 | 74.162 | 213.6144 | 16.76% | 0 | 0 | 0 | 0% | 28.9974
6463 | 254 | 59 | 26 | 3.0223 | 17.7 | 127.8426 | 0 | 0 | 0 | 3.6323 | 0 | 0 | 3.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.6144 | 16.76% | 0 | 0 | 0 | 0% | 3.6323
6464 | 633 | 247 | 59 | 1.2089 | 22 | 318.5999 | 157.2843 | 0 | 129.4583 | 27.5948 | 0 | 0 | 27.5948 | 0 | 0 | 0 | 0 | 0 | 129.4583 | 0 | 336.3666 | 26.39% | 0 | 0 | 0 | 0% | 27.5948
6465 | 799 | 450 | 71 | 1.8134 | 24.7 | 402.1506 | 232.9561 | 0 | 200.1129 | 57.8139 | 0 | 5.857 | 51.957 | 0 | 0 | 0 | 0 | 0 | 200.1129 | 0 | 526.1134 | 41.28% | 4.4923 | 0 | 4.6657 | 9.331% | 46.1
6466 | 881 | 623 | 75 | 2.8208 | 26.1 | 443.4226 | 277.2925 | 0 | 241.0888 | 92.8743 | 0 | 23.1372 | 69.7372 | 0 | 0 | 0 | 0 | 0 | 241.0888 | 0 | 754.7136 | 59.22% | 17.7462 | 0 | 23.0971 | 46.19% | 46.6
6467 | 922 | 747 | 78 | 3.0223 | 27.1 | 464.0586 | 300.8905 | 0 | 263.203 | 104.7 | 4.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 263.203 | 0 | 1004.2823 | 78.8% | 19.175 | 0 | 43.0125 | 86.03% | 45.3
6468 | 939 | 812 | 79 | 3.8283 | 28.2 | 472.615 | 310.0982 | 0 | 271.5071 | 105.7 | 21.9286 | 8.7714 | 75 | 0 | 0 | 0 | 0 | 0 | 271.5071 | 0 | 1261.725 | 99% | 6.7277 | 0 | 50 | 100% | 44.3
6469 | 928 | 809 | 84 | 5.4401 | 28.9 | 467.0785 | 0 | 305.5523 | 0 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.725 | 99% | 0 | 0 | 50 | 100% | 43.9
6470 | 906 | 743 | 84 | 7.052 | 29.5 | 456.0056 | 0 | 292.9793 | 0 | 106.4 | 31.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.725 | 99% | 0 | 0 | 50 | 100% | 43.6
6471 | 865 | 619 | 80 | 7.858 | 29.7 | 435.3695 | 0 | 266.7304 | 0 | 98.1932 | 27.7466 | 0 | 70.4466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.725 | 99% | 0 | 0 | 50 | 100% | 42.7
6472 | 774 | 443 | 74 | 7.858 | 29 | 389.5677 | 0 | 216.2574 | 0 | 61.2314 | 9.4157 | 0 | 51.8157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.725 | 99% | 0 | 0 | 50 | 100% | 42.4
6473 | 605 | 241 | 59 | 6.4476 | 28 | 304.507 | 0 | 137.1159 | 0 | 26.7906 | 0 | 0 | 26.7906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.725 | 99% | 0 | 17.5094 | 31.8173 | 63.63% | 44.3
6474 | 235 | 56 | 26 | 7.052 | 24.7 | 118.2796 | 0 | 0 | 0 | 3.6933 | 0 | 0 | 3.6933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.725 | 99% | 0 | 25 | 5.8549 | 11.71% | 28.6933
6475 | 0 | 0 | 0 | 3.6268 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4208 | 33.8611 | 0 | 86.4208 | 1180.1364 | 92.6% | 0 | 5.6389 | 0 | 0% | 39.5
6476 | 0 | 0 | 0 | 1.4104 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9369 | 36.6 | 0 | 92.9369 | 1090.8605 | 85.59% | 0 | 0 | 0 | 0% | 36.6
6477 | 0 | 0 | 0 | 1.6119 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2796 | 35.1 | 0 | 89.2796 | 1005.7685 | 78.91% | 0 | 0 | 0 | 0% | 35.1
6478 | 0 | 0 | 0 | 2.4178 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1278 | 33.4 | 0 | 85.1278 | 925.5776 | 72.62% | 0 | 0 | 0 | 0% | 33.4
6479 | 0 | 0 | 0 | 1.8134 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6438 | 32 | 0 | 81.6438 | 849.2906 | 66.64% | 0 | 0 | 0 | 0% | 32
6480 | 0 | 0 | 0 | 0.40297 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6435 | 31.2 | 0 | 79.6435 | 775.2053 | 60.82% | 0 | 0 | 0 | 0% | 31.2
6481 | 0 | 0 | 0 | 2.8208 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1125 | 30.6 | 0 | 78.1125 | 702.7839 | 55.14% | 0 | 0 | 0 | 0% | 30.6
6482 | 0 | 0 | 0 | 2.2164 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4149 | 30.3 | 0 | 77.4149 | 631.1215 | 49.52% | 0 | 0 | 0 | 0% | 30.3
6483 | 0 | 0 | 0 | 2.6193 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8404 | 30.9 | 0 | 78.8404 | 557.8748 | 43.77% | 0 | 0 | 0 | 0% | 30.9
6484 | 0 | 0 | 0 | 4.0297 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.486 | 32.4 | 0 | 82.486 | 480.4632 | 37.7% | 0 | 0 | 0 | 0% | 32.4
6485 | 0 | 0 | 0 | 2.0149 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3943 | 33.6 | 0 | 85.3943 | 399.6038 | 31.35% | 0 | 0 | 0 | 0% | 33.6
6486 | 0 | 0 | 0 | 2.4178 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2734 | 36.5 | 0 | 92.2734 | 310.4596 | 24.36% | 0 | 0 | 0 | 0% | 36.5
6487 | 281 | 58 | 23 | 2.2164 | 19.2 | 141.4322 | 0 | 0 | 0 | 3.5268 | 0 | 0 | 3.5268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.4596 | 24.36% | 0 | 0 | 0 | 0% | 3.5268
6488 | 655 | 245 | 53 | 2.2164 | 22.8 | 329.6729 | 161.924 | 0 | 133.4454 | 27.9208 | 0 | 0 | 27.9208 | 0 | 0 | 0 | 0 | 0 | 133.4454 | 0 | 435.6957 | 34.19% | 0 | 0 | 0 | 0% | 27.9208
6489 | 803 | 446 | 68 | 3.0223 | 24.8 | 404.1639 | 233.5623 | 0 | 200.284 | 64.8905 | 0 | 12.4452 | 52.4452 | 0 | 0 | 0 | 0 | 0 | 200.284 | 0 | 623.6587 | 48.93% | 9.5455 | 0 | 9.9155 | 19.83% | 40
6490 | 875 | 617 | 76 | 2.2164 | 27 | 440.4027 | 275.1323 | 0 | 239.2594 | 97.3516 | 3.4758 | 25 | 68.8758 | 0 | 0 | 0 | 0 | 0 | 239.2594 | 0 | 848.1993 | 66.55% | 19.175 | 0 | 29.8338 | 59.67% | 40.4
6491 | 909 | 738 | 81 | 3.2238 | 28.3 | 457.5155 | 296.5534 | 0 | 259.1276 | 110.4 | 10.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 259.1276 | 0 | 1091.3859 | 85.63% | 19.175 | 0 | 49.7521 | 99.5% | 39.6
6492 | 918 | 800 | 86 | 7.455 | 28.9 | 462.0454 | 303.0702 | 0 | 263.1524 | 112 | 37 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 263.1524 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7521 | 99.5% | 38
6493 | 906 | 796 | 91 | 7.6565 | 28.9 | 456.0056 | 0 | 298.2558 | 0 | 113.1 | 38.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7521 | 99.5% | 36.9
6494 | 875 | 730 | 96 | 7.2535 | 29.2 | 440.4027 | 0 | 282.7813 | 0 | 113.5 | 38.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7521 | 99.5% | 36.5
6495 | 818 | 604 | 97 | 9.2684 | 29 | 411.7136 | 0 | 252.1548 | 0 | 103.2368 | 33.5184 | 0 | 69.7184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7521 | 99.5% | 36.2
6496 | 733 | 432 | 85 | 8.6639 | 28.4 | 368.9316 | 0 | 204.58 | 0 | 64.9974 | 14.2987 | 0 | 50.6987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7521 | 99.5% | 36.4
6497 | 561 | 232 | 65 | 9.4699 | 27.2 | 282.3611 | 0 | 126.6117 | 0 | 25.9421 | 0 | 0 | 25.9421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 12.9579 | 36.2939 | 72.59% | 38.9
6498 | 185 | 51 | 27 | 8.261 | 25 | 93.1137 | 0 | 0 | 0 | 3.33 | 0 | 0 | 3.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.328 | 20.66% | 28.33
6499 | 0 | 0 | 0 | 7.6565 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.33 | 26.4556 | 0 | 69.33 | 1210.8075 | 95% | 0 | 9.9444 | 0 | 0% | 36.4
6500 | 0 | 0 | 0 | 6.8506 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1441 | 34.2 | 0 | 87.1441 | 1128.3168 | 88.53% | 0 | 0 | 0 | 0% | 34.2
6501 | 0 | 0 | 0 | 5.6416 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7403 | 32 | 0 | 81.7403 | 1051.9465 | 82.54% | 0 | 0 | 0 | 0% | 32
6502 | 0 | 0 | 0 | 2.2164 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3241 | 30.2 | 0 | 77.3241 | 980.4388 | 76.93% | 0 | 0 | 0 | 0% | 30.2
6503 | 0 | 0 | 0 | 3.0223 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1 | 28.8 | 0 | 74.1 | 912.0966 | 71.56% | 0 | 0 | 0 | 0% | 28.8
6504 | 0 | 0 | 0 | 1.8134 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0718 | 27.9 | 0 | 72.0718 | 845.6994 | 66.35% | 0 | 0 | 0 | 0% | 27.9
6505 | 0 | 0 | 0 | 2.6193 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8262 | 27.4 | 0 | 70.8262 | 780.4858 | 61.24% | 0 | 0 | 0 | 0% | 27.4
6506 | 0 | 0 | 0 | 1.6119 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8262 | 27.4 | 0 | 70.8262 | 715.2625 | 56.12% | 0 | 0 | 0 | 0% | 27.4
6507 | 0 | 0 | 0 | 2.8208 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.929 | 27.9 | 0 | 71.929 | 648.9671 | 50.92% | 0 | 0 | 0 | 0% | 27.9
6508 | 0 | 0 | 0 | 1.0074 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8937 | 28.4 | 0 | 72.8937 | 581.7247 | 45.64% | 0 | 0 | 0 | 0% | 28.4
6509 | 0 | 0 | 0 | 1.8134 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7926 | 28.8 | 0 | 73.7926 | 513.6029 | 40.3% | 0 | 0 | 0 | 0% | 28.8
6510 | 0 | 0 | 0 | 2.6193 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0721 | 31.1 | 0 | 79.0721 | 439.8181 | 34.51% | 0 | 0 | 0 | 0% | 31.1
6511 | 189 | 54 | 29 | 3.6268 | 17.6 | 95.127 | 0 | 0 | 0 | 3.455 | 0 | 0 | 3.455 | 0 | 0 | 0 | 76.1475 | 29.845 | 0 | 76.1475 | 369.391 | 28.98% | 0 | 0 | 0 | 0% | 33.3
6512 | 530 | 237 | 81 | 2.4178 | 20.4 | 266.7582 | 130.3547 | 0 | 103.8019 | 26.5607 | 0 | 0 | 26.5607 | 0 | 0 | 0 | 0 | 0 | 103.8019 | 0 | 465.281 | 36.51% | 0 | 0 | 0 | 0% | 26.5607
6513 | 688 | 435 | 111 | 2.4178 | 24 | 346.2824 | 199.6343 | 0 | 168.7109 | 64.9842 | 0 | 14.7421 | 50.2421 | 0 | 0 | 0 | 0 | 0 | 168.7109 | 0 | 621.1324 | 48.73% | 11.3072 | 0 | 11.7472 | 23.49% | 35.5
6514 | 775 | 608 | 129 | 5.4401 | 24.6 | 390.071 | 243.4492 | 0 | 208.4893 | 103.404 | 8.502 | 25 | 69.902 | 0 | 0 | 0 | 0 | 0 | 208.4893 | 0 | 813.7303 | 63.85% | 19.175 | 0 | 31.6684 | 63.34% | 36.4
6515 | 831 | 732 | 132 | 5.2387 | 25.5 | 418.2567 | 271.0204 | 0 | 234.3125 | 113.5 | 15.4949 | 23.0051 | 75 | 0 | 0 | 0 | 0 | 0 | 234.3125 | 0 | 1030.1831 | 80.83% | 17.6449 | 0 | 50 | 100% | 36.5
6516 | 873 | 800 | 122 | 4.0297 | 27.3 | 439.3961 | 288.1255 | 0 | 250.945 | 114.9 | 39.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 250.945 | 0 | 1262.0006 | 99.02% | 0 | 0 | 50 | 100% | 35.1
6517 | 885 | 799 | 113 | 4.4327 | 28.2 | 445.4359 | 0 | 291.2904 | 0 | 115.7 | 40.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.0006 | 99.02% | 0 | 0 | 50 | 100% | 34.3
6518 | 860 | 730 | 110 | 4.4327 | 29.6 | 432.853 | 0 | 277.7611 | 0 | 116 | 41 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.0006 | 99.02% | 0 | 0 | 50 | 100% | 34
6519 | 794 | 600 | 110 | 5.0372 | 30 | 399.634 | 0 | 244.6747 | 0 | 101.4237 | 33.6619 | 0 | 67.7619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.0006 | 99.02% | 0 | 0 | 50 | 100% | 34.1
6520 | 705 | 428 | 97 | 6.4476 | 29.6 | 354.8388 | 0 | 196.5484 | 0 | 64.845 | 15.0225 | 0 | 49.8225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.0006 | 99.02% | 0 | 0 | 50 | 100% | 34.8
6521 | 554 | 233 | 70 | 7.6565 | 27.5 | 278.8378 | 0 | 124.5002 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.0006 | 99.02% | 0 | 12.3 | 37.2232 | 74.45% | 38.3
6522 | 175 | 48 | 27 | 7.2535 | 25.8 | 88.0805 | 0 | 0 | 0 | 3.1516 | 0 | 0 | 3.1516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.0006 | 99.02% | 0 | 25 | 11.2535 | 22.51% | 28.1516
6523 | 0 | 0 | 0 | 5.8431 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.005 | 25.8659 | 0 | 68.005 | 1199.5498 | 94.12% | 0 | 10.8341 | 0 | 0% | 36.7
6524 | 0 | 0 | 0 | 2.0149 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1744 | 34.2 | 0 | 87.1744 | 1117.0366 | 87.64% | 0 | 0 | 0 | 0% | 34.2
6525 | 0 | 0 | 0 | 1.6119 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7862 | 32 | 0 | 81.7862 | 1040.6029 | 81.65% | 0 | 0 | 0 | 0% | 32
6526 | 0 | 0 | 0 | 0.80595 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8486 | 30.4 | 0 | 77.8486 | 968.5081 | 75.99% | 0 | 0 | 0 | 0% | 30.4
6527 | 0 | 0 | 0 | 1.4104 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1925 | 29.3 | 0 | 75.1925 | 899.0913 | 70.54% | 0 | 0 | 0 | 0% | 29.3
6528 | 0 | 0 | 0 | 1.4104 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9859 | 28.8 | 0 | 73.9859 | 830.8267 | 65.19% | 0 | 0 | 0 | 0% | 28.8
6529 | 0 | 0 | 0 | 1.2089 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2069 | 28.9 | 0 | 74.2069 | 762.3389 | 59.81% | 0 | 0 | 0 | 0% | 28.9
6530 | 0 | 0 | 0 | 1.6119 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.11 | 29.8 | 0 | 76.11 | 691.9956 | 54.3% | 0 | 0 | 0 | 0% | 29.8
6531 | 0 | 0 | 0 | 1.0074 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6262 | 33.4 | 0 | 84.6262 | 611.7095 | 48% | 0 | 0 | 0 | 0% | 33.4
6532 | 0 | 0 | 0 | 3.4253 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7829 | 38.4 | 0 | 96.7829 | 517.1726 | 40.58% | 0 | 0 | 0 | 0% | 38.4
6533 | 0 | 0 | 0 | 2.8208 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4618 | 40.4 | 0 | 101.4618 | 416.8791 | 32.71% | 0 | 0 | 0 | 0% | 40.4
6534 | 0 | 0 | 0 | 1.6119 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2818 | 42.1 | 0 | 105.2818 | 311.7476 | 24.46% | 0 | 0 | 0 | 0% | 42.1
6535 | 286 | 57 | 22 | 1.8134 | 17.5 | 143.9488 | 0 | 0 | 0 | 3.639 | 0 | 0 | 3.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311.7476 | 24.46% | 0 | 0 | 0 | 0% | 3.639
6536 | 692 | 250 | 52 | 1.2089 | 22.4 | 348.2956 | 169.3293 | 0 | 140.7499 | 29.2133 | 0 | 0 | 29.2133 | 0 | 0 | 0 | 0 | 0 | 140.7499 | 0 | 443.8405 | 34.82% | 0 | 0 | 0 | 0% | 29.2133
6537 | 839 | 455 | 67 | 1.8134 | 25.1 | 422.2833 | 242.8668 | 0 | 209.2842 | 61.9663 | 0 | 8.3331 | 53.6331 | 0 | 0 | 0 | 0 | 0 | 209.2842 | 0 | 640.2523 | 50.24% | 6.3915 | 0 | 6.6412 | 13.28% | 45.3
6538 | 906 | 627 | 76 | 4.6342 | 25 | 456.0056 | 284.3215 | 0 | 247.1137 | 100.2074 | 2.2037 | 25 | 73.0037 | 0 | 0 | 0 | 0 | 0 | 247.1137 | 0 | 872.1669 | 68.43% | 19.175 | 0 | 26.5653 | 53.13% | 45.8
6539 | 928 | 746 | 85 | 4.0297 | 26 | 467.0785 | 302.5598 | 0 | 264.4107 | 105.3 | 5.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 264.4107 | 0 | 1120.3146 | 87.9% | 19.175 | 0 | 46.4895 | 92.98% | 44.7
6540 | 937 | 808 | 89 | 3.6268 | 28.5 | 471.6084 | 309.1534 | 0 | 270.696 | 106 | 26.5951 | 4.4049 | 75 | 0 | 0 | 0 | 0 | 0 | 270.696 | 0 | 1274.5104 | 100% | 3.3785 | 0 | 50 | 100% | 44
6541 | 927 | 804 | 92 | 4.6342 | 29.4 | 466.5752 | 0 | 305.0591 | 0 | 106 | 31 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44
6542 | 910 | 746 | 96 | 5.8431 | 30.3 | 458.0188 | 0 | 293.7252 | 0 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.9
6543 | 784 | 591 | 112 | 6.6491 | 30.2 | 394.6008 | 0 | 241.5107 | 0 | 92.3216 | 24.6108 | 0 | 67.7108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.1
6544 | 766 | 442 | 88 | 8.261 | 29.3 | 385.5411 | 0 | 213.3153 | 0 | 62.0562 | 9.5781 | 0 | 52.4781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.9
6545 | 429 | 206 | 76 | 7.858 | 26.5 | 215.9232 | 0 | 95.9926 | 0 | 21.9164 | 0 | 0 | 21.9164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.6836 | 25.3948 | 50.79% | 45.6
6546 | 48 | 39 | 33 | 5.0372 | 23.1 | 24.1592 | 0 | 0 | 0 | 2.377 | 0 | 0 | 2.377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.4437 | 0 | 0% | 26.8207
6547 | 0 | 0 | 0 | 3.0223 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1115 | 40 | 0 | 101.1115 | 1175.5136 | 92.23% | 0 | 0 | 0 | 0% | 40
6548 | 0 | 0 | 0 | 1.4104 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5497 | 36.5 | 0 | 92.5497 | 1086.4959 | 85.25% | 0 | 0 | 0 | 0% | 36.5
6549 | 0 | 0 | 0 | 2.8208 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.436 | 34.8 | 0 | 88.436 | 1002.244 | 78.64% | 0 | 0 | 0 | 0% | 34.8
6550 | 0 | 0 | 0 | 4.0297 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1783 | 33 | 0 | 84.1783 | 923.1209 | 72.43% | 0 | 0 | 0 | 0% | 33
6551 | 0 | 0 | 0 | 3.2238 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7289 | 32 | 0 | 81.7289 | 846.735 | 66.44% | 0 | 0 | 0 | 0% | 32
6552 | 0 | 0 | 0 | 2.4178 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3971 | 31.5 | 0 | 80.3971 | 771.8001 | 60.56% | 0 | 0 | 0 | 0% | 31.5
6553 | 0 | 0 | 0 | 1.2089 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9881 | 31.4 | 0 | 79.9881 | 697.2306 | 54.71% | 0 | 0 | 0 | 0% | 31.4
6554 | 0 | 0 | 0 | 0.40297 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5333 | 32.1 | 0 | 81.5333 | 620.6768 | 48.7% | 0 | 0 | 0 | 0% | 32.1
6555 | 0 | 0 | 0 | 1.8134 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0251 | 35.2 | 0 | 89.0251 | 535.2067 | 41.99% | 0 | 0 | 0 | 0% | 35.2
6556 | 0 | 0 | 0 | 2.2164 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4936 | 40 | 0 | 100.4936 | 436.0724 | 34.21% | 0 | 0 | 0 | 0% | 40
6557 | 0 | 0 | 0 | 0.80595 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3645 | 42.1 | 0 | 105.3645 | 330.9785 | 25.97% | 0 | 0 | 0 | 0% | 42.1
6558 | 0 | 0 | 0 | 0.60446 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7189 | 43.5 | 0 | 108.7189 | 221.8493 | 17.41% | 0 | 0 | 0 | 0% | 43.5
6559 | 36 | 37 | 34 | 3.2238 | 18.7 | 18.1194 | 0 | 0 | 0 | 2.4075 | 0 | 0 | 2.4075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8493 | 17.41% | 0 | 0 | 0 | 0% | 2.4075
6560 | 58 | 134 | 116 | 1.4104 | 19.7 | 29.1924 | 0 | 14.1196 | 0 | 11.433 | 0 | 0 | 11.433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8493 | 17.41% | 0 | 0 | 0 | 0% | 11.433
6561 | 229 | 365 | 256 | 1.8134 | 23 | 115.2597 | 66.1305 | 0 | 43.7546 | 35.7648 | 0 | 0 | 35.7648 | 0 | 0 | 0 | 0 | 0 | 43.7546 | 0 | 263.4686 | 20.67% | 0 | 0 | 0 | 0% | 35.7648
6562 | 375 | 604 | 361 | 2.0149 | 26.1 | 188.744 | 117.5682 | 0 | 92.2333 | 71.4196 | 0 | 12.4598 | 58.9598 | 0 | 0 | 0 | 0 | 0 | 92.2333 | 0 | 351.2008 | 27.56% | 9.5566 | 0 | 9.9315 | 19.86% | 46.5
6563 | 859 | 860 | 246 | 4.4327 | 27.5 | 432.3496 | 279.9751 | 0 | 243.1033 | 104.5 | 4.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 243.1033 | 0 | 582.4406 | 45.7% | 19.175 | 0 | 29.8585 | 59.72% | 45.5
6564 | 914 | 804 | 106 | 4.2312 | 26.8 | 460.0321 | 301.4725 | 0 | 263.3447 | 105.4 | 5.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 263.3447 | 0 | 832.9339 | 65.35% | 19.175 | 0 | 49.7856 | 99.57% | 44.6
6565 | 919 | 797 | 96 | 4.6342 | 28.1 | 462.5487 | 302.3712 | 0 | 264.0635 | 105.4 | 30.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 264.0635 | 0 | 1084.111 | 85.06% | 0 | 0 | 49.7856 | 99.57% | 44.6
6566 | 896 | 730 | 95 | 4.4327 | 29.5 | 450.9724 | 289.0221 | 0 | 251.6919 | 105.3 | 30.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 251.6919 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7856 | 99.57% | 44.7
6567 | 838 | 600 | 93 | 5.6416 | 30.1 | 421.78 | 0 | 258.0556 | 0 | 94.8351 | 25.4676 | 0 | 69.3676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7856 | 99.57% | 43.9
6568 | 372 | 309 | 126 | 5.0372 | 29 | 187.2341 | 0 | 103.4762 | 0 | 33.2682 | 0 | 0 | 33.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 10.3318 | 39.0502 | 78.1% | 43.6
6569 | 73 | 146 | 125 | 3.2238 | 28.6 | 36.7422 | 0 | 16.2627 | 0 | 12.4499 | 0 | 0 | 12.4499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 13.0731 | 26.15% | 37.4499
6570 | 10 | 22 | 22 | 7.2535 | 28.7 | 5.0332 | 0 | 0 | 0 | 1.052 | 0 | 0 | 1.052 | 0 | 0 | 0 | 81.9602 | 31.4662 | 0 | 81.9602 | 1198.2177 | 94.01% | 0 | 12.5819 | 0 | 0% | 45.1
6571 | 0 | 0 | 0 | 6.2461 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6612 | 40.9 | 0 | 104.6612 | 1096.3237 | 86.02% | 0 | 0 | 0 | 0% | 40.9
6572 | 0 | 0 | 0 | 4.6342 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0397 | 37.5 | 0 | 96.0397 | 1004.0787 | 78.78% | 0 | 0 | 0 | 0% | 37.5
6573 | 0 | 0 | 0 | 3.8283 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.062 | 35.6 | 0 | 91.062 | 917.2982 | 71.97% | 0 | 0 | 0 | 0% | 35.6
6574 | 0 | 0 | 0 | 7.052 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9413 | 33.9 | 0 | 86.9413 | 835.1734 | 65.53% | 0 | 0 | 0 | 0% | 33.9
6575 | 0 | 0 | 0 | 6.2461 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8173 | 32.7 | 0 | 83.8173 | 756.541 | 59.36% | 0 | 0 | 0 | 0% | 32.7
6576 | 0 | 0 | 0 | 5.8431 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7207 | 31.9 | 0 | 81.7207 | 680.219 | 53.37% | 0 | 0 | 0 | 0% | 31.9
6577 | 0 | 0 | 0 | 3.0223 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0372 | 31.7 | 0 | 81.0372 | 604.6107 | 47.44% | 0 | 0 | 0 | 0% | 31.7
6578 | 0 | 0 | 0 | 4.2312 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2281 | 32.3 | 0 | 82.2281 | 527.512 | 41.39% | 0 | 0 | 0 | 0% | 32.3
6579 | 0 | 0 | 0 | 5.4401 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5142 | 35.3 | 0 | 89.5142 | 441.7859 | 34.66% | 0 | 0 | 0 | 0% | 35.3
6580 | 0 | 0 | 0 | 5.2387 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.9586 | 39.7 | 0 | 99.9586 | 343.5448 | 26.96% | 0 | 0 | 0 | 0% | 39.7
6581 | 0 | 0 | 0 | 3.8283 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9009 | 41.8 | 0 | 104.9009 | 239.3252 | 18.78% | 0 | 0 | 0 | 0% | 41.8
6582 | 0 | 0 | 0 | 4.4327 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3252 | 18.78% | 0 | 0 | 0 | 0% | 0
6583 | 217 | 64 | 41 | 5.2387 | 18.6 | 109.2199 | 0 | 0 | 0 | 4.5506 | 0 | 0 | 4.5506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3252 | 18.78% | 0 | 0 | 0 | 0% | 4.5506
6584 | 305 | 191 | 98 | 3.0223 | 19.6 | 153.5118 | 73.8689 | 0 | 50.3584 | 20.2721 | 0 | 0 | 20.2721 | 0 | 0 | 0 | 0 | 0 | 50.3584 | 0 | 287.1263 | 22.53% | 0 | 0 | 0 | 0% | 20.2721
6585 | 614 | 426 | 143 | 1.6119 | 23.7 | 309.0369 | 176.8869 | 0 | 147.7623 | 51.4879 | 0 | 2.944 | 48.544 | 0 | 0 | 0 | 0 | 0 | 147.7623 | 0 | 427.3849 | 33.53% | 2.258 | 0 | 2.3469 | 4.694% | 45.6
6586 | 794 | 598 | 117 | 2.4178 | 25.1 | 399.634 | 248.6902 | 0 | 214.4747 | 91.1647 | 0 | 22.6824 | 68.4824 | 0 | 0 | 0 | 0 | 0 | 214.4747 | 0 | 630.9681 | 49.51% | 17.3974 | 0 | 20.4292 | 40.86% | 45.8
6587 | 949 | 744 | 76 | 2.2164 | 27.7 | 477.6482 | 309.2118 | 0 | 271.2019 | 105.4 | 5.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 271.2019 | 0 | 888.3977 | 69.71% | 19.175 | 0 | 40.3592 | 80.72% | 44.6
6588 | 955 | 805 | 81 | 3.0223 | 29.1 | 480.6681 | 314.8996 | 0 | 276.2493 | 106.2 | 19.1067 | 12.0933 | 75 | 0 | 0 | 0 | 0 | 0 | 276.2493 | 0 | 1150.6183 | 90.28% | 9.2756 | 0 | 50 | 100% | 43.8
6589 | 943 | 798 | 83 | 3.2238 | 29.8 | 474.6283 | 310.2105 | 0 | 271.8213 | 106.5 | 31.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 271.8213 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.5
6590 | 888 | 717 | 93 | 6.0446 | 29.9 | 446.9458 | 0 | 286.2569 | 0 | 106.7 | 31.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.3
6591 | 854 | 596 | 86 | 8.0595 | 29.4 | 429.833 | 0 | 262.8893 | 0 | 97.7924 | 27.6462 | 0 | 70.1462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
6592 | 703 | 409 | 86 | 8.6639 | 28.4 | 353.8321 | 0 | 195.3132 | 0 | 55.8841 | 6.842 | 0 | 49.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.2
6593 | 146 | 129 | 82 | 7.052 | 26.1 | 73.4843 | 0 | 32.3803 | 0 | 12.0615 | 0 | 0 | 12.0615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.0196 | 48.04% | 37.0615
6594 | 11 | 19 | 17 | 3.6268 | 23.9 | 5.5365 | 0 | 0 | 0 | 0.72706 | 0 | 0 | 0.72706 | 0 | 0 | 0 | 55.2411 | 20.2597 | 0 | 55.2411 | 1224.3694 | 96.07% | 0 | 23.1133 | 0 | 0% | 44.1
6595 | 0 | 0 | 0 | 8.261 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9514 | 39.9 | 0 | 100.9514 | 1125.6992 | 88.32% | 0 | 0 | 0 | 0% | 39.9
6596 | 0 | 0 | 0 | 8.261 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9125 | 36.6 | 0 | 92.9125 | 1036.4329 | 81.32% | 0 | 0 | 0 | 0% | 36.6
6597 | 0 | 0 | 0 | 3.6268 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6398 | 34.9 | 0 | 88.6398 | 951.9197 | 74.69% | 0 | 0 | 0 | 0% | 34.9
6598 | 0 | 0 | 0 | 2.6193 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7346 | 33.3 | 0 | 84.7346 | 872.0235 | 68.42% | 0 | 0 | 0 | 0% | 33.3
6599 | 0 | 0 | 0 | 4.0297 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2774 | 32.3 | 0 | 82.2774 | 794.9653 | 62.37% | 0 | 0 | 0 | 0% | 32.3
6600 | 0 | 0 | 0 | 3.8283 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7297 | 31.7 | 0 | 80.7297 | 719.5899 | 56.46% | 0 | 0 | 0 | 0% | 31.7
6601 | 0 | 0 | 0 | 4.4327 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.23 | 31.5 | 0 | 80.23 | 644.7647 | 50.59% | 0 | 0 | 0 | 0% | 31.5
6602 | 0 | 0 | 0 | 3.4253 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4059 | 32 | 0 | 81.4059 | 568.5187 | 44.61% | 0 | 0 | 0 | 0% | 32
6603 | 0 | 0 | 0 | 3.4253 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9775 | 34.8 | 0 | 87.9775 | 484.2173 | 37.99% | 0 | 0 | 0 | 0% | 34.8
6604 | 0 | 0 | 0 | 2.6193 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3442 | 39.2 | 0 | 98.3442 | 387.427 | 30.4% | 0 | 0 | 0 | 0% | 39.2
6605 | 0 | 0 | 0 | 1.4104 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0615 | 41.2 | 0 | 103.0615 | 284.9183 | 22.36% | 0 | 0 | 0 | 0% | 41.2
6606 | 0 | 0 | 0 | 2.2164 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8862 | 42.4 | 0 | 105.8862 | 178.9677 | 14.04% | 0 | 0 | 0 | 0% | 42.4
6607 | 153 | 39 | 18 | 2.4178 | 15.5 | 77.0076 | 0 | 0 | 0 | 2.5767 | 0 | 0 | 2.5767 | 0 | 0 | 0 | 59.1415 | 22.4072 | 0 | 59.1415 | 124.9167 | 9.801% | 0 | 0 | 0 | 0% | 24.9839
6608 | 662 | 237 | 54 | 1.6119 | 19.5 | 333.1961 | 159.5082 | 0 | 131.3813 | 29.0427 | 0 | 0 | 29.0427 | 0 | 0 | 0 | 0 | 0 | 131.3813 | 0 | 249.2988 | 19.56% | 0 | 0 | 0 | 0% | 29.0427
6609 | 818 | 438 | 68 | 2.6193 | 23.2 | 411.7136 | 235.0949 | 0 | 201.8343 | 63.3083 | 0 | 9.4042 | 53.9042 | 0 | 0 | 0 | 0 | 0 | 201.8343 | 0 | 440.3807 | 34.55% | 7.213 | 0 | 7.4981 | 15% | 44.5
6610 | 884 | 608 | 80 | 7.2535 | 25 | 444.9326 | 276.6131 | 0 | 238.3551 | 101.5136 | 3.4568 | 25 | 73.0568 | 0 | 0 | 0 | 0 | 0 | 238.3551 | 0 | 666.0377 | 52.26% | 19.175 | 0 | 27.4309 | 54.86% | 44.6
6611 | 914 | 735 | 94 | 6.8506 | 26.3 | 460.0321 | 297.7148 | 0 | 258.4999 | 106.5 | 6.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 258.4999 | 0 | 910.7664 | 71.46% | 19.175 | 0 | 47.3638 | 94.73% | 43.5
6612 | 826 | 772 | 147 | 6.8506 | 27.2 | 415.7402 | 272.2804 | 0 | 234.5596 | 107.1 | 28.7937 | 3.3063 | 75 | 0 | 0 | 0 | 0 | 0 | 234.5596 | 0 | 1132.8302 | 88.88% | 2.5359 | 0 | 50 | 100% | 42.9
6613 | 909 | 790 | 105 | 10.2758 | 27.3 | 457.5155 | 243.5446 | 55.4151 | 209.8802 | 107.3 | 32.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 209.8802 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.7
6614 | 760 | 692 | 158 | 12.8952 | 26.9 | 382.5212 | 0 | 244.8348 | 0 | 107.7 | 32.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
6615 | 616 | 570 | 200 | 11.4848 | 26.7 | 310.0435 | 0 | 189.4839 | 0 | 88.2978 | 23.1989 | 0 | 65.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.9
6616 | 666 | 430 | 131 | 10.2758 | 26.4 | 335.2094 | 0 | 184.5412 | 0 | 61.0322 | 9.5661 | 0 | 51.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.9
6617 | 358 | 189 | 87 | 9.2684 | 25.5 | 180.1876 | 0 | 79.0373 | 0 | 20.4828 | 0 | 0 | 20.4828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.2172 | 24.8295 | 49.66% | 44.7
6618 | 52 | 26 | 21 | 8.8654 | 23.3 | 26.1725 | 0 | 0 | 0 | 1.4756 | 0 | 0 | 1.4756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.8891 | 0 | 0% | 25.3646
6619 | 0 | 0 | 0 | 4.6342 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7115 | 39.4 | 0 | 99.7115 | 1177.3102 | 92.37% | 0 | 0 | 0 | 0% | 39.4
6620 | 0 | 0 | 0 | 1.8134 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0338 | 36.3 | 0 | 92.0338 | 1088.9109 | 85.44% | 0 | 0 | 0 | 0% | 36.3
6621 | 0 | 0 | 0 | 2.0149 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.018 | 34.7 | 0 | 88.018 | 1005.0037 | 78.85% | 0 | 0 | 0 | 0% | 34.7
6622 | 0 | 0 | 0 | 3.2238 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1068 | 33.1 | 0 | 84.1068 | 925.7016 | 72.63% | 0 | 0 | 0 | 0% | 33.1
6623 | 0 | 0 | 0 | 3.0223 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0673 | 31.9 | 0 | 81.0673 | 849.7948 | 66.68% | 0 | 0 | 0 | 0% | 31.9
6624 | 0 | 0 | 0 | 5.2387 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2621 | 31.5 | 0 | 80.2621 | 775.0023 | 60.81% | 0 | 0 | 0 | 0% | 31.5
6625 | 0 | 0 | 0 | 2.2164 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9703 | 31.5 | 0 | 79.9703 | 700.1985 | 54.94% | 0 | 0 | 0 | 0% | 31.5
6626 | 0 | 0 | 0 | 3.2238 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.81 | 31.8 | 0 | 80.81 | 624.539 | 49% | 0 | 0 | 0 | 0% | 31.8
6627 | 0 | 0 | 0 | 2.0149 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5859 | 34.7 | 0 | 87.5859 | 540.5554 | 42.41% | 0 | 0 | 0 | 0% | 34.7
6628 | 0 | 0 | 0 | 1.6119 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7546 | 39.4 | 0 | 98.7546 | 443.2206 | 34.78% | 0 | 0 | 0 | 0% | 39.4
6629 | 0 | 0 | 0 | 2.0149 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8315 | 41.1 | 0 | 102.8315 | 341.031 | 26.76% | 0 | 0 | 0 | 0% | 41.1
6630 | 0 | 0 | 0 | 2.2164 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.2196 | 42.5 | 0 | 106.2196 | 234.8372 | 18.43% | 0 | 0 | 0 | 0% | 42.5
6631 | 256 | 55 | 26 | 1.0074 | 16.4 | 128.8493 | 0 | 0 | 0 | 3.8926 | 0 | 0 | 3.8926 | 0 | 0 | 0 | 99.6358 | 39.7074 | 0 | 99.6358 | 136.5297 | 10.71% | 0 | 0 | 0 | 0% | 43.6
6632 | 654 | 230 | 50 | 0.60446 | 20.6 | 329.1696 | 156.7706 | 0 | 129.1862 | 28.2173 | 0 | 0 | 28.2173 | 0 | 0 | 0 | 0 | 0 | 129.1862 | 0 | 259.458 | 20.36% | 0 | 0 | 0 | 0% | 28.2173
6633 | 835 | 436 | 61 | 1.4104 | 24 | 420.27 | 239.4095 | 0 | 206.2219 | 61.4784 | 0 | 8.2392 | 53.2392 | 0 | 0 | 0 | 0 | 0 | 206.2219 | 0 | 455.6903 | 35.75% | 6.3195 | 0 | 6.5702 | 13.14% | 45
6634 | 907 | 607 | 68 | 1.0074 | 27.2 | 456.5089 | 283.539 | 0 | 247.5867 | 93.7191 | 0 | 24.2095 | 69.5095 | 0 | 0 | 0 | 0 | 0 | 247.5867 | 0 | 691.2837 | 54.24% | 18.5687 | 0 | 25.8756 | 51.75% | 45.3
6635 | 946 | 731 | 72 | 4.2312 | 28.1 | 476.1382 | 307.894 | 0 | 269.3245 | 106 | 6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 269.3245 | 0 | 947.5618 | 74.35% | 19.175 | 0 | 45.8115 | 91.62% | 44
6636 | 955 | 790 | 75 | 6.6491 | 28.7 | 480.6681 | 314.7079 | 0 | 274.4481 | 107.1 | 26.8475 | 5.2525 | 75 | 0 | 0 | 0 | 0 | 0 | 274.4481 | 0 | 1208.7153 | 94.84% | 4.0287 | 0 | 50 | 100% | 42.9
6637 | 947 | 784 | 76 | 10.6788 | 29 | 476.6416 | 131.731 | 179.6514 | 113.7862 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 113.7862 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.5
6638 | 925 | 717 | 75 | 12.0892 | 28.9 | 465.5686 | 0 | 297.793 | 0 | 107.8 | 32.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.2
6639 | 877 | 590 | 73 | 11.8877 | 28.7 | 441.4093 | 0 | 269.4044 | 0 | 101.1834 | 29.8417 | 0 | 71.3417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.5
6640 | 800 | 418 | 64 | 12.2907 | 28.3 | 402.6539 | 0 | 221.0723 | 0 | 63.4975 | 11.0487 | 0 | 52.4487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.4
6641 | 629 | 216 | 48 | 10.6788 | 27.6 | 316.5866 | 0 | 138.2253 | 0 | 26.1204 | 0 | 0 | 26.1204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 17.5796 | 31.7257 | 63.45% | 43.7
6642 | 152 | 35 | 16 | 7.858 | 25.4 | 76.5042 | 0 | 0 | 0 | 2.0654 | 0 | 0 | 2.0654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 5.7367 | 11.47% | 27.0654
6643 | 0 | 0 | 0 | 6.4476 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1818 | 33.2806 | 0 | 85.1818 | 1194.3948 | 93.71% | 0 | 5.5194 | 0 | 0% | 38.8
6644 | 0 | 0 | 0 | 3.8283 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6625 | 36.1 | 0 | 91.6625 | 1106.5575 | 86.82% | 0 | 0 | 0 | 0% | 36.1
6645 | 0 | 0 | 0 | 1.0074 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3384 | 34.8 | 0 | 88.3384 | 1022.3602 | 80.22% | 0 | 0 | 0 | 0% | 34.8
6646 | 0 | 0 | 0 | 0.60446 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.401 | 32.8 | 0 | 83.401 | 943.9153 | 74.06% | 0 | 0 | 0 | 0% | 32.8
6647 | 0 | 0 | 0 | 2.2164 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8604 | 31.4 | 0 | 79.8604 | 869.4152 | 68.22% | 0 | 0 | 0 | 0% | 31.4
6648 | 0 | 0 | 0 | 1.6119 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8388 | 30.6 | 0 | 77.8388 | 797.1367 | 62.54% | 0 | 0 | 0 | 0% | 30.6
6649 | 0 | 0 | 0 | 0.60446 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0967 | 30.3 | 0 | 77.0967 | 725.6793 | 56.94% | 0 | 0 | 0 | 0% | 30.3
6650 | 0 | 0 | 0 | 1.6119 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.621 | 30.1 | 0 | 76.621 | 654.7639 | 51.37% | 0 | 0 | 0 | 0% | 30.1
6651 | 0 | 0 | 0 | 3.4253 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1518 | 30.7 | 0 | 78.1518 | 582.1733 | 45.68% | 0 | 0 | 0 | 0% | 30.7
6652 | 0 | 0 | 0 | 3.2238 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2068 | 32.4 | 0 | 82.2068 | 504.7925 | 39.61% | 0 | 0 | 0 | 0% | 32.4
6653 | 0 | 0 | 0 | 3.4253 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1566 | 33.6 | 0 | 85.1566 | 423.9662 | 33.27% | 0 | 0 | 0 | 0% | 33.6
6654 | 0 | 0 | 0 | 2.8208 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7676 | 36.4 | 0 | 91.7676 | 335.1413 | 26.3% | 0 | 0 | 0 | 0% | 36.4
6655 | 226 | 45 | 20 | 3.4253 | 16.6 | 113.7497 | 0 | 0 | 0 | 3.1098 | 0 | 0 | 3.1098 | 0 | 0 | 0 | 89.2934 | 35.3902 | 0 | 89.2934 | 249.1223 | 19.55% | 0 | 0 | 0 | 0% | 38.5
6656 | 646 | 227 | 51 | 1.6119 | 21.7 | 325.143 | 154.0567 | 0 | 126.3279 | 28.173 | 0 | 0 | 28.173 | 0 | 0 | 0 | 0 | 0 | 126.3279 | 0 | 367.6152 | 28.84% | 0 | 0 | 0 | 0% | 28.173
6657 | 804 | 426 | 66 | 1.8134 | 25 | 404.6672 | 229.9794 | 0 | 197.3057 | 65.1235 | 0 | 12.6617 | 52.4617 | 0 | 0 | 0 | 0 | 0 | 197.3057 | 0 | 552.6839 | 43.36% | 9.7115 | 0 | 10.0983 | 20.2% | 39.8
6658 | 881 | 597 | 73 | 1.6119 | 27.6 | 443.4226 | 275.1501 | 0 | 239.4769 | 97.6024 | 3.7512 | 25 | 68.8512 | 0 | 0 | 0 | 0 | 0 | 239.4769 | 0 | 777.3082 | 60.99% | 19.175 | 0 | 30.037 | 60.07% | 40.1
6659 | 916 | 717 | 79 | 3.2238 | 28.8 | 461.0387 | 297.7933 | 0 | 260.2804 | 111 | 11 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 260.2804 | 0 | 1021.4458 | 80.14% | 19.175 | 0 | 49.9758 | 99.95% | 39
6660 | 930 | 779 | 82 | 4.8357 | 29.5 | 468.0852 | 306.3765 | 0 | 267.737 | 112.7 | 37.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 267.737 | 0 | 1272.5776 | 99.85% | 0 | 0 | 49.9758 | 99.95% | 37.3
6661 | 927 | 780 | 86 | 7.2535 | 29.7 | 466.5752 | 0 | 304.7327 | 0 | 113.7 | 38.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.5776 | 99.85% | 0 | 0 | 49.9758 | 99.95% | 36.3
6662 | 855 | 698 | 104 | 4.6342 | 30.3 | 430.3364 | 0 | 275.0735 | 0 | 114.2 | 39.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.5776 | 99.85% | 0 | 0 | 49.9758 | 99.95% | 35.8
6663 | 684 | 536 | 129 | 5.8431 | 30 | 344.2691 | 0 | 209.8304 | 0 | 89.3135 | 26.9567 | 0 | 62.3567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.5776 | 99.85% | 0 | 0 | 49.9758 | 99.95% | 35.4
6664 | 432 | 320 | 128 | 5.0372 | 29.2 | 217.4331 | 0 | 119.0517 | 0 | 37.5626 | 0.83132 | 0 | 36.7313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.5776 | 99.85% | 0 | 0 | 49.9758 | 99.95% | 35.9
6665 | 271 | 169 | 88 | 5.8431 | 27.7 | 136.399 | 0 | 59.2735 | 0 | 16.7559 | 0 | 0 | 16.7559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.5776 | 99.85% | 0 | 22.0441 | 27.0571 | 54.11% | 38.8
6666 | 3 | 21 | 21 | 4.8357 | 24.8 | 1.51 | 0 | 0 | 0 | 0.77397 | 0 | 0 | 0.77397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.5776 | 99.85% | 0 | 25 | 1.064 | 2.128% | 25.774
6667 | 0 | 0 | 0 | 3.2238 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.234 | 35.9 | 0 | 91.234 | 1185.2805 | 93% | 0 | 0 | 1.064 | 2.128% | 35.9
6668 | 0 | 0 | 0 | 0.40297 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0563 | 33.4 | 0 | 85.0563 | 1105.1138 | 86.71% | 0 | 0 | 1.064 | 2.128% | 33.4
6669 | 0 | 0 | 0 | 3.0223 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0154 | 31.7 | 0 | 81.0154 | 1029.5687 | 80.78% | 0 | 0 | 1.064 | 2.128% | 31.7
6670 | 0 | 0 | 0 | 3.4253 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.824 | 30 | 0 | 76.824 | 958.6201 | 75.21% | 0 | 0 | 1.064 | 2.128% | 30
6671 | 0 | 0 | 0 | 3.2238 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7456 | 28.6 | 0 | 73.7456 | 890.6383 | 69.88% | 0 | 0 | 1.064 | 2.128% | 28.6
6672 | 0 | 0 | 0 | 2.4178 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2395 | 28 | 0 | 72.2395 | 824.0914 | 64.66% | 0 | 0 | 1.064 | 2.128% | 28
6673 | 0 | 0 | 0 | 1.0074 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8562 | 27.5 | 0 | 70.8562 | 758.8547 | 59.54% | 0 | 0 | 1.064 | 2.128% | 27.5
6674 | 0 | 0 | 0 | 1.2089 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8455 | 27.5 | 0 | 70.8455 | 693.6181 | 54.42% | 0 | 0 | 1.064 | 2.128% | 27.5
6675 | 0 | 0 | 0 | 1.8134 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4429 | 27.8 | 0 | 71.4429 | 627.7934 | 49.26% | 0 | 0 | 1.064 | 2.128% | 27.8
6676 | 0 | 0 | 0 | 4.6342 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.1592 | 28.5 | 0 | 73.1592 | 560.3101 | 43.96% | 0 | 0 | 1.064 | 2.128% | 28.5
6677 | 0 | 0 | 0 | 2.0149 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1857 | 29 | 0 | 74.1857 | 491.8197 | 38.59% | 0 | 0 | 1.064 | 2.128% | 29
6678 | 0 | 0 | 0 | 1.8134 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5837 | 31.4 | 0 | 79.5837 | 417.2084 | 32.73% | 0 | 0 | 1.064 | 2.128% | 31.4
6679 | 169 | 46 | 25 | 2.4178 | 16.9 | 85.0606 | 0 | 0 | 0 | 3.0549 | 0 | 0 | 3.0549 | 0 | 0 | 0 | 77.9478 | 30.6451 | 0 | 77.9478 | 344.6907 | 27.04% | 0 | 0 | 1.064 | 2.128% | 33.7
6680 | 628 | 222 | 52 | 1.4104 | 19.6 | 316.0833 | 148.9944 | 0 | 121.7254 | 27.9029 | 0 | 0 | 27.9029 | 0 | 0 | 0 | 0 | 0 | 121.7254 | 0 | 457.466 | 35.89% | 0 | 0 | 1.064 | 2.128% | 27.9029
6681 | 799 | 422 | 66 | 1.2089 | 24.5 | 402.1506 | 228.0191 | 0 | 195.6597 | 68.4463 | 0 | 16.3731 | 52.0731 | 0 | 0 | 0 | 0 | 0 | 195.6597 | 0 | 638.7395 | 50.12% | 12.5582 | 0 | 14.1243 | 28.25% | 35.7
6682 | 882 | 594 | 73 | 1.4104 | 27.6 | 443.9259 | 275.2035 | 0 | 239.5929 | 101.0743 | 7.2872 | 25 | 68.7872 | 0 | 0 | 0 | 0 | 0 | 239.5929 | 0 | 860.7159 | 67.53% | 19.175 | 0 | 34.0659 | 68.13% | 36.5
6683 | 910 | 713 | 82 | 2.4178 | 29.1 | 458.0188 | 295.5099 | 0 | 258.4253 | 113.8 | 18.8255 | 19.9745 | 75 | 0 | 0 | 0 | 0 | 0 | 258.4253 | 0 | 1100.1401 | 86.32% | 15.3205 | 0 | 49.9989 | 100% | 36.2
6684 | 909 | 769 | 91 | 4.0297 | 29.4 | 457.5155 | 299.3678 | 0 | 261.4879 | 115.5 | 40.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 261.4879 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 34.5
6685 | 890 | 758 | 96 | 4.6342 | 29.8 | 447.9525 | 0 | 292.4992 | 0 | 116.4 | 41.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 33.6
6686 | 871 | 692 | 93 | 4.6342 | 29.9 | 438.3894 | 0 | 280.0319 | 0 | 116.8 | 41.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 33.2
6687 | 831 | 569 | 84 | 7.6565 | 29.4 | 418.2567 | 0 | 254.574 | 0 | 104.2592 | 35.6296 | 0 | 68.6296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 33
6688 | 692 | 396 | 92 | 8.8654 | 28.3 | 348.2956 | 0 | 190.1725 | 0 | 63.3855 | 14.5427 | 0 | 48.8427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9989 | 100% | 34.3
6689 | 561 | 209 | 66 | 7.2535 | 27.7 | 282.3611 | 0 | 122.1163 | 0 | 25.3066 | 0 | 0 | 25.3066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 12.7934 | 36.696 | 73.39% | 38.1
6690 | 123 | 33 | 17 | 5.8431 | 25.4 | 61.908 | 0 | 0 | 0 | 1.7603 | 0 | 0 | 1.7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 10.6996 | 21.4% | 26.7603
6691 | 0 | 0 | 0 | 3.4253 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.0459 | 25.9086 | 0 | 68.0459 | 1212.0326 | 95.1% | 0 | 10.2914 | 0 | 0% | 36.2
6692 | 0 | 0 | 0 | 0.60446 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1349 | 33.8 | 0 | 86.1349 | 1130.6945 | 88.72% | 0 | 0 | 0 | 0% | 33.8
6693 | 0 | 0 | 0 | 1.0074 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3896 | 31.9 | 0 | 81.3896 | 1054.6932 | 82.75% | 0 | 0 | 0 | 0% | 31.9
6694 | 0 | 0 | 0 | 3.2238 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2784 | 30.2 | 0 | 77.2784 | 983.225 | 77.15% | 0 | 0 | 0 | 0% | 30.2
6695 | 0 | 0 | 0 | 4.6342 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.0831 | 29.2 | 0 | 75.0831 | 913.9349 | 71.71% | 0 | 0 | 0 | 0% | 29.2
6696 | 0 | 0 | 0 | 4.6342 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3218 | 28.9 | 0 | 74.3218 | 845.3669 | 66.33% | 0 | 0 | 0 | 0% | 28.9
6697 | 0 | 0 | 0 | 2.8208 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.847 | 29.1 | 0 | 74.847 | 776.2851 | 60.91% | 0 | 0 | 0 | 0% | 29.1
6698 | 0 | 0 | 0 | 2.6193 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5123 | 29.9 | 0 | 76.5123 | 705.5769 | 55.36% | 0 | 0 | 0 | 0% | 29.9
6699 | 0 | 0 | 0 | 4.0297 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9748 | 33.4 | 0 | 84.9748 | 625.3104 | 49.06% | 0 | 0 | 0 | 0% | 33.4
6700 | 0 | 0 | 0 | 2.6193 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.156 | 38.5 | 0 | 97.156 | 530.511 | 41.62% | 0 | 0 | 0 | 0% | 38.5
6701 | 0 | 0 | 0 | 3.4253 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.0131 | 40.6 | 0 | 102.0131 | 429.6801 | 33.71% | 0 | 0 | 0 | 0% | 40.6
6702 | 0 | 0 | 0 | 5.0372 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3398 | 41.9 | 0 | 105.3398 | 325.1455 | 25.51% | 0 | 0 | 0 | 0% | 41.9
6703 | 166 | 45 | 25 | 1.6119 | 18.3 | 83.5507 | 0 | 0 | 0 | 2.8649 | 0 | 0 | 2.8649 | 0 | 0 | 0 | 100.4585 | 39.9351 | 0 | 100.4585 | 226.1399 | 17.74% | 0 | 0 | 0 | 0% | 42.8
6704 | 546 | 205 | 58 | 3.4253 | 22.4 | 274.8113 | 128.8746 | 0 | 102.0977 | 25.6767 | 0 | 0 | 25.6767 | 0 | 0 | 0 | 0 | 0 | 102.0977 | 0 | 322.2283 | 25.28% | 0 | 0 | 0 | 0% | 25.6767
6705 | 700 | 397 | 93 | 1.0074 | 26.6 | 352.3222 | 199.3058 | 0 | 168.8774 | 53.3325 | 0 | 4.3662 | 48.9662 | 0 | 0 | 0 | 0 | 0 | 168.8774 | 0 | 481.1659 | 37.75% | 3.3489 | 0 | 3.4833 | 6.967% | 44.6
6706 | 847 | 582 | 88 | 1.8134 | 28.3 | 426.3098 | 264.0364 | 0 | 228.9854 | 92.2386 | 0 | 23.6693 | 68.5693 | 0 | 0 | 0 | 0 | 0 | 228.9854 | 0 | 696.6736 | 54.66% | 18.1543 | 0 | 22.3662 | 44.73% | 44.9
6707 | 887 | 703 | 94 | 2.0149 | 30.2 | 446.4425 | 287.7182 | 0 | 251.2283 | 106.2 | 6.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 251.2283 | 0 | 933.115 | 73.21% | 19.175 | 0 | 42.3108 | 84.62% | 43.8
6708 | 872 | 751 | 107 | 3.0223 | 31.4 | 438.8928 | 287.0959 | 0 | 250.3293 | 107 | 22.3617 | 9.6383 | 75 | 0 | 0 | 0 | 0 | 0 | 250.3293 | 0 | 1168.7103 | 91.7% | 7.3925 | 0 | 50 | 100% | 43
6709 | 900 | 753 | 91 | 6.8506 | 31.3 | 452.9856 | 206.7296 | 88.9851 | 179.4837 | 107.2 | 32.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 179.4837 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.8
6710 | 902 | 689 | 77 | 11.4848 | 30.5 | 453.9923 | 0 | 289.8008 | 0 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
6711 | 785 | 549 | 94 | 11.6862 | 30.3 | 395.1041 | 0 | 240.1469 | 0 | 91.8504 | 24.9752 | 0 | 66.8752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.9
6712 | 600 | 389 | 132 | 8.8654 | 29.6 | 301.9904 | 0 | 164.4239 | 0 | 50.9107 | 4.2553 | 0 | 46.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.4
6713 | 181 | 154 | 111 | 7.455 | 28.2 | 91.1004 | 0 | 39.208 | 0 | 15.4851 | 0 | 0 | 15.4851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 24.0006 | 48% | 40.4851
6714 | 38 | 26 | 22 | 5.8431 | 26.3 | 19.1261 | 0 | 0 | 0 | 1.1545 | 0 | 0 | 1.1545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.0781 | 0 | 0% | 24.2326
6715 | 0 | 0 | 0 | 8.0595 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.487 | 39.6 | 0 | 100.487 | 1176.7064 | 92.33% | 0 | 0 | 0 | 0% | 39.6
6716 | 0 | 0 | 0 | 8.4625 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0975 | 36.3 | 0 | 92.0975 | 1088.2828 | 85.39% | 0 | 0 | 0 | 0% | 36.3
6717 | 0 | 0 | 0 | 8.4625 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4017 | 34.4 | 0 | 87.4017 | 1005.225 | 78.87% | 0 | 0 | 0 | 0% | 34.4
6718 | 0 | 0 | 0 | 6.6491 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3038 | 32.7 | 0 | 83.3038 | 927.0424 | 72.74% | 0 | 0 | 0 | 0% | 32.7
6719 | 0 | 0 | 0 | 5.0372 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7297 | 31.7 | 0 | 80.7297 | 851.6786 | 66.82% | 0 | 0 | 0 | 0% | 31.7
6720 | 0 | 0 | 0 | 3.8283 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6824 | 31.3 | 0 | 79.6824 | 777.4269 | 61% | 0 | 0 | 0 | 0% | 31.3
6721 | 0 | 0 | 0 | 3.6268 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2619 | 31.1 | 0 | 79.2619 | 703.7236 | 55.22% | 0 | 0 | 0 | 0% | 31.1
6722 | 0 | 0 | 0 | 4.4327 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7778 | 31.8 | 0 | 80.7778 | 628.044 | 49.28% | 0 | 0 | 0 | 0% | 31.8
6723 | 0 | 0 | 0 | 6.0446 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0823 | 34.8 | 0 | 88.0823 | 543.7459 | 42.66% | 0 | 0 | 0 | 0% | 34.8
6724 | 0 | 0 | 0 | 3.2238 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3432 | 39.5 | 0 | 99.3432 | 446.0957 | 35% | 0 | 0 | 0 | 0% | 39.5
6725 | 0 | 0 | 0 | 3.4253 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.879 | 41.4 | 0 | 103.879 | 343.0291 | 26.91% | 0 | 0 | 0 | 0% | 41.4
6726 | 0 | 0 | 0 | 4.0297 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7102 | 42.6 | 0 | 106.7102 | 236.5208 | 18.56% | 0 | 0 | 0 | 0% | 42.6
6727 | 0 | 18 | 18 | 1.6119 | 17.2 | 0 | 0 | 0 | 0 | 0.60947 | 0 | 0 | 0.60947 | 0 | 0 | 0 | 107.2002 | 42.7905 | 0 | 107.2002 | 129.4287 | 10.16% | 0 | 0 | 0 | 0% | 43.4
6728 | 0 | 96 | 96 | 2.4178 | 18.6 | 0 | 0 | 0 | 0 | 7.3094 | 0 | 0 | 7.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.4287 | 10.16% | 0 | 0 | 0 | 0% | 7.3094
6729 | 4 | 202 | 199 | 5.4401 | 20.5 | 2.0133 | 0 | 1.1363 | 0 | 16.3288 | 0 | 0 | 16.3288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.4287 | 10.16% | 0 | 0 | 0 | 0% | 16.3288
6730 | 124 | 352 | 273 | 6.8506 | 21.9 | 62.4114 | 0 | 38.619 | 0 | 34.2567 | 0 | 0 | 34.2567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.4287 | 10.16% | 0 | 0 | 0 | 0% | 34.2567
6731 | 440 | 534 | 225 | 7.455 | 23 | 221.4597 | 142.5646 | 0 | 113.0165 | 76.616 | 0 | 15.808 | 60.808 | 0 | 0 | 0 | 0 | 0 | 113.0165 | 0 | 237.0202 | 18.6% | 12.1248 | 0 | 12.6132 | 25.23% | 45
6732 | 748 | 715 | 164 | 7.6565 | 24.2 | 376.4814 | 246.1965 | 0 | 209.695 | 105.9 | 5.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 209.695 | 0 | 436.6495 | 34.26% | 19.175 | 0 | 32.5607 | 65.12% | 44.1
6733 | 761 | 692 | 135 | 6.2461 | 24.6 | 383.0245 | 249.9832 | 0 | 214.0553 | 106 | 9.1436 | 21.8564 | 75 | 0 | 0 | 0 | 0 | 0 | 214.0553 | 0 | 640.4298 | 50.25% | 16.7639 | 0 | 50 | 100% | 44
6734 | 742 | 661 | 159 | 6.6491 | 25.1 | 373.4615 | 238.2305 | 0 | 202.9642 | 106.1 | 31.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 202.9642 | 0 | 833.6515 | 65.41% | 0 | 0 | 50 | 100% | 43.9
6735 | 606 | 500 | 152 | 6.2461 | 25.2 | 305.0103 | 185.1262 | 0 | 153.5388 | 76.8738 | 16.8369 | 0 | 60.0369 | 0 | 0 | 0 | 0 | 0 | 153.5388 | 0 | 979.8202 | 76.88% | 0 | 0 | 50 | 100% | 43.2
6736 | 574 | 346 | 108 | 5.2387 | 25.1 | 288.9042 | 156.8483 | 0 | 127.6657 | 44.1454 | 0.37272 | 0 | 43.7727 | 0 | 0 | 0 | 0 | 0 | 127.6657 | 0 | 1101.3577 | 86.41% | 0 | 0 | 50 | 100% | 43.4
6737 | 508 | 182 | 56 | 3.4253 | 24.6 | 255.6852 | 109.4988 | 0 | 83.9596 | 22.5863 | 0 | 0 | 22.5863 | 0 | 0 | 0 | 0 | 0 | 83.9596 | 0 | 1181.2871 | 92.69% | 0 | 23.5137 | 25.5427 | 51.09% | 46.1
6738 | 72 | 24 | 15 | 4.0297 | 22.1 | 36.2389 | 0 | 0 | 0 | 1.2335 | 0 | 0 | 1.2335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1181.2871 | 92.69% | 0 | 24.5573 | 0 | 0% | 25.7908
6739 | 0 | 0 | 0 | 3.2238 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2141 | 40.1 | 0 | 101.2141 | 1082.0709 | 84.9% | 0 | 0 | 0 | 0% | 40.1
6740 | 0 | 0 | 0 | 3.4253 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8453 | 36.7 | 0 | 92.8453 | 992.544 | 77.88% | 0 | 0 | 0 | 0% | 36.7
6741 | 0 | 0 | 0 | 1.4104 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6132 | 35 | 0 | 88.6132 | 907.7579 | 71.22% | 0 | 0 | 0 | 0% | 35
6742 | 0 | 0 | 0 | 3.0223 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2467 | 33.2 | 0 | 84.2467 | 828.1657 | 64.98% | 0 | 0 | 0 | 0% | 33.2
6743 | 0 | 0 | 0 | 2.2164 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8906 | 31.8 | 0 | 80.8906 | 752.5362 | 59.05% | 0 | 0 | 0 | 0% | 31.8
6744 | 0 | 0 | 0 | 3.2238 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0221 | 31.5 | 0 | 80.0221 | 677.7385 | 53.18% | 0 | 0 | 0 | 0% | 31.5
6745 | 0 | 0 | 0 | 2.2164 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7967 | 31.4 | 0 | 79.7967 | 603.2091 | 47.33% | 0 | 0 | 0 | 0% | 31.4
6746 | 0 | 0 | 0 | 1.2089 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6909 | 31.8 | 0 | 80.6909 | 527.5422 | 41.39% | 0 | 0 | 0 | 0% | 31.8
6747 | 0 | 0 | 0 | 0.40297 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7769 | 34.4 | 0 | 86.7769 | 444.4216 | 34.87% | 0 | 0 | 0 | 0% | 34.4
6748 | 0 | 0 | 0 | 1.0074 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8408 | 38.6 | 0 | 96.8408 | 349.3724 | 27.41% | 0 | 0 | 0 | 0% | 38.6
6749 | 0 | 0 | 0 | 2.2164 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1298 | 40.4 | 0 | 101.1298 | 249.137 | 19.55% | 0 | 0 | 0 | 0% | 40.4
6750 | 0 | 0 | 0 | 2.0149 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.095 | 41.2182 | 0 | 103.095 | 146.5575 | 11.5% | 0 | 0 | 0 | 0% | 41.2182
6751 | 165 | 36 | 18 | 1.6119 | 15.1 | 83.0474 | 0 | 0 | 0 | 2.4335 | 0 | 0 | 2.4335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.5575 | 11.5% | 0 | 0 | 0 | 0% | 2.4335
6752 | 572 | 204 | 56 | 1.4104 | 18.3 | 287.8975 | 133.6319 | 0 | 107.2055 | 26.7529 | 0 | 0 | 26.7529 | 0 | 0 | 0 | 0 | 0 | 107.2055 | 0 | 248.4118 | 19.49% | 0 | 0 | 0 | 0% | 26.7529
6753 | 756 | 398 | 71 | 1.4104 | 20.9 | 380.5079 | 214.2679 | 0 | 182.7118 | 58.1041 | 0 | 6.9021 | 51.2021 | 0 | 0 | 0 | 0 | 0 | 182.7118 | 0 | 422.0033 | 33.11% | 5.2939 | 0 | 5.5079 | 11.02% | 44.3
6754 | 841 | 564 | 79 | 1.6119 | 22.6 | 423.2899 | 261.6847 | 0 | 226.8324 | 92.0029 | 0 | 23.7514 | 68.2514 | 0 | 0 | 0 | 0 | 0 | 226.8324 | 0 | 637.5131 | 50.02% | 18.2173 | 0 | 24.4619 | 48.92% | 44.5
6755 | 884 | 682 | 83 | 2.0149 | 24.1 | 444.9326 | 286.1073 | 0 | 249.6732 | 106.6 | 6.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 249.6732 | 0 | 874.7236 | 68.63% | 19.175 | 0 | 44.4124 | 88.82% | 43.4
6756 | 902 | 741 | 84 | 2.0149 | 25.5 | 453.9923 | 296.7955 | 0 | 259.7276 | 107.5 | 25.4981 | 7.0019 | 75 | 0 | 0 | 0 | 0 | 0 | 259.7276 | 0 | 1121.4866 | 87.99% | 5.3705 | 0 | 50 | 100% | 42.5
6757 | 900 | 738 | 84 | 3.0223 | 26.8 | 452.9856 | 284.1381 | 11.4348 | 248.2808 | 107.8 | 32.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 248.2808 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.2
6758 | 872 | 669 | 84 | 3.8283 | 28.1 | 438.8928 | 0 | 279.7741 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42
6759 | 824 | 545 | 79 | 7.455 | 28 | 414.7335 | 0 | 251.3648 | 0 | 93.182 | 25.891 | 0 | 67.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.4
6760 | 718 | 372 | 72 | 6.8506 | 27.3 | 361.3819 | 0 | 195.627 | 0 | 54.2917 | 6.2958 | 0 | 47.9958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
6761 | 523 | 178 | 51 | 7.858 | 25.7 | 263.235 | 0 | 112.166 | 0 | 22.6211 | 0 | 0 | 22.6211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 21.7789 | 27.3439 | 54.69% | 44.4
6762 | 81 | 23 | 13 | 5.8431 | 23.7 | 40.7687 | 0 | 0 | 0 | 1.1529 | 0 | 0 | 1.1529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 1.3356 | 2.671% | 26.1529
6763 | 0 | 0 | 0 | 2.2164 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3978 | 39.3 | 0 | 99.3978 | 1177.5964 | 92.4% | 0 | 0 | 1.3356 | 2.671% | 39.3
6764 | 0 | 0 | 0 | 1.0074 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5105 | 36.1 | 0 | 91.5105 | 1089.7563 | 85.5% | 0 | 0 | 1.3356 | 2.671% | 36.1
6765 | 0 | 0 | 0 | 2.8208 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5734 | 34.5 | 0 | 87.5734 | 1006.4294 | 78.97% | 0 | 0 | 1.3356 | 2.671% | 34.5
6766 | 0 | 0 | 0 | 3.2238 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6587 | 32.9 | 0 | 83.6587 | 927.6969 | 72.79% | 0 | 0 | 1.3356 | 2.671% | 32.9
6767 | 0 | 0 | 0 | 4.2312 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1806 | 31.9 | 0 | 81.1806 | 851.7889 | 66.83% | 0 | 0 | 1.3356 | 2.671% | 31.9
6768 | 0 | 0 | 0 | 3.0223 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8604 | 31.4 | 0 | 79.8604 | 777.2757 | 60.99% | 0 | 0 | 1.3356 | 2.671% | 31.4
6769 | 0 | 0 | 0 | 8.0595 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3612 | 31.2 | 0 | 79.3612 | 703.3113 | 55.18% | 0 | 0 | 1.3356 | 2.671% | 31.2
6770 | 0 | 0 | 0 | 7.455 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7128 | 31.8 | 0 | 80.7128 | 627.6506 | 49.25% | 0 | 0 | 1.3356 | 2.671% | 31.8
6771 | 0 | 0 | 0 | 6.8506 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1294 | 34.9 | 0 | 88.1294 | 543.082 | 42.61% | 0 | 0 | 1.3356 | 2.671% | 34.9
6772 | 0 | 0 | 0 | 5.2387 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7778 | 39.3 | 0 | 98.7778 | 446.0341 | 35% | 0 | 0 | 1.3356 | 2.671% | 39.3
6773 | 0 | 0 | 0 | 4.8357 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8398 | 41.4 | 0 | 103.8398 | 342.9945 | 26.91% | 0 | 0 | 1.3356 | 2.671% | 41.4
6774 | 0 | 0 | 0 | 4.8357 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.8662 | 42.7 | 0 | 106.8662 | 236.2284 | 18.53% | 0 | 0 | 1.3356 | 2.671% | 42.7
6775 | 91 | 27 | 16 | 3.8283 | 16.5 | 45.8019 | 0 | 0 | 0 | 1.6397 | 0 | 0 | 1.6397 | 0 | 0 | 0 | 105.0707 | 41.9603 | 0 | 105.0707 | 131.5323 | 10.32% | 0 | 0 | 1.3356 | 2.671% | 43.6
6776 | 558 | 200 | 56 | 4.6342 | 19.1 | 280.8511 | 129.6958 | 0 | 102.4061 | 26.5265 | 0 | 0 | 26.5265 | 0 | 0 | 0 | 0 | 0 | 102.4061 | 0 | 229.0521 | 17.97% | 0 | 0 | 1.3356 | 2.671% | 26.5265
6777 | 693 | 379 | 78 | 10.6788 | 21.3 | 348.7989 | 195.9684 | 0 | 160.9437 | 55.3773 | 0 | 5.2887 | 50.0887 | 0 | 0 | 0 | 0 | 0 | 160.9437 | 0 | 382.3165 | 30% | 4.0564 | 0 | 5.5566 | 11.11% | 44.8
6778 | 839 | 562 | 81 | 11.8877 | 22.6 | 422.2833 | 260.8264 | 0 | 220.6865 | 98.7329 | 1.8165 | 25 | 71.9165 | 0 | 0 | 0 | 0 | 0 | 220.6865 | 0 | 592.4731 | 46.49% | 19.175 | 0 | 25.5099 | 51.02% | 45.1
6779 | 882 | 677 | 83 | 12.6937 | 23.6 | 443.9259 | 285.1448 | 0 | 243.1115 | 106 | 6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 243.1115 | 0 | 823.9848 | 64.65% | 19.175 | 0 | 45.4632 | 90.93% | 44
6780 | 904 | 738 | 83 | 11.8877 | 24.5 | 454.9989 | 297.3653 | 0 | 255.1209 | 106.8 | 26.1172 | 5.6828 | 75 | 0 | 0 | 0 | 0 | 0 | 255.1209 | 0 | 1066.9327 | 83.71% | 4.3587 | 0 | 49.9988 | 100% | 43.2
6781 | 907 | 735 | 81 | 12.6937 | 24.9 | 456.5089 | 297.8005 | 0 | 255.0518 | 106.9 | 31.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 255.0518 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9988 | 100% | 43.1
6782 | 885 | 667 | 78 | 11.6862 | 25.3 | 445.4359 | 0 | 283.7455 | 0 | 107.1 | 32.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9988 | 100% | 42.9
6783 | 833 | 540 | 75 | 12.2907 | 25.2 | 419.2634 | 0 | 253.7453 | 0 | 95.8995 | 26.8997 | 0 | 68.9997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9988 | 100% | 42.1
6784 | 747 | 372 | 65 | 12.2907 | 24.5 | 375.9781 | 0 | 202.9289 | 0 | 57.0888 | 7.2444 | 0 | 49.8444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.9988 | 100% | 42.6
6785 | 556 | 178 | 46 | 11.8877 | 23.2 | 279.8445 | 0 | 118.6349 | 0 | 23.4375 | 0 | 0 | 23.4375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 21.7625 | 27.3565 | 54.71% | 45.2
6786 | 89 | 22 | 12 | 12.2907 | 21 | 44.7952 | 0 | 0 | 0 | 1.097 | 0 | 0 | 1.097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 1.3444 | 2.689% | 26.097
6787 | 0 | 0 | 0 | 8.8654 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.373 | 39.8 | 0 | 100.373 | 1176.1626 | 92.28% | 0 | 0 | 1.3444 | 2.689% | 39.8
6788 | 0 | 0 | 0 | 8.0595 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8453 | 36.7 | 0 | 92.8453 | 1086.6448 | 85.26% | 0 | 0 | 1.3444 | 2.689% | 36.7
6789 | 0 | 0 | 0 | 7.858 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8893 | 35.1 | 0 | 88.8893 | 1001.5903 | 78.59% | 0 | 0 | 1.3444 | 2.689% | 35.1
6790 | 0 | 0 | 0 | 6.6491 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9674 | 33.5 | 0 | 84.9674 | 921.1472 | 72.27% | 0 | 0 | 1.3444 | 2.689% | 33.5
6791 | 0 | 0 | 0 | 5.4401 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.546 | 32.5 | 0 | 82.546 | 843.548 | 66.19% | 0 | 0 | 1.3444 | 2.689% | 32.5
6792 | 0 | 0 | 0 | 3.6268 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3754 | 31.6 | 0 | 80.3754 | 768.4793 | 60.3% | 0 | 0 | 1.3444 | 2.689% | 31.6
6793 | 0 | 0 | 0 | 3.6268 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2979 | 31.2 | 0 | 79.2979 | 694.5205 | 54.49% | 0 | 0 | 1.3444 | 2.689% | 31.2
6794 | 0 | 0 | 0 | 3.6268 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6582 | 31.8 | 0 | 80.6582 | 618.8655 | 48.56% | 0 | 0 | 1.3444 | 2.689% | 31.8
6795 | 0 | 0 | 0 | 4.0297 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8058 | 34.4 | 0 | 86.8058 | 535.7597 | 42.04% | 0 | 0 | 1.3444 | 2.689% | 34.4
6796 | 0 | 0 | 0 | 3.0223 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0663 | 39.1 | 0 | 98.0663 | 439.2949 | 34.47% | 0 | 0 | 1.3444 | 2.689% | 39.1
6797 | 0 | 0 | 0 | 2.2164 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7654 | 41.1 | 0 | 102.7654 | 337.1112 | 26.45% | 0 | 0 | 1.3444 | 2.689% | 41.1
6798 | 0 | 0 | 0 | 4.0297 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.1667 | 42.1 | 0 | 105.1667 | 232.063 | 18.21% | 0 | 0 | 1.3444 | 2.689% | 42.1
6799 | 116 | 25 | 15 | 4.6342 | 15.6 | 58.3848 | 0 | 0 | 0 | 1.7396 | 0 | 0 | 1.7396 | 0 | 0 | 0 | 103.2469 | 41.2604 | 0 | 103.2469 | 129.3593 | 10.15% | 0 | 0 | 1.3444 | 2.689% | 43
6800 | 500 | 183 | 64 | 3.6268 | 17.9 | 251.6587 | 115.4398 | 0 | 89.5765 | 25.2801 | 0 | 0 | 25.2801 | 0 | 0 | 0 | 0 | 0 | 89.5765 | 0 | 214.6951 | 16.85% | 0 | 0 | 1.3444 | 2.689% | 25.2801
6801 | 782 | 439 | 106 | 6.4476 | 20.8 | 393.5942 | 220.6403 | 0 | 186.5431 | 70.9164 | 0 | 13.2082 | 57.7082 | 0 | 0 | 0 | 0 | 0 | 186.5431 | 0 | 392.4069 | 30.79% | 10.1307 | 0 | 11.8878 | 23.78% | 44.5
6802 | 851 | 561 | 77 | 9.2684 | 23.2 | 428.3231 | 264.2701 | 0 | 225.5079 | 99.0715 | 2.2358 | 25 | 71.8358 | 0 | 0 | 0 | 0 | 0 | 225.5079 | 0 | 607.2389 | 47.64% | 19.175 | 0 | 31.8439 | 63.69% | 44.6
6803 | 863 | 688 | 110 | 10.6788 | 24.2 | 434.3629 | 278.6959 | 0 | 238.2385 | 106.6 | 8.8581 | 22.7419 | 75 | 0 | 0 | 0 | 0 | 0 | 238.2385 | 0 | 834.1988 | 65.45% | 17.443 | 0 | 49.9975 | 100% | 43.4
6804 | 598 | 725 | 287 | 11.8877 | 25.1 | 300.9838 | 196.6505 | 0 | 160.9729 | 107.8 | 32.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 160.9729 | 0 | 987.551 | 77.48% | 0 | 0 | 49.9975 | 100% | 42.2
6805 | 359 | 673 | 408 | 12.0892 | 25.5 | 180.6909 | 117.8444 | 0 | 87.3853 | 101.7157 | 29.9579 | 0 | 71.7579 | 0 | 0 | 0 | 0 | 0 | 87.3853 | 0 | 1070.7993 | 84.02% | 0 | 0 | 49.9975 | 100% | 41.8
6806 | 279 | 481 | 296 | 10.4773 | 25.3 | 140.4256 | 89.3885 | 0 | 61.719 | 62.7695 | 10.5847 | 0 | 52.1847 | 0 | 0 | 0 | 0 | 0 | 61.719 | 0 | 1129.5964 | 88.63% | 0 | 0 | 49.9975 | 100% | 41.6
6807 | 493 | 498 | 221 | 9.4699 | 25.6 | 248.1355 | 149.958 | 0 | 118.8321 | 75.1367 | 17.0684 | 0 | 58.0684 | 0 | 0 | 0 | 0 | 0 | 118.8321 | 0 | 1242.8028 | 97.51% | 0 | 0 | 49.9975 | 100% | 41
6808 | 429 | 313 | 129 | 10.0743 | 24.9 | 215.9232 | 0 | 116.1935 | 0 | 37.5055 | 0 | 0 | 37.5055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.8028 | 97.51% | 0 | 4.1945 | 45.6328 | 91.27% | 41.7
6809 | 2 | 70 | 70 | 9.8729 | 22.8 | 1.0066 | 0 | 0.42453 | 0 | 5.06 | 0 | 0 | 5.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.8028 | 97.51% | 0 | 25 | 19.6181 | 39.24% | 30.06
6810 | 1 | 10 | 10 | 9.8729 | 21 | 0.50332 | 0 | 0 | 0 | 0.12801 | 0 | 0 | 0.12801 | 0 | 0 | 0 | 62.1471 | 23.4165 | 0 | 62.1471 | 1186.0415 | 93.06% | 0 | 18.8555 | 0 | 0% | 42.4
6811 | 0 | 0 | 0 | 8.4625 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9942 | 38.8 | 0 | 97.9942 | 1090.5689 | 85.57% | 0 | 0 | 0 | 0% | 38.8
6812 | 0 | 0 | 0 | 6.6491 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1921 | 36 | 0 | 91.1921 | 1003.0135 | 78.7% | 0 | 0 | 0 | 0% | 36
6813 | 0 | 0 | 0 | 6.8506 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2813 | 34.4 | 0 | 87.2813 | 919.9809 | 72.18% | 0 | 0 | 0 | 0% | 34.4
6814 | 0 | 0 | 0 | 5.4401 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6613 | 32.5 | 0 | 82.6613 | 842.3895 | 66.1% | 0 | 0 | 0 | 0% | 32.5
6815 | 0 | 0 | 0 | 5.6416 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0196 | 31 | 0 | 79.0196 | 769.0078 | 60.34% | 0 | 0 | 0 | 0% | 31
6816 | 0 | 0 | 0 | 4.8357 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.8208 | 30.1 | 0 | 76.8208 | 698.0251 | 54.77% | 0 | 0 | 0 | 0% | 30.1
6817 | 0 | 0 | 0 | 3.4253 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.8759 | 29.7 | 0 | 75.8759 | 627.9739 | 49.27% | 0 | 0 | 0 | 0% | 29.7
6818 | 0 | 0 | 0 | 2.6193 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.4385 | 29.1 | 0 | 74.4385 | 559.2955 | 43.88% | 0 | 0 | 0 | 0% | 29.1
6819 | 0 | 0 | 0 | 5.0372 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1275 | 29.4 | 0 | 75.1275 | 489.9398 | 38.44% | 0 | 0 | 0 | 0% | 29.4
6820 | 0 | 0 | 0 | 3.6268 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.863 | 30.6 | 0 | 77.863 | 417.6089 | 32.77% | 0 | 0 | 0 | 0% | 30.6
6821 | 0 | 0 | 0 | 2.4178 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2211 | 31.6 | 0 | 80.2211 | 342.4654 | 26.87% | 0 | 0 | 0 | 0% | 31.6
6822 | 0 | 0 | 0 | 3.0223 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4929 | 34.2 | 0 | 86.4929 | 259.8753 | 20.39% | 0 | 0 | 0 | 0% | 34.2
6823 | 27 | 23 | 20 | 3.6268 | 17.5 | 13.5896 | 0 | 0 | 0 | 1.0626 | 0 | 0 | 1.0626 | 0 | 0 | 0 | 84.8354 | 33.4662 | 0 | 84.8354 | 179.3782 | 14.07% | 0 | 0 | 0 | 0% | 34.5288
6824 | 23 | 105 | 99 | 5.0372 | 18.7 | 11.5763 | 0 | 5.269 | 0 | 9.0506 | 0 | 0 | 9.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179.3782 | 14.07% | 0 | 0 | 0 | 0% | 9.0506
6825 | 270 | 340 | 221 | 6.4476 | 20.4 | 135.8957 | 76.0108 | 0 | 50.808 | 36.7008 | 0 | 0 | 36.7008 | 0 | 0 | 0 | 0 | 0 | 50.808 | 0 | 226.882 | 17.8% | 0 | 0 | 0 | 0% | 36.7008
6826 | 42 | 315 | 287 | 8.4625 | 21.2 | 21.1393 | 0 | 13.0129 | 0 | 28.6629 | 0 | 0 | 28.6629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.882 | 17.8% | 0 | 0 | 0 | 0% | 28.6629
6827 | 20 | 396 | 376 | 9.2684 | 22 | 10.0663 | 0 | 6.4517 | 0 | 33.3357 | 0 | 0 | 33.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.882 | 17.8% | 0 | 0 | 0 | 0% | 33.3357
6828 | 114 | 498 | 407 | 7.455 | 23.6 | 57.3782 | 0 | 37.4776 | 0 | 58.1773 | 0 | 11.3386 | 46.8386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.882 | 17.8% | 8.6967 | 0 | 9.0524 | 18.1% | 35.5
6829 | 485 | 651 | 299 | 5.8431 | 25.1 | 244.1089 | 159.1511 | 0 | 129.4498 | 111.0372 | 13.3686 | 25 | 72.6686 | 0 | 0 | 0 | 0 | 0 | 129.4498 | 0 | 347.9135 | 27.3% | 19.175 | 0 | 29.0115 | 58.02% | 34.3
6830 | 763 | 642 | 141 | 4.0297 | 26.5 | 384.0312 | 244.2818 | 0 | 209.869 | 116.1 | 16.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 209.869 | 0 | 544.1343 | 42.69% | 19.175 | 0 | 48.9707 | 97.94% | 33.9
6831 | 742 | 542 | 135 | 4.0297 | 27.3 | 373.4615 | 225.3672 | 0 | 192.2557 | 99.3167 | 32.8083 | 0 | 66.5083 | 0 | 0 | 0 | 0 | 0 | 192.2557 | 0 | 723.8873 | 56.8% | 0 | 0 | 48.9707 | 97.94% | 33.7
6832 | 662 | 355 | 89 | 7.2535 | 27 | 333.1961 | 178.7582 | 0 | 147.087 | 58.4877 | 11.8439 | 0 | 46.6439 | 0 | 0 | 0 | 0 | 0 | 147.087 | 0 | 861.4089 | 67.59% | 0 | 0 | 48.9707 | 97.94% | 34.8
6833 | 397 | 153 | 61 | 9.8729 | 25.1 | 199.817 | 83.8254 | 0 | 56.5519 | 19.2852 | 0 | 0 | 19.2852 | 0 | 0 | 0 | 0 | 0 | 56.5519 | 0 | 914.2831 | 71.74% | 0 | 18.6148 | 29.5977 | 59.2% | 37.9
6834 | 36 | 16 | 12 | 8.261 | 22.8 | 18.1194 | 0 | 0 | 0 | 0.61037 | 0 | 0 | 0.61037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.2831 | 71.74% | 0 | 25 | 3.5783 | 7.157% | 25.6104
6835 | 0 | 0 | 0 | 6.8506 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.703 | 31.9609 | 0 | 81.703 | 837.9863 | 65.75% | 0 | 3.4391 | 0 | 0% | 35.4
6836 | 0 | 0 | 0 | 5.4401 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4768 | 33.6 | 0 | 85.4768 | 757.2281 | 59.41% | 0 | 0 | 0 | 0% | 33.6
6837 | 0 | 0 | 0 | 4.4327 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5845 | 31.6 | 0 | 80.5845 | 682.1104 | 53.52% | 0 | 0 | 0 | 0% | 31.6
6838 | 0 | 0 | 0 | 2.4178 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5932 | 30 | 0 | 76.5932 | 611.356 | 47.97% | 0 | 0 | 0 | 0% | 30
6839 | 0 | 0 | 0 | 2.0149 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.484 | 28.6 | 0 | 73.484 | 543.5945 | 42.65% | 0 | 0 | 0 | 0% | 28.6
6840 | 0 | 0 | 0 | 3.0223 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.2738 | 27.6 | 0 | 71.2738 | 477.9504 | 37.5% | 0 | 0 | 0 | 0% | 27.6
6841 | 0 | 0 | 0 | 1.8134 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.4087 | 27.3 | 0 | 70.4087 | 413.1171 | 32.41% | 0 | 0 | 0 | 0% | 27.3
6842 | 0 | 0 | 0 | 2.2164 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1735 | 27.2 | 0 | 70.1735 | 348.4949 | 27.34% | 0 | 0 | 0 | 0% | 27.2
6843 | 0 | 0 | 0 | 2.8208 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5901 | 27.8 | 0 | 71.5901 | 282.4962 | 22.17% | 0 | 0 | 0 | 0% | 27.8
6844 | 0 | 0 | 0 | 3.2238 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.0305 | 25.8193 | 0 | 67.0305 | 220.8528 | 17.33% | 0 | 0 | 0 | 0% | 25.8193
6845 | 0 | 0 | 0 | 2.2164 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220.8528 | 17.33% | 0 | 0 | 0 | 0% | 0
6846 | 0 | 0 | 0 | 4.0297 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220.8528 | 17.33% | 0 | 0 | 0 | 0% | 0
6847 | 102 | 28 | 18 | 2.8208 | 16.2 | 51.3384 | 0 | 0 | 0 | 1.8432 | 0 | 0 | 1.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220.8528 | 17.33% | 0 | 0 | 0 | 0% | 1.8432
6848 | 509 | 191 | 63 | 1.4104 | 18.4 | 256.1886 | 115.6987 | 0 | 90.6052 | 25.3899 | 0 | 0 | 25.3899 | 0 | 0 | 0 | 0 | 0 | 90.6052 | 0 | 304.9134 | 23.92% | 0 | 0 | 0 | 0% | 25.3899
6849 | 705 | 385 | 88 | 2.2164 | 21.4 | 354.8388 | 197.9279 | 0 | 167.1545 | 66.1296 | 0 | 15.5148 | 50.6148 | 0 | 0 | 0 | 0 | 0 | 167.1545 | 0 | 459.994 | 36.09% | 11.8999 | 0 | 12.3882 | 24.78% | 35.1
6850 | 796 | 550 | 101 | 1.4104 | 24.3 | 400.6406 | 246.0641 | 0 | 212.3752 | 98.7311 | 6.4156 | 25 | 67.3156 | 0 | 0 | 0 | 0 | 0 | 212.3752 | 0 | 657.0289 | 51.55% | 19.175 | 0 | 32.3502 | 64.7% | 35.9
6851 | 840 | 666 | 109 | 3.0223 | 25.5 | 422.7866 | 270.6785 | 0 | 234.7951 | 114.2 | 17.0957 | 22.1043 | 75 | 0 | 0 | 0 | 0 | 0 | 234.7951 | 0 | 874.8643 | 68.64% | 16.954 | 0 | 50 | 100% | 35.8
6852 | 858 | 726 | 113 | 2.4178 | 27 | 431.8463 | 281.9859 | 0 | 245.6567 | 115.9 | 40.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 245.6567 | 0 | 1102.7768 | 86.53% | 0 | 0 | 50 | 100% | 34.1
6853 | 850 | 719 | 115 | 3.0223 | 28.1 | 427.8198 | 278.6438 | 0 | 242.3122 | 116.9 | 41.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 242.3122 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.1
6854 | 808 | 646 | 118 | 5.4401 | 28.5 | 406.6804 | 0 | 258.5023 | 0 | 117.4 | 42.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.6
6855 | 736 | 517 | 114 | 5.2387 | 27.5 | 370.4416 | 0 | 223.2147 | 0 | 96.5796 | 31.9398 | 0 | 64.6398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.7
6856 | 606 | 342 | 100 | 7.6565 | 27.3 | 305.0103 | 0 | 163.1349 | 0 | 54.4851 | 9.9425 | 0 | 44.5425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.6
6857 | 379 | 152 | 65 | 8.6639 | 25.8 | 190.7573 | 0 | 79.5963 | 0 | 18.701 | 0 | 0 | 18.701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 19.399 | 29.8079 | 59.62% | 38.1
6858 | 24 | 16 | 12 | 7.052 | 23.6 | 12.0796 | 0 | 0 | 0 | 0.44324 | 0 | 0 | 0.44324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 3.7846 | 7.569% | 25.4432
6859 | 0 | 0 | 0 | 7.052 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7156 | 32.3631 | 0 | 82.7156 | 1197.0931 | 93.93% | 0 | 3.6369 | 0 | 0% | 36
6860 | 0 | 0 | 0 | 6.6491 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7381 | 33.7 | 0 | 85.7381 | 1116.0548 | 87.57% | 0 | 0 | 0 | 0% | 33.7
6861 | 0 | 0 | 0 | 5.0372 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5523 | 31.6 | 0 | 80.5523 | 1040.9762 | 81.68% | 0 | 0 | 0 | 0% | 31.6
6862 | 0 | 0 | 0 | 2.6193 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.8208 | 30.1 | 0 | 76.8208 | 969.9818 | 76.11% | 0 | 0 | 0 | 0% | 30.1
6863 | 0 | 0 | 0 | 3.4253 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.4684 | 29.1 | 0 | 74.4684 | 901.278 | 70.72% | 0 | 0 | 0 | 0% | 29.1
6864 | 0 | 0 | 0 | 3.8283 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6311 | 28.7 | 0 | 73.6311 | 833.3752 | 65.39% | 0 | 0 | 0 | 0% | 28.7
6865 | 0 | 0 | 0 | 4.8357 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.41 | 28.6 | 0 | 73.41 | 765.676 | 60.08% | 0 | 0 | 0 | 0% | 28.6
6866 | 0 | 0 | 0 | 5.4401 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.672 | 29.6 | 0 | 75.672 | 695.7829 | 54.59% | 0 | 0 | 0 | 0% | 29.6
6867 | 0 | 0 | 0 | 4.6342 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.643 | 33.4 | 0 | 84.643 | 615.5269 | 48.3% | 0 | 0 | 0 | 0% | 33.4
6868 | 0 | 0 | 0 | 4.4327 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8305 | 38.9 | 0 | 97.8305 | 519.5926 | 40.77% | 0 | 0 | 0 | 0% | 38.9
6869 | 0 | 0 | 0 | 5.4401 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2529 | 41.5 | 0 | 104.2529 | 416.2313 | 32.66% | 0 | 0 | 0 | 0% | 41.5
6870 | 0 | 0 | 0 | 3.2238 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3547 | 42.8 | 0 | 107.3547 | 309.1433 | 24.26% | 0 | 0 | 0 | 0% | 42.8
6871 | 22 | 27 | 25 | 2.2164 | 16.9 | 11.073 | 0 | 0 | 0 | 1.2549 | 0 | 0 | 1.2549 | 0 | 0 | 0 | 106.0774 | 42.3451 | 0 | 106.0774 | 203.3233 | 15.95% | 0 | 0 | 0 | 0% | 43.6
6872 | 43 | 76 | 69 | 3.6268 | 18.2 | 21.6426 | 0 | 9.6983 | 0 | 6.8539 | 0 | 0 | 6.8539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.3233 | 15.95% | 0 | 0 | 0 | 0% | 6.8539
6873 | 32 | 163 | 148 | 2.6193 | 19.9 | 16.1062 | 0 | 8.9443 | 0 | 14.1798 | 0 | 0 | 14.1798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.3233 | 15.95% | 0 | 0 | 0 | 0% | 14.1798
6874 | 114 | 279 | 211 | 3.0223 | 22 | 57.3782 | 0 | 35.1606 | 0 | 27.522 | 0 | 0 | 27.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203.3233 | 15.95% | 0 | 0 | 0 | 0% | 27.522
6875 | 316 | 469 | 255 | 2.2164 | 24.3 | 159.0483 | 101.7171 | 0 | 77.0136 | 57.6243 | 0 | 7.1122 | 50.5122 | 0 | 0 | 0 | 0 | 0 | 77.0136 | 0 | 275.9921 | 21.65% | 5.455 | 0 | 5.6797 | 11.36% | 43.4
6876 | 655 | 722 | 254 | 5.8431 | 26.7 | 329.6729 | 215.0675 | 0 | 181.8032 | 107.7 | 7.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 181.8032 | 0 | 447.5387 | 35.11% | 19.175 | 0 | 25.6447 | 51.29% | 42.3
6877 | 860 | 723 | 118 | 12.2907 | 28 | 432.853 | 281.6378 | 0 | 240.1654 | 107.8 | 7.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 240.1654 | 0 | 674.155 | 52.9% | 19.175 | 0 | 45.6097 | 91.22% | 42.2
6878 | 825 | 646 | 112 | 12.8952 | 27.6 | 415.2368 | 263.7491 | 0 | 222.9649 | 108 | 27.5025 | 5.4975 | 75 | 0 | 0 | 0 | 0 | 0 | 222.9649 | 0 | 884.5412 | 69.4% | 4.2166 | 0 | 50 | 100% | 42
6879 | 262 | 298 | 147 | 18.3353 | 26.3 | 131.8692 | 79.3412 | 0 | 47.1797 | 33.3264 | 0 | 0 | 33.3264 | 0 | 0 | 0 | 0 | 0 | 47.1797 | 0 | 929.0591 | 72.9% | 0 | 8.1736 | 41.491 | 82.98% | 41.5
6880 | 590 | 336 | 99 | 21.5591 | 26.6 | 296.9573 | 158.3345 | 0 | 119.7095 | 46.0941 | 1.797 | 0 | 44.297 | 0 | 0 | 0 | 0 | 0 | 119.7095 | 0 | 1042.0151 | 81.76% | 0 | 0 | 41.491 | 82.98% | 42.5
6881 | 455 | 144 | 47 | 17.7308 | 25.3 | 229.0094 | 95.0379 | 0 | 62.5756 | 19.8278 | 0 | 0 | 19.8278 | 0 | 0 | 0 | 0 | 0 | 62.5756 | 0 | 1101.0605 | 86.39% | 0 | 24.9722 | 15.4935 | 30.99% | 44.8
6882 | 37 | 16 | 9 | 14.3056 | 23.6 | 18.6227 | 0 | 0 | 0 | 0.39203 | 0 | 0 | 0.39203 | 0 | 0 | 0 | 72.9751 | 28.0254 | 0 | 72.9751 | 1033.8812 | 81.12% | 0 | 14.8826 | 0 | 0% | 43.3
6883 | 0 | 0 | 0 | 12.8952 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6754 | 38.9 | 0 | 98.6754 | 938.0798 | 73.6% | 0 | 0 | 0 | 0% | 38.9
6884 | 0 | 0 | 0 | 13.0966 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4882 | 35.6 | 0 | 90.4882 | 851.6037 | 66.82% | 0 | 0 | 0 | 0% | 35.6
6885 | 0 | 0 | 0 | 15.9175 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3143 | 33.9 | 0 | 86.3143 | 769.9808 | 60.41% | 0 | 0 | 0 | 0% | 33.9
6886 | 0 | 0 | 0 | 13.2981 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5817 | 32.4 | 0 | 82.5817 | 692.6374 | 54.35% | 0 | 0 | 0 | 0% | 32.4
6887 | 0 | 0 | 0 | 8.6639 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7142 | 31.3 | 0 | 79.7142 | 618.3822 | 48.52% | 0 | 0 | 0 | 0% | 31.3
6888 | 0 | 0 | 0 | 7.858 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6829 | 30.9 | 0 | 78.6829 | 545.2321 | 42.78% | 0 | 0 | 0 | 0% | 30.9
6889 | 0 | 0 | 0 | 9.2684 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2143 | 30.7 | 0 | 78.2143 | 472.6255 | 37.08% | 0 | 0 | 0 | 0% | 30.7
6890 | 0 | 0 | 0 | 9.2684 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7967 | 31.4 | 0 | 79.7967 | 398.0478 | 31.23% | 0 | 0 | 0 | 0% | 31.4
6891 | 0 | 0 | 0 | 8.261 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7318 | 34.3 | 0 | 86.7318 | 315.1743 | 24.73% | 0 | 0 | 0 | 0% | 34.3
6892 | 0 | 0 | 0 | 4.8357 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0099 | 33.1971 | 0 | 84.0099 | 235.4601 | 18.47% | 0 | 0 | 0 | 0% | 33.1971
6893 | 0 | 0 | 0 | 4.2312 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235.4601 | 18.47% | 0 | 0 | 0 | 0% | 0
6894 | 0 | 0 | 0 | 4.6342 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235.4601 | 18.47% | 0 | 0 | 0 | 0% | 0
6895 | 170 | 27 | 12 | 4.4327 | 12.5 | 85.564 | 0 | 0 | 0 | 2.0458 | 0 | 0 | 2.0458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235.4601 | 18.47% | 0 | 0 | 0 | 0% | 2.0458
6896 | 688 | 206 | 43 | 3.2238 | 14.7 | 346.2824 | 153.9684 | 0 | 125.6338 | 30.5324 | 0 | 0 | 30.5324 | 0 | 0 | 0 | 0 | 0 | 125.6338 | 0 | 353.3739 | 27.73% | 0 | 0 | 0 | 0% | 30.5324
6897 | 852 | 406 | 58 | 3.0223 | 17.3 | 428.8264 | 237.0974 | 0 | 203.4944 | 69.6019 | 0 | 13.051 | 56.551 | 0 | 0 | 0 | 0 | 0 | 203.4944 | 0 | 544.3639 | 42.71% | 10.0101 | 0 | 10.424 | 20.85% | 43.5
6898 | 918 | 572 | 68 | 3.4253 | 19 | 462.0454 | 282.499 | 0 | 245.7375 | 106.0314 | 6.2657 | 25 | 74.7657 | 0 | 0 | 0 | 0 | 0 | 245.7375 | 0 | 775.0012 | 60.81% | 19.175 | 0 | 30.3918 | 60.78% | 43.5
6899 | 940 | 686 | 76 | 3.8283 | 20.5 | 473.1183 | 302.2527 | 0 | 264.1345 | 108.1 | 8.5502 | 24.5498 | 75 | 0 | 0 | 0 | 0 | 0 | 264.1345 | 0 | 1022.905 | 80.26% | 18.8297 | 0 | 50 | 100% | 41.9
6900 | 953 | 744 | 77 | 3.2238 | 21 | 479.6615 | 312.5616 | 0 | 273.9351 | 109 | 34 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 273.9351 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41
6901 | 942 | 735 | 79 | 4.2312 | 21.6 | 474.125 | 0 | 308.1805 | 0 | 109.2 | 34.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.8
6902 | 909 | 662 | 81 | 3.6268 | 22.2 | 457.5155 | 0 | 290.3905 | 0 | 109.4 | 34.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.6
6903 | 853 | 534 | 80 | 4.6342 | 22.3 | 429.3297 | 0 | 257.9251 | 0 | 99.821 | 29.8105 | 0 | 70.0105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.2
6904 | 743 | 357 | 71 | 5.6416 | 22 | 373.9648 | 0 | 198.7783 | 0 | 57.4887 | 7.8944 | 0 | 49.5944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.7
6905 | 503 | 156 | 47 | 6.4476 | 20.7 | 253.1686 | 0 | 104.4836 | 0 | 21.5051 | 0 | 0 | 21.5051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.8949 | 26.162 | 52.32% | 44.4
6906 | 25 | 12 | 8 | 4.2312 | 17.8 | 12.5829 | 0 | 0 | 0 | 0.27754 | 0 | 0 | 0.27754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 0.13096 | 0.2619% | 25.2775
6907 | 0 | 0 | 0 | 4.2312 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3635 | 39.2 | 0 | 98.3635 | 1177.8287 | 92.41% | 0 | 0 | 0.13096 | 0.2619% | 39.2
6908 | 0 | 0 | 0 | 1.8134 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.873 | 35.7 | 0 | 89.873 | 1091.0582 | 85.61% | 0 | 0 | 0.13096 | 0.2619% | 35.7
6909 | 0 | 0 | 0 | 1.6119 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2127 | 33.8 | 0 | 85.2127 | 1009.7109 | 79.22% | 0 | 0 | 0.13096 | 0.2619% | 33.8
6910 | 0 | 0 | 0 | 4.0297 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3045 | 32.2 | 0 | 81.3045 | 932.9236 | 73.2% | 0 | 0 | 0.13096 | 0.2619% | 32.2
6911 | 0 | 0 | 0 | 2.4178 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5706 | 31.1 | 0 | 78.5706 | 859.2195 | 67.42% | 0 | 0 | 0.13096 | 0.2619% | 31.1
6912 | 0 | 0 | 0 | 2.2164 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3457 | 30.6 | 0 | 77.3457 | 786.8985 | 61.74% | 0 | 0 | 0.13096 | 0.2619% | 30.6
6913 | 0 | 0 | 0 | 3.6268 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1205 | 30.5 | 0 | 77.1205 | 714.8443 | 56.09% | 0 | 0 | 0.13096 | 0.2619% | 30.5
6914 | 0 | 0 | 0 | 3.0223 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3148 | 31 | 0 | 78.3148 | 641.3863 | 50.32% | 0 | 0 | 0.13096 | 0.2619% | 31
6915 | 0 | 0 | 0 | 1.4104 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5853 | 34.1 | 0 | 85.5853 | 559.0978 | 43.87% | 0 | 0 | 0.13096 | 0.2619% | 34.1
6916 | 0 | 0 | 0 | 1.4104 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0542 | 39.3 | 0 | 98.0542 | 461.9941 | 36.25% | 0 | 0 | 0.13096 | 0.2619% | 39.3
6917 | 0 | 0 | 0 | 3.0223 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8577 | 41.7 | 0 | 103.8577 | 358.044 | 28.09% | 0 | 0 | 0.13096 | 0.2619% | 41.7
6918 | 0 | 0 | 0 | 2.2164 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.7427 | 42.5 | 0 | 105.7427 | 251.788 | 19.76% | 0 | 0 | 0.13096 | 0.2619% | 42.5
6919 | 177 | 27 | 13 | 2.8208 | 11.5 | 89.0872 | 0 | 0 | 0 | 2.1173 | 0 | 0 | 2.1173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251.788 | 19.76% | 0 | 0 | 0.13096 | 0.2619% | 2.1173
6920 | 659 | 197 | 42 | 2.2164 | 15.1 | 331.6862 | 146.3365 | 0 | 118.9831 | 29.2625 | 0 | 0 | 29.2625 | 0 | 0 | 0 | 0 | 0 | 118.9831 | 0 | 364.5229 | 28.6% | 0 | 0 | 0.13096 | 0.2619% | 29.2625
6921 | 823 | 392 | 59 | 1.8134 | 17.9 | 414.2302 | 228.0276 | 0 | 195.4381 | 65.0381 | 0 | 10.569 | 54.469 | 0 | 0 | 0 | 0 | 0 | 195.4381 | 0 | 549.6979 | 43.13% | 8.1065 | 0 | 8.5738 | 17.15% | 43.9
6922 | 918 | 563 | 63 | 2.6193 | 19.1 | 462.0454 | 281.8694 | 0 | 245.4277 | 103.6117 | 4.8558 | 25 | 73.7558 | 0 | 0 | 0 | 0 | 0 | 245.4277 | 0 | 782.2374 | 61.38% | 19.175 | 0 | 28.5445 | 57.09% | 43.9
6923 | 957 | 684 | 66 | 3.8283 | 20.6 | 481.6747 | 307.3928 | 0 | 268.9101 | 107.4 | 7.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 268.9101 | 0 | 1037.0261 | 81.37% | 19.175 | 0 | 48.5153 | 97.03% | 42.6
6924 | 966 | 741 | 69 | 3.6268 | 21.6 | 486.2046 | 316.4694 | 0 | 277.4447 | 108.1 | 33.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 277.4447 | 0 | 1274.5104 | 100% | 0 | 0 | 48.5153 | 97.03% | 41.9
6925 | 957 | 732 | 70 | 4.2312 | 22.6 | 481.6747 | 0 | 312.7718 | 0 | 108.5 | 33.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.5153 | 97.03% | 41.5
6926 | 935 | 660 | 68 | 5.6416 | 23.1 | 470.6018 | 0 | 298.4759 | 0 | 108.8 | 33.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.5153 | 97.03% | 41.2
6927 | 890 | 532 | 64 | 4.0297 | 23.7 | 447.9525 | 0 | 268.7054 | 0 | 98.6205 | 28.8602 | 0 | 69.7602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.5153 | 97.03% | 40.9
6928 | 789 | 355 | 56 | 6.8506 | 23.4 | 397.1174 | 0 | 210.4353 | 0 | 58.4779 | 7.989 | 0 | 50.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.5153 | 97.03% | 42.5
6929 | 567 | 158 | 40 | 7.858 | 21.2 | 285.381 | 0 | 117.1172 | 0 | 22.69 | 0 | 0 | 22.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.51 | 25.0747 | 50.15% | 45.2
6930 | 45 | 14 | 8 | 5.4401 | 18.9 | 22.6493 | 0 | 0 | 0 | 0.4938 | 0 | 0 | 0.4938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.0805 | 0 | 0% | 24.5743
6931 | 0 | 0 | 0 | 3.4253 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4769 | 39.6 | 0 | 99.4769 | 1176.6829 | 92.32% | 0 | 0 | 0 | 0% | 39.6
6932 | 0 | 0 | 0 | 2.2164 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.837 | 36.1 | 0 | 90.837 | 1088.7992 | 85.43% | 0 | 0 | 0 | 0% | 36.1
6933 | 0 | 0 | 0 | 1.0074 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6431 | 34.4 | 0 | 86.6431 | 1005.7218 | 78.91% | 0 | 0 | 0 | 0% | 34.4
6934 | 0 | 0 | 0 | 1.6119 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0717 | 32.5 | 0 | 82.0717 | 928.0893 | 72.82% | 0 | 0 | 0 | 0% | 32.5
6935 | 0 | 0 | 0 | 3.8283 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6095 | 31.5 | 0 | 79.6095 | 853.2698 | 66.95% | 0 | 0 | 0 | 0% | 31.5
6936 | 0 | 0 | 0 | 1.4104 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5316 | 31.1 | 0 | 78.5316 | 779.5602 | 61.17% | 0 | 0 | 0 | 0% | 31.1
6937 | 0 | 0 | 0 | 2.4178 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0668 | 30.9 | 0 | 78.0668 | 706.3978 | 55.43% | 0 | 0 | 0 | 0% | 30.9
6938 | 0 | 0 | 0 | 1.2089 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9256 | 31.3 | 0 | 78.9256 | 632.1053 | 49.6% | 0 | 0 | 0 | 0% | 31.3
6939 | 0 | 0 | 0 | 2.4178 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6742 | 34.1 | 0 | 85.6742 | 549.8222 | 43.14% | 0 | 0 | 0 | 0% | 34.1
6940 | 0 | 0 | 0 | 1.4104 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.568 | 39.1 | 0 | 97.568 | 453.301 | 35.57% | 0 | 0 | 0 | 0% | 39.1
6941 | 0 | 0 | 0 | 2.8208 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6876 | 41.6 | 0 | 103.6876 | 349.6412 | 27.43% | 0 | 0 | 0 | 0% | 41.6
6942 | 0 | 0 | 0 | 4.2312 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1595 | 36.7984 | 0 | 92.1595 | 259.6383 | 20.37% | 0 | 0 | 0 | 0% | 36.7984
6943 | 173 | 25 | 12 | 1.2089 | 10.6 | 87.0739 | 0 | 0 | 0 | 2.0492 | 0 | 0 | 2.0492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.6383 | 20.37% | 0 | 0 | 0 | 0% | 2.0492
6944 | 578 | 178 | 45 | 1.0074 | 15.4 | 290.9175 | 127.3582 | 0 | 101.4981 | 26.452 | 0 | 0 | 26.452 | 0 | 0 | 0 | 0 | 0 | 101.4981 | 0 | 355.7544 | 27.91% | 0 | 0 | 0 | 0% | 26.452
6945 | 822 | 388 | 58 | 1.4104 | 19.3 | 413.7269 | 226.7626 | 0 | 194.3956 | 63.578 | 0 | 9.689 | 53.889 | 0 | 0 | 0 | 0 | 0 | 194.3956 | 0 | 539.842 | 42.36% | 7.4315 | 0 | 7.741 | 15.48% | 44.2
6946 | 898 | 552 | 65 | 2.4178 | 21.2 | 451.979 | 275.1191 | 0 | 239.1455 | 99.6843 | 2.7422 | 25 | 71.9422 | 0 | 0 | 0 | 0 | 0 | 239.1455 | 0 | 766.3065 | 60.13% | 19.175 | 0 | 27.7146 | 55.43% | 44.2
6947 | 937 | 671 | 70 | 5.0372 | 22.4 | 471.6084 | 300.6523 | 0 | 262.2473 | 107.1 | 7.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 262.2473 | 0 | 1014.6479 | 79.61% | 19.175 | 0 | 47.6882 | 95.38% | 42.9
6948 | 947 | 728 | 73 | 4.4327 | 23.8 | 476.6416 | 309.8985 | 0 | 271.0704 | 108.2 | 30.3065 | 2.8935 | 75 | 0 | 0 | 0 | 0 | 0 | 271.0704 | 0 | 1271.3445 | 99.75% | 2.2194 | 0 | 50 | 100% | 41.8
6949 | 925 | 715 | 78 | 3.2238 | 25.1 | 465.5686 | 0 | 302.0082 | 0 | 108.2 | 33.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.3445 | 99.75% | 0 | 0 | 50 | 100% | 41.8
6950 | 829 | 621 | 97 | 2.4178 | 26.4 | 417.2501 | 0 | 264.4412 | 0 | 108.3 | 33.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.3445 | 99.75% | 0 | 0 | 50 | 100% | 41.7
6951 | 652 | 479 | 143 | 6.0446 | 26 | 328.1629 | 0 | 196.5489 | 0 | 82.6459 | 20.7229 | 0 | 61.9229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.3445 | 99.75% | 0 | 0 | 50 | 100% | 41.2
6952 | 398 | 294 | 142 | 6.0446 | 25.8 | 200.3203 | 0 | 105.8207 | 0 | 36.5076 | 0 | 0 | 36.5076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.3445 | 99.75% | 0 | 6.1924 | 43.5506 | 87.1% | 42.7
6953 | 391 | 172 | 97 | 7.455 | 24.4 | 196.7971 | 0 | 80.3035 | 0 | 21.861 | 0 | 0 | 21.861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.3445 | 99.75% | 0 | 23.139 | 19.4512 | 38.9% | 45
6954 | 29 | 15 | 10 | 5.4401 | 21.2 | 14.5962 | 0 | 0 | 0 | 0.2823 | 0 | 0 | 0.2823 | 0 | 0 | 0 | 64.751 | 24.5413 | 0 | 64.751 | 1212.0331 | 95.1% | 0 | 18.6764 | 0 | 0% | 43.5
6955 | 0 | 0 | 0 | 2.6193 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3216 | 39.5 | 0 | 99.3216 | 1114.4901 | 87.44% | 0 | 0 | 0 | 0% | 39.5
6956 | 0 | 0 | 0 | 1.0074 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4178 | 36.3 | 0 | 91.4178 | 1026.0416 | 80.5% | 0 | 0 | 0 | 0% | 36.3
6957 | 0 | 0 | 0 | 2.4178 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9861 | 34.5 | 0 | 86.9861 | 942.6698 | 73.96% | 0 | 0 | 0 | 0% | 34.5
6958 | 0 | 0 | 0 | 2.4178 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7371 | 32.7 | 0 | 82.7371 | 864.4647 | 67.83% | 0 | 0 | 0 | 0% | 32.7
6959 | 0 | 0 | 0 | 4.2312 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9392 | 31.5 | 0 | 79.9392 | 789.6412 | 61.96% | 0 | 0 | 0 | 0% | 31.5
6960 | 0 | 0 | 0 | 3.6268 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7959 | 31 | 0 | 78.7959 | 716.2064 | 56.19% | 0 | 0 | 0 | 0% | 31
6961 | 0 | 0 | 0 | 1.6119 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8883 | 30.8 | 0 | 77.8883 | 643.3179 | 50.48% | 0 | 0 | 0 | 0% | 30.8
6962 | 0 | 0 | 0 | 1.4104 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2077 | 31.3 | 0 | 79.2077 | 569.0198 | 44.65% | 0 | 0 | 0 | 0% | 31.3
6963 | 0 | 0 | 0 | 1.2089 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2175 | 34.3 | 0 | 86.2175 | 486.1494 | 38.14% | 0 | 0 | 0 | 0% | 34.3
6964 | 0 | 0 | 0 | 2.0149 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8325 | 38.7 | 0 | 96.8325 | 390.7678 | 30.66% | 0 | 0 | 0 | 0% | 38.7
6965 | 0 | 0 | 0 | 1.8134 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9737 | 37.0796 | 0 | 92.9737 | 299.982 | 23.54% | 0 | 0 | 0 | 0% | 37.0796
6966 | 0 | 0 | 0 | 3.8283 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299.982 | 23.54% | 0 | 0 | 0 | 0% | 0
6967 | 83 | 26 | 20 | 4.4327 | 14.7 | 41.7753 | 0 | 0 | 0 | 1.6145 | 0 | 0 | 1.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299.982 | 23.54% | 0 | 0 | 0 | 0% | 1.6145
6968 | 212 | 140 | 88 | 3.4253 | 16.4 | 106.7033 | 0 | 46.3529 | 0 | 16.4542 | 0 | 0 | 16.4542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299.982 | 23.54% | 0 | 0 | 0 | 0% | 16.4542
6969 | 515 | 328 | 115 | 2.0149 | 20.2 | 259.2085 | 141.4594 | 0 | 114.4053 | 42.2874 | 0 | 0 | 42.2874 | 0 | 0 | 0 | 0 | 0 | 114.4053 | 0 | 407.7902 | 32% | 0 | 0 | 0 | 0% | 42.2874
6970 | 634 | 504 | 157 | 2.6193 | 23.6 | 319.1032 | 193.8123 | 0 | 163.1621 | 82.0933 | 0 | 19.3966 | 62.6966 | 0 | 0 | 0 | 0 | 0 | 163.1621 | 0 | 561.5439 | 44.06% | 14.8772 | 0 | 15.4991 | 31% | 43.3
6971 | 685 | 632 | 190 | 2.0149 | 26 | 344.7724 | 219.5648 | 0 | 187.4688 | 107.4752 | 7.7876 | 25 | 74.6876 | 0 | 0 | 0 | 0 | 0 | 187.4688 | 0 | 738.2026 | 57.92% | 19.175 | 0 | 35.4757 | 70.95% | 41.9
6972 | 505 | 578 | 225 | 2.4178 | 26.7 | 254.1753 | 165.0741 | 0 | 136.3558 | 92.1022 | 7.5245 | 18.1766 | 66.4011 | 0 | 0 | 0 | 0 | 0 | 136.3558 | 0 | 866.6957 | 68% | 13.9415 | 0 | 50 | 100% | 40.7
6973 | 714 | 673 | 182 | 6.6491 | 26.7 | 359.3686 | 232.8824 | 0 | 198.0403 | 109.9 | 34.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 198.0403 | 0 | 1053.3164 | 82.64% | 0 | 0 | 50 | 100% | 40.1
6974 | 819 | 637 | 124 | 8.8654 | 26.5 | 412.2169 | 261.0559 | 0 | 222.8252 | 110 | 35 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 222.8252 | 0 | 1263.2927 | 99.12% | 0 | 0 | 50 | 100% | 40
6975 | 629 | 489 | 161 | 10.0743 | 25.8 | 316.5866 | 0 | 189.3239 | 0 | 85.4006 | 22.8003 | 0 | 62.6003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.2927 | 99.12% | 0 | 0 | 50 | 100% | 39.8
6976 | 252 | 236 | 130 | 8.8654 | 24.5 | 126.836 | 0 | 66.7911 | 0 | 26.5958 | 0 | 0 | 26.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.2927 | 99.12% | 0 | 14.6042 | 34.7876 | 69.58% | 41.2
6977 | 12 | 68 | 66 | 6.4476 | 23 | 6.0398 | 0 | 2.4503 | 0 | 5.1534 | 0 | 0 | 5.1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.2927 | 99.12% | 0 | 25 | 8.7457 | 17.49% | 30.1534
6978 | 3 | 8 | 8 | 4.4327 | 20.8 | 1.51 | 0 | 0 | 0 | 0.052499 | 0 | 0 | 0.052499 | 0 | 0 | 0 | 85.038 | 33.3509 | 0 | 85.038 | 1183.2383 | 92.84% | 0 | 8.3966 | 0 | 0% | 41.8
6979 | 0 | 0 | 0 | 2.6193 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9832 | 38.5 | 0 | 96.9832 | 1088.5597 | 85.41% | 0 | 0 | 0 | 0% | 38.5
6980 | 0 | 0 | 0 | 1.6119 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3371 | 35.8 | 0 | 90.3371 | 1001.5048 | 78.58% | 0 | 0 | 0 | 0% | 35.8
6981 | 0 | 0 | 0 | 2.2164 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9533 | 34 | 0 | 85.9533 | 919.5753 | 72.15% | 0 | 0 | 0 | 0% | 34
6982 | 0 | 0 | 0 | 0.80595 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4497 | 32.2 | 0 | 81.4497 | 842.7829 | 66.13% | 0 | 0 | 0 | 0% | 32.2
6983 | 0 | 0 | 0 | 1.8134 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8099 | 30.7 | 0 | 77.8099 | 770.1888 | 60.43% | 0 | 0 | 0 | 0% | 30.7
6984 | 0 | 0 | 0 | 2.0149 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.166 | 30 | 0 | 76.166 | 699.5238 | 54.89% | 0 | 0 | 0 | 0% | 30
6985 | 0 | 0 | 0 | 2.2164 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2944 | 29.6 | 0 | 75.2944 | 629.8287 | 49.42% | 0 | 0 | 0 | 0% | 29.6
6986 | 0 | 0 | 0 | 3.8283 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8424 | 29.4 | 0 | 74.8424 | 560.6121 | 43.99% | 0 | 0 | 0 | 0% | 29.4
6987 | 0 | 0 | 0 | 1.6119 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5426 | 30.2 | 0 | 76.5426 | 489.3578 | 38.4% | 0 | 0 | 0 | 0% | 30.2
6988 | 0 | 0 | 0 | 2.4178 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3215 | 31.8 | 0 | 80.3215 | 413.6177 | 32.45% | 0 | 0 | 0 | 0% | 31.8
6989 | 0 | 0 | 0 | 3.0223 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5174 | 28.3884 | 0 | 72.5174 | 346.6935 | 27.2% | 0 | 0 | 0 | 0% | 28.3884
6990 | 0 | 0 | 0 | 1.8134 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346.6935 | 27.2% | 0 | 0 | 0 | 0% | 0
6991 | 154 | 22 | 10 | 1.4104 | 13.4 | 77.5109 | 0 | 0 | 0 | 1.6759 | 0 | 0 | 1.6759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346.6935 | 27.2% | 0 | 0 | 0 | 0% | 1.6759
6992 | 639 | 181 | 38 | 1.6119 | 16.6 | 321.6198 | 138.6422 | 0 | 111.852 | 28.0091 | 0 | 0 | 28.0091 | 0 | 0 | 0 | 0 | 0 | 111.852 | 0 | 451.1585 | 35.4% | 0 | 0 | 0 | 0% | 28.0091
6993 | 784 | 363 | 55 | 1.2089 | 20.4 | 394.6008 | 214.427 | 0 | 182.9283 | 63.5363 | 0 | 12.2681 | 51.2681 | 0 | 0 | 0 | 0 | 0 | 182.9283 | 0 | 622.0058 | 48.8% | 9.4097 | 0 | 9.8044 | 19.61% | 39
6994 | 881 | 532 | 59 | 2.2164 | 22.6 | 443.4226 | 268.7354 | 0 | 233.2249 | 100.4399 | 5.6699 | 25 | 69.7699 | 0 | 0 | 0 | 0 | 0 | 233.2249 | 0 | 839.8279 | 65.89% | 19.175 | 0 | 29.7839 | 59.57% | 39.1
6995 | 926 | 651 | 63 | 5.4401 | 23.9 | 466.0719 | 296.5067 | 0 | 258.1859 | 111.7 | 11.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 258.1859 | 0 | 1080.9626 | 84.81% | 19.175 | 0 | 49.7634 | 99.53% | 38.3
6996 | 926 | 709 | 75 | 8.8654 | 24.9 | 466.0719 | 302.3567 | 0 | 261.5647 | 113.6 | 38.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 261.5647 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7634 | 99.53% | 36.4
6997 | 804 | 665 | 117 | 10.4773 | 25 | 404.6672 | 0 | 261.9729 | 0 | 114.6 | 39.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7634 | 99.53% | 35.4
6998 | 330 | 436 | 225 | 11.4848 | 25.6 | 166.0947 | 0 | 105.1081 | 0 | 64.5593 | 14.6796 | 0 | 49.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7634 | 99.53% | 35.2
6999 | 355 | 372 | 189 | 13.4996 | 25.1 | 178.6777 | 0 | 106.6866 | 0 | 53.5127 | 9.1063 | 0 | 44.4063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.7634 | 99.53% | 35.3
7000 | 231 | 234 | 142 | 8.6639 | 25.1 | 116.2663 | 0 | 61.0303 | 0 | 26.5917 | 0 | 0 | 26.5917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 10.6083 | 38.7118 | 77.42% | 37.2
7001 | 150 | 122 | 90 | 8.261 | 24.2 | 75.4976 | 0 | 30.4494 | 0 | 12.9617 | 0 | 0 | 12.9617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 12.6662 | 25.33% | 37.9617
7002 | 5 | 8 | 7 | 3.6268 | 21.9 | 2.5166 | 0 | 0 | 0 | 0.0066541 | 0 | 0 | 0.0066541 | 0 | 0 | 0 | 69.3815 | 26.535 | 0 | 69.3815 | 1210.7452 | 95% | 0 | 12.1583 | 0 | 0% | 38.7
7003 | 0 | 0 | 0 | 7.858 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.234 | 35.9 | 0 | 91.234 | 1123.4063 | 88.14% | 0 | 0 | 0 | 0% | 35.9
7004 | 0 | 0 | 0 | 6.0446 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7381 | 33.7 | 0 | 85.7381 | 1042.339 | 81.78% | 0 | 0 | 0 | 0% | 33.7
7005 | 0 | 0 | 0 | 5.6416 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5684 | 31.6 | 0 | 80.5684 | 967.2186 | 75.89% | 0 | 0 | 0 | 0% | 31.6
7006 | 0 | 0 | 0 | 10.0743 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.4132 | 29.8 | 0 | 76.4132 | 896.6356 | 70.35% | 0 | 0 | 0 | 0% | 29.8
7007 | 0 | 0 | 0 | 14.1041 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.8272 | 28.6 | 0 | 73.8272 | 828.5461 | 65.01% | 0 | 0 | 0 | 0% | 28.6
7008 | 0 | 0 | 0 | 17.5294 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.7954 | 27.7 | 0 | 71.7954 | 762.404 | 59.82% | 0 | 0 | 0 | 0% | 27.7
7009 | 0 | 0 | 0 | 15.9175 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.6719 | 27.2 | 0 | 70.6719 | 697.3325 | 54.71% | 0 | 0 | 0 | 0% | 27.2
7010 | 0 | 0 | 0 | 11.2833 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.6109 | 27.2 | 0 | 70.6109 | 632.3069 | 49.61% | 0 | 0 | 0 | 0% | 27.2
7011 | 0 | 0 | 0 | 9.0669 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.7029 | 27.7 | 0 | 71.7029 | 566.2185 | 44.43% | 0 | 0 | 0 | 0% | 27.7
7012 | 0 | 0 | 0 | 12.2907 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6944 | 28.6 | 0 | 73.6944 | 498.1972 | 39.09% | 0 | 0 | 0 | 0% | 28.6
7013 | 0 | 0 | 0 | 13.7011 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6883 | 29.2 | 0 | 74.6883 | 429.187 | 33.67% | 0 | 0 | 0 | 0% | 29.2
7014 | 0 | 0 | 0 | 7.2535 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7892 | 31.1 | 0 | 78.7892 | 355.3756 | 27.88% | 0 | 0 | 0 | 0% | 31.1
7015 | 2 | 6 | 6 | 7.2535 | 14.5 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3756 | 27.88% | 0 | 0 | 0 | 0% | 0
7016 | 0 | 30 | 30 | 7.455 | 13.2 | 0 | 0 | 0 | 0 | 1.8355 | 0 | 0 | 1.8355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3756 | 27.88% | 0 | 0 | 0 | 0% | 1.8355
7017 | 0 | 137 | 137 | 3.2238 | 13.2 | 0 | 0 | 0 | 0 | 10.9437 | 0 | 0 | 10.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3756 | 27.88% | 0 | 0 | 0 | 0% | 10.9437
7018 | 0 | 96 | 95 | 5.0372 | 14.6 | 0 | 0 | 0 | 0 | 6.8722 | 0 | 0 | 6.8722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3756 | 27.88% | 0 | 0 | 0 | 0% | 6.8722
7019 | 0 | 136 | 134 | 3.8283 | 14.9 | 0 | 0 | 0 | 0 | 10.0251 | 0 | 0 | 10.0251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3756 | 27.88% | 0 | 0 | 0 | 0% | 10.0251
7020 | 1 | 213 | 210 | 6.0446 | 15.6 | 0.50332 | 0 | 0.32616 | 0 | 16.6604 | 0 | 0 | 16.6604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3756 | 27.88% | 0 | 0 | 0 | 0% | 16.6604
7021 | 10 | 269 | 258 | 7.455 | 16 | 5.0332 | 0 | 3.2551 | 0 | 21.9246 | 0 | 0 | 21.9246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3756 | 27.88% | 0 | 0 | 0 | 0% | 21.9246
7022 | 424 | 515 | 249 | 7.6565 | 17.4 | 213.4066 | 134.9458 | 0 | 105.5471 | 90.5283 | 4.3642 | 25 | 61.1642 | 0 | 0 | 0 | 0 | 0 | 105.5471 | 0 | 453.0692 | 35.55% | 19.175 | 0 | 19.9826 | 39.97% | 31.8
7023 | 282 | 404 | 252 | 10.0743 | 18.4 | 141.9355 | 84.6161 | 0 | 57.0686 | 60.1938 | 0 | 13.9469 | 46.2469 | 0 | 0 | 0 | 0 | 0 | 57.0686 | 0 | 505.8914 | 39.69% | 10.6973 | 0 | 31.1304 | 62.26% | 32.3
7024 | 582 | 347 | 142 | 8.0595 | 19.3 | 292.9307 | 153.2699 | 0 | 122.5691 | 60.7111 | 0 | 13.0055 | 47.7055 | 0 | 0 | 0 | 0 | 0 | 122.5691 | 0 | 619.3405 | 48.59% | 9.9752 | 0 | 41.5257 | 83.05% | 34.7
7025 | 298 | 121 | 66 | 6.4476 | 18.2 | 149.9886 | 60.1329 | 0 | 36.577 | 16.4009 | 0 | 0 | 16.4009 | 0 | 0 | 0 | 0 | 0 | 36.577 | 0 | 653.1959 | 51.25% | 0 | 21.5991 | 19.0206 | 38.04% | 38
7026 | 38 | 13 | 9 | 3.0223 | 16.7 | 19.1261 | 0 | 0 | 0 | 0.25951 | 0 | 0 | 0.25951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653.1959 | 51.25% | 0 | 18.2547 | 0 | 0% | 18.5142
7027 | 0 | 0 | 0 | 5.6416 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6408 | 35.6 | 0 | 89.6408 | 566.5346 | 44.45% | 0 | 0 | 0 | 0% | 35.6
7028 | 0 | 0 | 0 | 1.8134 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9356 | 33.3 | 0 | 83.9356 | 486.4649 | 38.17% | 0 | 0 | 0 | 0% | 33.3
7029 | 0 | 0 | 0 | 2.2164 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3536 | 31 | 0 | 78.3536 | 412.9001 | 32.4% | 0 | 0 | 0 | 0% | 31
7030 | 0 | 0 | 0 | 1.8134 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.7376 | 24.1322 | 0 | 62.7376 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 24.1322
7031 | 0 | 0 | 0 | 4.4327 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 0
7032 | 0 | 0 | 0 | 5.2387 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 0
7033 | 0 | 0 | 0 | 3.2238 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 0
7034 | 0 | 0 | 0 | 4.4327 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 0
7035 | 0 | 0 | 0 | 4.0297 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 0
7036 | 0 | 0 | 0 | 4.2312 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 0
7037 | 0 | 0 | 0 | 2.4178 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 0
7038 | 0 | 0 | 0 | 1.8134 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 0
7039 | 19 | 11 | 9 | 1.8134 | 8.8 | 9.563 | 0 | 0 | 0 | 0.28762 | 0 | 0 | 0.28762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355.3231 | 27.88% | 0 | 0 | 0 | 0% | 0.28762
7040 | 492 | 161 | 55 | 2.6193 | 11.8 | 247.6322 | 105.1263 | 0 | 79.9827 | 24.9958 | 0 | 0 | 24.9958 | 0 | 0 | 0 | 0 | 0 | 79.9827 | 0 | 429.5597 | 33.7% | 0 | 0 | 0 | 0% | 24.9958
7041 | 330 | 231 | 101 | 1.6119 | 13.4 | 166.0947 | 89.4954 | 0 | 66.0507 | 31.0265 | 0 | 0 | 31.0265 | 0 | 0 | 0 | 0 | 0 | 66.0507 | 0 | 490.8652 | 38.51% | 0 | 0 | 0 | 0% | 31.0265
7042 | 169 | 285 | 192 | 2.4178 | 14.1 | 85.0606 | 0 | 51.3308 | 0 | 30.8746 | 0 | 0 | 30.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490.8652 | 38.51% | 0 | 0 | 0 | 0% | 30.8746
7043 | 93 | 338 | 275 | 1.6119 | 15.6 | 46.8085 | 0 | 29.7182 | 0 | 32.386 | 0 | 0 | 32.386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490.8652 | 38.51% | 0 | 0 | 0 | 0% | 32.386
7044 | 108 | 351 | 273 | 1.6119 | 16.5 | 54.3583 | 0 | 35.1872 | 0 | 35.3209 | 0 | 0 | 35.3209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 490.8652 | 38.51% | 0 | 0 | 0 | 0% | 35.3209
7045 | 263 | 549 | 363 | 2.4178 | 17.6 | 132.3725 | 85.5227 | 0 | 61.9449 | 74.7694 | 0 | 17.0847 | 57.6847 | 0 | 0 | 0 | 0 | 0 | 61.9449 | 0 | 548.3599 | 43.03% | 13.104 | 0 | 13.6576 | 27.32% | 40.6
7046 | 14 | 383 | 369 | 1.4104 | 18.4 | 7.0464 | 0 | 4.4523 | 0 | 32.7558 | 0 | 0 | 32.7558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548.3599 | 43.03% | 0 | 7.8442 | 5.4833 | 10.97% | 40.6
7047 | 4 | 254 | 250 | 2.8208 | 18.3 | 2.0133 | 0 | 1.1983 | 0 | 21.2633 | 0 | 0 | 21.2633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 548.3599 | 43.03% | 0 | 5.2619 | 0 | 0% | 26.5252
7048 | 28 | 200 | 188 | 9.0669 | 17.4 | 14.0929 | 0 | 7.3498 | 0 | 17.8966 | 0 | 0 | 17.8966 | 0 | 0 | 0 | 64.8337 | 24.8034 | 0 | 64.8337 | 488.69 | 38.34% | 0 | 0 | 0 | 0% | 42.7
7049 | 44 | 87 | 80 | 8.6639 | 16.2 | 22.146 | 0 | 8.8251 | 0 | 8.4159 | 0 | 0 | 8.4159 | 0 | 0 | 0 | 92.5839 | 36.7841 | 0 | 92.5839 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 45.2
7050 | 16 | 9 | 8 | 6.0446 | 15.2 | 8.0531 | 0 | 0 | 0 | 0.11513 | 0 | 0 | 0.11513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0.11513
7051 | 0 | 0 | 0 | 5.8431 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7052 | 0 | 0 | 0 | 5.8431 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7053 | 0 | 0 | 0 | 3.4253 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7054 | 0 | 0 | 0 | 4.0297 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7055 | 0 | 0 | 0 | 3.0223 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7056 | 0 | 0 | 0 | 2.4178 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7057 | 0 | 0 | 0 | 4.4327 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7058 | 0 | 0 | 0 | 2.8208 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7059 | 0 | 0 | 0 | 3.2238 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7060 | 0 | 0 | 0 | 2.8208 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7061 | 0 | 0 | 0 | 3.4253 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7062 | 0 | 0 | 0 | 3.6268 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7063 | 0 | 1 | 2 | 3.6268 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7064 | 0 | 6 | 6 | 3.6268 | 11.1 | 0 | 0 | 0 | 0 | 0.048029 | 0 | 0 | 0.048029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0.048029
7065 | 0 | 24 | 24 | 5.4401 | 10.8 | 0 | 0 | 0 | 0 | 1.4007 | 0 | 0 | 1.4007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 1.4007
7066 | 0 | 45 | 45 | 7.2535 | 10.4 | 0 | 0 | 0 | 0 | 3.0077 | 0 | 0 | 3.0077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 3.0077
7067 | 0 | 93 | 92 | 5.4401 | 10.8 | 0 | 0 | 0 | 0 | 6.6602 | 0 | 0 | 6.6602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 6.6602
7068 | 0 | 89 | 88 | 4.0297 | 11.2 | 0 | 0 | 0 | 0 | 6.3097 | 0 | 0 | 6.3097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 6.3097
7069 | 0 | 126 | 125 | 3.6268 | 11.5 | 0 | 0 | 0 | 0 | 9.3504 | 0 | 0 | 9.3504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 9.3504
7070 | 0 | 71 | 71 | 2.2164 | 11.4 | 0 | 0 | 0 | 0 | 4.9895 | 0 | 0 | 4.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 4.9895
7071 | 0 | 59 | 59 | 2.8208 | 11.3 | 0 | 0 | 0 | 0 | 4.09 | 0 | 0 | 4.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 4.09
7072 | 0 | 40 | 40 | 1.8134 | 11 | 0 | 0 | 0 | 0 | 2.6392 | 0 | 0 | 2.6392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 2.6392
7073 | 0 | 8 | 9 | 5.8431 | 10.9 | 0 | 0 | 0 | 0 | 0.25947 | 0 | 0 | 0.25947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0.25947
7074 | 0 | 0 | 0 | 3.6268 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7075 | 0 | 0 | 0 | 2.6193 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7076 | 0 | 0 | 0 | 4.4327 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7077 | 0 | 0 | 0 | 3.4253 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7078 | 0 | 0 | 0 | 2.6193 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7079 | 0 | 0 | 0 | 1.4104 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7080 | 0 | 0 | 0 | 1.4104 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7081 | 0 | 0 | 0 | 2.8208 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7082 | 0 | 0 | 0 | 1.8134 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7083 | 0 | 0 | 0 | 1.6119 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7084 | 0 | 0 | 0 | 2.4178 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7085 | 0 | 0 | 0 | 2.6193 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7086 | 0 | 0 | 0 | 1.8134 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0
7087 | 53 | 14 | 10 | 3.6268 | 8.3 | 26.6758 | 0 | 0 | 0 | 0.84876 | 0 | 0 | 0.84876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398.4878 | 31.27% | 0 | 0 | 0 | 0% | 0.84876
7088 | 513 | 159 | 50 | 2.4178 | 10.8 | 258.2018 | 107.9664 | 0 | 82.7418 | 25.3965 | 0 | 0 | 25.3965 | 0 | 0 | 0 | 0 | 0 | 82.7418 | 0 | 475.422 | 37.3% | 0 | 0 | 0 | 0% | 25.3965
7089 | 734 | 357 | 78 | 3.8283 | 13.3 | 369.435 | 197.4126 | 0 | 166.0294 | 61.3533 | 0 | 7.7767 | 53.5767 | 0 | 0 | 0 | 0 | 0 | 166.0294 | 0 | 629.7979 | 49.41% | 5.9647 | 0 | 6.2174 | 12.43% | 45.8
7090 | 712 | 539 | 170 | 8.0595 | 14.1 | 358.362 | 215.3553 | 0 | 180.4982 | 101.2135 | 2.8067 | 25 | 73.4067 | 0 | 0 | 0 | 0 | 0 | 180.4982 | 0 | 797.6271 | 62.58% | 19.175 | 0 | 26.2046 | 52.41% | 45.6
7091 | 613 | 562 | 178 | 9.2684 | 14.8 | 308.5336 | 195.4949 | 0 | 161.1897 | 103.9658 | 4.8329 | 25 | 74.1329 | 0 | 0 | 0 | 0 | 0 | 161.1897 | 0 | 947.503 | 74.34% | 19.175 | 0 | 46.1919 | 92.38% | 44.3
7092 | 886 | 707 | 118 | 10.6788 | 16.3 | 445.9392 | 288.0459 | 0 | 246.8845 | 106.7 | 26.9369 | 4.7631 | 75 | 0 | 0 | 0 | 0 | 0 | 246.8845 | 0 | 1177.0588 | 92.35% | 3.6533 | 0 | 50 | 100% | 43.3
7093 | 771 | 669 | 158 | 10.2758 | 17.1 | 388.0577 | 250.2128 | 0 | 211.6535 | 107.4 | 32.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 211.6535 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.6
7094 | 199 | 360 | 233 | 7.858 | 17 | 100.1602 | 0 | 63.1776 | 0 | 39.1988 | 0 | 0 | 39.1988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 3.3012 | 46.5594 | 93.12% | 42.5
7095 | 9 | 181 | 175 | 9.6714 | 16.5 | 4.5299 | 0 | 2.6875 | 0 | 14.7176 | 0 | 0 | 14.7176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 20.5042 | 41.01% | 39.7176
7096 | 1 | 53 | 53 | 13.2981 | 15.1 | 0.50332 | 0 | 0.26077 | 0 | 3.6678 | 0 | 0 | 3.6678 | 0 | 0 | 0 | 56.4236 | 21.2581 | 0 | 56.4236 | 1222.9931 | 95.96% | 0 | 19.6741 | 0 | 0% | 44.6
7097 | 0 | 16 | 16 | 4.8357 | 14.1 | 0 | 0 | 0 | 0 | 0.75672 | 0 | 0 | 0.75672 | 0 | 0 | 0 | 114.7978 | 46.1433 | 0 | 114.7978 | 1106.0276 | 86.78% | 0 | 0 | 0 | 0% | 46.9
7098 | 0 | 1 | 1 | 5.2387 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.6411 | 45.3 | 0 | 112.6411 | 991.4764 | 77.79% | 0 | 0 | 0 | 0% | 45.3
7099 | 0 | 0 | 0 | 5.0372 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5216 | 41.1 | 0 | 102.5216 | 888.9753 | 69.75% | 0 | 0 | 0 | 0% | 41.1
7100 | 0 | 0 | 0 | 4.2312 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.3639 | 37.7 | 0 | 94.3639 | 796.1967 | 62.47% | 0 | 0 | 0 | 0% | 37.7
7101 | 0 | 0 | 0 | 5.4401 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8367 | 35 | 0 | 87.8367 | 711.0241 | 55.79% | 0 | 0 | 0 | 0% | 35
7102 | 0 | 0 | 0 | 8.261 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.112 | 33 | 0 | 83.112 | 631.6456 | 49.56% | 0 | 0 | 0 | 0% | 33
7103 | 0 | 0 | 0 | 10.2758 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.242 | 31.8 | 0 | 80.242 | 555.6738 | 43.6% | 0 | 0 | 0 | 0% | 31.8
7104 | 0 | 0 | 0 | 10.8803 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8107 | 31.2 | 0 | 78.8107 | 481.3806 | 37.77% | 0 | 0 | 0 | 0% | 31.2
7105 | 0 | 0 | 0 | 6.6491 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5628 | 31.1 | 0 | 78.5628 | 407.3532 | 31.96% | 0 | 0 | 0 | 0% | 31.1
7106 | 0 | 0 | 0 | 4.4327 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9232 | 31.7 | 0 | 79.9232 | 331.617 | 26.02% | 0 | 0 | 0 | 0% | 31.7
7107 | 0 | 0 | 0 | 6.8506 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.9917 | 27.3422 | 0 | 69.9917 | 266.8808 | 20.94% | 0 | 0 | 0 | 0% | 27.3422
7108 | 0 | 0 | 0 | 8.4625 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266.8808 | 20.94% | 0 | 0 | 0 | 0% | 0
7109 | 0 | 0 | 0 | 9.2684 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266.8808 | 20.94% | 0 | 0 | 0 | 0% | 0
7110 | 0 | 0 | 0 | 4.6342 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266.8808 | 20.94% | 0 | 0 | 0 | 0% | 0
7111 | 75 | 17 | 10 | 2.8208 | 11.3 | 37.7488 | 0 | 0 | 0 | 0.94109 | 0 | 0 | 0.94109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266.8808 | 20.94% | 0 | 0 | 0 | 0% | 0.94109
7112 | 595 | 169 | 46 | 3.0223 | 12.4 | 299.4738 | 124.2894 | 0 | 97.9191 | 27.7713 | 0 | 0 | 27.7713 | 0 | 0 | 0 | 0 | 0 | 97.9191 | 0 | 359.6132 | 28.22% | 0 | 0 | 0 | 0% | 27.7713
7113 | 788 | 361 | 65 | 2.0149 | 16 | 396.6141 | 211.0712 | 0 | 179.5071 | 63.1669 | 0 | 9.0835 | 54.0835 | 0 | 0 | 0 | 0 | 0 | 179.5071 | 0 | 529.6121 | 41.55% | 6.967 | 0 | 7.2632 | 14.53% | 45
7114 | 888 | 517 | 60 | 2.0149 | 17.5 | 446.9458 | 268.0385 | 0 | 232.6161 | 98.4383 | 2.0192 | 25 | 71.4192 | 0 | 0 | 0 | 0 | 0 | 232.6161 | 0 | 749.9068 | 58.84% | 19.175 | 0 | 27.2534 | 54.51% | 44.4
7115 | 933 | 633 | 62 | 4.2312 | 18.5 | 469.5951 | 297.2567 | 0 | 259.3396 | 107 | 7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 259.3396 | 0 | 995.5095 | 78.11% | 19.175 | 0 | 47.2437 | 94.49% | 43
7116 | 949 | 691 | 65 | 2.4178 | 19.3 | 477.6482 | 308.2006 | 0 | 270.1445 | 107.9 | 29.4529 | 3.4471 | 75 | 0 | 0 | 0 | 0 | 0 | 270.1445 | 0 | 1251.3449 | 98.18% | 2.6439 | 0 | 50 | 100% | 42.1
7117 | 943 | 682 | 67 | 5.4401 | 20.1 | 474.6283 | 0 | 305.7268 | 0 | 108.3 | 33.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.3449 | 98.18% | 0 | 0 | 50 | 100% | 41.7
7118 | 921 | 611 | 63 | 7.858 | 20.6 | 463.5553 | 0 | 292.1446 | 0 | 108.7 | 33.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.3449 | 98.18% | 0 | 0 | 50 | 100% | 41.3
7119 | 874 | 486 | 59 | 7.2535 | 20.6 | 439.8994 | 0 | 260.5392 | 0 | 97.9297 | 28.4149 | 0 | 69.5149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.3449 | 98.18% | 0 | 0 | 50 | 100% | 41.1
7120 | 784 | 316 | 48 | 9.4699 | 19.7 | 394.6008 | 0 | 203.7569 | 0 | 55.2193 | 5.8596 | 0 | 49.3596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.3449 | 98.18% | 0 | 0 | 50 | 100% | 43.5
7121 | 525 | 124 | 30 | 4.6342 | 19 | 264.2416 | 0 | 103.3536 | 0 | 19.8001 | 0 | 0 | 19.8001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.3449 | 98.18% | 0 | 25 | 23.9411 | 47.88% | 44.8001
7122 | 14 | 6 | 4 | 4.0297 | 15.9 | 7.0464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.7729 | 22.2318 | 0 | 58.7729 | 1197.6993 | 93.97% | 0 | 22.9682 | 0 | 0% | 45.2
7123 | 0 | 0 | 0 | 2.8208 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.1756 | 41.3 | 0 | 103.1756 | 1094.9151 | 85.91% | 0 | 0 | 0 | 0% | 41.3
7124 | 0 | 0 | 0 | 3.2238 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6623 | 37.8 | 0 | 94.6623 | 1002.1058 | 78.63% | 0 | 0 | 0 | 0% | 37.8
7125 | 0 | 0 | 0 | 2.6193 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8598 | 35.4 | 0 | 88.8598 | 916.0506 | 71.87% | 0 | 0 | 0 | 0% | 35.4
7126 | 0 | 0 | 0 | 1.4104 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5068 | 33.2 | 0 | 83.5068 | 836.3146 | 65.62% | 0 | 0 | 0 | 0% | 33.2
7127 | 0 | 0 | 0 | 2.4178 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4259 | 31.9 | 0 | 80.4259 | 760.2672 | 59.65% | 0 | 0 | 0 | 0% | 31.9
7128 | 0 | 0 | 0 | 5.4401 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0586 | 31.3 | 0 | 79.0586 | 685.8975 | 53.82% | 0 | 0 | 0 | 0% | 31.3
7129 | 0 | 0 | 0 | 4.6342 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.276 | 31 | 0 | 78.276 | 612.356 | 48.05% | 0 | 0 | 0 | 0% | 31
7130 | 0 | 0 | 0 | 3.8283 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4992 | 31.5 | 0 | 79.4992 | 537.3989 | 42.17% | 0 | 0 | 0 | 0% | 31.5
7131 | 0 | 0 | 0 | 1.8134 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0125 | 34.7 | 0 | 87.0125 | 453.2521 | 35.56% | 0 | 0 | 0 | 0% | 34.7
7132 | 0 | 0 | 0 | 2.2164 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1903 | 40.2 | 0 | 100.1903 | 353.4198 | 27.73% | 0 | 0 | 0 | 0% | 40.2
7133 | 0 | 0 | 0 | 3.2238 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.1917 | 21.3381 | 0 | 56.1917 | 302.1336 | 23.71% | 0 | 0 | 0 | 0% | 21.3381
7134 | 0 | 0 | 0 | 2.0149 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.1336 | 23.71% | 0 | 0 | 0 | 0% | 0
7135 | 81 | 15 | 8 | 2.8208 | 11.4 | 40.7687 | 0 | 0 | 0 | 0.93101 | 0 | 0 | 0.93101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.1336 | 23.71% | 0 | 0 | 0 | 0% | 0.93101
7136 | 614 | 161 | 37 | 1.0074 | 13.7 | 309.0369 | 127.3082 | 0 | 101.4485 | 27.2605 | 0 | 0 | 27.2605 | 0 | 0 | 0 | 0 | 0 | 101.4485 | 0 | 397.7223 | 31.21% | 0 | 0 | 0 | 0% | 27.2605
7137 | 821 | 353 | 49 | 1.4104 | 17.2 | 413.2236 | 219.0233 | 0 | 187.136 | 62.2254 | 0 | 8.8127 | 53.4127 | 0 | 0 | 0 | 0 | 0 | 187.136 | 0 | 574.0489 | 45.04% | 6.7594 | 0 | 7.0477 | 14.1% | 44.6
7138 | 905 | 517 | 55 | 1.2089 | 20.2 | 455.5022 | 272.6171 | 0 | 237.21 | 97.1065 | 1.4532 | 25 | 70.6532 | 0 | 0 | 0 | 0 | 0 | 237.21 | 0 | 797.5571 | 62.58% | 19.175 | 0 | 27.0409 | 54.08% | 44.2
7139 | 945 | 633 | 59 | 2.8208 | 20.9 | 475.6349 | 300.7891 | 0 | 263.1294 | 107.3 | 7.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 263.1294 | 0 | 1045.4877 | 82.03% | 19.175 | 0 | 47.0341 | 94.07% | 42.7
7140 | 960 | 690 | 62 | 2.4178 | 21.6 | 483.1847 | 311.4453 | 0 | 273.1789 | 108.2 | 29.4914 | 3.7086 | 75 | 0 | 0 | 0 | 0 | 0 | 273.1789 | 0 | 1274.5104 | 100% | 2.8445 | 0 | 50 | 100% | 41.8
7141 | 956 | 682 | 62 | 3.6268 | 22.3 | 481.1714 | 0 | 309.6334 | 0 | 108.9 | 33.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
7142 | 932 | 610 | 61 | 6.2461 | 22.5 | 469.0918 | 0 | 295.3805 | 0 | 109.3 | 34.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.7
7143 | 880 | 482 | 56 | 6.4476 | 22.3 | 442.9193 | 0 | 261.8731 | 0 | 97.4555 | 28.5277 | 0 | 68.9277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 40.4
7144 | 780 | 311 | 48 | 7.455 | 21.5 | 392.5876 | 0 | 202.0335 | 0 | 54.8472 | 6.2736 | 0 | 48.5736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.3
7145 | 529 | 123 | 31 | 6.6491 | 20.1 | 266.2549 | 0 | 103.4784 | 0 | 19.9352 | 0 | 0 | 19.9352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.3648 | 24.5994 | 49.2% | 44.3
7146 | 10 | 6 | 4 | 4.6342 | 17.2 | 5.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.5964 | 0 | 0% | 23.5964
7147 | 0 | 0 | 0 | 1.2089 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4811 | 39.7 | 0 | 99.4811 | 1176.3377 | 92.3% | 0 | 0 | 0 | 0% | 39.7
7148 | 0 | 0 | 0 | 1.0074 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4031 | 36.8 | 0 | 92.4031 | 1086.4353 | 85.24% | 0 | 0 | 0 | 0% | 36.8
7149 | 0 | 0 | 0 | 1.0074 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4657 | 34.8 | 0 | 87.4657 | 1002.1463 | 78.63% | 0 | 0 | 0 | 0% | 34.8
7150 | 0 | 0 | 0 | 1.2089 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9499 | 32.5 | 0 | 81.9499 | 924.4706 | 72.54% | 0 | 0 | 0 | 0% | 32.5
7151 | 0 | 0 | 0 | 1.8134 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.842 | 30.8 | 0 | 77.842 | 851.5682 | 66.82% | 0 | 0 | 0 | 0% | 30.8
7152 | 0 | 0 | 0 | 2.0149 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.6604 | 29.9 | 0 | 75.6604 | 781.1203 | 61.29% | 0 | 0 | 0 | 0% | 29.9
7153 | 0 | 0 | 0 | 1.6119 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.973 | 29.6 | 0 | 74.973 | 711.398 | 55.82% | 0 | 0 | 0 | 0% | 29.6
7154 | 0 | 0 | 0 | 2.4178 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5728 | 29.4 | 0 | 74.5728 | 642.1551 | 50.38% | 0 | 0 | 0 | 0% | 29.4
7155 | 0 | 0 | 0 | 1.4104 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3377 | 30.2 | 0 | 76.3377 | 570.8746 | 44.79% | 0 | 0 | 0 | 0% | 30.2
7156 | 0 | 0 | 0 | 2.2164 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.402 | 31.9 | 0 | 80.402 | 494.8255 | 38.82% | 0 | 0 | 0 | 0% | 31.9
7157 | 0 | 0 | 0 | 2.4178 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.708 | 34.1 | 0 | 85.708 | 412.464 | 32.36% | 0 | 0 | 0 | 0% | 34.1
7158 | 0 | 0 | 0 | 4.2312 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9757 | 36.7 | 0 | 91.9757 | 322.6922 | 25.32% | 0 | 0 | 0 | 0% | 36.7
7159 | 76 | 14 | 7 | 4.2312 | 13.3 | 38.2521 | 0 | 0 | 0 | 0.41195 | 0 | 0 | 0.41195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322.6922 | 25.32% | 0 | 0 | 0 | 0% | 0.41195
7160 | 628 | 161 | 35 | 2.6193 | 16 | 316.0833 | 129.2545 | 0 | 102.6783 | 27.5321 | 0 | 0 | 27.5321 | 0 | 0 | 0 | 0 | 0 | 102.6783 | 0 | 419.0497 | 32.88% | 0 | 0 | 0 | 0% | 27.5321
7161 | 822 | 351 | 49 | 4.2312 | 18.4 | 413.7269 | 218.416 | 0 | 185.5743 | 69.8709 | 0 | 15.6355 | 54.2355 | 0 | 0 | 0 | 0 | 0 | 185.5743 | 0 | 593.2 | 46.54% | 11.9924 | 0 | 12.5059 | 25.01% | 38.6
7162 | 909 | 517 | 56 | 2.8208 | 21.5 | 457.5155 | 273.2755 | 0 | 237.2732 | 105.3035 | 8.3517 | 25 | 71.9517 | 0 | 0 | 0 | 0 | 0 | 237.2732 | 0 | 815.8666 | 64.01% | 19.175 | 0 | 32.502 | 65% | 38.6
7163 | 948 | 632 | 60 | 3.4253 | 22 | 477.1449 | 301.4563 | 0 | 263.5494 | 112.2 | 15.3233 | 21.8767 | 75 | 0 | 0 | 0 | 0 | 0 | 263.5494 | 0 | 1063.1918 | 83.42% | 16.7794 | 0 | 50 | 100% | 37.8
7164 | 960 | 686 | 62 | 3.0223 | 22.7 | 483.1847 | 311.1211 | 0 | 272.6768 | 113.9 | 38.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 272.6768 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.1
7165 | 952 | 676 | 62 | 2.6193 | 23.9 | 479.1582 | 0 | 308.0326 | 0 | 115 | 40 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35
7166 | 927 | 604 | 61 | 5.0372 | 24.1 | 466.5752 | 0 | 293.5441 | 0 | 115.3 | 40.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.7
7167 | 878 | 477 | 56 | 6.6491 | 24 | 441.9127 | 0 | 260.8235 | 0 | 102.0639 | 33.682 | 0 | 68.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.7
7168 | 777 | 306 | 47 | 6.4476 | 23.2 | 391.0776 | 0 | 200.5719 | 0 | 58.8765 | 11.0383 | 0 | 47.8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.8
7169 | 525 | 117 | 29 | 5.6416 | 21.9 | 264.2416 | 0 | 102.0342 | 0 | 19.3863 | 0 | 0 | 19.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 19.5137 | 29.6538 | 59.31% | 38.9
7170 | 9 | 5 | 3 | 2.4178 | 18.9 | 4.5299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 3.586 | 7.172% | 25
7171 | 0 | 0 | 0 | 2.8208 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2697 | 32.8597 | 0 | 83.2697 | 1195.8594 | 93.83% | 0 | 3.4403 | 0 | 0% | 36.3
7172 | 0 | 0 | 0 | 3.6268 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2178 | 34.2 | 0 | 86.2178 | 1113.3463 | 87.35% | 0 | 0 | 0 | 0% | 34.2
7173 | 0 | 0 | 0 | 3.8283 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.113 | 32.1 | 0 | 81.113 | 1036.8332 | 81.35% | 0 | 0 | 0 | 0% | 32.1
7174 | 0 | 0 | 0 | 3.4253 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0599 | 30 | 0 | 76.0599 | 966.1766 | 75.81% | 0 | 0 | 0 | 0% | 30
7175 | 0 | 0 | 0 | 2.0149 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8798 | 28.6 | 0 | 72.8798 | 898.9399 | 70.53% | 0 | 0 | 0 | 0% | 28.6
7176 | 0 | 0 | 0 | 1.4104 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.0489 | 27.8 | 0 | 71.0489 | 833.4761 | 65.4% | 0 | 0 | 0 | 0% | 27.8
7177 | 0 | 0 | 0 | 2.4178 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.4563 | 27.1 | 0 | 69.4563 | 769.5328 | 60.38% | 0 | 0 | 0 | 0% | 27.1
7178 | 0 | 0 | 0 | 4.0297 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.8314 | 26.8 | 0 | 68.8314 | 706.1818 | 55.41% | 0 | 0 | 0 | 0% | 26.8
7179 | 0 | 0 | 0 | 4.2312 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.3618 | 27 | 0 | 69.3618 | 642.3146 | 50.4% | 0 | 0 | 0 | 0% | 27
7180 | 0 | 0 | 0 | 3.2238 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.5675 | 27.6 | 0 | 70.5675 | 577.272 | 45.29% | 0 | 0 | 0 | 0% | 27.6
7181 | 0 | 0 | 0 | 3.8283 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1146 | 28.3 | 0 | 72.1146 | 510.7055 | 40.07% | 0 | 0 | 0 | 0% | 28.3
7182 | 0 | 0 | 0 | 4.8357 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4793 | 29.8 | 0 | 75.4793 | 440.4501 | 34.56% | 0 | 0 | 0 | 0% | 29.8
7183 | 70 | 14 | 8 | 3.2238 | 11.3 | 35.2322 | 0 | 0 | 0 | 0.4447 | 0 | 0 | 0.4447 | 0 | 0 | 0 | 81.2198 | 32.2553 | 0 | 81.2198 | 363.371 | 28.51% | 0 | 0 | 0 | 0% | 32.7
7184 | 569 | 148 | 37 | 3.6268 | 14.7 | 286.3876 | 116.2589 | 0 | 90.3469 | 25.7463 | 0 | 0 | 25.7463 | 0 | 0 | 0 | 0 | 0 | 90.3469 | 0 | 446.9921 | 35.07% | 0 | 0 | 0 | 0% | 25.7463
7185 | 795 | 343 | 53 | 4.4327 | 16.6 | 400.1373 | 210.4106 | 0 | 178.0302 | 72.2798 | 0 | 18.7899 | 53.4899 | 0 | 0 | 0 | 0 | 0 | 178.0302 | 0 | 611.769 | 48% | 14.4118 | 0 | 15.0312 | 30.06% | 34.7
7186 | 867 | 505 | 68 | 4.6342 | 18.7 | 436.3762 | 260.1362 | 0 | 224.2961 | 109.2376 | 12.3188 | 25 | 71.9188 | 0 | 0 | 0 | 0 | 0 | 224.2961 | 0 | 819.3676 | 64.29% | 19.175 | 0 | 35.0302 | 70.06% | 34.6
7187 | 906 | 617 | 73 | 4.4327 | 19.9 | 456.0056 | 287.8297 | 0 | 250.4415 | 114.8 | 21.0869 | 18.7131 | 75 | 0 | 0 | 0 | 0 | 0 | 250.4415 | 0 | 1051.1651 | 82.48% | 14.353 | 0 | 50 | 100% | 35.2
7188 | 930 | 672 | 71 | 3.2238 | 21.2 | 468.0852 | 301.0877 | 0 | 263.2696 | 115.1 | 40.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 263.2696 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.9
7189 | 925 | 663 | 70 | 2.8208 | 22.1 | 465.5686 | 0 | 299.0014 | 0 | 116.8 | 41.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.2
7190 | 808 | 567 | 96 | 4.8357 | 22.7 | 406.6804 | 0 | 255.6424 | 0 | 117.6 | 42.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.4
7191 | 540 | 405 | 155 | 7.052 | 21.5 | 271.7914 | 0 | 160.1355 | 0 | 78.7403 | 23.1201 | 0 | 55.6201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 32.5
7192 | 292 | 187 | 83 | 6.2461 | 20.6 | 146.9687 | 0 | 75.1174 | 0 | 25.3882 | 0 | 0 | 25.3882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.6118 | 39.9767 | 79.95% | 35
7193 | 340 | 99 | 45 | 5.2387 | 19 | 171.1279 | 0 | 65.6483 | 0 | 15.5141 | 0 | 0 | 15.5141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 21.9859 | 17.049 | 34.1% | 37.5
7194 | 3 | 4 | 4 | 3.4253 | 17 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.2152 | 21.9509 | 0 | 58.2152 | 1221.4539 | 95.84% | 0 | 16.3491 | 0 | 0% | 38.3
7195 | 0 | 0 | 0 | 2.6193 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2102 | 37.9 | 0 | 95.2102 | 1128.4628 | 88.54% | 0 | 0 | 0 | 0% | 37.9
7196 | 0 | 0 | 0 | 1.4104 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3284 | 35.9 | 0 | 90.3284 | 1041.106 | 81.69% | 0 | 0 | 0 | 0% | 35.9
7197 | 0 | 0 | 0 | 1.2089 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2684 | 33 | 0 | 83.2684 | 962.0299 | 75.48% | 0 | 0 | 0 | 0% | 33
7198 | 0 | 0 | 0 | 1.0074 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9038 | 30.8 | 0 | 77.9038 | 889.1503 | 69.76% | 0 | 0 | 0 | 0% | 30.8
7199 | 0 | 0 | 0 | 2.4178 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8853 | 29.5 | 0 | 74.8853 | 819.7054 | 64.32% | 0 | 0 | 0 | 0% | 29.5
7200 | 0 | 0 | 0 | 2.6193 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.11 | 28.7 | 0 | 73.11 | 752.2093 | 59.02% | 0 | 0 | 0 | 0% | 28.7
7201 | 0 | 0 | 0 | 1.2089 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.3893 | 28.4 | 0 | 72.3893 | 685.4365 | 53.78% | 0 | 0 | 0 | 0% | 28.4
7202 | 0 | 0 | 0 | 1.0074 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7698 | 28.6 | 0 | 72.7698 | 618.1637 | 48.5% | 0 | 0 | 0 | 0% | 28.6
7203 | 0 | 0 | 0 | 2.6193 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1843 | 29.7 | 0 | 75.1843 | 548.184 | 43.01% | 0 | 0 | 0 | 0% | 29.7
7204 | 0 | 0 | 0 | 2.8208 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4846 | 33.6 | 0 | 84.4846 | 467.297 | 36.66% | 0 | 0 | 0 | 0% | 33.6
7205 | 0 | 0 | 0 | 1.4104 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7886 | 38.3 | 0 | 95.7886 | 373.0123 | 29.27% | 0 | 0 | 0 | 0% | 38.3
7206 | 0 | 0 | 0 | 0.60446 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.0123 | 29.27% | 0 | 0 | 0 | 0% | 0
7207 | 14 | 17 | 14 | 1.6119 | 12.2 | 7.0464 | 0 | 0 | 0 | 0.45918 | 0 | 0 | 0.45918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.0123 | 29.27% | 0 | 0 | 0 | 0% | 0.45918
7208 | 177 | 151 | 103 | 0.80595 | 14.4 | 89.0872 | 0 | 35.9044 | 0 | 16.9699 | 0 | 0 | 16.9699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.0123 | 29.27% | 0 | 0 | 0 | 0% | 16.9699
7209 | 5 | 139 | 136 | 0.80595 | 15.6 | 2.5166 | 0 | 1.3182 | 0 | 11.2575 | 0 | 0 | 11.2575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.0123 | 29.27% | 0 | 0 | 0 | 0% | 11.2575
7210 | 2 | 195 | 193 | 2.2164 | 15.8 | 1.0066 | 0 | 0.59892 | 0 | 15.8501 | 0 | 0 | 15.8501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.0123 | 29.27% | 0 | 0 | 0 | 0% | 15.8501
7211 | 4 | 252 | 246 | 3.6268 | 16.8 | 2.0133 | 0 | 1.2696 | 0 | 20.5543 | 0 | 0 | 20.5543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.0123 | 29.27% | 0 | 0 | 0 | 0% | 20.5543
7212 | 17 | 319 | 304 | 4.4327 | 17.7 | 8.5564 | 0 | 5.4981 | 0 | 27.0507 | 0 | 0 | 27.0507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.0123 | 29.27% | 0 | 0 | 0 | 0% | 27.0507
7213 | 39 | 332 | 302 | 5.8431 | 18.1 | 19.6294 | 0 | 12.5942 | 0 | 31.0153 | 0 | 0 | 31.0153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373.0123 | 29.27% | 0 | 0 | 0 | 0% | 31.0153
7214 | 787 | 607 | 145 | 4.8357 | 19.8 | 396.1108 | 248.7852 | 0 | 213.68 | 108.6 | 8.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 213.68 | 0 | 572.4682 | 44.92% | 19.175 | 0 | 20.0021 | 40% | 41.4
7215 | 786 | 453 | 76 | 4.4327 | 21 | 395.6075 | 232.6783 | 0 | 198.9316 | 87.7849 | 0 | 23.1424 | 64.6424 | 0 | 0 | 0 | 0 | 0 | 198.9316 | 0 | 758.1575 | 59.49% | 17.7503 | 0 | 38.5181 | 77.04% | 41.5
7216 | 659 | 282 | 63 | 5.0372 | 21 | 331.6862 | 168.943 | 0 | 139.0578 | 43.9694 | 0.18472 | 0 | 43.7847 | 0 | 0 | 0 | 0 | 0 | 139.0578 | 0 | 887.9587 | 69.67% | 0 | 0 | 38.5181 | 77.04% | 43.6
7217 | 332 | 94 | 36 | 5.2387 | 19.2 | 167.1014 | 63.6805 | 0 | 40.33 | 14.4025 | 0 | 0 | 14.4025 | 0 | 0 | 0 | 0 | 0 | 40.33 | 0 | 925.604 | 72.62% | 0 | 25 | 12.4438 | 24.89% | 39.4025
7218 | 1 | 2 | 2 | 4.6342 | 16.7 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9541 | 33.5689 | 0 | 84.9541 | 844.8577 | 66.29% | 0 | 11.9311 | 0 | 0% | 45.5
7219 | 0 | 0 | 0 | 1.8134 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8195 | 43.6 | 0 | 108.8195 | 735.5203 | 57.71% | 0 | 0 | 0 | 0% | 43.6
7220 | 0 | 0 | 0 | 0.60446 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4284 | 39.3 | 0 | 98.4284 | 638.4159 | 50.09% | 0 | 0 | 0 | 0% | 39.3
7221 | 0 | 0 | 0 | 0.80595 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3819 | 36 | 0 | 90.3819 | 550.6817 | 43.21% | 0 | 0 | 0 | 0% | 36
7222 | 0 | 0 | 0 | 1.6119 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0697 | 33.8 | 0 | 85.0697 | 469.215 | 36.82% | 0 | 0 | 0 | 0% | 33.8
7223 | 0 | 0 | 0 | 1.6119 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.224 | 32.2 | 0 | 81.224 | 392.31 | 30.78% | 0 | 0 | 0 | 0% | 32.2
7224 | 0 | 0 | 0 | 1.4104 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7662 | 24.9961 | 0 | 64.7662 | 332.7945 | 26.11% | 0 | 0 | 0 | 0% | 24.9961
7225 | 0 | 0 | 0 | 0.60446 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.7945 | 26.11% | 0 | 0 | 0 | 0% | 0
7226 | 0 | 0 | 0 | 0.60446 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.7945 | 26.11% | 0 | 0 | 0 | 0% | 0
7227 | 0 | 0 | 0 | 1.2089 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.7945 | 26.11% | 0 | 0 | 0 | 0% | 0
7228 | 0 | 0 | 0 | 2.8208 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.7945 | 26.11% | 0 | 0 | 0 | 0% | 0
7229 | 0 | 0 | 0 | 1.6119 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.7945 | 26.11% | 0 | 0 | 0 | 0% | 0
7230 | 0 | 0 | 0 | 1.4104 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.7945 | 26.11% | 0 | 0 | 0 | 0% | 0
7231 | 30 | 10 | 7 | 2.6193 | 12.1 | 15.0995 | 0 | 0 | 0 | 0.15272 | 0 | 0 | 0.15272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.7945 | 26.11% | 0 | 0 | 0 | 0% | 0.15272
7232 | 531 | 142 | 38 | 3.0223 | 16 | 267.2615 | 106.9455 | 0 | 81.5877 | 24.2435 | 0 | 0 | 24.2435 | 0 | 0 | 0 | 0 | 0 | 81.5877 | 0 | 409.7274 | 32.15% | 0 | 0 | 0 | 0% | 24.2435
7233 | 760 | 328 | 56 | 1.6119 | 18.2 | 382.5212 | 199.6 | 0 | 168.9267 | 58.2294 | 0 | 7.2147 | 51.0147 | 0 | 0 | 0 | 0 | 0 | 168.9267 | 0 | 569.0164 | 44.65% | 5.5337 | 0 | 5.773 | 11.55% | 43.8
7234 | 851 | 489 | 65 | 2.2164 | 20.2 | 428.3231 | 254.3547 | 0 | 219.7774 | 93.5965 | 0 | 24.7983 | 68.7983 | 0 | 0 | 0 | 0 | 0 | 219.7774 | 0 | 776.2549 | 60.91% | 19.0203 | 0 | 25.616 | 51.23% | 44
7235 | 898 | 605 | 71 | 4.4327 | 21.1 | 451.979 | 284.7632 | 0 | 247.5504 | 105.9 | 5.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 247.5504 | 0 | 1009.682 | 79.22% | 19.175 | 0 | 45.6205 | 91.24% | 44.1
7236 | 918 | 662 | 74 | 3.8283 | 22.8 | 462.0454 | 296.5995 | 0 | 258.9182 | 107.2 | 26.7269 | 5.4731 | 75 | 0 | 0 | 0 | 0 | 0 | 258.9182 | 0 | 1253.8282 | 98.38% | 4.1979 | 0 | 50 | 100% | 42.8
7237 | 908 | 653 | 77 | 5.0372 | 23.4 | 457.0122 | 0 | 292.9326 | 0 | 108.1 | 33.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1253.8282 | 98.38% | 0 | 0 | 50 | 100% | 41.9
7238 | 881 | 584 | 77 | 6.2461 | 23.4 | 443.4226 | 0 | 278.2624 | 0 | 108.2 | 33.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1253.8282 | 98.38% | 0 | 0 | 50 | 100% | 41.8
7239 | 779 | 447 | 80 | 4.6342 | 23.6 | 392.0842 | 0 | 230.2018 | 0 | 85.907 | 21.9035 | 0 | 64.0035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1253.8282 | 98.38% | 0 | 0 | 50 | 100% | 42.1
7240 | 589 | 269 | 76 | 4.6342 | 23.2 | 296.4539 | 0 | 150.4722 | 0 | 40.9486 | 0 | 0 | 40.9486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1253.8282 | 98.38% | 0 | 3.0514 | 46.8171 | 93.63% | 44
7241 | 314 | 95 | 43 | 5.4401 | 20.7 | 158.0417 | 0 | 59.8258 | 0 | 14.0561 | 0 | 0 | 14.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1253.8282 | 98.38% | 0 | 25 | 20.7395 | 41.48% | 39.0561
7242 | 2 | 3 | 3 | 3.2238 | 17.5 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.4747 | 25.5174 | 0 | 66.4747 | 1192.7836 | 93.59% | 0 | 19.8826 | 0 | 0% | 45.4
7243 | 0 | 0 | 0 | 1.0074 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1759 | 43.7 | 0 | 109.1759 | 1083.1974 | 84.99% | 0 | 0 | 0 | 0% | 43.7
7244 | 0 | 0 | 0 | 0.40297 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4909 | 39.7 | 0 | 99.4909 | 984.9746 | 77.28% | 0 | 0 | 0 | 0% | 39.7
7245 | 0 | 0 | 0 | 1.8134 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2915 | 36.3 | 0 | 91.2915 | 896.4343 | 70.34% | 0 | 0 | 0 | 0% | 36.3
7246 | 0 | 0 | 0 | 2.8208 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9453 | 34.1 | 0 | 85.9453 | 814.1372 | 63.88% | 0 | 0 | 0 | 0% | 34.1
7247 | 0 | 0 | 0 | 3.8283 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.02 | 32.4 | 0 | 82.02 | 736.7043 | 57.8% | 0 | 0 | 0 | 0% | 32.4
7248 | 0 | 0 | 0 | 3.8283 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2864 | 31.3 | 0 | 79.2864 | 662.364 | 51.97% | 0 | 0 | 0 | 0% | 31.3
7249 | 0 | 0 | 0 | 0.80595 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9192 | 30.8 | 0 | 77.9192 | 589.4098 | 46.25% | 0 | 0 | 0 | 0% | 30.8
7250 | 0 | 0 | 0 | 4.0297 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9889 | 30.8 | 0 | 77.9889 | 516.4426 | 40.52% | 0 | 0 | 0 | 0% | 30.8
7251 | 0 | 0 | 0 | 4.2312 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6885 | 31.5 | 0 | 79.6885 | 441.5001 | 34.64% | 0 | 0 | 0 | 0% | 31.5
7252 | 0 | 0 | 0 | 4.4327 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5654 | 31.8451 | 0 | 80.5654 | 365.5685 | 28.68% | 0 | 0 | 0 | 0% | 31.8451
7253 | 0 | 0 | 0 | 5.4401 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.5685 | 28.68% | 0 | 0 | 0 | 0% | 0
7254 | 0 | 0 | 0 | 5.4401 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.5685 | 28.68% | 0 | 0 | 0 | 0% | 0
7255 | 5 | 7 | 6 | 3.8283 | 14.6 | 2.5166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.5685 | 28.68% | 0 | 0 | 0 | 0% | 0
7256 | 236 | 120 | 68 | 3.0223 | 15.8 | 118.7829 | 0 | 47.1966 | 0 | 15.6418 | 0 | 0 | 15.6418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.5685 | 28.68% | 0 | 0 | 0 | 0% | 15.6418
7257 | 393 | 293 | 151 | 1.0074 | 19.8 | 197.8037 | 102.8253 | 0 | 78.4419 | 37.9756 | 0 | 0 | 37.9756 | 0 | 0 | 0 | 0 | 0 | 78.4419 | 0 | 439.4171 | 34.48% | 0 | 0 | 0 | 0% | 37.9756
7258 | 487 | 474 | 229 | 1.2089 | 22.2 | 245.1156 | 145.2859 | 0 | 118.3526 | 70.4029 | 0 | 13.1515 | 57.2515 | 0 | 0 | 0 | 0 | 0 | 118.3526 | 0 | 550.8393 | 43.22% | 10.0872 | 0 | 10.5251 | 21.05% | 44.1
7259 | 349 | 511 | 295 | 2.4178 | 23.1 | 175.6578 | 110.5712 | 0 | 85.3127 | 71.4529 | 0 | 13.6764 | 57.7764 | 0 | 0 | 0 | 0 | 0 | 85.3127 | 0 | 631.1564 | 49.52% | 10.4898 | 0 | 21.4703 | 42.94% | 44.1
7260 | 864 | 652 | 105 | 3.6268 | 23.9 | 434.8662 | 278.8736 | 0 | 242.291 | 107 | 7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 242.291 | 0 | 859.2596 | 67.42% | 19.175 | 0 | 41.4777 | 82.96% | 43
7261 | 707 | 609 | 162 | 3.0223 | 24.6 | 355.8454 | 227.8663 | 0 | 194.9107 | 107.6 | 21.9511 | 10.6489 | 75 | 0 | 0 | 0 | 0 | 0 | 194.9107 | 0 | 1042.757 | 81.82% | 8.1677 | 0 | 50 | 100% | 42.4
7262 | 634 | 542 | 182 | 5.8431 | 24.6 | 319.1032 | 199.8559 | 0 | 167.5653 | 100.063 | 29.0815 | 0 | 70.9815 | 0 | 0 | 0 | 0 | 0 | 167.5653 | 0 | 1200.5102 | 94.19% | 0 | 0 | 50 | 100% | 41.9
7263 | 286 | 295 | 161 | 7.455 | 23.7 | 143.9488 | 84.3672 | 0 | 58.4993 | 36.6089 | 0 | 0 | 36.6089 | 0 | 0 | 0 | 0 | 0 | 58.4993 | 0 | 1255.584 | 98.52% | 0 | 5.6911 | 44.0628 | 88.13% | 42.3
7264 | 57 | 88 | 70 | 8.0595 | 21.8 | 28.6891 | 0 | 14.5108 | 0 | 9.0516 | 0 | 0 | 9.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.584 | 98.52% | 0 | 25 | 17.9812 | 35.96% | 34.0516
7265 | 306 | 107 | 58 | 7.2535 | 21.5 | 154.0151 | 0 | 57.908 | 0 | 15.0477 | 0 | 0 | 15.0477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.584 | 98.52% | 0 | 17.2359 | 0 | 0% | 32.2836
7266 | 1 | 2 | 2 | 6.4476 | 19.5 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4199 | 44.8 | 0 | 112.4199 | 1142.8726 | 89.67% | 0 | 0 | 0 | 0% | 44.8
7267 | 0 | 0 | 0 | 4.4327 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.4399 | 43.2 | 0 | 108.4399 | 1034.7544 | 81.19% | 0 | 0 | 0 | 0% | 43.2
7268 | 0 | 0 | 0 | 1.8134 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0284 | 39.4 | 0 | 99.0284 | 937.4272 | 73.55% | 0 | 0 | 0 | 0% | 39.4
7269 | 0 | 0 | 0 | 2.0149 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2489 | 36.2 | 0 | 91.2489 | 849.1935 | 66.63% | 0 | 0 | 0 | 0% | 36.2
7270 | 0 | 0 | 0 | 3.4253 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6519 | 34.3 | 0 | 86.6519 | 766.3399 | 60.13% | 0 | 0 | 0 | 0% | 34.3
7271 | 0 | 0 | 0 | 2.4178 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8865 | 32.7 | 0 | 82.8865 | 688.0751 | 53.99% | 0 | 0 | 0 | 0% | 32.7
7272 | 0 | 0 | 0 | 2.0149 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4258 | 31.3 | 0 | 79.4258 | 613.7547 | 48.16% | 0 | 0 | 0 | 0% | 31.3
7273 | 0 | 0 | 0 | 2.6193 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4522 | 30.9 | 0 | 78.4522 | 540.5405 | 42.41% | 0 | 0 | 0 | 0% | 30.9
7274 | 0 | 0 | 0 | 3.0223 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.914 | 30.7 | 0 | 77.914 | 467.8702 | 36.71% | 0 | 0 | 0 | 0% | 30.7
7275 | 0 | 0 | 0 | 3.2238 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2685 | 31.2 | 0 | 79.2685 | 393.7878 | 30.9% | 0 | 0 | 0 | 0% | 31.2
7276 | 0 | 0 | 0 | 2.8208 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393.7878 | 30.9% | 0 | 0 | 0 | 0% | 0
7277 | 0 | 0 | 0 | 3.0223 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393.7878 | 30.9% | 0 | 0 | 0 | 0% | 0
7278 | 0 | 0 | 0 | 2.2164 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393.7878 | 30.9% | 0 | 0 | 0 | 0% | 0
7279 | 17 | 8 | 6 | 2.6193 | 15.8 | 8.5564 | 0 | 0 | 0 | 0.018486 | 0 | 0 | 0.018486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393.7878 | 30.9% | 0 | 0 | 0 | 0% | 0.018486
7280 | 483 | 133 | 43 | 2.2164 | 18.7 | 243.1023 | 95.9215 | 0 | 71.6447 | 22.8568 | 0 | 0 | 22.8568 | 0 | 0 | 0 | 0 | 0 | 71.6447 | 0 | 461.7458 | 36.23% | 0 | 0 | 0 | 0% | 22.8568
7281 | 696 | 304 | 59 | 1.4104 | 22.4 | 350.3089 | 181.4277 | 0 | 152.0207 | 50.6896 | 0 | 3.7448 | 46.9448 | 0 | 0 | 0 | 0 | 0 | 152.0207 | 0 | 605.944 | 47.54% | 2.8723 | 0 | 2.9974 | 5.995% | 43.2
7282 | 827 | 476 | 73 | 5.0372 | 24.5 | 416.2435 | 246.2627 | 0 | 211.3311 | 93.7905 | 0 | 24.9453 | 68.8453 | 0 | 0 | 0 | 0 | 0 | 211.3311 | 0 | 806.4006 | 63.27% | 19.133 | 0 | 22.9639 | 45.93% | 43.9
7283 | 820 | 580 | 100 | 6.0446 | 25.8 | 412.7203 | 259.5648 | 0 | 223.1092 | 105.9 | 5.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 223.1092 | 0 | 1018.0292 | 79.88% | 19.175 | 0 | 42.9743 | 85.95% | 44.1
7284 | 753 | 617 | 141 | 9.8729 | 26.4 | 378.998 | 242.806 | 0 | 205.2931 | 107.3 | 23.5224 | 8.7776 | 75 | 0 | 0 | 0 | 0 | 0 | 205.2931 | 0 | 1212.7585 | 95.15% | 6.7324 | 0 | 50 | 100% | 42.7
7285 | 730 | 610 | 152 | 11.4848 | 26.7 | 367.4217 | 235.0527 | 0 | 197.2235 | 108.5 | 33.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 197.2235 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.5
7286 | 638 | 598 | 228 | 10.2758 | 27.6 | 321.1165 | 0 | 200.723 | 0 | 108.9 | 33.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
7287 | 17 | 205 | 195 | 9.4699 | 26.2 | 8.5564 | 0 | 5.006 | 0 | 16.9911 | 0 | 0 | 16.9911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 24.1089 | 24.8447 | 49.69% | 41.1
7288 | 282 | 231 | 136 | 5.6416 | 26.4 | 141.9355 | 0 | 71.5374 | 0 | 28.8305 | 0 | 0 | 28.8305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 13.9695 | 10.268 | 20.54% | 42.8
7289 | 84 | 67 | 51 | 3.6268 | 24.6 | 42.2787 | 0 | 0 | 0 | 6.7709 | 0 | 0 | 6.7709 | 0 | 0 | 0 | 70.611 | 26.8879 | 0 | 70.611 | 1209.5791 | 94.91% | 0 | 9.8412 | 1.3878e-15 | 2.776e-15% | 43.5
7290 | 0 | 2 | 2 | 10.0743 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5156 | 42.8 | 0 | 108.5156 | 1102.6353 | 86.51% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 42.8
7291 | 0 | 0 | 0 | 6.4476 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6987 | 41.3 | 0 | 104.6987 | 999.9406 | 78.46% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 41.3
7292 | 0 | 0 | 0 | 4.6342 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4193 | 38 | 0 | 96.4193 | 906.6412 | 71.14% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 38
7293 | 0 | 0 | 0 | 6.0446 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.034 | 35.4 | 0 | 90.034 | 820.6585 | 64.39% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 35.4
7294 | 0 | 0 | 0 | 6.0446 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2035 | 33.8 | 0 | 86.2035 | 739.2194 | 58% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 33.8
7295 | 0 | 0 | 0 | 4.6342 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.235 | 32.2 | 0 | 82.235 | 662.239 | 51.96% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 32.2
7296 | 0 | 0 | 0 | 5.2387 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4396 | 30.6 | 0 | 78.4396 | 589.4752 | 46.25% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 30.6
7297 | 0 | 0 | 0 | 2.2164 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2608 | 29.7 | 0 | 76.2608 | 518.993 | 40.72% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 29.7
7298 | 0 | 0 | 0 | 4.8357 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.6029 | 29.4 | 0 | 75.6029 | 449.1348 | 35.24% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 29.4
7299 | 0 | 0 | 0 | 7.455 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1307 | 29.1 | 0 | 75.1307 | 379.7274 | 29.79% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 29.1
7300 | 0 | 0 | 0 | 9.6714 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8541 | 26.7127 | 0 | 69.8541 | 315.3939 | 24.75% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 26.7127
7301 | 0 | 0 | 0 | 9.2684 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.3939 | 24.75% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
7302 | 0 | 0 | 0 | 9.4699 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.3939 | 24.75% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0
7303 | 30 | 10 | 6 | 5.4401 | 20 | 15.0995 | 0 | 0 | 0 | 0.057517 | 0 | 0 | 0.057517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.3939 | 24.75% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 0.057517
7304 | 536 | 146 | 47 | 5.8431 | 21.1 | 269.7781 | 105.7171 | 0 | 79.2806 | 25.1367 | 0 | 0 | 25.1367 | 0 | 0 | 0 | 0 | 0 | 79.2806 | 0 | 389.9864 | 30.6% | 0 | 0 | 1.3878e-15 | 2.776e-15% | 25.1367
7305 | 773 | 351 | 84 | 5.4401 | 23.2 | 389.0643 | 200.7651 | 0 | 168.6416 | 73.9921 | 0 | 19.1461 | 54.8461 | 0 | 0 | 0 | 0 | 0 | 168.6416 | 0 | 548.6557 | 43.05% | 14.685 | 0 | 15.327 | 30.65% | 35.7
7306 | 307 | 367 | 225 | 7.052 | 24.3 | 154.5184 | 91.2524 | 0 | 65.3418 | 54.8969 | 0 | 9.3984 | 45.4984 | 0 | 0 | 0 | 0 | 0 | 65.3418 | 0 | 610.1336 | 47.87% | 7.2086 | 0 | 22.8508 | 45.7% | 36.1
7307 | 12 | 286 | 275 | 6.4476 | 24.6 | 6.0398 | 0 | 3.7936 | 0 | 23.7698 | 0 | 0 | 23.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610.1336 | 47.87% | 0 | 12.9302 | 9.3574 | 18.71% | 36.7
7308 | 13 | 316 | 304 | 8.261 | 24.8 | 6.5431 | 0 | 4.1878 | 0 | 26.4322 | 0 | 0 | 26.4322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610.1336 | 47.87% | 0 | 8.9669 | 0 | 0% | 35.3991
7309 | 62 | 378 | 334 | 9.8729 | 25.4 | 31.2057 | 0 | 19.9443 | 0 | 38.0409 | 1.7704 | 0 | 36.2704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610.1336 | 47.87% | 0 | 0 | 0 | 0% | 34.5
7310 | 110 | 371 | 302 | 8.261 | 26.3 | 55.3649 | 0 | 34.5398 | 0 | 40.1054 | 0 | 3.3027 | 36.8027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610.1336 | 47.87% | 2.5332 | 0 | 2.6441 | 5.288% | 33.5
7311 | 111 | 273 | 218 | 4.4327 | 26.8 | 55.8682 | 0 | 32.6287 | 0 | 27.2742 | 0 | 0 | 27.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610.1336 | 47.87% | 0 | 2.5336 | 0 | 0% | 29.8078
7312 | 158 | 186 | 143 | 4.6342 | 26.7 | 79.5241 | 0 | 39.9392 | 0 | 22.0527 | 0 | 0 | 22.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610.1336 | 47.87% | 0 | 0 | 0 | 0% | 22.0527
7313 | 25 | 58 | 53 | 7.052 | 25.4 | 12.5829 | 0 | 0 | 0 | 4.9778 | 0 | 0 | 4.9778 | 0 | 0 | 0 | 82.3678 | 31.9222 | 0 | 82.3678 | 533.0636 | 41.82% | 0 | 0 | 0 | 0% | 36.9
7314 | 0 | 2 | 2 | 8.8654 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2305 | 37.4 | 0 | 95.2305 | 441.3014 | 34.63% | 0 | 0 | 0 | 0% | 37.4
7315 | 0 | 0 | 0 | 8.0595 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1819 | 37 | 0 | 94.1819 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 37
7316 | 0 | 0 | 0 | 11.4848 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7317 | 0 | 0 | 0 | 13.2981 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7318 | 0 | 0 | 0 | 11.0818 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7319 | 0 | 0 | 0 | 13.9026 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7320 | 0 | 0 | 0 | 13.0966 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7321 | 0 | 0 | 0 | 12.4922 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7322 | 0 | 0 | 0 | 14.1041 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7323 | 0 | 0 | 0 | 14.7085 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7324 | 0 | 0 | 0 | 14.7085 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7325 | 0 | 0 | 0 | 11.4848 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7326 | 0 | 0 | 0 | 14.5071 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7327 | 4 | 7 | 6 | 13.2981 | 20.8 | 2.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350.6537 | 27.51% | 0 | 0 | 0 | 0% | 0
7328 | 357 | 118 | 51 | 15.5145 | 21.7 | 179.6843 | 69.9365 | 0 | 39.6958 | 19.0195 | 0 | 0 | 19.0195 | 0 | 0 | 0 | 0 | 0 | 39.6958 | 0 | 388.0897 | 30.45% | 0 | 0 | 0 | 0% | 19.0195
7329 | 364 | 251 | 137 | 12.8952 | 22.7 | 183.2075 | 94.2003 | 0 | 64.4878 | 35.6713 | 0 | 0 | 35.6713 | 0 | 0 | 0 | 0 | 0 | 64.4878 | 0 | 448.9064 | 35.22% | 0 | 0 | 0 | 0% | 35.6713
7330 | 137 | 286 | 217 | 18.7383 | 22.4 | 68.9545 | 0 | 40.6494 | 0 | 31.4106 | 0 | 0 | 31.4106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 448.9064 | 35.22% | 0 | 0 | 0 | 0% | 31.4106
7331 | 306 | 365 | 184 | 20.1487 | 22.9 | 154.0151 | 96.5441 | 0 | 62.4794 | 53.08 | 0 | 7.74 | 45.34 | 0 | 0 | 0 | 0 | 0 | 62.4794 | 0 | 507.8291 | 39.85% | 5.9366 | 0 | 6.1967 | 12.39% | 37.6
7332 | 85 | 270 | 216 | 16.9249 | 23.1 | 42.782 | 0 | 27.3552 | 0 | 26.4454 | 0 | 0 | 26.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507.8291 | 39.85% | 0 | 5.9375 | 0 | 0% | 32.383
7333 | 169 | 334 | 226 | 17.9323 | 23.5 | 85.0606 | 0 | 54.3127 | 0 | 38.586 | 1.843 | 0 | 36.743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507.8291 | 39.85% | 0 | 0 | 0 | 0% | 34.9
7334 | 89 | 266 | 213 | 17.5294 | 22.8 | 44.7952 | 0 | 27.8913 | 0 | 26.2031 | 0 | 0 | 26.2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507.8291 | 39.85% | 0 | 0 | 0 | 0% | 26.2031
7335 | 559 | 387 | 135 | 18.9398 | 23.7 | 281.3544 | 164.03 | 0 | 126.3464 | 76.888 | 0 | 21.394 | 55.494 | 0 | 0 | 0 | 0 | 0 | 126.3464 | 0 | 626.9829 | 49.19% | 16.4092 | 0 | 17.1286 | 34.26% | 34.1
7336 | 182 | 161 | 113 | 15.716 | 23.1 | 91.6038 | 0 | 45.842 | 0 | 21.4718 | 0 | 0 | 21.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626.9829 | 49.19% | 0 | 15.1282 | 1.3397 | 2.679% | 36.6
7337 | 237 | 95 | 54 | 13.9026 | 22.7 | 119.2862 | 0 | 0 | 0 | 12.0655 | 0 | 0 | 12.0655 | 0 | 0 | 0 | 66.9921 | 25.4345 | 0 | 66.9921 | 565.2829 | 44.35% | 0 | 0 | 1.3397 | 2.679% | 37.5
7338 | 1 | 2 | 2 | 15.9175 | 21.8 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3886 | 38 | 0 | 96.3886 | 471.6505 | 37.01% | 0 | 0 | 1.3397 | 2.679% | 38
7339 | 0 | 0 | 0 | 16.119 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0654 | 37.5 | 0 | 95.0654 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 37.5
7340 | 0 | 0 | 0 | 10.2758 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7341 | 0 | 0 | 0 | 10.2758 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7342 | 0 | 0 | 0 | 11.2833 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7343 | 0 | 0 | 0 | 10.0743 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7344 | 0 | 0 | 0 | 9.4699 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7345 | 0 | 0 | 0 | 9.0669 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7346 | 0 | 0 | 0 | 8.261 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7347 | 0 | 0 | 0 | 13.9026 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7348 | 0 | 0 | 0 | 20.5517 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7349 | 0 | 0 | 0 | 25.3874 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7350 | 0 | 0 | 0 | 26.7978 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0
7351 | 11 | 9 | 8 | 23.574 | 18.9 | 5.5365 | 0 | 0 | 0 | 0.083479 | 0 | 0 | 0.083479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 0.083479
7352 | 270 | 142 | 92 | 18.9398 | 19.3 | 135.8957 | 0 | 52.5413 | 0 | 19.8926 | 0 | 0 | 19.8926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 19.8926
7353 | 51 | 200 | 181 | 17.3279 | 19.9 | 25.6692 | 0 | 13.152 | 0 | 20.4725 | 0 | 0 | 20.4725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 20.4725
7354 | 158 | 325 | 242 | 20.1487 | 20.6 | 79.5241 | 0 | 46.7986 | 0 | 37.7942 | 1.6971 | 0 | 36.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379.4262 | 29.77% | 0 | 0 | 1.3397 | 2.679% | 34.4
7355 | 224 | 382 | 244 | 23.3725 | 20.5 | 112.7431 | 70.5346 | 0 | 35.6894 | 51.8309 | 0 | 8.4654 | 43.3654 | 0 | 0 | 0 | 0 | 0 | 35.6894 | 0 | 413.1275 | 32.41% | 6.493 | 0 | 8.1179 | 16.24% | 34.9
7356 | 618 | 551 | 161 | 27.6037 | 21.2 | 311.0501 | 198.6996 | 0 | 153.814 | 115.2 | 15.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 153.814 | 0 | 558.3732 | 43.81% | 19.175 | 0 | 28.1349 | 56.27% | 34.8
7357 | 893 | 715 | 166 | 28.6111 | 21.8 | 449.4624 | 286.7196 | 0 | 235.4034 | 117.1 | 17.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 235.4034 | 0 | 780.6631 | 61.25% | 19.175 | 0 | 48.152 | 96.3% | 32.9
7358 | 865 | 557 | 76 | 26.1933 | 22.1 | 435.3695 | 270.5514 | 0 | 221.4837 | 118.2 | 43.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 221.4837 | 0 | 989.8088 | 77.66% | 0 | 0 | 48.152 | 96.3% | 31.8
7359 | 855 | 443 | 59 | 22.365 | 22.2 | 430.3364 | 250.4446 | 0 | 204.9513 | 105.9221 | 37.0111 | 0 | 68.9111 | 0 | 0 | 0 | 0 | 0 | 204.9513 | 0 | 1183.3431 | 92.85% | 0 | 0 | 48.152 | 96.3% | 31.9
7360 | 711 | 268 | 49 | 21.1561 | 21.8 | 357.8587 | 178.4448 | 0 | 138.6291 | 56.2045 | 10.6522 | 0 | 45.5522 | 0 | 0 | 0 | 0 | 0 | 138.6291 | 0 | 1274.5104 | 100% | 0 | 0 | 48.152 | 96.3% | 34.9
7361 | 431 | 85 | 26 | 19.9472 | 20.9 | 216.9298 | 0 | 0 | 0 | 14.0862 | 0 | 0 | 14.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.8138 | 24.34 | 48.68% | 36.9
7362 | 2 | 1 | 1 | 20.3502 | 20.1 | 1.0066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.3196 | 0 | 0% | 23.3196
7363 | 0 | 0 | 0 | 22.5665 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1656 | 37.6 | 0 | 95.1656 | 1182.2275 | 92.76% | 0 | 0 | 0 | 0% | 37.6
7364 | 0 | 0 | 0 | 11.2833 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7312 | 35.8 | 0 | 90.7312 | 1095.0149 | 85.92% | 0 | 0 | 0 | 0% | 35.8
7365 | 0 | 0 | 0 | 3.4253 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2831 | 33.3 | 0 | 84.2831 | 1014.9577 | 79.64% | 0 | 0 | 0 | 0% | 33.3
7366 | 0 | 0 | 0 | 2.6193 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.587 | 31.3 | 0 | 79.587 | 940.5691 | 73.8% | 0 | 0 | 0 | 0% | 31.3
7367 | 0 | 0 | 0 | 9.4699 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.9672 | 29.7 | 0 | 75.9672 | 870.2877 | 68.28% | 0 | 0 | 0 | 0% | 29.7
7368 | 0 | 0 | 0 | 10.8803 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0008 | 28.8 | 0 | 74.0008 | 801.902 | 62.92% | 0 | 0 | 0 | 0% | 28.8
7369 | 0 | 0 | 0 | 6.2461 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.6701 | 28.2 | 0 | 72.6701 | 734.7925 | 57.65% | 0 | 0 | 0 | 0% | 28.2
7370 | 0 | 0 | 0 | 11.8877 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2483 | 28.4 | 0 | 73.2483 | 667.1197 | 52.34% | 0 | 0 | 0 | 0% | 28.4
7371 | 0 | 0 | 0 | 6.4476 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.339 | 29.4 | 0 | 75.339 | 597.4067 | 46.87% | 0 | 0 | 0 | 0% | 29.4
7372 | 0 | 0 | 0 | 4.0297 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0169 | 33.2 | 0 | 84.0169 | 517.5517 | 40.61% | 0 | 0 | 0 | 0% | 33.2
7373 | 0 | 0 | 0 | 5.2387 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3229 | 37.9 | 0 | 95.3229 | 424.2704 | 33.29% | 0 | 0 | 0 | 0% | 37.9
7374 | 0 | 0 | 0 | 5.0372 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.021 | 35.3431 | 0 | 89.021 | 338.1952 | 26.54% | 0 | 0 | 0 | 0% | 35.3431
7375 | 31 | 7 | 4 | 5.2387 | 15.3 | 15.6028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338.1952 | 26.54% | 0 | 0 | 0 | 0% | 0
7376 | 580 | 128 | 28 | 10.2758 | 17.7 | 291.9241 | 112.1282 | 0 | 82.679 | 24.6129 | 0 | 0 | 24.6129 | 0 | 0 | 0 | 0 | 0 | 82.679 | 0 | 415.6769 | 32.61% | 0 | 0 | 0 | 0% | 24.6129
7377 | 800 | 309 | 43 | 11.8877 | 19.7 | 402.6539 | 205.5958 | 0 | 169.2699 | 61.7413 | 0 | 8.9206 | 52.8206 | 0 | 0 | 0 | 0 | 0 | 169.2699 | 0 | 574.3066 | 45.06% | 6.8421 | 0 | 7.1436 | 14.29% | 43.9
7378 | 891 | 468 | 50 | 13.4996 | 21.2 | 448.4558 | 263.4584 | 0 | 222.1183 | 101.2403 | 3.4702 | 25 | 72.7702 | 0 | 0 | 0 | 0 | 0 | 222.1183 | 0 | 782.4626 | 61.39% | 19.175 | 0 | 27.1634 | 54.33% | 44.3
7379 | 935 | 580 | 54 | 16.7234 | 22.4 | 470.6018 | 293.8515 | 0 | 248.9604 | 105.8 | 5.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 248.9604 | 0 | 1015.7734 | 79.7% | 19.175 | 0 | 47.1833 | 94.37% | 44.2
7380 | 954 | 636 | 54 | 15.9175 | 23.4 | 480.1648 | 306.4425 | 0 | 261.0879 | 107 | 28.4827 | 3.5173 | 75 | 0 | 0 | 0 | 0 | 0 | 261.0879 | 0 | 1260.4494 | 98.9% | 2.6978 | 0 | 50 | 100% | 43
7381 | 950 | 628 | 55 | 15.9175 | 24.6 | 478.1515 | 0 | 304.7364 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.4494 | 98.9% | 0 | 0 | 50 | 100% | 42
7382 | 915 | 554 | 54 | 14.1041 | 24.8 | 460.5354 | 0 | 285.6356 | 0 | 108.5 | 33.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.4494 | 98.9% | 0 | 0 | 50 | 100% | 41.5
7383 | 858 | 429 | 51 | 16.119 | 24.6 | 431.8463 | 0 | 250.8807 | 0 | 92.6375 | 25.4187 | 0 | 67.2187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.4494 | 98.9% | 0 | 0 | 50 | 100% | 41.8
7384 | 737 | 262 | 42 | 20.1487 | 23.2 | 370.9449 | 0 | 184.3051 | 0 | 47.2235 | 1.7118 | 0 | 45.5118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.4494 | 98.9% | 0 | 0 | 50 | 100% | 43.8
7385 | 432 | 83 | 24 | 19.5442 | 21.6 | 217.4331 | 0 | 0 | 0 | 13.5107 | 0 | 0 | 13.5107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.4494 | 98.9% | 0 | 25 | 23.9024 | 47.8% | 38.5107
7386 | 0 | 1 | 1 | 18.7383 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.3725 | 22.3028 | 0 | 59.3725 | 1206.273 | 94.65% | 0 | 22.8972 | 2.7756e-15 | 5.551e-15% | 45.2
7387 | 0 | 0 | 0 | 16.5219 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1341 | 43.5 | 0 | 109.1341 | 1097.2682 | 86.09% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.5
7388 | 0 | 0 | 0 | 17.9323 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1175 | 39.8 | 0 | 100.1175 | 998.7621 | 78.36% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.8
7389 | 0 | 0 | 0 | 14.91 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8664 | 36.4 | 0 | 91.8664 | 909.9461 | 71.4% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.4
7390 | 0 | 0 | 0 | 9.0669 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0733 | 34.4 | 0 | 87.0733 | 826.7838 | 64.87% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.4
7391 | 0 | 0 | 0 | 8.0595 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7044 | 32.6 | 0 | 82.7044 | 748.7873 | 58.75% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.6
7392 | 0 | 0 | 0 | 14.3056 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1019 | 31.5 | 0 | 80.1019 | 673.8904 | 52.87% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.5
7393 | 0 | 0 | 0 | 16.7234 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4408 | 30.8 | 0 | 78.4408 | 600.9413 | 47.15% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.8
7394 | 0 | 0 | 0 | 17.1264 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1674 | 30.7 | 0 | 78.1674 | 528.2581 | 41.45% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.7
7395 | 0 | 0 | 0 | 10.2758 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9392 | 31.5 | 0 | 79.9392 | 453.3214 | 35.57% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.5
7396 | 0 | 0 | 0 | 5.2387 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8626 | 35 | 0 | 87.8626 | 368.3182 | 28.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35
7397 | 0 | 0 | 0 | 4.2312 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368.3182 | 28.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
7398 | 0 | 0 | 0 | 13.7011 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368.3182 | 28.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
7399 | 17 | 6 | 5 | 22.768 | 16.4 | 8.5564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368.3182 | 28.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
7400 | 532 | 123 | 32 | 25.7903 | 16.1 | 267.7649 | 102.1879 | 0 | 64.1025 | 23.3286 | 0 | 0 | 23.3286 | 0 | 0 | 0 | 0 | 0 | 64.1025 | 0 | 428.7304 | 33.64% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 23.3286
7401 | 805 | 312 | 48 | 19.7457 | 16.4 | 405.1705 | 206.183 | 0 | 165.1066 | 65.1263 | 0 | 10.4631 | 54.6631 | 0 | 0 | 0 | 0 | 0 | 165.1066 | 0 | 584.3321 | 45.85% | 8.0252 | 0 | 8.38 | 16.76% | 44.2
7402 | 905 | 477 | 57 | 17.5294 | 17.2 | 455.5022 | 267.151 | 0 | 223.0427 | 105.4 | 5.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 223.0427 | 0 | 794.5346 | 62.34% | 19.175 | 0 | 28.4028 | 56.81% | 44.6
7403 | 956 | 596 | 62 | 19.9472 | 17.6 | 481.1714 | 299.8808 | 0 | 252.4702 | 105.3 | 5.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 252.4702 | 0 | 1032.4705 | 81.01% | 19.175 | 0 | 48.4257 | 96.85% | 44.7
7404 | 963 | 649 | 66 | 14.7085 | 18.8 | 484.6946 | 309.0472 | 0 | 264.0366 | 106.5 | 31.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 264.0366 | 0 | 1274.5104 | 100% | 0 | 0 | 48.4257 | 96.85% | 43.5
7405 | 952 | 639 | 68 | 11.6862 | 19.8 | 479.1582 | 0 | 305.0958 | 0 | 107.5 | 32.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.4257 | 96.85% | 42.5
7406 | 920 | 566 | 67 | 14.1041 | 20.1 | 463.052 | 0 | 286.6422 | 0 | 108 | 33 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.4257 | 96.85% | 42
7407 | 861 | 440 | 63 | 13.0966 | 20.5 | 433.3563 | 0 | 251.3149 | 0 | 96.59 | 27.245 | 0 | 69.345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.4257 | 96.85% | 42.1
7408 | 735 | 270 | 54 | 13.2981 | 19 | 369.9383 | 0 | 183.1415 | 0 | 50.3751 | 2.8876 | 0 | 47.4876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 48.4257 | 96.85% | 44.6
7409 | 330 | 82 | 32 | 13.2981 | 17.1 | 166.0947 | 0 | 0 | 0 | 11.8936 | 0 | 0 | 11.8936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 22.3243 | 44.65% | 36.8936
7410 | 0 | 1 | 1 | 11.8877 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.4163 | 24.7178 | 0 | 64.4163 | 1215.446 | 95.37% | 0 | 21.3822 | 0 | 0% | 46.1
7411 | 0 | 0 | 0 | 11.4848 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.6727 | 44.4 | 0 | 110.6727 | 1103.8686 | 86.61% | 0 | 0 | 0 | 0% | 44.4
7412 | 0 | 0 | 0 | 12.4922 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.3224 | 40.5 | 0 | 101.3224 | 1003.3951 | 78.73% | 0 | 0 | 0 | 0% | 40.5
7413 | 0 | 0 | 0 | 13.7011 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4578 | 36.8 | 0 | 92.4578 | 913.467 | 71.67% | 0 | 0 | 0 | 0% | 36.8
7414 | 0 | 0 | 0 | 15.313 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6645 | 34.8 | 0 | 87.6645 | 829.153 | 65.06% | 0 | 0 | 0 | 0% | 34.8
7415 | 0 | 0 | 0 | 11.6862 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.095 | 32.9 | 0 | 83.095 | 750.3139 | 58.87% | 0 | 0 | 0 | 0% | 32.9
7416 | 0 | 0 | 0 | 6.0446 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8496 | 31.6 | 0 | 79.8496 | 675.1479 | 52.97% | 0 | 0 | 0 | 0% | 31.6
7417 | 0 | 0 | 0 | 10.8803 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8967 | 31.2 | 0 | 78.8967 | 601.0925 | 47.16% | 0 | 0 | 0 | 0% | 31.2
7418 | 0 | 0 | 0 | 8.0595 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6329 | 31.1 | 0 | 78.6329 | 527.304 | 41.37% | 0 | 0 | 0 | 0% | 31.1
7419 | 0 | 0 | 0 | 9.6714 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0086 | 32.1 | 0 | 81.0086 | 450.6859 | 35.36% | 0 | 0 | 0 | 0% | 32.1
7420 | 0 | 0 | 0 | 9.4699 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.3857 | 25.7152 | 0 | 66.3857 | 389.6252 | 30.57% | 0 | 0 | 0 | 0% | 25.7152
7421 | 0 | 0 | 0 | 8.0595 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389.6252 | 30.57% | 0 | 0 | 0 | 0% | 0
7422 | 0 | 0 | 0 | 9.2684 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389.6252 | 30.57% | 0 | 0 | 0 | 0% | 0
7423 | 26 | 5 | 4 | 6.4476 | 11.5 | 13.0863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389.6252 | 30.57% | 0 | 0 | 0 | 0% | 0
7424 | 576 | 125 | 30 | 8.4625 | 13.3 | 289.9108 | 109.9422 | 0 | 81.5635 | 24.2393 | 0 | 0 | 24.2393 | 0 | 0 | 0 | 0 | 0 | 81.5635 | 0 | 466.4899 | 36.6% | 0 | 0 | 0 | 0% | 24.2393
7425 | 812 | 312 | 48 | 6.8506 | 15.5 | 408.6937 | 207.2896 | 0 | 173.7882 | 64.1081 | 0 | 9.9041 | 54.2041 | 0 | 0 | 0 | 0 | 0 | 173.7882 | 0 | 630.2664 | 49.45% | 7.5964 | 0 | 7.9334 | 15.87% | 44.3
7426 | 848 | 464 | 75 | 5.2387 | 17.1 | 426.8131 | 249.916 | 0 | 214.4846 | 99.7418 | 2.6709 | 25 | 72.0709 | 0 | 0 | 0 | 0 | 0 | 214.4846 | 0 | 832.3948 | 65.31% | 19.175 | 0 | 27.9591 | 55.92% | 44.4
7427 | 950 | 589 | 61 | 3.2238 | 18.8 | 478.1515 | 297.4416 | 0 | 259.869 | 105.6 | 5.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 259.869 | 0 | 1077.293 | 84.53% | 19.175 | 0 | 47.9848 | 95.97% | 44.4
7428 | 941 | 640 | 74 | 7.2535 | 18.9 | 473.6217 | 301.7116 | 0 | 261.819 | 107.1 | 29.5843 | 2.5157 | 75 | 0 | 0 | 0 | 0 | 0 | 261.819 | 0 | 1274.5104 | 100% | 1.9296 | 0 | 50 | 100% | 42.9
7429 | 876 | 611 | 89 | 6.2461 | 18.7 | 440.906 | 0 | 280.4826 | 0 | 107.9 | 32.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.1
7430 | 777 | 537 | 115 | 6.0446 | 18.8 | 391.0776 | 0 | 241.6231 | 0 | 108.2 | 33.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.8
7431 | 852 | 432 | 62 | 9.0669 | 19 | 428.8264 | 0 | 248.2509 | 0 | 94.4489 | 26.1244 | 0 | 68.3244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.2
7432 | 734 | 261 | 48 | 10.0743 | 18.2 | 369.435 | 0 | 182.2299 | 0 | 48.8624 | 2.1812 | 0 | 46.6812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.5
7433 | 401 | 80 | 25 | 7.455 | 16.9 | 201.8303 | 0 | 0 | 0 | 12.3273 | 0 | 0 | 12.3273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.8948 | 47.79% | 37.3273
7434 | 0 | 1 | 1 | 7.6565 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.8442 | 23.6167 | 0 | 61.8442 | 1217.9368 | 95.56% | 0 | 22.8833 | 0 | 0% | 46.5
7435 | 0 | 0 | 0 | 5.0372 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.4935 | 44.8 | 0 | 111.4935 | 1105.209 | 86.72% | 0 | 0 | 0 | 0% | 44.8
7436 | 0 | 0 | 0 | 3.8283 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2801 | 41 | 0 | 102.2801 | 1003.3317 | 78.72% | 0 | 0 | 0 | 0% | 41
7437 | 0 | 0 | 0 | 4.8357 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1594 | 37.2 | 0 | 93.1594 | 912.2777 | 71.58% | 0 | 0 | 0 | 0% | 37.2
7438 | 0 | 0 | 0 | 3.8283 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5782 | 35.3 | 0 | 88.5782 | 826.5485 | 64.85% | 0 | 0 | 0 | 0% | 35.3
7439 | 0 | 0 | 0 | 4.6342 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6761 | 33.3 | 0 | 83.6761 | 746.5683 | 58.58% | 0 | 0 | 0 | 0% | 33.3
7440 | 0 | 0 | 0 | 4.4327 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5569 | 32 | 0 | 80.5569 | 670.278 | 52.59% | 0 | 0 | 0 | 0% | 32
7441 | 0 | 0 | 0 | 4.6342 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3264 | 31.5 | 0 | 79.3264 | 595.3843 | 46.71% | 0 | 0 | 0 | 0% | 31.5
7442 | 0 | 0 | 0 | 3.4253 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2872 | 31.5 | 0 | 79.2872 | 520.4772 | 40.84% | 0 | 0 | 0 | 0% | 31.5
7443 | 0 | 0 | 0 | 3.6268 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9389 | 32.2 | 0 | 80.9389 | 443.5826 | 34.8% | 0 | 0 | 0 | 0% | 32.2
7444 | 0 | 0 | 0 | 3.6268 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7376 | 32.9395 | 0 | 82.7376 | 364.5615 | 28.6% | 0 | 0 | 0 | 0% | 32.9395
7445 | 0 | 0 | 0 | 3.2238 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364.5615 | 28.6% | 0 | 0 | 0 | 0% | 0
7446 | 0 | 0 | 0 | 2.6193 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364.5615 | 28.6% | 0 | 0 | 0 | 0% | 0
7447 | 24 | 5 | 4 | 2.2164 | 9 | 12.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364.5615 | 28.6% | 0 | 0 | 0 | 0% | 0
7448 | 532 | 119 | 33 | 1.2089 | 12.1 | 267.7649 | 100.9167 | 0 | 76.574 | 22.2706 | 0 | 0 | 22.2706 | 0 | 0 | 0 | 0 | 0 | 76.574 | 0 | 436.9207 | 34.28% | 0 | 0 | 0 | 0% | 22.2706
7449 | 780 | 304 | 53 | 2.8208 | 15 | 392.5876 | 198.4786 | 0 | 167.418 | 59.9681 | 0 | 7.4841 | 52.4841 | 0 | 0 | 0 | 0 | 0 | 167.418 | 0 | 595.1236 | 46.69% | 5.7403 | 0 | 5.9958 | 11.99% | 45
7450 | 878 | 455 | 54 | 3.8283 | 16.9 | 441.9127 | 258.3444 | 0 | 222.8923 | 96.3621 | 0.58104 | 25 | 70.781 | 0 | 0 | 0 | 0 | 0 | 222.8923 | 0 | 805.7473 | 63.22% | 19.175 | 0 | 26.0244 | 52.05% | 45.2
7451 | 669 | 537 | 170 | 6.0446 | 18.4 | 336.7193 | 209.0763 | 0 | 175.9829 | 104.8 | 4.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 175.9829 | 0 | 972.0437 | 76.27% | 19.175 | 0 | 46.0531 | 92.11% | 45.2
7452 | 335 | 517 | 310 | 9.6714 | 19.4 | 168.6113 | 107.3141 | 0 | 78.4533 | 81.5059 | 13.9764 | 4.9265 | 62.603 | 0 | 0 | 0 | 0 | 0 | 78.4533 | 0 | 1046.1787 | 82.08% | 3.7786 | 0 | 50 | 100% | 43.7
7453 | 254 | 427 | 271 | 10.2758 | 20.2 | 127.8426 | 81.2535 | 0 | 53.5876 | 59.1178 | 8.0089 | 0 | 51.1089 | 0 | 0 | 0 | 0 | 0 | 53.5876 | 0 | 1096.8167 | 86.06% | 0 | 0 | 50 | 100% | 43.1
7454 | 419 | 457 | 238 | 14.5071 | 20.9 | 210.89 | 130.0471 | 0 | 96.9301 | 77.086 | 17.093 | 0 | 59.993 | 0 | 0 | 0 | 0 | 0 | 96.9301 | 0 | 1188.4116 | 93.24% | 0 | 0 | 50 | 100% | 42.9
7455 | 51 | 201 | 175 | 14.5071 | 21 | 25.6692 | 0 | 14.834 | 0 | 19.3292 | 0 | 0 | 19.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1188.4116 | 93.24% | 0 | 24.0708 | 24.8615 | 49.72% | 43.4
7456 | 634 | 248 | 74 | 14.91 | 20.8 | 319.1032 | 156.8313 | 0 | 121.7843 | 44.0137 | 0 | 0 | 44.0137 | 0 | 0 | 0 | 0 | 0 | 121.7843 | 0 | 1274.5104 | 100% | 0 | 0 | 24.8615 | 49.72% | 44.0137
7457 | 412 | 78 | 22 | 17.5294 | 19.5 | 207.3668 | 0 | 0 | 0 | 11.8865 | 0 | 0 | 11.8865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 23.8043 | 0 | 0% | 35.6908
7458 | 0 | 1 | 1 | 11.0818 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.6114 | 47.5 | 0 | 118.6114 | 1154.0187 | 90.55% | 0 | 0 | 0 | 0% | 47.5
7459 | 0 | 0 | 0 | 11.2833 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.6821 | 45.6 | 0 | 113.6821 | 1039.007 | 81.52% | 0 | 0 | 0 | 0% | 45.6
7460 | 0 | 0 | 0 | 11.0818 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2406 | 41.7 | 0 | 104.2406 | 935.1647 | 73.37% | 0 | 0 | 0 | 0% | 41.7
7461 | 0 | 0 | 0 | 12.6937 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2197 | 38.4 | 0 | 96.2197 | 840.7094 | 65.96% | 0 | 0 | 0 | 0% | 38.4
7462 | 0 | 0 | 0 | 9.8729 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8357 | 36.2 | 0 | 90.8357 | 752.4745 | 59.04% | 0 | 0 | 0 | 0% | 36.2
7463 | 0 | 0 | 0 | 9.8729 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.801 | 34.1 | 0 | 85.801 | 670.1989 | 52.58% | 0 | 0 | 0 | 0% | 34.1
7464 | 0 | 0 | 0 | 7.2535 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8979 | 32.9 | 0 | 82.8979 | 591.3607 | 46.4% | 0 | 0 | 0 | 0% | 32.9
7465 | 0 | 0 | 0 | 12.2907 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4472 | 32.3 | 0 | 81.4472 | 514.2162 | 40.35% | 0 | 0 | 0 | 0% | 32.3
7466 | 0 | 0 | 0 | 14.3056 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1758 | 32.2 | 0 | 81.1758 | 437.3399 | 34.31% | 0 | 0 | 0 | 0% | 32.2
7467 | 0 | 0 | 0 | 13.7011 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2931 | 33.1 | 0 | 83.2931 | 357.8821 | 28.08% | 0 | 0 | 0 | 0% | 33.1
7468 | 0 | 0 | 0 | 8.8654 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357.8821 | 28.08% | 0 | 0 | 0 | 0% | 0
7469 | 0 | 0 | 0 | 8.4625 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357.8821 | 28.08% | 0 | 0 | 0 | 0% | 0
7470 | 0 | 0 | 0 | 7.2535 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357.8821 | 28.08% | 0 | 0 | 0 | 0% | 0
7471 | 3 | 3 | 3 | 5.2387 | 10.8 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357.8821 | 28.08% | 0 | 0 | 0 | 0% | 0
7472 | 129 | 65 | 37 | 9.2684 | 10.8 | 64.9279 | 0 | 0 | 0 | 8.0329 | 0 | 0 | 8.0329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357.8821 | 28.08% | 0 | 0 | 0 | 0% | 8.0329
7473 | 748 | 298 | 61 | 14.3056 | 12.5 | 376.4814 | 189.7369 | 0 | 152.6153 | 60.5723 | 0 | 7.1861 | 53.3861 | 0 | 0 | 0 | 0 | 0 | 152.6153 | 0 | 503.879 | 39.54% | 5.5118 | 0 | 5.758 | 11.52% | 46.2
7474 | 836 | 457 | 80 | 15.5145 | 13.7 | 420.7733 | 245.6031 | 0 | 204.061 | 102.3692 | 2.9846 | 25 | 74.3846 | 0 | 0 | 0 | 0 | 0 | 204.061 | 0 | 699.0906 | 54.85% | 19.175 | 0 | 25.7896 | 51.58% | 46.4
7475 | 898 | 591 | 100 | 11.8877 | 14.6 | 451.979 | 280.1363 | 0 | 238.5845 | 104.1 | 4.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 238.5845 | 0 | 927.3285 | 72.76% | 19.175 | 0 | 45.8212 | 91.64% | 45.9
7476 | 920 | 632 | 87 | 5.2387 | 15.8 | 463.052 | 294.4529 | 0 | 256.2878 | 105.5 | 25.2847 | 5.2153 | 75 | 0 | 0 | 0 | 0 | 0 | 256.2878 | 0 | 1172.5021 | 92% | 4.0001 | 0 | 50 | 100% | 44.5
7477 | 920 | 625 | 86 | 11.4848 | 16.1 | 463.052 | 294.0408 | 0 | 252.0522 | 106.6 | 31.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 252.0522 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.4
7478 | 891 | 553 | 81 | 9.6714 | 16.4 | 448.4558 | 0 | 276.0189 | 0 | 107 | 32 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43
7479 | 830 | 426 | 72 | 4.8357 | 16.9 | 417.7534 | 0 | 240.994 | 0 | 92.2862 | 24.5431 | 0 | 67.7431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.2
7480 | 721 | 259 | 55 | 10.6788 | 16.4 | 362.8918 | 0 | 177.703 | 0 | 48.1416 | 1.1708 | 0 | 46.9708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.8
7481 | 426 | 81 | 27 | 10.4773 | 14.9 | 214.4132 | 0 | 0 | 0 | 12.4583 | 0 | 0 | 12.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.8871 | 47.77% | 37.4583
7482 | 0 | 1 | 1 | 9.0669 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.1804 | 23.8309 | 0 | 62.1804 | 1217.6191 | 95.54% | 0 | 22.8691 | 2.7756e-15 | 5.551e-15% | 46.7
7483 | 0 | 0 | 0 | 2.6193 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.8755 | 45 | 0 | 111.8755 | 1104.3443 | 86.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 45
7484 | 0 | 0 | 0 | 9.2684 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9288 | 41.7 | 0 | 103.9288 | 1000.5155 | 78.5% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 41.7
7485 | 0 | 0 | 0 | 5.6416 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6325 | 38.7 | 0 | 96.6325 | 905.2138 | 71.02% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38.7
7486 | 0 | 0 | 0 | 7.858 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3798 | 36.1 | 0 | 90.3798 | 817.2717 | 64.12% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.1
7487 | 0 | 0 | 0 | 12.2907 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0962 | 33.9 | 0 | 85.0962 | 735.5861 | 57.72% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.9
7488 | 0 | 0 | 0 | 16.7234 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7968 | 32.1 | 0 | 80.7968 | 659.0333 | 51.71% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.1
7489 | 0 | 0 | 0 | 17.7308 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6467 | 31.2 | 0 | 78.6467 | 585.0009 | 45.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.2
7490 | 0 | 0 | 0 | 8.261 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1537 | 31 | 0 | 78.1537 | 511.5146 | 40.13% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31
7491 | 0 | 0 | 0 | 9.6714 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6981 | 30.8 | 0 | 77.6981 | 438.5721 | 34.41% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.8
7492 | 0 | 0 | 0 | 3.2238 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.721 | 31.7 | 0 | 79.721 | 363.0939 | 28.49% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.7
7493 | 0 | 0 | 0 | 6.6491 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.279 | 33.2 | 0 | 83.279 | 283.3269 | 22.23% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.2
7494 | 0 | 0 | 0 | 5.0372 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283.3269 | 22.23% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
7495 | 29 | 5 | 4 | 2.8208 | 5.4 | 14.5962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283.3269 | 22.23% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
7496 | 565 | 117 | 30 | 3.2238 | 7.6 | 284.3743 | 0 | 0 | 0 | 22.5907 | 0 | 0 | 22.5907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283.3269 | 22.23% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 22.5907
7497 | 804 | 300 | 48 | 2.4178 | 11.7 | 404.6672 | 203.3162 | 0 | 172.1163 | 65.4318 | 0 | 12.2159 | 53.2159 | 0 | 0 | 0 | 0 | 0 | 172.1163 | 0 | 446.0478 | 35% | 9.3696 | 0 | 9.7896 | 19.58% | 41
7498 | 898 | 458 | 55 | 2.0149 | 14.3 | 451.979 | 263.4172 | 0 | 228.2735 | 102.6736 | 6.0368 | 25 | 71.6368 | 0 | 0 | 0 | 0 | 0 | 228.2735 | 0 | 661.8603 | 51.93% | 19.175 | 0 | 29.8241 | 59.65% | 40.6
7499 | 939 | 570 | 59 | 2.2164 | 15.8 | 472.615 | 292.4065 | 0 | 255.5367 | 109.2 | 9.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 255.5367 | 0 | 903.4479 | 70.89% | 19.175 | 0 | 49.8587 | 99.72% | 40.8
7500 | 957 | 624 | 60 | 6.8506 | 16.5 | 481.6747 | 306.0287 | 0 | 266.028 | 110.1 | 35.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 266.028 | 0 | 1154.954 | 90.62% | 0 | 0 | 49.8587 | 99.72% | 39.9
7501 | 945 | 617 | 65 | 6.8506 | 16.7 | 475.6349 | 301.7639 | 0 | 262.0744 | 111.4 | 36.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 262.0744 | 0 | 1274.5104 | 100% | 0 | 0 | 49.8587 | 99.72% | 38.6
7502 | 830 | 531 | 93 | 7.2535 | 17.4 | 417.7534 | 0 | 256.6369 | 0 | 112.3 | 37.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.8587 | 99.72% | 37.7
7503 | 695 | 391 | 91 | 8.0595 | 17.4 | 349.8056 | 0 | 201.4441 | 0 | 84.8255 | 23.4128 | 0 | 61.4128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 49.8587 | 99.72% | 38
7504 | 53 | 135 | 116 | 7.052 | 16.3 | 26.6758 | 0 | 13.0151 | 0 | 13.5135 | 0 | 0 | 13.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.742 | 47.48% | 38.5135
7505 | 10 | 37 | 36 | 5.2387 | 14.7 | 5.0332 | 0 | 0 | 0 | 2.6456 | 0 | 0 | 2.6456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.7268 | 0 | 0% | 25.3724
7506 | 0 | 0 | 0 | 2.8208 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.7282 | 41.6 | 0 | 103.7282 | 1171.0198 | 91.88% | 0 | 0 | 0 | 0% | 41.6
7507 | 0 | 0 | 0 | 3.0223 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2801 | 41 | 0 | 102.2801 | 1069.2118 | 83.89% | 0 | 0 | 0 | 0% | 41
7508 | 0 | 0 | 0 | 4.0297 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0332 | 38.8 | 0 | 97.0332 | 973.6615 | 76.39% | 0 | 0 | 0 | 0% | 38.8
7509 | 0 | 0 | 0 | 7.455 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7921 | 36.1 | 0 | 90.7921 | 885.7546 | 69.5% | 0 | 0 | 0 | 0% | 36.1
7510 | 0 | 0 | 0 | 10.8803 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2025 | 33.3 | 0 | 84.2025 | 805.8283 | 63.23% | 0 | 0 | 0 | 0% | 33.3
7511 | 0 | 0 | 0 | 11.4848 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7488 | 31 | 0 | 78.7488 | 732.3975 | 57.47% | 0 | 0 | 0 | 0% | 31
7512 | 0 | 0 | 0 | 10.4773 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2044 | 29.5 | 0 | 75.2044 | 662.9502 | 52.02% | 0 | 0 | 0 | 0% | 29.5
7513 | 0 | 0 | 0 | 15.313 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.1766 | 28.6 | 0 | 73.1766 | 595.4491 | 46.72% | 0 | 0 | 0 | 0% | 28.6
7514 | 0 | 0 | 0 | 19.7457 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.3128 | 28.2 | 0 | 72.3128 | 528.7703 | 41.49% | 0 | 0 | 0 | 0% | 28.2
7515 | 0 | 0 | 0 | 21.5591 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5233 | 28.3 | 0 | 72.5233 | 461.8754 | 36.24% | 0 | 0 | 0 | 0% | 28.3
7516 | 0 | 0 | 0 | 18.5368 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5118 | 28.8 | 0 | 73.5118 | 394.0072 | 30.91% | 0 | 0 | 0 | 0% | 28.8
7517 | 0 | 0 | 0 | 12.0892 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.91 | 29.5 | 0 | 74.91 | 324.4999 | 25.46% | 0 | 0 | 0 | 0% | 29.5
7518 | 0 | 0 | 0 | 7.455 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9409 | 30.4 | 0 | 76.9409 | 252.6377 | 19.82% | 0 | 0 | 0 | 0% | 30.4
7519 | 0 | 2 | 2 | 6.4476 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8054 | 32.4294 | 0 | 81.8054 | 175.0471 | 13.73% | 0 | 0 | 0 | 0% | 32.4294
7520 | 0 | 35 | 35 | 6.0446 | 14.2 | 0 | 0 | 0 | 0 | 2.1946 | 0 | 0 | 2.1946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175.0471 | 13.73% | 0 | 0 | 0 | 0% | 2.1946
7521 | 0 | 87 | 87 | 9.2684 | 14.4 | 0 | 0 | 0 | 0 | 6.6244 | 0 | 0 | 6.6244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175.0471 | 13.73% | 0 | 0 | 0 | 0% | 6.6244
7522 | 2 | 186 | 184 | 11.8877 | 13.9 | 1.0066 | 0 | 0.58581 | 0 | 15.76 | 0 | 0 | 15.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175.0471 | 13.73% | 0 | 0 | 0 | 0% | 15.76
7523 | 121 | 319 | 247 | 13.2981 | 12.9 | 60.9014 | 0 | 37.614 | 0 | 35.6519 | 0 | 0 | 35.6519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175.0471 | 13.73% | 0 | 0 | 0 | 0% | 35.6519
7524 | 263 | 439 | 279 | 11.8877 | 14.3 | 132.3725 | 84.0301 | 0 | 55.2501 | 67.8613 | 0 | 15.3306 | 52.5306 | 0 | 0 | 0 | 0 | 0 | 55.2501 | 0 | 226.9051 | 17.8% | 11.7586 | 0 | 12.2875 | 24.58% | 37.2
7525 | 2 | 218 | 215 | 14.7085 | 14 | 1.0066 | 0 | 0.6381 | 0 | 18.0284 | 0 | 0 | 18.0284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 11.7605 | 0 | 0% | 29.7889
7526 | 1 | 152 | 151 | 12.6937 | 13.7 | 0.50332 | 0 | 0.30862 | 0 | 12.0365 | 0 | 0 | 12.0365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 12.0365
7527 | 0 | 116 | 115 | 14.7085 | 13.3 | 0 | 0 | 0 | 0 | 8.9467 | 0 | 0 | 8.9467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 8.9467
7528 | 0 | 69 | 69 | 12.0892 | 13.3 | 0 | 0 | 0 | 0 | 5.0614 | 0 | 0 | 5.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 5.0614
7529 | 1 | 22 | 22 | 15.9175 | 12.9 | 0.50332 | 0 | 0 | 0 | 1.1247 | 0 | 0 | 1.1247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 1.1247
7530 | 0 | 0 | 0 | 8.4625 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7531 | 0 | 0 | 0 | 9.8729 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7532 | 0 | 0 | 0 | 8.0595 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7533 | 0 | 0 | 0 | 8.6639 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7534 | 0 | 0 | 0 | 5.2387 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7535 | 0 | 0 | 0 | 9.8729 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7536 | 0 | 0 | 0 | 14.91 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7537 | 0 | 0 | 0 | 9.2684 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7538 | 0 | 0 | 0 | 13.2981 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7539 | 0 | 0 | 0 | 15.313 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7540 | 0 | 0 | 0 | 17.7308 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7541 | 0 | 0 | 0 | 18.1338 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7542 | 0 | 0 | 0 | 10.2758 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7543 | 5 | 3 | 3 | 6.0446 | 9.5 | 2.5166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7544 | 14 | 43 | 42 | 6.6491 | 10.5 | 7.0464 | 0 | 0 | 0 | 3.6742 | 0 | 0 | 3.6742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 3.6742
7545 | 0 | 116 | 116 | 11.8877 | 11.3 | 0 | 0 | 0 | 0 | 9.6926 | 0 | 0 | 9.6926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 9.6926
7546 | 12 | 217 | 209 | 9.2684 | 12.7 | 6.0398 | 0 | 3.5098 | 0 | 19.3026 | 0 | 0 | 19.3026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 19.3026
7547 | 16 | 267 | 255 | 8.8654 | 14 | 8.0531 | 0 | 4.9653 | 0 | 23.6183 | 0 | 0 | 23.6183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 23.6183
7548 | 1 | 223 | 221 | 14.1041 | 14.6 | 0.50332 | 0 | 0.31924 | 0 | 18.4841 | 0 | 0 | 18.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 18.4841
7549 | 8 | 235 | 228 | 11.2833 | 15.3 | 4.0265 | 0 | 2.5502 | 0 | 19.7966 | 0 | 0 | 19.7966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 19.7966
7550 | 0 | 154 | 153 | 9.0669 | 15.8 | 0 | 0 | 0 | 0 | 12.0452 | 0 | 0 | 12.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 12.0452
7551 | 0 | 132 | 131 | 12.4922 | 16.4 | 0 | 0 | 0 | 0 | 10.3745 | 0 | 0 | 10.3745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 10.3745
7552 | 0 | 108 | 107 | 13.4996 | 16.5 | 0 | 0 | 0 | 0 | 8.8529 | 0 | 0 | 8.8529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 8.8529
7553 | 0 | 35 | 35 | 10.8803 | 16.2 | 0 | 0 | 0 | 0 | 2.3492 | 0 | 0 | 2.3492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 2.3492
7554 | 0 | 0 | 0 | 4.8357 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7555 | 0 | 0 | 0 | 5.0372 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7556 | 0 | 0 | 0 | 2.6193 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7557 | 0 | 0 | 0 | 4.6342 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7558 | 0 | 0 | 0 | 2.4178 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7559 | 0 | 0 | 0 | 4.2312 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7560 | 0 | 0 | 0 | 4.0297 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7561 | 0 | 0 | 0 | 2.6193 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7562 | 0 | 0 | 0 | 2.4178 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7563 | 0 | 0 | 0 | 3.2238 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7564 | 0 | 0 | 0 | 4.4327 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7565 | 0 | 0 | 0 | 3.2238 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7566 | 0 | 0 | 0 | 3.0223 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7567 | 4 | 4 | 3 | 2.4178 | 10.1 | 2.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 0
7568 | 523 | 124 | 48 | 3.6268 | 12 | 263.235 | 0 | 0 | 0 | 21.3135 | 0 | 0 | 21.3135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.9051 | 17.8% | 0 | 0 | 0 | 0% | 21.3135
7569 | 788 | 321 | 83 | 5.2387 | 15.1 | 396.6141 | 197.5398 | 0 | 165.5968 | 65.5138 | 0 | 9.0569 | 56.4569 | 0 | 0 | 0 | 0 | 0 | 165.5968 | 0 | 382.3351 | 30% | 6.9466 | 0 | 7.2599 | 14.52% | 47.4
7570 | 863 | 446 | 70 | 2.4178 | 17.2 | 434.3629 | 252.0601 | 0 | 217.5548 | 94.358 | 0 | 23.629 | 70.729 | 0 | 0 | 0 | 0 | 0 | 217.5548 | 0 | 586.5331 | 46.02% | 18.1234 | 0 | 26.2006 | 52.4% | 47.1
7571 | 802 | 507 | 75 | 3.0223 | 18.4 | 403.6605 | 248.467 | 0 | 214.0114 | 103.2 | 3.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 214.0114 | 0 | 787.4054 | 61.78% | 19.175 | 0 | 46.2404 | 92.48% | 46.8
7572 | 941 | 603 | 60 | 7.6565 | 19.4 | 473.6217 | 300.1551 | 0 | 260.1395 | 104.6 | 24.9098 | 4.6902 | 75 | 0 | 0 | 0 | 0 | 0 | 260.1395 | 0 | 1031.5737 | 80.94% | 3.5974 | 0 | 50 | 100% | 45.4
7573 | 949 | 601 | 59 | 12.2907 | 19.7 | 477.6482 | 301.9783 | 0 | 258.9979 | 105.3 | 30.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 258.9979 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.7
7574 | 913 | 529 | 59 | 12.8952 | 19.9 | 459.5288 | 0 | 280.7301 | 0 | 105.6 | 30.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.4
7575 | 850 | 403 | 53 | 10.8803 | 20 | 427.8198 | 0 | 243.8207 | 0 | 89.0881 | 22.094 | 0 | 66.994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.9
7576 | 722 | 238 | 43 | 13.0966 | 19.4 | 363.3952 | 0 | 175.3645 | 0 | 45.3076 | 0 | 0 | 45.3076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.3076
7577 | 370 | 66 | 21 | 6.0446 | 18.3 | 186.2274 | 0 | 0 | 0 | 9.3486 | 0 | 0 | 9.3486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.8765 | 47.75% | 34.3486
7578 | 0 | 0 | 0 | 5.0372 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.7627 | 26.6503 | 0 | 68.7627 | 1211.0807 | 95.02% | 0 | 22.8497 | 0 | 0% | 49.5
7579 | 0 | 0 | 0 | 9.4699 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.1154 | 47.9 | 0 | 119.1154 | 1088.9759 | 85.44% | 0 | 0 | 0 | 0% | 47.9
7580 | 0 | 0 | 0 | 5.2387 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5175 | 44 | 0 | 109.5175 | 978.1665 | 76.75% | 0 | 0 | 0 | 0% | 44
7581 | 0 | 0 | 0 | 3.2238 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.306 | 39.8 | 0 | 99.306 | 879.337 | 68.99% | 0 | 0 | 0 | 0% | 39.8
7582 | 0 | 0 | 0 | 2.4178 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5371 | 37 | 0 | 92.5371 | 788.5343 | 61.87% | 0 | 0 | 0 | 0% | 37
7583 | 0 | 0 | 0 | 2.6193 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0136 | 34.7 | 0 | 87.0136 | 704.2264 | 55.25% | 0 | 0 | 0 | 0% | 34.7
7584 | 0 | 0 | 0 | 3.0223 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.211 | 33.1 | 0 | 83.211 | 624.5466 | 49% | 0 | 0 | 0 | 0% | 33.1
7585 | 0 | 0 | 0 | 6.8506 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.363 | 32.7 | 0 | 82.363 | 545.9998 | 42.84% | 0 | 0 | 0 | 0% | 32.7
7586 | 0 | 0 | 0 | 7.6565 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1728 | 32.6 | 0 | 82.1728 | 467.7241 | 36.7% | 0 | 0 | 0 | 0% | 32.6
7587 | 0 | 0 | 0 | 12.0892 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.166 | 33.4 | 0 | 84.166 | 387.1338 | 30.38% | 0 | 0 | 0 | 0% | 33.4
7588 | 0 | 0 | 0 | 14.3056 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1234 | 37.1 | 0 | 93.1234 | 295.9413 | 23.22% | 0 | 0 | 0 | 0% | 37.1
7589 | 0 | 0 | 0 | 19.7457 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3535 | 43 | 0 | 107.3535 | 187.8205 | 14.74% | 0 | 0 | 0 | 0% | 43
7590 | 0 | 0 | 0 | 19.9472 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.8205 | 14.74% | 0 | 0 | 0 | 0% | 0
7591 | 1 | 2 | 2 | 21.5591 | 14.6 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.8205 | 14.74% | 0 | 0 | 0 | 0% | 0
7592 | 329 | 84 | 37 | 17.9323 | 15.4 | 165.5914 | 0 | 0 | 0 | 14.3356 | 0 | 0 | 14.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.8205 | 14.74% | 0 | 0 | 0 | 0% | 14.3356
7593 | 739 | 284 | 62 | 20.5517 | 17.6 | 371.9515 | 184.7502 | 0 | 144.575 | 55.7225 | 0 | 3.7613 | 51.9613 | 0 | 0 | 0 | 0 | 0 | 144.575 | 0 | 325.9314 | 25.57% | 2.8849 | 0 | 3.0154 | 6.031% | 48.2
7594 | 874 | 441 | 62 | 20.3502 | 18.7 | 439.8994 | 254.927 | 0 | 210.0839 | 99.0825 | 0.69126 | 25 | 73.3913 | 0 | 0 | 0 | 0 | 0 | 210.0839 | 0 | 526.6221 | 41.32% | 19.175 | 0 | 23.0581 | 46.12% | 47.7
7595 | 925 | 555 | 66 | 16.119 | 21.1 | 465.5686 | 286.1041 | 0 | 241.9019 | 102.7 | 2.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 241.9019 | 0 | 757.7081 | 59.45% | 19.175 | 0 | 43.1008 | 86.2% | 47.3
7596 | 924 | 597 | 66 | 14.3056 | 21.7 | 465.0653 | 294.2737 | 0 | 250.7204 | 104.2 | 20.5944 | 8.6056 | 75 | 0 | 0 | 0 | 0 | 0 | 250.7204 | 0 | 997.2183 | 78.24% | 6.6005 | 0 | 50 | 100% | 45.8
7597 | 750 | 516 | 87 | 7.6565 | 22.1 | 377.488 | 238.1931 | 0 | 202.2704 | 105.1 | 30.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 202.2704 | 0 | 1190.4449 | 93.4% | 0 | 0 | 50 | 100% | 44.9
7598 | 864 | 511 | 68 | 0.20149 | 22 | 434.8662 | 250.5959 | 14.5827 | 217.9046 | 101.6873 | 28.6937 | 0 | 72.9937 | 0 | 0 | 0 | 0 | 0 | 217.9046 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.3
7599 | 852 | 404 | 56 | 0 | 22.1 | 428.8264 | 0 | 243.5243 | 0 | 80.3651 | 17.7826 | 0 | 62.5826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.8
7600 | 403 | 147 | 24 | 0 | 11.2 | 202.8369 | 0 | 97.526 | 0 | 25.4041 | 0 | 0 | 25.4041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.4959 | 26.4897 | 52.98% | 47.9
7601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9697 | 24 | 0 | 61.9697 | 1217.7943 | 95.55% | 0 | 25 | 0.36111 | 0.7222% | 49
7602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.6489 | 49.6 | 0 | 122.6489 | 1091.3351 | 85.63% | 0 | 0 | 0.36111 | 0.7222% | 49.6
7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.309 | 47.4 | 0 | 117.309 | 971.2092 | 76.2% | 0 | 0 | 0.36111 | 0.7222% | 47.4
7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3624 | 43.7 | 0 | 108.3624 | 861.6595 | 67.61% | 0 | 0 | 0.36111 | 0.7222% | 43.7
7605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7568 | 39.7 | 0 | 98.7568 | 763.469 | 59.9% | 0 | 0 | 0.36111 | 0.7222% | 39.7
7606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8027 | 36.8 | 0 | 91.8027 | 673.5661 | 52.85% | 0 | 0 | 0.36111 | 0.7222% | 36.8
7607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2761 | 34.5 | 0 | 86.2761 | 590.155 | 46.3% | 0 | 0 | 0.36111 | 0.7222% | 34.5
7608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1736 | 33.2 | 0 | 83.1736 | 510.474 | 40.05% | 0 | 0 | 0.36111 | 0.7222% | 33.2
7609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4985 | 32.5 | 0 | 81.4985 | 432.7709 | 33.96% | 0 | 0 | 0.36111 | 0.7222% | 32.5
7610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2589 | 32.4 | 0 | 81.2589 | 355.3337 | 27.88% | 0 | 0 | 0.36111 | 0.7222% | 32.4
7611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6516 | 33.4 | 0 | 83.6516 | 275.0241 | 21.58% | 0 | 0 | 0.36111 | 0.7222% | 33.4
7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7642 | 37.2 | 0 | 92.7642 | 183.8604 | 14.43% | 0 | 0 | 0.36111 | 0.7222% | 37.2
7613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.777 | 41.7886 | 0 | 103.777 | 79.5386 | 6.241% | 0 | 0 | 0.36111 | 0.7222% | 41.7886
7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5386 | 6.241% | 0 | 0 | 0.36111 | 0.7222% | 0
7615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5386 | 6.241% | 0 | 0 | 0.36111 | 0.7222% | 0
7616 | 137 | 48 | 22 | 3.8283 | 4.7 | 68.9545 | 0 | 0 | 0 | 6.7311 | 0 | 0 | 6.7311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5386 | 6.241% | 0 | 0 | 0.36111 | 0.7222% | 6.7311
7617 | 511 | 248 | 94 | 13.0966 | 15.8 | 257.1952 | 127.4124 | 0 | 95.1741 | 41.6506 | 0 | 0 | 41.6506 | 0 | 0 | 0 | 0 | 0 | 95.1741 | 0 | 170.7937 | 13.4% | 0 | 0 | 0.36111 | 0.7222% | 41.6506
7618 | 128 | 228 | 172 | 12.0892 | 16.4 | 64.4246 | 0 | 37.2858 | 0 | 26.7267 | 0 | 0 | 26.7267 | 0 | 0 | 0 | 59.6089 | 22.5733 | 0 | 59.6089 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 49.3
7619 | 72 | 296 | 256 | 17.9323 | 16.4 | 36.2389 | 0 | 22.2341 | 0 | 30.7543 | 0 | 0 | 30.7543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 30.7543
7620 | 16 | 248 | 237 | 26.1933 | 16.7 | 8.0531 | 0 | 5.0863 | 0 | 21.5429 | 0 | 0 | 21.5429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 21.5429
7621 | 64 | 292 | 254 | 22.365 | 17.1 | 32.2123 | 0 | 20.287 | 0 | 29.6781 | 0 | 0 | 29.6781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 29.6781
7622 | 170 | 301 | 210 | 24.9844 | 17.1 | 85.564 | 0 | 52.0821 | 0 | 35.4817 | 0 | 0 | 35.4817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 35.4817
7623 | 10 | 169 | 164 | 24.5814 | 14.2 | 5.0332 | 0 | 2.8481 | 0 | 14.6791 | 0 | 0 | 14.6791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 14.6791
7624 | 45 | 137 | 123 | 18.5368 | 13.2 | 22.6493 | 0 | 10.8503 | 0 | 14.488 | 0 | 0 | 14.488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 14.488
7625 | 3 | 34 | 33 | 20.7532 | 12.2 | 1.51 | 0 | 0 | 0 | 2.2187 | 0 | 0 | 2.2187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 2.2187
7626 | 0 | 0 | 0 | 11.2833 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7627 | 0 | 0 | 0 | 8.261 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7628 | 0 | 0 | 0 | 12.2907 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7629 | 0 | 0 | 0 | 13.4996 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7630 | 0 | 0 | 0 | 11.0818 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7631 | 0 | 0 | 0 | 8.6639 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7632 | 0 | 0 | 0 | 15.716 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7633 | 0 | 0 | 0 | 15.716 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7634 | 0 | 0 | 0 | 10.4773 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7635 | 0 | 0 | 0 | 10.8803 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7636 | 0 | 0 | 0 | 14.1041 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7637 | 0 | 0 | 0 | 12.8952 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7638 | 0 | 0 | 0 | 18.9398 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7639 | 1 | 2 | 2 | 12.8952 | 8.6 | 0.50332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 0
7640 | 387 | 88 | 32 | 15.1115 | 9 | 194.7838 | 0 | 0 | 0 | 15.1708 | 0 | 0 | 15.1708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2417 | 9.12% | 0 | 0 | 0.36111 | 0.7222% | 15.1708
7641 | 733 | 272 | 58 | 9.4699 | 10.6 | 368.9316 | 182.299 | 0 | 148.6576 | 53.8069 | 2.2034 | 0 | 51.6034 | 0 | 0 | 0 | 0 | 0 | 148.6576 | 0 | 258.4326 | 20.28% | 0 | 0 | 0.36111 | 0.7222% | 49.4
7642 | 848 | 433 | 72 | 12.0892 | 12.6 | 426.8131 | 246.6664 | 0 | 207.1206 | 98.1823 | 0 | 24.4912 | 73.6912 | 0 | 0 | 0 | 0 | 0 | 207.1206 | 0 | 456.5433 | 35.82% | 18.7847 | 0 | 19.9996 | 40% | 49.2
7643 | 909 | 556 | 84 | 13.9026 | 13 | 457.5155 | 280.2661 | 0 | 237.3941 | 101.4 | 1.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 237.3941 | 0 | 683.6106 | 53.64% | 19.175 | 0 | 40.0461 | 80.09% | 48.6
7644 | 301 | 394 | 220 | 8.0595 | 13.2 | 151.4985 | 95.5147 | 0 | 68.3377 | 55.4559 | 0 | 4.2279 | 51.2279 | 0 | 0 | 0 | 0 | 0 | 68.3377 | 0 | 748.9756 | 58.77% | 3.2428 | 0 | 43.4363 | 86.87% | 47
7645 | 139 | 300 | 219 | 13.4996 | 12.9 | 69.9611 | 0 | 43.9782 | 0 | 34.7632 | 0 | 0 | 34.7632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748.9756 | 58.77% | 0 | 11.2368 | 31.6907 | 63.38% | 46
7646 | 643 | 568 | 236 | 13.9026 | 13.9 | 323.6331 | 196.6407 | 0 | 159.388 | 104 | 6.1682 | 22.8318 | 75 | 0 | 0 | 0 | 0 | 0 | 159.388 | 0 | 901.4301 | 70.73% | 17.512 | 0 | 49.9992 | 100% | 46
7647 | 209 | 222 | 128 | 11.8877 | 12.6 | 105.1933 | 59.3163 | 0 | 32.5079 | 29.1675 | 0 | 0 | 29.1675 | 0 | 0 | 0 | 0 | 0 | 32.5079 | 0 | 932.5239 | 73.17% | 0 | 17.4325 | 31.7768 | 63.55% | 46.6
7648 | 192 | 150 | 92 | 11.2833 | 12.3 | 96.6369 | 0 | 46.0659 | 0 | 20.7641 | 0 | 0 | 20.7641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 932.5239 | 73.17% | 0 | 25 | 5.6429 | 11.29% | 45.7641
7649 | 150 | 62 | 40 | 7.858 | 11.3 | 75.4976 | 0 | 0 | 0 | 6.9092 | 0 | 0 | 6.9092 | 0 | 0 | 0 | 93.5248 | 37.391 | 0 | 93.5248 | 840.7614 | 65.97% | 0 | 5.3999 | 6.9389e-16 | 1.388e-15% | 49.7
7650 | 0 | 0 | 0 | 4.0297 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.8456 | 49.2 | 0 | 121.8456 | 715.0359 | 56.1% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 49.2
7651 | 0 | 0 | 0 | 2.0149 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.9258 | 47.6 | 0 | 117.9258 | 593.9637 | 46.6% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 47.6
7652 | 0 | 0 | 0 | 3.2238 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.6663 | 44.2 | 0 | 109.6663 | 482.6738 | 37.87% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 44.2
7653 | 0 | 0 | 0 | 1.4104 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2497 | 40.7 | 0 | 101.2497 | 381.3678 | 29.92% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 40.7
7654 | 0 | 0 | 0 | 2.8208 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0178 | 38.1 | 0 | 95.0178 | 287.4927 | 22.56% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 38.1
7655 | 0 | 0 | 0 | 3.8283 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7594 | 35.5 | 0 | 88.7594 | 200.9512 | 15.77% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 35.5
7656 | 0 | 0 | 0 | 1.6119 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9731 | 33.5 | 0 | 83.9731 | 120.1403 | 9.426% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 33.5
7657 | 0 | 0 | 0 | 2.0149 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1403 | 9.426% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
7658 | 0 | 0 | 0 | 5.0372 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1403 | 9.426% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
7659 | 0 | 0 | 0 | 3.8283 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1403 | 9.426% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
7660 | 0 | 0 | 0 | 3.4253 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1403 | 9.426% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
7661 | 0 | 0 | 0 | 1.2089 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1403 | 9.426% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
7662 | 0 | 0 | 0 | 3.0223 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1403 | 9.426% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
7663 | 0 | 2 | 2 | 2.4178 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1403 | 9.426% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 0
7664 | 387 | 105 | 51 | 1.8134 | 6.3 | 194.7838 | 0 | 0 | 0 | 15.9979 | 0 | 0 | 15.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1403 | 9.426% | 0 | 0 | 6.9389e-16 | 1.388e-15% | 15.9979
7665 | 699 | 267 | 64 | 6.8506 | 9.9 | 351.8189 | 173.4152 | 0 | 142.0118 | 57.1121 | 0 | 6.8061 | 50.3061 | 0 | 0 | 0 | 0 | 0 | 142.0118 | 0 | 257.3473 | 20.19% | 5.2203 | 0 | 5.4584 | 10.92% | 43.5
7666 | 807 | 416 | 75 | 9.6714 | 11.4 | 406.1771 | 234.105 | 0 | 197.0411 | 98.775 | 2.9375 | 25 | 70.8375 | 0 | 0 | 0 | 0 | 0 | 197.0411 | 0 | 447.7217 | 35.13% | 19.175 | 0 | 25.5084 | 51.02% | 42.9
7667 | 879 | 537 | 83 | 11.2833 | 12.8 | 442.416 | 270.6028 | 0 | 229.9252 | 107.3 | 7.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 229.9252 | 0 | 669.8677 | 52.56% | 19.175 | 0 | 45.5583 | 91.12% | 42.7
7668 | 899 | 592 | 86 | 9.2684 | 13.7 | 452.4823 | 284.7733 | 0 | 244.5887 | 108.2 | 27.6618 | 5.5382 | 75 | 0 | 0 | 0 | 0 | 0 | 244.5887 | 0 | 906.1809 | 71.1% | 4.2478 | 0 | 50 | 100% | 41.8
7669 | 914 | 591 | 81 | 10.2758 | 14.5 | 460.0321 | 288.6461 | 0 | 247.6575 | 109.6 | 34.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 247.6575 | 0 | 1145.4592 | 89.87% | 0 | 0 | 50 | 100% | 40.4
7670 | 903 | 526 | 73 | 11.6862 | 15.1 | 454.4956 | 211.7522 | 63.9132 | 180.1336 | 110.6 | 35.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 180.1336 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.4
7671 | 865 | 403 | 58 | 10.4773 | 15 | 435.3695 | 0 | 244.6359 | 0 | 99.1883 | 29.6442 | 0 | 69.5442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.9
7672 | 741 | 236 | 44 | 10.8803 | 14.4 | 372.9582 | 0 | 176.7621 | 0 | 51.3939 | 4.347 | 0 | 47.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 42.7
7673 | 359 | 61 | 20 | 9.6714 | 12.8 | 180.6909 | 0 | 0 | 0 | 8.3944 | 0 | 0 | 8.3944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.8632 | 47.73% | 33.3944
7674 | 0 | 0 | 0 | 8.4625 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.9985 | 21.6746 | 0 | 56.9985 | 1222.5856 | 95.93% | 0 | 22.8254 | 0 | 0% | 44.5
7675 | 0 | 0 | 0 | 4.8357 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3787 | 44 | 0 | 109.3787 | 1112.184 | 87.26% | 0 | 0 | 0 | 0% | 44
7676 | 0 | 0 | 0 | 5.0372 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2708 | 41.5 | 0 | 103.2708 | 1008.9076 | 79.16% | 0 | 0 | 0 | 0% | 41.5
7677 | 0 | 0 | 0 | 4.8357 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4698 | 38.7 | 0 | 96.4698 | 913.5972 | 71.68% | 0 | 0 | 0 | 0% | 38.7
7678 | 0 | 0 | 0 | 3.0223 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7243 | 35.9 | 0 | 89.7243 | 826.2036 | 64.83% | 0 | 0 | 0 | 0% | 35.9
7679 | 0 | 0 | 0 | 3.8283 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7767 | 33 | 0 | 82.7767 | 747.0933 | 58.62% | 0 | 0 | 0 | 0% | 33
7680 | 0 | 0 | 0 | 4.0297 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9748 | 31 | 0 | 77.9748 | 673.6228 | 52.85% | 0 | 0 | 0 | 0% | 31
7681 | 0 | 0 | 0 | 1.6119 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1225 | 29.8 | 0 | 75.1225 | 603.409 | 47.34% | 0 | 0 | 0 | 0% | 29.8
7682 | 0 | 0 | 0 | 2.2164 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.459 | 29.5 | 0 | 74.459 | 533.9187 | 41.89% | 0 | 0 | 0 | 0% | 29.5
7683 | 0 | 0 | 0 | 3.8283 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2374 | 29.4 | 0 | 74.2374 | 464.6603 | 36.46% | 0 | 0 | 0 | 0% | 29.4
7684 | 0 | 0 | 0 | 4.4327 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0463 | 30.2 | 0 | 76.0463 | 393.3608 | 30.86% | 0 | 0 | 0 | 0% | 30.2
7685 | 0 | 0 | 0 | 3.8283 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4525 | 31.2 | 0 | 78.4525 | 319.2571 | 25.05% | 0 | 0 | 0 | 0% | 31.2
7686 | 0 | 0 | 0 | 4.6342 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6191 | 32.1 | 0 | 80.6191 | 242.5957 | 19.03% | 0 | 0 | 0 | 0% | 32.1
7687 | 0 | 1 | 1 | 3.4253 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2751 | 35.3 | 0 | 88.2751 | 156.7086 | 12.3% | 0 | 0 | 0 | 0% | 35.3
7688 | 470 | 101 | 37 | 4.0297 | 7.2 | 236.5592 | 0 | 0 | 0 | 17.0132 | 0 | 0 | 17.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156.7086 | 12.3% | 0 | 0 | 0 | 0% | 17.0132
7689 | 761 | 321 | 103 | 5.2387 | 11.2 | 383.0245 | 188.3495 | 0 | 156.9247 | 73.4807 | 0 | 16.7404 | 56.7404 | 0 | 0 | 0 | 0 | 0 | 156.9247 | 0 | 304.5195 | 23.89% | 12.8399 | 0 | 13.4277 | 26.86% | 40
7690 | 707 | 490 | 191 | 10.6788 | 14.2 | 355.8454 | 204.5572 | 0 | 168.8807 | 108.2707 | 8.9353 | 25 | 74.3353 | 0 | 0 | 0 | 0 | 0 | 168.8807 | 0 | 463.592 | 36.37% | 19.175 | 0 | 33.4806 | 66.96% | 40.4
7691 | 290 | 436 | 288 | 11.2833 | 15 | 145.962 | 89.1446 | 0 | 60.7465 | 68.7715 | 0 | 13.7857 | 54.9857 | 0 | 0 | 0 | 0 | 0 | 60.7465 | 0 | 520.8104 | 40.86% | 10.5737 | 0 | 44.5383 | 89.08% | 41.2
7692 | 1 | 195 | 192 | 8.0595 | 13.7 | 0.50332 | 0 | 0.31622 | 0 | 15.8152 | 0 | 0 | 15.8152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520.8104 | 40.86% | 0 | 25 | 18.3979 | 36.8% | 40.8152
7693 | 0 | 176 | 174 | 6.6491 | 13 | 0 | 0 | 0 | 0 | 14.0315 | 0 | 0 | 14.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520.8104 | 40.86% | 0 | 17.5953 | 0 | 0% | 31.6268
7694 | 0 | 144 | 143 | 9.2684 | 13.6 | 0 | 0 | 0 | 0 | 11.3032 | 0 | 0 | 11.3032 | 0 | 0 | 0 | 68.6819 | 26.6968 | 0 | 68.6819 | 457.625 | 35.91% | 0 | 0 | 0 | 0% | 38
7695 | 1 | 141 | 139 | 19.3427 | 14.9 | 0.50332 | 0 | 0.28183 | 0 | 11.4599 | 0 | 0 | 11.4599 | 0 | 0 | 0 | 69.3987 | 26.9401 | 0 | 69.3987 | 393.7452 | 30.89% | 0 | 0 | 0 | 0% | 38.4
7696 | 161 | 113 | 80 | 17.5294 | 15.4 | 81.0341 | 0 | 38.185 | 0 | 17.4907 | 0 | 0 | 17.4907 | 0 | 0 | 0 | 62.3545 | 23.8093 | 0 | 62.3545 | 336.6321 | 26.41% | 0 | 0 | 0 | 0% | 41.3
7697 | 146 | 51 | 30 | 14.7085 | 15.2 | 73.4843 | 0 | 0 | 0 | 5.6909 | 0 | 0 | 5.6909 | 0 | 0 | 0 | 93.4957 | 37.2091 | 0 | 93.4957 | 245.4797 | 19.26% | 0 | 0 | 0 | 0% | 42.9
7698 | 0 | 0 | 0 | 8.0595 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.7472 | 44.1 | 0 | 109.7472 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 44.1
7699 | 0 | 0 | 0 | 6.4476 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7700 | 0 | 0 | 0 | 7.052 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7701 | 0 | 0 | 0 | 8.4625 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7702 | 0 | 0 | 0 | 4.0297 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7703 | 0 | 0 | 0 | 2.2164 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7704 | 0 | 0 | 0 | 2.2164 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7705 | 0 | 0 | 0 | 1.6119 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7706 | 0 | 0 | 0 | 2.2164 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7707 | 0 | 0 | 0 | 8.0595 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7708 | 0 | 0 | 0 | 7.858 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7709 | 0 | 0 | 0 | 8.6639 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7710 | 0 | 0 | 0 | 6.0446 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7711 | 0 | 1 | 1 | 7.052 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 0
7712 | 222 | 63 | 28 | 6.8506 | 8 | 111.7365 | 0 | 0 | 0 | 9.5566 | 0 | 0 | 9.5566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.6135 | 10.56% | 0 | 0 | 0 | 0% | 9.5566
7713 | 716 | 256 | 54 | 2.8208 | 11.1 | 360.3752 | 176.8089 | 0 | 147.1927 | 48.8117 | 0 | 0 | 48.8117 | 0 | 0 | 0 | 0 | 0 | 147.1927 | 0 | 273.3214 | 21.45% | 0 | 0 | 0 | 0% | 48.8117
7714 | 849 | 415 | 63 | 4.2312 | 13.5 | 427.3165 | 245.0176 | 0 | 210.3274 | 91.1498 | 0 | 21.3249 | 69.8249 | 0 | 0 | 0 | 0 | 0 | 210.3274 | 0 | 471.5245 | 37% | 16.3562 | 0 | 17.1073 | 34.21% | 48.5
7715 | 908 | 530 | 69 | 4.0297 | 14.9 | 457.0122 | 278.7108 | 0 | 241.9001 | 101.3 | 1.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 241.9001 | 0 | 699.4805 | 54.88% | 19.175 | 0 | 37.163 | 74.33% | 48.7
7716 | 929 | 586 | 71 | 7.2535 | 15.7 | 467.5819 | 293.2765 | 0 | 253.9526 | 102.6 | 11.5983 | 16.0017 | 75 | 0 | 0 | 0 | 0 | 0 | 253.9526 | 0 | 938.7942 | 73.66% | 12.2733 | 0 | 50 | 100% | 47.4
7717 | 927 | 580 | 71 | 10.8803 | 15.7 | 466.5752 | 291.6991 | 0 | 250.2209 | 103.2 | 28.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 250.2209 | 0 | 1174.5912 | 92.16% | 0 | 0 | 50 | 100% | 46.8
7718 | 901 | 512 | 67 | 13.2981 | 15.6 | 453.489 | 184.7154 | 89.3866 | 156.3707 | 103.6 | 28.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 156.3707 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.4
7719 | 843 | 391 | 60 | 12.4922 | 15.4 | 424.2966 | 0 | 236.7643 | 0 | 89.6347 | 21.2674 | 0 | 68.3674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47.1
7720 | 717 | 227 | 45 | 4.6342 | 15.9 | 360.8786 | 0 | 169.0781 | 0 | 44.9891 | 0 | 0 | 44.9891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.0109 | 44.7598 | 89.52% | 50
7721 | 351 | 59 | 20 | 10.4773 | 13.3 | 176.6644 | 0 | 0 | 0 | 8.0838 | 0 | 0 | 8.0838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 18.6153 | 37.23% | 33.0838
7722 | 0 | 0 | 0 | 4.6342 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1019 | 32.1993 | 0 | 81.1019 | 1197.7133 | 93.97% | 0 | 17.8007 | 0 | 0% | 50
7723 | 0 | 0 | 0 | 2.0149 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0741 | 49.7 | 0 | 123.0741 | 1070.7969 | 84.02% | 0 | 0 | 0 | 0% | 49.7
7724 | 0 | 0 | 0 | 1.8134 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.5764 | 45.8 | 0 | 113.5764 | 955.1791 | 74.94% | 0 | 0 | 0 | 0% | 45.8
7725 | 0 | 0 | 0 | 2.6193 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7055 | 41.3 | 0 | 102.7055 | 852.4299 | 66.88% | 0 | 0 | 0 | 0% | 41.3
7726 | 0 | 0 | 0 | 5.8431 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5686 | 37.9 | 0 | 94.5686 | 759.3765 | 59.58% | 0 | 0 | 0 | 0% | 37.9
7727 | 0 | 0 | 0 | 4.0297 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5501 | 35.4 | 0 | 88.5501 | 673.3576 | 52.83% | 0 | 0 | 0 | 0% | 35.4
7728 | 0 | 0 | 0 | 3.8283 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1678 | 34 | 0 | 85.1678 | 591.3379 | 46.4% | 0 | 0 | 0 | 0% | 34
7729 | 0 | 0 | 0 | 4.0297 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4947 | 33.3 | 0 | 83.4947 | 511.3209 | 40.12% | 0 | 0 | 0 | 0% | 33.3
7730 | 0 | 0 | 0 | 2.6193 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4947 | 33.3 | 0 | 83.4947 | 431.2877 | 33.84% | 0 | 0 | 0 | 0% | 33.3
7731 | 0 | 0 | 0 | 2.0149 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8838 | 34.3 | 0 | 85.8838 | 348.3471 | 27.33% | 0 | 0 | 0 | 0% | 34.3
7732 | 0 | 0 | 0 | 2.8208 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4732 | 38.3 | 0 | 95.4732 | 254.0244 | 19.93% | 0 | 0 | 0 | 0% | 38.3
7733 | 0 | 0 | 0 | 3.4253 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.1009 | 44.8 | 0 | 111.1009 | 141.0543 | 11.07% | 0 | 0 | 0 | 0% | 44.8
7734 | 0 | 0 | 0 | 4.6342 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.1474 | 25.3672 | 0 | 65.1474 | 81.098 | 6.363% | 0 | 0 | 0 | 0% | 25.3672
7735 | 0 | 2 | 1 | 4.8357 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.098 | 6.363% | 0 | 0 | 0 | 0% | 0
7736 | 31 | 46 | 43 | 3.8283 | 5.3 | 15.6028 | 0 | 0 | 0 | 4.5451 | 0 | 0 | 4.5451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.098 | 6.363% | 0 | 0 | 0 | 0% | 4.5451
7737 | 147 | 203 | 158 | 2.0149 | 8.4 | 73.9877 | 0 | 36.2211 | 0 | 26.0971 | 0 | 0 | 26.0971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.098 | 6.363% | 0 | 0 | 0 | 0% | 26.0971
7738 | 195 | 312 | 228 | 1.2089 | 11.5 | 98.1469 | 0 | 56.1378 | 0 | 38.1829 | 0 | 0 | 38.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.098 | 6.363% | 0 | 0 | 0 | 0% | 38.1829
7739 | 343 | 424 | 243 | 3.4253 | 12.7 | 172.6379 | 105.1358 | 0 | 79.6993 | 60.7425 | 0 | 5.7713 | 54.9713 | 0 | 0 | 0 | 0 | 0 | 79.6993 | 0 | 157.4711 | 12.36% | 4.4266 | 0 | 4.6305 | 9.261% | 49.2
7740 | 732 | 544 | 137 | 3.6268 | 13.8 | 368.4283 | 230.7062 | 0 | 197.2761 | 102 | 2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 197.2761 | 0 | 346.514 | 27.19% | 19.175 | 0 | 24.6892 | 49.38% | 48
7741 | 698 | 546 | 160 | 3.4253 | 14.5 | 351.3155 | 219.2554 | 0 | 186.6068 | 102.6 | 2.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 186.6068 | 0 | 525.3329 | 41.22% | 19.175 | 0 | 44.7479 | 89.5% | 47.4
7742 | 251 | 336 | 207 | 1.6119 | 14.9 | 126.3327 | 76.2295 | 0 | 53.071 | 42.4877 | 0 | 0 | 42.4877 | 0 | 0 | 0 | 0 | 0 | 53.071 | 0 | 576.189 | 45.21% | 0 | 4.7123 | 39.8192 | 79.64% | 47.2
7743 | 157 | 276 | 208 | 4.4327 | 15 | 79.0208 | 0 | 43.9439 | 0 | 32.9844 | 0 | 0 | 32.9844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.189 | 45.21% | 0 | 15.4156 | 23.6956 | 47.39% | 48.4
7744 | 95 | 161 | 139 | 7.455 | 13.5 | 47.8152 | 0 | 22.2741 | 0 | 19.8388 | 0 | 0 | 19.8388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.189 | 45.21% | 0 | 22.6551 | 0 | 0% | 42.4939
7745 | 52 | 48 | 41 | 6.4476 | 12.3 | 26.1725 | 0 | 0 | 0 | 4.7144 | 0 | 0 | 4.7144 | 0 | 0 | 0 | 112.6015 | 45.2856 | 0 | 112.6015 | 462.0247 | 36.25% | 0 | 0 | 0 | 0% | 50
7746 | 0 | 0 | 0 | 4.6342 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.8591 | 50 | 0 | 123.8591 | 334.1395 | 26.22% | 0 | 0 | 0 | 0% | 50
7747 | 0 | 0 | 0 | 4.2312 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.8591 | 50 | 0 | 123.8591 | 206.2174 | 16.18% | 0 | 0 | 0 | 0% | 50
7748 | 0 | 0 | 0 | 2.8208 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.8297 | 46.3 | 0 | 114.8297 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 46.3
7749 | 0 | 0 | 0 | 3.0223 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7750 | 0 | 0 | 0 | 2.8208 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7751 | 0 | 0 | 0 | 2.2164 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7752 | 0 | 0 | 0 | 2.6193 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7753 | 0 | 0 | 0 | 3.4253 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7754 | 0 | 0 | 0 | 1.4104 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7755 | 0 | 0 | 0 | 2.4178 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7756 | 0 | 0 | 0 | 1.4104 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7757 | 0 | 0 | 0 | 1.4104 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7758 | 0 | 0 | 0 | 1.6119 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7759 | 0 | 1 | 1 | 2.6193 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 0
7760 | 330 | 70 | 29 | 1.4104 | 5.3 | 166.0947 | 0 | 0 | 0 | 11.7615 | 0 | 0 | 11.7615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0422 | 6.986% | 0 | 0 | 0 | 0% | 11.7615
7761 | 668 | 248 | 66 | 1.6119 | 9.2 | 336.216 | 164.2539 | 0 | 135.7816 | 47.4191 | 0 | 0 | 47.4191 | 0 | 0 | 0 | 0 | 0 | 135.7816 | 0 | 220.9691 | 17.34% | 0 | 0 | 0 | 0% | 47.4191
7762 | 635 | 360 | 103 | 1.4104 | 12.1 | 319.6065 | 182.3738 | 0 | 152.8652 | 67.7145 | 0 | 8.8572 | 58.8572 | 0 | 0 | 0 | 0 | 0 | 152.8652 | 0 | 369.4947 | 28.99% | 6.7935 | 0 | 7.1075 | 14.22% | 50
7763 | 629 | 472 | 154 | 4.4327 | 12.8 | 316.5866 | 192.5366 | 0 | 161.22 | 92.2898 | 0 | 21.1449 | 71.1449 | 0 | 0 | 0 | 0 | 0 | 161.22 | 0 | 526.1378 | 41.28% | 16.2181 | 0 | 24.0753 | 48.15% | 50
7764 | 883 | 577 | 92 | 6.4476 | 13.8 | 444.4293 | 277.8518 | 0 | 239.8107 | 101 | 1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 239.8107 | 0 | 759.1407 | 59.56% | 19.175 | 0 | 44.1367 | 88.27% | 49
7765 | 707 | 546 | 157 | 7.052 | 14.4 | 355.8454 | 221.7016 | 0 | 187.0502 | 101.5 | 19.1934 | 7.3066 | 75 | 0 | 0 | 0 | 0 | 0 | 187.0502 | 0 | 940.8808 | 73.82% | 5.6042 | 0 | 50 | 100% | 48.5
7766 | 124 | 289 | 222 | 6.8506 | 14 | 62.4114 | 0 | 37.5962 | 0 | 33.044 | 0 | 0 | 33.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940.8808 | 73.82% | 0 | 15.356 | 33.9368 | 67.87% | 48.4
7767 | 1 | 164 | 163 | 5.4401 | 13.7 | 0.50332 | 0 | 0.27895 | 0 | 14.0506 | 0 | 0 | 14.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940.8808 | 73.82% | 0 | 25 | 7.7843 | 15.57% | 39.0506
7768 | 0 | 49 | 49 | 4.4327 | 13.5 | 0 | 0 | 0 | 0 | 3.3134 | 0 | 0 | 3.3134 | 0 | 0 | 0 | 98.1124 | 39.2444 | 0 | 98.1124 | 843.9843 | 66.22% | 0 | 7.4422 | 0 | 0% | 50
7769 | 45 | 23 | 20 | 4.4327 | 12.8 | 22.6493 | 0 | 0 | 0 | 2.3117 | 0 | 0 | 2.3117 | 0 | 0 | 0 | 118.4568 | 47.6883 | 0 | 118.4568 | 722.8773 | 56.72% | 0 | 0 | 0 | 0% | 50
7770 | 0 | 0 | 0 | 2.6193 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.9073 | 50 | 0 | 123.9073 | 594.9851 | 46.68% | 0 | 0 | 0 | 0% | 50
7771 | 0 | 0 | 0 | 2.4178 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.8591 | 50 | 0 | 123.8591 | 467.0681 | 36.65% | 0 | 0 | 0 | 0% | 50
7772 | 0 | 0 | 0 | 3.4253 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.85 | 46.3 | 0 | 114.85 | 349.9126 | 27.45% | 0 | 0 | 0 | 0% | 46.3
7773 | 0 | 0 | 0 | 3.0223 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9941 | 41.8 | 0 | 103.9941 | 245.6483 | 19.27% | 0 | 0 | 0 | 0% | 41.8
7774 | 0 | 0 | 0 | 1.0074 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2335 | 38.6 | 0 | 96.2335 | 150.4814 | 11.81% | 0 | 0 | 0 | 0% | 38.6
7775 | 0 | 0 | 0 | 2.0149 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.9052 | 28.3224 | 0 | 71.9052 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 28.3224
7776 | 0 | 0 | 0 | 2.2164 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7777 | 0 | 0 | 0 | 2.2164 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7778 | 0 | 0 | 0 | 1.4104 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7779 | 0 | 0 | 0 | 1.0074 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7780 | 0 | 0 | 0 | 2.0149 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7781 | 0 | 0 | 0 | 2.0149 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7782 | 0 | 0 | 0 | 2.6193 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7783 | 0 | 0 | 0 | 2.2164 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7784 | 0 | 25 | 25 | 2.0149 | 6.3 | 0 | 0 | 0 | 0 | 1.3777 | 0 | 0 | 1.3777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 1.3777
7785 | 11 | 113 | 109 | 1.8134 | 9.6 | 5.5365 | 0 | 2.6994 | 0 | 9.9942 | 0 | 0 | 9.9942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 9.9942
7786 | 0 | 127 | 126 | 1.0074 | 10.4 | 0 | 0 | 0 | 0 | 10.1155 | 0 | 0 | 10.1155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 10.1155
7787 | 0 | 114 | 113 | 2.2164 | 11.4 | 0 | 0 | 0 | 0 | 8.5785 | 0 | 0 | 8.5785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 8.5785
7788 | 0 | 222 | 220 | 2.2164 | 12.2 | 0 | 0 | 0 | 0 | 18.5697 | 0 | 0 | 18.5697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 18.5697
7789 | 9 | 328 | 320 | 3.8283 | 13.7 | 4.5299 | 0 | 2.8175 | 0 | 30.1232 | 0 | 0 | 30.1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 30.1232
7790 | 136 | 311 | 243 | 4.0297 | 14.8 | 68.4512 | 0 | 41.1666 | 0 | 36.1808 | 0 | 0 | 36.1808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 36.1808
7791 | 68 | 213 | 183 | 5.4401 | 15.1 | 34.2256 | 0 | 18.9048 | 0 | 22.5489 | 0 | 0 | 22.5489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 22.5489
7792 | 11 | 96 | 93 | 5.2387 | 14.9 | 5.5365 | 0 | 2.5498 | 0 | 8.2737 | 0 | 0 | 8.2737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 8.2737
7793 | 14 | 35 | 33 | 4.6342 | 14.4 | 7.0464 | 0 | 0 | 0 | 2.5178 | 0 | 0 | 2.5178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 2.5178
7794 | 0 | 0 | 0 | 5.0372 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7795 | 0 | 0 | 0 | 5.8431 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7796 | 0 | 0 | 0 | 4.2312 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7797 | 0 | 0 | 0 | 5.6416 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7798 | 0 | 0 | 0 | 3.4253 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7799 | 0 | 0 | 0 | 3.6268 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7800 | 0 | 0 | 0 | 4.2312 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7801 | 0 | 0 | 0 | 4.6342 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7802 | 0 | 0 | 0 | 4.8357 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7803 | 0 | 0 | 0 | 4.4327 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7804 | 0 | 0 | 0 | 3.6268 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7805 | 0 | 0 | 0 | 3.8283 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7806 | 0 | 0 | 0 | 2.0149 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7807 | 0 | 0 | 0 | 1.6119 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7808 | 0 | 6 | 6 | 2.6193 | 11.5 | 0 | 0 | 0 | 0 | 0.015191 | 0 | 0 | 0.015191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0.015191
7809 | 0 | 23 | 23 | 5.0372 | 12.3 | 0 | 0 | 0 | 0 | 1.3163 | 0 | 0 | 1.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 1.3163
7810 | 2 | 155 | 152 | 6.4476 | 12.9 | 1.0066 | 0 | 0.57183 | 0 | 12.906 | 0 | 0 | 12.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 12.906
7811 | 0 | 111 | 110 | 6.8506 | 13.3 | 0 | 0 | 0 | 0 | 8.2913 | 0 | 0 | 8.2913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 8.2913
7812 | 2 | 201 | 197 | 11.6862 | 13.9 | 1.0066 | 0 | 0.6274 | 0 | 16.5591 | 0 | 0 | 16.5591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 16.5591
7813 | 2 | 156 | 154 | 13.4996 | 14.1 | 1.0066 | 0 | 0.62508 | 0 | 12.4005 | 0 | 0 | 12.4005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 12.4005
7814 | 20 | 231 | 219 | 16.119 | 14.1 | 10.0663 | 0 | 6.0441 | 0 | 20.8885 | 0 | 0 | 20.8885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 20.8885
7815 | 1 | 126 | 124 | 12.0892 | 14 | 0.50332 | 0 | 0.27709 | 0 | 10.0671 | 0 | 0 | 10.0671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 10.0671
7816 | 2 | 88 | 88 | 12.0892 | 14.1 | 1.0066 | 0 | 0.46099 | 0 | 7.2917 | 0 | 0 | 7.2917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 7.2917
7817 | 0 | 19 | 19 | 10.0743 | 13.8 | 0 | 0 | 0 | 0 | 0.75101 | 0 | 0 | 0.75101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0.75101
7818 | 0 | 0 | 0 | 9.2684 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7819 | 0 | 0 | 0 | 6.2461 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7820 | 0 | 0 | 0 | 6.8506 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7821 | 0 | 0 | 0 | 5.2387 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7822 | 0 | 0 | 0 | 5.0372 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7823 | 0 | 0 | 0 | 8.0595 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7824 | 0 | 0 | 0 | 9.2684 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7825 | 0 | 0 | 0 | 11.4848 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7826 | 0 | 0 | 0 | 18.1338 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7827 | 0 | 0 | 0 | 24.9844 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7828 | 0 | 0 | 0 | 29.6186 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7829 | 0 | 0 | 0 | 27.2007 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7830 | 0 | 0 | 0 | 21.9621 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7831 | 0 | 0 | 0 | 14.7085 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 0
7832 | 360 | 66 | 23 | 14.5071 | 11.7 | 181.1943 | 0 | 0 | 0 | 10.3048 | 0 | 0 | 10.3048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7964 | 6.575% | 0 | 0 | 0 | 0% | 10.3048
7833 | 713 | 236 | 48 | 19.5442 | 13.3 | 358.8653 | 174.3308 | 0 | 135.3322 | 54.4008 | 0 | 5.8004 | 48.6004 | 0 | 0 | 0 | 0 | 0 | 135.3322 | 0 | 215.9679 | 16.95% | 4.4489 | 0 | 4.6556 | 9.311% | 42.8
7834 | 843 | 396 | 61 | 21.9621 | 14.6 | 424.2966 | 240.5198 | 0 | 195.6924 | 99.5313 | 3.5157 | 25 | 71.0157 | 0 | 0 | 0 | 0 | 0 | 195.6924 | 0 | 407.0899 | 31.94% | 19.175 | 0 | 24.7216 | 49.44% | 42.5
7835 | 909 | 514 | 67 | 5.8431 | 15.2 | 457.5155 | 277.1763 | 0 | 239.5752 | 107.3 | 7.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 239.5752 | 0 | 641.0699 | 50.3% | 19.175 | 0 | 44.7877 | 89.58% | 42.7
7836 | 930 | 574 | 73 | 0 | 15.7 | 468.0852 | 291.3113 | 0 | 255.2962 | 108.4 | 26.9061 | 6.4939 | 75 | 0 | 0 | 0 | 0 | 0 | 255.2962 | 0 | 890.4037 | 69.86% | 4.9808 | 0 | 50 | 100% | 41.6
7837 | 755 | 506 | 100 | 0.60446 | 16.5 | 380.0046 | 235.5885 | 0 | 202.9683 | 109.4387 | 34.7693 | 0 | 74.6693 | 0 | 0 | 0 | 0 | 0 | 202.9683 | 0 | 1088.6318 | 85.42% | 0 | 0 | 50 | 100% | 39.9
7838 | 0 | 173 | 171 | 4.6342 | 19.5 | 0 | 0 | 0 | 0 | 13.7952 | 0 | 0 | 13.7952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.6318 | 85.42% | 0 | 25 | 23.8424 | 47.68% | 38.7952
7839 | 0 | 110 | 109 | 12.2907 | 20.9 | 0 | 0 | 0 | 0 | 8.3093 | 0 | 0 | 8.3093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.6318 | 85.42% | 0 | 22.7873 | 0 | 0% | 31.0966
7840 | 278 | 170 | 110 | 14.7085 | 21.4 | 139.9222 | 63.7177 | 0 | 34.7335 | 27.3048 | 0 | 0 | 27.3048 | 0 | 0 | 0 | 0 | 0 | 34.7335 | 0 | 1122.5541 | 88.08% | 0 | 0 | 0 | 0% | 27.3048
7841 | 306 | 64 | 33 | 11.0818 | 20.9 | 154.0151 | 0 | 0 | 0 | 7.2366 | 0 | 0 | 7.2366 | 0 | 0 | 0 | 90.3827 | 35.5634 | 0 | 90.3827 | 1035.6143 | 81.26% | 0 | 0 | 0 | 0% | 42.8
7842 | 0 | 0 | 0 | 5.2387 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7951 | 43.3 | 0 | 108.7951 | 926.5329 | 72.7% | 0 | 0 | 0 | 0% | 43.3
7843 | 0 | 0 | 0 | 11.6862 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3851 | 42.8 | 0 | 107.3851 | 818.8768 | 64.25% | 0 | 0 | 0 | 0% | 42.8
7844 | 0 | 0 | 0 | 12.6937 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0222 | 41 | 0 | 103.0222 | 716.3531 | 56.21% | 0 | 0 | 0 | 0% | 41
7845 | 0 | 0 | 0 | 4.6342 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9866 | 38.2 | 0 | 95.9866 | 621.8637 | 48.79% | 0 | 0 | 0 | 0% | 38.2
7846 | 0 | 0 | 0 | 4.8357 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5356 | 35.2 | 0 | 88.5356 | 535.8784 | 42.05% | 0 | 0 | 0 | 0% | 35.2
7847 | 0 | 0 | 0 | 4.2312 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9499 | 32.5 | 0 | 81.9499 | 457.7007 | 35.91% | 0 | 0 | 0 | 0% | 32.5
7848 | 0 | 0 | 0 | 9.2684 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4225 | 30.6 | 0 | 77.4225 | 384.8873 | 30.2% | 0 | 0 | 0 | 0% | 30.6
7849 | 0 | 0 | 0 | 11.4848 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4223 | 29.7 | 0 | 75.4223 | 314.4728 | 24.67% | 0 | 0 | 0 | 0% | 29.7
7850 | 0 | 0 | 0 | 18.1338 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2138 | 29.1 | 0 | 74.2138 | 245.4853 | 19.26% | 0 | 0 | 0 | 0% | 29.1
7851 | 0 | 0 | 0 | 24.9844 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2273 | 29.1 | 0 | 74.2273 | 176.4619 | 13.85% | 0 | 0 | 0 | 0% | 29.1
7852 | 0 | 0 | 0 | 29.6186 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.4619 | 13.85% | 0 | 0 | 0 | 0% | 0
7853 | 0 | 0 | 0 | 27.2007 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.4619 | 13.85% | 0 | 0 | 0 | 0% | 0
7854 | 0 | 0 | 0 | 21.9621 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.4619 | 13.85% | 0 | 0 | 0 | 0% | 0
7855 | 0 | 0 | 0 | 14.7085 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.4619 | 13.85% | 0 | 0 | 0 | 0% | 0
7856 | 360 | 66 | 23 | 14.5071 | 11.7 | 181.1943 | 0 | 0 | 0 | 9.907 | 0 | 0 | 9.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.4619 | 13.85% | 0 | 0 | 0 | 0% | 9.907
7857 | 713 | 236 | 48 | 19.5442 | 13.3 | 358.8653 | 174.038 | 0 | 135.0509 | 58.6641 | 0 | 10.1821 | 48.4821 | 0 | 0 | 0 | 0 | 0 | 135.0509 | 0 | 305.3336 | 23.96% | 7.8096 | 0 | 8.1737 | 16.35% | 38.3
7858 | 843 | 396 | 61 | 21.9621 | 14.6 | 424.2966 | 240.035 | 0 | 195.2491 | 104.8252 | 8.3126 | 25 | 71.5126 | 0 | 0 | 0 | 0 | 0 | 195.2491 | 0 | 491.6491 | 38.58% | 19.175 | 0 | 28.2427 | 56.49% | 38.2
7859 | 909 | 514 | 67 | 5.8431 | 15.2 | 457.5155 | 276.8453 | 0 | 239.2631 | 111.4 | 11.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 239.2631 | 0 | 719.9648 | 56.49% | 19.175 | 0 | 48.3117 | 96.62% | 38.6
7860 | 930 | 574 | 73 | 0 | 15.7 | 468.0852 | 290.8944 | 0 | 254.9007 | 111.5 | 36.5 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 254.9007 | 0 | 963.2025 | 75.57% | 0 | 0 | 48.3117 | 96.62% | 38.5
7861 | 755 | 506 | 100 | 0.60446 | 16.5 | 380.0046 | 235.2192 | 0 | 202.6281 | 112.2568 | 37.6284 | 0 | 74.6284 | 0 | 0 | 0 | 0 | 0 | 202.6281 | 0 | 1156.5594 | 90.75% | 0 | 0 | 48.3117 | 96.62% | 37
7862 | 0 | 173 | 171 | 4.6342 | 19.5 | 0 | 0 | 0 | 0 | 13.8174 | 0 | 0 | 13.8174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.5594 | 90.75% | 0 | 22.3826 | 24.8892 | 49.78% | 36.2
7863 | 0 | 110 | 109 | 12.2907 | 20.9 | 0 | 0 | 0 | 0 | 8.3211 | 0 | 0 | 8.3211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.5594 | 90.75% | 0 | 23.7842 | 0 | 0% | 32.1053
7864 | 278 | 170 | 110 | 14.7085 | 21.4 | 139.9222 | 63.3622 | 0 | 34.4346 | 27.3477 | 0 | 0 | 27.3477 | 0 | 0 | 0 | 0 | 0 | 34.4346 | 0 | 1189.4184 | 93.32% | 0 | 0 | 0 | 0% | 27.3477
7865 | 306 | 64 | 33 | 11.0818 | 20.9 | 154.0151 | 0 | 0 | 0 | 6.9473 | 0 | 0 | 6.9473 | 0 | 0 | 0 | 89.3894 | 35.1527 | 0 | 89.3894 | 1104.0797 | 86.63% | 0 | 0 | 0 | 0% | 42.1
7866 | 0 | 0 | 0 | 5.2387 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.276 | 43.5 | 0 | 109.276 | 995.0132 | 78.07% | 0 | 0 | 0 | 0% | 43.5
7867 | 0 | 0 | 0 | 11.6862 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.111 | 43.1 | 0 | 108.111 | 887.0795 | 69.6% | 0 | 0 | 0 | 0% | 43.1
7868 | 0 | 0 | 0 | 12.6937 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.7503 | 41.3 | 0 | 103.7503 | 784.2578 | 61.53% | 0 | 0 | 0 | 0% | 41.3
7869 | 0 | 0 | 0 | 4.6342 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7466 | 38.1 | 0 | 95.7466 | 690.5572 | 54.18% | 0 | 0 | 0 | 0% | 38.1
7870 | 0 | 0 | 0 | 4.8357 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1021 | 34.6 | 0 | 87.1021 | 606.751 | 47.61% | 0 | 0 | 0 | 0% | 34.6
7871 | 0 | 0 | 0 | 4.2312 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4714 | 32.3 | 0 | 81.4714 | 529.5485 | 41.55% | 0 | 0 | 0 | 0% | 32.3
7872 | 0 | 0 | 0 | 4.2312 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3536 | 31 | 0 | 78.3536 | 455.9948 | 35.78% | 0 | 0 | 0 | 0% | 31
7873 | 0 | 0 | 0 | 9.2684 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9409 | 30.4 | 0 | 76.9409 | 384.0984 | 30.14% | 0 | 0 | 0 | 0% | 30.4
7874 | 0 | 0 | 0 | 11.4848 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2814 | 30.5 | 0 | 77.2814 | 311.9067 | 24.47% | 0 | 0 | 0 | 0% | 30.5
7875 | 0 | 0 | 0 | 18.1338 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7583 | 31.9 | 0 | 80.7583 | 235.7663 | 18.5% | 0 | 0 | 0 | 0% | 31.9
7876 | 0 | 0 | 0 | 24.9844 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.6282 | 21.7685 | 0 | 57.6282 | 183.1009 | 14.37% | 0 | 0 | 0 | 0% | 21.7685
7877 | 0 | 0 | 0 | 29.6186 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.1009 | 14.37% | 0 | 0 | 0 | 0% | 0
7878 | 0 | 0 | 0 | 27.2007 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.1009 | 14.37% | 0 | 0 | 0 | 0% | 0
7879 | 0 | 0 | 0 | 21.9621 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.1009 | 14.37% | 0 | 0 | 0 | 0% | 0
7880 | 0 | 0 | 0 | 14.7085 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.1009 | 14.37% | 0 | 0 | 0 | 0% | 0
7881 | 360 | 66 | 23 | 14.5071 | 11.7 | 181.1943 | 87.7348 | 0 | 57.4442 | 24.4554 | 0 | 0 | 24.4554 | 0 | 0 | 0 | 0 | 0 | 57.4442 | 0 | 237.6017 | 18.64% | 0 | 0 | 0 | 0% | 24.4554
7882 | 713 | 236 | 48 | 19.5442 | 13.3 | 358.8653 | 202.6286 | 0 | 161.7386 | 71.885 | 0 | 12.0925 | 59.7925 | 0 | 0 | 0 | 0 | 0 | 161.7386 | 0 | 391.0527 | 30.68% | 9.275 | 0 | 9.7088 | 19.42% | 47.7
7883 | 843 | 396 | 61 | 21.9621 | 14.6 | 424.2966 | 256.4492 | 0 | 210.3666 | 102.4 | 2.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 210.3666 | 0 | 590.64 | 46.34% | 19.175 | 0 | 29.7807 | 59.56% | 47.6
7884 | 909 | 514 | 67 | 5.8431 | 15.2 | 457.5155 | 283.9316 | 0 | 245.9581 | 103.7 | 3.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 245.9581 | 0 | 823.995 | 64.65% | 19.175 | 0 | 49.8526 | 99.71% | 46.3
7885 | 930 | 574 | 73 | 0 | 15.7 | 468.0852 | 289.2972 | 0 | 253.3858 | 104.3 | 29.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 253.3858 | 0 | 1064.3971 | 83.51% | 0 | 0 | 49.8526 | 99.71% | 45.7
7886 | 0 | 173 | 171 | 4.6342 | 19.5 | 0 | 0 | 0 | 0 | 13.8391 | 0 | 0 | 13.8391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1064.3971 | 83.51% | 0 | 25 | 23.6874 | 47.37% | 38.8391
7887 | 0 | 110 | 109 | 12.2907 | 20.9 | 0 | 0 | 0 | 0 | 8.3327 | 0 | 0 | 8.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1064.3971 | 83.51% | 0 | 22.6324 | 0 | 0% | 30.9651
7888 | 278 | 170 | 110 | 14.7085 | 21.4 | 139.9222 | 63.0114 | 0 | 34.1407 | 27.3911 | 0 | 0 | 27.3911 | 0 | 0 | 0 | 57.7688 | 21.5089 | 34.1407 | 57.7688 | 1044.1878 | 81.93% | 0 | 0 | 0 | 0% | 48.9
7889 | 306 | 64 | 33 | 11.0818 | 20.9 | 154.0151 | 0 | 0 | 0 | 6.6673 | 0 | 0 | 6.6673 | 0 | 0 | 0 | 107.705 | 42.7327 | 0 | 107.705 | 937.4457 | 73.55% | 0 | 0 | 0 | 0% | 49.4
7890 | 0 | 0 | 0 | 5.2387 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.5645 | 49.8 | 0 | 124.5645 | 810.1627 | 63.57% | 0 | 0 | 0 | 0% | 49.8
7891 | 0 | 0 | 0 | 11.6862 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1854 | 48.1 | 0 | 120.1854 | 687.8918 | 53.97% | 0 | 0 | 0 | 0% | 48.1
7892 | 0 | 0 | 0 | 12.6937 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.2523 | 44.4 | 0 | 111.2523 | 576.3114 | 45.22% | 0 | 0 | 0 | 0% | 44.4
7893 | 0 | 0 | 0 | 4.6342 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5368 | 40.1 | 0 | 100.5368 | 476.9536 | 37.42% | 0 | 0 | 0 | 0% | 40.1
7894 | 0 | 0 | 0 | 4.8357 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1051 | 37.1 | 0 | 93.1051 | 386.1634 | 30.3% | 0 | 0 | 0 | 0% | 37.1
7895 | 0 | 0 | 0 | 4.2312 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4312 | 34.8 | 0 | 87.4312 | 301.8275 | 23.68% | 0 | 0 | 0 | 0% | 34.8
7896 | 0 | 0 | 0 | 3.6268 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7782 | 33.3 | 0 | 83.7782 | 221.8112 | 17.4% | 0 | 0 | 0 | 0% | 33.3
7897 | 0 | 0 | 0 | 3.2238 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8112 | 17.4% | 0 | 0 | 0 | 0% | 0
7898 | 0 | 0 | 0 | 3.0223 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8112 | 17.4% | 0 | 0 | 0 | 0% | 0
7899 | 0 | 0 | 0 | 2.2164 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8112 | 17.4% | 0 | 0 | 0 | 0% | 0
7900 | 0 | 0 | 0 | 3.0223 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8112 | 17.4% | 0 | 0 | 0 | 0% | 0
7901 | 0 | 0 | 0 | 4.0297 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8112 | 17.4% | 0 | 0 | 0 | 0% | 0
7902 | 0 | 0 | 0 | 2.0149 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8112 | 17.4% | 0 | 0 | 0 | 0% | 0
7903 | 0 | 1 | 1 | 3.0223 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8112 | 17.4% | 0 | 0 | 0 | 0% | 0
7904 | 183 | 53 | 33 | 1.6119 | 10.7 | 92.1071 | 0 | 0 | 0 | 7.1489 | 0 | 0 | 7.1489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221.8112 | 17.4% | 0 | 0 | 0 | 0% | 7.1489
7905 | 522 | 226 | 94 | 1.8134 | 14.4 | 262.7317 | 127.028 | 0 | 100.8977 | 40.6133 | 0 | 0 | 40.6133 | 0 | 0 | 0 | 0 | 0 | 100.8977 | 0 | 319.1037 | 25.04% | 0 | 0 | 0 | 0% | 40.6133
7906 | 584 | 334 | 105 | 2.0149 | 16.9 | 293.9374 | 165.6643 | 0 | 136.9924 | 61.4071 | 0 | 6.9035 | 54.5035 | 0 | 0 | 0 | 0 | 0 | 136.9924 | 0 | 451.2013 | 35.4% | 5.295 | 0 | 5.5435 | 11.09% | 47.6
7907 | 884 | 517 | 88 | 6.8506 | 19.6 | 444.9326 | 268.6248 | 0 | 230.9854 | 102.2 | 2.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 230.9854 | 0 | 673.9333 | 52.88% | 19.175 | 0 | 25.6183 | 51.24% | 47.8
7908 | 847 | 568 | 118 | 7.6565 | 20.6 | 426.3098 | 264.2107 | 0 | 226.3759 | 103.6 | 3.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 226.3759 | 0 | 892.2206 | 70% | 19.175 | 0 | 45.6932 | 91.39% | 46.4
7909 | 206 | 361 | 248 | 6.4476 | 20.6 | 103.6834 | 63.9855 | 0 | 39.8894 | 42.9671 | 0 | 0 | 42.9671 | 0 | 0 | 0 | 0 | 0 | 39.8894 | 0 | 930.6847 | 73.02% | 0 | 2.6329 | 42.9372 | 85.87% | 45.6
7910 | 276 | 330 | 198 | 5.0372 | 20.5 | 138.9156 | 82.8942 | 0 | 58.3982 | 43.5702 | 0 | 0 | 43.5702 | 0 | 0 | 0 | 0 | 0 | 58.3982 | 0 | 986.9963 | 77.44% | 0 | 0 | 42.9372 | 85.87% | 43.5702
7911 | 350 | 338 | 202 | 5.4401 | 20.6 | 176.1611 | 95.7374 | 0 | 70.2668 | 46.7502 | 0.22508 | 0 | 46.5251 | 0 | 0 | 0 | 0 | 0 | 70.2668 | 0 | 1054.7524 | 82.76% | 0 | 0 | 42.9372 | 85.87% | 46.3
7912 | 41 | 94 | 82 | 5.4401 | 18.9 | 20.636 | 0 | 9.242 | 0 | 9.3112 | 0 | 0 | 9.3112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.7524 | 82.76% | 0 | 25 | 16.7679 | 33.54% | 34.3112
7913 | 15 | 19 | 18 | 4.8357 | 17.2 | 7.5498 | 0 | 0 | 0 | 0.88248 | 0 | 0 | 0.88248 | 0 | 0 | 0 | 81.9798 | 32.2989 | 0 | 81.9798 | 977.6851 | 76.71% | 0 | 16.0186 | 0 | 0% | 49.2
7914 | 0 | 0 | 0 | 4.4327 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.6041 | 49.3 | 0 | 122.6041 | 851.8987 | 66.84% | 0 | 0 | 0 | 0% | 49.3
7915 | 0 | 0 | 0 | 2.6193 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.551 | 47.7 | 0 | 118.551 | 730.8034 | 57.34% | 0 | 0 | 0 | 0% | 47.7
7916 | 0 | 0 | 0 | 2.0149 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4679 | 44.4 | 0 | 110.4679 | 619.2036 | 48.58% | 0 | 0 | 0 | 0% | 44.4
7917 | 0 | 0 | 0 | 4.8357 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1742 | 40.1 | 0 | 100.1742 | 519.8296 | 40.79% | 0 | 0 | 0 | 0% | 40.1
7918 | 0 | 0 | 0 | 5.4401 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8616 | 37.4 | 0 | 93.8616 | 428.1755 | 33.6% | 0 | 0 | 0 | 0% | 37.4
7919 | 0 | 0 | 0 | 6.4476 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3992 | 35.1 | 0 | 88.3992 | 342.9653 | 26.91% | 0 | 0 | 0 | 0% | 35.1
7920 | 0 | 0 | 0 | 2.8208 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6306 | 33.2 | 0 | 83.6306 | 263.2277 | 20.65% | 0 | 0 | 0 | 0% | 33.2
7921 | 0 | 0 | 0 | 3.2238 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263.2277 | 20.65% | 0 | 0 | 0 | 0% | 0
7922 | 0 | 0 | 0 | 2.4178 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.1583 | 20.0087 | 0 | 53.1583 | 214.8733 | 16.86% | 0 | 0 | 0 | 0% | 20.0087
7923 | 0 | 0 | 0 | 3.6268 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.8733 | 16.86% | 0 | 0 | 0 | 0% | 0
7924 | 0 | 0 | 0 | 6.4476 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.8733 | 16.86% | 0 | 0 | 0 | 0% | 0
7925 | 0 | 0 | 0 | 5.4401 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.8733 | 16.86% | 0 | 0 | 0 | 0% | 0
7926 | 0 | 0 | 0 | 7.2535 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.8733 | 16.86% | 0 | 0 | 0 | 0% | 0
7927 | 0 | 0 | 0 | 8.4625 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.8733 | 16.86% | 0 | 0 | 0 | 0% | 0
7928 | 306 | 57 | 22 | 7.455 | 17.3 | 154.0151 | 0 | 0 | 0 | 7.6031 | 0 | 0 | 7.6031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.8733 | 16.86% | 0 | 0 | 0 | 0% | 7.6031
7929 | 721 | 243 | 61 | 8.6639 | 18.5 | 362.8918 | 175.2143 | 0 | 142.7952 | 50.9379 | 2.069 | 0 | 48.869 | 0 | 0 | 0 | 0 | 0 | 142.7952 | 0 | 352.5577 | 27.66% | 0 | 0 | 0 | 0% | 46.8
7930 | 845 | 390 | 65 | 12.6937 | 19.8 | 425.3032 | 239.2871 | 0 | 200.1769 | 92.9024 | 0 | 23.1012 | 69.8012 | 0 | 0 | 0 | 0 | 0 | 200.1769 | 0 | 545.5701 | 42.81% | 17.7186 | 0 | 18.5527 | 37.11% | 46.7
7931 | 900 | 484 | 61 | 11.4848 | 20.9 | 452.9856 | 273.1974 | 0 | 232.4727 | 103.4 | 3.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 232.4727 | 0 | 769.7224 | 60.39% | 19.175 | 0 | 38.6303 | 77.26% | 46.6
7932 | 925 | 548 | 64 | 12.6937 | 21.6 | 465.5686 | 288.168 | 0 | 245.9212 | 104.6 | 15.4429 | 14.1571 | 75 | 0 | 0 | 0 | 0 | 0 | 245.9212 | 0 | 1006.8418 | 79% | 10.8585 | 0 | 50 | 100% | 45.4
7933 | 928 | 544 | 58 | 11.6862 | 22.1 | 467.0785 | 287.828 | 0 | 246.2237 | 105.2 | 30.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 246.2237 | 0 | 1244.2529 | 97.63% | 0 | 0 | 50 | 100% | 44.8
7934 | 897 | 478 | 55 | 10.4773 | 22.1 | 451.4757 | 0 | 269.0111 | 0 | 105.6 | 30.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.2529 | 97.63% | 0 | 0 | 50 | 100% | 44.4
7935 | 836 | 362 | 50 | 14.1041 | 22 | 420.7733 | 0 | 227.9656 | 0 | 85.548 | 20.174 | 0 | 65.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.2529 | 97.63% | 0 | 0 | 50 | 100% | 45.2
7936 | 692 | 203 | 39 | 14.7085 | 21.2 | 348.2956 | 0 | 155.1387 | 0 | 43.1104 | 0 | 0 | 43.1104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.2529 | 97.63% | 0 | 4.5896 | 45.1951 | 90.39% | 47.7
7937 | 269 | 44 | 16 | 10.8803 | 19.3 | 135.3924 | 0 | 0 | 0 | 5.1945 | 0 | 0 | 5.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.2529 | 97.63% | 0 | 25 | 19.022 | 38.04% | 30.1945
7938 | 0 | 0 | 0 | 5.8431 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0455 | 30.6303 | 0 | 78.0455 | 1171.8799 | 91.95% | 0 | 18.1697 | 2.7756e-15 | 5.551e-15% | 48.8
7939 | 0 | 0 | 0 | 3.6268 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.109 | 47.4 | 0 | 118.109 | 1051.6748 | 82.52% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 47.4
7940 | 0 | 0 | 0 | 6.4476 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.2651 | 43.8 | 0 | 109.2651 | 941.8455 | 73.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 43.8
7941 | 0 | 0 | 0 | 5.2387 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1479 | 39.7 | 0 | 99.1479 | 843.6609 | 66.19% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.7
7942 | 0 | 0 | 0 | 2.2164 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3595 | 36.9 | 0 | 92.3595 | 753.4634 | 59.12% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.9
7943 | 0 | 0 | 0 | 3.0223 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0095 | 34.7 | 0 | 87.0095 | 669.4517 | 52.53% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.7
7944 | 0 | 0 | 0 | 3.8283 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9498 | 33 | 0 | 82.9498 | 590.3349 | 46.32% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33
7945 | 0 | 0 | 0 | 3.0223 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5204 | 32.4 | 0 | 81.5204 | 512.9135 | 40.24% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.4
7946 | 0 | 0 | 0 | 5.2387 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2808 | 32.3 | 0 | 81.2808 | 435.7604 | 34.19% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.3
7947 | 0 | 0 | 0 | 3.2238 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6428 | 33.3 | 0 | 83.6428 | 355.736 | 27.91% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.3
7948 | 0 | 0 | 0 | 6.0446 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2866 | 36.9 | 0 | 92.2866 | 265.4289 | 20.83% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 36.9
7949 | 0 | 0 | 0 | 3.4253 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265.4289 | 20.83% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
7950 | 0 | 0 | 0 | 4.2312 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265.4289 | 20.83% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
7951 | 0 | 0 | 0 | 2.8208 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265.4289 | 20.83% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
7952 | 315 | 57 | 21 | 2.0149 | 8.4 | 158.545 | 0 | 0 | 0 | 7.3813 | 0 | 0 | 7.3813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265.4289 | 20.83% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 7.3813
7953 | 703 | 221 | 48 | 2.6193 | 11.9 | 353.8321 | 170.4829 | 0 | 141.2913 | 46.1892 | 0 | 0 | 46.1892 | 0 | 0 | 0 | 0 | 0 | 141.2913 | 0 | 400.2987 | 31.41% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 46.1892
7954 | 845 | 379 | 58 | 2.4178 | 16.1 | 425.3032 | 238.8953 | 0 | 205.3606 | 86.0817 | 0 | 19.5909 | 66.4909 | 0 | 0 | 0 | 0 | 0 | 205.3606 | 0 | 596.3259 | 46.79% | 15.0262 | 0 | 15.7358 | 31.47% | 46.9
7955 | 905 | 492 | 62 | 4.4327 | 17.6 | 455.5022 | 274.4372 | 0 | 237.7586 | 103.1 | 3.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 237.7586 | 0 | 823.2786 | 64.6% | 19.175 | 0 | 35.8164 | 71.63% | 46.9
7956 | 932 | 552 | 64 | 7.455 | 18.5 | 469.0918 | 289.9861 | 0 | 250.7656 | 104.5 | 11.8417 | 17.6583 | 75 | 0 | 0 | 0 | 0 | 0 | 250.7656 | 0 | 1062.6472 | 83.38% | 13.5439 | 0 | 50 | 100% | 45.5
7957 | 932 | 549 | 63 | 5.0372 | 19.5 | 469.0918 | 288.6622 | 0 | 251.0051 | 105 | 30 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 251.0051 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45
7958 | 879 | 485 | 72 | 5.8431 | 20.1 | 442.416 | 0 | 263.2351 | 0 | 105.3 | 30.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44.7
7959 | 725 | 364 | 93 | 6.4476 | 19.9 | 364.9051 | 0 | 197.0935 | 0 | 79.6965 | 17.0482 | 0 | 62.6482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 45.6
7960 | 553 | 197 | 62 | 6.2461 | 19.3 | 278.3345 | 0 | 123.3088 | 0 | 38.1712 | 0 | 0 | 38.1712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 9.6288 | 39.918 | 79.84% | 47.8
7961 | 210 | 50 | 28 | 5.2387 | 17.1 | 105.6967 | 0 | 0 | 0 | 5.4244 | 0 | 0 | 5.4244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 13.7407 | 27.48% | 30.4244
7962 | 0 | 0 | 0 | 3.2238 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8095 | 35.7767 | 0 | 89.8095 | 1187.5338 | 93.18% | 0 | 13.1233 | 0 | 0% | 48.9
7963 | 0 | 0 | 0 | 1.4104 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.9585 | 47.5 | 0 | 117.9585 | 1067.0836 | 83.72% | 0 | 0 | 0 | 0% | 47.5
7964 | 0 | 0 | 0 | 0.60446 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5653 | 44.1 | 0 | 109.5653 | 956.4118 | 75.04% | 0 | 0 | 0 | 0% | 44.1
7965 | 0 | 0 | 0 | 1.6119 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.6685 | 40 | 0 | 99.6685 | 857.3773 | 67.27% | 0 | 0 | 0 | 0% | 40
7966 | 0 | 0 | 0 | 2.8208 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0011 | 37.2 | 0 | 93.0011 | 766.3483 | 60.13% | 0 | 0 | 0 | 0% | 37.2
7967 | 0 | 0 | 0 | 3.4253 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9828 | 34.7 | 0 | 86.9828 | 682.3522 | 53.54% | 0 | 0 | 0 | 0% | 34.7
7968 | 0 | 0 | 0 | 4.0297 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6428 | 33.3 | 0 | 83.6428 | 602.391 | 47.26% | 0 | 0 | 0 | 0% | 33.3
7969 | 0 | 0 | 0 | 3.2238 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3788 | 32.8 | 0 | 82.3788 | 523.8504 | 41.1% | 0 | 0 | 0 | 0% | 32.8
7970 | 0 | 0 | 0 | 3.4253 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6591 | 32.5 | 0 | 81.6591 | 446.1537 | 35.01% | 0 | 0 | 0 | 0% | 32.5
7971 | 0 | 0 | 0 | 2.6193 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0557 | 33.5 | 0 | 84.0557 | 365.5899 | 28.68% | 0 | 0 | 0 | 0% | 33.5
7972 | 0 | 0 | 0 | 3.0223 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4391 | 37 | 0 | 92.4391 | 275.032 | 21.58% | 0 | 0 | 0 | 0% | 37
7973 | 0 | 0 | 0 | 3.6268 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.032 | 21.58% | 0 | 0 | 0 | 0% | 0
7974 | 0 | 0 | 0 | 3.8283 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.032 | 21.58% | 0 | 0 | 0 | 0% | 0
7975 | 0 | 0 | 0 | 3.0223 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.032 | 21.58% | 0 | 0 | 0 | 0% | 0
7976 | 336 | 55 | 19 | 3.8283 | 8.8 | 169.1146 | 0 | 0 | 0 | 6.7389 | 0 | 0 | 6.7389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.032 | 21.58% | 0 | 0 | 0 | 0% | 6.7389
7977 | 726 | 218 | 40 | 3.0223 | 13.1 | 365.4084 | 175.7096 | 0 | 146.1221 | 45.963 | 0 | 0 | 45.963 | 0 | 0 | 0 | 0 | 0 | 146.1221 | 0 | 414.8025 | 32.55% | 0 | 0 | 0 | 0% | 45.963
7978 | 857 | 373 | 49 | 0.60446 | 17 | 431.343 | 241.9149 | 0 | 208.8056 | 82.8697 | 0 | 18.2349 | 64.6349 | 0 | 0 | 0 | 0 | 0 | 208.8056 | 0 | 614.5319 | 48.22% | 13.9861 | 0 | 14.6488 | 29.3% | 46.4
7979 | 914 | 487 | 55 | 2.6193 | 18.4 | 460.0321 | 276.8991 | 0 | 240.7331 | 104.1 | 4.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 240.7331 | 0 | 844.8009 | 66.28% | 19.175 | 0 | 34.7324 | 69.46% | 45.9
7980 | 929 | 542 | 58 | 2.6193 | 19.2 | 467.5819 | 288.7053 | 0 | 251.8998 | 105.5 | 11.495 | 19.005 | 75 | 0 | 0 | 0 | 0 | 0 | 251.8998 | 0 | 1085.7512 | 85.19% | 14.5769 | 0 | 50 | 100% | 44.5
7981 | 916 | 535 | 60 | 2.4178 | 20 | 461.0387 | 283.3197 | 0 | 246.8751 | 106.4 | 31.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 246.8751 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.6
7982 | 876 | 469 | 60 | 3.0223 | 20.7 | 440.906 | 0 | 261.9698 | 0 | 106.9 | 31.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 43.1
7983 | 801 | 351 | 55 | 4.4327 | 20.7 | 403.1572 | 0 | 217.1008 | 0 | 80.4028 | 18.2014 | 0 | 62.2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 44
7984 | 647 | 196 | 44 | 4.4327 | 20.2 | 325.6463 | 0 | 143.5009 | 0 | 40.7137 | 0 | 0 | 40.7137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.5863 | 44.1499 | 88.3% | 46.3
7985 | 237 | 43 | 18 | 3.8283 | 17.6 | 119.2862 | 0 | 0 | 0 | 4.8483 | 0 | 0 | 4.8483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 17.969 | 35.94% | 29.8483
7986 | 0 | 0 | 0 | 1.4104 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.669 | 29.3412 | 0 | 74.669 | 1205.5126 | 94.59% | 0 | 17.1588 | 0 | 0% | 46.5
7987 | 0 | 0 | 0 | 2.8208 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.6928 | 45.3 | 0 | 112.6928 | 1091.4037 | 85.63% | 0 | 0 | 0 | 0% | 45.3
7988 | 0 | 0 | 0 | 3.6268 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.9495 | 42.5 | 0 | 105.9495 | 985.3222 | 77.31% | 0 | 0 | 0 | 0% | 42.5
7989 | 0 | 0 | 0 | 4.2312 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.434 | 39.4 | 0 | 98.434 | 888.0274 | 69.68% | 0 | 0 | 0 | 0% | 39.4
7990 | 0 | 0 | 0 | 3.8283 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6625 | 37 | 0 | 92.6625 | 797.5692 | 62.58% | 0 | 0 | 0 | 0% | 37
7991 | 0 | 0 | 0 | 5.2387 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4722 | 34.4 | 0 | 86.4722 | 714.4513 | 56.06% | 0 | 0 | 0 | 0% | 34.4
7992 | 0 | 0 | 0 | 4.6342 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2216 | 32.6 | 0 | 82.2216 | 636.4948 | 49.94% | 0 | 0 | 0 | 0% | 32.6
7993 | 0 | 0 | 0 | 2.2164 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6995 | 31.6 | 0 | 79.6995 | 561.3539 | 44.04% | 0 | 0 | 0 | 0% | 31.6
7994 | 0 | 0 | 0 | 1.6119 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9818 | 30.9 | 0 | 77.9818 | 488.1602 | 38.3% | 0 | 0 | 0 | 0% | 30.9
7995 | 0 | 0 | 0 | 3.2238 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2528 | 31 | 0 | 78.2528 | 414.6723 | 32.54% | 0 | 0 | 0 | 0% | 31
7996 | 0 | 0 | 0 | 5.4401 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3056 | 31.8 | 0 | 80.3056 | 338.9212 | 26.59% | 0 | 0 | 0 | 0% | 31.8
7997 | 0 | 0 | 0 | 3.2238 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1818 | 33.9 | 0 | 85.1818 | 257.1509 | 20.18% | 0 | 0 | 0 | 0% | 33.9
7998 | 0 | 0 | 0 | 3.2238 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.1509 | 20.18% | 0 | 0 | 0 | 0% | 0
7999 | 0 | 0 | 0 | 2.8208 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.1509 | 20.18% | 0 | 0 | 0 | 0% | 0
8000 | 219 | 43 | 20 | 2.8208 | 11.1 | 110.2265 | 0 | 0 | 0 | 5.3902 | 0 | 0 | 5.3902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257.1509 | 20.18% | 0 | 0 | 0 | 0% | 5.3902
8001 | 683 | 212 | 45 | 1.8134 | 15.2 | 343.7658 | 165.0002 | 0 | 136.4323 | 46.5807 | 0 | 2.7404 | 43.8404 | 0 | 0 | 0 | 0 | 0 | 136.4323 | 0 | 386.4441 | 30.32% | 2.1019 | 0 | 2.2018 | 4.404% | 41.1
8002 | 826 | 364 | 53 | 4.2312 | 16.9 | 415.7402 | 232.8281 | 0 | 199.0936 | 89.8485 | 0 | 24.7243 | 65.1243 | 0 | 0 | 0 | 0 | 0 | 199.0936 | 0 | 575.1197 | 45.12% | 18.9635 | 0 | 22.0667 | 44.13% | 40.4
8003 | 887 | 475 | 57 | 3.6268 | 18.4 | 446.4425 | 268.473 | 0 | 232.4524 | 109.5 | 9.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 232.4524 | 0 | 795.4086 | 62.41% | 19.175 | 0 | 42.1533 | 84.31% | 40.5
8004 | 916 | 534 | 58 | 3.6268 | 19.4 | 461.0387 | 284.3368 | 0 | 247.4088 | 110.3 | 25.5339 | 9.7661 | 75 | 0 | 0 | 0 | 0 | 0 | 247.4088 | 0 | 1029.8712 | 80.81% | 7.4906 | 0 | 50 | 100% | 39.7
8005 | 916 | 532 | 58 | 5.0372 | 19.7 | 461.0387 | 282.9456 | 0 | 245.5912 | 112 | 37 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 245.5912 | 0 | 1262.6113 | 99.07% | 0 | 0 | 50 | 100% | 38
8006 | 887 | 469 | 57 | 6.2461 | 20.3 | 446.4425 | 0 | 264.8978 | 0 | 113 | 38 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6113 | 99.07% | 0 | 0 | 50 | 100% | 37
8007 | 819 | 353 | 51 | 7.455 | 19.9 | 412.2169 | 0 | 221.3255 | 0 | 90.4345 | 26.5172 | 0 | 63.9172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6113 | 99.07% | 0 | 0 | 50 | 100% | 37.4
8008 | 657 | 195 | 42 | 8.0595 | 19.1 | 330.6795 | 0 | 144.9523 | 0 | 43.0071 | 1.4035 | 0 | 41.6035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6113 | 99.07% | 0 | 0 | 50 | 100% | 40.2
8009 | 229 | 41 | 17 | 7.455 | 16.2 | 115.2597 | 0 | 0 | 0 | 4.5698 | 0 | 0 | 4.5698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6113 | 99.07% | 0 | 25 | 23.8155 | 47.63% | 29.5698
8010 | 0 | 0 | 0 | 4.6342 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.6113 | 99.07% | 0 | 22.7383 | 0 | 0% | 22.7383
8011 | 0 | 0 | 0 | 2.0149 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.0387 | 40.9 | 0 | 102.0387 | 1161.0825 | 91.1% | 0 | 0 | 0 | 0% | 40.9
8012 | 0 | 0 | 0 | 1.8134 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5837 | 39.1 | 0 | 97.5837 | 1064.6684 | 83.54% | 0 | 0 | 0 | 0% | 39.1
8013 | 0 | 0 | 0 | 1.8134 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1259 | 36.4 | 0 | 91.1259 | 975.9178 | 76.57% | 0 | 0 | 0 | 0% | 36.4
8014 | 0 | 0 | 0 | 1.2089 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8402 | 33.8 | 0 | 84.8402 | 894.5529 | 70.19% | 0 | 0 | 0 | 0% | 33.8
8015 | 0 | 0 | 0 | 2.6193 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.023 | 31.4 | 0 | 79.023 | 820.0025 | 64.34% | 0 | 0 | 0 | 0% | 31.4
8016 | 0 | 0 | 0 | 2.0149 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4793 | 29.9 | 0 | 75.4793 | 749.5821 | 58.81% | 0 | 0 | 0 | 0% | 29.9
8017 | 0 | 0 | 0 | 1.6119 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7131 | 29.1 | 0 | 73.7131 | 681.1119 | 53.44% | 0 | 0 | 0 | 0% | 29.1
8018 | 0 | 0 | 0 | 4.6342 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8451 | 28.7 | 0 | 72.8451 | 613.6094 | 48.14% | 0 | 0 | 0 | 0% | 28.7
8019 | 0 | 0 | 0 | 2.8208 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5919 | 28.6 | 0 | 72.5919 | 546.3397 | 42.87% | 0 | 0 | 0 | 0% | 28.6
8020 | 0 | 0 | 0 | 3.2238 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3279 | 29.4 | 0 | 74.3279 | 477.0981 | 37.43% | 0 | 0 | 0 | 0% | 29.4
8021 | 0 | 0 | 0 | 2.8208 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1293 | 30.2 | 0 | 76.1293 | 405.8163 | 31.84% | 0 | 0 | 0 | 0% | 30.2
8022 | 0 | 0 | 0 | 3.8283 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2928 | 31.1 | 0 | 78.2928 | 332.0129 | 26.05% | 0 | 0 | 0 | 0% | 31.1
8023 | 0 | 0 | 0 | 4.0297 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.0129 | 26.05% | 0 | 0 | 0 | 0% | 0
8024 | 252 | 58 | 33 | 3.2238 | 10.8 | 126.836 | 0 | 0 | 0 | 6.382 | 0 | 0 | 6.382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332.0129 | 26.05% | 0 | 0 | 0 | 0% | 6.382
8025 | 248 | 112 | 41 | 1.2089 | 10.3 | 124.8227 | 59.8126 | 0 | 38.466 | 19.3426 | 0 | 0 | 19.3426 | 0 | 0 | 0 | 0 | 0 | 38.466 | 0 | 368.0502 | 28.88% | 0 | 0 | 0 | 0% | 19.3426
8026 | 818 | 380 | 73 | 1.8134 | 16.1 | 411.7136 | 230.2637 | 0 | 197.5367 | 94.0175 | 2.9587 | 25 | 66.0587 | 0 | 0 | 0 | 0 | 0 | 197.5367 | 0 | 553.1143 | 43.4% | 19.175 | 0 | 20.0895 | 40.18% | 38.1
8027 | 887 | 477 | 60 | 4.4327 | 18 | 446.4425 | 268.2398 | 0 | 231.941 | 111.3 | 11.3 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 231.941 | 0 | 770.4105 | 60.45% | 19.175 | 0 | 40.179 | 80.36% | 38.7
8028 | 915 | 536 | 62 | 7.2535 | 18.7 | 460.5354 | 283.7125 | 0 | 244.9406 | 111.4 | 24.1784 | 12.2216 | 75 | 0 | 0 | 0 | 0 | 0 | 244.9406 | 0 | 999.8855 | 78.45% | 9.3739 | 0 | 50 | 100% | 38.6
8029 | 804 | 522 | 104 | 6.2461 | 19.3 | 404.6672 | 248.0327 | 0 | 212.1559 | 113.1 | 38.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 212.1559 | 0 | 1198.6458 | 94.05% | 0 | 0 | 50 | 100% | 36.9
8030 | 784 | 459 | 93 | 6.0446 | 19.4 | 394.6008 | 233.8268 | 0 | 199.1671 | 113.6773 | 38.8886 | 0 | 74.7886 | 0 | 0 | 0 | 0 | 0 | 199.1671 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.9
8031 | 521 | 316 | 126 | 6.8506 | 19 | 262.2284 | 0 | 140.3877 | 0 | 66.8084 | 14.9542 | 0 | 51.8542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.9
8032 | 610 | 195 | 54 | 6.6491 | 18.1 | 307.0236 | 0 | 133.8841 | 0 | 41.8405 | 1.1702 | 0 | 40.6702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.5
8033 | 215 | 40 | 18 | 5.6416 | 15.9 | 108.2132 | 0 | 0 | 0 | 4.4074 | 0 | 0 | 4.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.8117 | 47.62% | 29.4074
8034 | 0 | 0 | 0 | 3.0223 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.7312 | 0 | 0% | 22.7312
8035 | 0 | 0 | 0 | 2.4178 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2004 | 41.8 | 0 | 104.2004 | 1170.4414 | 91.83% | 0 | 0 | 0 | 0% | 41.8
8036 | 0 | 0 | 0 | 1.0074 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5263 | 39.9 | 0 | 99.5263 | 1071.7237 | 84.09% | 0 | 0 | 0 | 0% | 39.9
8037 | 0 | 0 | 0 | 1.4104 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0437 | 36.8 | 0 | 92.0437 | 981.851 | 77.04% | 0 | 0 | 0 | 0% | 36.8
8038 | 0 | 0 | 0 | 2.2164 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.392 | 33.6 | 0 | 84.392 | 901.0658 | 70.7% | 0 | 0 | 0 | 0% | 33.6
8039 | 0 | 0 | 0 | 1.8134 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5672 | 31.6 | 0 | 79.5672 | 825.9573 | 64.81% | 0 | 0 | 0 | 0% | 31.6
8040 | 0 | 0 | 0 | 3.0223 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1745 | 30.2 | 0 | 76.1745 | 754.7421 | 59.22% | 0 | 0 | 0 | 0% | 30.2
8041 | 0 | 0 | 0 | 2.4178 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3266 | 29.8 | 0 | 75.3266 | 684.5594 | 53.71% | 0 | 0 | 0 | 0% | 29.8
8042 | 0 | 0 | 0 | 1.4104 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2818 | 29.8 | 0 | 75.2818 | 614.3653 | 48.2% | 0 | 0 | 0 | 0% | 29.8
8043 | 0 | 0 | 0 | 1.4104 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5647 | 31.2 | 0 | 78.5647 | 540.331 | 42.4% | 0 | 0 | 0 | 0% | 31.2
8044 | 0 | 0 | 0 | 2.6193 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8448 | 35.5 | 0 | 88.8448 | 454.0121 | 35.62% | 0 | 0 | 0 | 0% | 35.5
8045 | 0 | 0 | 0 | 3.4253 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2037 | 41.9 | 0 | 104.2037 | 349.4863 | 27.42% | 0 | 0 | 0 | 0% | 41.9
8046 | 0 | 0 | 0 | 3.0223 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.1398 | 45.6 | 0 | 113.1398 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 45.6
8047 | 0 | 0 | 0 | 3.8283 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8048 | 0 | 21 | 21 | 3.6268 | 8.5 | 0 | 0 | 0 | 0 | 0.82697 | 0 | 0 | 0.82697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0.82697
8049 | 0 | 67 | 66 | 4.2312 | 9.1 | 0 | 0 | 0 | 0 | 5.017 | 0 | 0 | 5.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 5.017
8050 | 5 | 118 | 115 | 6.6491 | 10.7 | 2.5166 | 0 | 1.4057 | 0 | 9.6602 | 0 | 0 | 9.6602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 9.6602
8051 | 50 | 291 | 262 | 8.0595 | 12.5 | 25.1659 | 0 | 15.1082 | 0 | 31.0539 | 0 | 0 | 31.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 31.0539
8052 | 5 | 226 | 222 | 9.2684 | 13.3 | 2.5166 | 0 | 1.5487 | 0 | 19.7267 | 0 | 0 | 19.7267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 19.7267
8053 | 1 | 160 | 158 | 10.6788 | 13.1 | 0.50332 | 0 | 0.30812 | 0 | 12.8587 | 0 | 0 | 12.8587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 12.8587
8054 | 1 | 157 | 155 | 9.2684 | 12.9 | 0.50332 | 0 | 0.29786 | 0 | 12.8196 | 0 | 0 | 12.8196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 12.8196
8055 | 0 | 156 | 155 | 9.4699 | 13 | 0 | 0 | 0 | 0 | 13.5293 | 0 | 0 | 13.5293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 13.5293
8056 | 13 | 109 | 104 | 10.6788 | 13.1 | 6.5431 | 0 | 2.8387 | 0 | 10.0825 | 0 | 0 | 10.0825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 10.0825
8057 | 0 | 9 | 9 | 7.455 | 12.1 | 0 | 0 | 0 | 0 | 0.088611 | 0 | 0 | 0.088611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0.088611
8058 | 0 | 0 | 0 | 6.8506 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8059 | 0 | 0 | 0 | 5.8431 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8060 | 0 | 0 | 0 | 5.8431 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8061 | 0 | 0 | 0 | 6.4476 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8062 | 0 | 0 | 0 | 6.0446 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8063 | 0 | 0 | 0 | 5.2387 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8064 | 0 | 0 | 0 | 5.2387 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8065 | 0 | 0 | 0 | 4.6342 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8066 | 0 | 0 | 0 | 9.4699 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8067 | 0 | 0 | 0 | 9.4699 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8068 | 0 | 0 | 0 | 10.4773 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8069 | 0 | 0 | 0 | 6.8506 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8070 | 0 | 0 | 0 | 9.6714 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8071 | 0 | 0 | 0 | 6.6491 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8072 | 0 | 4 | 4 | 11.0818 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8073 | 0 | 30 | 30 | 16.119 | 11 | 0 | 0 | 0 | 0 | 1.8607 | 0 | 0 | 1.8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 1.8607
8074 | 0 | 20 | 20 | 14.3056 | 10.7 | 0 | 0 | 0 | 0 | 1.0979 | 0 | 0 | 1.0979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 1.0979
8075 | 0 | 8 | 7 | 15.1115 | 10.6 | 0 | 0 | 0 | 0 | 0.12224 | 0 | 0 | 0.12224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0.12224
8076 | 0 | 65 | 64 | 17.5294 | 10.9 | 0 | 0 | 0 | 0 | 4.5013 | 0 | 0 | 4.5013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 4.5013
8077 | 0 | 100 | 99 | 15.5145 | 10.5 | 0 | 0 | 0 | 0 | 7.3959 | 0 | 0 | 7.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 7.3959
8078 | 1 | 145 | 143 | 17.5294 | 10.7 | 0.50332 | 0 | 0.29749 | 0 | 11.7591 | 0 | 0 | 11.7591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 11.7591
8079 | 0 | 50 | 50 | 15.9175 | 10.5 | 0 | 0 | 0 | 0 | 3.4404 | 0 | 0 | 3.4404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 3.4404
8080 | 0 | 31 | 31 | 11.0818 | 10.3 | 0 | 0 | 0 | 0 | 1.9423 | 0 | 0 | 1.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 1.9423
8081 | 0 | 4 | 4 | 6.6491 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8082 | 0 | 0 | 0 | 6.0446 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8083 | 0 | 0 | 0 | 5.2387 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8084 | 0 | 0 | 0 | 5.8431 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8085 | 0 | 0 | 0 | 4.0297 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8086 | 0 | 0 | 0 | 4.6342 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8087 | 0 | 0 | 0 | 3.2238 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8088 | 0 | 0 | 0 | 3.4253 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8089 | 0 | 0 | 0 | 1.8134 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8090 | 0 | 0 | 0 | 2.8208 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8091 | 0 | 0 | 0 | 1.4104 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8092 | 0 | 0 | 0 | 2.4178 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8093 | 0 | 0 | 0 | 2.4178 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8094 | 0 | 0 | 0 | 3.0223 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8095 | 0 | 0 | 0 | 2.0149 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0
8096 | 0 | 21 | 21 | 2.0149 | 7.9 | 0 | 0 | 0 | 0 | 0.80798 | 0 | 0 | 0.80798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3081 | 18.38% | 0 | 0 | 0 | 0% | 0.80798
8097 | 484 | 191 | 70 | 1.2089 | 10.6 | 243.6056 | 116.2671 | 0 | 91.2113 | 35.7191 | 0 | 0 | 35.7191 | 0 | 0 | 0 | 0 | 0 | 91.2113 | 0 | 320.9303 | 25.18% | 0 | 0 | 0 | 0% | 35.7191
8098 | 770 | 364 | 83 | 2.0149 | 14.1 | 387.5544 | 216.0113 | 0 | 184.0936 | 79.82 | 0 | 15.26 | 64.56 | 0 | 0 | 0 | 0 | 0 | 184.0936 | 0 | 495.7617 | 38.9% | 11.7044 | 0 | 12.2655 | 24.53% | 49.3
8099 | 641 | 428 | 134 | 8.6639 | 15.4 | 322.6264 | 193.3988 | 0 | 159.6066 | 90.3778 | 0 | 20.4889 | 69.8889 | 0 | 0 | 0 | 0 | 0 | 159.6066 | 0 | 647.3381 | 50.79% | 15.715 | 0 | 28.7338 | 57.47% | 49.4
8100 | 309 | 334 | 175 | 12.2907 | 15.5 | 155.5251 | 95.5222 | 0 | 65.8122 | 46.9499 | 0 | 0 | 46.9499 | 0 | 0 | 0 | 0 | 0 | 65.8122 | 0 | 709.8391 | 55.7% | 0 | 0 | 28.7338 | 57.47% | 46.9499
8101 | 839 | 573 | 145 | 14.1041 | 16.9 | 422.2833 | 257.9106 | 0 | 216.4267 | 102.6 | 2.6 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 216.4267 | 0 | 915.3768 | 71.82% | 19.175 | 0 | 48.8281 | 97.66% | 47.4
8102 | 813 | 487 | 114 | 15.1115 | 16.9 | 409.197 | 241.5675 | 0 | 200.7013 | 102.7 | 27.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 200.7013 | 0 | 1105.9804 | 86.78% | 0 | 0 | 48.8281 | 97.66% | 47.3
8103 | 557 | 288 | 79 | 13.0966 | 16.3 | 280.3478 | 148.847 | 0 | 115.3936 | 54.2838 | 3.1419 | 0 | 51.1419 | 0 | 0 | 0 | 0 | 0 | 115.3936 | 0 | 1215.5682 | 95.38% | 0 | 0 | 48.8281 | 97.66% | 48
8104 | 145 | 112 | 71 | 7.6565 | 14.5 | 72.981 | 0 | 31.3464 | 0 | 15.775 | 0 | 0 | 15.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215.5682 | 95.38% | 0 | 25 | 22.6337 | 45.27% | 40.775
8105 | 6 | 15 | 14 | 6.0446 | 12.8 | 3.0199 | 0 | 0 | 0 | 0.43351 | 0 | 0 | 0.43351 | 0 | 0 | 0 | 71.4375 | 27.9649 | 0 | 71.4375 | 1149.5494 | 90.2% | 0 | 21.6016 | 0 | 0% | 50
8106 | 0 | 0 | 0 | 7.858 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.9796 | 50 | 0 | 123.9796 | 1021.2926 | 80.13% | 0 | 0 | 0 | 0% | 50
8107 | 0 | 0 | 0 | 8.261 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.7646 | 49.1 | 0 | 121.7646 | 895.6715 | 70.28% | 0 | 0 | 0 | 0% | 49.1
8108 | 0 | 0 | 0 | 3.4253 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0304 | 45.1 | 0 | 112.0304 | 781.6544 | 61.33% | 0 | 0 | 0 | 0% | 45.1
8109 | 0 | 0 | 0 | 2.6193 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.116 | 40.6 | 0 | 101.116 | 680.5316 | 53.4% | 0 | 0 | 0 | 0% | 40.6
8110 | 0 | 0 | 0 | 4.4327 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9087 | 37.6 | 0 | 93.9087 | 588.0025 | 46.14% | 0 | 0 | 0 | 0% | 37.6
8111 | 0 | 0 | 0 | 3.6268 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1614 | 34.8 | 0 | 87.1614 | 503.3993 | 39.5% | 0 | 0 | 0 | 0% | 34.8
8112 | 0 | 0 | 0 | 4.2312 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5769 | 33.3 | 0 | 83.5769 | 423.1315 | 33.2% | 0 | 0 | 0 | 0% | 33.3
8113 | 0 | 0 | 0 | 3.6268 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6591 | 32.5 | 0 | 81.6591 | 345.1419 | 27.08% | 0 | 0 | 0 | 0% | 32.5
8114 | 0 | 0 | 0 | 2.4178 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8613 | 32.6 | 0 | 81.8613 | 266.8363 | 20.94% | 0 | 0 | 0 | 0% | 32.6
8115 | 0 | 0 | 0 | 4.4327 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.1898 | 26.2274 | 0 | 67.1898 | 204.7764 | 16.07% | 0 | 0 | 0 | 0% | 26.2274
8116 | 0 | 0 | 0 | 4.6342 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.7764 | 16.07% | 0 | 0 | 0 | 0% | 0
8117 | 0 | 0 | 0 | 3.0223 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.7764 | 16.07% | 0 | 0 | 0 | 0% | 0
8118 | 0 | 0 | 0 | 2.8208 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.7764 | 16.07% | 0 | 0 | 0 | 0% | 0
8119 | 0 | 0 | 0 | 4.0297 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.7764 | 16.07% | 0 | 0 | 0 | 0% | 0
8120 | 0 | 13 | 13 | 4.2312 | 7 | 0 | 0 | 0 | 0 | 0.31639 | 0 | 0 | 0.31639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.7764 | 16.07% | 0 | 0 | 0 | 0% | 0.31639
8121 | 538 | 185 | 56 | 3.4253 | 9.6 | 270.7848 | 129.1115 | 0 | 102.1946 | 37.4635 | 0 | 0 | 37.4635 | 0 | 0 | 0 | 0 | 0 | 102.1946 | 0 | 302.7224 | 23.75% | 0 | 0 | 0 | 0% | 37.4635
8122 | 616 | 319 | 96 | 5.2387 | 11.1 | 310.0435 | 172.6473 | 0 | 142.3025 | 65.7107 | 0 | 8.5553 | 57.1553 | 0 | 0 | 0 | 0 | 0 | 142.3025 | 0 | 439.1088 | 34.45% | 6.562 | 0 | 6.8775 | 13.76% | 48.6
8123 | 459 | 398 | 187 | 7.455 | 12.6 | 231.0227 | 138.394 | 0 | 108.8317 | 72.4728 | 0 | 12.0864 | 60.3864 | 0 | 0 | 0 | 0 | 0 | 108.8317 | 0 | 543.416 | 42.64% | 9.2703 | 0 | 16.5936 | 33.19% | 48.3
8124 | 25 | 250 | 235 | 7.858 | 12.3 | 12.5829 | 0 | 7.7213 | 0 | 23.1056 | 0 | 0 | 23.1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 543.416 | 42.64% | 0 | 15.8348 | 0 | 0% | 38.9403
8125 | 6 | 254 | 249 | 8.4625 | 13 | 3.0199 | 0 | 1.8424 | 0 | 22.878 | 0 | 0 | 22.878 | 0 | 0 | 0 | 61.1842 | 23.422 | 0 | 61.1842 | 487.3391 | 38.24% | 0 | 0 | 0 | 0% | 46.3
8126 | 103 | 295 | 243 | 10.2758 | 13.3 | 51.8417 | 0 | 30.5686 | 0 | 33.2973 | 0 | 0 | 33.2973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 487.3391 | 38.24% | 0 | 0 | 0 | 0% | 33.2973
8127 | 211 | 266 | 188 | 9.4699 | 13.6 | 106.2 | 0 | 56.237 | 0 | 35.722 | 0 | 0 | 35.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 487.3391 | 38.24% | 0 | 0 | 0 | 0% | 35.722
8128 | 215 | 147 | 100 | 10.0743 | 13.1 | 108.2132 | 0 | 46.2529 | 0 | 23.429 | 0 | 0 | 23.429 | 0 | 0 | 0 | 65.3938 | 25.271 | 0 | 65.3938 | 427.1479 | 33.51% | 0 | 0 | 0 | 0% | 48.7
8129 | 58 | 33 | 25 | 7.858 | 11.9 | 29.1924 | 0 | 0 | 0 | 2.6449 | 0 | 0 | 2.6449 | 0 | 0 | 0 | 114.4502 | 46.0551 | 0 | 114.4502 | 310.4357 | 24.36% | 0 | 0 | 0 | 0% | 48.7
8130 | 0 | 0 | 0 | 6.6491 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2699 | 38.1322 | 0 | 95.2699 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 38.1322
8131 | 0 | 0 | 0 | 6.6491 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8132 | 0 | 0 | 0 | 5.2387 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8133 | 0 | 0 | 0 | 5.0372 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8134 | 0 | 0 | 0 | 5.4401 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8135 | 0 | 0 | 0 | 4.6342 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8136 | 0 | 0 | 0 | 7.2535 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8137 | 0 | 0 | 0 | 6.4476 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8138 | 0 | 0 | 0 | 5.2387 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8139 | 0 | 0 | 0 | 3.6268 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8140 | 0 | 0 | 0 | 4.8357 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8141 | 0 | 0 | 0 | 4.6342 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8142 | 0 | 0 | 0 | 5.6416 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8143 | 0 | 0 | 0 | 8.6639 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0
8144 | 0 | 13 | 13 | 9.6714 | 11.8 | 0 | 0 | 0 | 0 | 0.30284 | 0 | 0 | 0.30284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 0.30284
8145 | 3 | 89 | 88 | 10.0743 | 12.2 | 1.51 | 0 | 0.71936 | 0 | 7.6579 | 0 | 0 | 7.6579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 7.6579
8146 | 199 | 265 | 189 | 9.8729 | 13.1 | 100.1602 | 0 | 55.7276 | 0 | 35.0716 | 0 | 0 | 35.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 35.0716
8147 | 160 | 321 | 245 | 9.0669 | 13.8 | 80.5308 | 0 | 48.212 | 0 | 39.6409 | 0 | 0 | 39.6409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.4309 | 16.98% | 0 | 0 | 0 | 0% | 39.6409
8148 | 281 | 345 | 202 | 9.6714 | 14.4 | 141.4322 | 86.7137 | 0 | 59.3826 | 54.4287 | 0 | 6.9643 | 47.4643 | 0 | 0 | 0 | 0 | 0 | 59.3826 | 0 | 273.2347 | 21.44% | 5.3416 | 0 | 5.599 | 11.2% | 40.5
8149 | 600 | 514 | 207 | 9.8729 | 15.2 | 301.9904 | 184.0475 | 0 | 150.141 | 111.4 | 11.4 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 150.141 | 0 | 416.8555 | 32.71% | 19.175 | 0 | 25.6977 | 51.4% | 38.6
8150 | 628 | 432 | 143 | 10.6788 | 15.4 | 316.0833 | 186.1689 | 0 | 151.6204 | 102.001 | 7.1005 | 25 | 69.9005 | 0 | 0 | 0 | 0 | 0 | 151.6204 | 0 | 561.8914 | 44.09% | 19.175 | 0 | 45.7965 | 91.59% | 37.8
8151 | 656 | 337 | 99 | 10.0743 | 15.5 | 330.1762 | 174.3928 | 0 | 141.082 | 82.0639 | 16.6535 | 5.2285 | 60.182 | 0 | 0 | 0 | 0 | 0 | 141.082 | 0 | 696.8466 | 54.68% | 4.0102 | 0 | 50 | 100% | 38.3
8152 | 487 | 180 | 67 | 12.0892 | 14.6 | 245.1156 | 104.2678 | 0 | 73.9613 | 35.5637 | 0 | 0 | 35.5637 | 0 | 0 | 0 | 0 | 0 | 73.9613 | 0 | 767.596 | 60.23% | 0 | 5.4363 | 44.3027 | 88.61% | 41
8153 | 90 | 33 | 23 | 10.6788 | 12.9 | 45.2986 | 0 | 0 | 0 | 2.7849 | 0 | 0 | 2.7849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.596 | 60.23% | 0 | 25 | 18.102 | 36.2% | 27.7849
8154 | 0 | 0 | 0 | 7.2535 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.0984 | 25.2271 | 0 | 65.0984 | 707.7192 | 55.53% | 0 | 17.2729 | 0 | 0% | 42.5
8155 | 0 | 0 | 0 | 6.8506 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.4918 | 42.4 | 0 | 105.4918 | 601.6231 | 47.2% | 0 | 0 | 0 | 0% | 42.4
8156 | 0 | 0 | 0 | 6.8506 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5623 | 41.2 | 0 | 102.5623 | 498.9227 | 39.15% | 0 | 0 | 0 | 0% | 41.2
8157 | 0 | 0 | 0 | 6.4476 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3198 | 38.6 | 0 | 96.3198 | 403.6371 | 31.67% | 0 | 0 | 0 | 0% | 38.6
8158 | 0 | 0 | 0 | 6.4476 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5668 | 35.8 | 0 | 89.5668 | 316.2899 | 24.82% | 0 | 0 | 0 | 0% | 35.8
8159 | 0 | 0 | 0 | 6.4476 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8582 | 33 | 0 | 82.8582 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 33
8160 | 0 | 0 | 0 | 2.2164 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 0
8161 | 0 | 0 | 0 | 2.0149 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 0
8162 | 0 | 0 | 0 | 3.0223 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 0
8163 | 0 | 0 | 0 | 3.4253 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 0
8164 | 0 | 0 | 0 | 2.6193 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 0
8165 | 0 | 0 | 0 | 2.4178 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 0
8166 | 0 | 0 | 0 | 3.0223 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 0
8167 | 0 | 0 | 0 | 4.6342 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 0
8168 | 2 | 16 | 16 | 4.2312 | 8.3 | 1.0066 | 0 | 0 | 0 | 0.49798 | 0 | 0 | 0.49798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 0.49798
8169 | 0 | 69 | 69 | 4.0297 | 9.2 | 0 | 0 | 0 | 0 | 5.4155 | 0 | 0 | 5.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 5.4155
8170 | 1 | 145 | 143 | 2.8208 | 10.6 | 0.50332 | 0 | 0.27983 | 0 | 12.4078 | 0 | 0 | 12.4078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 12.4078
8171 | 12 | 246 | 237 | 3.8283 | 12.4 | 6.0398 | 0 | 3.6138 | 0 | 22.6815 | 0 | 0 | 22.6815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236.9615 | 18.59% | 0 | 0 | 0 | 0% | 22.6815
8172 | 523 | 444 | 174 | 4.4327 | 14 | 263.235 | 161.263 | 0 | 131.9653 | 92.4206 | 1.3103 | 25 | 66.1103 | 0 | 0 | 0 | 0 | 0 | 131.9653 | 0 | 363.1323 | 28.49% | 19.175 | 0 | 20.1017 | 40.2% | 39.8
8173 | 786 | 507 | 109 | 5.2387 | 15.4 | 395.6075 | 240.8619 | 0 | 206.0825 | 111.5 | 11.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 206.0825 | 0 | 560.1659 | 43.95% | 19.175 | 0 | 40.2034 | 80.41% | 38.5
8174 | 628 | 480 | 188 | 4.6342 | 16.4 | 316.0833 | 185.9661 | 0 | 155.0602 | 106.8128 | 22.4727 | 12.1837 | 72.1564 | 0 | 0 | 0 | 0 | 0 | 155.0602 | 0 | 708.4175 | 55.58% | 9.3449 | 0 | 50 | 100% | 37.5
8175 | 113 | 199 | 160 | 4.0297 | 16.1 | 56.8749 | 0 | 29.9654 | 0 | 24.6458 | 0 | 0 | 24.6458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 708.4175 | 55.58% | 0 | 13.5542 | 35.793 | 71.59% | 38.2
8176 | 6 | 83 | 81 | 4.2312 | 15.1 | 3.0199 | 0 | 1.2786 | 0 | 6.9036 | 0 | 0 | 6.9036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 708.4175 | 55.58% | 0 | 25 | 9.588 | 19.18% | 31.9036
8177 | 15 | 23 | 22 | 4.8357 | 13.7 | 7.5498 | 0 | 0 | 0 | 1.1687 | 0 | 0 | 1.1687 | 0 | 0 | 0 | 79.5616 | 31.4833 | 0 | 79.5616 | 633.4795 | 49.7% | 0 | 9.148 | 0 | 0% | 41.8
8178 | 0 | 0 | 0 | 3.2238 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.1386 | 42.6 | 0 | 106.1386 | 526.8222 | 41.34% | 0 | 0 | 0 | 0% | 42.6
8179 | 0 | 0 | 0 | 1.4104 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2821 | 42.3 | 0 | 105.2821 | 421.0006 | 33.03% | 0 | 0 | 0 | 0% | 42.3
8180 | 0 | 0 | 0 | 2.2164 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.116 | 40.6 | 0 | 101.116 | 319.9822 | 25.11% | 0 | 0 | 0 | 0% | 40.6
8181 | 0 | 0 | 0 | 1.8134 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9864 | 33.4711 | 0 | 83.9864 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 33.4711
8182 | 0 | 0 | 0 | 1.0074 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8183 | 0 | 0 | 0 | 1.2089 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8184 | 0 | 0 | 0 | 1.4104 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8185 | 0 | 0 | 0 | 1.8134 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8186 | 0 | 0 | 0 | 2.4178 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8187 | 0 | 0 | 0 | 2.0149 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8188 | 0 | 0 | 0 | 2.6193 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8189 | 0 | 0 | 0 | 3.6268 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8190 | 0 | 0 | 0 | 3.2238 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8191 | 0 | 0 | 0 | 4.2312 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 0
8192 | 149 | 34 | 19 | 3.2238 | 7.5 | 74.9943 | 0 | 0 | 0 | 3.4762 | 0 | 0 | 3.4762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3163 | 18.78% | 0 | 0 | 0 | 0% | 3.4762
8193 | 569 | 182 | 54 | 2.2164 | 10.4 | 286.3876 | 136.287 | 0 | 109.373 | 37.5281 | 0 | 0 | 37.5281 | 0 | 0 | 0 | 0 | 0 | 109.373 | 0 | 344.1009 | 27% | 0 | 0 | 0 | 0% | 37.5281
8194 | 756 | 339 | 69 | 1.0074 | 13.9 | 380.5079 | 211.4222 | 0 | 180.1926 | 83.4872 | 0 | 22.5936 | 60.8936 | 0 | 0 | 0 | 0 | 0 | 180.1926 | 0 | 516.7342 | 40.54% | 17.3293 | 0 | 18.1694 | 36.34% | 38.3
8195 | 836 | 454 | 76 | 1.4104 | 15.7 | 420.7733 | 251.6347 | 0 | 217.5185 | 111.3729 | 11.4365 | 25 | 74.9365 | 0 | 0 | 0 | 0 | 0 | 217.5185 | 0 | 725.1276 | 56.89% | 19.175 | 0 | 38.2741 | 76.55% | 38.5
8196 | 871 | 515 | 77 | 3.4253 | 16 | 438.3894 | 268.3649 | 0 | 232.4005 | 111.7 | 22.1189 | 14.5811 | 75 | 0 | 0 | 0 | 0 | 0 | 232.4005 | 0 | 947.7787 | 74.36% | 11.1837 | 0 | 50 | 100% | 38.3
8197 | 872 | 516 | 76 | 5.2387 | 16.7 | 438.8928 | 266.9626 | 0 | 230.3735 | 113.2 | 38.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 230.3735 | 0 | 1168.4877 | 91.68% | 0 | 0 | 50 | 100% | 36.8
8198 | 842 | 456 | 73 | 5.2387 | 17.3 | 423.7932 | 249.0757 | 0 | 213.7083 | 113.9 | 38.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 213.7083 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.1
8199 | 774 | 342 | 63 | 5.2387 | 17.6 | 389.5677 | 0 | 204.753 | 0 | 89.1793 | 26.1896 | 0 | 62.9896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.8
8200 | 627 | 190 | 47 | 6.2461 | 17.1 | 315.58 | 0 | 133.0027 | 0 | 40.5491 | 0.57453 | 0 | 39.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39.4
8201 | 218 | 39 | 17 | 4.0297 | 15.1 | 109.7232 | 0 | 0 | 0 | 4.3086 | 0 | 0 | 4.3086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.7919 | 47.58% | 29.3086
8202 | 0 | 0 | 0 | 5.4401 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.6953 | 0 | 0% | 22.6953
8203 | 0 | 0 | 0 | 1.2089 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5803 | 42 | 0 | 104.5803 | 1169.7885 | 91.78% | 0 | 0 | 0 | 0% | 42
8204 | 0 | 0 | 0 | 1.6119 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1556 | 40.6 | 0 | 101.1556 | 1069.0145 | 83.88% | 0 | 0 | 0 | 0% | 40.6
8205 | 0 | 0 | 0 | 2.8208 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0092 | 37.2 | 0 | 93.0092 | 977.939 | 76.73% | 0 | 0 | 0 | 0% | 37.2
8206 | 0 | 0 | 0 | 3.6268 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8151 | 34.2 | 0 | 85.8151 | 895.3564 | 70.25% | 0 | 0 | 0 | 0% | 34.2
8207 | 0 | 0 | 0 | 5.0372 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8758 | 31.7 | 0 | 79.8758 | 819.9078 | 64.33% | 0 | 0 | 0 | 0% | 31.7
8208 | 0 | 0 | 0 | 3.0223 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5555 | 30.3 | 0 | 76.5555 | 748.3605 | 58.72% | 0 | 0 | 0 | 0% | 30.3
8209 | 0 | 0 | 0 | 3.4253 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.558 | 29.4 | 0 | 74.558 | 679.1052 | 53.28% | 0 | 0 | 0 | 0% | 29.4
8210 | 0 | 0 | 0 | 1.6119 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3532 | 29.3 | 0 | 74.3532 | 610.0838 | 47.87% | 0 | 0 | 0 | 0% | 29.3
8211 | 0 | 0 | 0 | 2.2164 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5479 | 30.3 | 0 | 76.5479 | 538.5012 | 42.25% | 0 | 0 | 0 | 0% | 30.3
8212 | 0 | 0 | 0 | 1.8134 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6559 | 33.7 | 0 | 84.6559 | 457.2839 | 35.88% | 0 | 0 | 0 | 0% | 33.7
8213 | 0 | 0 | 0 | 2.4178 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9412 | 38 | 0 | 94.9412 | 363.8067 | 28.54% | 0 | 0 | 0 | 0% | 38
8214 | 0 | 0 | 0 | 4.8357 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4513 | 40.3 | 0 | 100.4513 | 263.6986 | 20.69% | 0 | 0 | 0 | 0% | 40.3
8215 | 0 | 0 | 0 | 7.455 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2683 | 31.8674 | 0 | 80.2683 | 187.6543 | 14.72% | 0 | 0 | 0 | 0% | 31.8674
8216 | 232 | 50 | 28 | 4.8357 | 11.6 | 116.7696 | 0 | 0 | 0 | 4.7605 | 0 | 0 | 4.7605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187.6543 | 14.72% | 0 | 0 | 0 | 0% | 4.7605
8217 | 375 | 187 | 102 | 3.6268 | 13.7 | 188.744 | 89.793 | 0 | 65.5881 | 31.7214 | 0 | 0 | 31.7214 | 0 | 0 | 0 | 0 | 0 | 65.5881 | 0 | 249.7185 | 19.59% | 0 | 0 | 0 | 0% | 31.7214
8218 | 331 | 269 | 150 | 1.6119 | 16.8 | 166.5981 | 92.519 | 0 | 68.7684 | 39.4907 | 0 | 0 | 39.4907 | 0 | 0 | 0 | 0 | 0 | 68.7684 | 0 | 314.792 | 24.7% | 0 | 0 | 0 | 0% | 39.4907
8219 | 483 | 393 | 170 | 1.0074 | 18.7 | 243.1023 | 145.3146 | 0 | 118.4416 | 69.4611 | 0 | 12.3806 | 57.0806 | 0 | 0 | 0 | 0 | 0 | 118.4416 | 0 | 426.8699 | 33.49% | 9.4959 | 0 | 9.9577 | 19.92% | 44.7
8220 | 352 | 372 | 192 | 1.4104 | 19.6 | 177.1677 | 108.3796 | 0 | 83.5429 | 56.0807 | 0 | 6.0903 | 49.9903 | 0 | 0 | 0 | 0 | 0 | 83.5429 | 0 | 505.9241 | 39.7% | 4.6713 | 0 | 14.8562 | 29.71% | 43.9
8221 | 849 | 523 | 96 | 2.0149 | 20.8 | 427.3165 | 259.6878 | 0 | 224.8207 | 107.1 | 7.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 224.8207 | 0 | 718.6655 | 56.39% | 19.175 | 0 | 34.9639 | 69.93% | 42.9
8222 | 870 | 494 | 99 | 4.4327 | 21.5 | 437.8861 | 257.1002 | 0 | 221.572 | 107.8 | 14.1056 | 18.6944 | 75 | 0 | 0 | 0 | 0 | 0 | 221.572 | 0 | 928.3327 | 72.84% | 14.3386 | 0 | 50 | 100% | 42.2
8223 | 728 | 362 | 99 | 3.8283 | 21.7 | 366.4151 | 192.133 | 0 | 161.1614 | 82.1961 | 19.648 | 0 | 62.548 | 0 | 0 | 0 | 0 | 0 | 161.1614 | 0 | 1080.8351 | 84.8% | 0 | 0 | 50 | 100% | 42.9
8224 | 350 | 195 | 106 | 4.2312 | 20.7 | 176.1611 | 73.9121 | 0 | 49.9834 | 30.4844 | 0 | 0 | 30.4844 | 0 | 0 | 0 | 0 | 0 | 49.9834 | 0 | 1128.133 | 88.52% | 0 | 15.0156 | 34.2566 | 68.51% | 45.5
8225 | 8 | 27 | 26 | 3.0223 | 16.9 | 4.0265 | 0 | 0 | 0 | 1.4753 | 0 | 0 | 1.4753 | 0 | 0 | 0 | 53.8989 | 20.1247 | 0 | 53.8989 | 1079.2209 | 84.68% | 0 | 25 | 8.0438 | 16.09% | 46.6
8226 | 0 | 0 | 0 | 1.6119 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3125 | 39.7275 | 0 | 99.3125 | 981.0421 | 76.97% | 0 | 7.6725 | 0 | 0% | 47.4
8227 | 0 | 0 | 0 | 2.8208 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.0473 | 46.7 | 0 | 116.0473 | 862.9377 | 67.71% | 0 | 0 | 0 | 0% | 46.7
8228 | 0 | 0 | 0 | 3.2238 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0642 | 43.4 | 0 | 108.0642 | 754.3055 | 59.18% | 0 | 0 | 0 | 0% | 43.4
8229 | 0 | 0 | 0 | 3.4253 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1545 | 39.3 | 0 | 98.1545 | 657.3161 | 51.57% | 0 | 0 | 0 | 0% | 39.3
8230 | 0 | 0 | 0 | 4.8357 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9758 | 36.3 | 0 | 90.9758 | 568.8431 | 44.63% | 0 | 0 | 0 | 0% | 36.3
8231 | 0 | 0 | 0 | 4.0297 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.731 | 33.7 | 0 | 84.731 | 487.7593 | 38.27% | 0 | 0 | 0 | 0% | 33.7
8232 | 0 | 0 | 0 | 3.0223 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8199 | 32.1 | 0 | 80.8199 | 411.2262 | 32.27% | 0 | 0 | 0 | 0% | 32.1
8233 | 0 | 0 | 0 | 4.0297 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1102 | 31.4 | 0 | 79.1102 | 336.6476 | 26.41% | 0 | 0 | 0 | 0% | 31.4
8234 | 0 | 0 | 0 | 5.4401 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0777 | 31.4 | 0 | 79.0777 | 262.0491 | 20.56% | 0 | 0 | 0 | 0% | 31.4
8235 | 0 | 0 | 0 | 3.6268 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.0276 | 21.3511 | 0 | 56.0276 | 210.9799 | 16.55% | 0 | 0 | 0 | 0% | 21.3511
8236 | 0 | 0 | 0 | 4.0297 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.9799 | 16.55% | 0 | 0 | 0 | 0% | 0
8237 | 0 | 0 | 0 | 2.8208 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.9799 | 16.55% | 0 | 0 | 0 | 0% | 0
8238 | 0 | 0 | 0 | 5.4401 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.9799 | 16.55% | 0 | 0 | 0 | 0% | 0
8239 | 0 | 0 | 0 | 5.4401 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.9799 | 16.55% | 0 | 0 | 0 | 0% | 0
8240 | 261 | 38 | 14 | 5.0372 | 8.1 | 131.3658 | 0 | 0 | 0 | 4.031 | 0 | 0 | 4.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.9799 | 16.55% | 0 | 0 | 0 | 0% | 4.031
8241 | 736 | 196 | 37 | 1.0074 | 10.5 | 370.4416 | 176.2109 | 0 | 147.3165 | 42.3184 | 0 | 0 | 42.3184 | 0 | 0 | 0 | 0 | 0 | 147.3165 | 0 | 350.9147 | 27.53% | 0 | 0 | 0 | 0% | 42.3184
8242 | 893 | 359 | 48 | 0.80595 | 15.3 | 449.4624 | 249.5017 | 0 | 215.7583 | 84.0179 | 0 | 17.9089 | 66.1089 | 0 | 0 | 0 | 0 | 0 | 215.7583 | 0 | 555.8618 | 43.61% | 13.7362 | 0 | 14.4063 | 28.81% | 48.2
8243 | 962 | 480 | 52 | 1.8134 | 17.6 | 484.1913 | 289.3064 | 0 | 252.7461 | 102.1 | 2.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 252.7461 | 0 | 795.9433 | 62.45% | 19.175 | 0 | 34.5169 | 69.03% | 47.9
8244 | 987 | 543 | 53 | 2.2164 | 18.7 | 496.7743 | 303.6983 | 0 | 266.0273 | 103.2 | 8.9526 | 19.2474 | 75 | 0 | 0 | 0 | 0 | 0 | 266.0273 | 0 | 1048.6405 | 82.28% | 14.7627 | 0 | 50 | 100% | 46.8
8245 | 980 | 541 | 53 | 3.0223 | 19.8 | 493.251 | 299.5032 | 0 | 261.8585 | 103.8 | 28.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 261.8585 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.2
8246 | 950 | 479 | 51 | 3.0223 | 20.4 | 478.1515 | 0 | 280.4721 | 0 | 103.9 | 28.9 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.1
8247 | 879 | 360 | 46 | 3.6268 | 20.5 | 442.416 | 0 | 231.4592 | 0 | 85.8356 | 19.4678 | 0 | 66.3678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.9
8248 | 729 | 201 | 37 | 5.6416 | 18.4 | 366.9184 | 0 | 153.2774 | 0 | 43.5553 | 0 | 0 | 43.5553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 5.7447 | 43.9759 | 87.95% | 49.3
8249 | 290 | 43 | 15 | 3.0223 | 15.8 | 145.962 | 0 | 0 | 0 | 4.8235 | 0 | 0 | 4.8235 | 0 | 0 | 0 | 53.9472 | 20.1765 | 0 | 53.9472 | 1225.5425 | 96.16% | 0 | 25 | 17.7598 | 35.52% | 50
8250 | 0 | 0 | 0 | 1.6119 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2559 | 33.0637 | 0 | 83.2559 | 1146.3368 | 89.94% | 0 | 16.9363 | 0 | 0% | 50
8251 | 0 | 0 | 0 | 1.2089 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.8764 | 49.6 | 0 | 122.8764 | 1019.7823 | 80.01% | 0 | 0 | 0 | 0% | 49.6
8252 | 0 | 0 | 0 | 2.2164 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3952 | 45.7 | 0 | 113.3952 | 904.5226 | 70.97% | 0 | 0 | 0 | 0% | 45.7
8253 | 0 | 0 | 0 | 1.6119 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.259 | 41.1 | 0 | 102.259 | 802.406 | 62.96% | 0 | 0 | 0 | 0% | 41.1
8254 | 0 | 0 | 0 | 3.2238 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6496 | 37.9 | 0 | 94.6496 | 709.4011 | 55.66% | 0 | 0 | 0 | 0% | 37.9
8255 | 0 | 0 | 0 | 1.4104 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6382 | 35 | 0 | 87.6382 | 624.569 | 49% | 0 | 0 | 0 | 0% | 35
8256 | 0 | 0 | 0 | 3.2238 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0557 | 33.5 | 0 | 84.0557 | 544.0617 | 42.69% | 0 | 0 | 0 | 0% | 33.5
8257 | 0 | 0 | 0 | 3.0223 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3788 | 32.8 | 0 | 82.3788 | 465.5359 | 36.53% | 0 | 0 | 0 | 0% | 32.8
8258 | 0 | 0 | 0 | 2.6193 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3788 | 32.8 | 0 | 82.3788 | 386.9949 | 30.36% | 0 | 0 | 0 | 0% | 32.8
8259 | 0 | 0 | 0 | 3.8283 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5219 | 33.7 | 0 | 84.5219 | 305.856 | 24% | 0 | 0 | 0 | 0% | 33.7
8260 | 0 | 0 | 0 | 4.0297 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1293 | 37.7 | 0 | 94.1293 | 213.305 | 16.74% | 0 | 0 | 0 | 0% | 37.7
8261 | 0 | 0 | 0 | 4.0297 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.305 | 16.74% | 0 | 0 | 0 | 0% | 0
8262 | 0 | 0 | 0 | 5.2387 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.305 | 16.74% | 0 | 0 | 0 | 0% | 0
8263 | 0 | 0 | 0 | 4.6342 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.305 | 16.74% | 0 | 0 | 0 | 0% | 0
8264 | 81 | 29 | 22 | 5.0372 | 9.8 | 40.7687 | 0 | 0 | 0 | 2.494 | 0 | 0 | 2.494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.305 | 16.74% | 0 | 0 | 0 | 0% | 2.494
8265 | 334 | 155 | 81 | 3.0223 | 11.8 | 168.108 | 79.9686 | 0 | 56.1369 | 27.2485 | 0 | 0 | 27.2485 | 0 | 0 | 0 | 0 | 0 | 56.1369 | 0 | 266.9076 | 20.94% | 0 | 0 | 0 | 0% | 27.2485
8266 | 711 | 386 | 139 | 2.4178 | 17 | 357.8587 | 198.5897 | 0 | 167.6816 | 80.3185 | 0 | 15.8092 | 64.5092 | 0 | 0 | 0 | 0 | 0 | 167.6816 | 0 | 427.0192 | 33.5% | 12.1257 | 0 | 12.7192 | 25.44% | 48.7
8267 | 527 | 382 | 144 | 7.052 | 19.2 | 265.2483 | 158.4299 | 0 | 127.9519 | 71.365 | 0 | 11.5325 | 59.8325 | 0 | 0 | 0 | 0 | 0 | 127.9519 | 0 | 549.1948 | 43.09% | 8.8454 | 0 | 21.9976 | 44% | 48.3
8268 | 619 | 467 | 157 | 12.2907 | 20.7 | 311.5535 | 190.353 | 0 | 154.6915 | 97.9794 | 0.48972 | 25 | 72.4897 | 0 | 0 | 0 | 0 | 0 | 154.6915 | 0 | 696.9027 | 54.68% | 19.175 | 0 | 42.1112 | 84.22% | 47
8269 | 800 | 499 | 100 | 16.3204 | 21.7 | 402.6539 | 244.2975 | 0 | 202.7015 | 103.1 | 18.2947 | 9.8053 | 75 | 0 | 0 | 0 | 0 | 0 | 202.7015 | 0 | 890.4534 | 69.87% | 7.5207 | 0 | 50 | 100% | 46.9
8270 | 898 | 465 | 61 | 17.5294 | 21.2 | 451.979 | 264.8772 | 0 | 221.0794 | 103.6 | 28.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 221.0794 | 0 | 1101.5522 | 86.43% | 0 | 0 | 50 | 100% | 46.4
8271 | 579 | 334 | 116 | 13.2981 | 20.8 | 291.4208 | 152.1297 | 0 | 118.4191 | 63.8802 | 8.3401 | 0 | 55.5401 | 0 | 0 | 0 | 0 | 0 | 118.4191 | 0 | 1214.6252 | 95.3% | 0 | 0 | 50 | 100% | 47.2
8272 | 385 | 178 | 94 | 12.2907 | 19.3 | 193.7772 | 80.6055 | 0 | 51.6917 | 32.129 | 0 | 0 | 32.129 | 0 | 0 | 0 | 0 | 0 | 51.6917 | 0 | 1263.9833 | 99.17% | 0 | 17.571 | 31.5718 | 63.14% | 49.7
8273 | 65 | 36 | 28 | 11.6862 | 17.4 | 32.7156 | 0 | 0 | 0 | 3.0133 | 0 | 0 | 3.0133 | 0 | 0 | 0 | 58.3474 | 21.9867 | 0 | 58.3474 | 1210.8326 | 95% | 0 | 25 | 5.3511 | 10.7% | 50
8274 | 0 | 0 | 0 | 12.2907 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.9911 | 44.897 | 0 | 111.9911 | 1097.9258 | 86.14% | 0 | 5.103 | 0 | 0% | 50
8275 | 0 | 0 | 0 | 5.6416 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.1608 | 50 | 0 | 124.1608 | 970.191 | 76.12% | 0 | 0 | 0 | 0% | 50
8276 | 0 | 0 | 0 | 6.2461 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.3505 | 46 | 0 | 114.3505 | 854.091 | 67.01% | 0 | 0 | 0 | 0% | 46
8277 | 0 | 0 | 0 | 6.4476 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0043 | 41.3 | 0 | 103.0043 | 751.4275 | 58.96% | 0 | 0 | 0 | 0% | 41.3
8278 | 0 | 0 | 0 | 6.6491 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9728 | 38 | 0 | 94.9728 | 658.1537 | 51.64% | 0 | 0 | 0 | 0% | 38
8279 | 0 | 0 | 0 | 2.4178 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3629 | 35.3 | 0 | 88.3629 | 572.4731 | 44.92% | 0 | 0 | 0 | 0% | 35.3
8280 | 0 | 0 | 0 | 5.6416 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.295 | 33.6 | 0 | 84.295 | 491.6807 | 38.58% | 0 | 0 | 0 | 0% | 33.6
8281 | 0 | 0 | 0 | 3.6268 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5808 | 32.9 | 0 | 82.5808 | 412.871 | 32.39% | 0 | 0 | 0 | 0% | 32.9
8282 | 0 | 0 | 0 | 3.0223 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0581 | 32.7 | 0 | 82.0581 | 334.6102 | 26.25% | 0 | 0 | 0 | 0% | 32.7
8283 | 0 | 0 | 0 | 3.6268 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7041 | 33.8 | 0 | 84.7041 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 33.8
8284 | 0 | 0 | 0 | 4.2312 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8285 | 0 | 0 | 0 | 2.8208 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8286 | 0 | 0 | 0 | 1.0074 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8287 | 0 | 0 | 0 | 0.80595 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8288 | 7 | 19 | 19 | 2.0149 | 6.6 | 3.5232 | 0 | 0 | 0 | 0.88405 | 0 | 0 | 0.88405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0.88405
8289 | 100 | 113 | 91 | 1.2089 | 8.3 | 50.3317 | 0 | 23.9478 | 0 | 14.9381 | 0 | 0 | 14.9381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 14.9381
8290 | 45 | 150 | 132 | 9.6714 | 10.6 | 22.6493 | 0 | 12.5664 | 0 | 15.678 | 0 | 0 | 15.678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 15.678
8291 | 0 | 118 | 117 | 2.4178 | 11.1 | 0 | 0 | 0 | 0 | 9.1346 | 0 | 0 | 9.1346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 9.1346
8292 | 150 | 272 | 194 | 7.2535 | 13.2 | 75.4976 | 0 | 46.1028 | 0 | 33.2104 | 0 | 0 | 33.2104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 33.2104
8293 | 3 | 158 | 155 | 14.5071 | 13.3 | 1.51 | 0 | 0.91543 | 0 | 12.8511 | 0 | 0 | 12.8511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 12.8511
8294 | 0 | 155 | 154 | 17.7308 | 14 | 0 | 0 | 0 | 0 | 12.7172 | 0 | 0 | 12.7172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 12.7172
8295 | 71 | 181 | 155 | 16.5219 | 14.5 | 35.7355 | 0 | 18.6157 | 0 | 20.221 | 0 | 0 | 20.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 20.221
8296 | 90 | 136 | 114 | 17.5294 | 14.5 | 45.2986 | 0 | 18.7652 | 0 | 16.8759 | 0 | 0 | 16.8759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 16.8759
8297 | 30 | 30 | 26 | 19.3427 | 13.1 | 15.0995 | 0 | 0 | 0 | 2.0835 | 0 | 0 | 2.0835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 2.0835
8298 | 0 | 0 | 0 | 21.9621 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8299 | 0 | 0 | 0 | 23.171 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8300 | 0 | 0 | 0 | 11.8877 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8301 | 0 | 0 | 0 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8302 | 0 | 0 | 0 | 0 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8303 | 0 | 0 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8312 | 0 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11283 | 0 | 0 | 0.11283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0.11283
8313 | 0 | 44 | 45 | 17.5294 | 11.6 | 0 | 0 | 0 | 0 | 3.0174 | 0 | 0 | 3.0174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 3.0174
8314 | 0 | 67 | 67 | 23.9769 | 18.5 | 0 | 0 | 0 | 0 | 4.654 | 0 | 0 | 4.654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 4.654
8315 | 0 | 88 | 88 | 19.7457 | 18.3 | 0 | 0 | 0 | 0 | 6.3372 | 0 | 0 | 6.3372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 6.3372
8316 | 0 | 122 | 121 | 17.1264 | 17 | 0 | 0 | 0 | 0 | 9.2184 | 0 | 0 | 9.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 9.2184
8317 | 0 | 142 | 141 | 18.3353 | 16.5 | 0 | 0 | 0 | 0 | 11.0993 | 0 | 0 | 11.0993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 11.0993
8318 | 0 | 116 | 116 | 17.3279 | 16.2 | 0 | 0 | 0 | 0 | 8.9121 | 0 | 0 | 8.9121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 8.9121
8319 | 0 | 80 | 80 | 0 | 16.3 | 0 | 0 | 0 | 0 | 5.787 | 0 | 0 | 5.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 5.787
8320 | 0 | 31 | 31 | 0 | 15.9 | 0 | 0 | 0 | 0 | 1.885 | 0 | 0 | 1.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 1.885
8321 | 7 | 6 | 6 | 0 | 1.1 | 3.5232 | 0 | 0 | 0 | 0.080184 | 0 | 0 | 0.080184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0.080184
8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 0
8336 | 77 | 28 | 21 | 0 | 0 | 38.7554 | 0 | 0 | 0 | 2.3934 | 0 | 0 | 2.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.173 | 19.86% | 0 | 0 | 0 | 0% | 2.3934
8337 | 435 | 164 | 76 | 0 | 0 | 218.9431 | 104.2707 | 0 | 80.1694 | 31.8844 | 0 | 0 | 31.8844 | 0 | 0 | 0 | 0 | 0 | 80.1694 | 0 | 330.1107 | 25.9% | 0 | 0 | 0 | 0% | 31.8844
8338 | 431 | 267 | 121 | 0 | 0 | 216.9298 | 120.3466 | 0 | 95.4383 | 50.1419 | 0 | 4.171 | 45.971 | 0 | 0 | 0 | 0 | 0 | 95.4383 | 0 | 421.7021 | 33.09% | 3.1991 | 0 | 3.3565 | 6.713% | 41.8
8339 | 666 | 412 | 124 | 0 | 0 | 335.2094 | 200.064 | 0 | 169.9574 | 97.2242 | 2.6621 | 25 | 69.5621 | 0 | 0 | 0 | 0 | 0 | 169.9574 | 0 | 584.8091 | 45.89% | 19.175 | 0 | 23.4748 | 46.95% | 41.9
8340 | 846 | 505 | 97 | 0 | 0 | 425.8065 | 259.7835 | 0 | 225.6482 | 108.9 | 8.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 225.6482 | 0 | 801.3623 | 62.88% | 19.175 | 0 | 43.5931 | 87.19% | 41.1
8341 | 873 | 503 | 80 | 0 | 0 | 439.3961 | 266.0349 | 0 | 231.4922 | 110.4 | 27.4385 | 7.9615 | 75 | 0 | 0 | 0 | 0 | 0 | 231.4922 | 0 | 1023.524 | 80.31% | 6.1065 | 0 | 50 | 100% | 39.6
8342 | 885 | 452 | 65 | 0 | 0 | 445.4359 | 260.0854 | 0 | 225.9299 | 111.4 | 36.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 225.9299 | 0 | 1240.3476 | 97.32% | 0 | 0 | 50 | 100% | 38.6
8343 | 823 | 346 | 60 | 0 | 0 | 414.2302 | 0 | 214.932 | 0 | 94.9864 | 27.8432 | 0 | 67.1432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.3476 | 97.32% | 0 | 0 | 50 | 100% | 39.3
8344 | 565 | 177 | 48 | 0 | 0 | 284.3743 | 0 | 116.8785 | 0 | 38.3592 | 0 | 0 | 38.3592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.3476 | 97.32% | 0 | 3.6408 | 46.1806 | 92.36% | 42
8345 | 156 | 39 | 26 | 0 | 0 | 78.5175 | 0 | 0 | 0 | 4.6402 | 0 | 0 | 4.6402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.3476 | 97.32% | 0 | 25 | 19.9546 | 39.91% | 29.6402
8346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.1476 | 24.078 | 0 | 62.1476 | 1183.2471 | 92.84% | 0 | 19.022 | 0 | 0% | 43.1
8347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.7252 | 42.6 | 0 | 105.7252 | 1076.4522 | 84.46% | 0 | 0 | 0 | 0% | 42.6
8348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6408 | 40.9 | 0 | 101.6408 | 974.4859 | 76.46% | 0 | 0 | 0 | 0% | 40.9
8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9249 | 38.1 | 0 | 94.9249 | 880.548 | 69.09% | 0 | 0 | 0 | 0% | 38.1
8350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7077 | 35.1 | 0 | 87.7077 | 795.1011 | 62.38% | 0 | 0 | 0 | 0% | 35.1
8351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0192 | 32.3 | 0 | 81.0192 | 717.7138 | 56.31% | 0 | 0 | 0 | 0% | 32.3
8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.4535 | 30.4 | 0 | 76.4535 | 645.6551 | 50.66% | 0 | 0 | 0 | 0% | 30.4
8353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9425 | 29.3 | 0 | 73.9425 | 576.4176 | 45.23% | 0 | 0 | 0 | 0% | 29.3
8354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8321 | 28.8 | 0 | 72.8321 | 508.3966 | 39.89% | 0 | 0 | 0 | 0% | 28.8
8355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.6094 | 28.7 | 0 | 72.6094 | 440.6077 | 34.57% | 0 | 0 | 0 | 0% | 28.7
8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8274 | 29.7 | 0 | 74.8274 | 370.3428 | 29.06% | 0 | 0 | 0 | 0% | 29.7
8357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1384 | 31.1 | 0 | 78.1384 | 296.2527 | 23.24% | 0 | 0 | 0 | 0% | 31.1
8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296.2527 | 23.24% | 0 | 0 | 0 | 0% | 0
8359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296.2527 | 23.24% | 0 | 0 | 0 | 0% | 0
8360 | 71 | 27 | 22 | 0 | 0 | 35.7355 | 0 | 0 | 0 | 2.4155 | 0 | 0 | 2.4155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296.2527 | 23.24% | 0 | 0 | 0 | 0% | 2.4155
8361 | 381 | 145 | 64 | 0 | 0 | 191.7639 | 91.3927 | 0 | 68.3452 | 27.6739 | 0 | 0 | 27.6739 | 0 | 0 | 0 | 0 | 0 | 68.3452 | 0 | 360.5427 | 28.29% | 0 | 0 | 0 | 0% | 27.6739
8362 | 813 | 334 | 63 | 0 | 0 | 409.197 | 227.036 | 0 | 195.1782 | 91.8156 | 1.5078 | 25 | 65.3078 | 0 | 0 | 0 | 0 | 0 | 195.1782 | 0 | 544.141 | 42.69% | 19.175 | 0 | 20.1212 | 40.24% | 38.8
8363 | 892 | 439 | 57 | 0 | 0 | 448.9591 | 267.914 | 0 | 233.2527 | 110.7 | 10.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 233.2527 | 0 | 763.555 | 59.91% | 19.175 | 0 | 40.2425 | 80.48% | 39.3
8364 | 922 | 500 | 58 | 0 | 0 | 464.0586 | 283.0156 | 0 | 247.4649 | 110.8 | 23.6766 | 12.1234 | 75 | 0 | 0 | 0 | 0 | 0 | 247.4649 | 0 | 996.338 | 78.17% | 9.2986 | 0 | 50 | 100% | 39.2
8365 | 923 | 505 | 58 | 0 | 0 | 464.5619 | 281.1058 | 0 | 245.6613 | 112.3 | 37.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 245.6613 | 0 | 1227.4245 | 96.31% | 0 | 0 | 50 | 100% | 37.7
8366 | 886 | 447 | 59 | 0 | 0 | 445.9392 | 0 | 259.9994 | 0 | 113.2 | 38.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.4245 | 96.31% | 0 | 0 | 50 | 100% | 36.8
8367 | 627 | 294 | 69 | 0 | 0 | 315.58 | 0 | 163.4427 | 0 | 73.4959 | 18.048 | 0 | 55.448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.4245 | 96.31% | 0 | 0 | 50 | 100% | 37.4
8368 | 370 | 188 | 116 | 0 | 0 | 186.2274 | 0 | 76.2539 | 0 | 34.5912 | 0 | 0 | 34.5912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.4245 | 96.31% | 0 | 5.8088 | 43.9054 | 87.81% | 40.4
8369 | 136 | 50 | 35 | 0 | 0 | 68.4512 | 0 | 0 | 0 | 5.0551 | 0 | 0 | 5.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.4245 | 96.31% | 0 | 25 | 17.6754 | 35.35% | 30.0551
8370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.7846 | 26.5531 | 0 | 67.7846 | 1165.0506 | 91.41% | 0 | 16.8469 | 0 | 0% | 43.4
8371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.404 | 43.3 | 0 | 107.404 | 1056.5441 | 82.9% | 0 | 0 | 0 | 0% | 43.3
8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3239 | 41.6 | 0 | 103.3239 | 952.8737 | 74.76% | 0 | 0 | 0 | 0% | 41.6
8373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1648 | 38.2 | 0 | 95.1648 | 858.9021 | 67.39% | 0 | 0 | 0 | 0% | 38.2
8374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7524 | 34.7 | 0 | 86.7524 | 774.836 | 60.79% | 0 | 0 | 0 | 0% | 34.7
8375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0192 | 32.3 | 0 | 81.0192 | 697.6507 | 54.74% | 0 | 0 | 0 | 0% | 32.3
8376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.176 | 30.7 | 0 | 77.176 | 624.9446 | 49.03% | 0 | 0 | 0 | 0% | 30.7
8377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7304 | 30.1 | 0 | 75.7304 | 553.8895 | 43.46% | 0 | 0 | 0 | 0% | 30.1
8378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7304 | 30.1 | 0 | 75.7304 | 482.8208 | 37.88% | 0 | 0 | 0 | 0% | 30.1
8379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8595 | 31.4 | 0 | 78.8595 | 408.1163 | 32.02% | 0 | 0 | 0 | 0% | 31.4
8380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6364 | 35.9 | 0 | 89.6364 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 35.9
8381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8384 | 0 | 17 | 17 | 2.8208 | 4.5 | 0 | 0 | 0 | 0 | 0.56566 | 0 | 0 | 0.56566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0.56566
8385 | 148 | 127 | 91 | 2.0149 | 10.1 | 74.491 | 0 | 35.5333 | 0 | 17.1646 | 0 | 0 | 17.1646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 17.1646
8386 | 167 | 213 | 158 | 2.8208 | 11.8 | 84.054 | 0 | 46.646 | 0 | 28.6346 | 0 | 0 | 28.6346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 28.6346
8387 | 129 | 273 | 215 | 5.6416 | 12.9 | 64.9279 | 0 | 38.7417 | 0 | 33.4442 | 0 | 0 | 33.4442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 33.4442
8388 | 35 | 252 | 232 | 4.8357 | 14 | 17.6161 | 0 | 10.7401 | 0 | 25.6263 | 0 | 0 | 25.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 25.6263
8389 | 45 | 266 | 241 | 5.6416 | 14.3 | 22.6493 | 0 | 13.6977 | 0 | 27.5914 | 0 | 0 | 27.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 27.5914
8390 | 14 | 202 | 194 | 6.2461 | 14 | 7.0464 | 0 | 4.1027 | 0 | 18.0813 | 0 | 0 | 18.0813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 18.0813
8391 | 9 | 131 | 127 | 5.6416 | 13.6 | 4.5299 | 0 | 2.3419 | 0 | 11.1971 | 0 | 0 | 11.1971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 11.1971
8392 | 10 | 103 | 99 | 6.8506 | 12.9 | 5.0332 | 0 | 2.0535 | 0 | 9.3682 | 0 | 0 | 9.3682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 9.3682
8393 | 58 | 35 | 30 | 9.0669 | 11.4 | 29.1924 | 0 | 0 | 0 | 2.9985 | 0 | 0 | 2.9985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 2.9985
8394 | 0 | 0 | 0 | 10.0743 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8395 | 0 | 0 | 0 | 7.455 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8396 | 0 | 0 | 0 | 5.8431 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8397 | 0 | 0 | 0 | 5.4401 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8398 | 0 | 0 | 0 | 4.6342 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8399 | 0 | 0 | 0 | 2.8208 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8400 | 0 | 0 | 0 | 3.8283 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8401 | 0 | 0 | 0 | 2.2164 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8402 | 0 | 0 | 0 | 4.0297 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8403 | 0 | 0 | 0 | 2.6193 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8404 | 0 | 0 | 0 | 4.0297 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8405 | 0 | 0 | 0 | 4.0297 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8406 | 0 | 0 | 0 | 3.8283 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8407 | 0 | 0 | 0 | 6.4476 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0
8408 | 0 | 10 | 11 | 3.0223 | 8.8 | 0 | 0 | 0 | 0 | 0.20307 | 0 | 0 | 0.20307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 0.20307
8409 | 0 | 49 | 49 | 1.6119 | 9.1 | 0 | 0 | 0 | 0 | 3.447 | 0 | 0 | 3.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 3.447
8410 | 8 | 114 | 110 | 0.60446 | 10 | 4.0265 | 0 | 2.2353 | 0 | 9.5308 | 0 | 0 | 9.5308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320.5541 | 25.15% | 0 | 0 | 0 | 0% | 9.5308
8411 | 510 | 377 | 148 | 1.8134 | 12.6 | 256.6919 | 153.1587 | 0 | 125.3887 | 68.2041 | 0 | 9.852 | 58.352 | 0 | 0 | 0 | 0 | 0 | 125.3887 | 0 | 438.8959 | 34.44% | 7.5565 | 0 | 7.9309 | 15.86% | 48.5
8412 | 706 | 471 | 122 | 4.8357 | 13.6 | 355.3421 | 216.5871 | 0 | 183.5873 | 103.1 | 3.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 183.5873 | 0 | 612.1654 | 48.03% | 19.175 | 0 | 28.0561 | 56.11% | 46.9
8413 | 839 | 506 | 91 | 5.2387 | 14.2 | 422.2833 | 255.2624 | 0 | 219.4088 | 103.7 | 3.7 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 219.4088 | 0 | 819.2433 | 64.28% | 19.175 | 0 | 48.1812 | 96.36% | 46.3
8414 | 529 | 393 | 147 | 5.6416 | 14.9 | 266.2549 | 154.8291 | 0 | 125.3945 | 76.8644 | 15.4822 | 0 | 61.3822 | 0 | 0 | 0 | 0 | 0 | 125.3945 | 0 | 937.5905 | 73.56% | 0 | 0 | 48.1812 | 96.36% | 45.9
8415 | 1 | 105 | 104 | 3.8283 | 13.9 | 0.50332 | 0 | 0.25978 | 0 | 8.2239 | 0 | 0 | 8.2239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 937.5905 | 73.56% | 0 | 25 | 21.9466 | 43.89% | 33.2239
8416 | 3 | 83 | 82 | 3.2238 | 13.5 | 1.51 | 0 | 0.61392 | 0 | 6.893 | 0 | 0 | 6.893 | 0 | 0 | 0 | 54.9107 | 20.6932 | 0 | 54.9107 | 887.5038 | 69.63% | 0 | 20.9137 | 0 | 0% | 48.5
8417 | 1 | 21 | 21 | 2.2164 | 12.3 | 0.50332 | 0 | 0 | 0 | 0.7971 | 0 | 0 | 0.7971 | 0 | 0 | 0 | 120.1553 | 48.4029 | 0 | 120.1553 | 763.9424 | 59.94% | 0 | 0 | 0 | 0% | 49.2
8418 | 0 | 0 | 0 | 1.8134 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.8591 | 50 | 0 | 123.8591 | 635.6609 | 49.87% | 0 | 0 | 0 | 0% | 50
8419 | 0 | 0 | 0 | 2.8208 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.3348 | 49 | 0 | 121.3348 | 510.3423 | 40.04% | 0 | 0 | 0 | 0% | 49
8420 | 0 | 0 | 0 | 1.6119 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8983 | 45.5 | 0 | 112.8983 | 395.1458 | 31% | 0 | 0 | 0 | 0% | 45.5
8421 | 0 | 0 | 0 | 1.8134 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5086 | 40.8 | 0 | 101.5086 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 40.8
8422 | 0 | 0 | 0 | 2.8208 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8423 | 0 | 0 | 0 | 1.8134 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8424 | 0 | 0 | 0 | 1.6119 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8425 | 0 | 0 | 0 | 2.0149 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8426 | 0 | 0 | 0 | 2.8208 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8427 | 0 | 0 | 0 | 2.6193 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8428 | 0 | 0 | 0 | 5.6416 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8429 | 0 | 0 | 0 | 5.2387 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8430 | 0 | 0 | 0 | 3.6268 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8431 | 0 | 0 | 0 | 6.0446 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 0
8432 | 81 | 31 | 24 | 6.4476 | 6 | 40.7687 | 0 | 0 | 0 | 2.6287 | 0 | 0 | 2.6287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.4184 | 23.02% | 0 | 0 | 0 | 0% | 2.6287
8433 | 425 | 138 | 55 | 2.8208 | 7.9 | 213.9099 | 102.271 | 0 | 77.2005 | 28.182 | 0 | 0 | 28.182 | 0 | 0 | 0 | 0 | 0 | 77.2005 | 0 | 368.0918 | 28.88% | 0 | 0 | 0 | 0% | 28.182
8434 | 856 | 335 | 48 | 3.6268 | 10.4 | 430.8397 | 239.2733 | 0 | 205.2146 | 83.0127 | 0 | 17.3063 | 65.7063 | 0 | 0 | 0 | 0 | 0 | 205.2146 | 0 | 566.5887 | 44.46% | 13.274 | 0 | 13.9337 | 27.87% | 48.4
8435 | 929 | 456 | 52 | 2.4178 | 13.4 | 467.5819 | 278.9927 | 0 | 242.7483 | 101.8 | 1.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 242.7483 | 0 | 801.3906 | 62.88% | 19.175 | 0 | 34.0617 | 68.12% | 48.2
8436 | 957 | 522 | 56 | 1.8134 | 14.5 | 481.6747 | 293.5283 | 0 | 256.7242 | 103 | 8.2038 | 19.7962 | 75 | 0 | 0 | 0 | 0 | 0 | 256.7242 | 0 | 1049.711 | 82.36% | 15.1837 | 0 | 50 | 100% | 47
8437 | 952 | 534 | 65 | 2.6193 | 15.3 | 479.1582 | 289.5177 | 0 | 252.6447 | 103.6 | 28.6 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 252.6447 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.4
8438 | 923 | 467 | 54 | 4.2312 | 16.2 | 464.5619 | 0 | 269.8311 | 0 | 103.8 | 28.8 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 46.2
8439 | 819 | 348 | 54 | 5.6416 | 16.5 | 412.2169 | 0 | 212.4253 | 0 | 83.8562 | 18.4281 | 0 | 65.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 47
8440 | 395 | 156 | 67 | 5.2387 | 14.8 | 198.8104 | 0 | 80.565 | 0 | 30.274 | 0 | 0 | 30.274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 18.826 | 30.2414 | 60.48% | 49.1
8441 | 170 | 45 | 29 | 6.0446 | 12.9 | 85.564 | 0 | 0 | 0 | 4.9698 | 0 | 0 | 4.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 4.0018 | 8.004% | 29.9698
8442 | 0 | 0 | 0 | 3.8283 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1476 | 45.9861 | 0 | 114.1476 | 1158.2667 | 90.88% | 0 | 3.8139 | 0 | 0% | 49.8
8443 | 0 | 0 | 0 | 2.4178 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.1687 | 48.1 | 0 | 119.1687 | 1035.9147 | 81.28% | 0 | 0 | 0 | 0% | 48.1
8444 | 0 | 0 | 0 | 3.0223 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.932 | 45.1 | 0 | 111.932 | 922.1838 | 72.36% | 0 | 0 | 0 | 0% | 45.1
8445 | 0 | 0 | 0 | 2.6193 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2596 | 40.7 | 0 | 101.2596 | 821.0296 | 64.42% | 0 | 0 | 0 | 0% | 40.7
8446 | 0 | 0 | 0 | 3.2238 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0698 | 37.7 | 0 | 94.0698 | 728.4487 | 57.16% | 0 | 0 | 0 | 0% | 37.7
8447 | 0 | 0 | 0 | 3.2238 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5522 | 35 | 0 | 87.5522 | 643.4504 | 50.49% | 0 | 0 | 0 | 0% | 35
8448 | 0 | 0 | 0 | 2.4178 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7418 | 33.4 | 0 | 83.7418 | 563.0836 | 44.18% | 0 | 0 | 0 | 0% | 33.4
8449 | 0 | 0 | 0 | 2.8208 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5787 | 32.5 | 0 | 81.5787 | 485.2776 | 38.08% | 0 | 0 | 0 | 0% | 32.5
8450 | 0 | 0 | 0 | 2.0149 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.099 | 32.3 | 0 | 81.099 | 408.0242 | 32.01% | 0 | 0 | 0 | 0% | 32.3
8451 | 0 | 0 | 0 | 2.6193 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9805 | 33.5 | 0 | 83.9805 | 327.3182 | 25.68% | 0 | 0 | 0 | 0% | 33.5
8452 | 0 | 0 | 0 | 1.4104 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.3182 | 25.68% | 0 | 0 | 0 | 0% | 0
8453 | 0 | 0 | 0 | 1.0074 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.3182 | 25.68% | 0 | 0 | 0 | 0% | 0
8454 | 0 | 0 | 0 | 1.6119 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.3182 | 25.68% | 0 | 0 | 0 | 0% | 0
8455 | 0 | 0 | 0 | 1.2089 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.3182 | 25.68% | 0 | 0 | 0 | 0% | 0
8456 | 2 | 15 | 15 | 2.8208 | 6.9 | 1.0066 | 0 | 0 | 0 | 0.44383 | 0 | 0 | 0.44383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.3182 | 25.68% | 0 | 0 | 0 | 0% | 0.44383
8457 | 81 | 111 | 91 | 2.6193 | 8.7 | 40.7687 | 0 | 19.5171 | 0 | 13.9773 | 0 | 0 | 13.9773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.3182 | 25.68% | 0 | 0 | 0 | 0% | 13.9773
8458 | 686 | 344 | 110 | 4.0297 | 12.4 | 345.2757 | 191.8553 | 0 | 160.7266 | 73.55 | 0 | 12.375 | 61.175 | 0 | 0 | 0 | 0 | 0 | 160.7266 | 0 | 481.9974 | 37.82% | 9.4916 | 0 | 9.9648 | 19.93% | 48.8
8459 | 567 | 419 | 174 | 6.0446 | 14.5 | 285.381 | 170.2899 | 0 | 139.6202 | 83.5154 | 0 | 17.2077 | 66.3077 | 0 | 0 | 0 | 0 | 0 | 139.6202 | 0 | 616.3643 | 48.36% | 13.1983 | 0 | 23.8211 | 47.64% | 49.1
8460 | 64 | 208 | 175 | 7.858 | 14.4 | 32.2123 | 0 | 19.6269 | 0 | 21.6842 | 0 | 0 | 21.6842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616.3643 | 48.36% | 0 | 22.6935 | 0 | 0% | 44.3777
8461 | 1 | 156 | 155 | 7.858 | 14.6 | 0.50332 | 0 | 0.304 | 0 | 12.5991 | 0 | 0 | 12.5991 | 0 | 0 | 0 | 86.4242 | 34.3009 | 0 | 86.4242 | 533.3936 | 41.85% | 0 | 0 | 0 | 0% | 46.9
8462 | 6 | 168 | 163 | 8.6639 | 15 | 3.0199 | 0 | 1.7522 | 0 | 14.0812 | 0 | 0 | 14.0812 | 0 | 0 | 0 | 82.4705 | 32.6188 | 0 | 82.4705 | 455.2502 | 35.72% | 0 | 0 | 0 | 0% | 46.7
8463 | 533 | 293 | 100 | 10.6788 | 16.4 | 268.2682 | 138.04 | 0 | 106.6083 | 56.8382 | 0 | 4.7691 | 52.0691 | 0 | 0 | 0 | 0 | 0 | 106.6083 | 0 | 557.3969 | 43.73% | 3.6579 | 0 | 3.8405 | 7.681% | 47.3
8464 | 113 | 126 | 98 | 15.313 | 16 | 56.8749 | 0 | 22.9748 | 0 | 16.6466 | 0 | 0 | 16.6466 | 0 | 0 | 0 | 72.9936 | 28.4949 | 0 | 72.9936 | 490.0001 | 38.45% | 0 | 3.6585 | 0 | 0% | 48.8
8465 | 9 | 29 | 28 | 12.2907 | 15.6 | 4.5299 | 0 | 0 | 0 | 1.7715 | 0 | 0 | 1.7715 | 0 | 0 | 0 | 117.5951 | 47.2285 | 0 | 117.5951 | 370.0493 | 29.03% | 0 | 0 | 0 | 0% | 49
8466 | 0 | 0 | 0 | 6.8506 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.1446 | 25.0636 | 0 | 65.1446 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 25.0636
8467 | 0 | 0 | 0 | 4.8357 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8468 | 0 | 0 | 0 | 7.2535 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8469 | 0 | 0 | 0 | 10.6788 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8470 | 0 | 0 | 0 | 10.8803 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8471 | 0 | 0 | 0 | 11.8877 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8472 | 0 | 0 | 0 | 12.6937 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8473 | 0 | 0 | 0 | 16.5219 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8474 | 0 | 0 | 0 | 19.5442 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8475 | 0 | 0 | 0 | 17.5294 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8476 | 0 | 0 | 0 | 11.4848 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8477 | 0 | 0 | 0 | 11.8877 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8478 | 0 | 0 | 0 | 14.91 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8479 | 0 | 0 | 0 | 18.3353 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8480 | 0 | 7 | 8 | 18.3353 | 16 | 0 | 0 | 0 | 0 | 0.029309 | 0 | 0 | 0.029309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0.029309
8481 | 2 | 65 | 64 | 12.6937 | 16.4 | 1.0066 | 0 | 0.48261 | 0 | 5.0366 | 0 | 0 | 5.0366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 5.0366
8482 | 57 | 165 | 142 | 11.8877 | 17.1 | 28.6891 | 0 | 15.9514 | 0 | 17.5551 | 0 | 0 | 17.5551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 17.5551
8483 | 15 | 176 | 168 | 15.313 | 17.5 | 7.5498 | 0 | 4.5056 | 0 | 15.3882 | 0 | 0 | 15.3882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 15.3882
8484 | 90 | 263 | 216 | 15.9175 | 18 | 45.2986 | 0 | 27.5977 | 0 | 28.5993 | 0 | 0 | 28.5993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 28.5993
8485 | 50 | 221 | 194 | 16.7234 | 18.6 | 25.1659 | 0 | 15.1952 | 0 | 22.3706 | 0 | 0 | 22.3706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 22.3706
8486 | 141 | 281 | 214 | 15.1115 | 18.9 | 70.9678 | 0 | 41.1365 | 0 | 34.1256 | 0 | 0 | 34.1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 34.1256
8487 | 3 | 163 | 161 | 14.7085 | 18.2 | 1.51 | 0 | 0.77588 | 0 | 14.3435 | 0 | 0 | 14.3435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 14.3435
8488 | 7 | 109 | 107 | 13.4996 | 18.3 | 3.5232 | 0 | 1.4189 | 0 | 10.008 | 0 | 0 | 10.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 10.008
8489 | 1 | 35 | 34 | 13.9026 | 18 | 0.50332 | 0 | 0 | 0 | 2.1379 | 0 | 0 | 2.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 2.1379
8490 | 0 | 0 | 0 | 15.9175 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8491 | 0 | 0 | 0 | 13.2981 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8492 | 0 | 0 | 0 | 13.7011 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8493 | 0 | 0 | 0 | 13.9026 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8494 | 0 | 0 | 0 | 13.4996 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8495 | 0 | 0 | 0 | 15.9175 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8496 | 0 | 0 | 0 | 16.5219 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8497 | 0 | 0 | 0 | 15.716 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8498 | 0 | 0 | 0 | 14.7085 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8499 | 0 | 0 | 0 | 15.5145 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8500 | 0 | 0 | 0 | 15.9175 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8501 | 0 | 0 | 0 | 11.0818 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8502 | 0 | 0 | 0 | 9.6714 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8503 | 0 | 0 | 0 | 11.8877 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0
8504 | 0 | 9 | 9 | 8.261 | 17.8 | 0 | 0 | 0 | 0 | 0.07748 | 0 | 0 | 0.07748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 0.07748
8505 | 13 | 67 | 64 | 9.2684 | 17.5 | 6.5431 | 0 | 3.1421 | 0 | 5.5233 | 0 | 0 | 5.5233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 5.5233
8506 | 52 | 146 | 125 | 10.2758 | 17.5 | 26.1725 | 0 | 14.5628 | 0 | 15.0758 | 0 | 0 | 15.0758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 15.0758
8507 | 148 | 281 | 214 | 10.2758 | 18.3 | 74.491 | 0 | 44.4626 | 0 | 34.5335 | 0 | 0 | 34.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 34.5335
8508 | 49 | 272 | 244 | 18.1338 | 19.8 | 24.6626 | 0 | 15.0248 | 0 | 28.2 | 0 | 0 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.1599 | 24.34% | 0 | 0 | 0 | 0% | 28.2
8509 | 603 | 534 | 233 | 13.9026 | 21.1 | 303.5004 | 183.2045 | 0 | 147.0915 | 112.1 | 12.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 147.0915 | 0 | 450.8474 | 35.37% | 19.175 | 0 | 20.134 | 40.27% | 37.9
8510 | 730 | 496 | 166 | 15.5145 | 21.8 | 367.4217 | 212.7921 | 0 | 173.8276 | 112.9 | 12.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 173.8276 | 0 | 617.1071 | 48.42% | 19.175 | 0 | 40.268 | 80.54% | 37.1
8511 | 504 | 329 | 139 | 18.5368 | 21.3 | 253.672 | 130.1796 | 0 | 94.7851 | 69.2422 | 3.837 | 12.0841 | 53.3211 | 0 | 0 | 0 | 0 | 0 | 94.7851 | 0 | 707.7655 | 55.53% | 9.2685 | 0 | 50 | 100% | 37.4
8512 | 155 | 138 | 105 | 14.3056 | 19.9 | 78.0142 | 0 | 31.3296 | 0 | 19.7308 | 0 | 0 | 19.7308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707.7655 | 55.53% | 0 | 19.6692 | 29.3504 | 58.7% | 39.4
8513 | 215 | 55 | 32 | 11.0818 | 19.1 | 108.2132 | 0 | 0 | 0 | 6.2864 | 0 | 0 | 6.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707.7655 | 55.53% | 0 | 25 | 3.103 | 6.206% | 31.2864
8514 | 0 | 0 | 0 | 12.0892 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6845 | 37.5433 | 0 | 94.6845 | 615.1835 | 48.27% | 0 | 2.9567 | 0 | 0% | 40.5
8515 | 0 | 0 | 0 | 25.9918 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1736 | 40.1 | 0 | 101.1736 | 515.2024 | 40.42% | 0 | 0 | 0 | 0% | 40.1
8516 | 0 | 0 | 0 | 29.2156 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6151 | 38.2 | 0 | 96.6151 | 420.7014 | 33.01% | 0 | 0 | 0 | 0% | 38.2
8517 | 0 | 0 | 0 | 28.0067 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0069 | 35.5 | 0 | 90.0069 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 35.5
8518 | 0 | 0 | 0 | 30.223 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8519 | 0 | 0 | 0 | 30.8275 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8520 | 0 | 0 | 0 | 32.0364 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8521 | 0 | 0 | 0 | 29.6186 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8522 | 0 | 0 | 0 | 22.1636 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8523 | 0 | 0 | 0 | 15.716 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8524 | 0 | 0 | 0 | 10.8803 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8525 | 0 | 0 | 0 | 15.1115 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8526 | 0 | 0 | 0 | 25.7903 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8527 | 0 | 0 | 0 | 20.7532 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 0
8528 | 166 | 23 | 10 | 18.9398 | 16.7 | 83.5507 | 0 | 0 | 0 | 2.2027 | 0 | 0 | 2.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8586 | 26.2% | 0 | 0 | 0 | 0% | 2.2027
8529 | 673 | 166 | 33 | 18.5368 | 17.5 | 338.7326 | 162.9553 | 0 | 125.2988 | 35.4714 | 0 | 0 | 35.4714 | 0 | 0 | 0 | 0 | 0 | 125.2988 | 0 | 453.8634 | 35.61% | 0 | 0 | 0 | 0% | 35.4714
8530 | 840 | 323 | 45 | 18.5368 | 18.2 | 422.7866 | 235.4425 | 0 | 193.1855 | 92.1604 | 2.6802 | 25 | 64.4802 | 0 | 0 | 0 | 0 | 0 | 193.1855 | 0 | 638.8866 | 50.13% | 19.175 | 0 | 20.1368 | 40.27% | 36.8
8531 | 910 | 443 | 50 | 17.5294 | 19.4 | 458.0188 | 273.4473 | 0 | 229.0475 | 112.8 | 12.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 229.0475 | 0 | 858.2567 | 67.34% | 19.175 | 0 | 40.2737 | 80.55% | 37.2
8532 | 936 | 510 | 53 | 18.1338 | 20.2 | 471.1051 | 287.0096 | 0 | 241.5762 | 113.4 | 26.3248 | 12.0752 | 75 | 0 | 0 | 0 | 0 | 0 | 241.5762 | 0 | 1089.626 | 85.49% | 9.2617 | 0 | 50 | 100% | 36.6
8533 | 945 | 520 | 52 | 19.7457 | 20.8 | 475.6349 | 287.0505 | 0 | 240.7202 | 115.2 | 40.2 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 240.7202 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.8
8534 | 928 | 469 | 49 | 24.9844 | 21.1 | 467.0785 | 0 | 270.3025 | 0 | 116.3 | 41.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.7
8535 | 867 | 359 | 45 | 22.5665 | 21.6 | 436.3762 | 0 | 223.6721 | 0 | 103.6863 | 34.7931 | 0 | 68.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.1
8536 | 727 | 207 | 36 | 20.9546 | 21.1 | 365.9117 | 0 | 146.5501 | 0 | 53.487 | 8.3435 | 0 | 45.1435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.8
8537 | 313 | 49 | 16 | 20.1487 | 19.5 | 157.5383 | 0 | 0 | 0 | 5.8045 | 0 | 0 | 5.8045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.7499 | 47.5% | 30.8045
8538 | 0 | 0 | 0 | 20.9546 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.6189 | 2.7756e-15 | 5.551e-15% | 22.6189
8539 | 0 | 0 | 0 | 22.365 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6397 | 39.2 | 0 | 98.6397 | 1177.5811 | 92.39% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 39.2
8540 | 0 | 0 | 0 | 22.768 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5249 | 37.5 | 0 | 94.5249 | 1085.5103 | 85.17% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.5
8541 | 0 | 0 | 0 | 22.5665 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4649 | 34.6 | 0 | 87.4649 | 1001.6356 | 78.59% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.6
8542 | 0 | 0 | 0 | 23.9769 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2 | 31.6 | 0 | 80.2 | 926.3553 | 72.68% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.6
8543 | 0 | 0 | 0 | 20.3502 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8202 | 29.3 | 0 | 74.8202 | 857.1298 | 67.25% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 29.3
8544 | 0 | 0 | 0 | 19.7457 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.718 | 27.9 | 0 | 71.718 | 790.8948 | 62.05% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27.9
8545 | 0 | 0 | 0 | 16.9249 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.6792 | 27 | 0 | 69.6792 | 726.614 | 57.01% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27
8546 | 0 | 0 | 0 | 16.7234 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.2169 | 26.8 | 0 | 69.2169 | 662.7675 | 52% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 26.8
8547 | 0 | 0 | 0 | 7.052 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.688 | 28 | 0 | 71.688 | 596.52 | 46.8% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 28
8548 | 0 | 0 | 0 | 4.6342 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0359 | 30.9 | 0 | 78.0359 | 523.1365 | 41.05% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.9
8549 | 0 | 0 | 0 | 4.8357 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.087 | 35.1 | 0 | 88.087 | 437.703 | 34.34% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.1
8550 | 0 | 0 | 0 | 5.0372 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0256 | 38.4 | 0 | 96.0256 | 342.9048 | 26.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38.4
8551 | 0 | 0 | 0 | 3.4253 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342.9048 | 26.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
8552 | 183 | 25 | 11 | 3.6268 | 12.4 | 92.1071 | 0 | 0 | 0 | 2.4114 | 0 | 0 | 2.4114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342.9048 | 26.9% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 2.4114
8553 | 695 | 180 | 44 | 2.8208 | 16.4 | 349.8056 | 168.6113 | 0 | 139.4796 | 37.0413 | 0 | 0 | 37.0413 | 0 | 0 | 0 | 0 | 0 | 139.4796 | 0 | 473.8661 | 37.18% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.0413
8554 | 839 | 331 | 52 | 2.2164 | 20.4 | 422.2833 | 235.3827 | 0 | 202.2201 | 82.5437 | 0 | 20.7718 | 61.7718 | 0 | 0 | 0 | 0 | 0 | 202.2201 | 0 | 663.7363 | 52.08% | 15.932 | 0 | 16.7336 | 33.47% | 41
8555 | 901 | 467 | 76 | 6.2461 | 21.1 | 453.489 | 270.8189 | 0 | 233.442 | 108.9 | 8.9 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 233.442 | 0 | 882.9215 | 69.28% | 19.175 | 0 | 36.8735 | 73.75% | 41.1
8556 | 930 | 513 | 57 | 4.4327 | 21.7 | 468.0852 | 285.1902 | 0 | 247.9623 | 109.8 | 18.5059 | 16.2941 | 75 | 0 | 0 | 0 | 0 | 0 | 247.9623 | 0 | 1115.7402 | 87.54% | 12.4976 | 0 | 50 | 100% | 40.2
8557 | 866 | 500 | 68 | 6.4476 | 20.9 | 435.8729 | 263.0121 | 0 | 225.9999 | 111 | 36 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 225.9999 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39
8558 | 847 | 450 | 64 | 7.052 | 21.1 | 426.3098 | 0 | 246.5471 | 0 | 111.4 | 36.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.6
8559 | 772 | 339 | 57 | 7.858 | 20.9 | 388.561 | 0 | 198.9452 | 0 | 87.1674 | 24.0837 | 0 | 63.0837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 39
8560 | 666 | 202 | 44 | 7.2535 | 20.3 | 335.2094 | 0 | 133.9139 | 0 | 44.6229 | 1.7614 | 0 | 42.8614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 41.1
8561 | 286 | 49 | 19 | 4.6342 | 18 | 143.9488 | 0 | 0 | 0 | 6.1899 | 0 | 0 | 6.1899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.746 | 47.49% | 31.1899
8562 | 0 | 0 | 0 | 4.2312 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.6119 | 0 | 0% | 22.6119
8563 | 0 | 0 | 0 | 1.0074 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0043 | 41.3 | 0 | 103.0043 | 1171.7667 | 91.94% | 0 | 0 | 0 | 0% | 41.3
8564 | 0 | 0 | 0 | 2.0149 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4053 | 39 | 0 | 97.4053 | 1075.5606 | 84.39% | 0 | 0 | 0 | 0% | 39
8565 | 0 | 0 | 0 | 2.0149 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1746 | 35.6 | 0 | 89.1746 | 988.9807 | 77.6% | 0 | 0 | 0 | 0% | 35.6
8566 | 0 | 0 | 0 | 1.4104 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4271 | 32.4 | 0 | 81.4271 | 911.5584 | 71.52% | 0 | 0 | 0 | 0% | 32.4
8567 | 0 | 0 | 0 | 2.4178 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5808 | 29.5 | 0 | 74.5808 | 842.0745 | 66.07% | 0 | 0 | 0 | 0% | 29.5
8568 | 0 | 0 | 0 | 2.6193 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.3924 | 27.6 | 0 | 70.3924 | 777.1923 | 60.98% | 0 | 0 | 0 | 0% | 27.6
8569 | 0 | 0 | 0 | 3.0223 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1061 | 26.6 | 0 | 68.1061 | 714.4952 | 56.06% | 0 | 0 | 0 | 0% | 26.6
8570 | 0 | 0 | 0 | 1.8134 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.4402 | 26.3 | 0 | 67.4402 | 652.4272 | 51.19% | 0 | 0 | 0 | 0% | 26.3
8571 | 0 | 0 | 0 | 2.4178 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.5787 | 26.8 | 0 | 68.5787 | 589.2568 | 46.23% | 0 | 0 | 0 | 0% | 26.8
8572 | 0 | 0 | 0 | 5.4401 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.1849 | 28.8 | 0 | 73.1849 | 521.4335 | 40.91% | 0 | 0 | 0 | 0% | 28.8
8573 | 0 | 0 | 0 | 3.0223 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4822 | 32 | 0 | 80.4822 | 445.0566 | 34.92% | 0 | 0 | 0 | 0% | 32
8574 | 0 | 0 | 0 | 3.6268 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9999 | 34.7 | 0 | 86.9999 | 360.8972 | 28.32% | 0 | 0 | 0 | 0% | 34.7
8575 | 0 | 0 | 0 | 3.6268 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360.8972 | 28.32% | 0 | 0 | 0 | 0% | 0
8576 | 128 | 22 | 12 | 5.0372 | 11.7 | 64.4246 | 0 | 0 | 0 | 2.2184 | 0 | 0 | 2.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360.8972 | 28.32% | 0 | 0 | 0 | 0% | 2.2184
8577 | 538 | 148 | 37 | 3.4253 | 12.9 | 270.7848 | 130.7982 | 0 | 103.7948 | 29.695 | 0 | 0 | 29.695 | 0 | 0 | 0 | 0 | 0 | 103.7948 | 0 | 458.1052 | 35.94% | 0 | 0 | 0 | 0% | 29.695
8578 | 747 | 304 | 53 | 2.8208 | 16.2 | 375.9781 | 209.7895 | 0 | 178.0288 | 77.5694 | 0 | 19.8847 | 57.6847 | 0 | 0 | 0 | 0 | 0 | 178.0288 | 0 | 624.8362 | 49.03% | 15.2516 | 0 | 16.0214 | 32.04% | 37.8
8579 | 763 | 398 | 70 | 3.8283 | 18.4 | 384.0312 | 229.416 | 0 | 196.0347 | 100.6546 | 6.6273 | 25 | 69.0273 | 0 | 0 | 0 | 0 | 0 | 196.0347 | 0 | 808.4305 | 63.43% | 19.175 | 0 | 36.1642 | 72.33% | 37.4
8580 | 917 | 523 | 72 | 4.6342 | 20.1 | 461.542 | 281.2396 | 0 | 244.1346 | 113.9 | 21.7279 | 17.1721 | 75 | 0 | 0 | 0 | 0 | 0 | 244.1346 | 0 | 1037.0722 | 81.37% | 13.171 | 0 | 50 | 100% | 36.1
8581 | 947 | 534 | 63 | 3.8283 | 21 | 476.6416 | 287.5828 | 0 | 250.4298 | 115.3 | 40.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 250.4298 | 0 | 1271.6097 | 99.77% | 0 | 0 | 50 | 100% | 34.7
8582 | 860 | 454 | 61 | 4.6342 | 21.4 | 432.853 | 0 | 250.1925 | 0 | 116 | 41 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.6097 | 99.77% | 0 | 0 | 50 | 100% | 34
8583 | 785 | 357 | 70 | 4.8357 | 21.5 | 395.1041 | 0 | 202.0936 | 0 | 94.4562 | 29.9281 | 0 | 64.5281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.6097 | 99.77% | 0 | 0 | 50 | 100% | 34.6
8584 | 256 | 120 | 55 | 4.4327 | 19.8 | 128.8493 | 0 | 51.3527 | 0 | 21.2438 | 0 | 0 | 21.2438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.6097 | 99.77% | 0 | 16.5562 | 32.6108 | 65.22% | 37.8
8585 | 192 | 39 | 20 | 3.2238 | 17.5 | 96.6369 | 0 | 0 | 0 | 5.2473 | 0 | 0 | 5.2473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.6097 | 99.77% | 0 | 25 | 6.352 | 12.7% | 30.2473
8586 | 0 | 0 | 0 | 4.2312 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.693 | 30.6515 | 0 | 77.693 | 1199.1629 | 94.09% | 0 | 6.0485 | 0 | 0% | 36.7
8587 | 0 | 0 | 0 | 1.8134 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3785 | 34.4 | 0 | 86.3785 | 1116.0549 | 87.57% | 0 | 0 | 0 | 0% | 34.4
8588 | 0 | 0 | 0 | 2.4178 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8985 | 31.3 | 0 | 78.8985 | 1041.7802 | 81.74% | 0 | 0 | 0 | 0% | 31.3
8589 | 0 | 0 | 0 | 5.0372 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.9089 | 30 | 0 | 75.9089 | 971.1114 | 76.19% | 0 | 0 | 0 | 0% | 30
8590 | 0 | 0 | 0 | 3.4253 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.011 | 29.2 | 0 | 74.011 | 902.3947 | 70.8% | 0 | 0 | 0 | 0% | 29.2
8591 | 0 | 0 | 0 | 5.8431 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.911 | 27.8 | 0 | 70.911 | 837.0466 | 65.68% | 0 | 0 | 0 | 0% | 27.8
8592 | 0 | 0 | 0 | 4.4327 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.0633 | 26.1 | 0 | 67.0633 | 775.3816 | 60.84% | 0 | 0 | 0 | 0% | 26.1
8593 | 0 | 0 | 0 | 5.8431 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.008 | 24.7 | 0 | 64.008 | 716.6435 | 56.23% | 0 | 0 | 0 | 0% | 24.7
8594 | 0 | 0 | 0 | 4.6342 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.2953 | 24 | 0 | 62.2953 | 659.5513 | 51.75% | 0 | 0 | 0 | 0% | 24
8595 | 0 | 0 | 0 | 5.6416 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.236 | 23.9 | 0 | 62.236 | 602.5159 | 47.27% | 0 | 0 | 0 | 0% | 23.9
8596 | 0 | 0 | 0 | 4.4327 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.141 | 24.4 | 0 | 63.141 | 544.5808 | 42.73% | 0 | 0 | 0 | 0% | 24.4
8597 | 0 | 0 | 0 | 4.6342 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.7549 | 25.1 | 0 | 64.7549 | 485.0712 | 38.06% | 0 | 0 | 0 | 0% | 25.1
8598 | 0 | 0 | 0 | 3.6268 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.4613 | 25.4 | 0 | 65.4613 | 424.8752 | 33.34% | 0 | 0 | 0 | 0% | 25.4
8599 | 0 | 0 | 0 | 4.2312 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.5235 | 24.9903 | 0 | 64.5235 | 365.5625 | 28.68% | 0 | 0 | 0 | 0% | 24.9903
8600 | 118 | 19 | 9 | 4.2312 | 10.6 | 59.3915 | 0 | 0 | 0 | 1.7923 | 0 | 0 | 1.7923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365.5625 | 28.68% | 0 | 0 | 0 | 0% | 1.7923
8601 | 613 | 154 | 33 | 2.0149 | 12.6 | 308.5336 | 149.3706 | 0 | 121.8257 | 32.9969 | 0.69846 | 0 | 32.2985 | 0 | 0 | 0 | 0 | 0 | 121.8257 | 0 | 477.7792 | 37.49% | 0 | 0 | 0 | 0% | 31.6
8602 | 851 | 330 | 48 | 3.0223 | 15.8 | 428.3231 | 239.2691 | 0 | 205.4842 | 94.5818 | 6.2909 | 25 | 63.2909 | 0 | 0 | 0 | 0 | 0 | 205.4842 | 0 | 667.0559 | 52.34% | 19.175 | 0 | 20.1458 | 40.29% | 32
8603 | 921 | 453 | 54 | 3.6268 | 18.5 | 463.5553 | 277.0301 | 0 | 240.4989 | 118.2 | 18.2 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 240.4989 | 0 | 888.5856 | 69.72% | 19.175 | 0 | 40.2916 | 80.58% | 31.8
8604 | 943 | 536 | 73 | 4.0297 | 20.6 | 474.6283 | 289.2666 | 0 | 251.9532 | 119.2 | 32.1524 | 12.0476 | 75 | 0 | 0 | 0 | 0 | 0 | 251.9532 | 0 | 1120.666 | 87.93% | 9.2405 | 0 | 50 | 100% | 30.8
8605 | 918 | 561 | 103 | 4.8357 | 21.3 | 462.0454 | 278.7627 | 0 | 241.7418 | 121.4 | 46.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 241.7418 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 28.6
8606 | 781 | 437 | 78 | 4.8357 | 21.7 | 393.0909 | 0 | 227.1077 | 0 | 117.2898 | 44.6449 | 0 | 72.6449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 28
8607 | 633 | 337 | 105 | 4.4327 | 21.6 | 318.5999 | 0 | 162.8159 | 0 | 87.281 | 29.2905 | 0 | 57.9905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 28.7
8608 | 480 | 203 | 81 | 3.8283 | 21 | 241.5923 | 0 | 96.0751 | 0 | 41.2982 | 4.7491 | 0 | 36.5491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 31.8
8609 | 253 | 61 | 35 | 4.4327 | 17.4 | 127.3393 | 0 | 0 | 0 | 7.6988 | 0 | 0 | 7.6988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.7382 | 47.48% | 32.6988
8610 | 0 | 0 | 0 | 1.2089 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.5978 | 0 | 0% | 22.5978
8611 | 0 | 0 | 0 | 4.4327 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4743 | 34.8 | 0 | 87.4743 | 1190.2559 | 93.39% | 0 | 0 | 0 | 0% | 34.8
8612 | 0 | 0 | 0 | 4.0297 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2322 | 33.9 | 0 | 85.2322 | 1108.6033 | 86.98% | 0 | 0 | 0 | 0% | 33.9
8613 | 0 | 0 | 0 | 5.0372 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8263 | 31.2 | 0 | 78.8263 | 1034.6151 | 81.18% | 0 | 0 | 0 | 0% | 31.2
8614 | 0 | 0 | 0 | 2.2164 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2601 | 28.4 | 0 | 72.2601 | 967.8703 | 75.94% | 0 | 0 | 0 | 0% | 28.4
8615 | 0 | 0 | 0 | 1.6119 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.2216 | 26.2 | 0 | 67.2216 | 906.0739 | 71.09% | 0 | 0 | 0 | 0% | 26.2
8616 | 0 | 0 | 0 | 1.6119 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.2733 | 24.9 | 0 | 64.2733 | 847.0904 | 66.46% | 0 | 0 | 0 | 0% | 24.9
8617 | 0 | 0 | 0 | 1.6119 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6282 | 24.2 | 0 | 62.6282 | 789.6918 | 61.96% | 0 | 0 | 0 | 0% | 24.2
8618 | 0 | 0 | 0 | 2.4178 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.9865 | 23.9 | 0 | 61.9865 | 732.9082 | 57.51% | 0 | 0 | 0 | 0% | 23.9
8619 | 0 | 0 | 0 | 4.2312 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.8911 | 24.7 | 0 | 63.8911 | 674.2735 | 52.9% | 0 | 0 | 0 | 0% | 24.7
8620 | 0 | 0 | 0 | 3.4253 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.5364 | 27.2 | 0 | 69.5364 | 610.2118 | 47.88% | 0 | 0 | 0 | 0% | 27.2
8621 | 0 | 0 | 0 | 4.8357 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8265 | 30.8 | 0 | 77.8265 | 537.2527 | 42.15% | 0 | 0 | 0 | 0% | 30.8
8622 | 0 | 0 | 0 | 6.0446 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5629 | 34 | 0 | 85.5629 | 455.1843 | 35.71% | 0 | 0 | 0 | 0% | 34
8623 | 0 | 0 | 0 | 4.6342 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.433 | 36.9 | 0 | 92.433 | 364.8525 | 28.63% | 0 | 0 | 0 | 0% | 36.9
8624 | 132 | 28 | 18 | 5.0372 | 12.4 | 66.4379 | 0 | 0 | 0 | 2.5633 | 0 | 0 | 2.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364.8525 | 28.63% | 0 | 0 | 0 | 0% | 2.5633
8625 | 379 | 149 | 80 | 4.0297 | 15.4 | 190.7573 | 92.5755 | 0 | 67.9469 | 26.8367 | 0 | 0 | 26.8367 | 0 | 0 | 0 | 0 | 0 | 67.9469 | 0 | 427.9194 | 33.58% | 0 | 0 | 0 | 0% | 26.8367
8626 | 476 | 266 | 103 | 1.4104 | 18.6 | 239.5791 | 133.9988 | 0 | 107.5507 | 49.3686 | 0 | 5.1843 | 44.1843 | 0 | 0 | 0 | 0 | 0 | 107.5507 | 0 | 527.7456 | 41.41% | 3.9764 | 0 | 4.1783 | 8.357% | 39
8627 | 800 | 430 | 81 | 1.2089 | 21.8 | 402.6539 | 240.7402 | 0 | 207.5134 | 100.8388 | 5.8194 | 25 | 70.0194 | 0 | 0 | 0 | 0 | 0 | 207.5134 | 0 | 720.3551 | 56.52% | 19.175 | 0 | 24.3271 | 48.65% | 39.2
8628 | 848 | 509 | 91 | 0.80595 | 23.7 | 426.8131 | 260.1873 | 0 | 225.7118 | 111.8 | 11.8 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 225.7118 | 0 | 929.8561 | 72.96% | 19.175 | 0 | 44.476 | 88.95% | 38.2
8629 | 754 | 505 | 126 | 1.0074 | 24.4 | 379.5013 | 228.9635 | 0 | 196.6157 | 113.5 | 31.646 | 6.854 | 75 | 0 | 0 | 0 | 0 | 0 | 196.6157 | 0 | 1112.3506 | 87.28% | 5.257 | 0 | 50 | 100% | 36.5
8630 | 577 | 423 | 154 | 5.2387 | 23.7 | 290.4141 | 167.7286 | 0 | 137.83 | 92.474 | 28.337 | 0 | 64.137 | 0 | 0 | 0 | 0 | 0 | 137.83 | 0 | 1240.2815 | 97.31% | 0 | 0 | 50 | 100% | 35.8
8631 | 544 | 344 | 139 | 4.6342 | 23.4 | 273.8047 | 0 | 139.8127 | 0 | 72.7737 | 18.1368 | 0 | 54.6368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.2815 | 97.31% | 0 | 0 | 50 | 100% | 36.5
8632 | 369 | 201 | 109 | 3.0223 | 21.9 | 185.7241 | 0 | 73.7084 | 0 | 33.2314 | 0 | 0 | 33.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.2815 | 97.31% | 0 | 5.7686 | 43.9393 | 87.88% | 39
8633 | 133 | 55 | 39 | 1.6119 | 19.1 | 66.9412 | 0 | 0 | 0 | 5.8668 | 0 | 0 | 5.8668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.2815 | 97.31% | 0 | 25 | 17.6734 | 35.35% | 30.8668
8634 | 0 | 0 | 0 | 2.0149 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.7013 | 23.4781 | 0 | 61.7013 | 1183.8685 | 92.89% | 0 | 16.8219 | 2.7756e-15 | 5.551e-15% | 40.3
8635 | 0 | 0 | 0 | 2.0149 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.9812 | 40 | 0 | 99.9812 | 1084.8434 | 85.12% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 40
8636 | 0 | 0 | 0 | 3.6268 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6437 | 37.8 | 0 | 94.6437 | 992.1223 | 77.84% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 37.8
8637 | 0 | 0 | 0 | 5.2387 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6672 | 34.5 | 0 | 86.6672 | 908.7197 | 71.3% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 34.5
8638 | 0 | 0 | 0 | 6.8506 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2182 | 31.8 | 0 | 80.2182 | 833.0354 | 65.36% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 31.8
8639 | 0 | 0 | 0 | 8.8654 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3458 | 29.3 | 0 | 74.3458 | 764.0777 | 59.95% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 29.3
8640 | 0 | 0 | 0 | 8.4625 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.2258 | 27.9 | 0 | 71.2258 | 698.4334 | 54.8% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27.9
8641 | 0 | 0 | 0 | 6.6491 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.4162 | 27.1 | 0 | 69.4162 | 634.5178 | 49.79% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27.1
8642 | 0 | 0 | 0 | 6.4476 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.1361 | 27 | 0 | 69.1361 | 570.8582 | 44.79% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27
8643 | 0 | 0 | 0 | 4.2312 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.1063 | 27.9 | 0 | 71.1063 | 505.2799 | 39.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27.9
8644 | 0 | 0 | 0 | 3.8283 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4512 | 30.7 | 0 | 77.4512 | 432.6023 | 33.94% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.7
8645 | 0 | 0 | 0 | 4.8357 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.349 | 33.1668 | 0 | 83.349 | 352.9356 | 27.69% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 33.1668
8646 | 0 | 0 | 0 | 4.4327 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352.9356 | 27.69% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
8647 | 0 | 0 | 0 | 6.4476 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352.9356 | 27.69% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0
8648 | 24 | 12 | 10 | 4.8357 | 9.8 | 12.0796 | 0 | 0 | 0 | 0.6553 | 0 | 0 | 0.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352.9356 | 27.69% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0.6553
8649 | 231 | 100 | 53 | 5.2387 | 11 | 116.2663 | 0 | 56.5701 | 0 | 17.476 | 0 | 0 | 17.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352.9356 | 27.69% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 17.476
8650 | 629 | 286 | 76 | 6.4476 | 13.7 | 316.5866 | 177.306 | 0 | 145.9868 | 66.2124 | 0 | 12.3062 | 53.9062 | 0 | 0 | 0 | 0 | 0 | 145.9868 | 0 | 489.0749 | 38.37% | 9.4388 | 0 | 9.9197 | 19.84% | 41.6
8651 | 759 | 415 | 86 | 7.2535 | 15.2 | 382.0179 | 228.5148 | 0 | 193.3396 | 102.6946 | 5.5473 | 25 | 72.1473 | 0 | 0 | 0 | 0 | 0 | 193.3396 | 0 | 669.373 | 52.52% | 19.175 | 0 | 30.0715 | 60.14% | 41.6
8652 | 810 | 493 | 93 | 8.0595 | 16 | 407.6871 | 248.6011 | 0 | 211.5037 | 109.6 | 9.877 | 24.723 | 75 | 0 | 0 | 0 | 0 | 0 | 211.5037 | 0 | 866.6098 | 68% | 18.9625 | 0 | 50 | 100% | 40.4
8653 | 832 | 509 | 91 | 8.261 | 17.4 | 418.7601 | 252.665 | 0 | 215.1773 | 111.1 | 36.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 215.1773 | 0 | 1067.2725 | 83.74% | 0 | 0 | 50 | 100% | 38.9
8654 | 795 | 454 | 88 | 8.4625 | 18.3 | 400.1373 | 231.044 | 0 | 195.0503 | 111.7 | 36.7 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 195.0503 | 0 | 1249.1658 | 98.01% | 0 | 0 | 50 | 100% | 38.3
8655 | 715 | 353 | 86 | 9.2684 | 18.7 | 359.8719 | 0 | 183.6339 | 0 | 88.3575 | 24.7287 | 0 | 63.6287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.1658 | 98.01% | 0 | 0 | 50 | 100% | 38.9
8656 | 474 | 196 | 76 | 9.2684 | 17.7 | 238.5724 | 0 | 94.5074 | 0 | 36.9118 | 0 | 0 | 36.9118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.1658 | 98.01% | 0 | 4.4882 | 45.2839 | 90.57% | 41.4
8657 | 74 | 41 | 31 | 7.052 | 15.4 | 37.2455 | 0 | 0 | 0 | 4.2336 | 0 | 0 | 4.2336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.1658 | 98.01% | 0 | 25 | 19.0141 | 38.03% | 29.2336
8658 | 0 | 0 | 0 | 6.0446 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.7522 | 24.1047 | 0 | 62.7522 | 1191.713 | 93.5% | 0 | 18.0953 | 0 | 0% | 42.2
8659 | 0 | 0 | 0 | 5.0372 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9694 | 41.7 | 0 | 103.9694 | 1087.8869 | 85.36% | 0 | 0 | 0 | 0% | 41.7
8660 | 0 | 0 | 0 | 6.0446 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1901 | 39.3 | 0 | 98.1901 | 990.8637 | 77.74% | 0 | 0 | 0 | 0% | 39.3
8661 | 0 | 0 | 0 | 6.4476 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5142 | 36.1 | 0 | 90.5142 | 902.9248 | 70.84% | 0 | 0 | 0 | 0% | 36.1
8662 | 0 | 0 | 0 | 4.8357 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9751 | 33.4 | 0 | 83.9751 | 822.6829 | 64.55% | 0 | 0 | 0 | 0% | 33.4
8663 | 0 | 0 | 0 | 4.4327 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4248 | 30.7 | 0 | 77.4248 | 750.0627 | 58.85% | 0 | 0 | 0 | 0% | 30.7
8664 | 0 | 0 | 0 | 2.6193 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2374 | 28.9 | 0 | 73.2374 | 682.0685 | 53.52% | 0 | 0 | 0 | 0% | 28.9
8665 | 0 | 0 | 0 | 4.6342 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.27 | 28 | 0 | 71.27 | 616.2636 | 48.35% | 0 | 0 | 0 | 0% | 28
8666 | 0 | 0 | 0 | 4.4327 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.9304 | 27.4 | 0 | 69.9304 | 551.8311 | 43.3% | 0 | 0 | 0 | 0% | 27.4
8667 | 0 | 0 | 0 | 6.2461 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.3994 | 27.6 | 0 | 70.3994 | 486.9362 | 38.21% | 0 | 0 | 0 | 0% | 27.6
8668 | 0 | 0 | 0 | 4.2312 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2269 | 28.9 | 0 | 73.2269 | 418.8925 | 32.87% | 0 | 0 | 0 | 0% | 28.9
8669 | 0 | 0 | 0 | 3.4253 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418.8925 | 32.87% | 0 | 0 | 0 | 0% | 0
8670 | 0 | 0 | 0 | 3.6268 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418.8925 | 32.87% | 0 | 0 | 0 | 0% | 0
8671 | 0 | 0 | 0 | 4.2312 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418.8925 | 32.87% | 0 | 0 | 0 | 0% | 0
8672 | 138 | 20 | 10 | 4.4327 | 8.3 | 69.4578 | 0 | 0 | 0 | 1.9821 | 0 | 0 | 1.9821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418.8925 | 32.87% | 0 | 0 | 0 | 0% | 1.9821
8673 | 626 | 157 | 36 | 4.4327 | 10.8 | 315.0767 | 153.6036 | 0 | 124.8079 | 33.2851 | 0 | 0 | 33.2851 | 0 | 0 | 0 | 0 | 0 | 124.8079 | 0 | 535.6485 | 42.03% | 0 | 0 | 0 | 0% | 33.2851
8674 | 801 | 315 | 50 | 3.8283 | 13.5 | 403.1572 | 226.1134 | 0 | 192.8748 | 82.866 | 0 | 21.983 | 60.883 | 0 | 0 | 0 | 0 | 0 | 192.8748 | 0 | 716.0799 | 56.18% | 16.861 | 0 | 17.7225 | 35.44% | 38.9
8675 | 888 | 440 | 56 | 6.2461 | 15.3 | 446.9458 | 267.4992 | 0 | 230.2269 | 111.1 | 11.1 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 230.2269 | 0 | 931.4538 | 73.08% | 19.175 | 0 | 37.8773 | 75.75% | 38.9
8676 | 923 | 512 | 58 | 6.2461 | 16.3 | 464.5619 | 283.3814 | 0 | 245.2052 | 111.8 | 21.763 | 15.037 | 75 | 0 | 0 | 0 | 0 | 0 | 245.2052 | 0 | 1160.8396 | 91.08% | 11.5334 | 0 | 50 | 100% | 38.2
8677 | 935 | 526 | 57 | 2.8208 | 17.4 | 470.6018 | 283.9776 | 0 | 247.3375 | 113.4 | 38.4 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 247.3375 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36.6
8678 | 914 | 475 | 55 | 2.0149 | 18.9 | 460.0321 | 0 | 265.5926 | 0 | 114.3 | 39.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 35.7
8679 | 857 | 369 | 50 | 1.8134 | 19.8 | 431.343 | 0 | 219.974 | 0 | 95.8462 | 29.9231 | 0 | 65.9231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 36
8680 | 709 | 216 | 42 | 8.261 | 17.4 | 356.852 | 0 | 141.1265 | 0 | 55.0718 | 8.1359 | 0 | 46.9359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 38.8
8681 | 313 | 56 | 20 | 10.0743 | 13.2 | 157.5383 | 0 | 0 | 0 | 7.6045 | 0 | 0 | 7.6045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.7266 | 47.45% | 32.6045
8682 | 0 | 0 | 0 | 8.261 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.5766 | 2.7756e-15 | 5.551e-15% | 22.5766
8683 | 0 | 0 | 0 | 8.261 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.116 | 40.6 | 0 | 101.116 | 1173.7871 | 92.1% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 40.6
8684 | 0 | 0 | 0 | 6.8506 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7704 | 38.8 | 0 | 96.7704 | 1078.1999 | 84.6% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 38.8
8685 | 0 | 0 | 0 | 6.2461 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8124 | 35.9 | 0 | 89.8124 | 990.8183 | 77.74% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 35.9
8686 | 0 | 0 | 0 | 5.8431 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6186 | 32.9 | 0 | 82.6186 | 912.0071 | 71.56% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.9
8687 | 0 | 0 | 0 | 7.052 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3633 | 30.3 | 0 | 76.3633 | 840.4962 | 65.95% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.3
8688 | 0 | 0 | 0 | 4.2312 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.3094 | 28.5 | 0 | 72.3094 | 773.4795 | 60.69% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 28.5
8689 | 0 | 0 | 0 | 4.0297 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.6023 | 27.3 | 0 | 69.6023 | 709.3692 | 55.66% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27.3
8690 | 0 | 0 | 0 | 3.4253 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4518 | 26.8 | 0 | 68.4518 | 646.3523 | 50.71% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 26.8
8691 | 0 | 0 | 0 | 3.6268 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.9118 | 27 | 0 | 68.9118 | 582.8836 | 45.73% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27
8692 | 0 | 0 | 0 | 3.8283 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2383 | 27.6 | 0 | 70.2383 | 518.0215 | 40.64% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 27.6
8693 | 0 | 0 | 0 | 4.0297 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9113 | 28.8 | 0 | 72.9113 | 450.2126 | 35.32% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 28.8
8694 | 0 | 0 | 0 | 4.4327 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.8053 | 30.1 | 0 | 75.8053 | 379.1679 | 29.75% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.1
8695 | 0 | 0 | 0 | 5.2387 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5787 | 32.5 | 0 | 81.5787 | 301.3675 | 23.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 32.5
8696 | 32 | 14 | 11 | 3.8283 | 4.9 | 16.1062 | 0 | 0 | 0 | 0.83642 | 0 | 0 | 0.83642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.3675 | 23.65% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 0.83642
8697 | 537 | 152 | 46 | 4.2312 | 7.5 | 270.2814 | 132.0153 | 0 | 104.567 | 30.9912 | 0 | 0 | 30.9912 | 0 | 0 | 0 | 0 | 0 | 104.567 | 0 | 399.0026 | 31.31% | 0 | 0 | 2.7756e-15 | 5.551e-15% | 30.9912
8698 | 762 | 317 | 64 | 4.0297 | 10.7 | 383.5278 | 215.4324 | 0 | 182.7756 | 85.7897 | 0 | 24.8449 | 60.9449 | 0 | 0 | 0 | 0 | 0 | 182.7756 | 0 | 569.6617 | 44.7% | 19.056 | 0 | 20.0327 | 40.07% | 36.1
8699 | 821 | 466 | 109 | 6.2461 | 12.6 | 413.2236 | 247.4641 | 0 | 211.5136 | 113.5 | 13.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 211.5136 | 0 | 767.1537 | 60.19% | 19.175 | 0 | 40.1904 | 80.38% | 36.5
8700 | 755 | 479 | 104 | 6.8506 | 13 | 380.0046 | 231.8955 | 0 | 196.7355 | 113.7 | 26.5341 | 12.1659 | 75 | 0 | 0 | 0 | 0 | 0 | 196.7355 | 0 | 950.8473 | 74.6% | 9.3313 | 0 | 50 | 100% | 36.3
8701 | 873 | 521 | 82 | 6.2461 | 13.3 | 439.3961 | 265.1926 | 0 | 228.0316 | 115.3 | 40.3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 228.0316 | 0 | 1163.7623 | 91.31% | 0 | 0 | 50 | 100% | 34.7
8702 | 890 | 475 | 64 | 5.4401 | 14.1 | 447.9525 | 258.6116 | 0 | 222.4014 | 116.1 | 41.1 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 222.4014 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 33.9
8703 | 816 | 366 | 61 | 8.4625 | 14.4 | 410.707 | 0 | 209.3484 | 0 | 103.1443 | 34.4221 | 0 | 68.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 34.3
8704 | 684 | 217 | 48 | 8.4625 | 13.8 | 344.2691 | 0 | 135.9475 | 0 | 56.839 | 9.7695 | 0 | 47.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 0 | 50 | 100% | 37.3
8705 | 305 | 57 | 22 | 6.0446 | 12.3 | 153.5118 | 0 | 0 | 0 | 7.8148 | 0 | 0 | 7.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 25 | 23.7227 | 47.45% | 32.8148
8706 | 0 | 0 | 0 | 4.4327 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.5104 | 100% | 0 | 22.5696 | 0 | 0% | 22.5696
8707 | 0 | 0 | 0 | 4.2312 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1511 | 40.2 | 0 | 100.1511 | 1174.9571 | 92.19% | 0 | 0 | 0 | 0% | 40.2
8708 | 0 | 0 | 0 | 3.2238 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.46 | 38.7 | 0 | 96.46 | 1079.6984 | 84.71% | 0 | 0 | 0 | 0% | 38.7
8709 | 0 | 0 | 0 | 3.4253 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.242 | 35.7 | 0 | 89.242 | 992.9152 | 77.91% | 0 | 0 | 0 | 0% | 35.7
8710 | 0 | 0 | 0 | 5.8431 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3806 | 32.4 | 0 | 81.3806 | 915.5597 | 71.84% | 0 | 0 | 0 | 0% | 32.4
8711 | 0 | 0 | 0 | 5.8431 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.7475 | 29.6 | 0 | 74.7475 | 845.8899 | 66.37% | 0 | 0 | 0 | 0% | 29.6
8712 | 0 | 0 | 0 | 2.8208 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5826 | 28.2 | 0 | 71.5826 | 779.635 | 61.17% | 0 | 0 | 0 | 0% | 28.2
8713 | 0 | 0 | 0 | 3.6268 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.6195 | 27.3 | 0 | 69.6195 | 715.5366 | 56.14% | 0 | 0 | 0 | 0% | 27.3
8714 | 0 | 0 | 0 | 3.2238 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.6646 | 27.3 | 0 | 69.6646 | 651.3864 | 51.11% | 0 | 0 | 0 | 0% | 27.3
8715 | 0 | 0 | 0 | 4.6342 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4578 | 28.1 | 0 | 71.4578 | 585.344 | 45.93% | 0 | 0 | 0 | 0% | 28.1
8716 | 0 | 0 | 0 | 4.4327 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3285 | 30.7 | 0 | 77.3285 | 512.6972 | 40.23% | 0 | 0 | 0 | 0% | 30.7
8717 | 0 | 0 | 0 | 2.0149 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1203 | 34.8 | 0 | 87.1203 | 428.3522 | 33.61% | 0 | 0 | 0 | 0% | 34.8
8718 | 0 | 0 | 0 | 0.80595 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5011 | 38.3 | 0 | 95.5011 | 334.0778 | 26.21% | 0 | 0 | 0 | 0% | 38.3
8719 | 0 | 0 | 0 | 1.8134 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9057 | 41.8 | 0 | 103.9057 | 229.7884 | 18.03% | 0 | 0 | 0 | 0% | 41.8
8720 | 0 | 6 | 6 | 2.0149 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.7884 | 18.03% | 0 | 0 | 0 | 0% | 0
8721 | 0 | 47 | 47 | 2.0149 | 8.8 | 0 | 0 | 0 | 0 | 3.3046 | 0 | 0 | 3.3046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.7884 | 18.03% | 0 | 0 | 0 | 0% | 3.3046
8722 | 7 | 159 | 154 | 2.0149 | 10.1 | 3.5232 | 0 | 1.9822 | 0 | 14.5146 | 0 | 0 | 14.5146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.7884 | 18.03% | 0 | 0 | 0 | 0% | 14.5146
8723 | 21 | 254 | 241 | 2.8208 | 11.6 | 10.5697 | 0 | 6.3339 | 0 | 24.3318 | 0 | 0 | 24.3318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.7884 | 18.03% | 0 | 0 | 0 | 0% | 24.3318
8724 | 7 | 273 | 266 | 1.6119 | 12.4 | 3.5232 | 0 | 2.151 | 0 | 24.9396 | 0 | 0 | 24.9396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.7884 | 18.03% | 0 | 0 | 0 | 0% | 24.9396
8725 | 116 | 336 | 273 | 3.2238 | 12.7 | 58.3848 | 0 | 35.2455 | 0 | 37.7466 | 0 | 0 | 37.7466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.7884 | 18.03% | 0 | 0 | 0 | 0% | 37.7466
8726 | 749 | 545 | 197 | 3.6268 | 13.6 | 376.9847 | 217.6578 | 0 | 185.032 | 110.5 | 10.5 | 25 | 75 | 0 | 0 | 0 | 0 | 0 | 185.032 | 0 | 404.1104 | 31.71% | 19.175 | 0 | 20.1609 | 40.32% | 39.5
8727 | 611 | 393 | 159 | 3.0223 | 14.1 | 307.5269 | 156.6949 | 0 | 128.2277 | 85.5111 | 0 | 22.8055 | 62.7055 | 0 | 0 | 0 | 0 | 0 | 128.2277 | 0 | 524.9159 | 41.19% | 17.4919 | 0 | 38.5521 | 77.1% | 39.9
8728 | 546 | 222 | 82 | 2.8208 | 13.9 | 274.8113 | 108.3777 | 0 | 83.0062 | 42.1097 | 0 | 0 | 42.1097 | 0 | 0 | 0 | 0 | 0 | 83.0062 | 0 | 603.1175 | 47.32% | 0 | 0 | 38.5521 | 77.1% | 42.1097
8729 | 226 | 52 | 27 | 0.80595 | 13 | 113.7497 | 0 | 0 | 0 | 7.2144 | 0 | 0 | 7.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603.1175 | 47.32% | 0 | 25 | 12.2709 | 24.54% | 32.2144
8730 | 0 | 0 | 0 | 2.6193 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3874 | 31.9274 | 0 | 80.3874 | 527.024 | 41.35% | 0 | 11.6726 | 0 | 0% | 43.6
8731 | 0 | 0 | 0 | 2.2164 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.6134 | 43.3 | 0 | 107.6134 | 418.5025 | 32.84% | 0 | 0 | 0 | 0% | 43.3
8732 | 0 | 0 | 0 | 3.0223 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5118 | 40.8 | 0 | 101.5118 | 317.072 | 24.88% | 0 | 0 | 0 | 0% | 40.8
8733 | 0 | 0 | 0 | 2.8208 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.855 | 37.2 | 0 | 92.855 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 37.2
8734 | 0 | 0 | 0 | 4.4327 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8735 | 0 | 0 | 0 | 5.8431 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8736 | 0 | 0 | 0 | 5.4401 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8737 | 0 | 0 | 0 | 3.4253 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8738 | 0 | 0 | 0 | 4.8357 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8739 | 0 | 0 | 0 | 3.8283 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8740 | 0 | 0 | 0 | 2.4178 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8741 | 0 | 0 | 0 | 3.6268 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8742 | 0 | 0 | 0 | 4.4327 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8743 | 0 | 0 | 0 | 4.2312 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0
8744 | 1 | 9 | 9 | 2.8208 | 4.5 | 0.50332 | 0 | 0 | 0 | 0.1114 | 0 | 0 | 0.1114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 0.1114
8745 | 13 | 90 | 86 | 1.6119 | 6.5 | 6.5431 | 0 | 3.2089 | 0 | 8.6022 | 0 | 0 | 8.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 8.6022
8746 | 14 | 163 | 158 | 2.2164 | 8.2 | 7.0464 | 0 | 3.9713 | 0 | 15.5938 | 0 | 0 | 15.5938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 15.5938
8747 | 12 | 238 | 230 | 1.4104 | 10.5 | 6.0398 | 0 | 3.6219 | 0 | 22.2545 | 0 | 0 | 22.2545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 22.2545
8748 | 23 | 282 | 267 | 2.4178 | 12.2 | 11.5763 | 0 | 7.0712 | 0 | 26.5386 | 0 | 0 | 26.5386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225.8999 | 17.72% | 0 | 0 | 0 | 0% | 26.5386
8749 | 589 | 483 | 183 | 2.8208 | 12.9 | 296.4539 | 179.0125 | 0 | 149.2386 | 106.35 | 9.325 | 25 | 72.025 | 0 | 0 | 0 | 0 | 0 | 149.2386 | 0 | 367.4728 | 28.83% | 19.175 | 0 | 20.1633 | 40.33% | 37.7
8750 | 366 | 334 | 159 | 3.4253 | 13.2 | 184.2142 | 106.3785 | 0 | 80.8781 | 62.4195 | 0 | 12.7098 | 49.7098 | 0 | 0 | 0 | 0 | 0 | 80.8781 | 0 | 444.1966 | 34.85% | 9.7484 | 0 | 30.4142 | 60.83% | 37
8751 | 132 | 165 | 117 | 2.6193 | 12.9 | 66.4379 | 0 | 33.8429 | 0 | 21.3845 | 0 | 0 | 21.3845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 444.1966 | 34.85% | 0 | 16.1155 | 13.4707 | 26.94% | 37.5
8752 | 471 | 207 | 83 | 3.2238 | 13.5 | 237.0625 | 93.3857 | 0 | 68.9481 | 38.1118 | 0 | 0 | 38.1118 | 0 | 0 | 0 | 0 | 0 | 68.9481 | 0 | 509.6031 | 39.98% | 0 | 2.6882 | 10.6443 | 21.29% | 40.8
8753 | 248 | 56 | 27 | 4.0297 | 11.8 | 124.8227 | 0 | 0 | 0 | 7.9662 | 0 | 0 | 7.9662 | 0 | 0 | 0 | 62.2078 | 23.91 | 0 | 62.2078 | 452.4901 | 35.5% | 0 | 10.1239 | 0 | 0% | 42
8754 | 0 | 0 | 0 | 2.6193 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8393 | 40.9 | 0 | 101.8393 | 350.5714 | 27.51% | 0 | 0 | 0 | 0% | 40.9
8755 | 0 | 0 | 0 | 1.6119 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7648 | 38.4 | 0 | 95.7648 | 255.8019 | 20.07% | 0 | 0 | 0 | 0% | 38.4
8756 | 0 | 0 | 0 | 2.4178 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255.8019 | 20.07% | 0 | 0 | 0 | 0% | 0
8757 | 0 | 0 | 0 | 0.80595 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255.8019 | 20.07% | 0 | 0 | 0 | 0% | 0
8758 | 0 | 0 | 0 | 1.6119 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255.8019 | 20.07% | 0 | 0 | 0 | 0% | 0
8759 | 0 | 0 | 0 | 1.2089 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255.8019 | 20.07% | 0 | 0 | 0 | 0% | 0

## 2.2 - Output Operation- AESOPT
Hours | DNI | GHI | DHI | Wspd | T_amb | Q_in_SF | Q_out_SF | Q_def_SF | Q_out_rec | PV_AC_tot | PV_AC_waste | PV_AC_toBESS | PV_AC_togrid | PV_AC_toEH | P_in_EH | Q_out_EH | Q_in_PB | P_net_PB | TES_ch | TES_disch | TES_SOC | TES_SOC_normalized | BESS_ch | BESS_disch | BESS_SOC | BESS_SOC_normalized | P_injected_to_grid | Legend
h | W/m2 | W/m2 | W/m2 | m/s | C | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MW | MWh | % | MW | MW | MWh | % | MW | Symbol | Description | Unit
0 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5253 | 29.7145 | 0 | 76.5253 | 637.7551 | 50% | 0 | 0 | 31.25 | 50% | 29.7145 | DNI | Direct Normal Irradiance | W/m2
1 | 0 | 0 | 0 | 0.5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8532 | 28.1101 | 0 | 72.8532 | 564.9019 | 44.29% | 0 | 0 | 31.25 | 50% | 28.1101 | GHI | Global Horizontal Irradiance | W/m2
2 | 0 | 0 | 0 | 0.9 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.449 | 27.06 | 0 | 70.449 | 494.4529 | 38.77% | 0 | 0 | 31.25 | 50% | 27.06 | DHI | Diffuse Horizontal Irradiance | W/m2
3 | 0 | 0 | 0 | 0.7 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.5917 | 26.6854 | 0 | 69.5917 | 424.8612 | 33.31% | 0 | 0 | 31.25 | 50% | 26.6854 | Wspd | Wind Speed | m/s
4 | 0 | 0 | 0 | 1.2 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1673 | 26.9375 | 0 | 70.1673 | 354.6939 | 27.81% | 0 | 0 | 31.25 | 50% | 26.9375 | T_amb | Ambient Temperature | C
5 | 0 | 0 | 0 | 1.8 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.6072 | 27.567 | 0 | 71.6072 | 283.0867 | 22.19% | 0 | 0 | 31.25 | 50% | 27.567 | Q_in_SF | Thermal power hitting the surface of SF mirrors (DNI x SF area) | MW
6 | 0 | 0 | 0 | 1.5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3918 | 27.4723 | 0 | 71.3918 | 211.6949 | 16.6% | 0 | 0 | 31.25 | 50% | 27.4723 | Q_out_SF | Thermal power reflected by SF mirrors and hitting the receiver (DNI x SF area x opt eff. - defocus), not defocused | MW
7 | 0 | 0 | 0 | 0.8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5019 | 28.3915 | 0 | 73.5019 | 138.193 | 10.83% | 0 | 0 | 31.25 | 50% | 28.3915 | Q_def_SF | Thermal power defocused from the receiver (i.e., wasted) | MW
8 | 154 | 18 | 8 | 0.7 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.3003 | 16.5186 | 0 | 46.3003 | 91.8927 | 7.204% | 0 | 14.1945 | 15.5405 | 24.86% | 30.7131 | Q_out_rec | Thermal power produced by the receiver and absorbed by HTF | MW
9 | 699 | 158 | 31 | 0.3 | 9.5 | 0 | 0 | 0 | 0 | 24.0664 | 0 | 0 | 24.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8927 | 7.204% | 0 | 8.3945 | 6.25 | 10% | 32.4609 | PV_AC_tot | Total PV AC electricitry production, not curtailed | MW
10 | 873 | 324 | 42 | 0.2 | 14.6 | 0 | 0 | 0 | 176.7394 | 33.2269 | 11.2176 | 0 | 33.2269 | 0 | 0 | 0 | 0 | 0 | 176.7394 | 0 | 268.6321 | 21.06% | 0 | 0 | 6.25 | 10% | 33.2269 | PV_AC_waste | PV AC electricitry production wasted (curtailed) | MW
11 | 945 | 454 | 47 | 0.8 | 16.7 | 0 | 0 | 0 | 225.0919 | 33.8982 | 24.1157 | 0 | 33.8982 | 0 | 0 | 0 | 0 | 0 | 225.0919 | 0 | 493.724 | 38.71% | 0 | 0 | 6.25 | 10% | 33.8982 | PV_AC_toBESS | Fraction of total AC production not wasted and used to charge the BESS | MW
12 | 974 | 529 | 49 | 2.5 | 17.5 | 0 | 0 | 0 | 249.8572 | 33.7645 | 34.3342 | 0 | 33.7645 | 0 | 0 | 0 | 0 | 0 | 249.8572 | 0 | 743.5812 | 58.3% | 0 | 0 | 6.25 | 10% | 33.7645 | PV_AC_togrid | Fraction of total AC production not wasted and injected into the grid | MW
13 | 979 | 543 | 49 | 3.2 | 18.5 | 0 | 0 | 0 | 0 | 32.0417 | 39.5423 | 0 | 32.0417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743.5812 | 58.3% | 0 | 0 | 6.25 | 10% | 32.0417 | PV_AC_toEH | Fraction of total AC production not wasted and injected into the EH | MW
14 | 959 | 494 | 48 | 3.1 | 19.2 | 0 | 0 | 0 | 248.7578 | 56.3426 | 12.5762 | 25 | 31.3426 | 0 | 0 | 0 | 0 | 0 | 248.7578 | 0 | 992.339 | 77.8% | 25 | 0 | 28.839 | 46.14% | 31.3426 | P_in_EH | Electric AC power absorbed by the EH | MW
15 | 907 | 387 | 44 | 4 | 18.9 | 0 | 0 | 0 | 224.202 | 56.94 | 4.3558 | 25 | 31.94 | 0 | 0 | 0 | 0 | 0 | 224.202 | 0 | 1216.541 | 95.38% | 25 | 0 | 51.428 | 82.28% | 31.94 | Q_out_EH | Thermal power produced by the EH | MW
16 | 788 | 235 | 36 | 3.8 | 18.3 | 0 | 0 | 0 | 0 | 40.9423 | 5.0041 | 5.3367 | 35.6056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.541 | 95.38% | 5.3367 | 0 | 56.25 | 90% | 35.6056 | Q_in_PB | Thermal power absorbed by the PB | MW
17 | 440 | 68 | 18 | 3 | 16.1 | 0 | 0 | 0 | 58.9692 | 19.2589 | 0 | 0 | 19.2589 | 0 | 0 | 0 | 0 | 0 | 58.9692 | 0 | 1275.5102 | 100% | 0 | 18.4399 | 35.842 | 57.35% | 37.6988 | P_net_PB | Electric power produced by the PB | MW
18 | 1 | 0 | 0 | 1.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4584 | 39.2099 | 0 | 98.4584 | 1177.0518 | 92.28% | 0 | 0 | 35.842 | 57.35% | 39.2099 | TES_ch | Thermal power charged in the TES | MW
19 | 0 | 0 | 0 | 0.2 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4076 | 39.6764 | 0 | 99.4076 | 1077.6442 | 84.49% | 0 | 0 | 35.842 | 57.35% | 39.6764 | TES_disch | Thermal power discharged from the TES | MW
20 | 0 | 0 | 0 | 0.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5738 | 38.462 | 0 | 96.5738 | 981.0704 | 76.92% | 0 | 0 | 35.842 | 57.35% | 38.462 | TES_SOC | TES State of Charge | MWh
21 | 0 | 0 | 0 | 1.1 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1554 | 35.6613 | 0 | 90.1554 | 890.915 | 69.85% | 0 | 0 | 35.842 | 57.35% | 35.6613 | TES_SOC_normalized | Normalized fraction of TES SOC | %
22 | 0 | 0 | 0 | 1.4 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.389 | 32.2729 | 0 | 82.389 | 808.526 | 63.39% | 0 | 0 | 35.842 | 57.35% | 32.2729 | BESS_ch | Electric AC power charged in the BESS | MW
23 | 0 | 0 | 0 | 1.7 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.4987 | 29.702 | 0 | 76.4987 | 732.0272 | 57.39% | 0 | 0 | 35.842 | 57.35% | 29.702 | BESS_disch | Electric AC power discharged from the BESS | MW
24 | 0 | 0 | 0 | 2.1 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.6864 | 28.0377 | 0 | 72.6864 | 659.3409 | 51.69% | 0 | 0 | 35.842 | 57.35% | 28.0377 | BESS_SOC | BESS State of Charge | MWh
25 | 0 | 0 | 0 | 1.2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659.3409 | 51.69% | 0 | 25 | 8.1736 | 13.08% | 25 | BESS_SOC_normalized | Normalized fraction of BESS SOC | %
26 | 0 | 0 | 0 | 1.1 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 659.3409 | 51.69% | 0 | 1.6199 | 6.3809 | 10.21% | 1.6199 | P_injected_to_grid | Electric power injected to the grid | MW
27 | 0 | 0 | 0 | 2.4 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6066 | 28.4402 | 0 | 73.6066 | 585.7343 | 45.92% | 0 | 0 | 6.3809 | 10.21% | 28.4402
28 | 0 | 0 | 0 | 2.2 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4752 | 32.3105 | 0 | 82.4752 | 503.2591 | 39.46% | 0 | 0 | 6.3809 | 10.21% | 32.3105
29 | 0 | 0 | 0 | 1.8 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7189 | 37.6557 | 0 | 94.7189 | 408.5402 | 32.03% | 0 | 0 | 6.3809 | 10.21% | 37.6557
30 | 0 | 0 | 0 | 2.9 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3313 | 44.907 | 0 | 111.3313 | 297.2089 | 23.3% | 2.5998 | 0 | 8.7299 | 13.97% | 42.3072
31 | 0 | 0 | 0 | 2.5 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.9942 | 46.0689 | 0 | 113.9942 | 183.2147 | 14.36% | 0 | 0 | 8.7299 | 13.97% | 46.0689
32 | 154 | 18 | 8 | 2.9 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.0481 | 48.2708 | 0 | 119.0481 | 64.1666 | 5.031% | 0 | 0 | 8.7299 | 13.97% | 48.2708
33 | 705 | 159 | 31 | 0.8 | 10.9 | 0 | 0 | 0 | 0 | 24.1781 | 0 | 0 | 24.1781 | 0 | 0 | 0 | 64.1666 | 24.2904 | 0 | 64.1666 | 0 | 0% | 0 | 0 | 8.7299 | 13.97% | 48.4685
34 | 879 | 327 | 42 | 1 | 14.6 | 0 | 0 | 0 | 83.0966 | 45.5245 | 0 | 0 | 45.5245 | 0 | 0 | 0 | 0 | 0 | 83.0966 | 0 | 83.0966 | 6.515% | 0 | 2.2407 | 6.25 | 10% | 47.7652
35 | 952 | 458 | 48 | 0.9 | 17.2 | 0 | 0 | 0 | 226.8811 | 47.5521 | 10.9265 | 0 | 47.5521 | 0 | 0 | 0 | 0 | 0 | 226.8811 | 0 | 309.9778 | 24.3% | 0 | 0 | 6.25 | 10% | 47.5521
36 | 980 | 534 | 51 | 1.4 | 18.4 | 0 | 0 | 0 | 252.1576 | 46.4589 | 20.4408 | 0 | 46.4589 | 0 | 0 | 0 | 0 | 0 | 252.1576 | 0 | 562.1354 | 44.07% | 0 | 0 | 6.25 | 10% | 46.4589
37 | 976 | 546 | 53 | 2.6 | 18.2 | 0 | 0 | 0 | 256.055 | 63.0835 | 8.1548 | 18.0034 | 45.0801 | 0 | 0 | 0 | 0 | 0 | 256.055 | 0 | 818.1904 | 64.15% | 18.0034 | 0 | 22.5172 | 36.03% | 45.0801
38 | 947 | 495 | 53 | 2.5 | 18.6 | 0 | 0 | 0 | 245.8823 | 68.2499 | 0 | 23.9456 | 44.3044 | 0 | 0 | 0 | 0 | 0 | 245.8823 | 0 | 1064.0727 | 83.42% | 23.9456 | 0 | 44.1534 | 70.65% | 44.3044
39 | 854 | 377 | 50 | 2.6 | 18.6 | 0 | 0 | 0 | 211.4376 | 58.075 | 0 | 13.3877 | 44.6874 | 0 | 0 | 0 | 0 | 0 | 211.4376 | 0 | 1275.5102 | 100% | 13.3877 | 0 | 56.25 | 90% | 44.6874
40 | 729 | 229 | 44 | 2.4 | 17.6 | 0 | 0 | 0 | 0 | 43.4569 | 0 | 0 | 43.4569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 4.0799 | 51.7346 | 82.78% | 47.5368
41 | 376 | 67 | 23 | 1.7 | 15.7 | 0 | 0 | 0 | 0 | 17.7183 | 0 | 0 | 17.7183 | 0 | 0 | 0 | 79.0755 | 30.6629 | 0 | 79.0755 | 1196.4347 | 93.8% | 0 | 0.060873 | 51.6672 | 82.67% | 48.4421
42 | 1 | 1 | 0 | 2.6 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.8895 | 48.9977 | 0 | 120.8895 | 1075.5452 | 84.32% | 0 | 0 | 51.6672 | 82.67% | 48.9977
43 | 0 | 0 | 0 | 2.1 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.6775 | 48.5201 | 0 | 119.6775 | 955.8677 | 74.94% | 0 | 0 | 51.6672 | 82.67% | 48.5201
44 | 0 | 0 | 0 | 2.5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8187 | 45.5299 | 0 | 112.8187 | 843.049 | 66.1% | 0 | 0 | 51.6672 | 82.67% | 45.5299
45 | 0 | 0 | 0 | 3 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2307 | 41.3519 | 0 | 103.2307 | 739.8183 | 58% | 0 | 0 | 51.6672 | 82.67% | 41.3519
46 | 0 | 0 | 0 | 3 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 739.8183 | 58% | 0 | 0 | 51.6672 | 82.67% | 0
47 | 0 | 0 | 0 | 3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 739.8183 | 58% | 0 | 0 | 51.6672 | 82.67% | 0
48 | 0 | 0 | 0 | 2.7 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 739.8183 | 58% | 0 | 0 | 51.6672 | 82.67% | 0
49 | 0 | 0 | 0 | 3.1 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 739.8183 | 58% | 0 | 0 | 51.6672 | 82.67% | 0
50 | 0 | 0 | 0 | 2.6 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 739.8183 | 58% | 0 | 0 | 51.6672 | 82.67% | 0
51 | 0 | 0 | 0 | 2.4 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 739.8183 | 58% | 0 | 0 | 51.6672 | 82.67% | 0
52 | 0 | 0 | 0 | 2.9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 739.8183 | 58% | 0 | 0 | 51.6672 | 82.67% | 0
53 | 0 | 0 | 0 | 2.8 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8952 | 40.785 | 0 | 101.8952 | 637.9231 | 50.01% | 0 | 0 | 51.6672 | 82.67% | 40.785
54 | 0 | 0 | 0 | 2.8 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.5993 | 45.4561 | 0 | 112.5993 | 525.3238 | 41.19% | 0 | 0 | 51.6672 | 82.67% | 45.4561
55 | 0 | 0 | 0 | 2.5 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.503 | 48.903 | 0 | 120.503 | 404.8208 | 31.74% | 0 | 0 | 51.6672 | 82.67% | 48.903
56 | 8 | 9 | 8 | 2.6 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0325 | 50 | 0 | 123.0325 | 281.7883 | 22.09% | 0 | 0 | 51.6672 | 82.67% | 50
57 | 599 | 148 | 38 | 1.4 | 7.1 | 0 | 0 | 0 | 78.5402 | 21.1263 | 0 | 0 | 21.1263 | 0 | 0 | 0 | 0 | 0 | 78.5402 | 0 | 360.3285 | 28.25% | 0 | 25 | 23.9989 | 38.4% | 46.1263
58 | 788 | 314 | 58 | 4.1 | 10.3 | 0 | 0 | 0 | 155.3025 | 45.1765 | 0 | 0 | 45.1765 | 0 | 0 | 0 | 0 | 0 | 155.3025 | 0 | 515.631 | 40.43% | 0 | 4.3407 | 19.1949 | 30.71% | 49.5172
59 | 835 | 439 | 76 | 5.2 | 11.7 | 0 | 0 | 0 | 194.0329 | 59.3155 | 0 | 10.2996 | 49.0159 | 0 | 0 | 0 | 0 | 0 | 194.0329 | 0 | 709.6638 | 55.64% | 10.2996 | 0 | 28.5013 | 45.6% | 49.0159
60 | 417 | 400 | 191 | 3.9 | 12.5 | 0 | 0 | 0 | 95.6124 | 46.4381 | 0 | 0 | 46.4381 | 0 | 0 | 0 | 0 | 0 | 95.6124 | 0 | 805.2763 | 63.13% | 0 | 1.2185 | 27.1527 | 43.44% | 47.6566
61 | 540 | 454 | 178 | 4.8 | 12.6 | 0 | 0 | 0 | 131.8221 | 56.6952 | 0 | 10.267 | 46.4282 | 0 | 0 | 0 | 0 | 0 | 131.8221 | 0 | 937.0983 | 73.47% | 10.267 | 0 | 36.4296 | 58.29% | 46.4282
62 | 525 | 425 | 172 | 3.7 | 13.1 | 0 | 0 | 0 | 127.4729 | 54.0147 | 0 | 7.9736 | 46.0411 | 0 | 0 | 0 | 0 | 0 | 127.4729 | 0 | 1064.5712 | 83.46% | 7.9736 | 0 | 43.6342 | 69.81% | 46.0411
63 | 464 | 297 | 119 | 2.9 | 12.9 | 0 | 0 | 0 | 106.505 | 42.322 | 0 | 0 | 42.322 | 0 | 0 | 0 | 0 | 0 | 106.505 | 0 | 1171.0761 | 91.81% | 0 | 4.2872 | 38.8894 | 62.22% | 46.6093
64 | 514 | 206 | 80 | 2.9 | 12.8 | 0 | 0 | 0 | 104.4341 | 37.2368 | 0 | 0 | 37.2368 | 0 | 0 | 0 | 0 | 0 | 104.4341 | 0 | 1275.5102 | 100% | 0 | 11.8055 | 25.8239 | 41.32% | 49.0423
65 | 140 | 63 | 42 | 4 | 11.6 | 0 | 0 | 0 | 0 | 9.4808 | 0 | 0 | 9.4808 | 0 | 0 | 0 | 86.4282 | 33.9809 | 0 | 86.4282 | 1189.082 | 93.22% | 0 | 6.4399 | 18.6966 | 29.91% | 49.9016
66 | 0 | 1 | 0 | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0894 | 50 | 0 | 123.0894 | 1065.9926 | 83.57% | 0 | 0 | 18.6966 | 29.91% | 50
67 | 0 | 0 | 0 | 2.5 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.4373 | 49.7178 | 0 | 122.4373 | 943.5553 | 73.97% | 0 | 0 | 18.6966 | 29.91% | 49.7178
68 | 0 | 0 | 0 | 2.7 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.1705 | 46.5522 | 0 | 115.1705 | 828.3848 | 64.95% | 0 | 0 | 18.6966 | 29.91% | 46.5522
69 | 0 | 0 | 0 | 2.1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6627 | 42.4228 | 0 | 105.6627 | 722.7221 | 56.66% | 0 | 0 | 18.6966 | 29.91% | 42.4228
70 | 0 | 0 | 0 | 2.2 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8273 | 38.572 | 0 | 96.8273 | 625.8948 | 49.07% | 0 | 0 | 18.6966 | 29.91% | 38.572
71 | 0 | 0 | 0 | 2.2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.41 | 35.3382 | 0 | 89.41 | 536.4848 | 42.06% | 0 | 0 | 18.6966 | 29.91% | 35.3382
72 | 0 | 0 | 0 | 1.3 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.4848 | 42.06% | 0 | 0 | 18.6966 | 29.91% | 0
73 | 0 | 0 | 0 | 1 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.4848 | 42.06% | 0 | 0 | 18.6966 | 29.91% | 0
74 | 0 | 0 | 0 | 1.2 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.4848 | 42.06% | 0 | 0 | 18.6966 | 29.91% | 0
75 | 0 | 0 | 0 | 1.1 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 536.4848 | 42.06% | 0 | 0 | 18.6966 | 29.91% | 0
76 | 0 | 0 | 0 | 1.3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.4848 | 42.06% | 0 | 6.4524 | 11.5555 | 18.49% | 6.4524
77 | 0 | 0 | 0 | 2.1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.804 | 41.6095 | 0 | 103.804 | 432.6808 | 33.92% | 0 | 0 | 11.5555 | 18.49% | 41.6095
78 | 0 | 0 | 0 | 2.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.7779 | 45.9617 | 0 | 113.7779 | 318.9029 | 25% | 0 | 0 | 11.5555 | 18.49% | 45.9617
79 | 0 | 0 | 0 | 2.2 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.0985 | 49.5896 | 0 | 122.0985 | 196.8044 | 15.43% | 0 | 0 | 11.5555 | 18.49% | 49.5896
80 | 97 | 16 | 10 | 2.4 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0295 | 50 | 0 | 123.0295 | 73.7749 | 5.784% | 0 | 0 | 11.5555 | 18.49% | 50
81 | 580 | 156 | 47 | 1.6 | 6.5 | 0 | 0 | 0 | 0 | 21.4856 | 0 | 0 | 21.4856 | 0 | 0 | 0 | 73.7749 | 28.5144 | 0 | 73.7749 | 0 | 0% | 0 | 0 | 11.5555 | 18.49% | 50
82 | 806 | 330 | 65 | 0.9 | 9 | 0 | 0 | 0 | 161.3843 | 45.1481 | 7.1054e-15 | 0 | 45.1481 | 0 | 0 | 0 | 0 | 0 | 161.3843 | 0 | 161.3843 | 12.65% | 0 | 4.7939 | 6.25 | 10% | 49.942
83 | 898 | 456 | 62 | 1 | 11.5 | 0 | 0 | 0 | 213.1395 | 57.9679 | 0.24697 | 8.6498 | 49.3181 | 0 | 0 | 0 | 0 | 0 | 213.1395 | 0 | 374.5238 | 29.36% | 8.6498 | 0 | 14.0656 | 22.5% | 49.3181
84 | 944 | 535 | 61 | 1.4 | 12.5 | 0 | 0 | 0 | 242.3517 | 47.5006 | 19.6179 | 0 | 47.5006 | 0 | 0 | 0 | 0 | 0 | 242.3517 | 0 | 616.8755 | 48.36% | 0 | 0 | 14.0656 | 22.5% | 47.5006
85 | 944 | 547 | 61 | 1.8 | 13.3 | 0 | 0 | 0 | 247.8327 | 70.2093 | 0 | 24.0652 | 46.1441 | 0 | 0 | 0 | 0 | 0 | 247.8327 | 0 | 864.7081 | 67.79% | 24.0652 | 0 | 35.81 | 57.3% | 46.1441
86 | 927 | 501 | 60 | 1.9 | 14 | 0 | 0 | 0 | 240.9636 | 68.1363 | 0 | 22.6217 | 45.5146 | 0 | 0 | 0 | 0 | 0 | 240.9636 | 0 | 1105.6717 | 86.68% | 22.6217 | 0 | 56.25 | 90% | 45.5146
87 | 883 | 397 | 53 | 2 | 14.7 | 0 | 0 | 0 | 110.6606 | 45.8698 | 14.5736 | 0 | 45.8698 | 0 | 0 | 0 | 0 | 0 | 110.6606 | 0 | 1216.3324 | 95.36% | 0 | 0 | 56.25 | 90% | 45.8698
88 | 761 | 243 | 44 | 2.8 | 14.3 | 0 | 0 | 0 | 0 | 45.9389 | 0 | 0 | 45.9389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.3324 | 95.36% | 0 | 2.6619 | 53.304 | 85.29% | 48.6008
89 | 407 | 72 | 23 | 2.9 | 12.2 | 0 | 0 | 0 | 59.1778 | 19.4176 | 0 | 0 | 19.4176 | 0 | 0 | 0 | 0 | 0 | 59.1778 | 0 | 1275.5102 | 100% | 0 | 25 | 25.6356 | 41.02% | 44.4176
90 | 0 | 1 | 1 | 2.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.2539 | 49.6495 | 0 | 122.2539 | 1153.2563 | 90.42% | 0 | 0 | 25.6356 | 41.02% | 49.6495
91 | 0 | 0 | 0 | 0.2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.4976 | 48.9072 | 0 | 120.4976 | 1032.7587 | 80.97% | 0 | 0 | 25.6356 | 41.02% | 48.9072
92 | 0 | 0 | 0 | 0.9 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.4361 | 46.2597 | 0 | 114.4361 | 918.3226 | 72% | 0 | 0 | 25.6356 | 41.02% | 46.2597
93 | 0 | 0 | 0 | 1.1 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.6767 | 42.8713 | 0 | 106.6767 | 811.6458 | 63.63% | 0 | 0 | 25.6356 | 41.02% | 42.8713
94 | 0 | 0 | 0 | 2.1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3262 | 39.6611 | 0 | 99.3262 | 712.3196 | 55.85% | 0 | 0 | 25.6356 | 41.02% | 39.6611
95 | 0 | 0 | 0 | 1.6 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8389 | 36.3841 | 0 | 91.8389 | 620.4807 | 48.65% | 0 | 0 | 25.6356 | 41.02% | 36.3841
96 | 0 | 0 | 0 | 1.6 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4118 | 34.0151 | 0 | 86.4118 | 534.0689 | 41.87% | 0 | 0 | 25.6356 | 41.02% | 34.0151
97 | 0 | 0 | 0 | 0.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5945 | 32.7715 | 0 | 83.5945 | 450.4745 | 35.32% | 0 | 0 | 25.6356 | 41.02% | 32.7715
98 | 0 | 0 | 0 | 0.3 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6755 | 32.3495 | 0 | 82.6755 | 367.799 | 28.84% | 0 | 0 | 25.6356 | 41.02% | 32.3495
99 | 0 | 0 | 0 | 0.9 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367.799 | 28.84% | 0 | 0 | 25.6356 | 41.02% | 0
100 | 0 | 0 | 0 | 1.8 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367.799 | 28.84% | 0 | 0 | 25.6356 | 41.02% | 0
101 | 0 | 0 | 0 | 1.4 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8521 | 35.0555 | 0 | 88.8521 | 278.9469 | 21.87% | 0 | 0 | 25.6356 | 41.02% | 35.0555
102 | 0 | 0 | 0 | 0.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.2392 | 25.1863 | 0 | 66.2392 | 212.7077 | 16.68% | 0 | 0 | 25.6356 | 41.02% | 25.1863
103 | 0 | 0 | 0 | 1.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4776 | 40.9661 | 0 | 102.4776 | 110.2301 | 8.642% | 0 | 0 | 25.6356 | 41.02% | 40.9661
104 | 156 | 18 | 8 | 1.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.2301 | 44.3712 | 0 | 110.2301 | 0 | 0% | 0 | 0 | 25.6356 | 41.02% | 44.3712
105 | 694 | 159 | 32 | 0.4 | 5.8 | 0 | 0 | 0 | 0 | 23.5382 | 0 | 0 | 23.5382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 17.5161 | 6.25 | 10% | 41.0542
106 | 871 | 329 | 43 | 0.7 | 10.8 | 0 | 0 | 0 | 175.9752 | 43.9116 | 1.4908 | 0 | 43.9116 | 0 | 0 | 0 | 0 | 0 | 175.9752 | 0 | 175.9752 | 13.8% | 0 | 0 | 6.25 | 10% | 43.9116
107 | 941 | 461 | 48 | 0.7 | 13.6 | 0 | 0 | 0 | 224.4422 | 43.5189 | 14.714 | 0 | 43.5189 | 0 | 0 | 0 | 0 | 0 | 224.4422 | 0 | 400.4174 | 31.39% | 0 | 0 | 6.25 | 10% | 43.5189
108 | 968 | 537 | 52 | 1.8 | 13.8 | 0 | 0 | 0 | 155.22 | 42.7641 | 25.2507 | 0 | 42.7641 | 0 | 0 | 0 | 0 | 0 | 155.22 | 0 | 555.6373 | 43.56% | 0 | 0 | 6.25 | 10% | 42.7641
109 | 977 | 553 | 52 | 2 | 14.4 | 0 | 0 | 0 | 0 | 44.592 | 26.8731 | 3.3321 | 41.2599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555.6373 | 43.56% | 3.3321 | 0 | 9.2607 | 14.82% | 41.2599
110 | 957 | 505 | 51 | 2.5 | 15.3 | 0 | 0 | 0 | 249.3813 | 65.2391 | 4.3869 | 25 | 40.2391 | 0 | 0 | 0 | 0 | 0 | 249.3813 | 0 | 805.0186 | 63.11% | 25 | 0 | 31.8497 | 50.96% | 40.2391
111 | 910 | 400 | 47 | 3.4 | 15.4 | 0 | 0 | 0 | 226.723 | 62.4778 | 0 | 22.3307 | 40.1472 | 0 | 0 | 0 | 0 | 0 | 226.723 | 0 | 1031.7416 | 80.89% | 22.3307 | 0 | 52.0268 | 83.24% | 40.1472
112 | 798 | 248 | 39 | 2.6 | 15.2 | 0 | 0 | 0 | 173.5676 | 47.1956 | 0 | 4.6739 | 42.5217 | 0 | 0 | 0 | 0 | 0 | 173.5676 | 0 | 1205.3092 | 94.5% | 4.6739 | 0 | 56.25 | 90% | 42.5217
113 | 463 | 77 | 21 | 2.9 | 13.1 | 0 | 0 | 0 | 70.201 | 21.0834 | 0 | 0 | 21.0834 | 0 | 0 | 0 | 0 | 0 | 70.201 | 0 | 1275.5102 | 100% | 0 | 22.0233 | 31.8761 | 51% | 43.1067
114 | 1 | 1 | 1 | 1.5 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.9895 | 43.8643 | 0 | 108.9895 | 1166.5207 | 91.46% | 0 | 0 | 31.8761 | 51% | 43.8643
115 | 0 | 0 | 0 | 0.7 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.9336 | 44.2946 | 0 | 109.9336 | 1056.5871 | 82.84% | 0 | 0 | 31.8761 | 51% | 44.2946
116 | 0 | 0 | 0 | 0.9 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9965 | 43.0147 | 0 | 106.9965 | 949.5907 | 74.45% | 0 | 0 | 31.8761 | 51% | 43.0147
117 | 0 | 0 | 0 | 0.9 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9309 | 40.7962 | 0 | 101.9309 | 847.6598 | 66.46% | 0 | 0 | 31.8761 | 51% | 40.7962
118 | 0 | 0 | 0 | 0.9 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9655 | 29.8928 | 0 | 76.9655 | 770.6943 | 60.42% | 0 | 7.93 | 23.0997 | 36.96% | 37.8228
119 | 0 | 0 | 0 | 1.1 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.642 | 34.5597 | 0 | 87.642 | 683.0523 | 53.55% | 0 | 0 | 23.0997 | 36.96% | 34.5597
120 | 0 | 0 | 0 | 1.8 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4441 | 32.2952 | 0 | 82.4441 | 600.6082 | 47.09% | 0 | 0 | 23.0997 | 36.96% | 32.2952
121 | 0 | 0 | 0 | 2.5 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.0486 | 20.3406 | 0 | 55.0486 | 545.5596 | 42.77% | 0 | 0 | 23.0997 | 36.96% | 20.3406
122 | 0 | 0 | 0 | 2.4 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7693 | 30.2577 | 0 | 77.7693 | 467.7903 | 36.67% | 0 | 0 | 23.0997 | 36.96% | 30.2577
123 | 0 | 0 | 0 | 2 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 13.0149 | 0 | 38.2653 | 429.525 | 33.67% | 0 | 0 | 23.0997 | 36.96% | 13.0149
124 | 0 | 0 | 0 | 2.5 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4461 | 30.5529 | 0 | 78.4461 | 351.0789 | 27.52% | 0 | 0 | 23.0997 | 36.96% | 30.5529
125 | 0 | 0 | 0 | 2.4 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9796 | 31.6573 | 0 | 80.9796 | 270.0993 | 21.18% | 0 | 0 | 23.0997 | 36.96% | 31.6573
126 | 0 | 0 | 0 | 1.3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5154 | 32.7603 | 0 | 83.5154 | 186.5839 | 14.63% | 0 | 0 | 23.0997 | 36.96% | 32.7603
127 | 0 | 0 | 0 | 1.2 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0029 | 35.5819 | 0 | 90.0029 | 96.581 | 7.572% | 0 | 0 | 23.0997 | 36.96% | 35.5819
128 | 164 | 18 | 8 | 1.5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.581 | 38.4662 | 0 | 96.581 | 0 | 0% | 0 | 0 | 23.0997 | 36.96% | 38.4662
129 | 717 | 161 | 31 | 0.8 | 8.9 | 0 | 0 | 0 | 0 | 24.3305 | 0 | 0 | 24.3305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 15.2248 | 6.25 | 10% | 39.5553
130 | 888 | 331 | 42 | 0.7 | 13.3 | 0 | 0 | 0 | 179.7973 | 39.0107 | 6.577 | 0 | 39.0107 | 0 | 0 | 0 | 0 | 0 | 179.7973 | 0 | 179.7973 | 14.1% | 0 | 0 | 6.25 | 10% | 39.0107
131 | 958 | 465 | 48 | 0.9 | 16.1 | 0 | 0 | 0 | 228.8617 | 38.5372 | 20.3446 | 0 | 38.5372 | 0 | 0 | 0 | 0 | 0 | 228.8617 | 0 | 408.6589 | 32.04% | 0 | 0 | 6.25 | 10% | 38.5372
132 | 989 | 544 | 51 | 1.5 | 17.1 | 0 | 0 | 0 | 160.4391 | 37.5818 | 30.2907 | 0 | 37.5818 | 0 | 0 | 0 | 0 | 0 | 160.4391 | 0 | 569.0981 | 44.62% | 0 | 0 | 6.25 | 10% | 37.5818
133 | 991 | 560 | 52 | 0.7 | 19 | 0 | 0 | 0 | 0 | 35.8354 | 32.7011 | 0 | 35.8354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.0981 | 44.62% | 0 | 0 | 6.25 | 10% | 35.8354
134 | 957 | 508 | 53 | 2 | 19.1 | 0 | 0 | 0 | 249.9369 | 58.3984 | 9.9306 | 23.3151 | 35.0833 | 0 | 0 | 0 | 0 | 0 | 249.9369 | 0 | 819.0349 | 64.21% | 23.3151 | 0 | 27.3166 | 43.71% | 35.0833
135 | 897 | 400 | 50 | 3.3 | 18.6 | 0 | 0 | 0 | 223.6088 | 60.4775 | 0.86937 | 25 | 35.4775 | 0 | 0 | 0 | 0 | 0 | 223.6088 | 0 | 1042.6438 | 81.74% | 25 | 0 | 49.9056 | 79.85% | 35.4775
136 | 771 | 246 | 42 | 3.3 | 17.6 | 0 | 0 | 0 | 167.2437 | 46.109 | 0 | 7.0216 | 39.0873 | 0 | 0 | 0 | 0 | 0 | 167.2437 | 0 | 1209.8875 | 94.86% | 7.0216 | 0 | 56.25 | 90% | 39.0873
137 | 432 | 76 | 23 | 1.5 | 15.1 | 0 | 0 | 0 | 65.6227 | 20.232 | 0 | 0 | 20.232 | 0 | 0 | 0 | 0 | 0 | 65.6227 | 0 | 1275.5102 | 100% | 0 | 21.2452 | 32.7372 | 52.38% | 41.4772
138 | 1 | 1 | 1 | 2.9 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.1057 | 42.9994 | 0 | 107.1057 | 1168.4045 | 91.6% | 0 | 0 | 32.7372 | 52.38% | 42.9994
139 | 0 | 0 | 0 | 1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.1935 | 43.5272 | 0 | 108.1935 | 1060.211 | 83.12% | 0 | 0 | 32.7372 | 52.38% | 43.5272
140 | 0 | 0 | 0 | 0.6 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.134 | 46.5668 | 0 | 115.134 | 945.077 | 74.09% | 3.942 | 0 | 36.2991 | 58.08% | 42.6248
141 | 0 | 0 | 0 | 0.7 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3772 | 39.6848 | 0 | 99.3772 | 845.6998 | 66.3% | 0 | 0 | 36.2991 | 58.08% | 39.6848
142 | 0 | 0 | 0 | 1.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1712 | 36.1014 | 0 | 91.1712 | 754.5286 | 59.16% | 0 | 0 | 36.2991 | 58.08% | 36.1014
143 | 0 | 0 | 0 | 1.7 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8046 | 33.3272 | 0 | 84.8046 | 669.724 | 52.51% | 0 | 0 | 36.2991 | 58.08% | 33.3272
144 | 0 | 0 | 0 | 0.6 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0549 | 31.681 | 0 | 81.0549 | 588.6691 | 46.15% | 0 | 0 | 36.2991 | 58.08% | 31.681
145 | 0 | 0 | 0 | 2.3 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.6691 | 46.15% | 0 | 0 | 36.2991 | 58.08% | 0
146 | 0 | 0 | 0 | 2.8 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588.6691 | 46.15% | 0 | 0 | 36.2991 | 58.08% | 0
147 | 0 | 0 | 0 | 1.5 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.2947 | 26.5504 | 0 | 69.2947 | 519.3743 | 40.72% | 0 | 0 | 36.2991 | 58.08% | 26.5504
148 | 0 | 0 | 0 | 1 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1054 | 34.7491 | 0 | 88.1054 | 431.2689 | 33.81% | 0 | 0 | 36.2991 | 58.08% | 34.7491
149 | 0 | 0 | 0 | 0.6 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8759 | 39.0066 | 0 | 97.8759 | 333.3929 | 26.14% | 0 | 0 | 36.2991 | 58.08% | 39.0066
150 | 0 | 0 | 0 | 0.9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.0866 | 42.1499 | 0 | 105.0866 | 228.3063 | 17.9% | 0 | 0 | 36.2991 | 58.08% | 42.1499
151 | 0 | 0 | 0 | 0.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.6784 | 45.0188 | 0 | 111.6784 | 116.6279 | 9.144% | 0 | 0 | 36.2991 | 58.08% | 45.0188
152 | 151 | 18 | 8 | 0.5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.6279 | 47.1914 | 0 | 116.6279 | 0 | 0% | 0 | 0 | 36.2991 | 58.08% | 47.1914
153 | 685 | 158 | 33 | 0.5 | 7.6 | 0 | 0 | 0 | 92.9611 | 23.061 | 0 | 0 | 23.061 | 0 | 0 | 0 | 0 | 0 | 92.9611 | 0 | 92.9611 | 7.288% | 0 | 24.7794 | 8.8749 | 14.2% | 47.8404
154 | 860 | 326 | 45 | 0.7 | 12 | 0 | 0 | 0 | 0 | 44.8252 | 0 | 0 | 44.8252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9611 | 7.288% | 0 | 2.3717 | 6.25 | 10% | 47.197
155 | 933 | 458 | 50 | 0.7 | 14.9 | 0 | 0 | 0 | 222.7026 | 57.6859 | 0 | 10.397 | 47.2889 | 0 | 0 | 0 | 0 | 0 | 222.7026 | 0 | 315.6637 | 24.75% | 10.397 | 0 | 15.6443 | 25.03% | 47.2889
156 | 963 | 537 | 53 | 1.5 | 16.2 | 0 | 0 | 0 | 81.4552 | 66.802 | 0 | 20.5618 | 46.2402 | 0 | 0 | 0 | 0 | 0 | 81.4552 | 0 | 397.1189 | 31.13% | 20.5618 | 0 | 34.2232 | 54.76% | 46.2402
157 | 966 | 553 | 55 | 1.6 | 16.3 | 0 | 0 | 0 | 254.7575 | 52.9909 | 17.0408 | 7.9344 | 45.0564 | 0 | 0 | 0 | 0 | 0 | 254.7575 | 0 | 651.8764 | 51.11% | 7.9344 | 0 | 41.3924 | 66.23% | 45.0564
158 | 939 | 504 | 55 | 1.4 | 17.4 | 0 | 0 | 0 | 245.4242 | 44.2236 | 22.7786 | 0 | 44.2236 | 0 | 0 | 0 | 0 | 0 | 245.4242 | 0 | 897.3006 | 70.35% | 0 | 0 | 41.3924 | 66.23% | 44.2236
159 | 875 | 397 | 52 | 3.8 | 16.9 | 0 | 0 | 0 | 217.4613 | 60.9664 | 0 | 16.4434 | 44.523 | 0 | 0 | 0 | 0 | 0 | 217.4613 | 0 | 1114.7619 | 87.4% | 16.4434 | 0 | 56.25 | 90% | 44.523
160 | 745 | 244 | 44 | 4 | 16.1 | 0 | 0 | 0 | 160.7483 | 45.4928 | 0 | 0 | 45.4928 | 0 | 0 | 0 | 0 | 0 | 160.7483 | 0 | 1275.5102 | 100% | 0 | 2.3727 | 53.6241 | 85.8% | 47.8655
161 | 410 | 76 | 24 | 4.4 | 14 | 0 | 0 | 0 | 0 | 19.8393 | 0 | 0 | 19.8393 | 0 | 0 | 0 | 47.4234 | 16.9517 | 0 | 47.4234 | 1228.0868 | 96.28% | 0 | 13.0675 | 39.1619 | 62.66% | 49.8584
162 | 1 | 1 | 1 | 3.5 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1167 | 50 | 0 | 123.1167 | 1104.9701 | 86.63% | 0 | 0 | 39.1619 | 62.66% | 50
163 | 0 | 0 | 0 | 1.7 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0085 | 50 | 0 | 123.0085 | 981.9616 | 76.99% | 0 | 0 | 39.1619 | 62.66% | 50
164 | 0 | 0 | 0 | 2 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.1801 | 47.0215 | 0 | 116.1801 | 865.7814 | 67.88% | 0 | 0 | 39.1619 | 62.66% | 47.0215
165 | 0 | 0 | 0 | 1.9 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8988 | 42.5356 | 0 | 105.8988 | 759.8826 | 59.57% | 0 | 0 | 39.1619 | 62.66% | 42.5356
166 | 0 | 0 | 0 | 1.1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3289 | 39.2266 | 0 | 98.3289 | 661.5537 | 51.87% | 0 | 0 | 39.1619 | 62.66% | 39.2266
167 | 0 | 0 | 0 | 2.2 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2802 | 30.9148 | 0 | 79.2802 | 582.2735 | 45.65% | 0 | 0 | 39.1619 | 62.66% | 30.9148
168 | 0 | 0 | 0 | 1.7 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.2735 | 45.65% | 0 | 0 | 39.1619 | 62.66% | 0
169 | 0 | 0 | 0 | 1.8 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.2735 | 45.65% | 0 | 0 | 39.1619 | 62.66% | 0
170 | 0 | 0 | 0 | 1.6 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.2735 | 45.65% | 0 | 0 | 39.1619 | 62.66% | 0
171 | 0 | 0 | 0 | 1.5 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582.2735 | 45.65% | 0 | 0 | 39.1619 | 62.66% | 0
172 | 0 | 0 | 0 | 2.2 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3518 | 39.2071 | 0 | 98.3518 | 483.9217 | 37.94% | 0 | 0 | 39.1619 | 62.66% | 39.2071
173 | 0 | 0 | 0 | 1.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.6291 | 46.3098 | 0 | 114.6291 | 369.2927 | 28.95% | 0 | 0 | 39.1619 | 62.66% | 46.3098
174 | 0 | 0 | 0 | 2.1 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1174 | 50 | 0 | 123.1174 | 246.1753 | 19.3% | 0 | 0 | 39.1619 | 62.66% | 50
175 | 0 | 0 | 0 | 2.7 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0801 | 50 | 0 | 123.0801 | 123.0952 | 9.651% | 0 | 0 | 39.1619 | 62.66% | 50
176 | 124 | 17 | 8 | 2.7 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0952 | 50 | 0 | 123.0952 | 0 | 0% | 0 | 0 | 39.1619 | 62.66% | 50
177 | 625 | 152 | 37 | 2.7 | 5.7 | 0 | 0 | 0 | 48.1647 | 21.8499 | 0 | 0 | 21.8499 | 0 | 0 | 0 | 0 | 0 | 48.1647 | 0 | 48.1647 | 3.776% | 0 | 25 | 11.4936 | 18.39% | 46.8499
178 | 818 | 320 | 51 | 2.3 | 9.3 | 0 | 0 | 0 | 0 | 45.2621 | 0 | 0 | 45.2621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.1647 | 3.776% | 0 | 4.7379 | 6.25 | 10% | 50
179 | 896 | 452 | 60 | 2.6 | 10.9 | 0 | 0 | 0 | 212.328 | 50.4025 | 9.1886 | 0.40255 | 50 | 0 | 0 | 0 | 0 | 0 | 212.328 | 0 | 260.4927 | 20.42% | 0.40255 | 0 | 6.6137 | 10.58% | 50
180 | 932 | 531 | 62 | 1.9 | 12 | 0 | 0 | 0 | 239.2942 | 67.3597 | 0 | 17.3597 | 50 | 0 | 0 | 0 | 0 | 0 | 239.2942 | 0 | 499.7869 | 39.18% | 17.3597 | 0 | 22.2992 | 35.68% | 50
181 | 946 | 549 | 61 | 1.2 | 13.3 | 0 | 0 | 0 | 249.5984 | 69.4015 | 0 | 19.8077 | 49.5938 | 0 | 0 | 0 | 0 | 0 | 249.5984 | 0 | 749.3853 | 58.75% | 19.8077 | 0 | 40.1966 | 64.31% | 49.5938
182 | 934 | 505 | 57 | 1 | 14.5 | 0 | 0 | 0 | 244.4933 | 66.8774 | 0 | 17.7668 | 49.1106 | 0 | 0 | 0 | 0 | 0 | 244.4933 | 0 | 993.8786 | 77.92% | 17.7668 | 0 | 56.25 | 90% | 49.1106
183 | 871 | 399 | 55 | 2.9 | 14.9 | 0 | 0 | 0 | 217.3065 | 49.4671 | 11.4899 | 0 | 49.4671 | 0 | 0 | 0 | 0 | 0 | 217.3065 | 0 | 1211.1851 | 94.96% | 0 | 0 | 56.25 | 90% | 49.4671
184 | 742 | 247 | 47 | 3.9 | 14 | 0 | 0 | 0 | 0 | 46.0264 | 0 | 0 | 46.0264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1211.1851 | 94.96% | 0 | 3.9735 | 51.8523 | 82.96% | 50
185 | 428 | 80 | 25 | 3.7 | 11.9 | 0 | 0 | 0 | 64.3251 | 20.8748 | 0 | 0 | 20.8748 | 0 | 0 | 0 | 0 | 0 | 64.3251 | 0 | 1275.5102 | 100% | 0 | 25 | 24.184 | 38.69% | 45.8748
186 | 1 | 1 | 1 | 2.3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0456 | 50 | 0 | 123.0456 | 1152.4646 | 90.35% | 0 | 0 | 24.184 | 38.69% | 50
187 | 0 | 0 | 0 | 1.7 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0121 | 50 | 0 | 123.0121 | 1029.4524 | 80.71% | 0 | 0 | 24.184 | 38.69% | 50
188 | 0 | 0 | 0 | 1 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.9569 | 49.5451 | 0 | 121.9569 | 907.4955 | 71.15% | 0 | 0 | 24.184 | 38.69% | 49.5451
189 | 0 | 0 | 0 | 1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.7359 | 44.6442 | 0 | 110.7359 | 796.7596 | 62.47% | 0 | 0 | 24.184 | 38.69% | 44.6442
190 | 0 | 0 | 0 | 1.3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.3981 | 41.0009 | 0 | 102.3981 | 694.3615 | 54.44% | 0 | 0 | 24.184 | 38.69% | 41.0009
191 | 0 | 0 | 0 | 1.3 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4303 | 33.5929 | 0 | 85.4303 | 608.9312 | 47.74% | 0 | 0 | 24.184 | 38.69% | 33.5929
192 | 0 | 0 | 0 | 1.4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 608.9312 | 47.74% | 0 | 0 | 24.184 | 38.69% | 0
193 | 0 | 0 | 0 | 1.1 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608.9312 | 47.74% | 0 | 0 | 24.184 | 38.69% | 0
194 | 0 | 0 | 0 | 2.3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608.9312 | 47.74% | 0 | 0 | 24.184 | 38.69% | 0
195 | 0 | 0 | 0 | 2.4 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608.9312 | 47.74% | 0 | 0 | 24.184 | 38.69% | 0
196 | 0 | 0 | 0 | 2.6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.271 | 41.3835 | 0 | 103.271 | 505.6602 | 39.64% | 1.5413 | 0 | 25.5767 | 40.92% | 39.8422
197 | 0 | 0 | 0 | 2.5 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9838 | 0 | 127.551 | 378.1092 | 29.64% | 5.2604 | 0 | 30.3297 | 48.53% | 46.7235
198 | 0 | 0 | 0 | 2.2 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0072 | 50 | 0 | 123.0072 | 255.102 | 20% | 0 | 0 | 30.3297 | 48.53% | 50
199 | 0 | 0 | 0 | 2.6 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9862 | 0 | 127.551 | 127.551 | 10% | 1.9862 | 0 | 32.1243 | 51.4% | 50
200 | 152 | 17 | 7 | 3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9855 | 0 | 127.551 | 0 | 0% | 1.9855 | 0 | 33.9183 | 54.27% | 50
201 | 686 | 157 | 31 | 2.8 | 9.4 | 0 | 0 | 0 | 0 | 23.2304 | 0 | 0 | 23.2304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 6.25 | 10% | 48.2304
202 | 867 | 327 | 42 | 0.7 | 14.1 | 0 | 0 | 0 | 0 | 44.4166 | 0 | 0 | 44.4166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 44.4166
203 | 933 | 458 | 48 | 1 | 15.7 | 0 | 0 | 0 | 222.9577 | 57.7915 | 0 | 7.7915 | 50 | 0 | 0 | 0 | 0 | 0 | 222.9577 | 0 | 222.9577 | 17.48% | 7.7915 | 0 | 13.2901 | 21.26% | 50
204 | 956 | 535 | 52 | 1.2 | 17.5 | 0 | 0 | 0 | 246.5856 | 49.9072 | 15.6121 | 0 | 49.9072 | 0 | 0 | 0 | 0 | 0 | 246.5856 | 0 | 469.5433 | 36.81% | 0 | 0 | 13.2901 | 21.26% | 49.9072
205 | 953 | 550 | 55 | 3.3 | 17.2 | 0 | 0 | 0 | 250.7124 | 71.1574 | 0 | 22.0886 | 49.0688 | 0 | 0 | 0 | 0 | 0 | 250.7124 | 0 | 720.2557 | 56.47% | 22.0886 | 0 | 33.2484 | 53.2% | 49.0688
206 | 926 | 502 | 55 | 3.7 | 17.2 | 0 | 0 | 0 | 240.9439 | 68.9238 | 0 | 20.1781 | 48.7457 | 0 | 0 | 0 | 0 | 0 | 240.9439 | 0 | 961.1996 | 75.36% | 20.1781 | 0 | 51.4806 | 82.37% | 48.7457
207 | 882 | 402 | 50 | 3.6 | 16.8 | 0 | 0 | 0 | 220.1041 | 54.4155 | 6.8493 | 5.2785 | 49.137 | 0 | 0 | 0 | 0 | 0 | 220.1041 | 0 | 1181.3036 | 92.61% | 5.2785 | 0 | 56.25 | 90% | 49.137
208 | 773 | 252 | 41 | 4 | 16 | 0 | 0 | 0 | 94.2066 | 46.8606 | 0 | 0 | 46.8606 | 0 | 0 | 0 | 0 | 0 | 94.2066 | 0 | 1275.5102 | 100% | 0 | 3.1394 | 52.7755 | 84.44% | 50
209 | 483 | 84 | 23 | 4 | 14.4 | 0 | 0 | 0 | 0 | 22.4418 | 0 | 0 | 22.4418 | 0 | 0 | 0 | 39.768 | 13.6168 | 0 | 39.768 | 1235.7422 | 96.88% | 0 | 13.9413 | 37.3462 | 59.75% | 50
210 | 1 | 1 | 1 | 1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1679 | 50 | 0 | 123.1679 | 1112.5743 | 87.23% | 0 | 0 | 37.3462 | 59.75% | 50
211 | 0 | 0 | 0 | 0.4 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0573 | 50 | 0 | 123.0573 | 989.517 | 77.58% | 0 | 0 | 37.3462 | 59.75% | 50
212 | 0 | 0 | 0 | 1.8 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.7387 | 49.0005 | 0 | 120.7387 | 868.7783 | 68.11% | 0 | 0 | 37.3462 | 59.75% | 49.0005
213 | 0 | 0 | 0 | 1.2 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.7832 | 42.48 | 0 | 105.7832 | 762.995 | 59.82% | 0 | 0 | 37.3462 | 59.75% | 42.48
214 | 0 | 0 | 0 | 1.6 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1547 | 40.4536 | 0 | 101.1547 | 661.8403 | 51.89% | 0 | 0 | 37.3462 | 59.75% | 40.4536
215 | 0 | 0 | 0 | 2.4 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 13.0113 | 0 | 38.2653 | 623.575 | 48.89% | 0 | 0 | 37.3462 | 59.75% | 13.0113
216 | 0 | 0 | 0 | 1.7 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 13.015 | 0 | 38.2653 | 585.3097 | 45.89% | 0 | 0 | 37.3462 | 59.75% | 13.015
217 | 0 | 0 | 0 | 1.8 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.3097 | 45.89% | 0 | 0 | 37.3462 | 59.75% | 0
218 | 0 | 0 | 0 | 3.1 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.3097 | 45.89% | 0 | 0 | 37.3462 | 59.75% | 0
219 | 0 | 0 | 0 | 2.8 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.3097 | 45.89% | 0 | 0 | 37.3462 | 59.75% | 0
220 | 0 | 0 | 0 | 2.3 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0566 | 39.9856 | 0 | 100.0566 | 485.2531 | 38.04% | 0 | 0 | 37.3462 | 59.75% | 39.9856
221 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.1737 | 47.0146 | 0 | 116.1737 | 369.0794 | 28.94% | 0 | 0 | 37.3462 | 59.75% | 47.0146
222 | 0 | 0 | 0 | 1.2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0325 | 50 | 0 | 123.0325 | 246.0469 | 19.29% | 0 | 0 | 37.3462 | 59.75% | 50
223 | 0 | 0 | 0 | 3.1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0144 | 50 | 0 | 123.0144 | 123.0325 | 9.646% | 0 | 0 | 37.3462 | 59.75% | 50
224 | 154 | 18 | 8 | 2.1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0325 | 50 | 0 | 123.0325 | 0 | 0% | 0 | 0 | 37.3462 | 59.75% | 50
225 | 690 | 159 | 32 | 1.8 | 8.2 | 0 | 0 | 0 | 93.148 | 23.3037 | 0 | 0 | 23.3037 | 0 | 0 | 0 | 0 | 0 | 93.148 | 0 | 93.148 | 7.303% | 0 | 25 | 9.6778 | 15.48% | 48.3037
226 | 869 | 330 | 44 | 3.7 | 10.2 | 0 | 0 | 0 | 20.5118 | 46.9027 | 0 | 0 | 46.9027 | 0 | 0 | 0 | 0 | 0 | 20.5118 | 0 | 113.6599 | 8.911% | 0 | 3.0972 | 6.25 | 10% | 50
227 | 932 | 461 | 51 | 4.9 | 11.3 | 0 | 0 | 0 | 220.1486 | 50 | 11.8269 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 220.1486 | 0 | 333.8085 | 26.17% | 0 | 0 | 6.25 | 10% | 50
228 | 956 | 539 | 55 | 5.1 | 12 | 0 | 0 | 0 | 243.9297 | 70.7155 | 0 | 20.7155 | 50 | 0 | 0 | 0 | 0 | 0 | 243.9297 | 0 | 577.7382 | 45.29% | 20.7155 | 0 | 24.9677 | 39.95% | 50
229 | 944 | 554 | 62 | 5.7 | 12.1 | 0 | 0 | 0 | 246.1644 | 62.5492 | 9.4508 | 12.6852 | 49.864 | 0 | 0 | 0 | 0 | 0 | 246.1644 | 0 | 823.9026 | 64.59% | 12.6852 | 0 | 36.4295 | 58.29% | 49.864
230 | 922 | 509 | 61 | 5.3 | 11.9 | 0 | 0 | 0 | 238.5445 | 71.4504 | 0 | 21.936 | 49.5144 | 0 | 0 | 0 | 0 | 0 | 238.5445 | 0 | 1062.4472 | 83.3% | 21.936 | 0 | 56.25 | 90% | 49.5144
231 | 861 | 404 | 59 | 5.3 | 11.8 | 0 | 0 | 0 | 213.0631 | 49.988 | 12.7414 | 0 | 49.988 | 0 | 0 | 0 | 0 | 0 | 213.0631 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 49.988
232 | 725 | 253 | 52 | 6 | 10.7 | 0 | 0 | 0 | 0 | 47.2227 | 0 | 0 | 47.2227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 2.7773 | 53.1763 | 85.08% | 50
233 | 400 | 85 | 31 | 5.7 | 9 | 0 | 0 | 0 | 0 | 20.9374 | 0 | 0 | 20.9374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 25.5079 | 40.81% | 45.9374
234 | 1 | 2 | 1 | 3.9 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0021 | 50 | 0 | 123.0021 | 1152.5081 | 90.36% | 0 | 0 | 25.5079 | 40.81% | 50
235 | 0 | 0 | 0 | 2.7 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0001 | 50 | 0 | 123.0001 | 1029.508 | 80.71% | 0 | 0 | 25.5079 | 40.81% | 50
236 | 0 | 0 | 0 | 2.2 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0001 | 50 | 0 | 123.0001 | 906.508 | 71.07% | 0 | 0 | 25.5079 | 40.81% | 50
237 | 0 | 0 | 0 | 1.5 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1433 | 45.243 | 0 | 112.1433 | 794.3647 | 62.28% | 0 | 0 | 25.5079 | 40.81% | 45.243
238 | 0 | 0 | 0 | 1.2 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.1238 | 43.0365 | 0 | 107.1238 | 687.2409 | 53.88% | 1.583 | 0 | 26.9383 | 43.1% | 41.4535
239 | 0 | 0 | 0 | 1.7 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6011 | 38.4537 | 0 | 96.6011 | 590.6397 | 46.31% | 0 | 0 | 26.9383 | 43.1% | 38.4537
240 | 0 | 0 | 0 | 2.3 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590.6397 | 46.31% | 0 | 0 | 26.9383 | 43.1% | 0
241 | 0 | 0 | 0 | 3.1 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590.6397 | 46.31% | 0 | 0 | 26.9383 | 43.1% | 0
242 | 0 | 0 | 0 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590.6397 | 46.31% | 0 | 0 | 26.9383 | 43.1% | 0
243 | 0 | 0 | 0 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590.6397 | 46.31% | 0 | 0 | 26.9383 | 43.1% | 0
244 | 0 | 0 | 0 | 1.9 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5337 | 40.9758 | 0 | 102.5337 | 488.106 | 38.27% | 0 | 0 | 26.9383 | 43.1% | 40.9758
245 | 0 | 0 | 0 | 2.6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.4098 | 47.9073 | 0 | 118.4098 | 369.6962 | 28.98% | 0 | 0 | 26.9383 | 43.1% | 47.9073
246 | 0 | 0 | 0 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2376 | 50 | 0 | 123.2376 | 246.4587 | 19.32% | 0 | 0 | 26.9383 | 43.1% | 50
247 | 0 | 0 | 0 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2293 | 50 | 0 | 123.2293 | 123.2293 | 9.661% | 0 | 0 | 26.9383 | 43.1% | 50
248 | 119 | 17 | 9 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2293 | 50 | 0 | 123.2293 | 0 | 0% | 0 | 0 | 26.9383 | 43.1% | 50
249 | 620 | 154 | 38 | 2.3 | 3.9 | 0 | 0 | 0 | 0 | 21.7291 | 0 | 0 | 21.7291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 18.6931 | 6.25 | 10% | 40.4222
250 | 809 | 323 | 55 | 1.1 | 7.1 | 0 | 0 | 0 | 0 | 44.6804 | 0 | 0 | 44.6804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 44.6804
251 | 902 | 460 | 61 | 0.6 | 9.5 | 0 | 0 | 0 | 215.7027 | 50 | 7.9152 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 215.7027 | 0 | 215.7027 | 16.91% | 0 | 0 | 6.25 | 10% | 50
252 | 930 | 538 | 65 | 1.1 | 9.8 | 0 | 0 | 0 | 239.735 | 66.79 | 0 | 16.7901 | 50 | 0 | 0 | 0 | 0 | 0 | 239.735 | 0 | 455.4378 | 35.71% | 16.7901 | 0 | 21.4208 | 34.27% | 50
253 | 945 | 559 | 65 | 1.6 | 10.5 | 0 | 0 | 0 | 249.8667 | 57.1981 | 14.0036 | 7.1981 | 50 | 0 | 0 | 0 | 0 | 0 | 249.8667 | 0 | 705.3045 | 55.3% | 7.1981 | 0 | 27.9247 | 44.68% | 50
254 | 922 | 514 | 65 | 2 | 11.2 | 0 | 0 | 0 | 241.4392 | 69.4632 | 0 | 19.6257 | 49.8375 | 0 | 0 | 0 | 0 | 0 | 241.4392 | 0 | 946.7437 | 74.22% | 19.6257 | 0 | 45.6577 | 73.05% | 49.8375
255 | 843 | 406 | 66 | 3.6 | 11.3 | 0 | 0 | 0 | 170.903 | 61.7229 | 0 | 11.7229 | 50 | 0 | 0 | 0 | 0 | 0 | 170.903 | 0 | 1117.6467 | 87.62% | 11.7229 | 0 | 56.25 | 90% | 50
256 | 726 | 258 | 55 | 4.2 | 10.6 | 0 | 0 | 0 | 157.8635 | 47.3075 | 0 | 0 | 47.3075 | 0 | 0 | 0 | 0 | 0 | 157.8635 | 0 | 1275.5102 | 100% | 0 | 2.6926 | 53.2701 | 85.23% | 50
257 | 422 | 87 | 30 | 3.6 | 9.2 | 0 | 0 | 0 | 0 | 21.5908 | 0 | 0 | 21.5908 | 0 | 0 | 0 | 73.5647 | 28.4092 | 0 | 73.5647 | 1201.9455 | 94.23% | 0 | 0 | 53.2701 | 85.23% | 50
258 | 1 | 2 | 2 | 2.3 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9993 | 50 | 0 | 122.9993 | 1078.9462 | 84.59% | 0 | 0 | 53.2701 | 85.23% | 50
259 | 0 | 0 | 0 | 2.8 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0032 | 50 | 0 | 123.0032 | 955.943 | 74.95% | 0 | 0 | 53.2701 | 85.23% | 50
260 | 0 | 0 | 0 | 1.3 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.1529 | 49.6175 | 0 | 122.1529 | 833.79 | 65.37% | 0 | 0 | 53.2701 | 85.23% | 49.6175
261 | 0 | 0 | 0 | 0.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8267 | 45.5258 | 0 | 112.8267 | 720.9634 | 56.52% | 0 | 0 | 53.2701 | 85.23% | 45.5258
262 | 0 | 0 | 0 | 1.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8151 | 42.434 | 0 | 105.8151 | 615.1483 | 48.23% | 0 | 0 | 53.2701 | 85.23% | 42.434
263 | 0 | 0 | 0 | 1.3 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0841 | 39.0623 | 0 | 98.0841 | 517.0642 | 40.54% | 0 | 0 | 53.2701 | 85.23% | 39.0623
264 | 0 | 0 | 0 | 0.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2419 | 36.5067 | 0 | 92.2419 | 424.8224 | 33.31% | 0 | 0 | 53.2701 | 85.23% | 36.5067
265 | 0 | 0 | 0 | 2.2 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424.8224 | 33.31% | 0 | 0 | 53.2701 | 85.23% | 0
266 | 0 | 0 | 0 | 1.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424.8224 | 33.31% | 0 | 0 | 53.2701 | 85.23% | 0
267 | 0 | 0 | 0 | 0.9 | -0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424.8224 | 33.31% | 0 | 0 | 53.2701 | 85.23% | 0
268 | 0 | 0 | 0 | 0.8 | -1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 424.8224 | 33.31% | 0 | 15.2941 | 36.3435 | 58.15% | 15.2941
269 | 0 | 0 | 0 | 0.5 | -0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2628 | 37.7685 | 0 | 95.2628 | 329.5596 | 25.84% | 0 | 0 | 36.3435 | 58.15% | 37.7685
270 | 0 | 0 | 0 | 1.1 | -0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.578 | 40.5371 | 0 | 101.578 | 227.9815 | 17.87% | 0 | 0 | 36.3435 | 58.15% | 40.5371
271 | 0 | 0 | 0 | 0.5 | -0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.0919 | 44.2198 | 0 | 110.0919 | 117.8896 | 9.243% | 0 | 0.31578 | 35.9941 | 57.59% | 44.5356
272 | 138 | 18 | 9 | 1 | -0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.8896 | 47.6371 | 0 | 117.8896 | 0 | 0% | 0 | 0 | 35.9941 | 57.59% | 47.6371
273 | 657 | 158 | 35 | 1 | 3.6 | 0 | 0 | 0 | 88.5509 | 22.6056 | 0 | 0 | 22.6056 | 0 | 0 | 0 | 0 | 0 | 88.5509 | 0 | 88.5509 | 6.942% | 0 | 25 | 8.3257 | 13.32% | 47.6056
274 | 840 | 328 | 48 | 1 | 7.1 | 0 | 0 | 0 | 0 | 45.0401 | 0 | 0 | 45.0401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5509 | 6.942% | 0 | 1.8755 | 6.25 | 10% | 46.9157
275 | 924 | 464 | 53 | 0.7 | 10 | 0 | 0 | 0 | 221.6067 | 46.5452 | 11.8604 | 0 | 46.5452 | 0 | 0 | 0 | 0 | 0 | 221.6067 | 0 | 310.1576 | 24.32% | 0 | 0 | 6.25 | 10% | 46.5452
276 | 961 | 547 | 55 | 1.3 | 11.1 | 0 | 0 | 0 | 248.5322 | 50.8638 | 16.9149 | 5.3367 | 45.5272 | 0 | 0 | 0 | 0 | 0 | 248.5322 | 0 | 558.6898 | 43.8% | 5.3367 | 0 | 11.072 | 17.72% | 45.5272
277 | 963 | 564 | 57 | 1.1 | 11.9 | 0 | 0 | 0 | 255.4997 | 68.8838 | 1.4583 | 25 | 43.8838 | 0 | 0 | 0 | 0 | 0 | 255.4997 | 0 | 814.1895 | 63.83% | 25 | 0 | 33.661 | 53.86% | 43.8838
278 | 943 | 519 | 56 | 1.6 | 12.6 | 0 | 0 | 0 | 247.9965 | 67.6471 | 1.454 | 25 | 42.6471 | 0 | 0 | 0 | 0 | 0 | 247.9965 | 0 | 1062.186 | 83.28% | 25 | 0 | 56.25 | 90% | 42.6471
279 | 884 | 414 | 53 | 2.4 | 13.1 | 0 | 0 | 0 | 213.3242 | 42.6916 | 19.1475 | 0 | 42.6916 | 0 | 0 | 0 | 0 | 0 | 213.3242 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 42.6916
280 | 765 | 263 | 46 | 3.7 | 11.9 | 0 | 0 | 0 | 0 | 45.8809 | 1.9038 | 0 | 45.8809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 45.8809
281 | 471 | 91 | 27 | 3.7 | 10.3 | 0 | 0 | 0 | 0 | 23.3069 | 0 | 0 | 23.3069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 24.3218 | 29.3322 | 46.93% | 47.6287
282 | 2 | 2 | 2 | 2.4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.4406 | 48.4435 | 0 | 119.4406 | 1156.0696 | 90.64% | 0 | 0 | 29.3322 | 46.93% | 48.4435
283 | 0 | 0 | 0 | 1.1 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.1778 | 48.3293 | 0 | 119.1778 | 1036.8918 | 81.29% | 0 | 0 | 29.3322 | 46.93% | 48.3293
284 | 0 | 0 | 0 | 0.7 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.6533 | 46.3461 | 0 | 114.6533 | 922.2385 | 72.3% | 0 | 0 | 29.3322 | 46.93% | 46.3461
285 | 0 | 0 | 0 | 0.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.4168 | 43.1749 | 0 | 107.4168 | 814.8217 | 63.88% | 0 | 0 | 29.3322 | 46.93% | 43.1749
286 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6238 | 39.3311 | 0 | 98.6238 | 716.1979 | 56.15% | 0 | 0 | 29.3322 | 46.93% | 39.3311
287 | 0 | 0 | 0 | 0.5 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4599 | 36.1905 | 0 | 91.4599 | 624.738 | 48.98% | 0 | 0 | 29.3322 | 46.93% | 36.1905
288 | 0 | 0 | 0 | 1.1 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5138 | 34.036 | 0 | 86.5138 | 538.2242 | 42.2% | 0 | 0 | 29.3322 | 46.93% | 34.036
289 | 0 | 0 | 0 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9328 | 32.8773 | 0 | 83.9328 | 454.2914 | 35.62% | 0 | 0 | 29.3322 | 46.93% | 32.8773
290 | 0 | 0 | 0 | 0.3 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454.2914 | 35.62% | 0 | 0 | 29.3322 | 46.93% | 0
291 | 0 | 0 | 0 | 1.2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454.2914 | 35.62% | 0 | 0 | 29.3322 | 46.93% | 0
292 | 0 | 0 | 0 | 0.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.213 | 30.3792 | 0 | 78.213 | 376.0784 | 29.48% | 0 | 0 | 29.3322 | 46.93% | 30.3792
293 | 0 | 0 | 0 | 0.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8992 | 34.1767 | 0 | 86.8992 | 289.1792 | 22.67% | 0 | 0 | 29.3322 | 46.93% | 34.1767
294 | 0 | 0 | 0 | 0.5 | -0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0451 | 34.6407 | 0 | 88.0451 | 201.1341 | 15.77% | 0 | 0.82421 | 28.4201 | 45.47% | 35.4649
295 | 0 | 0 | 0 | 0.4 | -0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4789 | 38.3144 | 0 | 96.4789 | 104.6552 | 8.205% | 0 | 0 | 28.4201 | 45.47% | 38.3144
296 | 159 | 19 | 8 | 0.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6552 | 41.9089 | 0 | 104.6552 | 0 | 0% | 0 | 0 | 28.4201 | 45.47% | 41.9089
297 | 696 | 163 | 32 | 0.5 | 5 | 0 | 0 | 0 | 85.2853 | 23.4019 | 0 | 0 | 23.4019 | 0 | 0 | 0 | 0 | 0 | 85.2853 | 0 | 85.2853 | 6.686% | 0 | 20.032 | 6.25 | 10% | 43.4339
298 | 873 | 335 | 43 | 1.1 | 9.4 | 0 | 0 | 0 | 177.34 | 42.934 | 2.7692 | 0 | 42.934 | 0 | 0 | 0 | 0 | 0 | 177.34 | 0 | 262.6253 | 20.59% | 0 | 0 | 6.25 | 10% | 42.934
299 | 947 | 472 | 49 | 1.8 | 11.7 | 0 | 0 | 0 | 0 | 43.0913 | 17.2908 | 0 | 43.0913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.6253 | 20.59% | 0 | 0 | 6.25 | 10% | 43.0913
300 | 978 | 555 | 52 | 2.6 | 13.6 | 0 | 0 | 0 | 0 | 42.8462 | 26.8457 | 0 | 42.8462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.6253 | 20.59% | 0 | 0 | 6.25 | 10% | 42.8462
301 | 981 | 573 | 53 | 4.1 | 14.5 | 0 | 0 | 0 | 258.9565 | 42.3388 | 29.6612 | 1.2975 | 41.0413 | 0 | 0 | 0 | 0 | 0 | 258.9565 | 0 | 521.5818 | 40.89% | 1.2975 | 0 | 7.4224 | 11.88% | 41.0413
302 | 962 | 529 | 53 | 4.2 | 15.3 | 0 | 0 | 0 | 251.962 | 64.8645 | 7.1355 | 25 | 39.8645 | 0 | 0 | 0 | 0 | 0 | 251.962 | 0 | 773.5438 | 60.65% | 25 | 0 | 30.0114 | 48.02% | 39.8645
303 | 914 | 425 | 49 | 3.6 | 15.8 | 0 | 0 | 0 | 230.0922 | 63.624 | 0 | 23.6077 | 40.0163 | 0 | 0 | 0 | 0 | 0 | 230.0922 | 0 | 1003.636 | 78.69% | 23.6077 | 0 | 51.3424 | 82.15% | 40.0163
304 | 813 | 274 | 41 | 3.3 | 16.1 | 0 | 0 | 0 | 181.2163 | 49.0994 | 0 | 5.4314 | 43.6679 | 0 | 0 | 0 | 0 | 0 | 181.2163 | 0 | 1184.8523 | 92.89% | 5.4314 | 0 | 56.25 | 90% | 43.6679
305 | 548 | 99 | 25 | 3.6 | 14.1 | 0 | 0 | 0 | 90.6579 | 25.6839 | 0 | 0 | 25.6839 | 0 | 0 | 0 | 0 | 0 | 90.6579 | 0 | 1275.5102 | 100% | 0 | 20.9351 | 33.0804 | 52.93% | 46.619
306 | 6 | 2 | 2 | 2.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2398 | 39.1603 | 0 | 98.2398 | 1177.2704 | 92.3% | 0 | 9.045 | 23.07 | 36.91% | 48.2053
307 | 0 | 0 | 0 | 0.2 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.7306 | 48.1287 | 0 | 118.7306 | 1058.5397 | 82.99% | 0 | 0 | 23.07 | 36.91% | 48.1287
308 | 0 | 0 | 0 | 0.9 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.5066 | 46.2931 | 0 | 114.5066 | 944.0331 | 74.01% | 0 | 0 | 23.07 | 36.91% | 46.2931
309 | 0 | 0 | 0 | 1 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5782 | 42.3936 | 0 | 105.5782 | 838.4549 | 65.73% | 0 | 0 | 23.07 | 36.91% | 42.3936
310 | 0 | 0 | 0 | 1.9 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9314 | 38.6208 | 0 | 96.9314 | 741.5236 | 58.14% | 0 | 0 | 23.07 | 36.91% | 38.6208
311 | 0 | 0 | 0 | 2.7 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8397 | 35.5248 | 0 | 89.8397 | 651.6839 | 51.09% | 0 | 0 | 23.07 | 36.91% | 35.5248
312 | 0 | 0 | 0 | 2.9 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 651.6839 | 51.09% | 0 | 8.7827 | 13.3499 | 21.36% | 8.7827
313 | 0 | 0 | 0 | 2.4 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 651.6839 | 51.09% | 0 | 0 | 13.3499 | 21.36% | 0
314 | 0 | 0 | 0 | 1.4 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 651.6839 | 51.09% | 0 | 0 | 13.3499 | 21.36% | 0
315 | 0 | 0 | 0 | 1.7 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 651.6839 | 51.09% | 0 | 0 | 13.3499 | 21.36% | 0
316 | 0 | 0 | 0 | 2.8 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.7308 | 38.969 | 0 | 97.7308 | 553.9531 | 43.43% | 0 | 0 | 13.3499 | 21.36% | 38.969
317 | 0 | 0 | 0 | 2.8 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.2292 | 46.172 | 0 | 114.2292 | 439.724 | 34.47% | 0 | 0 | 13.3499 | 21.36% | 46.172
318 | 0 | 0 | 0 | 3.4 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9996 | 50 | 0 | 122.9996 | 316.7244 | 24.83% | 0 | 0 | 13.3499 | 21.36% | 50
319 | 0 | 0 | 0 | 0.9 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0357 | 50 | 0 | 123.0357 | 193.6887 | 15.19% | 0 | 0 | 13.3499 | 21.36% | 50
320 | 159 | 19 | 8 | 1.2 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0057 | 50 | 0 | 123.0057 | 70.683 | 5.542% | 0 | 0 | 13.3499 | 21.36% | 50
321 | 680 | 159 | 31 | 2 | 9.8 | 0 | 0 | 0 | 0 | 22.8542 | 0 | 0 | 22.8542 | 0 | 0 | 0 | 70.683 | 27.1458 | 0 | 70.683 | 0 | 0% | 0 | 0 | 13.3499 | 21.36% | 50
322 | 854 | 328 | 42 | 0.7 | 14.7 | 0 | 0 | 0 | 173.5501 | 43.5848 | 0 | 0 | 43.5848 | 0 | 0 | 0 | 0 | 0 | 173.5501 | 0 | 173.5501 | 13.61% | 0 | 6.4152 | 6.25 | 10% | 50
323 | 924 | 462 | 48 | 1.4 | 16.2 | 0 | 0 | 0 | 221.9015 | 57.7009 | 0 | 7.7009 | 50 | 0 | 0 | 0 | 0 | 0 | 221.9015 | 0 | 395.4516 | 31% | 7.7009 | 0 | 13.2082 | 21.13% | 50
324 | 951 | 542 | 51 | 2.1 | 17.5 | 0 | 0 | 0 | 245.8091 | 66.5507 | 0 | 16.5766 | 49.974 | 0 | 0 | 0 | 0 | 0 | 245.8091 | 0 | 641.2607 | 50.27% | 16.5766 | 0 | 28.1862 | 45.1% | 49.974
325 | 957 | 561 | 52 | 2.3 | 18.2 | 0 | 0 | 0 | 253.8284 | 49.0172 | 21.0376 | 0 | 49.0172 | 0 | 0 | 0 | 0 | 0 | 253.8284 | 0 | 895.0891 | 70.17% | 0 | 0 | 28.1862 | 45.1% | 49.0172
326 | 934 | 517 | 53 | 3 | 18.6 | 0 | 0 | 0 | 206.7441 | 67.2441 | 1.4266 | 18.7756 | 48.4685 | 0 | 0 | 0 | 0 | 0 | 206.7441 | 0 | 1101.8332 | 86.38% | 18.7756 | 0 | 45.1511 | 72.24% | 48.4685
327 | 885 | 415 | 49 | 2.9 | 18.9 | 0 | 0 | 0 | 0 | 60.8704 | 0 | 12.2835 | 48.5869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101.8332 | 86.38% | 12.2835 | 0 | 56.25 | 90% | 48.5869
328 | 779 | 267 | 42 | 3 | 18.2 | 0 | 0 | 0 | 173.677 | 47.0498 | 3.7389e-11 | 0 | 47.0498 | 0 | 0 | 0 | 1.0582e-10 | 4.1138e-11 | 173.677 | 1.0582e-10 | 1275.5102 | 100% | 0 | 2.9502 | 52.9849 | 84.78% | 50
329 | 519 | 97 | 25 | 2.4 | 16.2 | 0 | 0 | 0 | 1.0552e-10 | 24.2512 | 0 | 0 | 24.2512 | 0 | 0 | 0 | 8.6235e-11 | 3.2754e-11 | 1.0552e-10 | 8.6235e-11 | 1275.5102 | 100% | 0 | 25 | 25.3166 | 40.51% | 49.2512
330 | 10 | 2 | 2 | 1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.3075 | 50 | 0 | 123.3075 | 1152.2027 | 90.33% | 0 | 0 | 25.3166 | 40.51% | 50
331 | 0 | 0 | 0 | 1.5 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1412 | 50 | 0 | 123.1412 | 1029.0615 | 80.68% | 0 | 0 | 25.3166 | 40.51% | 50
332 | 0 | 0 | 0 | 1.6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5115 | 48.864 | 0 | 120.5115 | 908.55 | 71.23% | 0 | 0 | 25.3166 | 40.51% | 48.864
333 | 0 | 0 | 0 | 2 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.8367 | 48.5855 | 0 | 119.8367 | 788.7133 | 61.84% | 4.504 | 0 | 29.3863 | 47.02% | 44.0815
334 | 0 | 0 | 0 | 3 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.7133 | 61.84% | 0 | 0 | 29.3863 | 47.02% | 0
335 | 0 | 0 | 0 | 2.3 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.7133 | 61.84% | 0 | 0 | 29.3863 | 47.02% | 0
336 | 0 | 0 | 0 | 2 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.7133 | 61.84% | 0 | 0 | 29.3863 | 47.02% | 0
337 | 0 | 0 | 0 | 2.7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.7133 | 61.84% | 0 | 0 | 29.3863 | 47.02% | 0
338 | 0 | 0 | 0 | 3 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.7133 | 61.84% | 0 | 0 | 29.3863 | 47.02% | 0
339 | 0 | 0 | 0 | 2.7 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.7133 | 61.84% | 0 | 0 | 29.3863 | 47.02% | 0
340 | 0 | 0 | 0 | 2.8 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 788.7133 | 61.84% | 0 | 20.905 | 6.25 | 10% | 20.905
341 | 0 | 0 | 0 | 2.8 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.9934 | 50.8571 | 0 | 124.9934 | 663.7199 | 52.04% | 3.9247 | 0 | 9.7962 | 15.67% | 46.9324
342 | 0 | 0 | 0 | 2.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9757 | 0 | 127.551 | 536.1689 | 42.04% | 1.9757 | 0 | 11.5814 | 18.53% | 50
343 | 0 | 0 | 0 | 2.8 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9809 | 0 | 127.551 | 408.6179 | 32.04% | 1.9809 | 0 | 13.3713 | 21.39% | 50
344 | 39 | 17 | 15 | 2.6 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9862 | 0 | 127.551 | 281.0669 | 22.04% | 1.9862 | 0 | 15.166 | 24.27% | 50
345 | 274 | 129 | 71 | 2 | 8.5 | 0 | 0 | 0 | 0 | 15.7714 | 0 | 0 | 15.7714 | 0 | 0 | 0 | 86.8868 | 34.2285 | 0 | 86.8868 | 194.1801 | 15.22% | 0 | 0 | 15.166 | 24.27% | 50
346 | 703 | 315 | 75 | 2.8 | 11.4 | 0 | 0 | 0 | 138.8388 | 41.9439 | 0 | 0 | 41.9439 | 0 | 0 | 0 | 0 | 0 | 138.8388 | 0 | 333.019 | 26.11% | 0 | 8.0561 | 6.25 | 10% | 50
347 | 715 | 435 | 110 | 4.6 | 13.6 | 0 | 0 | 0 | 165.9812 | 54.8488 | 0 | 4.8488 | 50 | 0 | 0 | 0 | 0 | 0 | 165.9812 | 0 | 499.0002 | 39.12% | 4.8488 | 0 | 10.6312 | 17.01% | 50
348 | 907 | 564 | 92 | 5.2 | 14.7 | 0 | 0 | 0 | 231.2967 | 67.5859 | 3.4727 | 17.9781 | 49.6077 | 0 | 0 | 0 | 0 | 0 | 231.2967 | 0 | 730.2969 | 57.26% | 17.9781 | 0 | 26.8755 | 43% | 49.6077
349 | 718 | 504 | 117 | 4.9 | 14.7 | 0 | 0 | 0 | 184.1529 | 64.0713 | 0 | 15.0847 | 48.9866 | 0 | 0 | 0 | 0 | 0 | 184.1529 | 0 | 914.4497 | 71.69% | 15.0847 | 0 | 40.5054 | 64.81% | 48.9866
350 | 701 | 520 | 166 | 4.8 | 15.2 | 0 | 0 | 0 | 178.3292 | 66.0078 | 0 | 17.4251 | 48.5827 | 0 | 0 | 0 | 0 | 0 | 178.3292 | 0 | 1092.7789 | 85.67% | 17.4251 | 0 | 56.25 | 90% | 48.5827
351 | 502 | 362 | 151 | 4.9 | 14.6 | 0 | 0 | 0 | 117.2292 | 48.3669 | 0 | 0 | 48.3669 | 0 | 0 | 0 | 0 | 0 | 117.2292 | 0 | 1210.0081 | 94.86% | 0 | 0.3927 | 55.8154 | 89.3% | 48.7596
352 | 346 | 213 | 109 | 4.9 | 13.4 | 0 | 0 | 0 | 65.5021 | 31.0178 | 0 | 0 | 31.0178 | 0 | 0 | 0 | 0 | 0 | 65.5021 | 0 | 1275.5102 | 100% | 0 | 18.9822 | 34.8072 | 55.69% | 50
353 | 201 | 94 | 58 | 4.4 | 12 | 0 | 0 | 0 | 0 | 14.8488 | 0 | 0 | 14.8488 | 0 | 0 | 0 | 89.1355 | 35.1512 | 0 | 89.1355 | 1186.3747 | 93.01% | 0 | 0 | 34.8072 | 55.69% | 50
354 | 1 | 2 | 2 | 3.4 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0748 | 50 | 0 | 123.0748 | 1063.2999 | 83.36% | 0 | 0 | 34.8072 | 55.69% | 50
355 | 0 | 0 | 0 | 2.9 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0186 | 50 | 0 | 123.0186 | 940.2813 | 73.72% | 0 | 0 | 34.8072 | 55.69% | 50
356 | 0 | 0 | 0 | 2.3 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.2056 | 49.2067 | 0 | 121.2056 | 819.0757 | 64.22% | 0 | 0 | 34.8072 | 55.69% | 49.2067
357 | 0 | 0 | 0 | 1.9 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.6538 | 44.1707 | 0 | 109.6538 | 709.422 | 55.62% | 0 | 0 | 34.8072 | 55.69% | 44.1707
358 | 0 | 0 | 0 | 1.8 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5973 | 40.6583 | 0 | 101.5973 | 607.8246 | 47.65% | 0 | 0 | 34.8072 | 55.69% | 40.6583
359 | 0 | 0 | 0 | 1.9 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.8246 | 47.65% | 0 | 0 | 34.8072 | 55.69% | 0
360 | 0 | 0 | 0 | 2.2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.8246 | 47.65% | 0 | 0 | 34.8072 | 55.69% | 0
361 | 0 | 0 | 0 | 2.5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.8246 | 47.65% | 0 | 0 | 34.8072 | 55.69% | 0
362 | 0 | 0 | 0 | 0.4 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.8246 | 47.65% | 0 | 0 | 34.8072 | 55.69% | 0
363 | 0 | 0 | 0 | 0.6 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.8246 | 47.65% | 0 | 0 | 34.8072 | 55.69% | 0
364 | 0 | 0 | 0 | 0.3 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607.8246 | 47.65% | 0 | 0 | 34.8072 | 55.69% | 0
365 | 0 | 0 | 0 | 0.4 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.3964 | 47.0939 | 0 | 116.3964 | 491.4282 | 38.53% | 0 | 0 | 34.8072 | 55.69% | 47.0939
366 | 0 | 0 | 0 | 1 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0952 | 50 | 0 | 123.0952 | 368.333 | 28.88% | 0 | 0 | 34.8072 | 55.69% | 50
367 | 0 | 0 | 0 | 2 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.039 | 50 | 0 | 123.039 | 245.294 | 19.23% | 0 | 0 | 34.8072 | 55.69% | 50
368 | 33 | 13 | 10 | 1.5 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0498 | 50 | 0 | 123.0498 | 122.2441 | 9.584% | 0 | 0 | 34.8072 | 55.69% | 50
369 | 328 | 122 | 56 | 0.4 | 5.1 | 0 | 0 | 0 | 10.2553 | 15.4039 | 0 | 0 | 15.4039 | 0 | 0 | 0 | 0 | 0 | 10.2553 | 0 | 132.4994 | 10.39% | 0 | 25 | 7.1388 | 11.42% | 40.4039
370 | 598 | 301 | 94 | 0.6 | 9.6 | 0 | 0 | 0 | 116.8217 | 37.6474 | 0 | 0 | 37.6474 | 0 | 0 | 0 | 0 | 0 | 116.8217 | 0 | 249.3211 | 19.55% | 0 | 0.80313 | 6.25 | 10% | 38.4506
371 | 778 | 450 | 96 | 1.6 | 11.3 | 0 | 0 | 0 | 184.7023 | 55.962 | 0 | 5.962 | 50 | 0 | 0 | 0 | 0 | 0 | 184.7023 | 0 | 434.0233 | 34.03% | 5.962 | 0 | 11.637 | 18.62% | 50
372 | 808 | 524 | 101 | 2.8 | 12.5 | 0 | 0 | 0 | 206.0902 | 64.627 | 0 | 14.6271 | 50 | 0 | 0 | 0 | 0 | 0 | 206.0902 | 0 | 640.1136 | 50.18% | 14.6271 | 0 | 24.8534 | 39.77% | 50
373 | 804 | 553 | 118 | 3 | 13.4 | 0 | 0 | 0 | 210.3871 | 68.9758 | 0 | 19.4279 | 49.5479 | 0 | 0 | 0 | 0 | 0 | 210.3871 | 0 | 850.5007 | 66.68% | 19.4279 | 0 | 42.4077 | 67.85% | 49.5479
374 | 561 | 450 | 161 | 3.5 | 13.8 | 0 | 0 | 0 | 140.2007 | 55.6649 | 0 | 6.4847 | 49.1802 | 0 | 0 | 0 | 0 | 0 | 140.2007 | 0 | 990.7014 | 77.67% | 6.4847 | 0 | 48.267 | 77.23% | 49.1802
375 | 371 | 319 | 157 | 3.7 | 13.6 | 0 | 0 | 0 | 82.534 | 40.3649 | 0 | 0 | 40.3649 | 0 | 0 | 0 | 0 | 0 | 82.534 | 0 | 1073.2354 | 84.14% | 0 | 8.8863 | 38.4322 | 61.49% | 49.2512
376 | 343 | 216 | 112 | 3.8 | 13.1 | 0 | 0 | 0 | 66.0405 | 31.0658 | 0 | 0 | 31.0658 | 0 | 0 | 0 | 0 | 0 | 66.0405 | 0 | 1139.2758 | 89.32% | 0 | 18.9342 | 17.4771 | 27.96% | 50
377 | 163 | 92 | 67 | 3.5 | 12.4 | 0 | 0 | 0 | 0 | 13.1765 | 0 | 0 | 13.1765 | 0 | 0 | 0 | 87.1097 | 34.2588 | 0 | 87.1097 | 1052.1662 | 82.49% | 0 | 2.5647 | 14.6386 | 23.42% | 50
378 | 2 | 3 | 3 | 3.1 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1167 | 50 | 0 | 123.1167 | 929.0494 | 72.84% | 0 | 0 | 14.6386 | 23.42% | 50
379 | 0 | 0 | 0 | 1.4 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0573 | 50 | 0 | 123.0573 | 805.9922 | 63.19% | 0 | 0 | 14.6386 | 23.42% | 50
380 | 0 | 0 | 0 | 1.5 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.7896 | 49.0214 | 0 | 120.7896 | 685.2026 | 53.72% | 0 | 0 | 14.6386 | 23.42% | 49.0214
381 | 0 | 0 | 0 | 1.5 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.4591 | 44.0857 | 0 | 109.4591 | 575.7435 | 45.14% | 0 | 0 | 14.6386 | 23.42% | 44.0857
382 | 0 | 0 | 0 | 0.7 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7435 | 45.14% | 0 | 0 | 14.6386 | 23.42% | 0
383 | 0 | 0 | 0 | 1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7435 | 45.14% | 0 | 0 | 14.6386 | 23.42% | 0
384 | 0 | 0 | 0 | 0.6 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7435 | 45.14% | 0 | 0 | 14.6386 | 23.42% | 0
385 | 0 | 0 | 0 | 0.8 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7435 | 45.14% | 0 | 0 | 14.6386 | 23.42% | 0
386 | 0 | 0 | 0 | 1.5 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7435 | 45.14% | 0 | 0 | 14.6386 | 23.42% | 0
387 | 0 | 0 | 0 | 2.2 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 575.7435 | 45.14% | 0 | 0 | 14.6386 | 23.42% | 0
388 | 0 | 0 | 0 | 1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7435 | 45.14% | 0 | 0 | 14.6386 | 23.42% | 0
389 | 0 | 0 | 0 | 1.5 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575.7435 | 45.14% | 0 | 0 | 14.6386 | 23.42% | 0
390 | 0 | 0 | 0 | 0.7 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0461 | 50 | 0 | 123.0461 | 452.6974 | 35.49% | 0 | 0 | 14.6386 | 23.42% | 50
391 | 0 | 0 | 0 | 0.7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0425 | 50 | 0 | 123.0425 | 329.6549 | 25.84% | 0 | 0 | 14.6386 | 23.42% | 50
392 | 108 | 25 | 18 | 1.7 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0266 | 50 | 0 | 123.0266 | 206.6283 | 16.2% | 0 | 0 | 14.6386 | 23.42% | 50
393 | 315 | 151 | 88 | 0.8 | 7.3 | 0 | 0 | 0 | 0 | 19.0573 | 0 | 0 | 19.0573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.6283 | 16.2% | 0 | 0 | 14.6386 | 23.42% | 19.0573
394 | 696 | 380 | 141 | 0.3 | 11.2 | 0 | 0 | 0 | 139.0295 | 44.8982 | 0 | 0 | 44.8982 | 0 | 0 | 0 | 0 | 0 | 139.0295 | 0 | 345.6578 | 27.1% | 0 | 0 | 14.6386 | 23.42% | 44.8982
395 | 526 | 365 | 121 | 1.4 | 12.3 | 0 | 0 | 0 | 119.5626 | 43.3087 | 0 | 0 | 43.3087 | 0 | 0 | 0 | 0 | 0 | 119.5626 | 0 | 465.2205 | 36.47% | 0 | 0 | 14.6386 | 23.42% | 43.3087
396 | 855 | 555 | 105 | 2.2 | 13.2 | 0 | 0 | 0 | 219.6614 | 67.0577 | 0 | 17.0577 | 50 | 0 | 0 | 0 | 0 | 0 | 219.6614 | 0 | 684.8819 | 53.69% | 17.0577 | 0 | 30.0513 | 48.08% | 50
397 | 793 | 591 | 160 | 1.5 | 14.3 | 0 | 0 | 0 | 208.4079 | 69.3477 | 0 | 19.3477 | 50 | 0 | 0 | 0 | 0 | 0 | 208.4079 | 0 | 893.2898 | 70.03% | 19.3477 | 0 | 47.5331 | 76.05% | 50
398 | 594 | 491 | 186 | 2.9 | 14.6 | 0 | 0 | 0 | 150.1345 | 59.4486 | 0 | 9.6473 | 49.8013 | 0 | 0 | 0 | 0 | 0 | 150.1345 | 0 | 1043.4244 | 81.8% | 9.6473 | 0 | 56.25 | 90% | 49.8013
399 | 350 | 350 | 196 | 1.6 | 14.7 | 0 | 0 | 0 | 78.1146 | 40.3832 | 0 | 0 | 40.3832 | 0 | 0 | 0 | 0 | 0 | 78.1146 | 0 | 1121.539 | 87.93% | 0 | 4.3291 | 51.4589 | 82.33% | 44.7123
400 | 7 | 86 | 82 | 3.4 | 13.5 | 0 | 0 | 0 | 0 | 5.5303 | 0 | 0 | 5.5303 | 0 | 0 | 0 | 106.8394 | 42.8129 | 0 | 106.8394 | 1014.6996 | 79.55% | 0 | 1.6568 | 49.6253 | 79.4% | 50
401 | 91 | 78 | 67 | 4.4 | 12.4 | 0 | 0 | 0 | 0 | 9.3368 | 0 | 0 | 9.3368 | 0 | 0 | 0 | 101.8151 | 40.6632 | 0 | 101.8151 | 912.8844 | 71.57% | 0 | 0 | 49.6253 | 79.4% | 50
402 | 3 | 3 | 3 | 3.9 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1286 | 50 | 0 | 123.1286 | 789.7558 | 61.92% | 0 | 0 | 49.6253 | 79.4% | 50
403 | 0 | 0 | 0 | 3.5 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0946 | 50 | 0 | 123.0946 | 666.6612 | 52.27% | 0 | 0 | 49.6253 | 79.4% | 50
404 | 0 | 0 | 0 | 2.9 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.4954 | 49.3069 | 0 | 121.4954 | 545.1658 | 42.74% | 0 | 0 | 49.6253 | 79.4% | 49.3069
405 | 0 | 0 | 0 | 2.5 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1658 | 42.74% | 0 | 0 | 49.6253 | 79.4% | 0
406 | 0 | 0 | 0 | 1.8 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1658 | 42.74% | 0 | 0 | 49.6253 | 79.4% | 0
407 | 0 | 0 | 0 | 1.4 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1658 | 42.74% | 0 | 0 | 49.6253 | 79.4% | 0
408 | 0 | 0 | 0 | 1.5 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1658 | 42.74% | 0 | 0 | 49.6253 | 79.4% | 0
409 | 0 | 0 | 0 | 1.6 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1658 | 42.74% | 0 | 0 | 49.6253 | 79.4% | 0
410 | 0 | 0 | 0 | 2.2 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1658 | 42.74% | 0 | 0 | 49.6253 | 79.4% | 0
411 | 0 | 0 | 0 | 0.9 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1658 | 42.74% | 0 | 0 | 49.6253 | 79.4% | 0
412 | 0 | 0 | 0 | 2.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.1658 | 42.74% | 0 | 0 | 49.6253 | 79.4% | 0
413 | 0 | 0 | 0 | 1.8 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.8321 | 47.2931 | 0 | 116.8321 | 428.3337 | 33.58% | 0 | 0 | 49.6253 | 79.4% | 47.2931
414 | 0 | 0 | 0 | 1.5 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0105 | 50 | 0 | 123.0105 | 305.3233 | 23.94% | 0 | 0 | 49.6253 | 79.4% | 50
415 | 0 | 0 | 0 | 0.3 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0213 | 50 | 0 | 123.0213 | 182.302 | 14.29% | 0 | 0 | 49.6253 | 79.4% | 50
416 | 0 | 8 | 8 | 0.5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0072 | 50 | 0 | 123.0072 | 59.2948 | 4.649% | 0 | 0 | 49.6253 | 79.4% | 50
417 | 214 | 141 | 88 | 0.2 | 7.5 | 0 | 0 | 0 | 0 | 16.0102 | 0 | 0 | 16.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.2948 | 4.649% | 0 | 25 | 21.9569 | 35.13% | 41.0102
418 | 547 | 281 | 95 | 1.5 | 10.3 | 0 | 0 | 0 | 105.0574 | 35.8079 | 0 | 0 | 35.8079 | 0 | 0 | 0 | 0 | 0 | 105.0574 | 0 | 164.3523 | 12.89% | 0 | 14.1921 | 6.25 | 10% | 50
419 | 799 | 460 | 94 | 2.3 | 11.8 | 0 | 0 | 0 | 190.5502 | 57.4466 | 0 | 7.4466 | 50 | 0 | 0 | 0 | 0 | 0 | 190.5502 | 0 | 354.9024 | 27.82% | 7.4466 | 0 | 12.9784 | 20.77% | 50
420 | 716 | 522 | 142 | 3.8 | 12.3 | 0 | 0 | 0 | 180.3007 | 58.9828 | 4.347 | 8.9828 | 50 | 0 | 0 | 0 | 0 | 0 | 180.3007 | 0 | 535.2031 | 41.96% | 8.9828 | 0 | 21.0949 | 33.75% | 50
421 | 735 | 570 | 168 | 3.6 | 12.9 | 0 | 0 | 0 | 191.0056 | 68.9651 | 0 | 19.3378 | 49.6272 | 0 | 0 | 0 | 0 | 0 | 191.0056 | 0 | 726.2087 | 56.93% | 19.3378 | 0 | 38.5678 | 61.71% | 49.6272
422 | 759 | 544 | 155 | 3.5 | 13.2 | 0 | 0 | 0 | 196.8667 | 68.8806 | 0 | 19.5695 | 49.3111 | 0 | 0 | 0 | 0 | 0 | 196.8667 | 0 | 923.0754 | 72.37% | 19.5695 | 0 | 56.25 | 90% | 49.3111
423 | 85 | 278 | 236 | 3.2 | 12.8 | 0 | 0 | 0 | 0 | 25.3067 | 0 | 0 | 25.3067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 923.0754 | 72.37% | 0 | 20.178 | 33.9183 | 54.27% | 45.4847
424 | 82 | 179 | 149 | 3.8 | 12.2 | 0 | 0 | 0 | 0 | 16.6013 | 0 | 0 | 16.6013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 923.0754 | 72.37% | 0 | 25 | 6.25 | 10% | 41.6013
425 | 6 | 42 | 41 | 3.3 | 11.2 | 0 | 0 | 0 | 0 | 2.5397 | 0 | 0 | 2.5397 | 0 | 0 | 0 | 117.3343 | 47.4603 | 0 | 117.3343 | 805.7411 | 63.17% | 0 | 0 | 6.25 | 10% | 50
426 | 0 | 2 | 2 | 2.7 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0999 | 50 | 0 | 123.0999 | 682.6412 | 53.52% | 0 | 0 | 6.25 | 10% | 50
427 | 0 | 0 | 0 | 2.6 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0748 | 50 | 0 | 123.0748 | 559.5665 | 43.87% | 0 | 0 | 6.25 | 10% | 50
428 | 0 | 0 | 0 | 1.9 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.6444 | 48.5075 | 0 | 119.6444 | 439.922 | 34.49% | 0 | 0 | 6.25 | 10% | 48.5075
429 | 0 | 0 | 0 | 1.2 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.381 | 44.4729 | 0 | 110.381 | 329.541 | 25.84% | 0 | 0 | 6.25 | 10% | 44.4729
430 | 0 | 0 | 0 | 0.6 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8718 | 41.2028 | 0 | 102.8718 | 226.6693 | 17.77% | 0 | 0 | 6.25 | 10% | 41.2028
431 | 0 | 0 | 0 | 0.5 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.6693 | 17.77% | 0 | 0 | 6.25 | 10% | 0
432 | 0 | 0 | 0 | 2.5 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.6693 | 17.77% | 0 | 0 | 6.25 | 10% | 0
433 | 0 | 0 | 0 | 2.2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.6693 | 17.77% | 0 | 0 | 6.25 | 10% | 0
434 | 0 | 0 | 0 | 1.6 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.6693 | 17.77% | 0 | 0 | 6.25 | 10% | 0
435 | 0 | 0 | 0 | 0.8 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.6693 | 17.77% | 0 | 0 | 6.25 | 10% | 0
436 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.6693 | 17.77% | 0 | 0 | 6.25 | 10% | 0
437 | 0 | 0 | 0 | 1.6 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.6693 | 17.77% | 0 | 0 | 6.25 | 10% | 0
438 | 0 | 0 | 0 | 1.1 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.6693 | 17.77% | 0 | 0 | 6.25 | 10% | 0
439 | 0 | 0 | 0 | 1.4 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.6854 | 44.1707 | 0 | 109.6854 | 116.9838 | 9.172% | 0 | 0 | 6.25 | 10% | 44.1707
440 | 154 | 22 | 11 | 1.4 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.9838 | 47.3502 | 0 | 116.9838 | 0 | 0% | 0 | 0 | 6.25 | 10% | 47.3502
441 | 551 | 154 | 44 | 1.4 | 6.8 | 0 | 0 | 0 | 72.2601 | 20.4867 | 0 | 0 | 20.4867 | 0 | 0 | 0 | 0 | 0 | 72.2601 | 0 | 72.2601 | 5.665% | 0 | 0 | 6.25 | 10% | 20.4867
442 | 806 | 338 | 59 | 1.5 | 10.7 | 0 | 0 | 0 | 163.543 | 44.4075 | 0 | 0 | 44.4075 | 0 | 0 | 0 | 0 | 0 | 163.543 | 0 | 235.8031 | 18.49% | 0 | 0 | 6.25 | 10% | 44.4075
443 | 831 | 462 | 77 | 3.4 | 12.3 | 0 | 0 | 0 | 198.6798 | 56.1846 | 1.8815 | 8.6338 | 47.5507 | 0 | 0 | 0 | 0 | 0 | 198.6798 | 0 | 434.4828 | 34.06% | 8.6338 | 0 | 14.0512 | 22.48% | 47.5507
444 | 872 | 547 | 84 | 4.3 | 13 | 0 | 0 | 0 | 223.4022 | 68.2035 | 0 | 21.7029 | 46.5006 | 0 | 0 | 0 | 0 | 0 | 223.4022 | 0 | 657.885 | 51.58% | 21.7029 | 0 | 33.661 | 53.86% | 46.5006
445 | 850 | 566 | 99 | 3.4 | 13.7 | 0 | 0 | 0 | 224.1864 | 69.6776 | 0.69084 | 25 | 44.6776 | 0 | 0 | 0 | 0 | 0 | 224.1864 | 0 | 882.0714 | 69.15% | 25 | 0 | 56.25 | 90% | 44.6776
446 | 668 | 476 | 126 | 3.7 | 14 | 0 | 0 | 0 | 171.1585 | 43.5091 | 17.1754 | 0 | 43.5091 | 0 | 0 | 0 | 0 | 0 | 171.1585 | 0 | 1053.23 | 82.57% | 0 | 0 | 56.25 | 90% | 43.5091
447 | 686 | 423 | 125 | 3.8 | 14 | 0 | 0 | 0 | 169.6349 | 43.622 | 14.6014 | 0 | 43.622 | 0 | 0 | 0 | 0 | 0 | 169.6349 | 0 | 1222.8649 | 95.87% | 0 | 0 | 56.25 | 90% | 43.622
448 | 197 | 163 | 93 | 4 | 12.5 | 0 | 0 | 0 | 0 | 19.7871 | 0 | 0 | 19.7871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.8649 | 95.87% | 0 | 16.8858 | 37.562 | 60.1% | 36.6728
449 | 0 | 34 | 34 | 3.4 | 10.8 | 0 | 0 | 0 | 0 | 1.8246 | 0 | 0 | 1.8246 | 0 | 0 | 0 | 113.4372 | 45.7721 | 0 | 113.4372 | 1109.4277 | 86.98% | 0 | 0 | 37.562 | 60.1% | 47.5967
450 | 0 | 3 | 3 | 1.5 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.212 | 33.4816 | 0 | 85.212 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 33.4816
451 | 0 | 0 | 0 | 1.6 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
452 | 0 | 0 | 0 | 1 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
453 | 0 | 0 | 0 | 0.6 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
454 | 0 | 0 | 0 | 0.7 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
455 | 0 | 0 | 0 | 0.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
456 | 0 | 0 | 0 | 0.8 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
457 | 0 | 0 | 0 | 0.9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
458 | 0 | 0 | 0 | 0.9 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
459 | 0 | 0 | 0 | 1.7 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
460 | 0 | 0 | 0 | 4.6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
461 | 0 | 0 | 0 | 5.1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
462 | 0 | 0 | 0 | 2.5 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
463 | 0 | 0 | 0 | 1.6 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
464 | 12 | 8 | 7 | 1.1 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 0
465 | 0 | 43 | 43 | 2.4 | 9.7 | 0 | 0 | 0 | 0 | 2.7995 | 0 | 0 | 2.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 2.7995
466 | 0 | 131 | 130 | 5.5 | 12.3 | 0 | 0 | 0 | 0 | 9.9256 | 0 | 0 | 9.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 9.9256
467 | 9 | 185 | 179 | 5 | 13.2 | 0 | 0 | 0 | 0 | 13.8008 | 0 | 0 | 13.8008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 13.8008
468 | 83 | 255 | 208 | 6.6 | 14.6 | 0 | 0 | 0 | 0 | 22.308 | 0 | 0 | 22.308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 22.308
469 | 1 | 130 | 128 | 5.2 | 13.5 | 0 | 0 | 0 | 0 | 8.4139 | 0 | 0 | 8.4139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 8.4139
470 | 0 | 137 | 135 | 2.4 | 13.4 | 0 | 0 | 0 | 0 | 8.8641 | 0 | 0 | 8.8641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 8.8641
471 | 22 | 113 | 102 | 2 | 13.7 | 0 | 0 | 0 | 0 | 8.4818 | 0 | 0 | 8.4818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.2158 | 80.3% | 0 | 0 | 37.562 | 60.1% | 8.4818
472 | 0 | 92 | 91 | 3.1 | 13.5 | 0 | 0 | 0 | 0 | 5.8079 | 0 | 0 | 5.8079 | 0 | 0 | 0 | 91.8368 | 36.2849 | 0 | 91.8368 | 932.3789 | 73.1% | 0 | 0 | 37.562 | 60.1% | 42.0928
473 | 14 | 27 | 26 | 6.5 | 12.4 | 0 | 0 | 0 | 0 | 1.9131 | 0 | 0 | 1.9131 | 0 | 0 | 0 | 107.0076 | 42.9246 | 0 | 107.0076 | 825.3714 | 64.71% | 0 | 0 | 37.562 | 60.1% | 44.8378
474 | 16 | 4 | 4 | 5.2 | 12 | 0 | 0 | 0 | 0 | 0.17286 | 0 | 0 | 0.17286 | 0 | 0 | 0 | 115.0147 | 46.4253 | 0 | 115.0147 | 710.3567 | 55.69% | 0 | 0 | 37.562 | 60.1% | 46.5981
475 | 0 | 0 | 0 | 2.4 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.7932 | 46.8043 | 0 | 115.7932 | 594.5635 | 46.61% | 0 | 0 | 37.562 | 60.1% | 46.8043
476 | 0 | 0 | 0 | 4 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.9121 | 45.0996 | 0 | 111.9121 | 482.6515 | 37.84% | 0 | 0 | 37.562 | 60.1% | 45.0996
477 | 0 | 0 | 0 | 1.6 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482.6515 | 37.84% | 0 | 0 | 37.562 | 60.1% | 0
478 | 0 | 0 | 0 | 1.8 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482.6515 | 37.84% | 0 | 0 | 37.562 | 60.1% | 0
479 | 0 | 0 | 0 | 2.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482.6515 | 37.84% | 0 | 0 | 37.562 | 60.1% | 0
480 | 0 | 0 | 0 | 1 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482.6515 | 37.84% | 0 | 0 | 37.562 | 60.1% | 0
481 | 0 | 0 | 0 | 0.7 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482.6515 | 37.84% | 0 | 0 | 37.562 | 60.1% | 0
482 | 0 | 0 | 0 | 1.2 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 482.6515 | 37.84% | 0 | 0 | 37.562 | 60.1% | 0
483 | 0 | 0 | 0 | 1.2 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 482.6515 | 37.84% | 0 | 0 | 37.562 | 60.1% | 0
484 | 0 | 0 | 0 | 0.8 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 482.6515 | 37.84% | 0 | 0 | 37.562 | 60.1% | 0
485 | 0 | 0 | 0 | 0.9 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.4526 | 45.8113 | 0 | 113.4526 | 369.1989 | 28.95% | 0 | 0 | 37.562 | 60.1% | 45.8113
486 | 0 | 0 | 0 | 1.2 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0707 | 50 | 0 | 123.0707 | 246.1282 | 19.3% | 0 | 0 | 37.562 | 60.1% | 50
487 | 0 | 0 | 0 | 1.3 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0662 | 50 | 0 | 123.0662 | 123.0619 | 9.648% | 0 | 0 | 37.562 | 60.1% | 50
488 | 193 | 23 | 9 | 1.1 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0619 | 50 | 0 | 123.0619 | 0 | 0% | 0 | 0 | 37.562 | 60.1% | 50
489 | 708 | 174 | 32 | 1.1 | 7 | 0 | 0 | 0 | 0 | 24.0623 | 0 | 0 | 24.0623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 9.8936 | 15.83% | 49.0623
490 | 875 | 350 | 44 | 3.2 | 10.2 | 0 | 0 | 0 | 0 | 46.7077 | 0 | 0 | 46.7077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.2923 | 6.25 | 10% | 50
491 | 945 | 490 | 49 | 4 | 12.4 | 0 | 0 | 0 | 228.8149 | 56.935 | 4.7817 | 6.935 | 50 | 0 | 0 | 0 | 0 | 0 | 228.8149 | 0 | 228.8149 | 17.94% | 6.935 | 0 | 12.5161 | 20.03% | 50
492 | 977 | 581 | 57 | 4.3 | 13 | 0 | 0 | 0 | 253.5163 | 71.8229 | 0 | 21.8229 | 50 | 0 | 0 | 0 | 0 | 0 | 253.5163 | 0 | 482.3312 | 37.81% | 21.8229 | 0 | 32.2345 | 51.58% | 50
493 | 868 | 562 | 79 | 3.9 | 13.5 | 0 | 0 | 0 | 229.622 | 69.6955 | 0 | 20.0097 | 49.6857 | 0 | 0 | 0 | 0 | 0 | 229.622 | 0 | 711.9533 | 55.82% | 20.0097 | 0 | 50.3145 | 80.5% | 49.6857
494 | 564 | 441 | 148 | 4.3 | 13.5 | 0 | 0 | 0 | 141.575 | 55.915 | 0 | 6.5691 | 49.3459 | 0 | 0 | 0 | 0 | 0 | 141.575 | 0 | 853.5282 | 66.92% | 6.5691 | 0 | 56.25 | 90% | 49.3459
495 | 918 | 482 | 79 | 5.3 | 13.7 | 0 | 0 | 0 | 232.6557 | 49.325 | 19.9126 | 0 | 49.325 | 0 | 0 | 0 | 0 | 0 | 232.6557 | 0 | 1086.1839 | 85.16% | 0 | 0 | 56.25 | 90% | 49.325
496 | 828 | 317 | 57 | 4.6 | 12.8 | 0 | 0 | 0 | 92.517 | 50 | 3.2464 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 92.517 | 0 | 1178.7009 | 92.41% | 0 | 0 | 56.25 | 90% | 50
497 | 562 | 124 | 33 | 5.4 | 11.4 | 0 | 0 | 0 | 96.8093 | 28.5875 | 0 | 0 | 28.5875 | 0 | 0 | 0 | 0 | 0 | 96.8093 | 0 | 1275.5102 | 100% | 0 | 21.4125 | 32.552 | 52.08% | 50
498 | 52 | 6 | 3 | 3.7 | 9.9 | 0 | 0 | 0 | 0 | 0.8885 | 0 | 0.8885 | 0 | 0 | 0 | 0 | 127.0861 | 51.7454 | 0 | 127.0861 | 1148.4242 | 90.04% | 2.6339 | 0 | 34.9319 | 55.89% | 50
499 | 0 | 0 | 0 | 1.8 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9757 | 0 | 127.551 | 1020.8731 | 80.04% | 1.9757 | 0 | 36.7171 | 58.75% | 50
500 | 0 | 0 | 0 | 0.7 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9868 | 0 | 127.551 | 893.3221 | 70.04% | 3.1367 | 0 | 39.5513 | 63.28% | 48.8501
501 | 0 | 0 | 0 | 1 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3221 | 70.04% | 0 | 0 | 39.5513 | 63.28% | 0
502 | 0 | 0 | 0 | 1.5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3221 | 70.04% | 0 | 0 | 39.5513 | 63.28% | 0
503 | 0 | 0 | 0 | 1.6 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3221 | 70.04% | 0 | 0 | 39.5513 | 63.28% | 0
504 | 0 | 0 | 0 | 1.7 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3221 | 70.04% | 0 | 0 | 39.5513 | 63.28% | 0
505 | 0 | 0 | 0 | 1.4 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3221 | 70.04% | 0 | 0 | 39.5513 | 63.28% | 0
506 | 0 | 0 | 0 | 0.9 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3221 | 70.04% | 0 | 0 | 39.5513 | 63.28% | 0
507 | 0 | 0 | 0 | 1.2 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3221 | 70.04% | 0 | 0 | 39.5513 | 63.28% | 0
508 | 0 | 0 | 0 | 2.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893.3221 | 70.04% | 0 | 0 | 39.5513 | 63.28% | 0
509 | 0 | 0 | 0 | 1.5 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9602 | 0 | 127.551 | 765.7711 | 60.04% | 4.6964 | 0 | 43.7947 | 70.07% | 47.2638
510 | 0 | 0 | 0 | 2.3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9583 | 0 | 127.551 | 638.2201 | 50.04% | 1.9583 | 0 | 45.5642 | 72.9% | 50
511 | 0 | 0 | 0 | 1.5 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9808 | 0 | 127.551 | 510.669 | 40.04% | 1.9808 | 0 | 47.354 | 75.77% | 50
512 | 192 | 41 | 27 | 1.3 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9638 | 0 | 127.551 | 383.118 | 30.04% | 1.9638 | 0 | 49.1285 | 78.61% | 50
513 | 288 | 165 | 115 | 4.8 | 8.2 | 0 | 0 | 0 | 0 | 21.8753 | 0 | 0 | 21.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383.118 | 30.04% | 0 | 25 | 21.4601 | 34.34% | 46.8753
514 | 11 | 150 | 145 | 6.1 | 8.8 | 0 | 0 | 0 | 0 | 12.0998 | 0 | 0 | 12.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383.118 | 30.04% | 0 | 13.7433 | 6.25 | 10% | 25.8431
515 | 0 | 157 | 155 | 4.3 | 9.7 | 0 | 0 | 0 | 0 | 11.1395 | 0 | 0 | 11.1395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383.118 | 30.04% | 0 | 0 | 6.25 | 10% | 11.1395
516 | 12 | 219 | 210 | 4.8 | 10.4 | 0 | 0 | 0 | 0 | 16.2608 | 0 | 0 | 16.2608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383.118 | 30.04% | 0 | 0 | 6.25 | 10% | 16.2608
517 | 7 | 280 | 272 | 3.2 | 11.2 | 0 | 0 | 0 | 0 | 21.0534 | 0 | 0 | 21.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383.118 | 30.04% | 0 | 0 | 6.25 | 10% | 21.0534
518 | 5 | 217 | 211 | 2.6 | 11.3 | 0 | 0 | 0 | 0 | 15.5015 | 0 | 0 | 15.5015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383.118 | 30.04% | 0 | 0 | 6.25 | 10% | 15.5015
519 | 0 | 127 | 125 | 2.2 | 10.9 | 0 | 0 | 0 | 0 | 8.2733 | 0 | 0 | 8.2733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383.118 | 30.04% | 0 | 0 | 6.25 | 10% | 8.2733
520 | 0 | 114 | 112 | 2.6 | 11 | 0 | 0 | 0 | 0 | 7.5405 | 0 | 0 | 7.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383.118 | 30.04% | 0 | 0 | 6.25 | 10% | 7.5405
521 | 110 | 54 | 41 | 4.4 | 11 | 0 | 0 | 0 | 0 | 8.3032 | 0 | 0 | 8.3032 | 0 | 0 | 0 | 104.1001 | 41.6968 | 0 | 104.1001 | 279.0179 | 21.88% | 0 | 0 | 6.25 | 10% | 50
522 | 14 | 4 | 3 | 6 | 9.9 | 0 | 0 | 0 | 0 | 0.176 | 0 | 0 | 0.176 | 0 | 0 | 0 | 122.6809 | 49.824 | 0 | 122.6809 | 156.337 | 12.26% | 0 | 0 | 6.25 | 10% | 50
523 | 0 | 0 | 0 | 6.2 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0748 | 50 | 0 | 123.0748 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 50
524 | 0 | 0 | 0 | 8.4 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
525 | 0 | 0 | 0 | 9.7 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
526 | 0 | 0 | 0 | 9.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
527 | 0 | 0 | 0 | 8.4 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
528 | 0 | 0 | 0 | 8.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
529 | 0 | 0 | 0 | 8.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
530 | 0 | 0 | 0 | 6 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
531 | 0 | 0 | 0 | 8.6 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
532 | 0 | 0 | 0 | 6.4 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
533 | 0 | 0 | 0 | 3.6 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
534 | 0 | 0 | 0 | 2.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
535 | 0 | 0 | 0 | 1.1 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
536 | 0 | 9 | 9 | 2.9 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2623 | 2.608% | 0 | 0 | 6.25 | 10% | 0
537 | 325 | 129 | 52 | 9.5 | 9.3 | 0 | 0 | 0 | 29.7952 | 15.1183 | 0 | 0 | 15.1183 | 0 | 0 | 0 | 0 | 0 | 29.7952 | 0 | 63.0575 | 4.944% | 0 | 0 | 6.25 | 10% | 15.1183
538 | 546 | 289 | 84 | 11.9 | 10.1 | 0 | 0 | 0 | 97.1038 | 36.2025 | 0 | 0 | 36.2025 | 0 | 0 | 0 | 0 | 0 | 97.1038 | 0 | 160.1612 | 12.56% | 0 | 0 | 6.25 | 10% | 36.2025
539 | 507 | 420 | 174 | 13.5 | 11.5 | 0 | 0 | 0 | 106.2318 | 48.9864 | 0 | 0 | 48.9864 | 0 | 0 | 0 | 0 | 0 | 106.2318 | 0 | 266.393 | 20.89% | 0 | 0 | 6.25 | 10% | 48.9864
540 | 617 | 527 | 185 | 13.5 | 12.8 | 0 | 0 | 0 | 145.1489 | 61.9969 | 0 | 11.9969 | 50 | 0 | 0 | 0 | 0 | 0 | 145.1489 | 0 | 411.5419 | 32.26% | 11.9969 | 0 | 17.0899 | 27.34% | 50
541 | 423 | 498 | 251 | 13.8 | 13.3 | 0 | 0 | 0 | 93.6838 | 54.9218 | 0 | 4.9218 | 50 | 0 | 0 | 0 | 0 | 0 | 93.6838 | 0 | 505.2257 | 39.61% | 4.9218 | 0 | 21.537 | 34.46% | 50
542 | 423 | 527 | 293 | 10.4 | 14.4 | 0 | 0 | 0 | 96.0817 | 58.0713 | 0 | 8.0713 | 50 | 0 | 0 | 0 | 0 | 0 | 96.0817 | 0 | 601.3075 | 47.14% | 8.0713 | 0 | 28.8299 | 46.13% | 50
543 | 294 | 362 | 219 | 8.3 | 14.8 | 0 | 0 | 0 | 58.5024 | 40.1992 | 0 | 0 | 40.1992 | 0 | 0 | 0 | 0 | 0 | 58.5024 | 0 | 659.8099 | 51.73% | 0 | 0 | 28.8299 | 46.13% | 40.1992
544 | 63 | 176 | 155 | 8.5 | 14.5 | 0 | 0 | 0 | 0 | 15.8911 | 0 | 0 | 15.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659.8099 | 51.73% | 0 | 0 | 28.8299 | 46.13% | 15.8911
545 | 32 | 58 | 53 | 9.9 | 13.1 | 0 | 0 | 0 | 0 | 4.7719 | 0 | 0 | 4.7719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659.8099 | 51.73% | 0 | 0 | 28.8299 | 46.13% | 4.7719
546 | 42 | 10 | 8 | 11.8 | 12.5 | 0 | 0 | 0 | 0 | 1.1335 | 0 | 0 | 1.1335 | 0 | 0 | 0 | 120.6592 | 48.8665 | 0 | 120.6592 | 539.1507 | 42.27% | 0 | 0 | 28.8299 | 46.13% | 50
547 | 0 | 0 | 0 | 8.8 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2621 | 50 | 0 | 123.2621 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 50
548 | 0 | 0 | 0 | 9.4 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
549 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
550 | 0 | 0 | 0 | 8.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
551 | 0 | 0 | 0 | 6.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
552 | 0 | 0 | 0 | 4.4 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
553 | 0 | 0 | 0 | 6.7 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
554 | 0 | 0 | 0 | 7.3 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
555 | 0 | 0 | 0 | 7.8 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
556 | 0 | 0 | 0 | 5.8 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
557 | 0 | 0 | 0 | 4.6 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
558 | 0 | 0 | 0 | 5.1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.8886 | 32.61% | 0 | 0 | 28.8299 | 46.13% | 0
559 | 0 | 0 | 0 | 4.2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.3075 | 50 | 0 | 123.3075 | 292.5811 | 22.94% | 0 | 0 | 28.8299 | 46.13% | 50
560 | 0 | 12 | 12 | 5 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.3772 | 50 | 0 | 123.3772 | 169.2038 | 13.27% | 0 | 0 | 28.8299 | 46.13% | 50
561 | 6 | 103 | 100 | 7 | 14.3 | 0 | 0 | 0 | 0 | 10.7713 | 0 | 0 | 10.7713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.2038 | 13.27% | 0 | 0 | 28.8299 | 46.13% | 10.7713
562 | 58 | 234 | 209 | 6.5 | 15.4 | 0 | 0 | 0 | 0 | 23.0533 | 0 | 0 | 23.0533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.2038 | 13.27% | 0 | 0 | 28.8299 | 46.13% | 23.0533
563 | 219 | 383 | 270 | 6.5 | 17 | 0 | 0 | 0 | 36.4056 | 37.8844 | 0 | 0 | 37.8844 | 0 | 0 | 0 | 0 | 0 | 36.4056 | 0 | 205.6094 | 16.12% | 0 | 0 | 28.8299 | 46.13% | 37.8844
564 | 331 | 488 | 298 | 7 | 18 | 0 | 0 | 0 | 70.8602 | 49.9492 | 0 | 0 | 49.9492 | 0 | 0 | 0 | 0 | 0 | 70.8602 | 0 | 276.4696 | 21.68% | 0 | 0 | 28.8299 | 46.13% | 49.9492
565 | 393 | 522 | 291 | 5.9 | 18.7 | 0 | 0 | 0 | 92.4135 | 54.4728 | 0 | 5.1199 | 49.3529 | 0 | 0 | 0 | 0 | 0 | 92.4135 | 0 | 368.8831 | 28.92% | 5.1199 | 0 | 33.456 | 53.53% | 49.3529
566 | 480 | 506 | 244 | 4.7 | 19.1 | 0 | 0 | 0 | 118.0066 | 56.624 | 0 | 7.7321 | 48.8919 | 0 | 0 | 0 | 0 | 0 | 118.0066 | 0 | 486.8897 | 38.17% | 7.7321 | 0 | 40.4425 | 64.71% | 48.8919
567 | 343 | 412 | 252 | 3.7 | 18.6 | 0 | 0 | 0 | 76.0453 | 45.185 | 0 | 0 | 45.185 | 0 | 0 | 0 | 0 | 0 | 76.0453 | 0 | 562.935 | 44.13% | 0 | 0 | 40.4425 | 64.71% | 45.185
568 | 272 | 279 | 188 | 4.9 | 18.5 | 0 | 0 | 0 | 48.8893 | 32.7357 | 0 | 0 | 32.7357 | 0 | 0 | 0 | 0 | 0 | 48.8893 | 0 | 611.8244 | 47.97% | 0 | 0 | 40.4425 | 64.71% | 32.7357
569 | 217 | 136 | 99 | 6.7 | 17.5 | 0 | 0 | 0 | 0 | 18.6064 | 0 | 0 | 18.6064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611.8244 | 47.97% | 0 | 25 | 12.7741 | 20.44% | 43.6065
570 | 18 | 11 | 10 | 5.9 | 16 | 0 | 0 | 0 | 0 | 0.47021 | 0 | 0 | 0.47021 | 0 | 0 | 0 | 122.5736 | 49.5298 | 0 | 122.5736 | 489.2508 | 38.36% | 0 | 0 | 12.7741 | 20.44% | 50
571 | 0 | 0 | 0 | 5.1 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.5765 | 50 | 0 | 123.5765 | 365.6742 | 28.67% | 0 | 0 | 12.7741 | 20.44% | 50
572 | 0 | 0 | 0 | 4.6 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.404 | 48.2039 | 0 | 119.404 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 48.2039
573 | 0 | 0 | 0 | 3.8 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 0
574 | 0 | 0 | 0 | 2.8 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 0
575 | 0 | 0 | 0 | 2.3 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 0
576 | 0 | 0 | 0 | 2.3 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 0
577 | 0 | 0 | 0 | 1.6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 0
578 | 0 | 0 | 0 | 1.3 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 0
579 | 0 | 0 | 0 | 1.8 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 0
580 | 0 | 0 | 0 | 1.9 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 0
581 | 0 | 0 | 0 | 0.9 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.2702 | 19.31% | 0 | 0 | 12.7741 | 20.44% | 0
582 | 0 | 0 | 0 | 1.6 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1476 | 50 | 0 | 123.1476 | 123.1226 | 9.653% | 0 | 0 | 12.7741 | 20.44% | 50
583 | 0 | 0 | 0 | 1.9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1226 | 50 | 0 | 123.1226 | 0 | 0% | 0 | 0 | 12.7741 | 20.44% | 50
584 | 185 | 25 | 10 | 1.9 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 5.895 | 6.25 | 10% | 5.895
585 | 686 | 176 | 33 | 2.8 | 14.7 | 0 | 0 | 0 | 76.5306 | 23.1048 | 0 | 0 | 23.1048 | 0 | 0 | 0 | 0 | 0 | 76.5306 | 0 | 76.5306 | 6% | 0 | 0 | 6.25 | 10% | 23.1048
586 | 856 | 351 | 43 | 2.8 | 17.2 | 0 | 0 | 0 | 0 | 44.5106 | 0 | 0 | 44.5106 | 0 | 0 | 0 | 38.2653 | 12.9208 | 0 | 38.2653 | 38.2653 | 3% | 7.4314 | 0 | 12.9647 | 20.74% | 50
587 | 927 | 490 | 49 | 2.3 | 18.5 | 0 | 0 | 0 | 0 | 36.8852 | 21.5719 | 0 | 36.8852 | 0 | 0 | 0 | 38.2653 | 12.8967 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 12.9647 | 20.74% | 49.7818
588 | 950 | 573 | 53 | 2.6 | 19.4 | 0 | 0 | 0 | 246.1179 | 67.1063 | 0 | 19.174 | 47.9323 | 0 | 0 | 0 | 0 | 0 | 246.1179 | 0 | 246.1179 | 19.3% | 19.174 | 0 | 30.2896 | 48.46% | 47.9323
589 | 964 | 604 | 57 | 3 | 19.8 | 0 | 0 | 0 | 259.8369 | 71.7708 | 0.10782 | 25 | 46.7708 | 0 | 0 | 0 | 0 | 0 | 259.8369 | 0 | 505.9547 | 39.67% | 25 | 0 | 52.8786 | 84.61% | 46.7708
590 | 904 | 557 | 73 | 3.6 | 20.2 | 0 | 0 | 0 | 240.9971 | 46.0968 | 23.3006 | 0 | 46.0968 | 0 | 0 | 0 | 0 | 0 | 240.9971 | 0 | 746.9518 | 58.56% | 0 | 0 | 52.8786 | 84.61% | 46.0968
591 | 886 | 459 | 59 | 3.6 | 19.8 | 0 | 0 | 0 | 227.1078 | 47.273 | 15.7303 | 1.374 | 45.899 | 0 | 0 | 0 | 0 | 0 | 227.1078 | 0 | 974.0596 | 76.37% | 1.374 | 0 | 54.12 | 86.59% | 45.899
592 | 813 | 310 | 45 | 2.9 | 19.3 | 0 | 0 | 0 | 189.6173 | 49.8398 | 0 | 2.3573 | 47.4825 | 0 | 0 | 0 | 0 | 0 | 189.6173 | 0 | 1163.6769 | 91.23% | 2.3573 | 0 | 56.25 | 90% | 47.4825
593 | 607 | 135 | 30 | 2.3 | 18.4 | 0 | 0 | 0 | 111.8333 | 29.0668 | 0 | 0 | 29.0668 | 0 | 0 | 0 | 0 | 0 | 111.8333 | 0 | 1275.5102 | 100% | 0 | 20.8529 | 33.1714 | 53.07% | 49.9197
594 | 76 | 9 | 5 | 1.5 | 15.6 | 0 | 0 | 0 | 0 | 1.5955 | 0 | 0 | 1.5955 | 0 | 0 | 0 | 112.2315 | 45.0626 | 0 | 112.2315 | 1163.2787 | 91.2% | 0 | 3.3419 | 29.4728 | 47.16% | 50
595 | 0 | 0 | 0 | 1.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.5487 | 49.2261 | 0 | 121.5487 | 1041.73 | 81.67% | 0 | 0 | 29.4728 | 47.16% | 49.2261
596 | 0 | 0 | 0 | 0.7 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.3944 | 46.1762 | 0 | 114.3944 | 927.3356 | 72.7% | 0 | 0 | 29.4728 | 47.16% | 46.1762
597 | 0 | 0 | 0 | 0.9 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.9365 | 42.5189 | 0 | 105.9365 | 821.3991 | 64.4% | 0 | 0 | 29.4728 | 47.16% | 42.5189
598 | 0 | 0 | 0 | 0.8 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0999 | 39.9801 | 0 | 100.0999 | 721.2991 | 56.55% | 0 | 0 | 29.4728 | 47.16% | 39.9801
599 | 0 | 0 | 0 | 2.3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6158 | 37.1501 | 0 | 93.6158 | 627.6834 | 49.21% | 0 | 0 | 29.4728 | 47.16% | 37.1501
600 | 0 | 0 | 0 | 1.9 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4562 | 34.9009 | 0 | 88.4562 | 539.2272 | 42.28% | 0 | 0 | 29.4728 | 47.16% | 34.9009
601 | 0 | 0 | 0 | 2.7 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.2272 | 42.28% | 0 | 0 | 29.4728 | 47.16% | 0
602 | 0 | 0 | 0 | 2.9 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.2272 | 42.28% | 0 | 0 | 29.4728 | 47.16% | 0
603 | 0 | 0 | 0 | 2.1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.3958 | 16.9959 | 0 | 47.3958 | 491.8314 | 38.56% | 0 | 0 | 29.4728 | 47.16% | 16.9959
604 | 0 | 0 | 0 | 1.8 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6478 | 34.1294 | 0 | 86.6478 | 405.1836 | 31.77% | 0 | 0 | 29.4728 | 47.16% | 34.1294
605 | 0 | 0 | 0 | 2.1 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6856 | 36.3312 | 0 | 91.6856 | 313.498 | 24.58% | 0 | 0 | 29.4728 | 47.16% | 36.3312
606 | 0 | 0 | 0 | 2.7 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8767 | 38.5929 | 0 | 96.8767 | 216.6213 | 16.98% | 0 | 0 | 29.4728 | 47.16% | 38.5929
607 | 0 | 0 | 0 | 1.6 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6173 | 42.4131 | 0 | 105.6173 | 111.004 | 8.703% | 0 | 0 | 29.4728 | 47.16% | 42.4131
608 | 203 | 28 | 11 | 1.5 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.004 | 44.764 | 0 | 111.004 | 0 | 0% | 0 | 0 | 29.4728 | 47.16% | 44.764
609 | 711 | 184 | 34 | 0.6 | 11.1 | 0 | 0 | 0 | 0 | 23.7849 | 0 | 0 | 23.7849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 20.9832 | 6.25 | 10% | 44.7681
610 | 872 | 361 | 45 | 0.6 | 14.8 | 0 | 0 | 0 | 181.5664 | 43.8838 | 0.4722 | 0 | 43.8838 | 0 | 0 | 0 | 0 | 0 | 181.5664 | 0 | 181.5664 | 14.23% | 0 | 0 | 6.25 | 10% | 43.8838
611 | 941 | 502 | 51 | 3.8 | 16.3 | 0 | 0 | 0 | 230.9993 | 43.5607 | 17.3061 | 0 | 43.5607 | 0 | 0 | 0 | 0 | 0 | 230.9993 | 0 | 412.5657 | 32.35% | 0 | 0 | 6.25 | 10% | 43.5607
612 | 972 | 590 | 53 | 4.2 | 17.2 | 0 | 0 | 0 | 254.1578 | 42.3588 | 27.9236 | 0 | 42.3588 | 0 | 0 | 0 | 0 | 0 | 254.1578 | 0 | 666.7235 | 52.27% | 0 | 0 | 6.25 | 10% | 42.3588
613 | 978 | 614 | 55 | 4.2 | 17.7 | 0 | 0 | 0 | 263.3265 | 40.3923 | 31.6077 | 0 | 40.3923 | 0 | 0 | 0 | 0 | 0 | 263.3265 | 0 | 930.0499 | 72.92% | 0 | 0 | 6.25 | 10% | 40.3923
614 | 961 | 572 | 54 | 4.2 | 18.1 | 0 | 0 | 0 | 152.709 | 58.9131 | 13.0869 | 19.6112 | 39.3018 | 0 | 0 | 0 | 0 | 0 | 152.709 | 0 | 1082.759 | 84.89% | 19.6112 | 0 | 23.9699 | 38.35% | 39.3018
615 | 919 | 471 | 51 | 4.7 | 17.9 | 0 | 0 | 0 | 0 | 63.9188 | 1.4458 | 25 | 38.9188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1082.759 | 84.89% | 25 | 0 | 46.5589 | 74.49% | 38.9188
616 | 828 | 319 | 45 | 4.7 | 17.4 | 0 | 0 | 0 | 192.7512 | 51.7208 | 0 | 10.7254 | 40.9953 | 0 | 0 | 0 | 0 | 0 | 192.7512 | 0 | 1275.5102 | 100% | 10.7254 | 0 | 56.25 | 90% | 40.9953
617 | 611 | 139 | 31 | 4.2 | 16 | 0 | 0 | 0 | 0 | 29.9401 | 0 | 0 | 29.9401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 13.9757 | 40.7827 | 65.25% | 43.9158
618 | 83 | 10 | 5 | 3.2 | 13.2 | 0 | 0 | 0 | 0 | 1.8882 | 0 | 0 | 1.8882 | 0 | 0 | 0 | 73.7733 | 28.4324 | 0 | 73.7733 | 1201.7369 | 94.22% | 0 | 14.5882 | 24.6374 | 39.42% | 44.9088
619 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.5156 | 44.9241 | 0 | 111.5156 | 1090.2213 | 85.47% | 0 | 0 | 24.6374 | 39.42% | 44.9241
620 | 0 | 0 | 0 | 0.5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3179 | 43.1303 | 0 | 107.3179 | 982.9034 | 77.06% | 0 | 0 | 24.6374 | 39.42% | 43.1303
621 | 0 | 0 | 0 | 1.7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5706 | 40.2043 | 0 | 100.5706 | 882.3328 | 69.17% | 0 | 0 | 24.6374 | 39.42% | 40.2043
622 | 0 | 0 | 0 | 0.6 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2725 | 37.0206 | 0 | 93.2725 | 789.0603 | 61.86% | 0 | 0 | 24.6374 | 39.42% | 37.0206
623 | 0 | 0 | 0 | 0.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1836 | 34.3647 | 0 | 87.1836 | 701.8768 | 55.03% | 0 | 0 | 24.6374 | 39.42% | 34.3647
624 | 0 | 0 | 0 | 1.3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.895 | 32.4929 | 0 | 82.895 | 618.9818 | 48.53% | 0 | 0 | 24.6374 | 39.42% | 32.4929
625 | 0 | 0 | 0 | 2.2 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9326 | 31.2019 | 0 | 79.9326 | 539.0492 | 42.26% | 0 | 0 | 24.6374 | 39.42% | 31.2019
626 | 0 | 0 | 0 | 1.2 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2565 | 30.9067 | 0 | 79.2565 | 459.7927 | 36.05% | 0 | 0 | 24.6374 | 39.42% | 30.9067
627 | 0 | 0 | 0 | 1.2 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.6832 | 23.6722 | 0 | 62.6832 | 397.1094 | 31.13% | 0 | 0 | 24.6374 | 39.42% | 23.6722
628 | 0 | 0 | 0 | 2.3 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 13.0144 | 0 | 38.2653 | 358.8441 | 28.13% | 0 | 0 | 24.6374 | 39.42% | 13.0144
629 | 0 | 0 | 0 | 2.9 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7796 | 32.4442 | 0 | 82.7796 | 276.0646 | 21.64% | 0 | 0 | 24.6374 | 39.42% | 32.4442
630 | 0 | 0 | 0 | 2.8 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3446 | 33.5625 | 0 | 85.3446 | 190.7199 | 14.95% | 0 | 0 | 24.6374 | 39.42% | 33.5625
631 | 0 | 0 | 0 | 1.7 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.117 | 36.5109 | 0 | 92.117 | 98.603 | 7.73% | 0 | 0 | 24.6374 | 39.42% | 36.5109
632 | 156 | 25 | 12 | 2.8 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.603 | 39.3255 | 0 | 98.603 | 0 | 0% | 0 | 0 | 24.6374 | 39.42% | 39.3255
633 | 697 | 187 | 37 | 4.7 | 13 | 0 | 0 | 0 | 0 | 24.0107 | 0 | 0 | 24.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 16.6141 | 6.25 | 10% | 40.6249
634 | 893 | 373 | 48 | 6.4 | 16.4 | 0 | 0 | 0 | 0 | 40.4954 | 7.2219 | 0 | 40.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 40.4954
635 | 965 | 519 | 54 | 8.8 | 18.7 | 0 | 0 | 0 | 0 | 40.8199 | 22.7554 | 0 | 40.8199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 40.8199
636 | 1002 | 615 | 61 | 10.1 | 20.1 | 0 | 0 | 0 | 242.7597 | 40.4243 | 31.5757 | 0 | 40.4243 | 0 | 0 | 0 | 0 | 0 | 242.7597 | 0 | 242.7597 | 19.03% | 0 | 0 | 6.25 | 10% | 40.4243
637 | 991 | 642 | 74 | 10.4 | 20 | 0 | 0 | 0 | 262.0068 | 38.4035 | 33.5965 | 0 | 38.4035 | 0 | 0 | 0 | 0 | 0 | 262.0068 | 0 | 504.7665 | 39.57% | 0 | 0 | 6.25 | 10% | 38.4035
638 | 989 | 642 | 107 | 8.7 | 20.1 | 0 | 0 | 0 | 261.8063 | 53.9606 | 18.0394 | 16.6364 | 37.3242 | 0 | 0 | 0 | 0 | 0 | 261.8063 | 0 | 766.5728 | 60.1% | 16.6364 | 0 | 21.282 | 34.05% | 37.3242
639 | 780 | 475 | 119 | 5.6 | 19.6 | 0 | 0 | 0 | 196.8076 | 62.2518 | 1.4385 | 25 | 37.2518 | 0 | 0 | 0 | 0 | 0 | 196.8076 | 0 | 963.3804 | 75.53% | 25 | 0 | 43.871 | 70.19% | 37.2518
640 | 841 | 330 | 49 | 7 | 17.6 | 0 | 0 | 0 | 194.7591 | 53.4004 | 0 | 13.7002 | 39.7001 | 0 | 0 | 0 | 0 | 0 | 194.7591 | 0 | 1158.1395 | 90.8% | 13.7002 | 0 | 56.25 | 90% | 39.7001
641 | 643 | 147 | 33 | 6.9 | 15.7 | 0 | 0 | 0 | 117.3707 | 31.8811 | 0 | 0 | 31.8811 | 0 | 0 | 0 | 0 | 0 | 117.3707 | 0 | 1275.5102 | 100% | 0 | 11.3328 | 43.7076 | 69.93% | 43.2139
642 | 96 | 11 | 5 | 6.1 | 13.4 | 0 | 0 | 0 | 0 | 2.2613 | 0 | 0 | 2.2613 | 0 | 0 | 0 | 107.1578 | 42.9552 | 0 | 107.1578 | 1168.3524 | 91.6% | 0 | 0 | 43.7076 | 69.93% | 45.2166
643 | 0 | 0 | 0 | 2.1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1659 | 45.1873 | 0 | 112.1659 | 1056.1865 | 82.81% | 0 | 0 | 43.7076 | 69.93% | 45.1873
644 | 0 | 0 | 0 | 1 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5924 | 43.6526 | 0 | 108.5924 | 947.5941 | 74.29% | 0 | 0 | 43.7076 | 69.93% | 43.6526
645 | 0 | 0 | 0 | 0.8 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.8725 | 39.8867 | 0 | 99.8725 | 847.7216 | 66.46% | 0 | 0 | 43.7076 | 69.93% | 39.8867
646 | 0 | 0 | 0 | 1 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0713 | 36.4969 | 0 | 92.0713 | 755.6504 | 59.24% | 0 | 0 | 43.7076 | 69.93% | 36.4969
647 | 0 | 0 | 0 | 1 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3019 | 33.9789 | 0 | 86.3019 | 669.3485 | 52.48% | 0 | 0 | 43.7076 | 69.93% | 33.9789
648 | 0 | 0 | 0 | 1.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 669.3485 | 52.48% | 0 | 6.7513 | 36.2357 | 57.98% | 6.7513
649 | 0 | 0 | 0 | 1.3 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 669.3485 | 52.48% | 0 | 0 | 36.2357 | 57.98% | 0
650 | 0 | 0 | 0 | 1.6 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 669.3485 | 52.48% | 0 | 0 | 36.2357 | 57.98% | 0
651 | 0 | 0 | 0 | 1.2 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0223 | 33.4205 | 0 | 85.0223 | 584.3261 | 45.81% | 0 | 0 | 36.2357 | 57.98% | 33.4205
652 | 0 | 0 | 0 | 1.2 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3135 | 42.2802 | 0 | 105.3135 | 479.0127 | 37.55% | 4.2276 | 0 | 40.0556 | 64.09% | 38.0526
653 | 0 | 0 | 0 | 1.6 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.69 | 45.0606 | 0 | 111.69 | 367.3226 | 28.8% | 0 | 0 | 40.0556 | 64.09% | 45.0606
654 | 0 | 0 | 0 | 1.5 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.3241 | 49.2679 | 0 | 121.3241 | 245.9985 | 19.29% | 0 | 0 | 40.0556 | 64.09% | 49.2679
655 | 0 | 0 | 0 | 1.2 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9993 | 50 | 0 | 122.9993 | 122.9992 | 9.643% | 0 | 0 | 40.0556 | 64.09% | 50
656 | 213 | 30 | 11 | 1.3 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9992 | 50 | 0 | 122.9992 | 0 | 0% | 0 | 0 | 40.0556 | 64.09% | 50
657 | 730 | 193 | 36 | 1.4 | 10.6 | 0 | 0 | 0 | 0 | 24.7595 | 0 | 0 | 24.7595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 12.3873 | 19.82% | 49.7595
658 | 831 | 367 | 61 | 0.6 | 13.7 | 0 | 0 | 0 | 0 | 44.4546 | 0 | 0 | 44.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 5.5454 | 6.25 | 10% | 50
659 | 896 | 503 | 67 | 2.1 | 15.6 | 0 | 0 | 0 | 0 | 58.8642 | 0 | 8.8642 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 8.8642 | 0 | 14.2593 | 22.81% | 50
660 | 1001 | 617 | 60 | 7.1 | 17.7 | 0 | 0 | 0 | 239.2647 | 49.1677 | 22.8323 | 0 | 49.1677 | 0 | 0 | 0 | 0 | 0 | 239.2647 | 0 | 239.2647 | 18.76% | 0 | 0 | 14.2593 | 22.81% | 49.1677
661 | 914 | 634 | 103 | 8.3 | 18.7 | 0 | 0 | 0 | 242.1609 | 69.3711 | 2.6289 | 21.021 | 48.3501 | 0 | 0 | 0 | 0 | 0 | 242.1609 | 0 | 481.4256 | 37.74% | 21.021 | 0 | 33.253 | 53.2% | 48.3501
662 | 942 | 592 | 77 | 6.6 | 19.9 | 0 | 0 | 0 | 250.7554 | 47.8752 | 24.1248 | 0 | 47.8752 | 0 | 0 | 0 | 0 | 0 | 250.7554 | 0 | 732.181 | 57.4% | 0 | 0 | 33.253 | 53.2% | 47.8752
663 | 946 | 492 | 53 | 7.8 | 20.3 | 0 | 0 | 0 | 241.5621 | 67.9341 | 0 | 20.18 | 47.7541 | 0 | 0 | 0 | 0 | 0 | 241.5621 | 0 | 973.7431 | 76.34% | 20.18 | 0 | 51.4869 | 82.38% | 47.7541
664 | 862 | 341 | 49 | 9.3 | 19.7 | 0 | 0 | 0 | 198.851 | 54.6174 | 0 | 5.2715 | 49.3459 | 0 | 0 | 0 | 0 | 0 | 198.851 | 0 | 1172.594 | 91.93% | 5.2715 | 0 | 56.25 | 90% | 49.3459
665 | 577 | 141 | 34 | 7.9 | 18.2 | 0 | 0 | 0 | 102.9162 | 29.3102 | 0 | 0 | 29.3102 | 0 | 0 | 0 | 0 | 0 | 102.9162 | 0 | 1275.5102 | 100% | 0 | 20.6898 | 33.3519 | 53.36% | 50
666 | 46 | 10 | 6 | 6.4 | 15.5 | 0 | 0 | 0 | 0 | 1.2758 | 0 | 0 | 1.2758 | 0 | 0 | 0 | 120.6515 | 48.7242 | 0 | 120.6515 | 1154.8587 | 90.54% | 0 | 0 | 33.3519 | 53.36% | 50
667 | 0 | 0 | 0 | 3.8 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.3772 | 50 | 0 | 123.3772 | 1031.4814 | 80.87% | 0 | 0 | 33.3519 | 53.36% | 50
668 | 0 | 0 | 0 | 4.7 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.193 | 46.9143 | 0 | 116.193 | 915.2884 | 71.76% | 0 | 0 | 33.3519 | 53.36% | 46.9143
669 | 0 | 0 | 0 | 2.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915.2884 | 71.76% | 0 | 0 | 33.3519 | 53.36% | 0
670 | 0 | 0 | 0 | 1.1 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915.2884 | 71.76% | 0 | 0 | 33.3519 | 53.36% | 0
671 | 0 | 0 | 0 | 2.1 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915.2884 | 71.76% | 0 | 0 | 33.3519 | 53.36% | 0
672 | 0 | 0 | 0 | 1.7 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915.2884 | 71.76% | 0 | 0 | 33.3519 | 53.36% | 0
673 | 0 | 0 | 0 | 1.9 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915.2884 | 71.76% | 0 | 0 | 33.3519 | 53.36% | 0
674 | 0 | 0 | 0 | 1.6 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915.2884 | 71.76% | 0 | 0 | 33.3519 | 53.36% | 0
675 | 0 | 0 | 0 | 2 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915.2884 | 71.76% | 0 | 0 | 33.3519 | 53.36% | 0
676 | 0 | 0 | 0 | 1.3 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915.2884 | 71.76% | 0 | 0 | 33.3519 | 53.36% | 0
677 | 0 | 0 | 0 | 1.7 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.424 | 45.8168 | 0 | 113.424 | 801.8644 | 62.87% | 0 | 0 | 33.3519 | 53.36% | 45.8168
678 | 0 | 0 | 0 | 1.3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.7046 | 49.4337 | 0 | 121.7046 | 680.1599 | 53.32% | 0 | 0 | 33.3519 | 53.36% | 49.4337
679 | 0 | 0 | 0 | 1.3 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9992 | 50 | 0 | 122.9992 | 557.1607 | 43.68% | 0 | 0 | 33.3519 | 53.36% | 50
680 | 104 | 30 | 22 | 2 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0006 | 50 | 0 | 123.0006 | 434.1601 | 34.04% | 0 | 0 | 33.3519 | 53.36% | 50
681 | 37 | 96 | 88 | 1.8 | 9.9 | 0 | 0 | 0 | 0 | 9.9257 | 0 | 0 | 9.9257 | 0 | 0 | 0 | 100.3273 | 40.0743 | 0 | 100.3273 | 333.8328 | 26.17% | 0 | 0 | 33.3519 | 53.36% | 50
682 | 20 | 160 | 149 | 3.5 | 12.1 | 0 | 0 | 0 | 0 | 12.4017 | 0 | 0 | 12.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8328 | 26.17% | 0 | 4.6324 | 28.225 | 45.16% | 17.0341
683 | 21 | 199 | 185 | 4.5 | 12.6 | 0 | 0 | 0 | 0 | 14.806 | 0 | 0 | 14.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8328 | 26.17% | 0 | 0 | 28.225 | 45.16% | 14.806
684 | 91 | 242 | 185 | 2.9 | 13.9 | 0 | 0 | 0 | 0 | 21.5855 | 0 | 0 | 21.5855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.8328 | 26.17% | 0 | 0 | 28.225 | 45.16% | 21.5855
685 | 742 | 544 | 109 | 6.1 | 17.4 | 0 | 0 | 0 | 194.633 | 65.0023 | 0 | 15.5115 | 49.4908 | 0 | 0 | 0 | 0 | 0 | 194.633 | 0 | 528.4658 | 41.43% | 15.5115 | 0 | 42.2406 | 67.59% | 49.4908
686 | 720 | 509 | 111 | 11.7 | 18.3 | 0 | 0 | 0 | 182.5113 | 64.5469 | 0 | 15.5046 | 49.0423 | 0 | 0 | 0 | 0 | 0 | 182.5113 | 0 | 710.9771 | 55.74% | 15.5046 | 0 | 56.25 | 90% | 49.0423
687 | 434 | 365 | 153 | 12 | 17.1 | 0 | 0 | 0 | 95.0703 | 44.9333 | 0 | 0 | 44.9333 | 0 | 0 | 0 | 0 | 0 | 95.0703 | 0 | 806.0474 | 63.19% | 0 | 0 | 56.25 | 90% | 44.9333
688 | 515 | 272 | 94 | 11.4 | 16 | 0 | 0 | 0 | 108.0216 | 40.5789 | 0 | 0 | 40.5789 | 0 | 0 | 0 | 0 | 0 | 108.0216 | 0 | 914.069 | 71.66% | 0 | 0 | 56.25 | 90% | 40.5789
689 | 351 | 142 | 70 | 12.4 | 14.6 | 0 | 0 | 0 | 50.1224 | 22.9634 | 0 | 0 | 22.9634 | 0 | 0 | 0 | 0 | 0 | 50.1224 | 0 | 964.1914 | 75.59% | 0 | 25 | 28.5817 | 45.73% | 47.9634
690 | 3 | 7 | 7 | 10.6 | 12.9 | 0 | 0 | 0 | 0 | 0.089335 | 0 | 0 | 0.089335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 20.178 | 6.25 | 10% | 20.2673
691 | 0 | 0 | 0 | 7.1 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
692 | 0 | 0 | 0 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
693 | 0 | 0 | 0 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
694 | 0 | 0 | 0 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.1914 | 75.59% | 0 | 0 | 6.25 | 10% | 0
701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.5208 | 45.743 | 0 | 113.5208 | 850.6706 | 66.69% | 0 | 0 | 6.25 | 10% | 45.743
702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.4238 | 49.6189 | 0 | 122.4238 | 728.2468 | 57.09% | 0 | 0 | 6.25 | 10% | 49.6189
703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2992 | 50 | 0 | 123.2992 | 604.9476 | 47.43% | 0 | 0 | 6.25 | 10% | 50
704 | 0 | 14 | 14 | 5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0044 | 50 | 0 | 123.0044 | 481.9432 | 37.78% | 0 | 0 | 6.25 | 10% | 50
705 | 8 | 95 | 91 | 8.6 | 11.7 | 0 | 0 | 0 | 0 | 8.4891 | 0 | 0 | 8.4891 | 0 | 0 | 0 | 103.7146 | 41.5109 | 0 | 103.7146 | 378.2286 | 29.65% | 0 | 0 | 6.25 | 10% | 50
706 | 283 | 296 | 182 | 10 | 13 | 0 | 0 | 0 | 39.8681 | 30.7576 | 0 | 0 | 30.7576 | 0 | 0 | 0 | 0 | 0 | 39.8681 | 0 | 418.0967 | 32.78% | 0 | 0 | 6.25 | 10% | 30.7576
707 | 451 | 458 | 230 | 11 | 14.3 | 0 | 0 | 0 | 94.9463 | 49.1576 | 0 | 0 | 49.1576 | 0 | 0 | 0 | 0 | 0 | 94.9463 | 0 | 513.043 | 40.22% | 0 | 0 | 6.25 | 10% | 49.1576
708 | 516 | 525 | 227 | 11.8 | 14.9 | 0 | 0 | 0 | 119.9135 | 58.1017 | 0 | 9.0496 | 49.0521 | 0 | 0 | 0 | 0 | 0 | 119.9135 | 0 | 632.9565 | 49.62% | 9.0496 | 0 | 14.4269 | 23.08% | 49.0521
709 | 282 | 470 | 298 | 9.6 | 14.8 | 0 | 0 | 0 | 58.0454 | 46.9087 | 0 | 0 | 46.9087 | 0 | 0 | 0 | 0 | 0 | 58.0454 | 0 | 691.0019 | 54.17% | 0 | 0 | 14.4269 | 23.08% | 46.9087
710 | 168 | 372 | 273 | 8.4 | 15.5 | 0 | 0 | 0 | 0 | 35.847 | 0 | 0 | 35.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.0019 | 54.17% | 0 | 0 | 14.4269 | 23.08% | 35.847
711 | 132 | 283 | 214 | 7.8 | 15.7 | 0 | 0 | 0 | 0 | 27.1141 | 0 | 0 | 27.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.0019 | 54.17% | 0 | 0 | 14.4269 | 23.08% | 27.1141
712 | 1 | 119 | 117 | 5.9 | 14.6 | 0 | 0 | 0 | 0 | 7.8066 | 0 | 0 | 7.8066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.0019 | 54.17% | 0 | 7.3883 | 6.25 | 10% | 15.1949
713 | 0 | 53 | 52 | 6.5 | 13.6 | 0 | 0 | 0 | 0 | 3.0102 | 0 | 0 | 3.0102 | 0 | 0 | 0 | 116.4482 | 46.9898 | 0 | 116.4482 | 574.5537 | 45.05% | 0 | 0 | 6.25 | 10% | 50
714 | 0 | 4 | 4 | 6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2889 | 50 | 0 | 123.2889 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 50
715 | 0 | 0 | 0 | 6.8 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
716 | 0 | 0 | 0 | 8 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
717 | 0 | 0 | 0 | 7.3 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
718 | 0 | 0 | 0 | 4.7 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
719 | 0 | 0 | 0 | 5.9 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
720 | 0 | 0 | 0 | 5 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7053e-13 | 0 | 0 | 1.7053e-13 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
721 | 0 | 0 | 0 | 7.7 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
722 | 0 | 0 | 0 | 6 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
723 | 0 | 0 | 0 | 8.7 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
724 | 0 | 0 | 0 | 7 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
725 | 0 | 0 | 0 | 4 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.2648 | 35.38% | 0 | 0 | 6.25 | 10% | 0
726 | 0 | 0 | 0 | 4.8 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9849 | 34.6679 | 0 | 87.9849 | 363.2799 | 28.48% | 0 | 0 | 6.25 | 10% | 34.6679
727 | 0 | 0 | 0 | 4 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1412 | 50 | 0 | 123.1412 | 240.1388 | 18.83% | 0 | 0 | 6.25 | 10% | 50
728 | 0 | 15 | 15 | 1.4 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1286 | 50 | 0 | 123.1286 | 117.0101 | 9.174% | 0 | 0 | 6.25 | 10% | 50
729 | 0 | 44 | 44 | 2.1 | 10.6 | 0 | 0 | 0 | 0 | 2.6651 | 0 | 0 | 2.6651 | 0 | 0 | 0 | 117.0101 | 47.3349 | 0 | 117.0101 | 0 | 0% | 0 | 0 | 6.25 | 10% | 50
730 | 177 | 203 | 134 | 3.7 | 13.1 | 0 | 0 | 0 | 0 | 20.0874 | 0 | 0 | 20.0874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 20.0874
731 | 0 | 156 | 154 | 3.4 | 14.6 | 0 | 0 | 0 | 0 | 10.6346 | 0 | 0 | 10.6346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 10.6346
732 | 97 | 307 | 247 | 7.2 | 17.3 | 0 | 0 | 0 | 0 | 26.3995 | 0 | 0 | 26.3995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 26.3995
733 | 356 | 508 | 290 | 10.2 | 18.9 | 0 | 0 | 0 | 79.1549 | 52.2597 | 0 | 4.1421 | 48.1176 | 0 | 0 | 0 | 0 | 0 | 79.1549 | 0 | 79.1549 | 6.206% | 4.1421 | 0 | 9.9927 | 15.99% | 48.1176
734 | 529 | 457 | 159 | 10.4 | 19.3 | 0 | 0 | 0 | 128.944 | 54.2581 | 0 | 6.4358 | 47.8223 | 0 | 0 | 0 | 0 | 0 | 128.944 | 0 | 208.0989 | 16.31% | 6.4358 | 0 | 15.8078 | 25.29% | 47.8223
735 | 908 | 492 | 59 | 9.4 | 19.5 | 0 | 0 | 0 | 230.7465 | 66.8503 | 0 | 18.9458 | 47.9045 | 0 | 0 | 0 | 0 | 0 | 230.7465 | 0 | 438.8454 | 34.41% | 18.9458 | 0 | 32.9264 | 52.68% | 47.9045
736 | 677 | 336 | 93 | 10.1 | 18.6 | 0 | 0 | 0 | 152.2964 | 49.477 | 0 | 0.17005 | 49.3069 | 0 | 0 | 0 | 0 | 0 | 152.2964 | 0 | 591.1418 | 46.35% | 0.17005 | 0 | 33.0801 | 52.93% | 49.3069
737 | 228 | 115 | 78 | 9.7 | 16.9 | 0 | 0 | 0 | 0 | 17.0576 | 0 | 0 | 17.0576 | 0 | 0 | 0 | 84.4392 | 32.9424 | 0 | 84.4392 | 506.7026 | 39.73% | 0 | 0 | 33.0801 | 52.93% | 50
738 | 51 | 14 | 10 | 8 | 16.2 | 0 | 0 | 0 | 0 | 1.981 | 0 | 0 | 1.981 | 0 | 0 | 0 | 119.1193 | 48.019 | 0 | 119.1193 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 50
739 | 0 | 0 | 0 | 9.2 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
740 | 0 | 0 | 0 | 8.9 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
741 | 0 | 0 | 0 | 5.2 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
742 | 0 | 0 | 0 | 4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
743 | 0 | 0 | 0 | 4.9 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
744 | 0 | 0 | 0 | 5.9 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
745 | 0 | 0 | 0 | 7 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
746 | 0 | 0 | 0 | 7.5 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
747 | 0 | 0 | 0 | 5.2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
748 | 0 | 0 | 0 | 5.5 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
749 | 0 | 0 | 0 | 7.2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387.5833 | 30.39% | 0 | 0 | 33.0801 | 52.93% | 0
750 | 0 | 0 | 0 | 5.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.8386 | 0 | 127.551 | 260.0323 | 20.39% | 3.4049 | 0 | 36.1566 | 57.85% | 48.4337
751 | 0 | 0 | 0 | 7.6 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1092 | 49.9011 | 0 | 123.1092 | 136.9231 | 10.73% | 0.018966 | 0 | 36.1737 | 57.88% | 49.8821
752 | 51 | 31 | 27 | 9.8 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.9231 | 10.73% | 0 | 25 | 8.5054 | 13.61% | 25
753 | 478 | 196 | 79 | 8.8 | 14.8 | 0 | 0 | 0 | 58.9825 | 21.5034 | 0 | 0 | 21.5034 | 0 | 0 | 0 | 0 | 0 | 58.9825 | 0 | 195.9056 | 15.36% | 0 | 2.0379 | 6.25 | 10% | 23.5413
754 | 59 | 150 | 129 | 7.7 | 14.7 | 0 | 0 | 0 | 0 | 12.9732 | 0 | 0 | 12.9732 | 0 | 0 | 0 | 93.6401 | 37.0268 | 0 | 93.6401 | 102.2655 | 8.018% | 0 | 0 | 6.25 | 10% | 50
755 | 10 | 136 | 129 | 7.4 | 14.7 | 0 | 0 | 0 | 0 | 9.2244 | 0 | 0 | 9.2244 | 0 | 0 | 0 | 102.2655 | 40.7756 | 0 | 102.2655 | 0 | 0% | 0 | 0 | 6.25 | 10% | 50
756 | 245 | 316 | 171 | 12.2 | 15.1 | 0 | 0 | 0 | 42.539 | 32.807 | 0 | 0 | 32.807 | 0 | 0 | 0 | 0 | 0 | 42.539 | 0 | 42.539 | 3.335% | 0 | 0 | 6.25 | 10% | 32.807
757 | 776 | 593 | 129 | 13.3 | 16.6 | 0 | 0 | 0 | 198.7627 | 50.3759 | 20.8927 | 2.8739 | 47.502 | 0 | 0 | 0 | 0 | 0 | 198.7627 | 0 | 241.3017 | 18.92% | 2.8739 | 0 | 8.8468 | 14.15% | 47.502
758 | 950 | 606 | 72 | 12.1 | 16.8 | 0 | 0 | 0 | 250.0295 | 71.9923 | 0.0077308 | 25 | 46.9923 | 0 | 0 | 0 | 0 | 0 | 250.0295 | 0 | 491.3312 | 38.52% | 25 | 0 | 31.4358 | 50.3% | 46.9923
759 | 858 | 480 | 71 | 13.2 | 15.2 | 0 | 0 | 0 | 213.6363 | 66.2332 | 0 | 19.4345 | 46.7987 | 0 | 0 | 0 | 0 | 0 | 213.6363 | 0 | 704.9674 | 55.27% | 19.4345 | 0 | 48.996 | 78.39% | 46.7987
760 | 855 | 352 | 51 | 12.8 | 14.5 | 0 | 0 | 0 | 197.0477 | 56.0023 | 0 | 8.0282 | 47.9741 | 0 | 0 | 0 | 0 | 0 | 197.0477 | 0 | 902.0152 | 70.72% | 8.0282 | 0 | 56.25 | 90% | 47.9741
761 | 650 | 165 | 36 | 11 | 13.3 | 0 | 0 | 0 | 118.4363 | 33.2987 | 0 | 0 | 33.2987 | 0 | 0 | 0 | 0 | 0 | 118.4363 | 0 | 1020.4514 | 80% | 0 | 16.7014 | 37.7661 | 60.43% | 50
762 | 46 | 11 | 7 | 12.5 | 11.8 | 0 | 0 | 0 | 0 | 1.543 | 0 | 0 | 1.543 | 0 | 0 | 0 | 85.0028 | 33.3554 | 0 | 85.0028 | 935.4486 | 73.34% | 0 | 15.1016 | 21.0526 | 33.68% | 50
763 | 0 | 0 | 0 | 10.7 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.4016 | 49.2331 | 0 | 121.4016 | 814.0471 | 63.82% | 0 | 0 | 21.0526 | 33.68% | 49.2331
764 | 0 | 0 | 0 | 10.6 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.322 | 46.172 | 0 | 114.322 | 699.725 | 54.86% | 0 | 0 | 21.0526 | 33.68% | 46.172
765 | 0 | 0 | 0 | 6.9 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.9631 | 42.5635 | 0 | 105.9631 | 593.7619 | 46.55% | 0 | 0 | 21.0526 | 33.68% | 42.5635
766 | 0 | 0 | 0 | 9.9 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4946 | 40.1695 | 0 | 100.4946 | 493.2673 | 38.67% | 0 | 0 | 21.0526 | 33.68% | 40.1695
767 | 0 | 0 | 0 | 10.6 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0447 | 37.352 | 0 | 94.0447 | 399.2226 | 31.3% | 0 | 0 | 21.0526 | 33.68% | 37.352
768 | 0 | 0 | 0 | 9.1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.2226 | 31.3% | 0 | 7.0335 | 13.2684 | 21.23% | 7.0335
769 | 0 | 0 | 0 | 7.8 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.2226 | 31.3% | 0 | 0 | 13.2684 | 21.23% | 0
770 | 0 | 0 | 0 | 11.7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.2226 | 31.3% | 0 | 0 | 13.2684 | 21.23% | 0
771 | 0 | 0 | 0 | 6.3 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.2226 | 31.3% | 0 | 0 | 13.2684 | 21.23% | 0
772 | 0 | 0 | 0 | 5.5 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.2226 | 31.3% | 0 | 0 | 13.2684 | 21.23% | 0
773 | 0 | 0 | 0 | 6.2 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.2226 | 31.3% | 0 | 0 | 13.2684 | 21.23% | 0
774 | 0 | 0 | 0 | 6.8 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2779 | 38.7726 | 0 | 97.2779 | 301.9448 | 23.67% | 0 | 0 | 13.2684 | 21.23% | 38.7726
775 | 0 | 0 | 0 | 7.2 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3417 | 42.7292 | 0 | 106.3417 | 195.6031 | 15.34% | 0 | 0 | 13.2684 | 21.23% | 42.7292
776 | 226 | 32 | 14 | 6.7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.9527 | 45.6051 | 0 | 112.9527 | 82.6504 | 6.48% | 0 | 0 | 13.2684 | 21.23% | 45.6051
777 | 304 | 117 | 47 | 6 | 9 | 0 | 0 | 0 | 0 | 13.9652 | 0 | 0 | 13.9652 | 0 | 0 | 0 | 82.6504 | 32.3753 | 0 | 82.6504 | 0 | 0% | 0 | 0 | 13.2684 | 21.23% | 46.3405
778 | 657 | 327 | 65 | 6.2 | 10.4 | 0 | 0 | 0 | 4.0562e-05 | 39.5755 | 7.0606e-06 | 0 | 39.5755 | 0 | 0 | 0 | 4.0562e-05 | 1.3783e-05 | 4.0562e-05 | 4.0562e-05 | 0 | 0% | 0 | 6.3416 | 6.25 | 10% | 45.9171
779 | 897 | 558 | 103 | 6 | 11.4 | 0 | 0 | 0 | 134.131 | 45.5982 | 19.8279 | 0 | 45.5982 | 0 | 0 | 0 | 4.0562e-05 | 1.3775e-05 | 134.131 | 4.0562e-05 | 134.1309 | 10.52% | 0 | 0 | 6.25 | 10% | 45.5982
780 | 945 | 630 | 83 | 3.9 | 11.8 | 0 | 0 | 0 | 249.8138 | 44.3336 | 27.6664 | 0 | 44.3336 | 0 | 0 | 0 | 0 | 0 | 249.8138 | 0 | 383.9447 | 30.1% | 0 | 0 | 6.25 | 10% | 44.3336
781 | 869 | 621 | 97 | 4.5 | 12.3 | 0 | 0 | 0 | 233.8381 | 58.8123 | 13.1877 | 16.4034 | 42.4089 | 0 | 0 | 0 | 0 | 0 | 233.8381 | 0 | 617.7828 | 48.43% | 16.4034 | 0 | 21.0714 | 33.71% | 42.4089
782 | 968 | 638 | 88 | 4.9 | 12.7 | 0 | 0 | 0 | 261.855 | 66.4563 | 5.5437 | 25 | 41.4563 | 0 | 0 | 0 | 0 | 0 | 261.855 | 0 | 879.6378 | 68.96% | 25 | 0 | 43.6604 | 69.86% | 41.4563
783 | 514 | 362 | 115 | 4.2 | 11.7 | 0 | 0 | 0 | 125.3606 | 47.5749 | 0 | 6.5865 | 40.9884 | 0 | 0 | 0 | 0 | 0 | 125.3606 | 0 | 1004.9984 | 78.79% | 6.5865 | 0 | 49.6117 | 79.38% | 40.9884
784 | 712 | 332 | 70 | 7.3 | 11.5 | 0 | 0 | 0 | 165.2239 | 50.0732 | 0 | 7.3468 | 42.7264 | 0 | 0 | 0 | 0 | 0 | 165.2239 | 0 | 1170.2223 | 91.75% | 7.3468 | 0 | 56.25 | 90% | 42.7264
785 | 569 | 162 | 49 | 6.1 | 10.2 | 0 | 0 | 0 | 105.2879 | 31.4493 | 0 | 0 | 31.4493 | 0 | 0 | 0 | 0 | 0 | 105.2879 | 0 | 1275.5102 | 100% | 0 | 14.2533 | 40.4754 | 64.76% | 45.7026
786 | 12 | 8 | 7 | 8.7 | 8.6 | 0 | 0 | 0 | 0 | 0.37801 | 0 | 0 | 0.37801 | 0 | 0 | 0 | 114.1209 | 46.1115 | 0 | 114.1209 | 1161.3893 | 91.05% | 0 | 0 | 40.4754 | 64.76% | 46.4895
787 | 0 | 0 | 0 | 5.8 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.4407 | 46.2583 | 0 | 114.4407 | 1046.9486 | 82.08% | 0 | 0 | 40.4754 | 64.76% | 46.2583
788 | 0 | 0 | 0 | 5.7 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.1582 | 44.3893 | 0 | 110.1582 | 936.7904 | 73.44% | 0 | 0 | 40.4754 | 64.76% | 44.3893
789 | 0 | 0 | 0 | 3.4 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6259 | 41.5399 | 0 | 103.6259 | 833.1645 | 65.32% | 0 | 0 | 40.4754 | 64.76% | 41.5399
790 | 0 | 0 | 0 | 2.5 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5948 | 38.4676 | 0 | 96.5948 | 736.5697 | 57.75% | 0 | 0 | 40.4754 | 64.76% | 38.4676
791 | 0 | 0 | 0 | 5.2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2451 | 35.2616 | 0 | 89.2451 | 647.3246 | 50.75% | 0 | 0 | 40.4754 | 64.76% | 35.2616
792 | 0 | 0 | 0 | 5.7 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3076 | 33.1099 | 0 | 84.3076 | 563.017 | 44.14% | 0 | 0 | 40.4754 | 64.76% | 33.1099
793 | 0 | 0 | 0 | 4.6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2225 | 31.7646 | 0 | 81.2225 | 481.7945 | 37.77% | 0 | 0 | 40.4754 | 64.76% | 31.7646
794 | 0 | 0 | 0 | 2.8 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481.7945 | 37.77% | 0 | 25 | 12.807 | 20.49% | 25
795 | 0 | 0 | 0 | 2.7 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481.7945 | 37.77% | 0 | 1.4656 | 11.185 | 17.9% | 1.4656
796 | 0 | 0 | 0 | 3.7 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.8736 | 46.0168 | 0 | 113.8736 | 367.9209 | 28.84% | 13.7495 | 0 | 23.6085 | 37.77% | 32.2673
797 | 0 | 0 | 0 | 2.6 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0323 | 33.4274 | 0 | 85.0323 | 282.8886 | 22.18% | 0 | 0 | 23.6085 | 37.77% | 33.4274
798 | 0 | 0 | 0 | 3.1 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1271 | 34.3424 | 0 | 87.1271 | 195.7614 | 15.35% | 0 | 0 | 23.6085 | 37.77% | 34.3424
799 | 0 | 0 | 0 | 3 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2568 | 37.4537 | 0 | 94.2568 | 101.5046 | 7.958% | 0 | 0 | 23.6085 | 37.77% | 37.4537
800 | 281 | 41 | 15 | 3.4 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5046 | 40.6165 | 0 | 101.5046 | 0 | 0% | 0 | 0 | 23.6085 | 37.77% | 40.6165
801 | 751 | 215 | 39 | 2.4 | 7.5 | 0 | 0 | 0 | 112.7211 | 26.3053 | 0 | 0 | 26.3053 | 0 | 0 | 0 | 0 | 0 | 112.7211 | 0 | 112.7211 | 8.837% | 0 | 15.6844 | 6.25 | 10% | 41.9897
802 | 895 | 399 | 50 | 3.3 | 8.8 | 0 | 0 | 0 | 189.6826 | 41.5357 | 7.0288 | 0 | 41.5357 | 0 | 0 | 0 | 0 | 0 | 189.6826 | 0 | 302.4037 | 23.71% | 0 | 0 | 6.25 | 10% | 41.5357
803 | 975 | 550 | 54 | 3.9 | 9.8 | 0 | 0 | 0 | 242.8163 | 41.675 | 23.0315 | 0 | 41.675 | 0 | 0 | 0 | 0 | 0 | 242.8163 | 0 | 545.22 | 42.75% | 0 | 0 | 6.25 | 10% | 41.675
804 | 1005 | 642 | 56 | 4.9 | 10.7 | 0 | 0 | 0 | 0 | 41.4257 | 30.5743 | 0 | 41.4257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545.22 | 42.75% | 0 | 0 | 6.25 | 10% | 41.4257
805 | 1012 | 669 | 58 | 4.8 | 11.7 | 0 | 0 | 0 | 275.5599 | 39.5177 | 32.4823 | 0 | 39.5177 | 0 | 0 | 0 | 0 | 0 | 275.5599 | 0 | 820.7799 | 64.35% | 0 | 0 | 6.25 | 10% | 39.5177
806 | 1001 | 629 | 56 | 5.1 | 12.1 | 0 | 0 | 0 | 0 | 52.9722 | 19.0278 | 14.5241 | 38.4481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820.7799 | 64.35% | 14.5241 | 0 | 19.3734 | 31% | 38.4481
807 | 961 | 524 | 54 | 4.3 | 12.4 | 0 | 0 | 0 | 240.1813 | 63.0916 | 6.8096 | 25 | 38.0916 | 0 | 0 | 0 | 0 | 0 | 240.1813 | 0 | 1060.9612 | 83.18% | 25 | 0 | 41.9624 | 67.14% | 38.0916
808 | 883 | 368 | 47 | 3.3 | 12.4 | 0 | 0 | 0 | 214.549 | 55.8803 | 0 | 15.8125 | 40.0678 | 0 | 0 | 0 | 0 | 0 | 214.549 | 0 | 1275.5102 | 100% | 15.8125 | 0 | 56.25 | 90% | 40.0678
809 | 711 | 179 | 34 | 3.7 | 11.5 | 0 | 0 | 0 | 0 | 35.5742 | 0 | 0 | 35.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 8.8987 | 46.4016 | 74.24% | 44.4729
810 | 176 | 22 | 8 | 2.3 | 9.5 | 0 | 0 | 0 | 0 | 5.0005 | 0 | 0 | 5.0005 | 0 | 0 | 0 | 104.0055 | 41.6853 | 0 | 104.0055 | 1171.5047 | 91.85% | 0 | 0 | 46.4016 | 74.24% | 46.6859
811 | 0 | 0 | 0 | 1.7 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.4341 | 46.6901 | 0 | 115.4341 | 1056.0706 | 82.8% | 0 | 0 | 46.4016 | 74.24% | 46.6901
812 | 0 | 0 | 0 | 1.7 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.7913 | 45.108 | 0 | 111.7913 | 944.2793 | 74.03% | 0 | 0 | 46.4016 | 74.24% | 45.108
813 | 0 | 0 | 0 | 1.1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.7829 | 41.6095 | 0 | 103.7829 | 840.4964 | 65.89% | 0 | 0 | 46.4016 | 74.24% | 41.6095
814 | 0 | 0 | 0 | 1.7 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0045 | 37.7726 | 0 | 95.0045 | 745.4919 | 58.45% | 0 | 0 | 46.4016 | 74.24% | 37.7726
815 | 0 | 0 | 0 | 0.8 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0384 | 35.1488 | 0 | 89.0384 | 656.4534 | 51.47% | 0 | 0 | 46.4016 | 74.24% | 35.1488
816 | 0 | 0 | 0 | 1.9 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 656.4534 | 51.47% | 0 | 6.8054 | 38.8698 | 62.19% | 6.8054
817 | 0 | 0 | 0 | 1.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 656.4534 | 51.47% | 0 | 0 | 38.8698 | 62.19% | 0
818 | 0 | 0 | 0 | 0.9 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 656.4534 | 51.47% | 0 | 0 | 38.8698 | 62.19% | 0
819 | 0 | 0 | 0 | 2.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9493 | 34.2241 | 0 | 86.9493 | 569.5041 | 44.65% | 0 | 0 | 38.8698 | 62.19% | 34.2241
820 | 0 | 0 | 0 | 2.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2117 | 38.7099 | 0 | 97.2117 | 472.2924 | 37.03% | 0 | 0 | 38.8698 | 62.19% | 38.7099
821 | 0 | 0 | 0 | 2.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1173 | 46.0606 | 0 | 114.1173 | 358.1751 | 28.08% | 0 | 0 | 38.8698 | 62.19% | 46.0606
822 | 0 | 0 | 0 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1979 | 50 | 0 | 123.1979 | 234.9772 | 18.42% | 0 | 0 | 38.8698 | 62.19% | 50
823 | 0 | 0 | 0 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.8353 | 45.043 | 0 | 111.8353 | 123.1419 | 9.654% | 0 | 4.957 | 33.3837 | 53.41% | 50
824 | 299 | 43 | 14 | 2.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1419 | 50 | 0 | 123.1419 | 0 | 0% | 0 | 0 | 33.3837 | 53.41% | 50
825 | 789 | 223 | 37 | 1.3 | 6.1 | 0 | 0 | 0 | 120.749 | 27.2575 | 0 | 0 | 27.2575 | 0 | 0 | 0 | 0 | 0 | 120.749 | 0 | 120.749 | 9.467% | 0 | 22.7425 | 8.2139 | 13.14% | 50
826 | 929 | 411 | 47 | 0.9 | 9.7 | 0 | 0 | 0 | 199.6291 | 48.2255 | 0 | 0 | 48.2255 | 0 | 0 | 0 | 0 | 0 | 199.6291 | 0 | 320.3781 | 25.12% | 0 | 1.7745 | 6.25 | 10% | 50
827 | 989 | 558 | 52 | 3.4 | 11.2 | 0 | 0 | 0 | 247.534 | 64.7513 | 0 | 14.7513 | 50 | 0 | 0 | 0 | 0 | 0 | 247.534 | 0 | 567.9121 | 44.52% | 14.7513 | 0 | 19.5787 | 31.33% | 50
828 | 1012 | 648 | 55 | 3.5 | 12.8 | 0 | 0 | 0 | 270.1666 | 50 | 22 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 270.1666 | 0 | 838.0786 | 65.71% | 0 | 0 | 19.5787 | 31.33% | 50
829 | 1006 | 671 | 59 | 3.9 | 13.6 | 0 | 0 | 0 | 274.9398 | 72 | 0 | 22.792 | 49.208 | 0 | 0 | 0 | 0 | 0 | 274.9398 | 0 | 1113.0184 | 87.26% | 22.792 | 0 | 40.1726 | 64.28% | 49.208
830 | 992 | 629 | 58 | 4.6 | 14.3 | 0 | 0 | 0 | 0 | 61.1331 | 10.8669 | 12.3985 | 48.7345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113.0184 | 87.26% | 12.3985 | 0 | 51.3754 | 82.2% | 48.7345
831 | 950 | 523 | 54 | 4.8 | 14.3 | 0 | 0 | 0 | 0 | 48.4908 | 20.6293 | 0 | 48.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113.0184 | 87.26% | 0 | 0 | 51.3754 | 82.2% | 48.4908
832 | 863 | 365 | 48 | 4.4 | 14.1 | 0 | 0 | 0 | 162.4918 | 55.0862 | 0 | 5.3948 | 49.6913 | 0 | 0 | 0 | 0 | 0 | 162.4918 | 0 | 1275.5102 | 100% | 5.3948 | 0 | 56.25 | 90% | 49.6913
833 | 669 | 176 | 36 | 4.3 | 12.8 | 0 | 0 | 0 | 0 | 33.9226 | 0 | 0 | 33.9226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 16.0773 | 38.4567 | 61.53% | 50
834 | 157 | 22 | 9 | 3.3 | 10.4 | 0 | 0 | 0 | 0 | 4.7077 | 0 | 0 | 4.7077 | 0 | 0 | 0 | 112.3148 | 45.2923 | 0 | 112.3148 | 1163.1954 | 91.19% | 0 | 0 | 38.4567 | 61.53% | 50
835 | 0 | 0 | 0 | 1.7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0236 | 50 | 0 | 123.0236 | 1040.1718 | 81.55% | 0 | 0 | 38.4567 | 61.53% | 50
836 | 0 | 0 | 0 | 0.5 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9868 | 0 | 127.551 | 912.6208 | 71.55% | 3.7801 | 0 | 41.8722 | 67% | 48.2067
837 | 0 | 0 | 0 | 0.9 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3218 | 43.5899 | 0 | 108.3218 | 804.299 | 63.06% | 0 | 0 | 41.8722 | 67% | 43.5899
838 | 0 | 0 | 0 | 1.2 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0983 | 40.4299 | 0 | 101.0983 | 703.2007 | 55.13% | 0 | 0 | 41.8722 | 67% | 40.4299
839 | 0 | 0 | 0 | 2.4 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.9221 | 48.2191 | 0 | 118.9221 | 584.2786 | 45.81% | 10.7668 | 0 | 51.6006 | 82.56% | 37.4523
840 | 0 | 0 | 0 | 2.2 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.2786 | 45.81% | 0 | 12.2652 | 38.0263 | 60.84% | 12.2652
841 | 0 | 0 | 0 | 1.2 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.2786 | 45.81% | 0 | 0 | 38.0263 | 60.84% | 0
842 | 0 | 0 | 0 | 0.7 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.2786 | 45.81% | 0 | 0 | 38.0263 | 60.84% | 0
843 | 0 | 0 | 0 | 1.1 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584.2786 | 45.81% | 0 | 0 | 38.0263 | 60.84% | 0
844 | 0 | 0 | 0 | 1.8 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.9709 | 39.9369 | 0 | 99.9709 | 484.3078 | 37.97% | 0 | 0 | 38.0263 | 60.84% | 39.9369
845 | 0 | 0 | 0 | 1.5 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.1824 | 46.5675 | 0 | 115.1824 | 369.1254 | 28.94% | 0 | 0 | 38.0263 | 60.84% | 46.5675
846 | 0 | 0 | 0 | 1.1 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0295 | 50 | 0 | 123.0295 | 246.0959 | 19.29% | 0 | 0 | 38.0263 | 60.84% | 50
847 | 0 | 0 | 0 | 0.9 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0461 | 50 | 0 | 123.0461 | 123.0498 | 9.647% | 0 | 0 | 38.0263 | 60.84% | 50
848 | 282 | 43 | 15 | 0.2 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0498 | 50 | 0 | 123.0498 | 0 | 0% | 0 | 0 | 38.0263 | 60.84% | 50
849 | 740 | 215 | 38 | 0.6 | 10.5 | 0 | 0 | 0 | 113.3285 | 25.3646 | 0 | 0 | 25.3646 | 0 | 0 | 0 | 0 | 0 | 113.3285 | 0 | 113.3285 | 8.885% | 0 | 24.6354 | 10.7615 | 17.22% | 50
850 | 898 | 402 | 46 | 0.7 | 14 | 0 | 0 | 0 | 0 | 45.9235 | 0 | 0 | 45.9235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3285 | 8.885% | 0 | 4.0765 | 6.25 | 10% | 50
851 | 964 | 549 | 51 | 1 | 15.9 | 0 | 0 | 0 | 242.5047 | 50 | 9.8813 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 242.5047 | 0 | 355.8332 | 27.9% | 0 | 0 | 6.25 | 10% | 50
852 | 992 | 639 | 54 | 2.3 | 17.4 | 0 | 0 | 0 | 265.7699 | 70.318 | 0 | 21.7408 | 48.5772 | 0 | 0 | 0 | 0 | 0 | 265.7699 | 0 | 621.6031 | 48.73% | 21.7408 | 0 | 25.8941 | 41.43% | 48.5772
853 | 999 | 666 | 55 | 2.8 | 18.2 | 0 | 0 | 0 | 0 | 53.4472 | 18.5528 | 5.8673 | 47.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621.6031 | 48.73% | 5.8673 | 0 | 31.1956 | 49.91% | 47.58
854 | 985 | 626 | 55 | 2.8 | 18.9 | 0 | 0 | 0 | 190.9758 | 47.0884 | 24.9116 | 0 | 47.0884 | 0 | 0 | 0 | 0 | 0 | 190.9758 | 0 | 812.579 | 63.71% | 0 | 0 | 31.1956 | 49.91% | 47.0884
855 | 951 | 524 | 52 | 4.2 | 18.8 | 0 | 0 | 0 | 250.2008 | 67.7062 | 0 | 20.8003 | 46.9059 | 0 | 0 | 0 | 0 | 0 | 250.2008 | 0 | 1062.7798 | 83.32% | 20.8003 | 0 | 49.9899 | 79.98% | 46.9059
856 | 877 | 371 | 46 | 4.6 | 18.5 | 0 | 0 | 0 | 212.7304 | 54.9887 | 0 | 6.9283 | 48.0605 | 0 | 0 | 0 | 0 | 0 | 212.7304 | 0 | 1275.5102 | 100% | 6.9283 | 0 | 56.25 | 90% | 48.0605
857 | 700 | 182 | 34 | 4.2 | 17 | 0 | 0 | 0 | 0 | 34.6355 | 0 | 0 | 34.6355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 15.3645 | 39.2456 | 62.79% | 50
858 | 185 | 24 | 9 | 2.8 | 14 | 0 | 0 | 0 | 0 | 5.3255 | 0 | 0 | 5.3255 | 0 | 0 | 0 | 110.6691 | 44.4589 | 0 | 110.6691 | 1164.8411 | 91.32% | 0 | 0.21553 | 39.0071 | 62.41% | 50
859 | 0 | 0 | 0 | 1.6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1167 | 50 | 0 | 123.1167 | 1041.7244 | 81.67% | 0 | 0 | 39.0071 | 62.41% | 50
860 | 0 | 0 | 0 | 0.9 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.8692 | 47.7471 | 0 | 117.8692 | 923.8552 | 72.43% | 0 | 0 | 39.0071 | 62.41% | 47.7471
861 | 0 | 0 | 0 | 0.8 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.2097 | 43.1067 | 0 | 107.2097 | 816.6455 | 64.03% | 0 | 0 | 39.0071 | 62.41% | 43.1067
862 | 0 | 0 | 0 | 0.8 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.8357 | 39.8895 | 0 | 99.8357 | 716.8098 | 56.2% | 0 | 0 | 39.0071 | 62.41% | 39.8895
863 | 0 | 0 | 0 | 0.4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5007 | 37.1195 | 0 | 93.5007 | 623.3091 | 48.87% | 0 | 0 | 39.0071 | 62.41% | 37.1195
864 | 0 | 0 | 0 | 0.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.3091 | 48.87% | 0 | 0 | 39.0071 | 62.41% | 0
865 | 0 | 0 | 0 | 1.1 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.3091 | 48.87% | 0 | 0 | 39.0071 | 62.41% | 0
866 | 0 | 0 | 0 | 0.8 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.3091 | 48.87% | 0 | 0 | 39.0071 | 62.41% | 0
867 | 0 | 0 | 0 | 0.4 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.8984 | 14.6001 | 0 | 41.8984 | 581.4107 | 45.58% | 0 | 0 | 39.0071 | 62.41% | 14.6001
868 | 0 | 0 | 0 | 0.5 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9313 | 39.494 | 0 | 98.9313 | 482.4794 | 37.83% | 0 | 0 | 39.0071 | 62.41% | 39.494
869 | 0 | 0 | 0 | 0.3 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.0627 | 46.0982 | 0 | 114.0627 | 368.4167 | 28.88% | 0 | 0 | 39.0071 | 62.41% | 46.0982
870 | 0 | 0 | 0 | 0.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.4131 | 49.7401 | 0 | 122.4131 | 246.0035 | 19.29% | 0 | 0 | 39.0071 | 62.41% | 49.7401
871 | 0 | 0 | 0 | 0.6 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0022 | 50 | 0 | 123.0022 | 123.0013 | 9.643% | 0 | 0 | 39.0071 | 62.41% | 50
872 | 279 | 44 | 15 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0013 | 50 | 0 | 123.0013 | 0 | 0% | 0 | 0 | 39.0071 | 62.41% | 50
873 | 734 | 216 | 37 | 0.3 | 13.2 | 0 | 0 | 0 | 0 | 24.8358 | 0 | 0 | 24.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 11.3388 | 18.14% | 49.8358
874 | 877 | 398 | 48 | 0.6 | 15.7 | 0 | 0 | 0 | 0 | 44.858 | 0 | 0 | 44.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 4.598 | 6.25 | 10% | 49.4559
875 | 949 | 545 | 51 | 1.6 | 17.9 | 0 | 0 | 0 | 147.1403 | 49.034 | 10.5294 | 0 | 49.034 | 0 | 0 | 0 | 0 | 0 | 147.1403 | 0 | 147.1403 | 11.54% | 0 | 0 | 6.25 | 10% | 49.034
876 | 979 | 635 | 53 | 2.2 | 18.8 | 0 | 0 | 0 | 0 | 47.5577 | 21.497 | 0 | 47.5577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.1403 | 11.54% | 0 | 0 | 6.25 | 10% | 47.5577
877 | 988 | 662 | 54 | 2.5 | 19.4 | 0 | 0 | 0 | 271.2617 | 71.6608 | 0.33919 | 25 | 46.6608 | 0 | 0 | 0 | 0 | 0 | 271.2617 | 0 | 418.402 | 32.8% | 25 | 0 | 28.839 | 46.14% | 46.6608
878 | 977 | 624 | 53 | 3.4 | 19.9 | 0 | 0 | 0 | 266.9936 | 71.1316 | 0.86842 | 25 | 46.1316 | 0 | 0 | 0 | 0 | 0 | 266.9936 | 0 | 685.3956 | 53.74% | 25 | 0 | 51.428 | 82.28% | 46.1316
879 | 932 | 519 | 52 | 4 | 20 | 0 | 0 | 0 | 245.5148 | 45.7918 | 20.426 | 0 | 45.7918 | 0 | 0 | 0 | 0 | 0 | 245.5148 | 0 | 930.9104 | 72.98% | 0 | 0 | 51.428 | 82.28% | 45.7918
880 | 859 | 367 | 46 | 5.2 | 19.3 | 0 | 0 | 0 | 207.8641 | 52.2927 | 1.8032 | 5.3367 | 46.9561 | 0 | 0 | 0 | 0 | 0 | 207.8641 | 0 | 1138.7745 | 89.28% | 5.3367 | 0 | 56.25 | 90% | 46.9561
881 | 696 | 183 | 34 | 5.4 | 17.8 | 0 | 0 | 0 | 136.7357 | 34.5665 | 0 | 0 | 34.5665 | 0 | 0 | 0 | 0 | 0 | 136.7357 | 0 | 1275.5102 | 100% | 0 | 15.4336 | 39.1692 | 62.67% | 50
882 | 190 | 25 | 9 | 3.9 | 15.3 | 0 | 0 | 0 | 0 | 5.4449 | 0 | 0 | 5.4449 | 0 | 0 | 0 | 111.0278 | 44.5551 | 0 | 111.0278 | 1164.4824 | 91.3% | 0 | 0 | 39.1692 | 62.67% | 50
883 | 0 | 0 | 0 | 1.3 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2889 | 50 | 0 | 123.2889 | 1041.1935 | 81.63% | 0 | 0 | 39.1692 | 62.67% | 50
884 | 0 | 0 | 0 | 0.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.1203 | 46.5243 | 0 | 115.1203 | 926.0733 | 72.6% | 0 | 0 | 39.1692 | 62.67% | 46.5243
885 | 0 | 0 | 0 | 0.6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9162 | 42.09 | 0 | 104.9162 | 821.1571 | 64.38% | 0 | 0 | 39.1692 | 62.67% | 42.09
886 | 0 | 0 | 0 | 0.3 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.782 | 38.9829 | 0 | 97.782 | 723.3751 | 56.71% | 0 | 0 | 39.1692 | 62.67% | 38.9829
887 | 0 | 0 | 0 | 1.5 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5096 | 36.6822 | 0 | 92.5096 | 630.8655 | 49.46% | 0.26462 | 0 | 39.4083 | 63.05% | 36.4175
888 | 0 | 0 | 0 | 1.3 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.8083 | 20.2319 | 0 | 54.8083 | 576.0572 | 45.16% | 0 | 0 | 39.4083 | 63.05% | 20.2319
889 | 0 | 0 | 0 | 1.8 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.0572 | 45.16% | 0 | 0 | 39.4083 | 63.05% | 0
890 | 0 | 0 | 0 | 2.4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.0572 | 45.16% | 0 | 0 | 39.4083 | 63.05% | 0
891 | 0 | 0 | 0 | 1.6 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.0572 | 45.16% | 0 | 0 | 39.4083 | 63.05% | 0
892 | 0 | 0 | 0 | 1.6 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3637 | 38.8088 | 0 | 97.3637 | 478.6935 | 37.53% | 0 | 0 | 39.4083 | 63.05% | 38.8088
893 | 0 | 0 | 0 | 2.4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.011 | 45.1971 | 0 | 112.011 | 366.6825 | 28.75% | 0 | 0 | 39.4083 | 63.05% | 45.1971
894 | 0 | 0 | 0 | 2 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.625 | 48.9615 | 0 | 120.625 | 246.0575 | 19.29% | 0 | 0 | 39.4083 | 63.05% | 48.9615
895 | 0 | 0 | 0 | 2.2 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0043 | 50 | 0 | 123.0043 | 123.0532 | 9.647% | 0 | 0 | 39.4083 | 63.05% | 50
896 | 109 | 39 | 28 | 2.3 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0532 | 50 | 0 | 123.0532 | 0 | 0% | 0 | 0 | 39.4083 | 63.05% | 50
897 | 436 | 188 | 76 | 1.4 | 12.1 | 0 | 0 | 0 | 60.2067 | 19.9968 | 0 | 0 | 19.9968 | 0 | 0 | 0 | 0 | 0 | 60.2067 | 0 | 60.2067 | 4.72% | 0 | 25 | 11.7399 | 18.78% | 44.9968
898 | 749 | 406 | 102 | 1 | 15.9 | 0 | 0 | 0 | 0 | 44.462 | 0 | 0 | 44.462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.2067 | 4.72% | 0 | 4.9605 | 6.25 | 10% | 49.4225
899 | 616 | 472 | 145 | 0.8 | 17.9 | 0 | 0 | 0 | 149.3962 | 49.0251 | 0 | 0.23486 | 48.7902 | 0 | 0 | 0 | 0 | 0 | 149.3962 | 0 | 209.6029 | 16.43% | 0.23486 | 0 | 6.4622 | 10.34% | 48.7902
900 | 815 | 620 | 128 | 1.7 | 19.2 | 0 | 0 | 0 | 82.9827 | 65.4624 | 0 | 18.1818 | 47.2806 | 0 | 0 | 0 | 0 | 0 | 82.9827 | 0 | 292.5856 | 22.94% | 18.1818 | 0 | 22.8906 | 36.62% | 47.2806
901 | 772 | 653 | 170 | 2.5 | 19.4 | 0 | 0 | 0 | 208.1832 | 46.4951 | 23.3082 | 0 | 46.4951 | 0 | 0 | 0 | 0 | 0 | 208.1832 | 0 | 500.7688 | 39.26% | 0 | 0 | 22.8906 | 36.62% | 46.4951
902 | 773 | 589 | 134 | 3.6 | 19.6 | 0 | 0 | 0 | 207.3538 | 57.1207 | 10.7072 | 11.1827 | 45.938 | 0 | 0 | 0 | 0 | 0 | 207.3538 | 0 | 708.1226 | 55.52% | 11.1827 | 0 | 32.9948 | 52.79% | 45.938
903 | 916 | 522 | 59 | 3.6 | 19.8 | 0 | 0 | 0 | 241.778 | 65.708 | 0 | 20.1377 | 45.5703 | 0 | 0 | 0 | 0 | 0 | 241.778 | 0 | 949.9007 | 74.47% | 20.1377 | 0 | 51.1905 | 81.9% | 45.5703
904 | 822 | 366 | 53 | 3.6 | 19.4 | 0 | 0 | 0 | 199.9761 | 52.2116 | 0 | 5.5996 | 46.6121 | 0 | 0 | 0 | 0 | 0 | 199.9761 | 0 | 1149.8768 | 90.15% | 5.5996 | 0 | 56.25 | 90% | 46.6121
905 | 638 | 181 | 40 | 3.7 | 17.8 | 0 | 0 | 0 | 125.6334 | 32.7875 | 0 | 0 | 32.7875 | 0 | 0 | 0 | 0 | 0 | 125.6334 | 0 | 1275.5102 | 100% | 0 | 17.2125 | 37.2004 | 59.52% | 50
906 | 175 | 26 | 11 | 2.3 | 15 | 0 | 0 | 0 | 0 | 5.3636 | 0 | 0 | 5.3636 | 0 | 0 | 0 | 108.6648 | 43.5431 | 0 | 108.6648 | 1166.8454 | 91.48% | 0 | 1.0933 | 35.9904 | 57.58% | 50
907 | 0 | 0 | 0 | 0.6 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2366 | 50 | 0 | 123.2366 | 1043.6088 | 81.82% | 0 | 0 | 35.9904 | 57.58% | 50
908 | 0 | 0 | 0 | 0.9 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.2462 | 46.5633 | 0 | 115.2462 | 928.3626 | 72.78% | 0 | 0 | 35.9904 | 57.58% | 46.5633
909 | 0 | 0 | 0 | 1.8 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3671 | 42.2724 | 0 | 105.3671 | 822.9955 | 64.52% | 0 | 0 | 35.9904 | 57.58% | 42.2724
910 | 0 | 0 | 0 | 2.2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5931 | 39.3088 | 0 | 98.5931 | 724.4024 | 56.79% | 0 | 0 | 35.9904 | 57.58% | 39.3088
911 | 0 | 0 | 0 | 3 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.214 | 36.4997 | 0 | 92.214 | 632.1884 | 49.56% | 0 | 0 | 35.9904 | 57.58% | 36.4997
912 | 0 | 0 | 0 | 1.8 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.557 | 20.5455 | 0 | 55.557 | 576.6314 | 45.21% | 0 | 0 | 35.9904 | 57.58% | 20.5455
913 | 0 | 0 | 0 | 1.2 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6314 | 45.21% | 0 | 0 | 35.9904 | 57.58% | 0
914 | 0 | 0 | 0 | 1.6 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6314 | 45.21% | 0 | 0 | 35.9904 | 57.58% | 0
915 | 0 | 0 | 0 | 1.8 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.6314 | 45.21% | 0 | 0 | 35.9904 | 57.58% | 0
916 | 0 | 0 | 0 | 2.3 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4436 | 38.8213 | 0 | 97.4436 | 479.1878 | 37.57% | 0 | 0 | 35.9904 | 57.58% | 38.8213
917 | 0 | 0 | 0 | 2.5 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.6488 | 45.4575 | 0 | 112.6488 | 366.539 | 28.74% | 0 | 0 | 35.9904 | 57.58% | 45.4575
918 | 0 | 0 | 0 | 2.4 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.458 | 48.871 | 0 | 120.458 | 246.081 | 19.29% | 0 | 0 | 35.9904 | 57.58% | 48.871
919 | 0 | 0 | 0 | 2.4 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0353 | 50 | 0 | 123.0353 | 123.0456 | 9.647% | 0 | 0 | 35.9904 | 57.58% | 50
920 | 255 | 46 | 17 | 2.8 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0456 | 50 | 0 | 123.0456 | 0 | 0% | 0 | 0 | 35.9904 | 57.58% | 50
921 | 708 | 221 | 43 | 1.3 | 12.2 | 0 | 0 | 0 | 0 | 25.0094 | 0 | 0 | 25.0094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 24.8978 | 8.4351 | 13.5% | 49.9072
922 | 859 | 407 | 56 | 2.8 | 14.5 | 0 | 0 | 0 | 0 | 46.8451 | 0 | 0 | 46.8451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 1.9744 | 6.25 | 10% | 48.8195
923 | 932 | 555 | 62 | 3.4 | 16 | 0 | 0 | 0 | 233.7143 | 48.3418 | 13.2762 | 0 | 48.3418 | 0 | 0 | 0 | 0 | 0 | 233.7143 | 0 | 233.7143 | 18.32% | 0 | 0 | 6.25 | 10% | 48.3418
924 | 960 | 646 | 67 | 1.5 | 17.2 | 0 | 0 | 0 | 258.6434 | 46.5954 | 21.9411 | 0 | 46.5954 | 0 | 0 | 0 | 0 | 0 | 258.6434 | 0 | 492.3576 | 38.6% | 0 | 0 | 6.25 | 10% | 46.5954
925 | 966 | 672 | 68 | 1.6 | 18.6 | 0 | 0 | 0 | 265.831 | 45.4506 | 26.5494 | 0 | 45.4506 | 0 | 0 | 0 | 0 | 0 | 265.831 | 0 | 758.1886 | 59.44% | 0 | 0 | 6.25 | 10% | 45.4506
926 | 950 | 631 | 68 | 2.6 | 19.3 | 0 | 0 | 0 | 260.1066 | 69.9673 | 2.0327 | 25 | 44.9673 | 0 | 0 | 0 | 0 | 0 | 260.1066 | 0 | 1018.2952 | 79.83% | 25 | 0 | 28.839 | 46.14% | 44.9673
927 | 933 | 534 | 59 | 3.5 | 19.6 | 0 | 0 | 0 | 247.2995 | 66.7694 | 0 | 22.2575 | 44.5119 | 0 | 0 | 0 | 0 | 0 | 247.2995 | 0 | 1265.5948 | 99.22% | 22.2575 | 0 | 48.95 | 78.32% | 44.5119
928 | 860 | 380 | 51 | 4.3 | 19.3 | 0 | 0 | 0 | 0 | 53.5618 | 0.87809 | 8.0792 | 45.4826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.5948 | 99.22% | 8.0792 | 0 | 56.25 | 90% | 45.4826
929 | 670 | 189 | 38 | 3.9 | 18 | 0 | 0 | 0 | 9.9154 | 33.7022 | 0 | 0 | 33.7022 | 0 | 0 | 0 | 0 | 0 | 9.9154 | 0 | 1275.5102 | 100% | 0 | 14.9627 | 39.6903 | 63.5% | 48.6649
930 | 171 | 26 | 11 | 2.9 | 14.5 | 0 | 0 | 0 | 0 | 5.2912 | 0 | 0 | 5.2912 | 0 | 0 | 0 | 91.767 | 36.2201 | 0 | 91.767 | 1183.7432 | 92.81% | 0 | 7.5352 | 31.3509 | 50.16% | 49.0465
931 | 0 | 0 | 0 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.3533 | 48.346 | 0 | 119.3533 | 1064.39 | 83.45% | 0 | 0 | 31.3509 | 50.16% | 48.346
932 | 0 | 0 | 0 | 1.2 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.546 | 45.4143 | 0 | 112.546 | 951.8439 | 74.62% | 0 | 0 | 31.3509 | 50.16% | 45.4143
933 | 0 | 0 | 0 | 1.2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0671 | 41.7195 | 0 | 104.0671 | 847.7768 | 66.47% | 0 | 0 | 31.3509 | 50.16% | 41.7195
934 | 0 | 0 | 0 | 0.4 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4244 | 39.2642 | 0 | 98.4244 | 749.3524 | 58.75% | 0 | 0 | 31.3509 | 50.16% | 39.2642
935 | 0 | 0 | 0 | 0.2 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.127 | 36.5248 | 0 | 92.127 | 657.2254 | 51.53% | 0 | 0 | 31.3509 | 50.16% | 36.5248
936 | 0 | 0 | 0 | 1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6304 | 34.5597 | 0 | 87.6304 | 569.595 | 44.66% | 0 | 0 | 31.3509 | 50.16% | 34.5597
937 | 0 | 0 | 0 | 1.4 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.595 | 44.66% | 0 | 0 | 31.3509 | 50.16% | 0
938 | 0 | 0 | 0 | 1.8 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569.595 | 44.66% | 0 | 4.7045 | 26.1442 | 41.83% | 4.7045
939 | 0 | 0 | 0 | 0.9 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3972 | 32.7144 | 0 | 83.3972 | 486.1978 | 38.12% | 0 | 0 | 26.1442 | 41.83% | 32.7144
940 | 0 | 0 | 0 | 1.7 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6823 | 33.7115 | 0 | 85.6823 | 400.5155 | 31.4% | 0 | 0 | 26.1442 | 41.83% | 33.7115
941 | 0 | 0 | 0 | 2.3 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2923 | 35.724 | 0 | 90.2923 | 310.2232 | 24.32% | 0 | 0 | 26.1442 | 41.83% | 35.724
942 | 0 | 0 | 0 | 2.9 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4565 | 37.976 | 0 | 95.4565 | 214.7666 | 16.84% | 0 | 0 | 26.1442 | 41.83% | 37.976
943 | 0 | 0 | 0 | 2.3 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5974 | 41.9674 | 0 | 104.5974 | 110.1692 | 8.637% | 0 | 0 | 26.1442 | 41.83% | 41.9674
944 | 290 | 52 | 18 | 2.3 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.1692 | 44.3963 | 0 | 110.1692 | 0 | 0% | 0 | 0 | 26.1442 | 41.83% | 44.3963
945 | 750 | 234 | 43 | 0.9 | 9.8 | 0 | 0 | 0 | 0 | 26.3845 | 0 | 0 | 26.3845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 17.9756 | 6.25 | 10% | 44.3601
946 | 898 | 424 | 55 | 0.7 | 14.7 | 0 | 0 | 0 | 0 | 43.466 | 3.2434 | 0 | 43.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 43.466
947 | 963 | 574 | 61 | 1.7 | 16.7 | 0 | 0 | 0 | 0 | 43.1819 | 18.4483 | 0 | 43.1819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 43.1819
948 | 997 | 669 | 63 | 2.2 | 18 | 0 | 0 | 0 | 269.4273 | 42.0022 | 29.2719 | 0 | 42.0022 | 0 | 0 | 0 | 0 | 0 | 269.4273 | 0 | 269.4273 | 21.12% | 0 | 0 | 6.25 | 10% | 42.0022
949 | 1000 | 694 | 65 | 2.8 | 18.1 | 0 | 0 | 0 | 159.7026 | 40.1917 | 31.8083 | 0 | 40.1917 | 0 | 0 | 0 | 0 | 0 | 159.7026 | 0 | 429.1299 | 33.64% | 0 | 0 | 6.25 | 10% | 40.1917
950 | 987 | 654 | 64 | 2.9 | 19 | 0 | 0 | 0 | 271.0099 | 55.4793 | 16.5207 | 16.4699 | 39.0093 | 0 | 0 | 0 | 0 | 0 | 271.0099 | 0 | 700.1398 | 54.89% | 16.4699 | 0 | 21.1316 | 33.81% | 39.0093
951 | 937 | 546 | 63 | 3.4 | 19 | 0 | 0 | 0 | 249.0555 | 63.5317 | 3.9404 | 25 | 38.5317 | 0 | 0 | 0 | 0 | 0 | 249.0555 | 0 | 949.1953 | 74.42% | 25 | 0 | 43.7206 | 69.95% | 38.5317
952 | 832 | 385 | 61 | 4.1 | 18 | 0 | 0 | 0 | 202.9055 | 54.0292 | 8.8818e-15 | 13.8668 | 40.1625 | 0 | 0 | 0 | 0 | 0 | 202.9055 | 0 | 1152.1008 | 90.32% | 13.8668 | 0 | 56.25 | 90% | 40.1625
953 | 624 | 192 | 48 | 3.8 | 16.1 | 0 | 0 | 0 | 123.4094 | 33.2211 | 0 | 0 | 33.2211 | 0 | 0 | 0 | 0 | 0 | 123.4094 | 0 | 1275.5102 | 100% | 0 | 10.3688 | 44.7745 | 71.64% | 43.5899
954 | 153 | 28 | 14 | 2.3 | 13.4 | 0 | 0 | 0 | 0 | 5.2611 | 0 | 0 | 5.2611 | 0 | 0 | 0 | 56.5185 | 20.9188 | 0 | 56.5185 | 1218.9917 | 95.57% | 0 | 18.46 | 24.3441 | 38.95% | 44.64
955 | 0 | 0 | 0 | 1.1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.7751 | 44.6066 | 0 | 110.7751 | 1108.2166 | 86.88% | 0 | 0 | 24.3441 | 38.95% | 44.6066
956 | 0 | 0 | 0 | 0.9 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.6826 | 42.8532 | 0 | 106.6826 | 1001.534 | 78.52% | 0 | 0 | 24.3441 | 38.95% | 42.8532
957 | 0 | 0 | 0 | 0.8 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.6597 | 39.799 | 0 | 99.6597 | 901.8742 | 70.71% | 0 | 0 | 24.3441 | 38.95% | 39.799
958 | 0 | 0 | 0 | 0.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.141 | 36.9649 | 0 | 93.141 | 808.7332 | 63.4% | 0 | 0 | 24.3441 | 38.95% | 36.9649
959 | 0 | 0 | 0 | 1 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8891 | 34.2352 | 0 | 86.8891 | 721.8441 | 56.59% | 0 | 0 | 24.3441 | 38.95% | 34.2352
960 | 0 | 0 | 0 | 0.4 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5467 | 31.9066 | 0 | 81.5467 | 640.2975 | 50.2% | 0 | 0 | 24.3441 | 38.95% | 31.9066
961 | 0 | 0 | 0 | 1.1 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7154 | 31.1072 | 0 | 79.7154 | 560.5821 | 43.95% | 0 | 0 | 24.3441 | 38.95% | 31.1072
962 | 0 | 0 | 0 | 1 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.721 | 18.0152 | 0 | 49.721 | 510.8611 | 40.05% | 0 | 0 | 24.3441 | 38.95% | 18.0152
963 | 0 | 0 | 0 | 0.9 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9619 | 30.3398 | 0 | 77.9619 | 432.8992 | 33.94% | 0 | 0 | 24.3441 | 38.95% | 30.3398
964 | 0 | 0 | 0 | 0.7 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2589 | 30.9081 | 0 | 79.2589 | 353.6402 | 27.73% | 0 | 0 | 24.3441 | 38.95% | 30.9081
965 | 0 | 0 | 0 | 0.5 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6087 | 31.9289 | 0 | 81.6087 | 272.0315 | 21.33% | 0 | 0 | 24.3441 | 38.95% | 31.9289
966 | 0 | 0 | 0 | 1 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9814 | 32.9678 | 0 | 83.9814 | 188.0501 | 14.74% | 0 | 0 | 24.3441 | 38.95% | 32.9678
967 | 0 | 0 | 0 | 0.7 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6257 | 35.8674 | 0 | 90.6257 | 97.4245 | 7.638% | 0 | 0 | 24.3441 | 38.95% | 35.8674
968 | 295 | 68 | 34 | 0.9 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4245 | 38.8339 | 0 | 97.4245 | 0 | 0% | 0 | 0 | 24.3441 | 38.95% | 38.8339
969 | 631 | 222 | 52 | 0.9 | 12.1 | 0 | 0 | 0 | 97.4238 | 23.766 | 0 | 0 | 23.766 | 0 | 0 | 0 | 0 | 0 | 97.4238 | 0 | 97.4238 | 7.638% | 0 | 16.3491 | 6.25 | 10% | 40.1151
970 | 908 | 435 | 57 | 2.5 | 16.1 | 0 | 0 | 0 | 198.1563 | 39.9759 | 8.5079 | 0 | 39.9759 | 0 | 0 | 0 | 0 | 0 | 198.1563 | 0 | 295.5802 | 23.17% | 0 | 0 | 6.25 | 10% | 39.9759
971 | 957 | 591 | 75 | 4.3 | 17.6 | 0 | 0 | 0 | 240.66 | 40.4452 | 23.9334 | 0 | 40.4452 | 0 | 0 | 0 | 0 | 0 | 240.66 | 0 | 536.2401 | 42.04% | 0 | 0 | 6.25 | 10% | 40.4452
972 | 976 | 667 | 67 | 2.7 | 18.3 | 0 | 0 | 0 | 263.6922 | 40.2823 | 30.6635 | 0 | 40.2823 | 0 | 0 | 0 | 0 | 0 | 263.6922 | 0 | 799.9323 | 62.71% | 0 | 0 | 6.25 | 10% | 40.2823
973 | 957 | 707 | 98 | 2.7 | 19.5 | 0 | 0 | 0 | 263.1745 | 38.3228 | 33.6772 | 0 | 38.3228 | 0 | 0 | 0 | 0 | 0 | 263.1745 | 0 | 1063.1068 | 83.35% | 0 | 0 | 6.25 | 10% | 38.3228
974 | 764 | 605 | 140 | 3.2 | 19.8 | 0 | 0 | 0 | 205.7033 | 62.0512 | 5.4187 | 25 | 37.0512 | 0 | 0 | 0 | 0 | 0 | 205.7033 | 0 | 1268.8102 | 99.47% | 25 | 0 | 28.839 | 46.14% | 37.0512
975 | 664 | 506 | 154 | 2.9 | 19.9 | 0 | 0 | 0 | 0 | 58.4834 | 1.0658e-14 | 21.531 | 36.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.8102 | 99.47% | 21.531 | 0 | 48.2936 | 77.27% | 36.9523
976 | 683 | 368 | 98 | 2.2 | 19.7 | 0 | 0 | 0 | 0 | 47.503 | 1.1111 | 8.8057 | 38.6974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.8102 | 99.47% | 8.8057 | 0 | 56.25 | 90% | 38.6974
977 | 444 | 191 | 79 | 3.9 | 18.9 | 0 | 0 | 0 | 6.7 | 27.9195 | 0 | 0 | 27.9195 | 0 | 0 | 0 | 0 | 0 | 6.7 | 0 | 1275.5102 | 100% | 0 | 14.6538 | 40.0322 | 64.05% | 42.5733
978 | 8 | 21 | 20 | 1.8 | 16.7 | 0 | 0 | 0 | 0 | 1.0506 | 0 | 0 | 1.0506 | 0 | 0 | 0 | 108.2766 | 43.2872 | 0 | 108.2766 | 1167.2336 | 91.51% | 0 | 0 | 40.0322 | 64.05% | 44.3378
979 | 0 | 0 | 0 | 1.8 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4903 | 44.3503 | 0 | 110.4903 | 1056.7432 | 82.85% | 0 | 0 | 40.0322 | 64.05% | 44.3503
980 | 0 | 0 | 0 | 0.6 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.4531 | 42.6666 | 0 | 106.4531 | 950.2901 | 74.5% | 0 | 0 | 40.0322 | 64.05% | 42.6666
981 | 0 | 0 | 0 | 1.2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9356 | 39.4285 | 0 | 98.9356 | 851.3545 | 66.75% | 0 | 0 | 40.0322 | 64.05% | 39.4285
982 | 0 | 0 | 0 | 0.6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1291 | 36.0541 | 0 | 91.1291 | 760.2254 | 59.6% | 0 | 0 | 40.0322 | 64.05% | 36.0541
983 | 0 | 0 | 0 | 1.3 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4613 | 33.5918 | 0 | 85.4613 | 674.764 | 52.9% | 0 | 0 | 40.0322 | 64.05% | 33.5918
984 | 0 | 0 | 0 | 1.9 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674.764 | 52.9% | 0 | 0 | 40.0322 | 64.05% | 0
985 | 0 | 0 | 0 | 2.1 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674.764 | 52.9% | 0 | 0 | 40.0322 | 64.05% | 0
986 | 0 | 0 | 0 | 2.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 674.764 | 52.9% | 0 | 13.7772 | 24.7845 | 39.66% | 13.7772
987 | 0 | 0 | 0 | 2.2 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.7731 | 42.4763 | 0 | 105.7731 | 568.9909 | 44.61% | 9.6825 | 0 | 33.5333 | 53.65% | 32.7938
988 | 0 | 0 | 0 | 1.5 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.924 | 37.3061 | 0 | 93.924 | 475.0669 | 37.25% | 0 | 0 | 33.5333 | 53.65% | 37.3061
989 | 0 | 0 | 0 | 1.5 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1314 | 43.9395 | 0 | 109.1314 | 365.9356 | 28.69% | 0 | 0 | 33.5333 | 53.65% | 43.9395
990 | 0 | 0 | 0 | 1.5 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.0362 | 47.3934 | 0 | 117.0362 | 248.8994 | 19.51% | 0 | 0 | 33.5333 | 53.65% | 47.3934
991 | 0 | 0 | 0 | 1.1 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9839 | 0 | 127.551 | 121.3484 | 9.514% | 2.9165 | 0 | 36.1685 | 57.87% | 49.0674
992 | 275 | 54 | 20 | 1.4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.3484 | 49.2721 | 0 | 121.3484 | 0 | 0% | 0 | 0 | 36.1685 | 57.87% | 49.2721
993 | 717 | 234 | 46 | 1.8 | 12.1 | 0 | 0 | 0 | 0 | 25.7828 | 0 | 0 | 25.7828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 23.3779 | 10.2954 | 16.47% | 49.1607
994 | 829 | 407 | 59 | 1.4 | 15.3 | 0 | 0 | 0 | 0 | 44.9665 | 0 | 0 | 44.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.6552 | 6.25 | 10% | 48.6217
995 | 926 | 563 | 61 | 2.2 | 17.2 | 0 | 0 | 0 | 234.0888 | 60.1721 | 0 | 11.9083 | 48.2638 | 0 | 0 | 0 | 0 | 0 | 234.0888 | 0 | 234.0888 | 18.35% | 11.9083 | 0 | 17.0099 | 27.22% | 48.2638
996 | 961 | 655 | 62 | 1.7 | 18.4 | 0 | 0 | 0 | 238.9088 | 46.7235 | 21.6571 | 0 | 46.7235 | 0 | 0 | 0 | 0 | 0 | 238.9088 | 0 | 472.9976 | 37.08% | 0 | 0 | 17.0099 | 27.22% | 46.7235
997 | 963 | 680 | 65 | 1.6 | 19.2 | 0 | 0 | 0 | 265.7769 | 64.2647 | 7.394 | 18.4283 | 45.8363 | 0 | 0 | 0 | 0 | 0 | 265.7769 | 0 | 738.7745 | 57.92% | 18.4283 | 0 | 33.661 | 53.86% | 45.8363
998 | 939 | 653 | 83 | 4.4 | 19.5 | 0 | 0 | 0 | 256.341 | 70.2013 | 1.7987 | 25 | 45.2013 | 0 | 0 | 0 | 0 | 0 | 256.341 | 0 | 995.1155 | 78.02% | 25 | 0 | 56.25 | 90% | 45.2013
999 | 862 | 592 | 139 | 5.5 | 18.9 | 0 | 0 | 0 | 226.4941 | 44.8977 | 26.4154 | 0 | 44.8977 | 0 | 0 | 0 | 0 | 0 | 226.4941 | 0 | 1221.6096 | 95.77% | 0 | 0 | 56.25 | 90% | 44.8977
1000 | 275 | 334 | 214 | 4.4 | 18.2 | 0 | 0 | 0 | 53.9006 | 34.8076 | 0 | 0 | 34.8076 | 0 | 0 | 0 | 0 | 0 | 53.9006 | 0 | 1275.5102 | 100% | 0 | 10.682 | 44.4279 | 71.08% | 45.4896
1001 | 48 | 109 | 96 | 5 | 16.2 | 0 | 0 | 0 | 0 | 8.9249 | 0 | 0 | 8.9249 | 0 | 0 | 0 | 100.9595 | 40.1397 | 0 | 100.9595 | 1174.5507 | 92.08% | 0 | 0 | 44.4279 | 71.08% | 49.0646
1002 | 1 | 25 | 25 | 3.6 | 15.1 | 0 | 0 | 0 | 0 | 1.1858 | 0 | 0 | 1.1858 | 0 | 0 | 0 | 120.8089 | 48.8143 | 0 | 120.8089 | 1053.7419 | 82.61% | 0 | 0 | 44.4279 | 71.08% | 50
1003 | 0 | 0 | 0 | 3.1 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.6153 | 49.215 | 0 | 121.6153 | 932.1266 | 73.08% | 0 | 0 | 44.4279 | 71.08% | 49.215
1004 | 0 | 0 | 0 | 2.8 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.0712 | 45.5285 | 0 | 113.0712 | 819.0554 | 64.21% | 0 | 0 | 44.4279 | 71.08% | 45.5285
1005 | 0 | 0 | 0 | 2.6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.045 | 41.1861 | 0 | 103.045 | 716.0105 | 56.14% | 0 | 0 | 44.4279 | 71.08% | 41.1861
1006 | 0 | 0 | 0 | 4.2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0788 | 38.6361 | 0 | 97.0788 | 618.9317 | 48.52% | 0 | 0 | 44.4279 | 71.08% | 38.6361
1007 | 0 | 0 | 0 | 4.2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.9317 | 48.52% | 0 | 0 | 44.4279 | 71.08% | 0
1008 | 0 | 0 | 0 | 4.4 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.9317 | 48.52% | 0 | 0 | 44.4279 | 71.08% | 0
1009 | 0 | 0 | 0 | 3 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.9317 | 48.52% | 0 | 0 | 44.4279 | 71.08% | 0
1010 | 0 | 0 | 0 | 3.5 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.9317 | 48.52% | 0 | 0 | 44.4279 | 71.08% | 0
1011 | 0 | 0 | 0 | 3.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 618.9317 | 48.52% | 0 | 0 | 44.4279 | 71.08% | 0
1012 | 0 | 0 | 0 | 3.8 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.9317 | 48.52% | 0 | 22.0968 | 19.9726 | 31.96% | 22.0968
1013 | 0 | 0 | 0 | 3.6 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9566 | 0 | 127.551 | 491.3806 | 38.52% | 6.6774 | 0 | 26.006 | 41.61% | 45.2793
1014 | 0 | 0 | 0 | 3.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9546 | 0 | 127.551 | 363.8296 | 28.52% | 3.4819 | 0 | 29.1521 | 46.64% | 48.4727
1015 | 0 | 0 | 0 | 2.3 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9605 | 0 | 127.551 | 236.2786 | 18.52% | 1.9605 | 0 | 30.9235 | 49.48% | 50
1016 | 0 | 13 | 13 | 2.2 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0494 | 50 | 0 | 123.0494 | 113.2292 | 8.877% | 0 | 0 | 30.9235 | 49.48% | 50
1017 | 18 | 95 | 88 | 3.3 | 9.8 | 0 | 0 | 0 | 0 | 7.1101 | 0 | 0 | 7.1101 | 0 | 0 | 0 | 113.2292 | 45.7035 | 0 | 113.2292 | 0 | 0% | 3.3145 | 0 | 33.9183 | 54.27% | 49.4991
1018 | 52 | 265 | 237 | 5 | 11 | 0 | 0 | 0 | 0 | 23.5825 | 0 | 0 | 23.5825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 6.25 | 10% | 48.5825
1019 | 403 | 561 | 326 | 5.7 | 12.1 | 0 | 0 | 0 | 89.2419 | 48.69 | 5.4092 | 0 | 48.69 | 0 | 0 | 0 | 0 | 0 | 89.2419 | 0 | 89.2419 | 6.997% | 0 | 0 | 6.25 | 10% | 48.69
1020 | 762 | 620 | 140 | 5.4 | 12.7 | 0 | 0 | 0 | 200.007 | 47.0187 | 20.5628 | 0 | 47.0187 | 0 | 0 | 0 | 0 | 0 | 200.007 | 0 | 289.2489 | 22.68% | 0 | 0 | 6.25 | 10% | 47.0187
1021 | 910 | 687 | 99 | 6.4 | 13.4 | 0 | 0 | 0 | 246.7289 | 46.158 | 25.842 | 0 | 46.158 | 0 | 0 | 0 | 0 | 0 | 246.7289 | 0 | 535.9779 | 42.02% | 0 | 0 | 6.25 | 10% | 46.158
1022 | 897 | 650 | 101 | 6.6 | 13.5 | 0 | 0 | 0 | 242.1524 | 70.7472 | 1.2528 | 25 | 45.7472 | 0 | 0 | 0 | 0 | 0 | 242.1524 | 0 | 778.1303 | 61.01% | 25 | 0 | 28.839 | 46.14% | 45.7472
1023 | 847 | 556 | 107 | 6 | 13.4 | 0 | 0 | 0 | 206.7703 | 68.9296 | 0 | 23.5306 | 45.399 | 0 | 0 | 0 | 0 | 0 | 206.7703 | 0 | 984.9006 | 77.22% | 23.5306 | 0 | 50.1003 | 80.16% | 45.399
1024 | 754 | 390 | 89 | 5.6 | 13.1 | 0 | 0 | 0 | 181.7449 | 52.6856 | 1.3233 | 6.806 | 45.8795 | 0 | 0 | 0 | 0 | 0 | 181.7449 | 0 | 1166.6455 | 91.47% | 6.806 | 0 | 56.25 | 90% | 45.8795
1025 | 561 | 191 | 57 | 5.5 | 12.3 | 0 | 0 | 0 | 108.8647 | 32.0397 | 0 | 0 | 32.0397 | 0 | 0 | 0 | 0 | 0 | 108.8647 | 0 | 1275.5102 | 100% | 0 | 17.4761 | 36.9086 | 59.05% | 49.5158
1026 | 149 | 32 | 17 | 4.8 | 10.8 | 0 | 0 | 0 | 0 | 5.5904 | 0 | 0 | 5.5904 | 0 | 0 | 0 | 98.2684 | 39.1591 | 0 | 98.2684 | 1177.2418 | 92.3% | 0 | 5.2505 | 31.0976 | 49.76% | 50
1027 | 0 | 0 | 0 | 3.4 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.1179 | 49.5952 | 0 | 122.1179 | 1055.1239 | 82.72% | 0 | 0 | 31.0976 | 49.76% | 49.5952
1028 | 0 | 0 | 0 | 3.4 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.2031 | 45.7221 | 0 | 113.2031 | 941.9208 | 73.85% | 0 | 0 | 31.0976 | 49.76% | 45.7221
1029 | 0 | 0 | 0 | 2.4 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9566 | 41.2516 | 0 | 102.9566 | 838.9642 | 65.77% | 0 | 0 | 31.0976 | 49.76% | 41.2516
1030 | 0 | 0 | 0 | 1.8 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6356 | 38.4927 | 0 | 96.6356 | 742.3286 | 58.2% | 0 | 0 | 31.0976 | 49.76% | 38.4927
1031 | 0 | 0 | 0 | 1.7 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.055 | 36.0568 | 0 | 91.055 | 651.2736 | 51.06% | 0 | 0 | 31.0976 | 49.76% | 36.0568
1032 | 0 | 0 | 0 | 1.1 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 651.2736 | 51.06% | 0 | 0 | 31.0976 | 49.76% | 0
1033 | 0 | 0 | 0 | 1.6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 651.2736 | 51.06% | 0 | 0 | 31.0976 | 49.76% | 0
1034 | 0 | 0 | 0 | 2.3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 651.2736 | 51.06% | 0 | 0 | 31.0976 | 49.76% | 0
1035 | 0 | 0 | 0 | 1.8 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3666 | 29.6422 | 0 | 76.3666 | 574.907 | 45.07% | 0 | 0 | 31.0976 | 49.76% | 29.6422
1036 | 0 | 0 | 0 | 2.2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8184 | 38.5651 | 0 | 96.8184 | 478.0885 | 37.48% | 0 | 0 | 31.0976 | 49.76% | 38.5651
1037 | 0 | 0 | 0 | 1.9 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.3324 | 45.3364 | 0 | 112.3324 | 365.7561 | 28.68% | 0 | 0 | 31.0976 | 49.76% | 45.3364
1038 | 0 | 0 | 0 | 1.8 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.7658 | 48.5688 | 0 | 119.7658 | 245.9903 | 19.29% | 0 | 0 | 31.0976 | 49.76% | 48.5688
1039 | 0 | 0 | 0 | 2.3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9478 | 49.9587 | 0 | 122.9478 | 123.0425 | 9.647% | 0 | 0 | 31.0976 | 49.76% | 49.9587
1040 | 256 | 56 | 22 | 1.9 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0425 | 50 | 0 | 123.0425 | 0 | 0% | 0 | 0 | 31.0976 | 49.76% | 50
1041 | 722 | 249 | 53 | 2.7 | 7.6 | 0 | 0 | 0 | 0 | 27.0673 | 0 | 0 | 27.0673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 22.4513 | 6.25 | 10% | 49.5186
1042 | 857 | 438 | 70 | 5.5 | 10.2 | 0 | 0 | 0 | 0 | 48.7652 | 0.84426 | 0 | 48.7652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 48.7652
1043 | 939 | 587 | 69 | 6 | 11.4 | 0 | 0 | 0 | 235.4173 | 48.0298 | 16.9415 | 0 | 48.0298 | 0 | 0 | 0 | 0 | 0 | 235.4173 | 0 | 235.4173 | 18.46% | 0 | 0 | 6.25 | 10% | 48.0298
1044 | 982 | 682 | 67 | 5.9 | 12.7 | 0 | 0 | 0 | 0 | 46.4798 | 25.5202 | 0 | 46.4798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235.4173 | 18.46% | 0 | 0 | 6.25 | 10% | 46.4798
1045 | 1001 | 713 | 64 | 6.4 | 13.8 | 0 | 0 | 0 | 168.1916 | 45.5662 | 26.4338 | 0 | 45.5662 | 0 | 0 | 0 | 0 | 0 | 168.1916 | 0 | 403.6089 | 31.64% | 0 | 0 | 6.25 | 10% | 45.5662
1046 | 980 | 671 | 66 | 6.5 | 14.3 | 0 | 0 | 0 | 266.8419 | 62.7709 | 9.2291 | 17.6964 | 45.0745 | 0 | 0 | 0 | 0 | 0 | 266.8419 | 0 | 670.4508 | 52.56% | 17.6964 | 0 | 22.2397 | 35.58% | 45.0745
1047 | 946 | 567 | 63 | 7.2 | 14 | 0 | 0 | 0 | 250.1573 | 69.6567 | 1.5811 | 25 | 44.6567 | 0 | 0 | 0 | 0 | 0 | 250.1573 | 0 | 920.6081 | 72.18% | 25 | 0 | 44.8287 | 71.73% | 44.6567
1048 | 875 | 410 | 56 | 6.9 | 13.4 | 0 | 0 | 0 | 213.2763 | 57.7789 | 0 | 12.6403 | 45.1386 | 0 | 0 | 0 | 0 | 0 | 213.2763 | 0 | 1133.8843 | 88.9% | 12.6403 | 0 | 56.25 | 90% | 45.1386
1049 | 703 | 215 | 44 | 6.2 | 12.3 | 0 | 0 | 0 | 141.6259 | 36.8842 | 0 | 0 | 36.8842 | 0 | 0 | 0 | 0 | 0 | 141.6259 | 0 | 1275.5102 | 100% | 0 | 12.1428 | 42.8111 | 68.5% | 49.027
1050 | 203 | 38 | 16 | 5.8 | 10.2 | 0 | 0 | 0 | 0 | 6.8517 | 0 | 0 | 6.8517 | 0 | 0 | 0 | 95.9913 | 38.1779 | 0 | 95.9913 | 1179.5189 | 92.47% | 0 | 4.9704 | 37.3102 | 59.7% | 50
1051 | 0 | 0 | 0 | 4.4 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.6396 | 49.3961 | 0 | 121.6396 | 1057.8793 | 82.94% | 0 | 0 | 37.3102 | 59.7% | 49.3961
1052 | 0 | 0 | 0 | 4.6 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.9086 | 45.5912 | 0 | 112.9086 | 944.9707 | 74.09% | 0 | 0 | 37.3102 | 59.7% | 45.5912
1053 | 0 | 0 | 0 | 4.1 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0796 | 41.3031 | 0 | 103.0796 | 841.8911 | 66% | 0 | 0 | 37.3102 | 59.7% | 41.3031
1054 | 0 | 0 | 0 | 3 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5429 | 38.4523 | 0 | 96.5429 | 745.3482 | 58.44% | 0 | 0 | 37.3102 | 59.7% | 38.4523
1055 | 0 | 0 | 0 | 2.4 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6819 | 35.8939 | 0 | 90.6819 | 654.6663 | 51.33% | 0 | 0 | 37.3102 | 59.7% | 35.8939
1056 | 0 | 0 | 0 | 3.4 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0256 | 34.2979 | 0 | 87.0256 | 567.6406 | 44.5% | 0 | 0 | 37.3102 | 59.7% | 34.2979
1057 | 0 | 0 | 0 | 2.9 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567.6406 | 44.5% | 0 | 6.0017 | 30.6679 | 49.07% | 6.0017
1058 | 0 | 0 | 0 | 2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567.6406 | 44.5% | 0 | 0 | 30.6679 | 49.07% | 0
1059 | 0 | 0 | 0 | 2.3 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 567.6406 | 44.5% | 0 | 0 | 30.6679 | 49.07% | 0
1060 | 0 | 0 | 0 | 2.1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9175 | 38.1682 | 0 | 95.9175 | 471.7231 | 36.98% | 0 | 0 | 30.6679 | 49.07% | 38.1682
1061 | 0 | 0 | 0 | 1.8 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3961 | 44.9074 | 0 | 111.3961 | 360.327 | 28.25% | 0 | 0 | 30.6679 | 49.07% | 44.9074
1062 | 0 | 0 | 0 | 2.3 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.7515 | 48.112 | 0 | 118.7515 | 241.5755 | 18.94% | 0 | 0 | 30.6679 | 49.07% | 48.112
1063 | 0 | 0 | 0 | 1.9 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.5617 | 49.3417 | 0 | 121.5617 | 120.0138 | 9.409% | 0 | 0 | 30.6679 | 49.07% | 49.3417
1064 | 264 | 59 | 24 | 1.7 | 3.4 | 0 | 0 | 0 | 0 | 0.82093 | 0 | 0 | 0.82093 | 0 | 0 | 0 | 120.0138 | 48.6684 | 0 | 120.0138 | 0 | 0% | 0 | 0 | 30.6679 | 49.07% | 49.4894
1065 | 716 | 250 | 52 | 2.3 | 7.8 | 0 | 0 | 0 | 115.7835 | 26.8373 | 0 | 0 | 26.8373 | 0 | 0 | 0 | 0 | 0 | 115.7835 | 0 | 115.7835 | 9.077% | 0 | 22.063 | 6.25 | 10% | 48.9003
1066 | 866 | 439 | 64 | 4.6 | 11 | 0 | 0 | 0 | 189.4959 | 48.4309 | 0.80298 | 0 | 48.4309 | 0 | 0 | 0 | 0 | 0 | 189.4959 | 0 | 305.2794 | 23.93% | 0 | 0 | 6.25 | 10% | 48.4309
1067 | 938 | 589 | 68 | 5.6 | 12.1 | 0 | 0 | 0 | 236.0136 | 47.8599 | 16.7299 | 0 | 47.8599 | 0 | 0 | 0 | 0 | 0 | 236.0136 | 0 | 541.293 | 42.44% | 0 | 0 | 6.25 | 10% | 47.8599
1068 | 964 | 682 | 73 | 5.6 | 13.3 | 0 | 0 | 0 | 258.775 | 46.3948 | 25.6052 | 0 | 46.3948 | 0 | 0 | 0 | 0 | 0 | 258.775 | 0 | 800.068 | 62.73% | 0 | 0 | 6.25 | 10% | 46.3948
1069 | 972 | 709 | 74 | 6 | 14.4 | 0 | 0 | 0 | 0 | 45.6622 | 26.3378 | 0 | 45.6622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800.068 | 62.73% | 0 | 0 | 6.25 | 10% | 45.6622
1070 | 946 | 665 | 77 | 6.4 | 14.8 | 0 | 0 | 0 | 0 | 65.9348 | 6.0652 | 20.8032 | 45.1316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800.068 | 62.73% | 20.8032 | 0 | 25.0469 | 40.08% | 45.1316
1071 | 902 | 560 | 75 | 6.8 | 14.7 | 0 | 0 | 0 | 238.2879 | 69.2071 | 0 | 24.2551 | 44.952 | 0 | 0 | 0 | 0 | 0 | 238.2879 | 0 | 1038.3559 | 81.41% | 24.2551 | 0 | 46.9628 | 75.14% | 44.952
1072 | 821 | 404 | 67 | 6.5 | 14.2 | 0 | 0 | 0 | 199.6696 | 55.4992 | 0 | 10.2784 | 45.2208 | 0 | 0 | 0 | 0 | 0 | 199.6696 | 0 | 1238.0256 | 97.06% | 10.2784 | 0 | 56.25 | 90% | 45.2208
1073 | 638 | 212 | 53 | 6.2 | 12.9 | 0 | 0 | 0 | 37.4846 | 35.0736 | 0 | 0 | 35.0736 | 0 | 0 | 0 | 0 | 0 | 37.4846 | 0 | 1275.5102 | 100% | 0 | 13.8294 | 40.9445 | 65.51% | 48.903
1074 | 168 | 38 | 19 | 5.8 | 10.8 | 0 | 0 | 0 | 0 | 6.2992 | 0 | 0 | 6.2992 | 0 | 0 | 0 | 94.4598 | 37.4986 | 0 | 94.4598 | 1181.0504 | 92.59% | 0 | 6.2021 | 34.0804 | 54.53% | 50
1075 | 0 | 0 | 0 | 3.9 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.1422 | 49.1663 | 0 | 121.1422 | 1059.9081 | 83.1% | 0 | 0 | 34.0804 | 54.53% | 49.1663
1076 | 0 | 0 | 0 | 3.8 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.9441 | 45.5926 | 0 | 112.9441 | 946.9641 | 74.24% | 0 | 0 | 34.0804 | 54.53% | 45.5926
1077 | 0 | 0 | 0 | 3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2755 | 41.3741 | 0 | 103.2755 | 843.6886 | 66.15% | 0 | 0 | 34.0804 | 54.53% | 41.3741
1078 | 0 | 0 | 0 | 1.8 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3716 | 38.8074 | 0 | 97.3716 | 746.317 | 58.51% | 0 | 0 | 34.0804 | 54.53% | 38.8074
1079 | 0 | 0 | 0 | 2.1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4055 | 36.2045 | 0 | 91.4055 | 654.9115 | 51.35% | 0 | 0 | 34.0804 | 54.53% | 36.2045
1080 | 0 | 0 | 0 | 2 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654.9115 | 51.35% | 0 | 0 | 34.0804 | 54.53% | 0
1081 | 0 | 0 | 0 | 2.3 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654.9115 | 51.35% | 0 | 0 | 34.0804 | 54.53% | 0
1082 | 0 | 0 | 0 | 2 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654.9115 | 51.35% | 0 | 0 | 34.0804 | 54.53% | 0
1083 | 0 | 0 | 0 | 1.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1831 | 34.361 | 0 | 87.1831 | 567.7283 | 44.51% | 0 | 0 | 34.0804 | 54.53% | 34.361
1084 | 0 | 0 | 0 | 2.3 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6417 | 38.4871 | 0 | 96.6417 | 471.0866 | 36.93% | 0 | 0 | 34.0804 | 54.53% | 38.4871
1085 | 0 | 0 | 0 | 2.2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.4092 | 44.9325 | 0 | 111.4092 | 359.6775 | 28.2% | 0 | 0 | 34.0804 | 54.53% | 44.9325
1086 | 0 | 0 | 0 | 1.8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.3706 | 47.9616 | 0 | 118.3706 | 241.3068 | 18.92% | 0 | 0 | 34.0804 | 54.53% | 47.9616
1087 | 0 | 0 | 0 | 1.6 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.8627 | 49.4768 | 0 | 121.8627 | 119.4442 | 9.364% | 0 | 0 | 34.0804 | 54.53% | 49.4768
1088 | 218 | 59 | 30 | 1.7 | 5.2 | 0 | 0 | 0 | 0 | 1.1127 | 0 | 0 | 1.1127 | 0 | 0 | 0 | 119.4442 | 48.4435 | 0 | 119.4442 | 0 | 0% | 0 | 0 | 34.0804 | 54.53% | 49.5562
1089 | 617 | 245 | 70 | 2.3 | 8.1 | 0 | 0 | 0 | 0 | 25.4454 | 0 | 0 | 25.4454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 24.0426 | 7.4717 | 11.95% | 49.488
1090 | 777 | 432 | 90 | 4.5 | 10.5 | 0 | 0 | 0 | 0 | 47.5332 | 0 | 0 | 47.5332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 1.1038 | 6.25 | 10% | 48.637
1091 | 858 | 581 | 98 | 5.8 | 11.6 | 0 | 0 | 0 | 214.2795 | 48.0215 | 15.1645 | 0 | 48.0215 | 0 | 0 | 0 | 0 | 0 | 214.2795 | 0 | 214.2795 | 16.8% | 0 | 0 | 6.25 | 10% | 48.0215
1092 | 897 | 674 | 102 | 6.5 | 12.2 | 0 | 0 | 0 | 238.7319 | 46.3642 | 25.6358 | 0 | 46.3642 | 0 | 0 | 0 | 0 | 0 | 238.7319 | 0 | 453.0114 | 35.52% | 0 | 0 | 6.25 | 10% | 46.3642
1093 | 908 | 698 | 101 | 6.6 | 12.8 | 0 | 0 | 0 | 165.98 | 45.1651 | 26.8349 | 0 | 45.1651 | 0 | 0 | 0 | 0 | 0 | 165.98 | 0 | 618.9914 | 48.53% | 0 | 0 | 6.25 | 10% | 45.1651
1094 | 896 | 660 | 98 | 7.1 | 13.7 | 0 | 0 | 0 | 242.1944 | 64.4125 | 7.5875 | 20.0204 | 44.3921 | 0 | 0 | 0 | 0 | 0 | 242.1944 | 0 | 861.1859 | 67.52% | 20.0204 | 0 | 24.3396 | 38.94% | 44.3921
1095 | 860 | 558 | 91 | 7.2 | 13.9 | 0 | 0 | 0 | 225.8796 | 68.8213 | 0 | 24.9014 | 43.92 | 0 | 0 | 0 | 0 | 0 | 225.8796 | 0 | 1087.0654 | 85.23% | 24.9014 | 0 | 46.8395 | 74.94% | 43.92
1096 | 779 | 402 | 79 | 6.9 | 14.1 | 0 | 0 | 0 | 188.4448 | 54.7652 | 0 | 10.4149 | 44.3503 | 0 | 0 | 0 | 0 | 0 | 188.4448 | 0 | 1275.5102 | 100% | 10.4149 | 0 | 56.25 | 90% | 44.3503
1097 | 611 | 213 | 58 | 6.4 | 13.3 | 0 | 0 | 0 | 0 | 34.2851 | 0 | 0 | 34.2851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 13.5957 | 41.2032 | 65.93% | 47.8808
1098 | 162 | 38 | 19 | 5.3 | 11.2 | 0 | 0 | 0 | 0 | 6.1249 | 0 | 0 | 6.1249 | 0 | 0 | 0 | 105.9913 | 42.5163 | 0 | 105.9913 | 1169.5189 | 91.69% | 0 | 0 | 41.2032 | 65.93% | 48.6412
1099 | 0 | 0 | 0 | 4.2 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.6973 | 47.6649 | 0 | 117.6973 | 1051.8216 | 82.46% | 0 | 0 | 41.2032 | 65.93% | 47.6649
1100 | 0 | 0 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4345 | 44.5091 | 0 | 110.4345 | 941.387 | 73.8% | 0 | 0 | 41.2032 | 65.93% | 44.5091
1101 | 0 | 0 | 0 | 3.1 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4521 | 41.0288 | 0 | 102.4521 | 838.9349 | 65.77% | 0 | 0 | 41.2032 | 65.93% | 41.0288
1102 | 0 | 0 | 0 | 2.5 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.768 | 38.5484 | 0 | 96.768 | 742.1669 | 58.19% | 0 | 0 | 41.2032 | 65.93% | 38.5484
1103 | 0 | 0 | 0 | 1.8 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.571 | 35.8451 | 0 | 90.571 | 651.5959 | 51.09% | 0 | 0 | 41.2032 | 65.93% | 35.8451
1104 | 0 | 0 | 0 | 2.6 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9148 | 33.8132 | 0 | 85.9148 | 565.6811 | 44.35% | 0 | 0 | 41.2032 | 65.93% | 33.8132
1105 | 0 | 0 | 0 | 2.4 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.3837 | 37.5097 | 0 | 94.3837 | 471.2974 | 36.95% | 4.7549 | 0 | 45.4995 | 72.8% | 32.7548
1106 | 0 | 0 | 0 | 2 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471.2974 | 36.95% | 0 | 19.9562 | 23.4134 | 37.46% | 19.9562
1107 | 0 | 0 | 0 | 2.9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471.2974 | 36.95% | 0 | 0 | 23.4134 | 37.46% | 0
1108 | 0 | 0 | 0 | 3 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.121 | 33.0291 | 0 | 84.121 | 387.1764 | 30.35% | 0 | 0 | 23.4134 | 37.46% | 33.0291
1109 | 0 | 0 | 0 | 3.8 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0112 | 35.1641 | 0 | 89.0112 | 298.1652 | 23.38% | 0 | 0 | 23.4134 | 37.46% | 35.1641
1110 | 0 | 0 | 0 | 3.7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.218 | 37.437 | 0 | 94.218 | 203.9472 | 15.99% | 0 | 0 | 23.4134 | 37.46% | 37.437
1111 | 0 | 1 | 1 | 3.7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9926 | 41.2669 | 0 | 102.9926 | 100.9547 | 7.915% | 0 | 0 | 23.4134 | 37.46% | 41.2669
1112 | 291 | 71 | 32 | 3.6 | 6.2 | 0 | 0 | 0 | 0 | 3.0241 | 0 | 0 | 3.0241 | 0 | 0 | 0 | 100.9547 | 40.3778 | 0 | 100.9547 | 0 | 0% | 0 | 0 | 23.4134 | 37.46% | 43.4019
1113 | 682 | 266 | 73 | 4.6 | 9.4 | 0 | 0 | 0 | 0 | 27.8255 | 0 | 0 | 27.8255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 15.5081 | 6.25 | 10% | 43.3337
1114 | 812 | 454 | 94 | 7 | 12.1 | 0 | 0 | 0 | 148.8779 | 42.5705 | 7.2286 | 0 | 42.5705 | 0 | 0 | 0 | 0 | 0 | 148.8779 | 0 | 148.8779 | 11.67% | 0 | 0 | 6.25 | 10% | 42.5705
1115 | 734 | 542 | 125 | 8.4 | 13 | 0 | 0 | 0 | 178.4755 | 42.2265 | 16.4827 | 0 | 42.2265 | 0 | 0 | 0 | 0 | 0 | 178.4755 | 0 | 327.3534 | 25.66% | 0 | 0 | 6.25 | 10% | 42.2265
1116 | 686 | 632 | 187 | 9.4 | 13.6 | 0 | 0 | 0 | 175.1228 | 41.2001 | 25.9135 | 0 | 41.2001 | 0 | 0 | 0 | 0 | 0 | 175.1228 | 0 | 502.4762 | 39.39% | 0 | 0 | 6.25 | 10% | 41.2001
1117 | 734 | 678 | 186 | 9.1 | 14.4 | 0 | 0 | 0 | 193.2995 | 39.3812 | 32.6188 | 0 | 39.3812 | 0 | 0 | 0 | 0 | 0 | 193.2995 | 0 | 695.7757 | 54.55% | 0 | 0 | 6.25 | 10% | 39.3812
1118 | 841 | 682 | 149 | 8.7 | 15 | 0 | 0 | 0 | 224.5982 | 61.2722 | 10.7278 | 23.097 | 38.1751 | 0 | 0 | 0 | 0 | 0 | 224.5982 | 0 | 920.3738 | 72.16% | 23.097 | 0 | 27.1196 | 43.39% | 38.1751
1119 | 719 | 531 | 130 | 7.8 | 15.4 | 0 | 0 | 0 | 185.0645 | 62.5846 | 0.44793 | 25 | 37.5846 | 0 | 0 | 0 | 0 | 0 | 185.0645 | 0 | 1105.4383 | 86.67% | 25 | 0 | 49.7086 | 79.53% | 37.5846
1120 | 562 | 360 | 121 | 7.4 | 15 | 0 | 0 | 0 | 129.6674 | 45.9454 | 0 | 7.2396 | 38.7057 | 0 | 0 | 0 | 0 | 0 | 129.6674 | 0 | 1235.1057 | 96.83% | 7.2396 | 0 | 56.25 | 90% | 38.7057
1121 | 270 | 160 | 86 | 7.4 | 12.8 | 0 | 0 | 0 | 40.4045 | 20.825 | 0 | 0 | 20.825 | 0 | 0 | 0 | 0 | 0 | 40.4045 | 0 | 1275.5102 | 100% | 0 | 21.7287 | 32.2021 | 51.52% | 42.5538
1122 | 3 | 24 | 24 | 6.2 | 10.3 | 0 | 0 | 0 | 0 | 1.2161 | 0 | 0 | 1.2161 | 0 | 0 | 0 | 106.5657 | 42.7874 | 0 | 106.5657 | 1168.9445 | 91.65% | 0 | 0 | 32.2021 | 51.52% | 44.0035
1123 | 0 | 0 | 0 | 4.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7245 | 43.7487 | 0 | 108.7245 | 1060.2199 | 83.12% | 0 | 0 | 32.2021 | 51.52% | 43.7487
1124 | 0 | 0 | 0 | 5.2 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1315 | 41.7502 | 0 | 104.1315 | 956.0885 | 74.96% | 0 | 0 | 32.2021 | 51.52% | 41.7502
1125 | 0 | 0 | 0 | 4 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4386 | 38.8367 | 0 | 97.4386 | 858.6499 | 67.32% | 0 | 0 | 32.2021 | 51.52% | 38.8367
1126 | 0 | 0 | 0 | 4.4 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6812 | 35.8925 | 0 | 90.6812 | 767.9686 | 60.21% | 0 | 0 | 32.2021 | 51.52% | 35.8925
1127 | 0 | 0 | 0 | 2.4 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0156 | 40.4045 | 0 | 101.0156 | 666.953 | 52.29% | 7.076 | 0 | 38.5957 | 61.75% | 33.3286
1128 | 0 | 0 | 0 | 2.7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 666.953 | 52.29% | 0 | 8.9851 | 28.6515 | 45.84% | 8.9851
1129 | 0 | 0 | 0 | 2.7 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 666.953 | 52.29% | 0 | 0 | 28.6515 | 45.84% | 0
1130 | 0 | 0 | 0 | 3.5 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 666.953 | 52.29% | 0 | 0 | 28.6515 | 45.84% | 0
1131 | 0 | 0 | 0 | 3.6 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 666.953 | 52.29% | 0 | 0 | 28.6515 | 45.84% | 0
1132 | 0 | 0 | 0 | 3.2 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9602 | 30.3398 | 0 | 77.9602 | 588.9928 | 46.18% | 0 | 0 | 28.6515 | 45.84% | 30.3398
1133 | 0 | 0 | 0 | 2.7 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2774 | 31.3495 | 0 | 80.2774 | 508.7154 | 39.88% | 0 | 0 | 28.6515 | 45.84% | 31.3495
1134 | 0 | 0 | 0 | 2.1 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4932 | 32.3161 | 0 | 82.4932 | 426.2222 | 33.42% | 0 | 0 | 28.6515 | 45.84% | 32.3161
1135 | 0 | 0 | 0 | 2.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9694 | 35.5805 | 0 | 89.9694 | 336.2528 | 26.36% | 0 | 0 | 28.6515 | 45.84% | 35.5805
1136 | 11 | 42 | 40 | 2.6 | 6.3 | 0 | 0 | 0 | 0 | 1.6779 | 0 | 0 | 1.6779 | 0 | 0 | 0 | 91.7545 | 36.3621 | 0 | 91.7545 | 244.4983 | 19.17% | 0 | 0 | 28.6515 | 45.84% | 38.04
1137 | 57 | 153 | 136 | 2.9 | 8.6 | 0 | 0 | 0 | 0 | 14.1067 | 0 | 0 | 14.1067 | 0 | 0 | 0 | 65.37 | 24.8386 | 0 | 65.37 | 179.1284 | 14.04% | 0 | 0 | 28.6515 | 45.84% | 38.9453
1138 | 72 | 222 | 183 | 3.6 | 10.5 | 0 | 0 | 0 | 0 | 18.2251 | 0 | 0 | 18.2251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179.1284 | 14.04% | 0 | 20.2411 | 6.25 | 10% | 38.4662
1139 | 431 | 469 | 217 | 5.6 | 12 | 0 | 0 | 0 | 97.9201 | 38.7057 | 7.334 | 0 | 38.7057 | 0 | 0 | 0 | 0 | 0 | 97.9201 | 0 | 277.0485 | 21.72% | 0 | 0 | 6.25 | 10% | 38.7057
1140 | 666 | 663 | 225 | 6.7 | 13.2 | 0 | 0 | 0 | 171.9815 | 38.2726 | 29.6103 | 0 | 38.2726 | 0 | 0 | 0 | 0 | 0 | 171.9815 | 0 | 449.03 | 35.2% | 0 | 0 | 6.25 | 10% | 38.2726
1141 | 708 | 677 | 198 | 6.5 | 14 | 0 | 0 | 0 | 188.2124 | 36.5638 | 35.2234 | 0 | 36.5638 | 0 | 0 | 0 | 0 | 0 | 188.2124 | 0 | 637.2423 | 49.96% | 0 | 0 | 6.25 | 10% | 36.5638
1142 | 680 | 624 | 188 | 6.6 | 14.5 | 0 | 0 | 0 | 179.3753 | 50.6043 | 18.0301 | 14.968 | 35.6362 | 0 | 0 | 0 | 0 | 0 | 179.3753 | 0 | 816.6176 | 64.02% | 14.968 | 0 | 19.7745 | 31.64% | 35.6362
1143 | 792 | 560 | 120 | 6 | 15 | 0 | 0 | 0 | 207.8143 | 60.4385 | 5.7634 | 25 | 35.4385 | 0 | 0 | 0 | 0 | 0 | 207.8143 | 0 | 1024.4319 | 80.32% | 25 | 0 | 42.3635 | 67.78% | 35.4385
1144 | 697 | 400 | 103 | 6.2 | 14.6 | 0 | 0 | 0 | 167.6641 | 52.1692 | 0 | 15.3686 | 36.8005 | 0 | 0 | 0 | 0 | 0 | 167.6641 | 0 | 1192.096 | 93.46% | 15.3686 | 0 | 56.25 | 90% | 36.8005
1145 | 444 | 201 | 82 | 5.9 | 13.6 | 0 | 0 | 0 | 83.4142 | 28.881 | 0 | 0 | 28.881 | 0 | 0 | 0 | 0 | 0 | 83.4142 | 0 | 1275.5102 | 100% | 0 | 12.4291 | 42.4943 | 67.99% | 41.3101
1146 | 67 | 35 | 26 | 5 | 11.6 | 0 | 0 | 0 | 0 | 3.5805 | 0 | 0 | 3.5805 | 0 | 0 | 0 | 100.3936 | 40.0665 | 0 | 100.3936 | 1175.1166 | 92.13% | 0 | 0 | 42.4943 | 67.99% | 43.647
1147 | 0 | 0 | 0 | 3.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3019 | 43.5579 | 0 | 108.3019 | 1066.8146 | 83.64% | 0 | 0 | 42.4943 | 67.99% | 43.5579
1148 | 0 | 0 | 0 | 2.4 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4076 | 41.8741 | 0 | 104.4076 | 962.407 | 75.45% | 0 | 0 | 42.4943 | 67.99% | 41.8741
1149 | 0 | 0 | 0 | 2.7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9127 | 38.6055 | 0 | 96.9127 | 865.4943 | 67.85% | 0 | 0 | 42.4943 | 67.99% | 38.6055
1150 | 0 | 0 | 0 | 2.6 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.4943 | 67.85% | 0 | 0 | 42.4943 | 67.99% | 0
1151 | 0 | 0 | 0 | 2.6 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.4943 | 67.85% | 0 | 0 | 42.4943 | 67.99% | 0
1152 | 0 | 0 | 0 | 2.7 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.4943 | 67.85% | 0 | 0 | 42.4943 | 67.99% | 0
1153 | 0 | 0 | 0 | 2.4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.4943 | 67.85% | 0 | 0 | 42.4943 | 67.99% | 0
1154 | 0 | 0 | 0 | 2.6 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.4943 | 67.85% | 0 | 0 | 42.4943 | 67.99% | 0
1155 | 0 | 0 | 0 | 2.5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.4943 | 67.85% | 0 | 0 | 42.4943 | 67.99% | 0
1156 | 0 | 0 | 0 | 2.2 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.4943 | 67.85% | 0 | 0 | 42.4943 | 67.99% | 0
1157 | 0 | 0 | 0 | 2.2 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.4943 | 67.85% | 0 | 0 | 42.4943 | 67.99% | 0
1158 | 0 | 0 | 0 | 2.6 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.692 | 47.2457 | 0 | 116.692 | 748.8023 | 58.71% | 0 | 0 | 42.4943 | 67.99% | 47.2457
1159 | 0 | 1 | 1 | 2.9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.7049 | 48.9964 | 0 | 120.7049 | 628.0974 | 49.24% | 0 | 0 | 42.4943 | 67.99% | 48.9964
1160 | 50 | 63 | 54 | 2.4 | 5.4 | 0 | 0 | 0 | 0 | 2.6418 | 0 | 0 | 2.6418 | 0 | 0 | 0 | 115.36 | 46.6624 | 0 | 115.36 | 512.7374 | 40.2% | 0 | 0 | 42.4943 | 67.99% | 49.3041
1161 | 288 | 238 | 149 | 3.2 | 8.8 | 0 | 0 | 0 | 36.8681 | 22.6574 | 0 | 0 | 22.6574 | 0 | 0 | 0 | 0 | 0 | 36.8681 | 0 | 549.6055 | 43.09% | 0 | 25 | 14.826 | 23.72% | 47.6574
1162 | 290 | 369 | 234 | 5.5 | 11.3 | 0 | 0 | 0 | 50.1101 | 34.8469 | 0 | 0 | 34.8469 | 0 | 0 | 0 | 0 | 0 | 50.1101 | 0 | 599.7155 | 47.02% | 0 | 0.79006 | 13.9516 | 22.32% | 35.637
1163 | 359 | 484 | 271 | 6.4 | 12.7 | 0 | 0 | 0 | 77.5165 | 46.3351 | 0 | 0 | 46.3351 | 0 | 0 | 0 | 0 | 0 | 77.5165 | 0 | 677.232 | 53.09% | 0 | 0 | 13.9516 | 22.32% | 46.3351
1164 | 483 | 634 | 309 | 6.8 | 13.7 | 0 | 0 | 0 | 118.8268 | 61.1431 | 0 | 14.1592 | 46.9839 | 0 | 0 | 0 | 0 | 0 | 118.8268 | 0 | 796.0588 | 62.41% | 14.1592 | 0 | 26.7453 | 42.79% | 46.9839
1165 | 512 | 680 | 325 | 6.7 | 14.6 | 0 | 0 | 0 | 130.1209 | 67.0871 | 0 | 21.0363 | 46.0508 | 0 | 0 | 0 | 0 | 0 | 130.1209 | 0 | 926.1797 | 72.61% | 21.0363 | 0 | 45.7528 | 73.2% | 46.0508
1166 | 208 | 471 | 328 | 6.9 | 14.6 | 0 | 0 | 0 | 39.3276 | 42.9526 | 0 | 0 | 42.9526 | 0 | 0 | 0 | 0 | 0 | 39.3276 | 0 | 965.5074 | 75.7% | 0 | 0 | 45.7528 | 73.2% | 42.9526
1167 | 200 | 438 | 319 | 6.4 | 14.6 | 0 | 0 | 0 | 36.3917 | 40.6581 | 0 | 0 | 40.6581 | 0 | 0 | 0 | 0 | 0 | 36.3917 | 0 | 1001.899 | 78.55% | 0 | 0 | 45.7528 | 73.2% | 40.6581
1168 | 95 | 256 | 208 | 6 | 14 | 0 | 0 | 0 | 0 | 21.6993 | 0 | 0 | 21.6993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.899 | 78.55% | 0 | 0 | 45.7528 | 73.2% | 21.6993
1169 | 18 | 119 | 113 | 5.7 | 12.5 | 0 | 0 | 0 | 0 | 8.4572 | 0 | 0 | 8.4572 | 0 | 0 | 0 | 101.9947 | 40.7384 | 0 | 101.9947 | 899.9044 | 70.55% | 0 | 0 | 45.7528 | 73.2% | 49.1955
1170 | 2 | 28 | 27 | 5 | 11.2 | 0 | 0 | 0 | 0 | 1.3845 | 0 | 0 | 1.3845 | 0 | 0 | 0 | 119.9846 | 48.6155 | 0 | 119.9846 | 779.9198 | 61.15% | 0 | 0 | 45.7528 | 73.2% | 50
1171 | 0 | 0 | 0 | 3.7 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.9334 | 49.0618 | 0 | 120.9334 | 658.9864 | 51.66% | 0 | 0 | 45.7528 | 73.2% | 49.0618
1172 | 0 | 0 | 0 | 2.8 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.8686 | 45.1275 | 0 | 111.8686 | 547.1178 | 42.89% | 0 | 0 | 45.7528 | 73.2% | 45.1275
1173 | 0 | 0 | 0 | 3.5 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.1178 | 42.89% | 0 | 0 | 45.7528 | 73.2% | 0
1174 | 0 | 0 | 0 | 3.3 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.1178 | 42.89% | 0 | 0 | 45.7528 | 73.2% | 0
1175 | 0 | 0 | 0 | 2.3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.1178 | 42.89% | 0 | 0 | 45.7528 | 73.2% | 0
1176 | 0 | 0 | 0 | 2.6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.1178 | 42.89% | 0 | 0 | 45.7528 | 73.2% | 0
1177 | 0 | 0 | 0 | 2.1 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.1178 | 42.89% | 0 | 0 | 45.7528 | 73.2% | 0
1178 | 0 | 0 | 0 | 2.1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.1178 | 42.89% | 0 | 0 | 45.7528 | 73.2% | 0
1179 | 0 | 0 | 0 | 1.6 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.1178 | 42.89% | 0 | 0 | 45.7528 | 73.2% | 0
1180 | 0 | 0 | 0 | 1.8 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.1178 | 42.89% | 0 | 0 | 45.7528 | 73.2% | 0
1181 | 0 | 0 | 0 | 1.3 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.0139 | 44.7556 | 0 | 111.0139 | 436.1039 | 34.19% | 0 | 0 | 45.7528 | 73.2% | 44.7556
1182 | 0 | 0 | 0 | 2 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.8416 | 47.7471 | 0 | 117.8416 | 318.2623 | 24.95% | 0 | 0 | 45.7528 | 73.2% | 47.7471
1183 | 0 | 0 | 0 | 2.4 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.5079 | 49.3487 | 0 | 121.5079 | 196.7544 | 15.43% | 0 | 0 | 45.7528 | 73.2% | 49.3487
1184 | 47 | 57 | 49 | 2.1 | 6.6 | 0 | 0 | 0 | 0 | 2.3549 | 0 | 0 | 2.3549 | 0 | 0 | 0 | 116.4821 | 47.1553 | 0 | 116.4821 | 80.2723 | 6.293% | 0 | 0 | 45.7528 | 73.2% | 49.5103
1185 | 191 | 227 | 162 | 1.9 | 9.1 | 0 | 0 | 0 | 0 | 21.031 | 0 | 0 | 21.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2723 | 6.293% | 0 | 25 | 18.0845 | 28.94% | 46.031
1186 | 436 | 401 | 193 | 1.9 | 12.1 | 0 | 0 | 0 | 89.7637 | 37.8603 | 0 | 0 | 37.8603 | 0 | 0 | 0 | 0 | 0 | 89.7637 | 0 | 170.036 | 13.33% | 0 | 10.6932 | 6.25 | 10% | 48.5535
1187 | 576 | 586 | 244 | 3.8 | 13.2 | 0 | 0 | 0 | 140.3002 | 48.1412 | 8.8014 | 0 | 48.1412 | 0 | 0 | 0 | 0 | 0 | 140.3002 | 0 | 310.3361 | 24.33% | 0 | 0 | 6.25 | 10% | 48.1412
1188 | 593 | 646 | 248 | 4.7 | 14.1 | 0 | 0 | 0 | 152.8933 | 63.8775 | 0 | 17.3309 | 46.5466 | 0 | 0 | 0 | 0 | 0 | 152.8933 | 0 | 463.2294 | 36.32% | 17.3309 | 0 | 21.9095 | 35.06% | 46.5466
1189 | 524 | 635 | 271 | 4.6 | 14.6 | 0 | 0 | 0 | 135.7914 | 63.2143 | 0 | 17.6286 | 45.5856 | 0 | 0 | 0 | 0 | 0 | 135.7914 | 0 | 599.0208 | 46.96% | 17.6286 | 0 | 37.838 | 60.54% | 45.5856
1190 | 494 | 605 | 277 | 4.1 | 15.1 | 0 | 0 | 0 | 126.9696 | 60.9478 | 0 | 16.1086 | 44.8392 | 0 | 0 | 0 | 0 | 0 | 126.9696 | 0 | 725.9904 | 56.92% | 16.1086 | 0 | 52.3931 | 83.83% | 44.8392
1191 | 569 | 563 | 239 | 3.8 | 15.3 | 0 | 0 | 0 | 145.8147 | 48.8306 | 11.1974 | 4.2685 | 44.562 | 0 | 0 | 0 | 0 | 0 | 145.8147 | 0 | 871.8051 | 68.35% | 4.2685 | 0 | 56.25 | 90% | 44.562
1192 | 441 | 383 | 189 | 4.3 | 14.9 | 0 | 0 | 0 | 100.3195 | 43.4558 | 0 | 0 | 43.4558 | 0 | 0 | 0 | 0 | 0 | 100.3195 | 0 | 972.1246 | 76.21% | 0 | 1.5686 | 54.5139 | 87.22% | 45.0244
1193 | 248 | 195 | 123 | 5.2 | 13.4 | 0 | 0 | 0 | 38.1782 | 22.047 | 0 | 0 | 22.047 | 0 | 0 | 0 | 0 | 0 | 38.1782 | 0 | 1010.3029 | 79.21% | 0 | 25 | 26.8456 | 42.95% | 47.047
1194 | 15 | 42 | 39 | 4.8 | 11 | 0 | 0 | 0 | 0 | 2.6763 | 0 | 0 | 2.6763 | 0 | 0 | 0 | 116.8429 | 47.2517 | 0 | 116.8429 | 893.4599 | 70.05% | 0 | 0.071984 | 26.7659 | 42.83% | 50
1195 | 0 | 0 | 0 | 3.6 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.9683 | 49.0869 | 0 | 120.9683 | 772.4916 | 60.56% | 0 | 0 | 26.7659 | 42.83% | 49.0869
1196 | 0 | 0 | 0 | 3.1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0488 | 45.2096 | 0 | 112.0488 | 660.4428 | 51.78% | 0 | 0 | 26.7659 | 42.83% | 45.2096
1197 | 0 | 0 | 0 | 1.3 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.7105 | 40.7001 | 0 | 101.7105 | 558.7323 | 43.8% | 0 | 0 | 26.7659 | 42.83% | 40.7001
1198 | 0 | 0 | 0 | 2.1 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7287 | 38.0888 | 0 | 95.7287 | 463.0036 | 36.3% | 0 | 0 | 26.7659 | 42.83% | 38.0888
1199 | 0 | 0 | 0 | 1.9 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463.0036 | 36.3% | 0 | 0 | 26.7659 | 42.83% | 0
1200 | 0 | 0 | 0 | 1.9 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463.0036 | 36.3% | 0 | 0 | 26.7659 | 42.83% | 0
1201 | 0 | 0 | 0 | 1.7 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463.0036 | 36.3% | 0 | 0 | 26.7659 | 42.83% | 0
1202 | 0 | 0 | 0 | 1.9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463.0036 | 36.3% | 0 | 0 | 26.7659 | 42.83% | 0
1203 | 0 | 0 | 0 | 1.5 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463.0036 | 36.3% | 0 | 0 | 26.7659 | 42.83% | 0
1204 | 0 | 0 | 0 | 2 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463.0036 | 36.3% | 0 | 0 | 26.7659 | 42.83% | 0
1205 | 0 | 0 | 0 | 2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.9064 | 44.2723 | 0 | 109.9064 | 353.0972 | 27.68% | 0 | 0 | 26.7659 | 42.83% | 44.2723
1206 | 0 | 0 | 0 | 2.2 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.014 | 47.3725 | 0 | 117.014 | 236.0831 | 18.51% | 0 | 0 | 26.7659 | 42.83% | 47.3725
1207 | 0 | 0 | 0 | 1.8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.4741 | 48.8794 | 0 | 120.4741 | 115.609 | 9.064% | 0 | 0 | 26.7659 | 42.83% | 48.8794
1208 | 54 | 55 | 46 | 2.3 | 4.6 | 0 | 0 | 0 | 0 | 2.2669 | 0 | 0 | 2.2669 | 0 | 0 | 0 | 115.609 | 46.7642 | 0 | 115.609 | 0 | 0% | 0 | 0 | 26.7659 | 42.83% | 49.0312
1209 | 304 | 225 | 129 | 1.2 | 7.7 | 0 | 0 | 0 | 41.6022 | 20.9303 | 0 | 0 | 20.9303 | 0 | 0 | 0 | 0 | 0 | 41.6022 | 0 | 41.6022 | 3.262% | 0 | 18.5374 | 6.25 | 10% | 39.4676
1210 | 493 | 416 | 184 | 2.1 | 10.6 | 0 | 0 | 0 | 103.9593 | 40.4582 | 0 | 0 | 40.4582 | 0 | 0 | 0 | 0 | 0 | 103.9593 | 0 | 145.5615 | 11.41% | 0 | 0 | 6.25 | 10% | 40.4582
1211 | 608 | 572 | 211 | 4.2 | 12 | 0 | 0 | 0 | 149.0284 | 47.5953 | 9.1968 | 0 | 47.5953 | 0 | 0 | 0 | 0 | 0 | 149.0284 | 0 | 294.5899 | 23.1% | 0 | 0 | 6.25 | 10% | 47.5953
1212 | 654 | 662 | 224 | 3.6 | 13 | 0 | 0 | 0 | 171.8894 | 65.7227 | 0 | 19.8474 | 45.8753 | 0 | 0 | 0 | 0 | 0 | 171.8894 | 0 | 466.4793 | 36.57% | 19.8474 | 0 | 24.1833 | 38.69% | 45.8753
1213 | 679 | 692 | 224 | 2.4 | 14.1 | 0 | 0 | 0 | 183.6451 | 69.0112 | 0 | 23.6776 | 45.3336 | 0 | 0 | 0 | 0 | 0 | 183.6451 | 0 | 650.1245 | 50.97% | 23.6776 | 0 | 45.5774 | 72.92% | 45.3336
1214 | 664 | 652 | 216 | 1.8 | 14.9 | 0 | 0 | 0 | 179.0767 | 44.406 | 21.8526 | 0 | 44.406 | 0 | 0 | 0 | 0 | 0 | 179.0767 | 0 | 829.2012 | 65.01% | 0 | 0 | 45.5774 | 72.92% | 44.406
1215 | 575 | 528 | 197 | 2.7 | 15.4 | 0 | 0 | 0 | 148.4293 | 55.7581 | 0.81168 | 11.8117 | 43.9464 | 0 | 0 | 0 | 0 | 0 | 148.4293 | 0 | 977.6305 | 76.65% | 11.8117 | 0 | 56.25 | 90% | 43.9464
1216 | 59 | 180 | 150 | 3.7 | 14.4 | 0 | 0 | 0 | 0 | 14.2822 | 0 | 0 | 14.2822 | 0 | 0 | 0 | 57.705 | 21.4151 | 0 | 57.705 | 919.9255 | 72.12% | 0 | 8.6307 | 46.6981 | 74.72% | 44.328
1217 | 1 | 85 | 84 | 4.6 | 13 | 0 | 0 | 0 | 0 | 5.3284 | 0 | 0 | 5.3284 | 0 | 0 | 0 | 106.8964 | 42.856 | 0 | 106.8964 | 813.0291 | 63.74% | 0 | 0 | 46.6981 | 74.72% | 48.1844
1218 | 3 | 29 | 29 | 4.1 | 11.4 | 0 | 0 | 0 | 0 | 1.5424 | 0 | 0 | 1.5424 | 0 | 0 | 0 | 119.6359 | 48.4576 | 0 | 119.6359 | 693.3932 | 54.36% | 0 | 0 | 46.6981 | 74.72% | 50
1219 | 0 | 0 | 0 | 3.8 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.8856 | 49.0451 | 0 | 120.8856 | 572.5076 | 44.88% | 0 | 0 | 46.6981 | 74.72% | 49.0451
1220 | 0 | 0 | 0 | 2.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.4483 | 45.8141 | 0 | 113.4483 | 459.0592 | 35.99% | 0 | 0 | 46.6981 | 74.72% | 45.8141
1221 | 0 | 0 | 0 | 3.1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.0592 | 35.99% | 0 | 11.5473 | 33.9183 | 54.27% | 11.5473
1222 | 0 | 0 | 0 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.0592 | 35.99% | 0 | 25 | 6.25 | 10% | 25
1223 | 0 | 0 | 0 | 2.4 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.0592 | 35.99% | 0 | 0 | 6.25 | 10% | 0
1224 | 0 | 0 | 0 | 2.2 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.0592 | 35.99% | 0 | 0 | 6.25 | 10% | 0
1225 | 0 | 0 | 0 | 1.7 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.0592 | 35.99% | 0 | 0 | 6.25 | 10% | 0
1226 | 0 | 0 | 0 | 2.1 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7053e-13 | 0 | 0 | 1.7053e-13 | 459.0592 | 35.99% | 0 | 0 | 6.25 | 10% | 0
1227 | 0 | 0 | 0 | 0.9 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.0592 | 35.99% | 0 | 0 | 6.25 | 10% | 0
1228 | 0 | 0 | 0 | 2.3 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459.0592 | 35.99% | 0 | 0 | 6.25 | 10% | 0
1229 | 0 | 0 | 0 | 3.3 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.8199 | 44.2459 | 0 | 109.8199 | 349.2394 | 27.38% | 0 | 0 | 6.25 | 10% | 44.2459
1230 | 0 | 0 | 0 | 2.4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.8673 | 46.8809 | 0 | 115.8673 | 233.372 | 18.3% | 0 | 0 | 6.25 | 10% | 46.8809
1231 | 0 | 1 | 1 | 1.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.8134 | 48.5772 | 0 | 119.8134 | 113.5586 | 8.903% | 0 | 0 | 6.25 | 10% | 48.5772
1232 | 95 | 67 | 51 | 3 | 5.9 | 0 | 0 | 0 | 0 | 2.7711 | 0 | 0 | 2.7711 | 0 | 0 | 0 | 113.5586 | 45.8785 | 0 | 113.5586 | 0 | 0% | 0 | 0 | 6.25 | 10% | 48.6496
1233 | 375 | 246 | 128 | 2.6 | 8.4 | 0 | 0 | 0 | 55.1015 | 23.1205 | 0 | 0 | 23.1205 | 0 | 0 | 0 | 0 | 0 | 55.1015 | 0 | 55.1015 | 4.32% | 0 | 0 | 6.25 | 10% | 23.1205
1234 | 572 | 439 | 169 | 4.3 | 10.8 | 0 | 0 | 0 | 122.5683 | 43.7542 | 0 | 0 | 43.7542 | 0 | 0 | 0 | 0 | 0 | 122.5683 | 0 | 177.6698 | 13.93% | 0 | 0 | 6.25 | 10% | 43.7542
1235 | 670 | 590 | 191 | 4.6 | 12.2 | 0 | 0 | 0 | 126.0868 | 47.2541 | 11.7875 | 0 | 47.2541 | 0 | 0 | 0 | 0 | 0 | 126.0868 | 0 | 303.7567 | 23.81% | 0 | 0 | 6.25 | 10% | 47.2541
1236 | 712 | 680 | 202 | 4.9 | 13.2 | 0 | 0 | 0 | 187.7872 | 45.6455 | 23.2048 | 0 | 45.6455 | 0 | 0 | 0 | 0 | 0 | 187.7872 | 0 | 491.5439 | 38.54% | 0 | 0 | 6.25 | 10% | 45.6455
1237 | 732 | 709 | 202 | 4.5 | 14 | 0 | 0 | 0 | 198.0501 | 52.2785 | 19.7215 | 7.5758 | 44.7027 | 0 | 0 | 0 | 0 | 0 | 198.0501 | 0 | 689.594 | 54.06% | 7.5758 | 0 | 13.0952 | 20.95% | 44.7027
1238 | 713 | 668 | 198 | 3.3 | 14.8 | 0 | 0 | 0 | 193.0478 | 69.0704 | 0.82195 | 25 | 44.0704 | 0 | 0 | 0 | 0 | 0 | 193.0478 | 0 | 882.6417 | 69.2% | 25 | 0 | 35.6842 | 57.09% | 44.0704
1239 | 680 | 566 | 176 | 3 | 15.4 | 0 | 0 | 0 | 178.8267 | 62.2366 | 0 | 18.5172 | 43.7194 | 0 | 0 | 0 | 0 | 0 | 178.8267 | 0 | 1061.4684 | 83.22% | 18.5172 | 0 | 52.4156 | 83.87% | 43.7194
1240 | 584 | 409 | 150 | 3.8 | 15.3 | 0 | 0 | 0 | 140.3135 | 48.2876 | 0 | 4.2436 | 44.0439 | 0 | 0 | 0 | 0 | 0 | 140.3135 | 0 | 1201.7819 | 94.22% | 4.2436 | 0 | 56.25 | 90% | 44.0439
1241 | 394 | 218 | 106 | 4.8 | 14.1 | 0 | 0 | 0 | 73.7283 | 28.0376 | 0 | 0 | 28.0376 | 0 | 0 | 0 | 0 | 0 | 73.7283 | 0 | 1275.5102 | 100% | 0 | 19.9811 | 34.1363 | 54.62% | 48.0187
1242 | 84 | 46 | 35 | 4.8 | 11.9 | 0 | 0 | 0 | 0 | 4.7896 | 0 | 0 | 4.7896 | 0 | 0 | 0 | 111.1427 | 44.7416 | 0 | 111.1427 | 1164.3675 | 91.29% | 0 | 0 | 34.1363 | 54.62% | 49.5311
1243 | 0 | 0 | 0 | 4 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.7011 | 48.5284 | 0 | 119.7011 | 1044.6664 | 81.9% | 0 | 0 | 34.1363 | 54.62% | 48.5284
1244 | 0 | 0 | 0 | 2.8 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.5732 | 45.0021 | 0 | 111.5732 | 933.0932 | 73.15% | 0 | 0 | 34.1363 | 54.62% | 45.0021
1245 | 0 | 0 | 0 | 2.3 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9553 | 40.8129 | 0 | 101.9553 | 831.1378 | 65.16% | 0 | 0 | 34.1363 | 54.62% | 40.8129
1246 | 0 | 0 | 0 | 1.8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.6767 | 38.0735 | 0 | 95.6767 | 735.4612 | 57.66% | 0 | 0 | 34.1363 | 54.62% | 38.0735
1247 | 0 | 0 | 0 | 2.3 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0185 | 35.6042 | 0 | 90.0185 | 645.4427 | 50.6% | 0 | 0 | 34.1363 | 54.62% | 35.6042
1248 | 0 | 0 | 0 | 2.1 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645.4427 | 50.6% | 0 | 4.4684 | 29.191 | 46.71% | 4.4684
1249 | 0 | 0 | 0 | 1.3 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645.4427 | 50.6% | 0 | 0 | 29.191 | 46.71% | 0
1250 | 0 | 0 | 0 | 3.2 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 645.4427 | 50.6% | 0 | 0 | 29.191 | 46.71% | 0
1251 | 0 | 0 | 0 | 3.1 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2791 | 34.4079 | 0 | 87.2791 | 558.1635 | 43.76% | 0 | 0 | 29.191 | 46.71% | 34.4079
1252 | 0 | 0 | 0 | 2.9 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2899 | 38.3409 | 0 | 96.2899 | 461.8736 | 36.21% | 0 | 0 | 29.191 | 46.71% | 38.3409
1253 | 0 | 0 | 0 | 3.2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.3524 | 44.4798 | 0 | 110.3524 | 351.5212 | 27.56% | 0 | 0 | 29.191 | 46.71% | 44.4798
1254 | 0 | 0 | 0 | 2.2 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.021 | 47.3906 | 0 | 117.021 | 234.5001 | 18.38% | 0 | 0 | 29.191 | 46.71% | 47.3906
1255 | 0 | 1 | 1 | 2.6 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.1136 | 48.7401 | 0 | 120.1136 | 114.3866 | 8.968% | 0 | 0 | 29.191 | 46.71% | 48.7401
1256 | 226 | 82 | 47 | 1.2 | 6.8 | 0 | 0 | 0 | 0 | 3.3801 | 0 | 0 | 3.3801 | 0 | 0 | 0 | 114.3866 | 46.2404 | 0 | 114.3866 | 0 | 0% | 1.0948 | 0 | 30.1803 | 48.29% | 48.5256
1257 | 577 | 278 | 96 | 0.6 | 9.1 | 0 | 0 | 0 | 30.3796 | 26.2532 | 0 | 0 | 26.2532 | 0 | 0 | 0 | 0 | 0 | 30.3796 | 0 | 30.3796 | 2.382% | 0 | 21.558 | 6.3213 | 10.11% | 47.8112
1258 | 778 | 479 | 110 | 0.8 | 13.4 | 0 | 0 | 0 | 176.8916 | 47.0087 | 0 | 0 | 47.0087 | 0 | 0 | 0 | 0 | 0 | 176.8916 | 0 | 207.2712 | 16.25% | 0 | 0.064395 | 6.25 | 10% | 47.073
1259 | 937 | 647 | 90 | 0.9 | 16 | 0 | 0 | 0 | 243.3767 | 46.6525 | 15.7788 | 0 | 46.6525 | 0 | 0 | 0 | 0 | 0 | 243.3767 | 0 | 450.648 | 35.33% | 0 | 0 | 6.25 | 10% | 46.6525
1260 | 995 | 744 | 78 | 1.3 | 17.9 | 0 | 0 | 0 | 273.1634 | 44.8921 | 26.5185 | 0 | 44.8921 | 0 | 0 | 0 | 0 | 0 | 273.1634 | 0 | 723.8114 | 56.75% | 0 | 0 | 6.25 | 10% | 44.8921
1261 | 996 | 766 | 78 | 2.5 | 18.7 | 0 | 0 | 0 | 278.3868 | 43.7375 | 28.2625 | 0 | 43.7375 | 0 | 0 | 0 | 0 | 0 | 278.3868 | 0 | 1002.1982 | 78.57% | 0 | 0 | 6.25 | 10% | 43.7375
1262 | 983 | 723 | 77 | 3.4 | 19.5 | 0 | 0 | 0 | 273.312 | 59.3062 | 12.6938 | 16.2914 | 43.0147 | 0 | 0 | 0 | 0 | 0 | 273.312 | 0 | 1275.5102 | 100% | 16.2914 | 0 | 20.9703 | 33.55% | 43.0147
1263 | 944 | 614 | 73 | 4.5 | 19.2 | 0 | 0 | 0 | 0 | 67.4228 | 2.488 | 25 | 42.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 25 | 0 | 43.5593 | 69.69% | 42.4228
1264 | 863 | 449 | 67 | 4.1 | 18.4 | 0 | 0 | 0 | 0 | 56.4862 | 0 | 14.0452 | 42.4409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 14.0452 | 0 | 56.25 | 90% | 42.4409
1265 | 685 | 245 | 54 | 3.9 | 17.6 | 0 | 0 | 0 | 0 | 36.4365 | 0 | 0 | 36.4365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 9.4834 | 45.7544 | 73.21% | 45.9199
1266 | 225 | 53 | 22 | 3.2 | 15.4 | 0 | 0 | 0 | 0 | 7.854 | 0 | 0 | 7.854 | 0 | 0 | 0 | 98.8583 | 39.265 | 0 | 98.8583 | 1176.6519 | 92.25% | 0 | 0 | 45.7544 | 73.21% | 47.119
1267 | 0 | 0 | 0 | 1.7 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.0804 | 46.4603 | 0 | 115.0804 | 1061.5715 | 83.23% | 0 | 0 | 45.7544 | 73.21% | 46.4603
1268 | 0 | 0 | 0 | 0.9 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.2113 | 43.5217 | 0 | 108.2113 | 953.3602 | 74.74% | 0 | 0 | 45.7544 | 73.21% | 43.5217
1269 | 0 | 0 | 0 | 0.6 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4276 | 40.1402 | 0 | 100.4276 | 852.9326 | 66.87% | 0 | 0 | 45.7544 | 73.21% | 40.1402
1270 | 0 | 0 | 0 | 0.8 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3548 | 37.93 | 0 | 95.3548 | 757.5778 | 59.39% | 0 | 0 | 45.7544 | 73.21% | 37.93
1271 | 0 | 0 | 0 | 1 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2247 | 35.256 | 0 | 89.2247 | 668.353 | 52.4% | 0 | 0 | 45.7544 | 73.21% | 35.256
1272 | 0 | 0 | 0 | 0.7 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6737 | 33.2701 | 0 | 84.6737 | 583.6793 | 45.76% | 0 | 0 | 45.7544 | 73.21% | 33.2701
1273 | 0 | 0 | 0 | 1 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3789 | 44.0544 | 0 | 109.3789 | 474.3004 | 37.19% | 11.6158 | 0 | 56.25 | 90% | 32.4386
1274 | 0 | 0 | 0 | 1.2 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474.3004 | 37.19% | 0 | 12.0969 | 42.862 | 68.58% | 12.0969
1275 | 0 | 0 | 0 | 2.5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474.3004 | 37.19% | 0 | 25 | 15.1936 | 24.31% | 25
1276 | 0 | 0 | 0 | 2.7 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8043 | 32.8843 | 0 | 83.8043 | 390.4961 | 30.61% | 0 | 0 | 15.1936 | 24.31% | 32.8843
1277 | 0 | 0 | 0 | 1.3 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5687 | 34.5332 | 0 | 87.5687 | 302.9274 | 23.75% | 0 | 0 | 15.1936 | 24.31% | 34.5332
1278 | 0 | 0 | 0 | 1.9 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9105 | 36.8632 | 0 | 92.9105 | 210.0169 | 16.47% | 0 | 0 | 15.1936 | 24.31% | 36.8632
1279 | 1 | 1 | 1 | 1.3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.0151 | 46.0774 | 0 | 114.0151 | 96.0018 | 7.527% | 5.4748 | 0 | 20.1405 | 32.22% | 40.6026
1280 | 471 | 97 | 32 | 1.7 | 9.2 | 0 | 0 | 0 | 0 | 4.1426 | 0 | 0 | 4.1426 | 0 | 0 | 0 | 96.0018 | 38.1981 | 0 | 96.0018 | 0 | 0% | 0 | 0 | 20.1405 | 32.22% | 42.3407
1281 | 805 | 311 | 59 | 1.3 | 14.8 | 0 | 0 | 0 | 0 | 29.84 | 0 | 0 | 29.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 12.5509 | 6.25 | 10% | 42.3908
1282 | 911 | 505 | 71 | 1.2 | 18.1 | 0 | 0 | 0 | 24.1428 | 41.3839 | 7.9774 | 0 | 41.3839 | 0 | 0 | 0 | 0 | 0 | 24.1428 | 0 | 24.1428 | 1.893% | 0 | 0 | 6.25 | 10% | 41.3839
1283 | 958 | 654 | 80 | 1.5 | 20.4 | 0 | 0 | 0 | 249.5687 | 41.1262 | 21.2509 | 0 | 41.1262 | 0 | 0 | 0 | 0 | 0 | 249.5687 | 0 | 273.7115 | 21.46% | 0 | 0 | 6.25 | 10% | 41.1262
1284 | 990 | 752 | 85 | 2.2 | 22.3 | 0 | 0 | 0 | 271.5541 | 40.1291 | 31.8709 | 0 | 40.1291 | 0 | 0 | 0 | 0 | 0 | 271.5541 | 0 | 545.2656 | 42.75% | 0 | 0 | 6.25 | 10% | 40.1291
1285 | 982 | 776 | 93 | 2 | 23.2 | 0 | 0 | 0 | 274.8384 | 38.4718 | 33.5282 | 0 | 38.4718 | 0 | 0 | 0 | 0 | 0 | 274.8384 | 0 | 820.104 | 64.3% | 0 | 0 | 6.25 | 10% | 38.4718
1286 | 910 | 716 | 111 | 3.6 | 23.7 | 0 | 0 | 0 | 251.9046 | 62.1738 | 9.8262 | 25 | 37.1738 | 0 | 0 | 0 | 0 | 0 | 251.9046 | 0 | 1072.0087 | 84.05% | 25 | 0 | 28.839 | 46.14% | 37.1738
1287 | 690 | 560 | 156 | 4.6 | 23.4 | 0 | 0 | 0 | 180.8247 | 60.6351 | 0 | 23.8917 | 36.7434 | 0 | 0 | 0 | 0 | 0 | 180.8247 | 0 | 1252.8333 | 98.22% | 23.8917 | 0 | 50.4266 | 80.68% | 36.7434
1288 | 546 | 412 | 162 | 4.9 | 22.5 | 0 | 0 | 0 | 0 | 43.5895 | 2.624 | 6.445 | 37.1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.8333 | 98.22% | 6.445 | 0 | 56.25 | 90% | 37.1445
1289 | 221 | 203 | 133 | 4.8 | 20.4 | 0 | 0 | 0 | 2.9691 | 21.0209 | 0 | 0 | 21.0209 | 0 | 0 | 0 | 0 | 0 | 2.9691 | 0 | 1255.8025 | 98.45% | 0 | 19.7836 | 34.3548 | 54.97% | 40.8045
1290 | 32 | 50 | 44 | 3 | 17.9 | 0 | 0 | 0 | 0 | 3.3842 | 0 | 0 | 3.3842 | 0 | 0 | 0 | 63.356 | 23.7699 | 0 | 63.356 | 1192.4464 | 93.49% | 0 | 15.2659 | 17.4595 | 27.94% | 42.4201
1291 | 0 | 0 | 0 | 1.3 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8875 | 42.4061 | 0 | 105.8875 | 1086.559 | 85.19% | 0 | 0 | 17.4595 | 27.94% | 42.4061
1292 | 0 | 0 | 0 | 0.7 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.7574 | 40.6708 | 0 | 101.7574 | 984.8016 | 77.21% | 0 | 0 | 17.4595 | 27.94% | 40.6708
1293 | 0 | 0 | 0 | 1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9981 | 37.7448 | 0 | 94.9981 | 889.8035 | 69.76% | 0 | 0 | 17.4595 | 27.94% | 37.7448
1294 | 0 | 0 | 0 | 1.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9741 | 35.107 | 0 | 88.9741 | 800.8294 | 62.79% | 0 | 0 | 17.4595 | 27.94% | 35.107
1295 | 0 | 0 | 0 | 1.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9168 | 32.4776 | 0 | 82.9168 | 717.9127 | 56.28% | 0 | 0 | 17.4595 | 27.94% | 32.4776
1296 | 0 | 0 | 0 | 0.9 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7297 | 30.6615 | 0 | 78.7297 | 639.1829 | 50.11% | 0 | 0 | 17.4595 | 27.94% | 30.6615
1297 | 0 | 0 | 0 | 1.3 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6547 | 29.7563 | 0 | 76.6547 | 562.5282 | 44.1% | 0 | 0 | 17.4595 | 27.94% | 29.7563
1298 | 0 | 0 | 0 | 1.7 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7839 | 29.3719 | 0 | 75.7839 | 486.7443 | 38.16% | 0 | 0 | 17.4595 | 27.94% | 29.3719
1299 | 0 | 0 | 0 | 2.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.9265 | 29.429 | 0 | 75.9265 | 410.8178 | 32.21% | 0 | 0 | 17.4595 | 27.94% | 29.429
1300 | 0 | 0 | 0 | 2.5 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3002 | 30.032 | 0 | 77.3002 | 333.5177 | 26.15% | 0 | 0 | 17.4595 | 27.94% | 30.032
1301 | 0 | 0 | 0 | 3.7 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9295 | 30.7312 | 0 | 78.9295 | 254.5882 | 19.96% | 0 | 0 | 17.4595 | 27.94% | 30.7312
1302 | 0 | 0 | 0 | 4.4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1124 | 31.6921 | 0 | 81.1124 | 173.4757 | 13.6% | 0 | 0 | 17.4595 | 27.94% | 31.6921
1303 | 1 | 2 | 2 | 4 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3555 | 34.8633 | 0 | 88.3555 | 85.1203 | 6.673% | 0 | 0 | 17.4595 | 27.94% | 34.8633
1304 | 325 | 89 | 40 | 4.3 | 9.9 | 0 | 0 | 0 | 0 | 3.6375 | 0 | 0 | 3.6375 | 0 | 0 | 0 | 85.1203 | 33.4416 | 0 | 85.1203 | 0 | 0% | 0 | 0 | 17.4595 | 27.94% | 37.0791
1305 | 660 | 288 | 75 | 4.4 | 13.4 | 0 | 0 | 0 | 0 | 27.6052 | 0 | 0 | 27.6052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 10.1285 | 6.25 | 10% | 37.7336
1306 | 810 | 481 | 90 | 5.1 | 15.7 | 0 | 0 | 0 | 183.5844 | 37.2518 | 11.5053 | 0 | 37.2518 | 0 | 0 | 0 | 0 | 0 | 183.5844 | 0 | 183.5844 | 14.39% | 0 | 0 | 6.25 | 10% | 37.2518
1307 | 905 | 640 | 92 | 7.2 | 16.6 | 0 | 0 | 0 | 230.6044 | 37.3757 | 27.8359 | 0 | 37.3757 | 0 | 0 | 0 | 0 | 0 | 230.6044 | 0 | 414.1888 | 32.47% | 0 | 0 | 6.25 | 10% | 37.3757
1308 | 937 | 739 | 100 | 7 | 17 | 0 | 0 | 0 | 252.4017 | 36.873 | 35.127 | 0 | 36.873 | 0 | 0 | 0 | 0 | 0 | 252.4017 | 0 | 666.5905 | 52.26% | 0 | 0 | 6.25 | 10% | 36.873
1309 | 922 | 769 | 120 | 7 | 16.9 | 0 | 0 | 0 | 253.2173 | 35.3591 | 36.6409 | 0 | 35.3591 | 0 | 0 | 0 | 0 | 0 | 253.2173 | 0 | 919.8078 | 72.11% | 0 | 0 | 6.25 | 10% | 35.3591
1310 | 815 | 681 | 134 | 6.7 | 16.9 | 0 | 0 | 0 | 0 | 42.7694 | 29.2306 | 8.4952 | 34.2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 919.8078 | 72.11% | 8.4952 | 0 | 13.926 | 22.28% | 34.2742
1311 | 864 | 622 | 115 | 6.6 | 17.4 | 0 | 0 | 0 | 155.443 | 58.8049 | 11.4383 | 25 | 33.8049 | 0 | 0 | 0 | 0 | 0 | 155.443 | 0 | 1075.2508 | 84.3% | 25 | 0 | 36.515 | 58.42% | 33.8049
1312 | 811 | 450 | 83 | 7 | 17 | 0 | 0 | 0 | 200.2594 | 56.4944 | 3.5527e-15 | 21.8414 | 34.653 | 0 | 0 | 0 | 0 | 0 | 200.2594 | 0 | 1275.5102 | 100% | 21.8414 | 0 | 56.25 | 90% | 34.653
1313 | 469 | 208 | 66 | 6.3 | 15.5 | 0 | 0 | 0 | 0 | 28.317 | 0 | 0 | 28.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 10.7759 | 44.3239 | 70.92% | 39.0929
1314 | 113 | 45 | 28 | 4.7 | 13.5 | 0 | 0 | 0 | 0 | 5.301 | 0 | 0 | 5.301 | 0 | 0 | 0 | 92.5696 | 36.6038 | 0 | 92.5696 | 1182.9406 | 92.74% | 0 | 0 | 44.3239 | 70.92% | 41.9048
1315 | 0 | 0 | 0 | 5.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5608 | 41.9089 | 0 | 104.5608 | 1078.3798 | 84.54% | 0 | 0 | 44.3239 | 70.92% | 41.9089
1316 | 0 | 0 | 0 | 4.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.84 | 40.3115 | 0 | 100.84 | 977.5398 | 76.64% | 0 | 0 | 44.3239 | 70.92% | 40.3115
1317 | 0 | 0 | 0 | 2.3 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5714 | 37.1473 | 0 | 93.5714 | 883.9684 | 69.3% | 0 | 0 | 44.3239 | 70.92% | 37.1473
1318 | 0 | 0 | 0 | 1.8 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8777 | 34.2254 | 0 | 86.8777 | 797.0908 | 62.49% | 0 | 0 | 44.3239 | 70.92% | 34.2254
1319 | 0 | 0 | 0 | 1.3 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9761 | 32.0904 | 0 | 81.9761 | 715.1147 | 56.06% | 0 | 0 | 44.3239 | 70.92% | 32.0904
1320 | 0 | 0 | 0 | 1.7 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8855 | 30.7451 | 0 | 78.8855 | 636.2291 | 49.88% | 0 | 0 | 44.3239 | 70.92% | 30.7451
1321 | 0 | 0 | 0 | 2.2 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.2291 | 49.88% | 0 | 0 | 44.3239 | 70.92% | 0
1322 | 0 | 0 | 0 | 1.2 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.2291 | 49.88% | 0 | 22.3896 | 19.5447 | 31.27% | 22.3896
1323 | 0 | 0 | 0 | 0.8 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1873 | 31.7437 | 0 | 81.1873 | 555.0418 | 43.52% | 0 | 0 | 19.5447 | 31.27% | 31.7437
1324 | 0 | 0 | 0 | 1.5 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4109 | 36.2086 | 0 | 91.4109 | 463.6309 | 36.35% | 0 | 0 | 19.5447 | 31.27% | 36.2086
1325 | 0 | 0 | 0 | 2.7 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5561 | 42.3852 | 0 | 105.5561 | 358.0748 | 28.07% | 0 | 0 | 19.5447 | 31.27% | 42.3852
1326 | 0 | 0 | 0 | 2.8 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.4244 | 49.3126 | 0 | 121.4244 | 236.6504 | 18.55% | 3.3607 | 0 | 22.5812 | 36.13% | 45.9519
1327 | 0 | 1 | 1 | 4.1 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9866 | 0 | 127.551 | 109.0994 | 8.553% | 4.4554 | 0 | 26.6069 | 42.57% | 47.5312
1328 | 309 | 95 | 41 | 2.5 | 7.4 | 0 | 0 | 0 | 0 | 3.6272 | 0 | 0 | 3.6272 | 0 | 0 | 0 | 109.0994 | 43.9305 | 0 | 109.0994 | 0 | 0% | 0 | 0 | 26.6069 | 42.57% | 47.5577
1329 | 696 | 299 | 71 | 3 | 9.3 | 0 | 0 | 0 | 0 | 28.7476 | 0 | 0 | 28.7476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 18.3937 | 6.25 | 10% | 47.1413
1330 | 869 | 497 | 75 | 4 | 12.5 | 0 | 0 | 0 | 0 | 46.6901 | 3.7072 | 0 | 46.6901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.6901
1331 | 949 | 652 | 74 | 4.1 | 15.3 | 0 | 0 | 0 | 0 | 46.5522 | 18.3803 | 0 | 46.5522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.5522
1332 | 979 | 746 | 77 | 5.3 | 17 | 0 | 0 | 0 | 266.4546 | 45.0272 | 26.9728 | 0 | 45.0272 | 0 | 0 | 0 | 0 | 0 | 266.4546 | 0 | 266.4546 | 20.89% | 0 | 0 | 6.25 | 10% | 45.0272
1333 | 985 | 772 | 77 | 5.7 | 17.3 | 0 | 0 | 0 | 85.6744 | 44.1428 | 27.8572 | 0 | 44.1428 | 0 | 0 | 0 | 0 | 0 | 85.6744 | 0 | 352.129 | 27.61% | 0 | 0 | 6.25 | 10% | 44.1428
1334 | 984 | 733 | 72 | 5.6 | 17.3 | 0 | 0 | 0 | 272.4692 | 58.0195 | 13.9805 | 14.7039 | 43.3156 | 0 | 0 | 0 | 0 | 0 | 272.4692 | 0 | 624.5982 | 48.97% | 14.7039 | 0 | 19.5359 | 31.26% | 43.3156
1335 | 957 | 627 | 67 | 5.1 | 17.1 | 0 | 0 | 0 | 258.178 | 67.8309 | 3.2699 | 25 | 42.8309 | 0 | 0 | 0 | 0 | 0 | 258.178 | 0 | 882.7762 | 69.21% | 25 | 0 | 42.1249 | 67.4% | 42.8309
1336 | 898 | 466 | 59 | 4.8 | 16.7 | 0 | 0 | 0 | 226.3694 | 58.3285 | 0 | 15.6327 | 42.6958 | 0 | 0 | 0 | 0 | 0 | 226.3694 | 0 | 1109.1456 | 86.96% | 15.6327 | 0 | 56.25 | 90% | 42.6958
1337 | 771 | 267 | 45 | 4.7 | 16 | 0 | 0 | 0 | 166.3646 | 39.4193 | 0 | 0 | 39.4193 | 0 | 0 | 0 | 0 | 0 | 166.3646 | 0 | 1275.5102 | 100% | 0 | 6.8891 | 48.6256 | 77.8% | 46.3085
1338 | 318 | 68 | 22 | 4.3 | 13.7 | 0 | 0 | 0 | 0 | 10.2607 | 0 | 0 | 10.2607 | 0 | 0 | 0 | 62.122 | 23.351 | 0 | 62.122 | 1213.3882 | 95.13% | 0 | 14.6548 | 32.4066 | 51.85% | 48.2666
1339 | 0 | 0 | 0 | 3.2 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3919 | 47.4936 | 0 | 117.3919 | 1095.9963 | 85.93% | 0 | 0 | 32.4066 | 51.85% | 47.4936
1340 | 0 | 0 | 0 | 3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5136 | 43.6596 | 0 | 108.5136 | 987.4828 | 77.42% | 0 | 0 | 32.4066 | 51.85% | 43.6596
1341 | 0 | 0 | 0 | 2.3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7507 | 39.4132 | 0 | 98.7507 | 888.7321 | 69.68% | 0 | 0 | 32.4066 | 51.85% | 39.4132
1342 | 0 | 0 | 0 | 1.7 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1151 | 36.9551 | 0 | 93.1151 | 795.617 | 62.38% | 0 | 0 | 32.4066 | 51.85% | 36.9551
1343 | 0 | 0 | 0 | 1.1 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5452 | 34.5249 | 0 | 87.5452 | 708.0718 | 55.51% | 0 | 0 | 32.4066 | 51.85% | 34.5249
1344 | 0 | 0 | 0 | 1.1 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3364 | 33.1224 | 0 | 84.3364 | 623.7353 | 48.9% | 0 | 0 | 32.4066 | 51.85% | 33.1224
1345 | 0 | 0 | 0 | 1.3 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.7353 | 48.9% | 0 | 6.1419 | 25.6092 | 40.97% | 6.1419
1346 | 0 | 0 | 0 | 2.3 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.7353 | 48.9% | 0 | 0 | 25.6092 | 40.97% | 0
1347 | 0 | 0 | 0 | 1.7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.118 | 33.465 | 0 | 85.118 | 538.6174 | 42.23% | 0 | 0 | 25.6092 | 40.97% | 33.465
1348 | 0 | 0 | 0 | 1.4 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6961 | 37.2016 | 0 | 93.6961 | 444.9213 | 34.88% | 0 | 0 | 25.6092 | 40.97% | 37.2016
1349 | 0 | 0 | 0 | 0.8 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.5117 | 43.2209 | 0 | 107.5117 | 337.4096 | 26.45% | 0 | 0 | 25.6092 | 40.97% | 43.2209
1350 | 0 | 0 | 0 | 2.3 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.8278 | 45.9923 | 0 | 113.8278 | 223.5818 | 17.53% | 0 | 0 | 25.6092 | 40.97% | 45.9923
1351 | 3 | 2 | 2 | 2.2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.9106 | 47.3418 | 0 | 116.9106 | 106.6712 | 8.363% | 0 | 0 | 25.6092 | 40.97% | 47.3418
1352 | 481 | 103 | 32 | 1.4 | 8.4 | 0 | 0 | 0 | 0 | 4.2658 | 0 | 0 | 4.2658 | 0 | 0 | 0 | 106.6712 | 42.8629 | 0 | 106.6712 | 0 | 0% | 0 | 0 | 25.6092 | 40.97% | 47.1288
1353 | 786 | 310 | 51 | 1.1 | 11.8 | 0 | 0 | 0 | 0 | 29.2034 | 0 | 0 | 29.2034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 17.4922 | 6.25 | 10% | 46.6956
1354 | 912 | 506 | 59 | 2.8 | 14.5 | 0 | 0 | 0 | 212.9541 | 46.4129 | 3.5568 | 0 | 46.4129 | 0 | 0 | 0 | 0 | 0 | 212.9541 | 0 | 212.9541 | 16.7% | 0 | 0 | 6.25 | 10% | 46.4129
1355 | 970 | 658 | 63 | 4.7 | 16.5 | 0 | 0 | 0 | 252.3561 | 46.2527 | 19.0491 | 0 | 46.2527 | 0 | 0 | 0 | 0 | 0 | 252.3561 | 0 | 465.3102 | 36.48% | 0 | 0 | 6.25 | 10% | 46.2527
1356 | 992 | 751 | 66 | 4 | 18.1 | 0 | 0 | 0 | 271.7597 | 44.8211 | 27.1789 | 0 | 44.8211 | 0 | 0 | 0 | 0 | 0 | 271.7597 | 0 | 737.0699 | 57.79% | 0 | 0 | 6.25 | 10% | 44.8211
1357 | 997 | 775 | 67 | 5.4 | 19.1 | 0 | 0 | 0 | 277.6852 | 43.7696 | 28.2304 | 0 | 43.7696 | 0 | 0 | 0 | 0 | 0 | 277.6852 | 0 | 1014.7551 | 79.56% | 0 | 0 | 6.25 | 10% | 43.7696
1358 | 984 | 732 | 66 | 6.2 | 19.3 | 0 | 0 | 0 | 260.7551 | 68.1345 | 3.8655 | 25 | 43.1345 | 0 | 0 | 0 | 0 | 0 | 260.7551 | 0 | 1275.5102 | 100% | 25 | 0 | 28.839 | 46.14% | 43.1345
1359 | 957 | 628 | 62 | 7 | 19.1 | 0 | 0 | 0 | 0 | 67.6499 | 3.3364 | 25 | 42.6499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 25 | 0 | 51.428 | 82.28% | 42.6499
1360 | 900 | 469 | 56 | 7.1 | 18.5 | 0 | 0 | 0 | 0 | 47.9378 | 10.5163 | 5.3367 | 42.6011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 5.3367 | 0 | 56.25 | 90% | 42.6011
1361 | 763 | 269 | 46 | 6.3 | 17.3 | 0 | 0 | 0 | 0 | 39.1822 | 0 | 0 | 39.1822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 7.2182 | 48.2614 | 77.22% | 46.4004
1362 | 333 | 70 | 21 | 4.3 | 15.7 | 0 | 0 | 0 | 0 | 10.4474 | 0 | 0 | 10.4474 | 0 | 0 | 0 | 62.9879 | 23.6785 | 0 | 62.9879 | 1212.5223 | 95.06% | 0 | 14.1267 | 32.6269 | 52.2% | 48.2527
1363 | 0 | 0 | 0 | 2.2 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.0899 | 47.2973 | 0 | 117.0899 | 1095.4324 | 85.88% | 0 | 0 | 32.6269 | 52.2% | 47.2973
1364 | 0 | 0 | 0 | 2.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3102 | 43.5481 | 0 | 108.3102 | 987.1221 | 77.39% | 0 | 0 | 32.6269 | 52.2% | 43.5481
1365 | 0 | 0 | 0 | 1.3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8608 | 39.4411 | 0 | 98.8608 | 888.2613 | 69.64% | 0 | 0 | 32.6269 | 52.2% | 39.4411
1366 | 0 | 0 | 0 | 0.6 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9571 | 36.8841 | 0 | 92.9571 | 795.3042 | 62.35% | 0 | 0 | 32.6269 | 52.2% | 36.8841
1367 | 0 | 0 | 0 | 0.4 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5518 | 34.5277 | 0 | 87.5518 | 707.7524 | 55.49% | 0 | 0 | 32.6269 | 52.2% | 34.5277
1368 | 0 | 0 | 0 | 0.7 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.33 | 33.1196 | 0 | 84.33 | 623.4224 | 48.88% | 0 | 0 | 32.6269 | 52.2% | 33.1196
1369 | 0 | 0 | 0 | 0.4 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.4224 | 48.88% | 0 | 0 | 32.6269 | 52.2% | 0
1370 | 0 | 0 | 0 | 0.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623.4224 | 48.88% | 0 | 6.9596 | 24.9245 | 39.88% | 6.9596
1371 | 0 | 0 | 0 | 0.8 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7468 | 33.738 | 0 | 85.7468 | 537.6756 | 42.15% | 0 | 0 | 24.9245 | 39.88% | 33.738
1372 | 0 | 0 | 0 | 2.2 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.418 | 37.5247 | 0 | 94.418 | 443.2575 | 34.75% | 0 | 0 | 24.9245 | 39.88% | 37.5247
1373 | 0 | 0 | 0 | 0.9 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3489 | 43.1624 | 0 | 107.3489 | 335.9087 | 26.34% | 0 | 0 | 24.9245 | 39.88% | 43.1624
1374 | 0 | 0 | 0 | 1 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.8132 | 45.9826 | 0 | 113.8132 | 222.0955 | 17.41% | 0 | 0 | 24.9245 | 39.88% | 45.9826
1375 | 10 | 2 | 2 | 1.2 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.7555 | 47.2708 | 0 | 116.7555 | 105.3399 | 8.259% | 0 | 0 | 24.9245 | 39.88% | 47.2708
1376 | 567 | 113 | 28 | 0.4 | 8.2 | 0 | 0 | 0 | 0 | 4.7529 | 0 | 0 | 4.7529 | 0 | 0 | 0 | 105.3399 | 42.284 | 0 | 105.3399 | 0 | 0% | 0 | 0 | 24.9245 | 39.88% | 47.0368
1377 | 830 | 321 | 45 | 0.9 | 13.8 | 0 | 0 | 0 | 153.1941 | 29.7023 | 0 | 0 | 29.7023 | 0 | 0 | 0 | 0 | 0 | 153.1941 | 0 | 153.1941 | 12.01% | 0 | 16.8735 | 6.25 | 10% | 46.5759
1378 | 935 | 515 | 53 | 1 | 16.9 | 0 | 0 | 0 | 220.7705 | 46.243 | 2.6094 | 0 | 46.243 | 0 | 0 | 0 | 0 | 0 | 220.7705 | 0 | 373.9646 | 29.32% | 0 | 0 | 6.25 | 10% | 46.243
1379 | 986 | 667 | 58 | 1.7 | 18 | 0 | 0 | 0 | 259.5424 | 45.8335 | 17.3105 | 0 | 45.8335 | 0 | 0 | 0 | 0 | 0 | 259.5424 | 0 | 633.507 | 49.67% | 0 | 0 | 6.25 | 10% | 45.8335
1380 | 1001 | 756 | 62 | 1.7 | 19.1 | 0 | 0 | 0 | 276.1883 | 44.3183 | 26.9316 | 0 | 44.3183 | 0 | 0 | 0 | 0 | 0 | 276.1883 | 0 | 909.6953 | 71.32% | 0 | 0 | 6.25 | 10% | 44.3183
1381 | 1001 | 779 | 64 | 2 | 20.1 | 0 | 0 | 0 | 93.1529 | 43.466 | 28.534 | 0 | 43.466 | 0 | 0 | 0 | 0 | 0 | 93.1529 | 0 | 1002.8481 | 78.62% | 0 | 0 | 6.25 | 10% | 43.466
1382 | 980 | 734 | 67 | 4.8 | 19.5 | 0 | 0 | 0 | 272.6621 | 58.7196 | 13.2804 | 15.8623 | 42.8574 | 0 | 0 | 0 | 0 | 0 | 272.6621 | 0 | 1275.5102 | 100% | 15.8623 | 0 | 20.5825 | 32.93% | 42.8574
1383 | 945 | 627 | 65 | 4.6 | 19.1 | 0 | 0 | 0 | 0 | 67.3616 | 2.0933 | 25 | 42.3616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 25 | 0 | 43.1715 | 69.07% | 42.3616
1384 | 877 | 466 | 60 | 5 | 18.7 | 0 | 0 | 0 | 0 | 56.907 | 0 | 14.4744 | 42.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 14.4744 | 0 | 56.25 | 90% | 42.4326
1385 | 736 | 267 | 48 | 4.7 | 17.8 | 0 | 0 | 0 | 0 | 37.8652 | 0 | 0 | 37.8652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 8.3458 | 47.0134 | 75.22% | 46.211
1386 | 304 | 71 | 23 | 3.5 | 16.1 | 0 | 0 | 0 | 0 | 9.8666 | 0 | 0 | 9.8666 | 0 | 0 | 0 | 83.459 | 32.5504 | 0 | 83.459 | 1192.0512 | 93.46% | 0 | 5.6031 | 40.8123 | 65.3% | 48.0201
1387 | 0 | 0 | 0 | 2.4 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.5576 | 46.6302 | 0 | 115.5576 | 1076.4937 | 84.4% | 0 | 0 | 40.8123 | 65.3% | 46.6302
1388 | 0 | 0 | 0 | 0.7 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.539 | 43.2139 | 0 | 107.539 | 968.9546 | 75.97% | 0 | 0 | 40.8123 | 65.3% | 43.2139
1389 | 0 | 0 | 0 | 0.9 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8286 | 39.4313 | 0 | 98.8286 | 870.126 | 68.22% | 0 | 0 | 40.8123 | 65.3% | 39.4313
1390 | 0 | 0 | 0 | 0.6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5404 | 37.1362 | 0 | 93.5404 | 776.5856 | 60.88% | 0 | 0 | 40.8123 | 65.3% | 37.1362
1391 | 0 | 0 | 0 | 1.1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4403 | 34.9065 | 0 | 88.4403 | 688.1453 | 53.95% | 0 | 0 | 40.8123 | 65.3% | 34.9065
1392 | 0 | 0 | 0 | 1 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9387 | 33.3801 | 0 | 84.9387 | 603.2066 | 47.29% | 0 | 0 | 40.8123 | 65.3% | 33.3801
1393 | 0 | 0 | 0 | 0.9 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603.2066 | 47.29% | 0 | 16.0187 | 23.0838 | 36.93% | 16.0187
1394 | 0 | 0 | 0 | 1.1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603.2066 | 47.29% | 0 | 0 | 23.0838 | 36.93% | 0
1395 | 0 | 0 | 0 | 0.7 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5808 | 33.6656 | 0 | 85.5808 | 517.6259 | 40.58% | 0 | 0 | 23.0838 | 36.93% | 33.6656
1396 | 0 | 0 | 0 | 0.9 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8506 | 36.8381 | 0 | 92.8506 | 424.7752 | 33.3% | 0 | 0 | 23.0838 | 36.93% | 36.8381
1397 | 0 | 0 | 0 | 0.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7297 | 41.1527 | 0 | 102.7297 | 322.0455 | 25.25% | 0 | 0 | 23.0838 | 36.93% | 41.1527
1398 | 0 | 0 | 0 | 1.5 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5569 | 43.6888 | 0 | 108.5569 | 213.4886 | 16.74% | 0 | 0 | 23.0838 | 36.93% | 43.6888
1399 | 22 | 3 | 3 | 1.2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.2918 | 45.3196 | 0 | 112.2918 | 101.1968 | 7.934% | 0 | 0 | 23.0838 | 36.93% | 45.3196
1400 | 584 | 120 | 29 | 0.6 | 9.9 | 0 | 0 | 0 | 0 | 4.926 | 0 | 0 | 4.926 | 0 | 0 | 0 | 101.1968 | 40.4535 | 0 | 101.1968 | 0 | 0% | 0 | 0 | 23.0838 | 36.93% | 45.3795
1401 | 849 | 334 | 47 | 0.2 | 16.3 | 0 | 0 | 0 | 115.082 | 29.892 | 0 | 0 | 29.892 | 0 | 0 | 0 | 0 | 0 | 115.082 | 0 | 115.082 | 9.022% | 0 | 15.2104 | 6.25 | 10% | 45.1024
1402 | 950 | 530 | 55 | 0.6 | 20.1 | 0 | 0 | 0 | 0 | 44.7083 | 3.9556 | 0 | 44.7083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.082 | 9.022% | 0 | 0 | 6.25 | 10% | 44.7083
1403 | 995 | 681 | 60 | 1.7 | 22 | 0 | 0 | 0 | 0 | 44.3879 | 18.5288 | 0 | 44.3879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.082 | 9.022% | 0 | 0 | 6.25 | 10% | 44.3879
1404 | 1011 | 772 | 65 | 3.2 | 22.6 | 0 | 0 | 0 | 0 | 43.0064 | 28.9936 | 0 | 43.0064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.082 | 9.022% | 0 | 0 | 6.25 | 10% | 43.0064
1405 | 1001 | 795 | 74 | 3.7 | 23.2 | 0 | 0 | 0 | 281.1768 | 42.2404 | 29.7596 | 0 | 42.2404 | 0 | 0 | 0 | 0 | 0 | 281.1768 | 0 | 396.2588 | 31.07% | 0 | 0 | 6.25 | 10% | 42.2404
1406 | 969 | 751 | 86 | 4.6 | 23.7 | 0 | 0 | 0 | 269.9433 | 56.515 | 15.485 | 14.9041 | 41.6109 | 0 | 0 | 0 | 0 | 0 | 269.9433 | 0 | 666.2021 | 52.23% | 14.9041 | 0 | 19.7168 | 31.55% | 41.6109
1407 | 954 | 644 | 70 | 5.5 | 23.7 | 0 | 0 | 0 | 257.698 | 66.0928 | 3.697 | 25 | 41.0928 | 0 | 0 | 0 | 0 | 0 | 257.698 | 0 | 923.9002 | 72.43% | 25 | 0 | 42.3058 | 67.69% | 41.0928
1408 | 866 | 478 | 71 | 5.8 | 23.2 | 0 | 0 | 0 | 217.9343 | 56.595 | 0 | 15.4325 | 41.1625 | 0 | 0 | 0 | 0 | 0 | 217.9343 | 0 | 1141.8344 | 89.52% | 15.4325 | 0 | 56.25 | 90% | 41.1625
1409 | 627 | 264 | 71 | 4.1 | 22.3 | 0 | 0 | 0 | 133.6758 | 34.7963 | 0 | 0 | 34.7963 | 0 | 0 | 0 | 0 | 0 | 133.6758 | 0 | 1275.5102 | 100% | 0 | 10.1027 | 45.069 | 72.11% | 44.8991
1410 | 263 | 81 | 38 | 3.2 | 19.8 | 0 | 0 | 0 | 0 | 10.1227 | 0 | 0 | 10.1227 | 0 | 0 | 0 | 73.0825 | 27.8972 | 0 | 73.0825 | 1202.4277 | 94.27% | 0 | 8.6478 | 35.4982 | 56.8% | 46.6678
1411 | 1 | 0 | 0 | 1.9 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.9604 | 45.8725 | 0 | 113.9604 | 1088.4673 | 85.34% | 0 | 0 | 35.4982 | 56.8% | 45.8725
1412 | 0 | 0 | 0 | 1.1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3064 | 42.6345 | 0 | 106.3064 | 982.1608 | 77% | 0 | 0 | 35.4982 | 56.8% | 42.6345
1413 | 0 | 0 | 0 | 0.7 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3225 | 39.1737 | 0 | 98.3225 | 883.8383 | 69.29% | 0 | 0 | 35.4982 | 56.8% | 39.1737
1414 | 0 | 0 | 0 | 0.8 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1288 | 36.9203 | 0 | 93.1288 | 790.7096 | 61.99% | 0 | 0 | 35.4982 | 56.8% | 36.9203
1415 | 0 | 0 | 0 | 1.4 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5483 | 34.9134 | 0 | 88.5483 | 702.1612 | 55.05% | 0 | 0 | 35.4982 | 56.8% | 34.9134
1416 | 0 | 0 | 0 | 1.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0539 | 33.4065 | 0 | 85.0539 | 617.1073 | 48.38% | 0 | 0 | 35.4982 | 56.8% | 33.4065
1417 | 0 | 0 | 0 | 1.1 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.1073 | 48.38% | 0 | 9.2433 | 25.2684 | 40.43% | 9.2433
1418 | 0 | 0 | 0 | 1.1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.1073 | 48.38% | 0 | 0 | 25.2684 | 40.43% | 0
1419 | 0 | 0 | 0 | 1 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6692 | 33.6865 | 0 | 85.6692 | 531.4381 | 41.66% | 0 | 0 | 25.2684 | 40.43% | 33.6865
1420 | 0 | 0 | 0 | 0.6 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5921 | 37.1612 | 0 | 93.5921 | 437.846 | 34.33% | 0 | 0 | 25.2684 | 40.43% | 37.1612
1421 | 0 | 0 | 0 | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7406 | 42.0134 | 0 | 104.7406 | 333.1054 | 26.12% | 0 | 0 | 25.2684 | 40.43% | 42.0134
1422 | 0 | 0 | 0 | 1.6 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.149 | 44.8016 | 0 | 111.149 | 221.9564 | 17.4% | 0 | 0 | 25.2684 | 40.43% | 44.8016
1423 | 20 | 5 | 5 | 0.8 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.193 | 46.5828 | 0 | 115.193 | 106.7634 | 8.37% | 0 | 0 | 25.2684 | 40.43% | 46.5828
1424 | 397 | 112 | 42 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 4.2899 | 0 | 0 | 4.2899 | 0 | 0 | 0 | 106.7634 | 42.8528 | 0 | 106.7634 | 0 | 0% | 0 | 0 | 25.2684 | 40.43% | 47.1427
1425 | 756 | 329 | 68 | 0.8 | 16 | 0 | 0 | 0 | 140.456 | 29.4445 | 0 | 0 | 29.4445 | 0 | 0 | 0 | 0 | 0 | 140.456 | 0 | 140.456 | 11.01% | 0 | 17.1842 | 6.25 | 10% | 46.6288
1426 | 773 | 520 | 127 | 0.8 | 19.7 | 0 | 0 | 0 | 181.3603 | 46.0007 | 1.1519 | 0 | 46.0007 | 0 | 0 | 0 | 0 | 0 | 181.3603 | 0 | 321.8163 | 25.23% | 0 | 0 | 6.25 | 10% | 46.0007
1427 | 494 | 561 | 248 | 1.5 | 20.8 | 0 | 0 | 0 | 121.9713 | 45.4116 | 4.3696 | 0 | 45.4116 | 0 | 0 | 0 | 0 | 0 | 121.9713 | 0 | 443.7875 | 34.79% | 0 | 0 | 6.25 | 10% | 45.4116
1428 | 626 | 675 | 229 | 2.8 | 20.9 | 0 | 0 | 0 | 166.0259 | 43.9548 | 18.1028 | 0 | 43.9548 | 0 | 0 | 0 | 0 | 0 | 166.0259 | 0 | 609.8134 | 47.81% | 0 | 0 | 6.25 | 10% | 43.9548
1429 | 730 | 766 | 231 | 3.4 | 21.7 | 0 | 0 | 0 | 200.4884 | 67.6262 | 4.3738 | 25 | 42.6262 | 0 | 0 | 0 | 0 | 0 | 200.4884 | 0 | 810.3018 | 63.53% | 25 | 0 | 28.839 | 46.14% | 42.6262
1430 | 523 | 671 | 300 | 3.9 | 22.2 | 0 | 0 | 0 | 137.5317 | 59.5077 | 3.3238 | 17.6057 | 41.902 | 0 | 0 | 0 | 0 | 0 | 137.5317 | 0 | 947.8335 | 74.31% | 17.6057 | 0 | 44.7468 | 71.59% | 41.902
1431 | 427 | 578 | 313 | 4.6 | 22 | 0 | 0 | 0 | 104.9156 | 54.3321 | 0 | 12.7309 | 41.6012 | 0 | 0 | 0 | 0 | 0 | 104.9156 | 0 | 1052.7491 | 82.54% | 12.7309 | 0 | 56.25 | 90% | 41.6012
1432 | 257 | 368 | 236 | 4.2 | 20.8 | 0 | 0 | 0 | 51.2713 | 34.4873 | 0 | 0 | 34.4873 | 0 | 0 | 0 | 0 | 0 | 51.2713 | 0 | 1104.0204 | 86.56% | 0 | 7.0581 | 48.4385 | 77.5% | 41.5454
1433 | 18 | 143 | 137 | 3.6 | 17.9 | 0 | 0 | 0 | 0 | 9.9451 | 0 | 0 | 9.9451 | 0 | 0 | 0 | 43.8355 | 15.3195 | 0 | 43.8355 | 1060.1849 | 83.12% | 0 | 19.7097 | 26.6252 | 42.6% | 44.9743
1434 | 27 | 47 | 42 | 2.5 | 15.8 | 0 | 0 | 0 | 0 | 3.0943 | 0 | 0 | 3.0943 | 0 | 0 | 0 | 107.9911 | 43.2114 | 0 | 107.9911 | 952.1938 | 74.65% | 0 | 0 | 26.6252 | 42.6% | 46.3057
1435 | 0 | 0 | 0 | 1.4 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4814 | 45.2514 | 0 | 112.4814 | 839.7124 | 65.83% | 0 | 0 | 26.6252 | 42.6% | 45.2514
1436 | 0 | 0 | 0 | 0.3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8213 | 42.388 | 0 | 105.8213 | 733.8911 | 57.54% | 0 | 0 | 26.6252 | 42.6% | 42.388
1437 | 0 | 0 | 0 | 0.3 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5183 | 39.2057 | 0 | 98.5183 | 635.3728 | 49.81% | 0 | 0 | 26.6252 | 42.6% | 39.2057
1438 | 0 | 0 | 0 | 1.5 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4502 | 36.9997 | 0 | 93.4502 | 541.9225 | 42.49% | 0 | 0 | 26.6252 | 42.6% | 36.9997
1439 | 0 | 0 | 0 | 1.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8961 | 34.5792 | 0 | 87.8961 | 454.0265 | 35.6% | 0 | 0 | 26.6252 | 42.6% | 34.5792
1440 | 0 | 0 | 0 | 1.2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4084 | 33.0667 | 0 | 84.4084 | 369.6181 | 28.98% | 0 | 0 | 26.6252 | 42.6% | 33.0667
1441 | 0 | 0 | 0 | 2 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369.6181 | 28.98% | 0 | 0 | 26.6252 | 42.6% | 0
1442 | 0 | 0 | 0 | 2 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369.6181 | 28.98% | 0 | 0 | 26.6252 | 42.6% | 0
1443 | 0 | 0 | 0 | 2.3 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369.6181 | 28.98% | 0 | 0 | 26.6252 | 42.6% | 0
1444 | 0 | 0 | 0 | 2.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369.6181 | 28.98% | 0 | 5.4505 | 20.593 | 32.95% | 5.4505
1445 | 0 | 0 | 0 | 2.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1871 | 33.8842 | 0 | 86.1871 | 283.431 | 22.22% | 0 | 0 | 20.593 | 32.95% | 33.8842
1446 | 0 | 0 | 0 | 1 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2411 | 36.1223 | 0 | 91.2411 | 192.1899 | 15.07% | 0 | 0 | 20.593 | 32.95% | 36.1223
1447 | 0 | 2 | 2 | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0429 | 39.5274 | 0 | 99.0429 | 93.147 | 7.303% | 0 | 0 | 20.593 | 32.95% | 39.5274
1448 | 394 | 112 | 41 | 1.4 | 11.1 | 0 | 0 | 0 | 0 | 4.2884 | 0 | 0 | 4.2884 | 0 | 0 | 0 | 93.147 | 36.92 | 0 | 93.147 | 0 | 0% | 0 | 0 | 20.593 | 32.95% | 41.2084
1449 | 703 | 319 | 73 | 1 | 16 | 0 | 0 | 0 | 130.3281 | 28.3754 | 0 | 0 | 28.3754 | 0 | 0 | 0 | 0 | 0 | 130.3281 | 0 | 130.3281 | 10.22% | 0 | 12.9597 | 6.25 | 10% | 41.3351
1450 | 785 | 502 | 99 | 0.7 | 18.8 | 0 | 0 | 0 | 184.9204 | 40.7614 | 5.0528 | 0 | 40.7614 | 0 | 0 | 0 | 0 | 0 | 184.9204 | 0 | 315.2485 | 24.72% | 0 | 0 | 6.25 | 10% | 40.7614
1451 | 846 | 655 | 117 | 2.4 | 20.7 | 0 | 0 | 0 | 221.2766 | 40.4508 | 20.3443 | 0 | 40.4508 | 0 | 0 | 0 | 0 | 0 | 221.2766 | 0 | 536.5251 | 42.06% | 0 | 0 | 6.25 | 10% | 40.4508
1452 | 709 | 697 | 189 | 5.1 | 20.7 | 0 | 0 | 0 | 188.7847 | 48.4616 | 17.8857 | 9.2378 | 39.2238 | 0 | 0 | 0 | 0 | 0 | 188.7847 | 0 | 725.3098 | 56.86% | 9.2378 | 0 | 14.5969 | 23.36% | 39.2238
1453 | 682 | 722 | 217 | 5.1 | 21 | 0 | 0 | 0 | 184.6358 | 62.5972 | 6.7101 | 25 | 37.5972 | 0 | 0 | 0 | 0 | 0 | 184.6358 | 0 | 909.9456 | 71.34% | 25 | 0 | 37.1859 | 59.5% | 37.5972
1454 | 304 | 532 | 307 | 3.8 | 20.8 | 0 | 0 | 0 | 71.9834 | 47.4007 | 0 | 10.9595 | 36.4412 | 0 | 0 | 0 | 0 | 0 | 71.9834 | 0 | 981.9291 | 76.98% | 10.9595 | 0 | 47.0884 | 75.34% | 36.4412
1455 | 322 | 491 | 289 | 3.3 | 20.8 | 0 | 0 | 0 | 75.3657 | 45.3332 | 0 | 9.6065 | 35.7268 | 0 | 0 | 0 | 0 | 0 | 75.3657 | 0 | 1057.2948 | 82.89% | 9.6065 | 0 | 55.7685 | 89.23% | 35.7268
1456 | 298 | 373 | 227 | 4.7 | 19.1 | 0 | 0 | 0 | 62.8068 | 36.353 | 0 | 0.53294 | 35.8201 | 0 | 0 | 0 | 0 | 0 | 62.8068 | 0 | 1120.1016 | 87.82% | 0.53294 | 0 | 56.25 | 90% | 35.8201
1457 | 326 | 225 | 117 | 3.6 | 18.3 | 0 | 0 | 0 | 61.4318 | 25.0882 | 0 | 0 | 25.0882 | 0 | 0 | 0 | 0 | 0 | 61.4318 | 0 | 1181.5334 | 92.63% | 0 | 14.1078 | 40.6364 | 65.02% | 39.196
1458 | 58 | 56 | 46 | 3.5 | 16.6 | 0 | 0 | 0 | 0 | 4.4877 | 0 | 0 | 4.4877 | 0 | 0 | 0 | 91.2031 | 35.8885 | 0 | 91.2031 | 1090.3304 | 85.48% | 0 | 0.90183 | 39.6383 | 63.42% | 41.278
1459 | 0 | 0 | 0 | 2.2 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.6663 | 40.9368 | 0 | 102.6663 | 987.6641 | 77.43% | 0 | 0 | 39.6383 | 63.42% | 40.9368
1460 | 0 | 0 | 0 | 0.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4715 | 39.182 | 0 | 98.4715 | 889.1925 | 69.71% | 0 | 0 | 39.6383 | 63.42% | 39.182
1461 | 0 | 0 | 0 | 0.5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2728 | 36.9635 | 0 | 93.2728 | 795.9198 | 62.4% | 0 | 0 | 39.6383 | 63.42% | 36.9635
1462 | 0 | 0 | 0 | 0.5 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4158 | 34.4218 | 0 | 87.4158 | 708.504 | 55.55% | 0 | 0 | 39.6383 | 63.42% | 34.4218
1463 | 0 | 0 | 0 | 0.4 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0753 | 32.1211 | 0 | 82.0753 | 626.4287 | 49.11% | 0 | 0 | 39.6383 | 63.42% | 32.1211
1464 | 0 | 0 | 0 | 0.5 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1854 | 30.4262 | 0 | 78.1854 | 548.2433 | 42.98% | 0 | 0 | 39.6383 | 63.42% | 30.4262
1465 | 0 | 0 | 0 | 0.8 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.215 | 29.5655 | 0 | 76.215 | 472.0283 | 37.01% | 0 | 0 | 39.6383 | 63.42% | 29.5655
1466 | 0 | 0 | 0 | 1.3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3944 | 29.202 | 0 | 75.3944 | 396.6339 | 31.1% | 0 | 0 | 39.6383 | 63.42% | 29.202
1467 | 0 | 0 | 0 | 0.7 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4275 | 29.2257 | 0 | 75.4275 | 321.2064 | 25.18% | 0 | 0 | 39.6383 | 63.42% | 29.2257
1468 | 0 | 0 | 0 | 0.5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7606 | 29.8064 | 0 | 76.7606 | 244.4458 | 19.16% | 0 | 0 | 39.6383 | 63.42% | 29.8064
1469 | 0 | 0 | 0 | 1.1 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4843 | 30.124 | 0 | 77.4843 | 166.9615 | 13.09% | 0 | 0 | 39.6383 | 63.42% | 30.124
1470 | 0 | 0 | 0 | 0.5 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1752 | 31.305 | 0 | 80.1752 | 86.7864 | 6.804% | 0 | 0 | 39.6383 | 63.42% | 31.305
1471 | 40 | 5 | 4 | 0.4 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7864 | 34.1892 | 0 | 86.7864 | 0 | 0% | 0 | 0 | 39.6383 | 63.42% | 34.1892
1472 | 560 | 129 | 33 | 1 | 11.3 | 0 | 0 | 0 | 0 | 5.0868 | 0 | 0 | 5.0868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 11.97 | 19.15% | 30.0868
1473 | 812 | 339 | 51 | 0.9 | 16.4 | 0 | 0 | 0 | 0 | 29.8381 | 0 | 0 | 29.8381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 5.1684 | 6.25 | 10% | 35.0065
1474 | 917 | 534 | 60 | 0.6 | 20.7 | 0 | 0 | 0 | 219.324 | 36.3298 | 11.374 | 0 | 36.3298 | 0 | 0 | 0 | 0 | 0 | 219.324 | 0 | 219.324 | 17.2% | 0 | 0 | 6.25 | 10% | 36.3298
1475 | 962 | 682 | 66 | 1.2 | 22.1 | 0 | 0 | 0 | 114.497 | 36.3897 | 24.6467 | 0 | 36.3897 | 0 | 0 | 0 | 0 | 0 | 114.497 | 0 | 333.821 | 26.17% | 0 | 0 | 6.25 | 10% | 36.3897
1476 | 979 | 771 | 71 | 1.5 | 22.8 | 0 | 0 | 0 | 0 | 36.0554 | 33.4285 | 0 | 36.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.821 | 26.17% | 0 | 0 | 6.25 | 10% | 36.0554
1477 | 986 | 798 | 73 | 4 | 23.2 | 0 | 0 | 0 | 0 | 34.4761 | 37.5239 | 0 | 34.4761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.821 | 26.17% | 0 | 0 | 6.25 | 10% | 34.4761
1478 | 982 | 757 | 69 | 4.1 | 23.5 | 0 | 0 | 0 | 275.0637 | 58.355 | 13.645 | 25 | 33.355 | 0 | 0 | 0 | 0 | 0 | 275.0637 | 0 | 608.8847 | 47.74% | 25 | 0 | 28.839 | 46.14% | 33.355
1479 | 954 | 651 | 66 | 4.7 | 23.7 | 0 | 0 | 0 | 259.0207 | 57.8536 | 11.194 | 25 | 32.8536 | 0 | 0 | 0 | 0 | 0 | 259.0207 | 0 | 867.9054 | 68.04% | 25 | 0 | 51.428 | 82.28% | 32.8536
1480 | 902 | 491 | 57 | 5.2 | 23.2 | 0 | 0 | 0 | 229.585 | 36.8713 | 20.278 | 3.1904 | 33.6809 | 0 | 0 | 0 | 0 | 0 | 229.585 | 0 | 1097.4903 | 86.04% | 3.1904 | 0 | 54.3107 | 86.9% | 33.6809
1481 | 805 | 295 | 44 | 5.2 | 21.8 | 0 | 0 | 0 | 178.0199 | 39.9649 | 0 | 2.1463 | 37.8186 | 0 | 0 | 0 | 0 | 0 | 178.0199 | 0 | 1275.5102 | 100% | 2.1463 | 0 | 56.25 | 90% | 37.8186
1482 | 417 | 86 | 23 | 4 | 19.5 | 0 | 0 | 0 | 0 | 12.5 | 0 | 0 | 12.5 | 0 | 0 | 0 | 38.2653 | 12.8762 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 15.4116 | 39.1935 | 62.71% | 40.7878
1483 | 0 | 1 | 0 | 3.4 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.1302 | 26.7359 | 0 | 70.1302 | 1167.1147 | 91.5% | 0 | 14.1536 | 23.5292 | 37.65% | 40.8895
1484 | 0 | 0 | 0 | 3.5 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9307 | 39.2642 | 0 | 98.9307 | 1068.184 | 83.75% | 0 | 0 | 23.5292 | 37.65% | 39.2642
1485 | 0 | 0 | 0 | 2.1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.482 | 36.1139 | 0 | 91.482 | 976.702 | 76.57% | 0 | 0 | 23.5292 | 37.65% | 36.1139
1486 | 0 | 0 | 0 | 0.8 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0448 | 33.3759 | 0 | 85.0448 | 891.6572 | 69.91% | 0 | 0 | 23.5292 | 37.65% | 33.3759
1487 | 0 | 0 | 0 | 0.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0881 | 31.2395 | 0 | 80.0881 | 811.5691 | 63.63% | 0 | 0 | 23.5292 | 37.65% | 31.2395
1488 | 0 | 0 | 0 | 1.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7569 | 30.2215 | 0 | 77.7569 | 733.8122 | 57.53% | 0 | 0 | 23.5292 | 37.65% | 30.2215
1489 | 0 | 0 | 0 | 0.8 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.0258 | 25.1234 | 0 | 66.0258 | 667.7864 | 52.35% | 0 | 0 | 23.5292 | 37.65% | 25.1234
1490 | 0 | 0 | 0 | 0.8 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9714 | 29.9025 | 0 | 76.9714 | 590.815 | 46.32% | 0 | 0 | 23.5292 | 37.65% | 29.9025
1491 | 0 | 0 | 0 | 1.7 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7301 | 31.103 | 0 | 79.7301 | 511.0849 | 40.07% | 0 | 0 | 23.5292 | 37.65% | 31.103
1492 | 0 | 0 | 0 | 2.3 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3314 | 35.2867 | 0 | 89.3314 | 421.7535 | 33.07% | 0 | 0 | 23.5292 | 37.65% | 35.2867
1493 | 0 | 0 | 0 | 2.1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.9376 | 39.9076 | 0 | 99.9376 | 321.8159 | 25.23% | 0 | 0 | 23.5292 | 37.65% | 39.9076
1494 | 0 | 0 | 0 | 2.2 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.5836 | 42.81 | 0 | 106.5836 | 215.2323 | 16.87% | 0 | 0 | 23.5292 | 37.65% | 42.81
1495 | 18 | 4 | 3 | 2.3 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.3236 | 45.3085 | 0 | 112.3236 | 102.9087 | 8.068% | 0 | 0 | 23.5292 | 37.65% | 45.3085
1496 | 460 | 123 | 34 | 2.1 | 11.1 | 0 | 0 | 0 | 0 | 4.7755 | 0 | 0 | 4.7755 | 0 | 0 | 0 | 102.9087 | 41.1751 | 0 | 102.9087 | 0 | 0% | 0 | 0 | 23.5292 | 37.65% | 45.9505
1497 | 807 | 343 | 55 | 1.3 | 16.3 | 0 | 0 | 0 | 0 | 30.2374 | 0 | 0 | 30.2374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 15.6128 | 6.25 | 10% | 45.8503
1498 | 901 | 536 | 68 | 1.1 | 18.9 | 0 | 0 | 0 | 0 | 45.6024 | 2.9646 | 0 | 45.6024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 45.6024
1499 | 957 | 696 | 80 | 1.7 | 20.7 | 0 | 0 | 0 | 254.0532 | 45.4673 | 17.425 | 0 | 45.4673 | 0 | 0 | 0 | 0 | 0 | 254.0532 | 0 | 254.0532 | 19.92% | 0 | 0 | 6.25 | 10% | 45.4673
1500 | 984 | 784 | 77 | 2.2 | 21.8 | 0 | 0 | 0 | 236.5506 | 44.2751 | 27.3614 | 0 | 44.2751 | 0 | 0 | 0 | 0 | 0 | 236.5506 | 0 | 490.6038 | 38.46% | 0 | 0 | 6.25 | 10% | 44.2751
1501 | 972 | 798 | 81 | 2.7 | 22.5 | 0 | 0 | 0 | 273.6991 | 45.3709 | 26.6291 | 2.086 | 43.2849 | 0 | 0 | 0 | 0 | 0 | 273.6991 | 0 | 764.3029 | 59.92% | 2.086 | 0 | 8.1348 | 13.02% | 43.2849
1502 | 955 | 754 | 82 | 2.8 | 23.7 | 0 | 0 | 0 | 268.0294 | 67.4298 | 4.5702 | 25 | 42.4298 | 0 | 0 | 0 | 0 | 0 | 268.0294 | 0 | 1032.3323 | 80.93% | 25 | 0 | 30.7238 | 49.16% | 42.4298
1503 | 896 | 642 | 88 | 3.7 | 23.6 | 0 | 0 | 0 | 243.1779 | 66.6064 | 0 | 24.5247 | 42.0816 | 0 | 0 | 0 | 0 | 0 | 243.1779 | 0 | 1275.5102 | 100% | 24.5247 | 0 | 52.8834 | 84.61% | 42.0816
1504 | 547 | 439 | 166 | 4.5 | 23.1 | 0 | 0 | 0 | 0 | 46.0847 | 0 | 3.7259 | 42.3588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 3.7259 | 0 | 56.25 | 90% | 42.3588
1505 | 424 | 233 | 109 | 5.2 | 21 | 0 | 0 | 0 | 0 | 28.6271 | 0 | 0 | 28.6271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 16.7594 | 37.7018 | 60.32% | 45.3865
1506 | 258 | 87 | 46 | 3.3 | 18.8 | 0 | 0 | 0 | 0 | 10.3012 | 0 | 0 | 10.3012 | 0 | 0 | 0 | 77.6142 | 29.9018 | 0 | 77.6142 | 1197.896 | 93.92% | 0 | 6.9411 | 30.0199 | 48.03% | 47.1441
1507 | 1 | 1 | 1 | 1.5 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.5533 | 46.1065 | 0 | 114.5533 | 1083.3427 | 84.93% | 0 | 0 | 30.0199 | 48.03% | 46.1065
1508 | 0 | 0 | 0 | 1.9 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.5908 | 42.7195 | 0 | 106.5908 | 976.7518 | 76.58% | 0 | 0 | 30.0199 | 48.03% | 42.7195
1509 | 0 | 0 | 0 | 0.9 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3138 | 38.7085 | 0 | 97.3138 | 879.438 | 68.95% | 0 | 0 | 30.0199 | 48.03% | 38.7085
1510 | 0 | 0 | 0 | 1.3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7962 | 36.3103 | 0 | 91.7962 | 787.6418 | 61.75% | 0 | 0 | 30.0199 | 48.03% | 36.3103
1511 | 0 | 0 | 0 | 1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.789 | 34.1266 | 0 | 86.789 | 700.8528 | 54.95% | 0 | 0 | 30.0199 | 48.03% | 34.1266
1512 | 0 | 0 | 0 | 2.4 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5782 | 32.7158 | 0 | 83.5782 | 617.2746 | 48.39% | 0 | 0 | 30.0199 | 48.03% | 32.7158
1513 | 0 | 0 | 0 | 2.2 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.2746 | 48.39% | 0 | 0 | 30.0199 | 48.03% | 0
1514 | 0 | 0 | 0 | 1.3 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.2746 | 48.39% | 0 | 0 | 30.0199 | 48.03% | 0
1515 | 0 | 0 | 0 | 2.1 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.2746 | 48.39% | 0 | 0 | 30.0199 | 48.03% | 0
1516 | 0 | 0 | 0 | 1.3 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0518 | 36.4468 | 0 | 92.0518 | 525.2228 | 41.18% | 0 | 0 | 30.0199 | 48.03% | 36.4468
1517 | 0 | 0 | 0 | 1.8 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3535 | 41.3825 | 0 | 103.3535 | 421.8693 | 33.07% | 0 | 0 | 30.0199 | 48.03% | 41.3825
1518 | 0 | 0 | 0 | 2.3 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.654 | 44.1275 | 0 | 109.654 | 312.2153 | 24.48% | 0 | 0 | 30.0199 | 48.03% | 44.1275
1519 | 23 | 6 | 5 | 2.2 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3576 | 45.7375 | 0 | 113.3576 | 198.8577 | 15.59% | 0 | 0 | 30.0199 | 48.03% | 45.7375
1520 | 13 | 64 | 63 | 2.3 | 12 | 0 | 0 | 0 | 0 | 3.8222 | 0 | 0 | 3.8222 | 0 | 0 | 0 | 105.9026 | 42.4557 | 0 | 105.9026 | 92.9551 | 7.288% | 0 | 0 | 30.0199 | 48.03% | 46.2778
1521 | 1 | 137 | 135 | 1.8 | 14.2 | 0 | 0 | 0 | 0 | 9.54 | 0 | 0 | 9.54 | 0 | 0 | 0 | 92.9551 | 36.7476 | 0 | 92.9551 | 0 | 0% | 0 | 0 | 30.0199 | 48.03% | 46.2876
1522 | 21 | 258 | 242 | 1.8 | 16.1 | 0 | 0 | 0 | 0 | 18.3682 | 0 | 0 | 18.3682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 21.4775 | 6.25 | 10% | 39.8457
1523 | 204 | 519 | 376 | 1.1 | 18.2 | 0 | 0 | 0 | 40.4887 | 41.5577 | 0 | 0 | 41.5577 | 0 | 0 | 0 | 0 | 0 | 40.4887 | 0 | 40.4887 | 3.174% | 0 | 0 | 6.25 | 10% | 41.5577
1524 | 333 | 581 | 328 | 1.7 | 19.6 | 0 | 0 | 0 | 80.5983 | 48.9145 | 0 | 4.2995 | 44.6149 | 0 | 0 | 0 | 0 | 0 | 80.5983 | 0 | 121.087 | 9.493% | 4.2995 | 0 | 10.1349 | 16.22% | 44.6149
1525 | 600 | 693 | 239 | 3.4 | 20.5 | 0 | 0 | 0 | 161.6998 | 64.0289 | 0 | 20.4543 | 43.5746 | 0 | 0 | 0 | 0 | 0 | 161.6998 | 0 | 282.7868 | 22.17% | 20.4543 | 0 | 28.6165 | 45.79% | 43.5746
1526 | 574 | 649 | 235 | 2.5 | 21.3 | 0 | 0 | 0 | 154.0429 | 60.7254 | 0 | 17.96 | 42.7654 | 0 | 0 | 0 | 0 | 0 | 154.0429 | 0 | 436.8297 | 34.25% | 17.96 | 0 | 44.8444 | 71.75% | 42.7654
1527 | 432 | 525 | 247 | 3.5 | 21.3 | 0 | 0 | 0 | 107.7243 | 50.2121 | 0 | 7.8352 | 42.3769 | 0 | 0 | 0 | 0 | 0 | 107.7243 | 0 | 544.554 | 42.69% | 7.8352 | 0 | 51.924 | 83.08% | 42.3769
1528 | 269 | 344 | 206 | 4.4 | 20.6 | 0 | 0 | 0 | 55.049 | 32.5638 | 0 | 0 | 32.5638 | 0 | 0 | 0 | 0 | 0 | 55.049 | 0 | 599.603 | 47.01% | 0 | 9.8187 | 41.0574 | 65.69% | 42.3825
1529 | 241 | 212 | 134 | 3.6 | 20 | 0 | 0 | 0 | 40.7121 | 21.5529 | 0 | 0 | 21.5529 | 0 | 0 | 0 | 0 | 0 | 40.7121 | 0 | 640.3151 | 50.2% | 0 | 24.3001 | 14.1636 | 22.66% | 45.853
1530 | 94 | 73 | 55 | 2.9 | 18.8 | 0 | 0 | 0 | 0 | 6.0249 | 0 | 0 | 6.0249 | 0 | 0 | 0 | 88.1849 | 34.4717 | 0 | 88.1849 | 552.1302 | 43.29% | 0 | 7.0709 | 6.3381 | 10.14% | 47.5675
1531 | 0 | 1 | 0 | 1.8 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.465 | 46.4101 | 0 | 115.465 | 436.6652 | 34.23% | 0 | 8.0252e-16 | 6.3381 | 10.14% | 46.4101
1532 | 0 | 0 | 0 | 1 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1533 | 0 | 0 | 0 | 0.6 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1534 | 0 | 0 | 0 | 0.3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1535 | 0 | 0 | 0 | 0.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1536 | 0 | 0 | 0 | 0.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1537 | 0 | 0 | 0 | 0.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1538 | 0 | 0 | 0 | 1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1539 | 0 | 0 | 0 | 0.6 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1540 | 0 | 0 | 0 | 1.3 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1541 | 0 | 0 | 0 | 0.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.3381 | 10.14% | 0
1542 | 0 | 0 | 0 | 1.1 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0.079573 | 6.25 | 10% | 0.079573
1543 | 0 | 4 | 4 | 0.8 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.25 | 10% | 0
1544 | 109 | 91 | 65 | 3.8 | 10.2 | 0 | 0 | 0 | 0 | 5.3286 | 0 | 0 | 5.3286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436.6652 | 34.23% | 0 | 0 | 6.25 | 10% | 5.3286
1545 | 295 | 292 | 180 | 5.7 | 14.8 | 0 | 0 | 0 | 42.1974 | 24.5344 | 0 | 0 | 24.5344 | 0 | 0 | 0 | 0 | 0 | 42.1974 | 0 | 478.8626 | 37.54% | 0 | 0 | 6.25 | 10% | 24.5344
1546 | 324 | 484 | 305 | 5.9 | 17.2 | 0 | 0 | 0 | 63.3302 | 41.0429 | 0 | 0 | 41.0429 | 0 | 0 | 0 | 0 | 0 | 63.3302 | 0 | 542.1927 | 42.51% | 0 | 0 | 6.25 | 10% | 41.0429
1547 | 101 | 423 | 349 | 5.1 | 18.1 | 0 | 0 | 0 | 0 | 33.3217 | 0 | 0 | 33.3217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542.1927 | 42.51% | 0 | 0 | 6.25 | 10% | 33.3217
1548 | 294 | 615 | 387 | 5.7 | 20.2 | 0 | 0 | 0 | 66.2956 | 51.3162 | 0 | 17.1438 | 34.1724 | 0 | 0 | 0 | 0 | 0 | 66.2956 | 0 | 608.4884 | 47.71% | 17.1438 | 0 | 21.7404 | 34.78% | 34.1724
1549 | 240 | 566 | 376 | 7.1 | 22.1 | 0 | 0 | 0 | 49.9038 | 47.5145 | 0 | 2.3202 | 45.1943 | 0 | 0 | 0 | 0 | 0 | 49.9038 | 0 | 658.3922 | 51.62% | 2.3202 | 0 | 23.8369 | 38.14% | 45.1943
1550 | 313 | 595 | 358 | 8.9 | 22.4 | 0 | 0 | 0 | 70.3055 | 52.6977 | 0 | 25 | 27.6977 | 0 | 0 | 0 | 0 | 0 | 70.3055 | 0 | 728.6977 | 57.13% | 25 | 0 | 46.4259 | 74.28% | 27.6977
1551 | 9 | 300 | 290 | 10.9 | 20.3 | 0 | 0 | 0 | 0 | 20.6824 | 0 | 0 | 20.6824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728.6977 | 57.13% | 0 | 0 | 46.4259 | 74.28% | 20.6824
1552 | 541 | 538 | 274 | 11.4 | 19.6 | 0 | 0 | 0 | 124.8898 | 55.3358 | 0 | 10.8727 | 44.4631 | 0 | 0 | 0 | 0 | 0 | 124.8898 | 0 | 853.5875 | 66.92% | 10.8727 | 0 | 56.25 | 90% | 44.4631
1553 | 189 | 177 | 103 | 10.6 | 17.8 | 0 | 0 | 0 | 0 | 16.86 | 0 | 0 | 16.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 56.25 | 90% | 16.86
1554 | 9 | 38 | 37 | 11.6 | 16.2 | 0 | 0 | 0 | 0 | 2.2673 | 0 | 0 | 2.2673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 15.3174 | 39.2978 | 62.88% | 17.5847
1555 | 0 | 2 | 2 | 10.6 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1556 | 0 | 0 | 0 | 7.4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1557 | 0 | 0 | 0 | 7.5 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1558 | 0 | 0 | 0 | 8.2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1559 | 0 | 0 | 0 | 7.5 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1560 | 0 | 0 | 0 | 7.5 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1561 | 0 | 0 | 0 | 5.5 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1562 | 0 | 0 | 0 | 2.3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1563 | 0 | 0 | 0 | 1.3 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1564 | 0 | 0 | 0 | 1.9 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 853.5875 | 66.92% | 0 | 0 | 39.2978 | 62.88% | 0
1565 | 0 | 0 | 0 | 1.6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3439 | 42.2766 | 0 | 105.3439 | 748.2436 | 58.66% | 0 | 0 | 39.2978 | 62.88% | 42.2766
1566 | 0 | 0 | 0 | 2.3 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1056 | 45.2375 | 0 | 112.1056 | 636.138 | 49.87% | 0 | 0 | 39.2978 | 62.88% | 45.2375
1567 | 0 | 4 | 3 | 2.1 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.6079 | 46.7639 | 0 | 115.6079 | 520.5301 | 40.81% | 0 | 0 | 39.2978 | 62.88% | 46.7639
1568 | 35 | 79 | 70 | 1 | 8.6 | 0 | 0 | 0 | 0 | 5.4919 | 0 | 0 | 5.4919 | 0 | 0 | 0 | 103.742 | 41.5826 | 0 | 103.742 | 416.7881 | 32.68% | 0 | 0 | 39.2978 | 62.88% | 47.0744
1569 | 219 | 251 | 167 | 1.2 | 10.8 | 0 | 0 | 0 | 0 | 20.4839 | 0 | 0 | 20.4839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.7881 | 32.68% | 0 | 25 | 11.6294 | 18.61% | 45.4839
1570 | 691 | 514 | 135 | 1.3 | 13.6 | 0 | 0 | 0 | 162.3415 | 45.7136 | 0 | 0 | 45.7136 | 0 | 0 | 0 | 0 | 0 | 162.3415 | 0 | 579.1296 | 45.4% | 0 | 0.76753 | 10.78 | 17.25% | 46.4812
1571 | 951 | 718 | 91 | 1.5 | 15.3 | 0 | 0 | 0 | 253.1893 | 64.4157 | 0 | 18.2841 | 46.1316 | 0 | 0 | 0 | 0 | 0 | 253.1893 | 0 | 832.319 | 65.25% | 18.2841 | 0 | 27.3008 | 43.68% | 46.1316
1572 | 528 | 552 | 161 | 2.1 | 15.6 | 0 | 0 | 0 | 138.473 | 51.8351 | 0 | 7.0391 | 44.796 | 0 | 0 | 0 | 0 | 0 | 138.473 | 0 | 970.7919 | 76.11% | 7.0391 | 0 | 33.661 | 53.86% | 44.796
1573 | 897 | 837 | 159 | 4.1 | 16.6 | 0 | 0 | 0 | 250.4284 | 68.9228 | 3.0772 | 25 | 43.9228 | 0 | 0 | 0 | 0 | 0 | 250.4284 | 0 | 1221.2203 | 95.74% | 25 | 0 | 56.25 | 90% | 43.9228
1574 | 245 | 373 | 190 | 3.7 | 16.2 | 0 | 0 | 0 | 54.2899 | 34.1084 | 0 | 0 | 34.1084 | 0 | 0 | 0 | 0 | 0 | 54.2899 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 34.1084
1575 | 29 | 119 | 99 | 2.6 | 15.2 | 0 | 0 | 0 | 0 | 8.4673 | 0 | 0 | 8.4673 | 0 | 0 | 0 | 87.2405 | 34.2271 | 0 | 87.2405 | 1188.2697 | 93.16% | 0 | 0 | 56.25 | 90% | 42.6944
1576 | 111 | 230 | 165 | 4.1 | 15.4 | 0 | 0 | 0 | 0 | 19.1774 | 0 | 0 | 19.1774 | 0 | 0 | 0 | 62.8155 | 23.6118 | 0 | 62.8155 | 1125.4542 | 88.24% | 0 | 0 | 56.25 | 90% | 42.7891
1577 | 441 | 258 | 125 | 2.9 | 15.8 | 0 | 0 | 0 | 91.6818 | 30.7958 | 0 | 0 | 30.7958 | 0 | 0 | 0 | 0 | 0 | 91.6818 | 0 | 1217.1361 | 95.42% | 0 | 15.2773 | 39.3421 | 62.95% | 46.0731
1578 | 288 | 107 | 58 | 1.2 | 15.6 | 0 | 0 | 0 | 39.1672 | 12.0339 | 0 | 0 | 12.0339 | 0 | 0 | 0 | 0 | 0 | 39.1672 | 0 | 1256.3032 | 98.49% | 0 | 25 | 11.6738 | 18.68% | 37.0339
1579 | 0 | 1 | 1 | 1.3 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.1698 | 46.885 | 0 | 116.1698 | 1140.1334 | 89.39% | 0 | 0 | 11.6738 | 18.68% | 46.885
1580 | 0 | 0 | 0 | 1.2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7832 | 43.7194 | 0 | 108.7832 | 1031.3503 | 80.86% | 0 | 0 | 11.6738 | 18.68% | 43.7194
1581 | 0 | 0 | 0 | 1.3 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1827 | 39.5678 | 0 | 99.1827 | 932.1676 | 73.08% | 0 | 0 | 11.6738 | 18.68% | 39.5678
1582 | 0 | 0 | 0 | 0.8 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.751 | 37.2239 | 0 | 93.751 | 838.4165 | 65.73% | 0 | 0 | 11.6738 | 18.68% | 37.2239
1583 | 0 | 0 | 0 | 1.7 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3011 | 34.8466 | 0 | 88.3011 | 750.1154 | 58.81% | 0 | 0 | 11.6738 | 18.68% | 34.8466
1584 | 0 | 0 | 0 | 1.2 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0734 | 33.4428 | 0 | 85.0734 | 665.0421 | 52.14% | 0 | 0 | 11.6738 | 18.68% | 33.4428
1585 | 0 | 0 | 0 | 2.1 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3953 | 28.345 | 0 | 73.3953 | 591.6467 | 46.39% | 0 | 0 | 11.6738 | 18.68% | 28.345
1586 | 0 | 0 | 0 | 2 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4868 | 32.7534 | 0 | 83.4868 | 508.1599 | 39.84% | 0 | 0 | 11.6738 | 18.68% | 32.7534
1587 | 0 | 0 | 0 | 2.3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1349 | 33.472 | 0 | 85.1349 | 423.025 | 33.17% | 0 | 0 | 11.6738 | 18.68% | 33.472
1588 | 0 | 0 | 0 | 2.6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1847 | 36.9858 | 0 | 93.1847 | 329.8403 | 25.86% | 0 | 0 | 11.6738 | 18.68% | 36.9858
1589 | 0 | 0 | 0 | 1.3 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1463 | 41.7669 | 0 | 104.1463 | 225.6941 | 17.69% | 0 | 0 | 11.6738 | 18.68% | 41.7669
1590 | 0 | 0 | 0 | 2.4 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.8522 | 44.6943 | 0 | 110.8522 | 114.8418 | 9.004% | 0 | 0 | 11.6738 | 18.68% | 44.6943
1591 | 58 | 10 | 7 | 1.1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.8418 | 46.4324 | 0 | 114.8418 | 0 | 0% | 0 | 0 | 11.6738 | 18.68% | 46.4324
1592 | 531 | 147 | 43 | 1.4 | 7.8 | 0 | 0 | 0 | 62.1589 | 7.4589 | 0 | 0 | 7.4589 | 0 | 0 | 0 | 0 | 0 | 62.1589 | 0 | 62.1589 | 4.873% | 0 | 4.9007 | 6.25 | 10% | 12.3596
1593 | 769 | 358 | 66 | 1.3 | 11.2 | 0 | 0 | 0 | 149.3877 | 30.7459 | 0 | 0 | 30.7459 | 0 | 0 | 0 | 0 | 0 | 149.3877 | 0 | 211.5465 | 16.59% | 0 | 0 | 6.25 | 10% | 30.7459
1594 | 885 | 554 | 75 | 1 | 14.2 | 0 | 0 | 0 | 213.3883 | 46.1037 | 3.4732 | 0 | 46.1037 | 0 | 0 | 0 | 0 | 0 | 213.3883 | 0 | 424.9349 | 33.31% | 0 | 0 | 6.25 | 10% | 46.1037
1595 | 935 | 704 | 82 | 2.6 | 15.7 | 0 | 0 | 0 | 248.319 | 45.6455 | 18.4442 | 0 | 45.6455 | 0 | 0 | 0 | 0 | 0 | 248.319 | 0 | 673.2539 | 52.78% | 0 | 0 | 6.25 | 10% | 45.6455
1596 | 950 | 794 | 91 | 3.2 | 16.4 | 0 | 0 | 0 | 263.0846 | 54.6593 | 17.3407 | 10.671 | 43.9882 | 0 | 0 | 0 | 0 | 0 | 263.0846 | 0 | 936.3385 | 73.41% | 10.671 | 0 | 15.8919 | 25.43% | 43.9882
1597 | 910 | 806 | 113 | 3 | 17 | 0 | 0 | 0 | 255.2834 | 67.9145 | 4.0855 | 25 | 42.9145 | 0 | 0 | 0 | 0 | 0 | 255.2834 | 0 | 1191.6218 | 93.42% | 25 | 0 | 38.4809 | 61.57% | 42.9145
1598 | 360 | 549 | 277 | 2.8 | 17.2 | 0 | 0 | 0 | 0 | 48.9239 | 0 | 19.6656 | 29.2583 | 0 | 0 | 0 | 38.2653 | 12.9208 | 0 | 38.2653 | 1153.3565 | 90.42% | 19.6656 | 0 | 56.25 | 90% | 42.1791
1599 | 124 | 329 | 249 | 2 | 16.8 | 0 | 0 | 0 | 0 | 27.5866 | 0 | 0 | 27.5866 | 0 | 0 | 0 | 38.2653 | 12.9277 | 0 | 38.2653 | 1115.0912 | 87.42% | 0 | 1.1035 | 55.0287 | 88.05% | 41.6179
1600 | 597 | 461 | 165 | 3.4 | 17.1 | 0 | 0 | 0 | 148.0384 | 42.7021 | 6.9521 | 1.3516 | 41.3505 | 0 | 0 | 0 | 0 | 0 | 148.0384 | 0 | 1263.1296 | 99.03% | 1.3516 | 0 | 56.25 | 90% | 41.3505
1601 | 660 | 299 | 80 | 4.5 | 16.1 | 0 | 0 | 0 | 12.3806 | 37.4689 | 0 | 0 | 37.4689 | 0 | 0 | 0 | 0 | 0 | 12.3806 | 0 | 1275.5102 | 100% | 0 | 6.6809 | 48.856 | 78.17% | 44.1498
1602 | 304 | 89 | 36 | 3.9 | 14.3 | 0 | 0 | 0 | 0 | 10.9286 | 0 | 0 | 10.9286 | 0 | 0 | 0 | 38.2653 | 12.9648 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 21.8928 | 24.6266 | 39.4% | 45.7862
1603 | 1 | 1 | 1 | 1.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6904 | 37.5685 | 0 | 94.6904 | 1142.5545 | 89.58% | 0 | 7.3013 | 16.546 | 26.47% | 44.8698
1604 | 0 | 0 | 0 | 0.5 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.725 | 42.4075 | 0 | 105.725 | 1036.8296 | 81.29% | 0 | 0 | 16.546 | 26.47% | 42.4075
1605 | 0 | 0 | 0 | 1.2 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9847 | 39.0525 | 0 | 97.9847 | 938.8449 | 73.61% | 0 | 0 | 16.546 | 26.47% | 39.0525
1606 | 0 | 0 | 0 | 1.6 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1942 | 36.9718 | 0 | 93.1942 | 845.6507 | 66.3% | 0 | 0 | 16.546 | 26.47% | 36.9718
1607 | 0 | 0 | 0 | 2.2 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6204 | 34.5402 | 0 | 87.6204 | 758.0304 | 59.43% | 0 | 0 | 16.546 | 26.47% | 34.5402
1608 | 0 | 0 | 0 | 2.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2309 | 32.6252 | 0 | 83.2309 | 674.7995 | 52.9% | 0 | 0 | 16.546 | 26.47% | 32.6252
1609 | 0 | 0 | 0 | 2.5 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2491 | 31.7618 | 0 | 81.2491 | 593.5504 | 46.53% | 0 | 0 | 16.546 | 26.47% | 31.7618
1610 | 0 | 0 | 0 | 1.7 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5538 | 31.4707 | 0 | 80.5538 | 512.9966 | 40.22% | 0 | 0 | 16.546 | 26.47% | 31.4707
1611 | 0 | 0 | 0 | 1.8 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5179 | 31.4568 | 0 | 80.5179 | 432.4787 | 33.91% | 0 | 0 | 16.546 | 26.47% | 31.4568
1612 | 0 | 0 | 0 | 1.4 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9195 | 32.5055 | 0 | 82.9195 | 349.5592 | 27.41% | 0 | 0 | 16.546 | 26.47% | 32.5055
1613 | 0 | 0 | 0 | 0.7 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1035 | 33.4553 | 0 | 85.1035 | 264.4557 | 20.73% | 0 | 0 | 16.546 | 26.47% | 33.4553
1614 | 0 | 0 | 0 | 0.6 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8644 | 32.0376 | 0 | 81.8644 | 182.5913 | 14.32% | 0 | 0 | 16.546 | 26.47% | 32.0376
1615 | 89 | 12 | 7 | 0.5 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5558 | 39.3241 | 0 | 98.5558 | 84.0356 | 6.588% | 0 | 0 | 16.546 | 26.47% | 39.3241
1616 | 618 | 160 | 37 | 0.7 | 9.5 | 0 | 0 | 0 | 0 | 7.9282 | 0 | 0 | 7.9282 | 0 | 0 | 0 | 84.0356 | 32.9738 | 0 | 84.0356 | 0 | 0% | 0 | 0 | 16.546 | 26.47% | 40.902
1617 | 839 | 375 | 53 | 0.9 | 14.4 | 0 | 0 | 0 | 0 | 31.4987 | 0 | 0 | 31.4987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 9.303 | 6.25 | 10% | 40.8017
1618 | 934 | 572 | 60 | 4 | 16.8 | 0 | 0 | 0 | 224.8251 | 40.3993 | 11.3518 | 0 | 40.3993 | 0 | 0 | 0 | 0 | 0 | 224.8251 | 0 | 224.8251 | 17.63% | 0 | 0 | 6.25 | 10% | 40.3993
1619 | 979 | 722 | 65 | 5.1 | 17.7 | 0 | 0 | 0 | 0 | 40.0901 | 26.321 | 0 | 40.0901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224.8251 | 17.63% | 0 | 0 | 6.25 | 10% | 40.0901
1620 | 999 | 811 | 67 | 4.7 | 19 | 0 | 0 | 0 | 276.6015 | 39.1584 | 32.8416 | 0 | 39.1584 | 0 | 0 | 0 | 0 | 0 | 276.6015 | 0 | 501.4266 | 39.31% | 0 | 0 | 6.25 | 10% | 39.1584
1621 | 999 | 834 | 70 | 5.8 | 19.4 | 0 | 0 | 0 | 279.6554 | 37.3813 | 34.6187 | 0 | 37.3813 | 0 | 0 | 0 | 0 | 0 | 279.6554 | 0 | 781.0819 | 61.24% | 0 | 0 | 6.25 | 10% | 37.3813
1622 | 985 | 788 | 71 | 5.5 | 19.4 | 0 | 0 | 0 | 275.079 | 43.6591 | 28.3409 | 7.5145 | 36.1446 | 0 | 0 | 0 | 0 | 0 | 275.079 | 0 | 1056.1609 | 82.8% | 7.5145 | 0 | 13.0398 | 20.86% | 36.1446
1623 | 957 | 679 | 67 | 4.7 | 19.4 | 0 | 0 | 0 | 0 | 60.5624 | 9.673 | 25 | 35.5624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056.1609 | 82.8% | 25 | 0 | 35.6288 | 57.01% | 35.5624
1624 | 894 | 513 | 62 | 4.6 | 19.4 | 0 | 0 | 0 | 73.3293 | 57.4457 | 0 | 21.8527 | 35.5931 | 0 | 0 | 0 | 0 | 0 | 73.3293 | 0 | 1129.4902 | 88.55% | 21.8527 | 0 | 55.374 | 88.6% | 35.5931
1625 | 777 | 313 | 53 | 4.2 | 18.6 | 0 | 0 | 0 | 0 | 39.5207 | 0 | 0.9695 | 38.5512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1129.4902 | 88.55% | 0.9695 | 0 | 56.25 | 90% | 38.5512
1626 | 437 | 100 | 29 | 4.1 | 16.9 | 0 | 0 | 0 | 0 | 13.4819 | 0 | 0 | 13.4819 | 0 | 0 | 0 | 71.3887 | 27.285 | 0 | 71.3887 | 1058.1014 | 82.96% | 0 | 0 | 56.25 | 90% | 40.7669
1627 | 1 | 1 | 1 | 3.2 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.7822 | 17.541 | 0 | 48.7822 | 1009.3193 | 79.13% | 0 | 23.2092 | 30.5636 | 48.9% | 40.7502
1628 | 0 | 0 | 0 | 2.2 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2573 | 39.1277 | 0 | 98.2573 | 911.062 | 71.43% | 0 | 0 | 30.5636 | 48.9% | 39.1277
1629 | 0 | 0 | 0 | 1.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3374 | 36.5791 | 0 | 92.3374 | 818.7246 | 64.19% | 0 | 0 | 30.5636 | 48.9% | 36.5791
1630 | 0 | 0 | 0 | 1.2 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2758 | 33.9511 | 0 | 86.2758 | 732.4488 | 57.42% | 0 | 0 | 30.5636 | 48.9% | 33.9511
1631 | 0 | 0 | 0 | 0.3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1012 | 31.7075 | 0 | 81.1012 | 651.3476 | 51.07% | 0 | 0 | 30.5636 | 48.9% | 31.7075
1632 | 0 | 0 | 0 | 1.3 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1237 | 29.9722 | 0 | 77.1237 | 574.224 | 45.02% | 0 | 0 | 30.5636 | 48.9% | 29.9722
1633 | 0 | 0 | 0 | 1.1 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1045 | 29.0892 | 0 | 75.1045 | 499.1195 | 39.13% | 0 | 0 | 30.5636 | 48.9% | 29.0892
1634 | 0 | 0 | 0 | 1.2 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9843 | 28.6004 | 0 | 73.9843 | 425.1352 | 33.33% | 0 | 0 | 30.5636 | 48.9% | 28.6004
1635 | 0 | 0 | 0 | 0.5 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2421 | 28.7173 | 0 | 74.2421 | 350.893 | 27.51% | 0 | 0 | 30.5636 | 48.9% | 28.7173
1636 | 0 | 0 | 0 | 1.8 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.9693 | 29.4666 | 0 | 75.9693 | 274.9237 | 21.55% | 0 | 0 | 30.5636 | 48.9% | 29.4666
1637 | 0 | 0 | 0 | 1.2 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 13.0122 | 0 | 38.2653 | 236.6584 | 18.55% | 0 | 16.7482 | 12.0277 | 19.24% | 29.7605
1638 | 0 | 0 | 0 | 1.4 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3889 | 30.9596 | 0 | 79.3889 | 157.2695 | 12.33% | 0 | 0 | 12.0277 | 19.24% | 30.9596
1639 | 104 | 14 | 7 | 0.6 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0064 | 33.8494 | 0 | 86.0064 | 71.2631 | 5.587% | 0 | 0 | 12.0277 | 19.24% | 33.8494
1640 | 637 | 165 | 35 | 0.7 | 10.5 | 0 | 0 | 0 | 0 | 8.2241 | 0 | 0 | 8.2241 | 0 | 0 | 0 | 71.2631 | 27.3899 | 0 | 71.2631 | 0 | 0% | 0 | 0 | 12.0277 | 19.24% | 35.614
1641 | 842 | 378 | 50 | 0.8 | 16.1 | 0 | 0 | 0 | 167.3778 | 31.055 | 0 | 0 | 31.055 | 0 | 0 | 0 | 0 | 0 | 167.3778 | 0 | 167.3778 | 13.12% | 0 | 5.2205 | 6.25 | 10% | 36.2755
1642 | 926 | 571 | 58 | 0.9 | 19.2 | 0 | 0 | 0 | 225.2071 | 35.7379 | 13.1433 | 0 | 35.7379 | 0 | 0 | 0 | 0 | 0 | 225.2071 | 0 | 392.5849 | 30.78% | 0 | 0 | 6.25 | 10% | 35.7379
1643 | 971 | 720 | 63 | 2.7 | 20.7 | 0 | 0 | 0 | 259.0217 | 36.0638 | 27.6022 | 0 | 36.0638 | 0 | 0 | 0 | 0 | 0 | 259.0217 | 0 | 651.6067 | 51.09% | 0 | 0 | 6.25 | 10% | 36.0638
1644 | 984 | 806 | 68 | 4.2 | 20.6 | 0 | 0 | 0 | 272.9484 | 35.6933 | 36.3067 | 0 | 35.6933 | 0 | 0 | 0 | 0 | 0 | 272.9484 | 0 | 924.5551 | 72.49% | 0 | 0 | 6.25 | 10% | 35.6933
1645 | 978 | 826 | 74 | 4.3 | 21.1 | 0 | 0 | 0 | 0 | 34.089 | 37.911 | 0 | 34.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 924.5551 | 72.49% | 0 | 0 | 6.25 | 10% | 34.089
1646 | 965 | 781 | 74 | 4.6 | 21.6 | 0 | 0 | 0 | 0 | 38.1579 | 33.8421 | 5.0731 | 33.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 924.5551 | 72.49% | 5.0731 | 0 | 10.8338 | 17.33% | 33.0848
1647 | 937 | 674 | 70 | 5.9 | 21 | 0 | 0 | 0 | 166.9522 | 57.6782 | 11.7082 | 25 | 32.6782 | 0 | 0 | 0 | 0 | 0 | 166.9522 | 0 | 1091.5073 | 85.57% | 25 | 0 | 33.4228 | 53.48% | 32.6782
1648 | 881 | 512 | 63 | 5.6 | 21.4 | 0 | 0 | 0 | 0 | 56.7056 | 0 | 23.625 | 33.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091.5073 | 85.57% | 23.625 | 0 | 54.7694 | 87.63% | 33.0807
1649 | 767 | 311 | 51 | 4.5 | 21.5 | 0 | 0 | 0 | 173.441 | 38.5227 | 0 | 1.6386 | 36.8841 | 0 | 0 | 0 | 0 | 0 | 173.441 | 0 | 1264.9483 | 99.17% | 1.6386 | 0 | 56.25 | 90% | 36.8841
1650 | 455 | 101 | 29 | 3.3 | 20.4 | 0 | 0 | 0 | 0 | 13.6867 | 0 | 0 | 13.6867 | 0 | 0 | 0 | 57.9617 | 21.3487 | 0 | 57.9617 | 1206.9866 | 94.63% | 0 | 5.0825 | 50.6251 | 81% | 40.1179
1651 | 2 | 2 | 1 | 2 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1431 | 40.2043 | 0 | 101.1431 | 1105.8435 | 86.7% | 0 | 0 | 50.6251 | 81% | 40.2043
1652 | 0 | 0 | 0 | 1 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.7629 | 13.625 | 0 | 39.7629 | 1066.0806 | 83.58% | 0 | 25 | 22.9567 | 36.73% | 38.625
1653 | 0 | 0 | 0 | 0.4 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1988 | 35.6014 | 0 | 90.1988 | 975.8819 | 76.51% | 0 | 0 | 22.9567 | 36.73% | 35.6014
1654 | 0 | 0 | 0 | 0.6 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1482 | 32.9762 | 0 | 84.1482 | 891.7336 | 69.91% | 0 | 0 | 22.9567 | 36.73% | 32.9762
1655 | 0 | 0 | 0 | 0.2 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8277 | 31.1086 | 0 | 79.8277 | 811.906 | 63.65% | 0 | 0 | 22.9567 | 36.73% | 31.1086
1656 | 0 | 0 | 0 | 0.7 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.278 | 29.9917 | 0 | 77.278 | 734.6279 | 57.59% | 0 | 0 | 22.9567 | 36.73% | 29.9917
1657 | 0 | 0 | 0 | 0.8 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.8406 | 29.3691 | 0 | 75.8406 | 658.7873 | 51.65% | 0 | 0 | 22.9567 | 36.73% | 29.3691
1658 | 0 | 0 | 0 | 2.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2158 | 29.5028 | 0 | 76.2158 | 582.5715 | 45.67% | 0 | 0 | 22.9567 | 36.73% | 29.5028
1659 | 0 | 0 | 0 | 2.5 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2858 | 30.8342 | 0 | 79.2858 | 503.2857 | 39.46% | 0 | 0 | 22.9567 | 36.73% | 30.8342
1660 | 0 | 0 | 0 | 1.6 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9358 | 35.0666 | 0 | 88.9358 | 414.3499 | 32.49% | 0 | 0 | 22.9567 | 36.73% | 35.0666
1661 | 0 | 0 | 0 | 1.1 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6907 | 40.1959 | 0 | 100.6907 | 313.6592 | 24.59% | 0 | 0 | 22.9567 | 36.73% | 40.1959
1662 | 0 | 0 | 0 | 1.8 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.8978 | 43.3337 | 0 | 107.8978 | 205.7614 | 16.13% | 0 | 0 | 22.9567 | 36.73% | 43.3337
1663 | 110 | 15 | 7 | 0.6 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.8954 | 45.1024 | 0 | 111.8954 | 93.866 | 7.359% | 0 | 0 | 22.9567 | 36.73% | 45.1024
1664 | 619 | 165 | 37 | 0.7 | 14.9 | 0 | 0 | 0 | 0 | 8.2122 | 0 | 0 | 8.2122 | 0 | 0 | 0 | 93.866 | 37.1172 | 0 | 93.866 | 0 | 0% | 0 | 0 | 22.9567 | 36.73% | 45.3294
1665 | 821 | 376 | 52 | 0.6 | 19.8 | 0 | 0 | 0 | 163.7485 | 30.2951 | 0 | 0 | 30.2951 | 0 | 0 | 0 | 0 | 0 | 163.7485 | 0 | 163.7485 | 12.84% | 0 | 15.0955 | 6.25 | 10% | 45.3907
1666 | 909 | 566 | 61 | 0.8 | 22.3 | 0 | 0 | 0 | 221.3515 | 45.3071 | 2.4581 | 0 | 45.3071 | 0 | 0 | 0 | 0 | 0 | 221.3515 | 0 | 385.1 | 30.19% | 0 | 0 | 6.25 | 10% | 45.3071
1667 | 941 | 709 | 70 | 2.4 | 24 | 0 | 0 | 0 | 0 | 44.8977 | 16.6965 | 0 | 44.8977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385.1 | 30.19% | 0 | 0 | 6.25 | 10% | 44.8977
1668 | 940 | 794 | 86 | 6.8 | 23.2 | 0 | 0 | 0 | 0 | 43.5732 | 28.4268 | 0 | 43.5732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385.1 | 30.19% | 0 | 0 | 6.25 | 10% | 43.5732
1669 | 918 | 818 | 108 | 7.2 | 22 | 0 | 0 | 0 | 234.0383 | 42.6666 | 29.3334 | 0 | 42.6666 | 0 | 0 | 0 | 0 | 0 | 234.0383 | 0 | 619.1383 | 48.54% | 0 | 0 | 6.25 | 10% | 42.6666
1670 | 885 | 776 | 123 | 7.2 | 20.8 | 0 | 0 | 0 | 243.8331 | 53.5967 | 18.4033 | 11.7435 | 41.8532 | 0 | 0 | 0 | 0 | 0 | 243.8331 | 0 | 862.9714 | 67.66% | 11.7435 | 0 | 16.8609 | 26.98% | 41.8532
1671 | 827 | 667 | 130 | 7.5 | 19.9 | 0 | 0 | 0 | 220.5701 | 66.1847 | 2.2236 | 25 | 41.1847 | 0 | 0 | 0 | 0 | 0 | 220.5701 | 0 | 1083.5415 | 84.95% | 25 | 0 | 39.4499 | 63.12% | 41.1847
1672 | 763 | 492 | 101 | 7.2 | 18.6 | 0 | 0 | 0 | 191.9687 | 54.4602 | 0 | 13.5498 | 40.9104 | 0 | 0 | 0 | 0 | 0 | 191.9687 | 0 | 1275.5102 | 100% | 13.5498 | 0 | 51.693 | 82.71% | 40.9104
1673 | 642 | 296 | 76 | 6.9 | 17.5 | 0 | 0 | 0 | 0 | 36.2317 | 0 | 0 | 36.2317 | 0 | 0 | 0 | 38.2653 | 12.9155 | 0 | 38.2653 | 1237.2449 | 97% | 5.0434 | 0 | 56.25 | 90% | 44.1038
1674 | 330 | 95 | 40 | 5.9 | 15.9 | 0 | 0 | 0 | 0 | 11.7868 | 0 | 0 | 11.7868 | 0 | 0 | 0 | 88.5761 | 34.7793 | 0 | 88.5761 | 1148.6688 | 90.06% | 0 | 0 | 56.25 | 90% | 46.5661
1675 | 0 | 2 | 2 | 5 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7376 | 45.3754 | 0 | 112.7376 | 1035.9312 | 81.22% | 0 | 0 | 56.25 | 90% | 45.3754
1676 | 0 | 0 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9769 | 42.0524 | 0 | 104.9769 | 930.9543 | 72.99% | 0 | 0 | 56.25 | 90% | 42.0524
1677 | 0 | 0 | 0 | 3.7 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3713 | 38.3186 | 0 | 96.3713 | 834.5829 | 65.43% | 0 | 0 | 56.25 | 90% | 38.3186
1678 | 0 | 0 | 0 | 3.2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3847 | 36.1599 | 0 | 91.3847 | 743.1983 | 58.27% | 0 | 0 | 56.25 | 90% | 36.1599
1679 | 0 | 0 | 0 | 3.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2803 | 33.9413 | 0 | 86.2803 | 656.918 | 51.5% | 0 | 0 | 56.25 | 90% | 33.9413
1680 | 0 | 0 | 0 | 2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2505 | 32.6169 | 0 | 83.2505 | 573.6674 | 44.98% | 0 | 0 | 56.25 | 90% | 32.6169
1681 | 0 | 0 | 0 | 1.6 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.286 | 32.213 | 0 | 82.286 | 491.3815 | 38.52% | 0 | 0 | 56.25 | 90% | 32.213
1682 | 0 | 0 | 0 | 1.6 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.056 | 32.1197 | 0 | 82.056 | 409.3255 | 32.09% | 0 | 0 | 56.25 | 90% | 32.1197
1683 | 0 | 0 | 0 | 2 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9992 | 32.9734 | 0 | 83.9992 | 325.3263 | 25.51% | 0 | 0 | 56.25 | 90% | 32.9734
1684 | 0 | 0 | 0 | 1.9 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2647 | 36.5819 | 0 | 92.2647 | 233.0616 | 18.27% | 0 | 0 | 56.25 | 90% | 36.5819
1685 | 0 | 0 | 0 | 1.3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3405 | 41.4131 | 0 | 103.3405 | 129.7211 | 10.17% | 0 | 0 | 56.25 | 90% | 41.4131
1686 | 0 | 0 | 0 | 1.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.8985 | 44.2723 | 0 | 109.8985 | 19.8226 | 1.554% | 0 | 0 | 56.25 | 90% | 44.2723
1687 | 92 | 16 | 9 | 0.3 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.8226 | 1.554% | 0 | 25 | 28.5817 | 45.73% | 25
1688 | 590 | 170 | 43 | 0.2 | 10.6 | 0 | 0 | 0 | 60.1923 | 8.7129 | 0 | 0 | 8.7129 | 0 | 0 | 0 | 0 | 0 | 60.1923 | 0 | 80.0149 | 6.273% | 0 | 20.178 | 6.25 | 10% | 28.8909
1689 | 818 | 385 | 58 | 0.5 | 15.1 | 0 | 0 | 0 | 0 | 31.1987 | 0 | 0 | 31.1987 | 0 | 0 | 0 | 41.7496 | 14.4678 | 0 | 41.7496 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 45.6664
1690 | 920 | 582 | 66 | 2 | 17.6 | 0 | 0 | 0 | 0 | 32.4714 | 18.1246 | 0 | 32.4714 | 0 | 0 | 0 | 38.2653 | 12.9137 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 45.3851
1691 | 967 | 731 | 70 | 4.1 | 19.7 | 0 | 0 | 0 | 257.3647 | 45.03 | 20.253 | 0 | 45.03 | 0 | 0 | 0 | 0 | 0 | 257.3647 | 0 | 257.3647 | 20.18% | 0 | 0 | 6.25 | 10% | 45.03
1692 | 985 | 819 | 74 | 4.5 | 20.6 | 0 | 0 | 0 | 273.2706 | 43.5537 | 28.4463 | 0 | 43.5537 | 0 | 0 | 0 | 0 | 0 | 273.2706 | 0 | 530.6353 | 41.6% | 0 | 0 | 6.25 | 10% | 43.5537
1693 | 980 | 837 | 77 | 4.8 | 21.2 | 0 | 0 | 0 | 275.1534 | 42.6499 | 29.3501 | 0 | 42.6499 | 0 | 0 | 0 | 0 | 0 | 275.1534 | 0 | 805.7887 | 63.17% | 0 | 0 | 6.25 | 10% | 42.6499
1694 | 961 | 789 | 79 | 4.4 | 21.8 | 0 | 0 | 0 | 269.1103 | 58.5523 | 13.4477 | 16.5459 | 42.0064 | 0 | 0 | 0 | 0 | 0 | 269.1103 | 0 | 1074.8991 | 84.27% | 16.5459 | 0 | 21.2002 | 33.92% | 42.0064
1695 | 918 | 676 | 79 | 4.5 | 22.4 | 0 | 0 | 0 | 200.6111 | 66.7418 | 1.0922 | 25 | 41.7418 | 0 | 0 | 0 | 0 | 0 | 200.6111 | 0 | 1275.5102 | 100% | 25 | 0 | 43.7892 | 70.06% | 41.7418
1696 | 855 | 512 | 72 | 4.3 | 21.7 | 0 | 0 | 0 | 0 | 55.4156 | 0 | 13.7908 | 41.6248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 13.7908 | 0 | 56.25 | 90% | 41.6248
1697 | 747 | 314 | 57 | 4.3 | 20.6 | 0 | 0 | 0 | 0 | 31.7994 | 6.5825 | 0 | 31.7994 | 0 | 0 | 0 | 38.2653 | 12.8518 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 44.6512
1698 | 428 | 103 | 34 | 4.1 | 17.3 | 0 | 0 | 0 | 0 | 13.5538 | 0 | 0 | 13.5538 | 0 | 0 | 0 | 49.3408 | 17.7177 | 0 | 49.3408 | 1187.9041 | 93.13% | 0 | 15.9771 | 38.5677 | 61.71% | 47.2485
1699 | 4 | 2 | 2 | 2.5 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1966 | 45.9798 | 0 | 114.1966 | 1073.7075 | 84.18% | 0 | 0 | 38.5677 | 61.71% | 45.9798
1700 | 0 | 0 | 0 | 1.5 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.0322 | 42.4967 | 0 | 106.0322 | 967.6753 | 75.87% | 0 | 0 | 38.5677 | 61.71% | 42.4967
1701 | 0 | 0 | 0 | 1.2 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3757 | 38.7587 | 0 | 97.3757 | 870.2996 | 68.23% | 0 | 0 | 38.5677 | 61.71% | 38.7587
1702 | 0 | 0 | 0 | 1.1 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2196 | 36.5136 | 0 | 92.2196 | 778.08 | 61% | 0 | 0 | 38.5677 | 61.71% | 36.5136
1703 | 0 | 0 | 0 | 0.8 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8839 | 34.2046 | 0 | 86.8839 | 691.1961 | 54.19% | 0 | 0 | 38.5677 | 61.71% | 34.2046
1704 | 0 | 0 | 0 | 1.2 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4086 | 33.0848 | 0 | 84.4086 | 606.7875 | 47.57% | 0 | 0 | 38.5677 | 61.71% | 33.0848
1705 | 0 | 0 | 0 | 1.7 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606.7875 | 47.57% | 0 | 16.3817 | 20.4375 | 32.7% | 16.3817
1706 | 0 | 0 | 0 | 2.9 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606.7875 | 47.57% | 0 | 0 | 20.4375 | 32.7% | 0
1707 | 0 | 0 | 0 | 2.4 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0599 | 33.699 | 0 | 86.0599 | 520.7277 | 40.83% | 0 | 0 | 20.4375 | 32.7% | 33.699
1708 | 0 | 0 | 0 | 1.2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5409 | 37.0094 | 0 | 93.5409 | 427.1867 | 33.49% | 0 | 0 | 20.4375 | 32.7% | 37.0094
1709 | 0 | 0 | 0 | 1.8 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8128 | 41.8463 | 0 | 104.8128 | 322.3739 | 25.27% | 0 | 0 | 20.4375 | 32.7% | 41.8463
1710 | 0 | 0 | 0 | 1.1 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.0309 | 44.5899 | 0 | 111.0309 | 211.343 | 16.57% | 0 | 0 | 20.4375 | 32.7% | 44.5899
1711 | 79 | 17 | 11 | 1.2 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.2326 | 46.0299 | 0 | 114.2326 | 97.1104 | 7.613% | 0 | 0 | 20.4375 | 32.7% | 46.0299
1712 | 516 | 164 | 43 | 1.7 | 16.4 | 0 | 0 | 0 | 0 | 8.0239 | 0 | 0 | 8.0239 | 0 | 0 | 0 | 97.1104 | 38.4601 | 0 | 97.1104 | 0 | 0% | 0 | 0 | 20.4375 | 32.7% | 46.4839
1713 | 903 | 414 | 50 | 5.7 | 20.9 | 0 | 0 | 0 | 180.274 | 33.7288 | 0 | 0 | 33.7288 | 0 | 0 | 0 | 0 | 0 | 180.274 | 0 | 180.274 | 14.13% | 0 | 12.8192 | 6.25 | 10% | 46.548
1714 | 976 | 618 | 66 | 7.6 | 22.8 | 0 | 0 | 0 | 169.6692 | 46.2862 | 7.9843 | 0 | 46.2862 | 0 | 0 | 0 | 0 | 0 | 169.6692 | 0 | 349.9432 | 27.44% | 0 | 0 | 6.25 | 10% | 46.2862
1715 | 977 | 802 | 129 | 9.5 | 24.1 | 0 | 0 | 0 | 255.7271 | 45.9074 | 25.8623 | 0 | 45.9074 | 0 | 0 | 0 | 0 | 0 | 255.7271 | 0 | 605.6703 | 47.48% | 0 | 0 | 6.25 | 10% | 45.9074
1716 | 1036 | 850 | 62 | 7.4 | 24.7 | 0 | 0 | 0 | 286.0637 | 49.7135 | 22.2865 | 5.3367 | 44.3768 | 0 | 0 | 0 | 0 | 0 | 286.0637 | 0 | 891.734 | 69.91% | 5.3367 | 0 | 11.072 | 17.72% | 44.3768
1717 | 1007 | 858 | 73 | 6.2 | 24.9 | 0 | 0 | 0 | 282.2169 | 68.466 | 3.534 | 25 | 43.466 | 0 | 0 | 0 | 0 | 0 | 282.2169 | 0 | 1173.9509 | 92.04% | 25 | 0 | 33.661 | 53.86% | 43.466
1718 | 907 | 789 | 112 | 6.9 | 23.1 | 0 | 0 | 0 | 0 | 67.6206 | 4.3794 | 25 | 42.6206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1173.9509 | 92.04% | 25 | 0 | 56.25 | 90% | 42.6206
1719 | 352 | 410 | 183 | 6.5 | 21 | 0 | 0 | 0 | 0 | 40.3025 | 0 | 0 | 40.3025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1173.9509 | 92.04% | 0 | 1.1645 | 54.9612 | 87.94% | 41.467
1720 | 434 | 445 | 218 | 5.3 | 20.8 | 0 | 0 | 0 | 101.5593 | 43.6779 | 0 | 1.4264 | 42.2515 | 0 | 0 | 0 | 0 | 0 | 101.5593 | 0 | 1275.5102 | 100% | 1.4264 | 0 | 56.25 | 90% | 42.2515
1721 | 108 | 152 | 115 | 6.8 | 17.9 | 0 | 0 | 0 | 0 | 13.2032 | 0 | 0 | 13.2032 | 0 | 0 | 0 | 82.8069 | 32.1902 | 0 | 82.8069 | 1192.7033 | 93.51% | 0 | 0 | 56.25 | 90% | 45.3935
1722 | 155 | 66 | 41 | 5.4 | 16.1 | 0 | 0 | 0 | 0 | 7.0828 | 0 | 0 | 7.0828 | 0 | 0 | 0 | 103.0878 | 41.0681 | 0 | 103.0878 | 1089.6155 | 85.43% | 0 | 0 | 56.25 | 90% | 48.151
1723 | 2 | 2 | 2 | 4.7 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.7734 | 46.6789 | 0 | 115.7734 | 973.8422 | 76.35% | 0 | 0 | 56.25 | 90% | 46.6789
1724 | 0 | 0 | 0 | 3.8 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.2615 | 43.0384 | 0 | 107.2615 | 866.5807 | 67.94% | 0 | 0 | 56.25 | 90% | 43.0384
1725 | 0 | 0 | 0 | 4 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3695 | 39.1988 | 0 | 98.3695 | 768.2112 | 60.23% | 0 | 0 | 56.25 | 90% | 39.1988
1726 | 0 | 0 | 0 | 3.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9794 | 36.859 | 0 | 92.9794 | 675.2318 | 52.94% | 0 | 0 | 56.25 | 90% | 36.859
1727 | 0 | 0 | 0 | 3.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3902 | 34.8647 | 0 | 88.3902 | 586.8416 | 46.01% | 0 | 0 | 56.25 | 90% | 34.8647
1728 | 0 | 0 | 0 | 1.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 13.0101 | 0 | 38.2653 | 548.5763 | 43.01% | 0 | 0 | 56.25 | 90% | 13.0101
1729 | 0 | 0 | 0 | 0.8 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.8047 | 26.3367 | 0 | 68.8047 | 479.7716 | 37.61% | 0 | 0 | 56.25 | 90% | 26.3367
1730 | 0 | 0 | 0 | 0.7 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0004 | 32.9762 | 0 | 84.0004 | 395.7712 | 31.03% | 0 | 0 | 56.25 | 90% | 32.9762
1731 | 0 | 0 | 0 | 0.3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1965 | 33.9358 | 0 | 86.1965 | 309.5747 | 24.27% | 0 | 0 | 56.25 | 90% | 33.9358
1732 | 0 | 0 | 0 | 0.8 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8918 | 37.2949 | 0 | 93.8918 | 215.6829 | 16.91% | 0 | 0 | 56.25 | 90% | 37.2949
1733 | 0 | 0 | 0 | 1.8 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4209 | 41.8908 | 0 | 104.4209 | 111.262 | 8.723% | 0 | 0 | 56.25 | 90% | 41.8908
1734 | 0 | 0 | 0 | 2.1 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.262 | 44.8768 | 0 | 111.262 | 0 | 0% | 0 | 0 | 56.25 | 90% | 44.8768
1735 | 155 | 21 | 10 | 1.6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 28.5817 | 45.73% | 25
1736 | 669 | 187 | 39 | 1.6 | 10 | 0 | 0 | 0 | 88.9369 | 9.468 | 0 | 0 | 9.468 | 0 | 0 | 0 | 0 | 0 | 88.9369 | 0 | 88.9369 | 6.973% | 0 | 20.178 | 6.25 | 10% | 29.646
1737 | 871 | 408 | 52 | 1.2 | 13.1 | 0 | 0 | 0 | 0 | 32.9367 | 0 | 0 | 32.9367 | 0 | 0 | 0 | 38.7805 | 13.2032 | 0 | 38.7805 | 50.1564 | 3.932% | 0 | 0 | 6.25 | 10% | 46.1399
1738 | 951 | 602 | 59 | 1.5 | 14.8 | 0 | 0 | 0 | 0 | 33.094 | 18.5402 | 0 | 33.094 | 0 | 0 | 0 | 38.2653 | 12.9582 | 0 | 38.2653 | 11.8911 | 0.9323% | 0 | 0 | 6.25 | 10% | 46.0522
1739 | 990 | 750 | 64 | 1.1 | 16.1 | 0 | 0 | 0 | 266.2956 | 45.5996 | 18.2928 | 0 | 45.5996 | 0 | 0 | 0 | 0 | 0 | 266.2956 | 0 | 278.1867 | 21.81% | 0 | 0 | 6.25 | 10% | 45.5996
1740 | 1003 | 835 | 68 | 1.6 | 17.4 | 0 | 0 | 0 | 280.761 | 43.9367 | 28.0633 | 0 | 43.9367 | 0 | 0 | 0 | 0 | 0 | 280.761 | 0 | 558.9477 | 43.82% | 0 | 0 | 6.25 | 10% | 43.9367
1741 | 1003 | 856 | 69 | 3.5 | 18.3 | 0 | 0 | 0 | 0 | 43.1122 | 28.8878 | 0 | 43.1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558.9477 | 43.82% | 0 | 0 | 6.25 | 10% | 43.1122
1742 | 986 | 807 | 71 | 4.8 | 18.7 | 0 | 0 | 0 | 225.5879 | 56.7609 | 15.2391 | 14.2824 | 42.4785 | 0 | 0 | 0 | 0 | 0 | 225.5879 | 0 | 784.5356 | 61.51% | 14.2824 | 0 | 19.155 | 30.65% | 42.4785
1743 | 954 | 696 | 69 | 5.5 | 18.2 | 0 | 0 | 0 | 260.3678 | 66.9521 | 3.7651 | 25 | 41.9521 | 0 | 0 | 0 | 0 | 0 | 260.3678 | 0 | 1044.9034 | 81.92% | 25 | 0 | 41.744 | 66.79% | 41.9521
1744 | 894 | 530 | 63 | 5.4 | 17.5 | 0 | 0 | 0 | 230.6068 | 57.8964 | 0 | 16.0543 | 41.8421 | 0 | 0 | 0 | 0 | 0 | 230.6068 | 0 | 1275.5102 | 100% | 16.0543 | 0 | 56.25 | 90% | 41.8421
1745 | 783 | 327 | 52 | 5 | 16.6 | 0 | 0 | 0 | 0 | 39.781 | 0 | 0 | 39.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 39.781
1746 | 508 | 113 | 31 | 3.7 | 15.3 | 0 | 0 | 0 | 0 | 15.24 | 0 | 0 | 15.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 40.24
1747 | 9 | 3 | 2 | 2.2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.4946 | 46.1636 | 0 | 114.4946 | 1161.0156 | 91.02% | 0 | 0 | 28.5817 | 45.73% | 46.1636
1748 | 0 | 0 | 0 | 0.8 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9172 | 42.9172 | 0 | 106.9172 | 1054.0985 | 82.64% | 0 | 0 | 28.5817 | 45.73% | 42.9172
1749 | 0 | 0 | 0 | 0.6 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.231 | 39.1528 | 0 | 98.231 | 955.8674 | 74.94% | 0 | 0 | 28.5817 | 45.73% | 39.1528
1750 | 0 | 0 | 0 | 0.9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0355 | 36.9064 | 0 | 93.0355 | 862.8319 | 67.65% | 0 | 0 | 28.5817 | 45.73% | 36.9064
1751 | 0 | 0 | 0 | 1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.816 | 34.6349 | 0 | 87.816 | 775.0159 | 60.76% | 0 | 0 | 28.5817 | 45.73% | 34.6349
1752 | 0 | 0 | 0 | 0.9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0359 | 33.4246 | 0 | 85.0359 | 689.98 | 54.09% | 0 | 0 | 28.5817 | 45.73% | 33.4246
1753 | 0 | 0 | 0 | 0.8 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8437 | 32.9066 | 0 | 83.8437 | 606.1363 | 47.52% | 0 | 0 | 28.5817 | 45.73% | 32.9066
1754 | 0 | 0 | 0 | 1.9 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4955 | 32.7562 | 0 | 83.4955 | 522.6408 | 40.98% | 0 | 0 | 28.5817 | 45.73% | 32.7562
1755 | 0 | 0 | 0 | 1.7 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5955 | 33.6642 | 0 | 85.5955 | 437.0453 | 34.26% | 0 | 0 | 28.5817 | 45.73% | 33.6642
1756 | 0 | 0 | 0 | 1.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.708 | 37.2142 | 0 | 93.708 | 343.3374 | 26.92% | 0 | 0 | 28.5817 | 45.73% | 37.2142
1757 | 0 | 0 | 0 | 1.2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8003 | 41.6193 | 0 | 103.8003 | 239.537 | 18.78% | 0 | 0 | 28.5817 | 45.73% | 41.6193
1758 | 0 | 0 | 0 | 1 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.4137 | 51.4902 | 0 | 126.4137 | 113.1233 | 8.869% | 6.9895 | 0 | 34.8971 | 55.84% | 44.5007
1759 | 189 | 23 | 10 | 0.8 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.1233 | 45.6873 | 0 | 113.1233 | 0 | 0% | 0 | 0 | 34.8971 | 55.84% | 45.6873
1760 | 695 | 195 | 38 | 0.4 | 12.4 | 0 | 0 | 0 | 0 | 9.6547 | 0 | 0 | 9.6547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 7.2287 | 11.57% | 34.6547
1761 | 876 | 414 | 52 | 0.4 | 17.2 | 0 | 0 | 0 | 0 | 32.2873 | 0 | 0 | 32.2873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0.88434 | 6.25 | 10% | 33.1716
1762 | 958 | 611 | 59 | 1.6 | 19.3 | 0 | 0 | 0 | 0 | 45.5411 | 5.7348 | 0 | 45.5411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 45.5411
1763 | 1001 | 762 | 64 | 2.6 | 20.8 | 0 | 0 | 0 | 268.9574 | 44.9603 | 20.4689 | 0 | 44.9603 | 0 | 0 | 0 | 0 | 0 | 268.9574 | 0 | 268.9574 | 21.09% | 0 | 0 | 6.25 | 10% | 44.9603
1764 | 1020 | 851 | 66 | 2.1 | 22.1 | 0 | 0 | 0 | 285.704 | 43.2821 | 28.7179 | 0 | 43.2821 | 0 | 0 | 0 | 0 | 0 | 285.704 | 0 | 554.6614 | 43.49% | 0 | 0 | 6.25 | 10% | 43.2821
1765 | 1021 | 872 | 67 | 2.2 | 22.8 | 0 | 0 | 0 | 289.7596 | 47.4448 | 24.5552 | 5.3367 | 42.1081 | 0 | 0 | 0 | 0 | 0 | 289.7596 | 0 | 844.421 | 66.2% | 5.3367 | 0 | 11.072 | 17.72% | 42.1081
1766 | 1007 | 823 | 66 | 3.4 | 23.6 | 0 | 0 | 0 | 284.0313 | 66.2209 | 5.7791 | 25 | 41.2209 | 0 | 0 | 0 | 0 | 0 | 284.0313 | 0 | 1128.4523 | 88.47% | 25 | 0 | 33.661 | 53.86% | 41.2209
1767 | 974 | 709 | 65 | 3.9 | 24 | 0 | 0 | 0 | 111.6105 | 65.707 | 3.569 | 25 | 40.707 | 0 | 0 | 0 | 0 | 0 | 111.6105 | 0 | 1240.0628 | 97.22% | 25 | 0 | 56.25 | 90% | 40.707
1768 | 916 | 541 | 61 | 2 | 23.9 | 0 | 0 | 0 | 0 | 40.3018 | 15.4868 | 0 | 40.3018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.0628 | 97.22% | 0 | 0 | 56.25 | 90% | 40.3018
1769 | 800 | 334 | 52 | 3.8 | 22.8 | 0 | 0 | 0 | 0 | 39.3832 | 0 | 0 | 39.3832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.0628 | 97.22% | 0 | 3.4323 | 52.4513 | 83.92% | 42.8156
1770 | 525 | 118 | 31 | 3.6 | 20.7 | 0 | 0 | 0 | 0 | 15.2963 | 0 | 0 | 15.2963 | 0 | 0 | 0 | 77.6398 | 29.8172 | 0 | 77.6398 | 1162.4231 | 91.13% | 0 | 0 | 52.4513 | 83.92% | 45.1135
1771 | 10 | 2 | 2 | 2.3 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.3297 | 18.9994 | 0 | 52.3297 | 1110.0934 | 87.03% | 0 | 25 | 24.783 | 39.65% | 43.9994
1772 | 0 | 0 | 0 | 0.7 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2798 | 41.1806 | 0 | 103.2798 | 1006.8136 | 78.93% | 0 | 0 | 24.783 | 39.65% | 41.1806
1773 | 0 | 0 | 0 | 1.2 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8537 | 38.008 | 0 | 95.8537 | 910.9599 | 71.42% | 0 | 0 | 24.783 | 39.65% | 38.008
1774 | 0 | 0 | 0 | 0.8 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6412 | 36.2323 | 0 | 91.6412 | 819.3187 | 64.23% | 0 | 0 | 24.783 | 39.65% | 36.2323
1775 | 0 | 0 | 0 | 1 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4635 | 33.9984 | 0 | 86.4635 | 732.8553 | 57.46% | 0 | 0 | 24.783 | 39.65% | 33.9984
1776 | 0 | 0 | 0 | 1.8 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9098 | 32.4456 | 0 | 82.9098 | 649.9455 | 50.96% | 0 | 0 | 24.783 | 39.65% | 32.4456
1777 | 0 | 0 | 0 | 1.3 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0878 | 31.6754 | 0 | 81.0878 | 568.8577 | 44.6% | 0 | 0 | 24.783 | 39.65% | 31.6754
1778 | 0 | 0 | 0 | 1 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0754 | 31.2451 | 0 | 80.0754 | 488.7824 | 38.32% | 0 | 0 | 24.783 | 39.65% | 31.2451
1779 | 0 | 0 | 0 | 1.1 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7571 | 31.1086 | 0 | 79.7571 | 409.0253 | 32.07% | 0 | 0 | 24.783 | 39.65% | 31.1086
1780 | 0 | 0 | 0 | 1.3 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6858 | 31.9512 | 0 | 81.6858 | 327.3395 | 25.66% | 0 | 0 | 24.783 | 39.65% | 31.9512
1781 | 0 | 0 | 0 | 1 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5729 | 32.7868 | 0 | 83.5729 | 243.7666 | 19.11% | 0 | 0 | 24.783 | 39.65% | 32.7868
1782 | 0 | 0 | 0 | 1.9 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8646 | 35.5193 | 0 | 89.8646 | 153.902 | 12.07% | 0 | 0 | 24.783 | 39.65% | 35.5193
1783 | 198 | 26 | 11 | 0.4 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2212 | 38.7392 | 0 | 97.2212 | 56.6808 | 4.444% | 0 | 0 | 24.783 | 39.65% | 38.7392
1784 | 700 | 202 | 40 | 1.4 | 12.5 | 0 | 0 | 0 | 0 | 10.0051 | 0 | 0 | 10.0051 | 0 | 0 | 0 | 56.6808 | 21.0049 | 0 | 56.6808 | 0 | 0% | 0 | 9.2709 | 14.5225 | 23.24% | 40.2809
1785 | 880 | 422 | 52 | 0.9 | 17.1 | 0 | 0 | 0 | 181.4464 | 32.7811 | 0 | 0 | 32.7811 | 0 | 0 | 0 | 0 | 0 | 181.4464 | 0 | 181.4464 | 14.23% | 0 | 7.4747 | 6.25 | 10% | 40.2558
1786 | 965 | 620 | 58 | 0.9 | 20.4 | 0 | 0 | 0 | 239.0175 | 39.5428 | 11.0721 | 0 | 39.5428 | 0 | 0 | 0 | 0 | 0 | 239.0175 | 0 | 420.4639 | 32.96% | 0 | 0 | 6.25 | 10% | 39.5428
1787 | 1007 | 770 | 61 | 1.4 | 22.1 | 0 | 0 | 0 | 271.5777 | 39.5163 | 24.2244 | 0 | 39.5163 | 0 | 0 | 0 | 0 | 0 | 271.5777 | 0 | 692.0416 | 54.26% | 0 | 0 | 6.25 | 10% | 39.5163
1788 | 1027 | 858 | 63 | 2.8 | 23 | 0 | 0 | 0 | 287.5488 | 38.4147 | 33.5853 | 0 | 38.4147 | 0 | 0 | 0 | 0 | 0 | 287.5488 | 0 | 979.5904 | 76.8% | 0 | 0 | 6.25 | 10% | 38.4147
1789 | 1031 | 881 | 64 | 3.2 | 23.8 | 0 | 0 | 0 | 0 | 36.6181 | 35.3819 | 0 | 36.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 979.5904 | 76.8% | 0 | 0 | 6.25 | 10% | 36.6181
1790 | 1021 | 833 | 63 | 5.4 | 24 | 0 | 0 | 0 | 0 | 40.9433 | 31.0567 | 5.6274 | 35.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 979.5904 | 76.8% | 5.6274 | 0 | 11.3347 | 18.14% | 35.3159
1791 | 988 | 718 | 62 | 5.9 | 24.1 | 0 | 0 | 0 | 0 | 60.0833 | 10.868 | 25 | 35.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 979.5904 | 76.8% | 25 | 0 | 33.9237 | 54.28% | 35.0833
1792 | 924 | 547 | 58 | 6 | 23.8 | 0 | 0 | 0 | 0 | 57.9503 | 0 | 22.8294 | 35.1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 979.5904 | 76.8% | 22.8294 | 0 | 54.5514 | 87.28% | 35.1209
1793 | 806 | 339 | 50 | 5.6 | 22.8 | 0 | 0 | 0 | 129.5284 | 39.7152 | 0 | 1.8799 | 37.8353 | 0 | 0 | 0 | 0 | 0 | 129.5284 | 0 | 1109.1189 | 86.95% | 1.8799 | 0 | 56.25 | 90% | 37.8353
1794 | 522 | 121 | 32 | 4.4 | 21.4 | 0 | 0 | 0 | 0 | 15.2386 | 0 | 0 | 15.2386 | 0 | 0 | 0 | 67.2303 | 25.2986 | 0 | 67.2303 | 1041.8886 | 81.68% | 0 | 0 | 56.25 | 90% | 40.5371
1795 | 17 | 3 | 3 | 3.6 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2698 | 40.5733 | 0 | 102.2698 | 939.6188 | 73.67% | 0 | 0 | 56.25 | 90% | 40.5733
1796 | 0 | 0 | 0 | 2.1 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4877 | 38.6654 | 0 | 97.4877 | 842.1311 | 66.02% | 0 | 0 | 56.25 | 90% | 38.6654
1797 | 0 | 0 | 0 | 1 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8381 | 35.8535 | 0 | 90.8381 | 751.293 | 58.9% | 0 | 0 | 56.25 | 90% | 35.8535
1798 | 0 | 0 | 0 | 0.3 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.9872 | 0 | 38.2653 | 713.0277 | 55.9% | 0 | 20.379 | 33.6959 | 53.91% | 33.3662
1799 | 0 | 0 | 0 | 0.2 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.6178 | 25.3531 | 0 | 66.6178 | 646.4099 | 50.68% | 0 | 5.9394 | 27.1226 | 43.4% | 31.2924
1800 | 0 | 0 | 0 | 0.7 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7951 | 29.805 | 0 | 76.7951 | 569.6148 | 44.66% | 0 | 0 | 27.1226 | 43.4% | 29.805
1801 | 0 | 0 | 0 | 1 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8821 | 28.9708 | 0 | 74.8821 | 494.7327 | 38.79% | 0 | 0 | 27.1226 | 43.4% | 28.9708
1802 | 0 | 0 | 0 | 0.7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 13.0048 | 0 | 38.2653 | 456.4674 | 35.79% | 0 | 15.6276 | 9.827 | 15.72% | 28.6324
1803 | 0 | 0 | 0 | 1.6 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2051 | 28.6756 | 0 | 74.2051 | 382.2623 | 29.97% | 0 | 0 | 9.827 | 15.72% | 28.6756
1804 | 0 | 0 | 0 | 2.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.5253 | 29.2438 | 0 | 75.5253 | 306.737 | 24.05% | 0 | 0 | 9.827 | 15.72% | 29.2438
1805 | 0 | 0 | 0 | 2.4 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.5061 | 29.2354 | 0 | 75.5061 | 231.2309 | 18.13% | 0 | 0 | 9.827 | 15.72% | 29.2354
1806 | 0 | 0 | 0 | 1.7 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3274 | 30.9136 | 0 | 79.3274 | 151.9035 | 11.91% | 0 | 0 | 9.827 | 15.72% | 30.9136
1807 | 203 | 28 | 11 | 2.1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3656 | 33.5514 | 0 | 85.3656 | 66.5379 | 5.217% | 0 | 0 | 9.827 | 15.72% | 33.5514
1808 | 720 | 210 | 39 | 1.5 | 14.1 | 0 | 0 | 0 | 0 | 10.212 | 0 | 0 | 10.212 | 0 | 0 | 0 | 66.5379 | 25.2627 | 0 | 66.5379 | 0 | 0% | 0 | 0 | 9.827 | 15.72% | 35.4747
1809 | 897 | 434 | 53 | 0.7 | 18.9 | 0 | 0 | 0 | 0 | 33.1424 | 0 | 0 | 33.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.232 | 6.25 | 10% | 36.3744
1810 | 971 | 632 | 61 | 2.7 | 21.8 | 0 | 0 | 0 | 0 | 36.2184 | 16.227 | 0 | 36.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 36.2184
1811 | 989 | 771 | 69 | 1.7 | 23.9 | 0 | 0 | 0 | 0 | 36.6181 | 26.8201 | 0 | 36.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 36.6181
1812 | 1001 | 856 | 75 | 4.7 | 25.4 | 0 | 0 | 0 | 41.1468 | 36.3451 | 35.6549 | 0 | 36.3451 | 0 | 0 | 0 | 0 | 0 | 41.1468 | 0 | 41.1468 | 3.226% | 0 | 0 | 6.25 | 10% | 36.3451
1813 | 1006 | 877 | 74 | 4.1 | 25.5 | 0 | 0 | 0 | 284.1815 | 34.4232 | 37.5768 | 0 | 34.4232 | 0 | 0 | 0 | 0 | 0 | 284.1815 | 0 | 325.3283 | 25.51% | 0 | 0 | 6.25 | 10% | 34.4232
1814 | 980 | 821 | 76 | 4.7 | 25.6 | 0 | 0 | 0 | 274.8848 | 36.9254 | 35.0746 | 3.6957 | 33.2297 | 0 | 0 | 0 | 0 | 0 | 274.8848 | 0 | 600.2131 | 47.06% | 3.6957 | 0 | 9.5893 | 15.34% | 33.2297
1815 | 952 | 711 | 74 | 5.2 | 25.9 | 0 | 0 | 0 | 260.7841 | 57.7464 | 11.1034 | 25 | 32.7464 | 0 | 0 | 0 | 0 | 0 | 260.7841 | 0 | 860.9972 | 67.5% | 25 | 0 | 32.1783 | 51.49% | 32.7464
1816 | 909 | 549 | 65 | 6 | 25.8 | 0 | 0 | 0 | 234.8279 | 57.2378 | 0 | 23.8884 | 33.3494 | 0 | 0 | 0 | 0 | 0 | 234.8279 | 0 | 1095.8251 | 85.91% | 23.8884 | 0 | 53.7629 | 86.02% | 33.3494
1817 | 786 | 343 | 59 | 5.8 | 24.9 | 0 | 0 | 0 | 179.6851 | 39.2871 | 0 | 2.7526 | 36.5345 | 0 | 0 | 0 | 0 | 0 | 179.6851 | 0 | 1275.5102 | 100% | 2.7526 | 0 | 56.25 | 90% | 36.5345
1818 | 501 | 125 | 39 | 4.7 | 23.4 | 0 | 0 | 0 | 0 | 15.1801 | 0 | 0 | 15.1801 | 0 | 0 | 0 | 66.2705 | 24.7846 | 0 | 66.2705 | 1209.2397 | 94.8% | 0 | 0 | 56.25 | 90% | 39.9647
1819 | 13 | 3 | 3 | 2.2 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2555 | 39.994 | 0 | 101.2555 | 1107.9842 | 86.87% | 0 | 0 | 56.25 | 90% | 39.994
1820 | 0 | 0 | 0 | 1.7 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5749 | 38.1222 | 0 | 96.5749 | 1011.4093 | 79.29% | 0 | 0 | 56.25 | 90% | 38.1222
1821 | 0 | 0 | 0 | 1.3 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1133 | 21.5244 | 0 | 58.1133 | 953.2959 | 74.74% | 0 | 0 | 56.25 | 90% | 21.5244
1822 | 0 | 0 | 0 | 1.3 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0024 | 32.8481 | 0 | 84.0024 | 869.2935 | 68.15% | 0 | 0 | 56.25 | 90% | 32.8481
1823 | 0 | 0 | 0 | 1.2 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 869.2935 | 68.15% | 0 | 0 | 56.25 | 90% | 0
1824 | 0 | 0 | 0 | 1.8 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 869.2935 | 68.15% | 0 | 0 | 56.25 | 90% | 0
1825 | 0 | 0 | 0 | 1.7 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 869.2935 | 68.15% | 0 | 0 | 56.25 | 90% | 0
1826 | 0 | 0 | 0 | 2 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 869.2935 | 68.15% | 0 | 0 | 56.25 | 90% | 0
1827 | 0 | 0 | 0 | 3.7 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 869.2935 | 68.15% | 0 | 0 | 56.25 | 90% | 0
1828 | 0 | 0 | 0 | 3.6 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2063 | 34.3243 | 0 | 87.2063 | 782.0872 | 61.32% | 0 | 0 | 56.25 | 90% | 34.3243
1829 | 0 | 0 | 0 | 2.5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8198 | 38.5275 | 0 | 96.8198 | 685.2674 | 53.72% | 0 | 0 | 56.25 | 90% | 38.5275
1830 | 0 | 0 | 0 | 3.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.3272 | 41.817 | 0 | 104.3272 | 580.9403 | 45.55% | 0 | 0 | 56.25 | 90% | 41.817
1831 | 72 | 24 | 16 | 4 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5359 | 43.6693 | 0 | 108.5359 | 472.4044 | 37.04% | 0 | 0 | 56.25 | 90% | 43.6693
1832 | 442 | 183 | 73 | 4.3 | 11.2 | 0 | 0 | 0 | 53.2781 | 9.955 | 0 | 0 | 9.955 | 0 | 0 | 0 | 0 | 0 | 53.2781 | 0 | 525.6825 | 41.21% | 0 | 25 | 28.5817 | 45.73% | 34.955
1833 | 435 | 375 | 195 | 6 | 13.6 | 0 | 0 | 0 | 78.0425 | 30.2398 | 0 | 0 | 30.2398 | 0 | 0 | 0 | 0 | 0 | 78.0425 | 0 | 603.725 | 47.33% | 0 | 12.7035 | 14.5223 | 23.24% | 42.9433
1834 | 338 | 449 | 240 | 6.2 | 14.2 | 0 | 0 | 0 | 68.8562 | 36.7463 | 0 | 0 | 36.7463 | 0 | 0 | 0 | 0 | 0 | 68.8562 | 0 | 672.5812 | 52.73% | 0 | 7.4745 | 6.25 | 10% | 44.2208
1835 | 652 | 694 | 224 | 6.8 | 15.6 | 0 | 0 | 0 | 165.9449 | 60.593 | 0 | 16.4209 | 44.1721 | 0 | 0 | 0 | 0 | 0 | 165.9449 | 0 | 838.5261 | 65.74% | 16.4209 | 0 | 21.0873 | 33.74% | 44.1721
1836 | 446 | 662 | 301 | 8 | 14.9 | 0 | 0 | 0 | 110.2138 | 48.342 | 9.8711 | 5.571 | 42.771 | 0 | 0 | 0 | 0 | 0 | 110.2138 | 0 | 948.7399 | 74.38% | 5.571 | 0 | 26.121 | 41.79% | 42.771
1837 | 798 | 917 | 268 | 7.8 | 16.2 | 0 | 0 | 0 | 217.8901 | 66.7098 | 5.2902 | 25 | 41.7098 | 0 | 0 | 0 | 0 | 0 | 217.8901 | 0 | 1166.63 | 91.46% | 25 | 0 | 48.71 | 77.94% | 41.7098
1838 | 208 | 492 | 322 | 7.8 | 15.5 | 0 | 0 | 0 | 39.49 | 40.9112 | 0 | 0.1053 | 40.8059 | 0 | 0 | 0 | 0 | 0 | 39.49 | 0 | 1206.12 | 94.56% | 0.1053 | 0 | 48.8051 | 78.09% | 40.8059
1839 | 312 | 546 | 328 | 7.7 | 15.6 | 0 | 0 | 0 | 69.3902 | 48.5023 | 0 | 8.2395 | 40.2628 | 0 | 0 | 0 | 0 | 0 | 69.3902 | 0 | 1275.5102 | 100% | 8.2395 | 0 | 56.25 | 90% | 40.2628
1840 | 36 | 225 | 204 | 7.3 | 14.3 | 0 | 0 | 0 | 0 | 16.6687 | 0 | 0 | 16.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 3.7688 | 52.0789 | 83.33% | 20.4375
1841 | 1 | 157 | 155 | 6.9 | 13.2 | 0 | 0 | 0 | 0 | 10.4186 | 0 | 0 | 10.4186 | 0 | 0 | 0 | 82.751 | 32.3399 | 0 | 82.751 | 1192.7592 | 93.51% | 0 | 0 | 52.0789 | 83.33% | 42.7585
1842 | 0 | 37 | 36 | 5.7 | 12.1 | 0 | 0 | 0 | 0 | 1.9548 | 0 | 0 | 1.9548 | 0 | 0 | 0 | 108.051 | 43.3886 | 0 | 108.051 | 1084.7081 | 85.04% | 0 | 0 | 52.0789 | 83.33% | 45.3433
1843 | 0 | 1 | 1 | 5.6 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.2051 | 44.3475 | 0 | 110.2051 | 974.503 | 76.4% | 0 | 0 | 52.0789 | 83.33% | 44.3475
1844 | 0 | 0 | 0 | 4.6 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.6011 | 45.8358 | 0 | 113.6011 | 860.9019 | 67.49% | 4.6163 | 0 | 56.25 | 90% | 41.2196
1845 | 0 | 0 | 0 | 3.7 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9019 | 67.49% | 0 | 0 | 56.25 | 90% | 0
1846 | 0 | 0 | 0 | 2.8 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9019 | 67.49% | 0 | 0 | 56.25 | 90% | 0
1847 | 0 | 0 | 0 | 2.8 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9019 | 67.49% | 0 | 0 | 56.25 | 90% | 0
1848 | 0 | 0 | 0 | 2.7 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9019 | 67.49% | 0 | 0 | 56.25 | 90% | 0
1849 | 0 | 0 | 0 | 2.4 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9019 | 67.49% | 0 | 0 | 56.25 | 90% | 0
1850 | 0 | 0 | 0 | 2.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9019 | 67.49% | 0 | 0 | 56.25 | 90% | 0
1851 | 0 | 0 | 0 | 2.2 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9019 | 67.49% | 0 | 0 | 56.25 | 90% | 0
1852 | 0 | 0 | 0 | 1.8 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9019 | 67.49% | 0 | 0 | 56.25 | 90% | 0
1853 | 0 | 0 | 0 | 1.5 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860.9019 | 67.49% | 0 | 0 | 56.25 | 90% | 0
1854 | 0 | 0 | 0 | 1.5 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4611 | 40.1291 | 0 | 100.4611 | 760.4408 | 59.62% | 0 | 0 | 56.25 | 90% | 40.1291
1855 | 0 | 12 | 12 | 1.3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5858 | 41.9298 | 0 | 104.5858 | 655.855 | 51.42% | 0 | 0 | 56.25 | 90% | 41.9298
1856 | 27 | 112 | 103 | 1.2 | 10.5 | 0 | 0 | 0 | 0 | 7.6592 | 0 | 0 | 7.6592 | 0 | 0 | 0 | 88.9244 | 35.0909 | 0 | 88.9244 | 566.9306 | 44.45% | 0 | 0 | 56.25 | 90% | 42.7501
1857 | 15 | 213 | 203 | 2.1 | 11.2 | 0 | 0 | 0 | 0 | 15.0345 | 0 | 0 | 15.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566.9306 | 44.45% | 0 | 0 | 56.25 | 90% | 15.0345
1858 | 0 | 280 | 276 | 1.2 | 12.2 | 0 | 0 | 0 | 0 | 19.3778 | 0 | 0 | 19.3778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566.9306 | 44.45% | 0 | 9.0055 | 46.2833 | 74.05% | 28.3834
1859 | 6 | 398 | 387 | 2.1 | 13.4 | 0 | 0 | 0 | 0 | 27.8469 | 0 | 0 | 27.8469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566.9306 | 44.45% | 0 | 0 | 46.2833 | 74.05% | 27.8469
1860 | 69 | 499 | 434 | 3.7 | 14.6 | 0 | 0 | 0 | 0 | 37.7212 | 0 | 0 | 37.7212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566.9306 | 44.45% | 0 | 0 | 46.2833 | 74.05% | 37.7212
1861 | 140 | 499 | 375 | 5.6 | 14.7 | 0 | 0 | 0 | 0 | 40.0461 | 0 | 0.084148 | 39.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566.9306 | 44.45% | 0.084148 | 0 | 46.3593 | 74.17% | 39.962
1862 | 296 | 581 | 347 | 4 | 15.4 | 0 | 0 | 0 | 69.7214 | 49.9822 | 0 | 10.9464 | 39.0358 | 0 | 0 | 0 | 0 | 0 | 69.7214 | 0 | 636.652 | 49.91% | 10.9464 | 0 | 56.25 | 90% | 39.0358
1863 | 14 | 225 | 212 | 4 | 15.4 | 0 | 0 | 0 | 0 | 14.9592 | 0 | 0 | 14.9592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.652 | 49.91% | 0 | 0 | 56.25 | 90% | 14.9592
1864 | 1 | 125 | 122 | 5.7 | 13.7 | 0 | 0 | 0 | 0 | 7.7675 | 0 | 0 | 7.7675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.652 | 49.91% | 0 | 20.178 | 33.9183 | 54.27% | 27.9454
1865 | 93 | 141 | 104 | 5.7 | 12.7 | 0 | 0 | 0 | 0 | 11.6972 | 0 | 0 | 11.6972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636.652 | 49.91% | 0 | 25 | 6.25 | 10% | 36.6972
1866 | 69 | 78 | 63 | 6.3 | 11.7 | 0 | 0 | 0 | 0 | 5.9583 | 0 | 0 | 5.9583 | 0 | 0 | 0 | 97.7107 | 38.8948 | 0 | 97.7107 | 538.9413 | 42.25% | 0 | 0 | 6.25 | 10% | 44.8531
1867 | 0 | 2 | 2 | 5.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3597 | 44.0119 | 0 | 109.3597 | 429.5816 | 33.68% | 0 | 0 | 6.25 | 10% | 44.0119
1868 | 0 | 0 | 0 | 5.1 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0168 | 41.2585 | 0 | 103.0168 | 326.5648 | 25.6% | 0 | 0 | 6.25 | 10% | 41.2585
1869 | 0 | 0 | 0 | 4.3 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6231 | 37.6013 | 0 | 94.6231 | 231.9417 | 18.18% | 0 | 0 | 6.25 | 10% | 37.6013
1870 | 0 | 0 | 0 | 3 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.9417 | 18.18% | 0 | 0 | 6.25 | 10% | 0
1871 | 0 | 0 | 0 | 3 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.9417 | 18.18% | 0 | 0 | 6.25 | 10% | 0
1872 | 0 | 0 | 0 | 2.1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.9417 | 18.18% | 0 | 0 | 6.25 | 10% | 0
1873 | 0 | 0 | 0 | 2.6 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.9417 | 18.18% | 0 | 0 | 6.25 | 10% | 0
1874 | 0 | 0 | 0 | 2.7 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.9417 | 18.18% | 0 | 0 | 6.25 | 10% | 0
1875 | 0 | 0 | 0 | 2.1 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.9417 | 18.18% | 0 | 0 | 6.25 | 10% | 0
1876 | 0 | 0 | 0 | 1.3 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.9417 | 18.18% | 0 | 0 | 6.25 | 10% | 0
1877 | 0 | 0 | 0 | 0.9 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231.9417 | 18.18% | 0 | 0 | 6.25 | 10% | 0
1878 | 0 | 0 | 0 | 1.2 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.757 | 45.0926 | 0 | 111.757 | 120.1847 | 9.422% | 0 | 0 | 6.25 | 10% | 45.0926
1879 | 207 | 36 | 16 | 2.1 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.4142 | 46.2527 | 0 | 114.4142 | 5.7705 | 0.4524% | 0 | 0 | 6.25 | 10% | 46.2527
1880 | 682 | 223 | 50 | 2.7 | 8.5 | 0 | 0 | 0 | 96.6913 | 11.2081 | 0 | 0 | 11.2081 | 0 | 0 | 0 | 0 | 0 | 96.6913 | 0 | 102.4618 | 8.033% | 0 | 0 | 6.25 | 10% | 11.2081
1881 | 839 | 465 | 95 | 5.7 | 10.7 | 0 | 0 | 0 | 172.3929 | 37.1662 | 0 | 0 | 37.1662 | 0 | 0 | 0 | 0 | 0 | 172.3929 | 0 | 274.8547 | 21.55% | 0 | 0 | 6.25 | 10% | 37.1662
1882 | 755 | 563 | 113 | 5.3 | 11.9 | 0 | 0 | 0 | 181.9655 | 46.3349 | 3.0179 | 0 | 46.3349 | 0 | 0 | 0 | 0 | 0 | 181.9655 | 0 | 456.8202 | 35.81% | 0 | 0 | 6.25 | 10% | 46.3349
1883 | 628 | 699 | 238 | 5.7 | 12.8 | 0 | 0 | 0 | 160.2582 | 46.1859 | 14.2112 | 0 | 46.1859 | 0 | 0 | 0 | 0 | 0 | 160.2582 | 0 | 617.0784 | 48.38% | 0 | 0 | 6.25 | 10% | 46.1859
1884 | 708 | 828 | 263 | 6.4 | 14.1 | 0 | 0 | 0 | 189.7337 | 47.9133 | 24.0867 | 3.3193 | 44.5941 | 0 | 0 | 0 | 0 | 0 | 189.7337 | 0 | 806.8121 | 63.25% | 3.3193 | 0 | 9.2492 | 14.8% | 44.5941
1885 | 187 | 500 | 339 | 6.6 | 13.2 | 0 | 0 | 0 | 34.8924 | 40.9886 | 0 | 0 | 40.9886 | 0 | 0 | 0 | 0 | 0 | 34.8924 | 0 | 841.7045 | 65.99% | 0 | 2.7099 | 6.25 | 10% | 43.6985
1886 | 555 | 780 | 346 | 8.1 | 12.5 | 0 | 0 | 0 | 143.9845 | 65.2189 | 6.031 | 22.3072 | 42.9117 | 0 | 0 | 0 | 0 | 0 | 143.9845 | 0 | 985.689 | 77.28% | 22.3072 | 0 | 26.4059 | 42.25% | 42.9117
1887 | 548 | 680 | 305 | 7.1 | 12.9 | 0 | 0 | 0 | 139.791 | 63.892 | 0 | 21.5319 | 42.3602 | 0 | 0 | 0 | 0 | 0 | 139.791 | 0 | 1125.48 | 88.24% | 21.5319 | 0 | 45.8612 | 73.38% | 42.3602
1888 | 611 | 544 | 202 | 7.1 | 13.4 | 0 | 0 | 0 | 150.0303 | 53.6071 | 0 | 11.4976 | 42.1095 | 0 | 0 | 0 | 0 | 0 | 150.0303 | 0 | 1275.5102 | 100% | 11.4976 | 0 | 56.25 | 90% | 42.1095
1889 | 179 | 198 | 118 | 7.4 | 11.7 | 0 | 0 | 0 | 0 | 17.4137 | 0 | 0 | 17.4137 | 0 | 0 | 0 | 71.4431 | 27.4492 | 0 | 71.4431 | 1204.0671 | 94.4% | 0 | 0 | 56.25 | 90% | 44.8628
1890 | 103 | 77 | 55 | 6.1 | 9.7 | 0 | 0 | 0 | 0 | 6.4935 | 0 | 0 | 6.4935 | 0 | 0 | 0 | 104.1728 | 41.755 | 0 | 104.1728 | 1099.8943 | 86.23% | 0 | 0 | 56.25 | 90% | 48.2485
1891 | 0 | 2 | 2 | 5 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.5125 | 47.1524 | 0 | 116.5125 | 983.3819 | 77.1% | 0 | 0 | 56.25 | 90% | 47.1524
1892 | 0 | 0 | 0 | 4.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.8209 | 43.3657 | 0 | 107.8209 | 875.5609 | 68.64% | 0 | 0 | 56.25 | 90% | 43.3657
1893 | 0 | 0 | 0 | 4.6 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.758 | 38.9743 | 0 | 97.758 | 777.8029 | 60.98% | 0 | 0 | 56.25 | 90% | 38.9743
1894 | 0 | 0 | 0 | 2.3 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8582 | 36.8409 | 0 | 92.8582 | 684.9447 | 53.7% | 0 | 0 | 56.25 | 90% | 36.8409
1895 | 0 | 0 | 0 | 1.3 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 684.9447 | 53.7% | 0 | 0 | 56.25 | 90% | 0
1896 | 0 | 0 | 0 | 1.9 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 684.9447 | 53.7% | 0 | 0 | 56.25 | 90% | 0
1897 | 0 | 0 | 0 | 1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 684.9447 | 53.7% | 0 | 0 | 56.25 | 90% | 0
1898 | 0 | 0 | 0 | 1.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 684.9447 | 53.7% | 0 | 0 | 56.25 | 90% | 0
1899 | 0 | 0 | 0 | 4 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2421 | 33.9553 | 0 | 86.2421 | 598.7026 | 46.94% | 0 | 0 | 56.25 | 90% | 33.9553
1900 | 0 | 0 | 0 | 5.1 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1309 | 37.3952 | 0 | 94.1309 | 504.5717 | 39.56% | 0 | 0 | 56.25 | 90% | 37.3952
1901 | 0 | 0 | 0 | 3.7 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.317 | 41.8421 | 0 | 104.317 | 400.2548 | 31.38% | 0 | 0 | 56.25 | 90% | 41.8421
1902 | 0 | 0 | 0 | 4.2 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0647 | 45.2222 | 0 | 112.0647 | 288.1901 | 22.59% | 0 | 0 | 56.25 | 90% | 45.2222
1903 | 192 | 36 | 16 | 3.9 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.032 | 46.5146 | 0 | 115.032 | 173.1581 | 13.58% | 0 | 0 | 56.25 | 90% | 46.5146
1904 | 688 | 225 | 47 | 4.1 | 9.4 | 0 | 0 | 0 | 97.7048 | 11.1048 | 0 | 0 | 11.1048 | 0 | 0 | 0 | 0 | 0 | 97.7048 | 0 | 270.8629 | 21.24% | 0 | 14.879 | 39.7829 | 63.65% | 25.9838
1905 | 853 | 446 | 66 | 6.6 | 10.5 | 0 | 0 | 0 | 175.706 | 35.4585 | 0 | 0 | 35.4585 | 0 | 0 | 0 | 0 | 0 | 175.706 | 0 | 446.5689 | 35.01% | 0 | 0 | 39.7829 | 63.65% | 35.4585
1906 | 791 | 591 | 114 | 6.7 | 11.2 | 0 | 0 | 0 | 190.8604 | 51.6466 | 0 | 5.3242 | 46.3224 | 0 | 0 | 0 | 0 | 0 | 190.8604 | 0 | 637.4293 | 49.97% | 5.3242 | 0 | 44.5936 | 71.35% | 46.3224
1907 | 271 | 437 | 240 | 6 | 11.5 | 0 | 0 | 0 | 57.1669 | 37.2113 | 0 | 0 | 37.2113 | 0 | 0 | 0 | 0 | 0 | 57.1669 | 0 | 694.5962 | 54.46% | 0 | 8.703 | 34.9617 | 55.94% | 45.9143
1908 | 232 | 540 | 347 | 6.4 | 12.5 | 0 | 0 | 0 | 47.2564 | 44.1653 | 0 | 0 | 44.1653 | 0 | 0 | 0 | 0 | 0 | 47.2564 | 0 | 741.8526 | 58.16% | 0 | 0.2575 | 34.6767 | 55.48% | 44.4227
1909 | 31 | 320 | 287 | 5.9 | 12.5 | 0 | 0 | 0 | 0 | 23.297 | 0 | 0 | 23.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741.8526 | 58.16% | 0 | 0 | 34.6767 | 55.48% | 23.297
1910 | 360 | 565 | 278 | 6.4 | 13.3 | 0 | 0 | 0 | 87.0587 | 51.4057 | 0 | 8.4899 | 42.9159 | 0 | 0 | 0 | 0 | 0 | 87.0587 | 0 | 828.9113 | 64.99% | 8.4899 | 0 | 42.3478 | 67.76% | 42.9159
1911 | 176 | 413 | 282 | 6.8 | 13.2 | 0 | 0 | 0 | 0 | 34.1971 | 0 | 0 | 34.1971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828.9113 | 64.99% | 0 | 0 | 42.3478 | 67.76% | 34.1971
1912 | 737 | 563 | 159 | 5.9 | 13.7 | 0 | 0 | 0 | 186.7251 | 57.593 | 0 | 15.386 | 42.207 | 0 | 0 | 0 | 0 | 0 | 186.7251 | 0 | 1015.6364 | 79.63% | 15.386 | 0 | 56.25 | 90% | 42.207
1913 | 427 | 240 | 95 | 5.8 | 12.9 | 0 | 0 | 0 | 88.588 | 27.8729 | 0 | 0 | 27.8729 | 0 | 0 | 0 | 0 | 0 | 88.588 | 0 | 1104.2244 | 86.57% | 0 | 0 | 56.25 | 90% | 27.8729
1914 | 423 | 126 | 47 | 6.2 | 11.9 | 0 | 0 | 0 | 67.2376 | 14.3156 | 0 | 0 | 14.3156 | 0 | 0 | 0 | 0 | 0 | 67.2376 | 0 | 1171.462 | 91.84% | 0 | 25 | 28.5817 | 45.73% | 39.3156
1915 | 17 | 5 | 4 | 4.9 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.4295 | 47.0953 | 0 | 116.4295 | 1055.0326 | 82.71% | 0 | 0 | 28.5817 | 45.73% | 47.0953
1916 | 0 | 0 | 0 | 3.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.1848 | 43.5161 | 0 | 108.1848 | 946.8478 | 74.23% | 0 | 0 | 28.5817 | 45.73% | 43.5161
1917 | 0 | 0 | 0 | 2.8 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1926 | 39.5901 | 0 | 99.1926 | 847.6552 | 66.46% | 0 | 0 | 28.5817 | 45.73% | 39.5901
1918 | 0 | 0 | 0 | 2.8 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6889 | 37.1849 | 0 | 93.6889 | 753.9663 | 59.11% | 0 | 0 | 28.5817 | 45.73% | 37.1849
1919 | 0 | 0 | 0 | 3.7 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3065 | 34.8452 | 0 | 88.3065 | 665.6598 | 52.19% | 0 | 0 | 28.5817 | 45.73% | 34.8452
1920 | 0 | 0 | 0 | 2.8 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0951 | 33.4511 | 0 | 85.0951 | 580.5648 | 45.52% | 0 | 0 | 28.5817 | 45.73% | 33.4511
1921 | 0 | 0 | 0 | 3.8 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.848 | 32.9107 | 0 | 83.848 | 496.7167 | 38.94% | 0 | 0 | 28.5817 | 45.73% | 32.9107
1922 | 0 | 0 | 0 | 1.9 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5536 | 32.7826 | 0 | 83.5536 | 413.1631 | 32.39% | 0 | 0 | 28.5817 | 45.73% | 32.7826
1923 | 0 | 0 | 0 | 0.6 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.563 | 33.6558 | 0 | 85.563 | 327.6001 | 25.68% | 0 | 0 | 28.5817 | 45.73% | 33.6558
1924 | 0 | 0 | 0 | 1.2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.026 | 37.3465 | 0 | 94.026 | 233.5741 | 18.31% | 0 | 0 | 28.5817 | 45.73% | 37.3465
1925 | 0 | 0 | 0 | 3.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8519 | 42.0761 | 0 | 104.8519 | 128.7222 | 10.09% | 0 | 0 | 28.5817 | 45.73% | 42.0761
1926 | 0 | 0 | 0 | 2.8 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.0236 | 45.2068 | 0 | 112.0236 | 16.6986 | 1.309% | 0 | 0 | 28.5817 | 45.73% | 45.2068
1927 | 34 | 25 | 20 | 2.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6986 | 1.309% | 0 | 20.178 | 6.25 | 10% | 20.178
1928 | 454 | 208 | 84 | 2.5 | 8.5 | 0 | 0 | 0 | 59.832 | 11.1549 | 0 | 0 | 11.1549 | 0 | 0 | 0 | 0 | 0 | 59.832 | 0 | 76.5306 | 6% | 0 | 0 | 6.25 | 10% | 11.1549
1929 | 689 | 451 | 137 | 3.9 | 11.2 | 0 | 0 | 0 | 0 | 33.6474 | 1.1709 | 0 | 33.6474 | 0 | 0 | 0 | 38.2653 | 12.9967 | 0 | 38.2653 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 46.6441
1930 | 721 | 580 | 134 | 4.9 | 12.3 | 0 | 0 | 0 | 0 | 33.3171 | 15.8421 | 0 | 33.3171 | 0 | 0 | 0 | 38.2653 | 12.9872 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.3043
1931 | 883 | 779 | 130 | 5.9 | 13.5 | 0 | 0 | 0 | 233.9536 | 45.704 | 22.1439 | 0 | 45.704 | 0 | 0 | 0 | 0 | 0 | 233.9536 | 0 | 233.9536 | 18.34% | 0 | 0 | 6.25 | 10% | 45.704
1932 | 903 | 862 | 134 | 6 | 14.4 | 0 | 0 | 0 | 248.3801 | 44.0788 | 27.9212 | 0 | 44.0788 | 0 | 0 | 0 | 0 | 0 | 248.3801 | 0 | 482.3337 | 37.81% | 0 | 0 | 6.25 | 10% | 44.0788
1933 | 892 | 883 | 149 | 6.1 | 15.3 | 0 | 0 | 0 | 248.3423 | 42.9535 | 29.0465 | 0 | 42.9535 | 0 | 0 | 0 | 0 | 0 | 248.3423 | 0 | 730.676 | 57.28% | 0 | 0 | 6.25 | 10% | 42.9535
1934 | 855 | 844 | 173 | 5.5 | 16.4 | 0 | 0 | 0 | 236.6579 | 67.0106 | 4.9894 | 25 | 42.0106 | 0 | 0 | 0 | 0 | 0 | 236.6579 | 0 | 967.3339 | 75.84% | 25 | 0 | 28.839 | 46.14% | 42.0106
1935 | 743 | 681 | 168 | 5.8 | 16.6 | 0 | 0 | 0 | 198.5175 | 65.7424 | 0 | 24.2777 | 41.4647 | 0 | 0 | 0 | 0 | 0 | 198.5175 | 0 | 1165.8514 | 91.4% | 24.2777 | 0 | 50.7754 | 81.24% | 41.4647
1936 | 693 | 549 | 164 | 6.5 | 16.3 | 0 | 0 | 0 | 109.6588 | 47.0626 | 7.9802 | 6.059 | 41.0037 | 0 | 0 | 0 | 0 | 0 | 109.6588 | 0 | 1275.5102 | 100% | 6.059 | 0 | 56.25 | 90% | 41.0037
1937 | 378 | 282 | 130 | 6.3 | 15.5 | 0 | 0 | 0 | 0 | 27.7814 | 0 | 0 | 27.7814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 15.5898 | 38.9962 | 62.39% | 43.3713
1938 | 198 | 99 | 59 | 5.9 | 13.6 | 0 | 0 | 0 | 0 | 9.3949 | 0 | 0 | 9.3949 | 0 | 0 | 0 | 92.6872 | 36.6517 | 0 | 92.6872 | 1182.823 | 92.73% | 0 | 0 | 38.9962 | 62.39% | 46.0466
1939 | 1 | 5 | 4 | 4.1 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.9735 | 45.1066 | 0 | 111.9735 | 1070.8495 | 83.95% | 0 | 0 | 38.9962 | 62.39% | 45.1066
1940 | 0 | 0 | 0 | 3 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.352 | 42.2376 | 0 | 105.352 | 965.4975 | 75.7% | 0 | 0 | 38.9962 | 62.39% | 42.2376
1941 | 0 | 0 | 0 | 3.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8022 | 38.9536 | 0 | 97.8022 | 867.6953 | 68.03% | 0 | 0 | 38.9962 | 62.39% | 38.9536
1942 | 0 | 0 | 0 | 3.3 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0213 | 36.8827 | 0 | 93.0213 | 774.674 | 60.73% | 0 | 0 | 38.9962 | 62.39% | 36.8827
1943 | 0 | 0 | 0 | 2.8 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8208 | 34.6224 | 0 | 87.8208 | 686.8532 | 53.85% | 0 | 0 | 38.9962 | 62.39% | 34.6224
1944 | 0 | 0 | 0 | 2.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4563 | 32.7269 | 0 | 83.4563 | 603.3969 | 47.31% | 0 | 0 | 38.9962 | 62.39% | 32.7269
1945 | 0 | 0 | 0 | 2.1 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6878 | 31.9581 | 0 | 81.6878 | 521.7091 | 40.9% | 0 | 0 | 38.9962 | 62.39% | 31.9581
1946 | 0 | 0 | 0 | 1 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521.7091 | 40.9% | 0 | 4.5882 | 33.9183 | 54.27% | 4.5882
1947 | 0 | 0 | 0 | 0.9 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521.7091 | 40.9% | 0 | 0 | 33.9183 | 54.27% | 0
1948 | 0 | 0 | 0 | 0.7 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521.7091 | 40.9% | 0 | 0 | 33.9183 | 54.27% | 0
1949 | 0 | 0 | 0 | 1 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 521.7091 | 40.9% | 0 | 0 | 33.9183 | 54.27% | 0
1950 | 0 | 0 | 0 | 2.1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1671 | 36.1042 | 0 | 91.1671 | 430.542 | 33.75% | 0 | 0 | 33.9183 | 54.27% | 36.1042
1951 | 127 | 36 | 21 | 1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7549 | 39.416 | 0 | 98.7549 | 331.7871 | 26.01% | 0 | 0 | 33.9183 | 54.27% | 39.416
1952 | 549 | 218 | 68 | 2.7 | 10.5 | 0 | 0 | 0 | 76.7526 | 11.1187 | 0 | 0 | 11.1187 | 0 | 0 | 0 | 0 | 0 | 76.7526 | 0 | 408.5398 | 32.03% | 0 | 25 | 6.25 | 10% | 36.1187
1953 | 659 | 405 | 99 | 6 | 13 | 0 | 0 | 0 | 132.9015 | 31.2755 | 0 | 0 | 31.2755 | 0 | 0 | 0 | 0 | 0 | 132.9015 | 0 | 541.4413 | 42.45% | 0 | 0 | 6.25 | 10% | 31.2755
1954 | 435 | 522 | 257 | 6.5 | 14.1 | 0 | 0 | 0 | 95.8852 | 42.9325 | 0 | 2.2937 | 40.6388 | 0 | 0 | 0 | 0 | 0 | 95.8852 | 0 | 637.3265 | 49.97% | 2.2937 | 0 | 8.3225 | 13.32% | 40.6388
1955 | 313 | 564 | 321 | 6.5 | 14.5 | 0 | 0 | 0 | 68.8754 | 45.9161 | 0 | 5.3957 | 40.5204 | 0 | 0 | 0 | 0 | 0 | 68.8754 | 0 | 706.2018 | 55.37% | 5.3957 | 0 | 13.1979 | 21.12% | 40.5204
1956 | 377 | 589 | 279 | 7.3 | 15 | 0 | 0 | 0 | 90.3583 | 51.344 | 0 | 11.8834 | 39.4606 | 0 | 0 | 0 | 0 | 0 | 90.3583 | 0 | 796.5601 | 62.45% | 11.8834 | 0 | 23.9353 | 38.3% | 39.4606
1957 | 76 | 468 | 397 | 7.4 | 12.1 | 0 | 0 | 0 | 0 | 35.806 | 0 | 0 | 35.806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 796.5601 | 62.45% | 0 | 0 | 23.9353 | 38.3% | 35.806
1958 | 307 | 709 | 451 | 6.1 | 13.4 | 0 | 0 | 0 | 71.0946 | 59.4485 | 0 | 23.0476 | 36.4008 | 0 | 0 | 0 | 0 | 0 | 71.0946 | 0 | 867.6547 | 68.02% | 23.0476 | 0 | 44.7602 | 71.62% | 36.4008
1959 | 13 | 269 | 255 | 5.4 | 12.6 | 0 | 0 | 0 | 0 | 18.1945 | 0 | 0 | 18.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 867.6547 | 68.02% | 0 | 0 | 44.7602 | 71.62% | 18.1945
1960 | 4 | 134 | 130 | 5.3 | 12.6 | 0 | 0 | 0 | 0 | 8.5261 | 0 | 0 | 8.5261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 867.6547 | 68.02% | 0 | 14.0014 | 29.2644 | 46.82% | 22.5275
1961 | 0 | 45 | 45 | 5 | 11.6 | 0 | 0 | 0 | 0 | 2.5403 | 0 | 0 | 2.5403 | 0 | 0 | 0 | 89.3896 | 35.2713 | 0 | 89.3896 | 778.2651 | 61.02% | 0 | 0 | 29.2644 | 46.82% | 37.8116
1962 | 0 | 54 | 53 | 4.6 | 11.7 | 0 | 0 | 0 | 0 | 3.1006 | 0 | 0 | 3.1006 | 0 | 0 | 0 | 88.0373 | 34.6798 | 0 | 88.0373 | 690.2278 | 54.11% | 0 | 2.9656 | 25.9823 | 41.57% | 40.746
1963 | 0 | 3 | 3 | 4.1 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9184 | 40.7335 | 0 | 101.9184 | 588.3094 | 46.12% | 0 | 0 | 25.9823 | 41.57% | 40.7335
1964 | 0 | 0 | 0 | 3.6 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1073 | 38.6417 | 0 | 97.1073 | 491.2021 | 38.51% | 0 | 0 | 25.9823 | 41.57% | 38.6417
1965 | 0 | 0 | 0 | 3.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1269 | 36.0373 | 0 | 91.1269 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 36.0373
1966 | 0 | 0 | 0 | 3.1 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1967 | 0 | 0 | 0 | 2.5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1968 | 0 | 0 | 0 | 1.9 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1969 | 0 | 0 | 0 | 3.5 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1970 | 0 | 0 | 0 | 3.6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1971 | 0 | 0 | 0 | 3.7 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1972 | 0 | 0 | 0 | 3.1 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1973 | 0 | 0 | 0 | 2.9 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1974 | 0 | 0 | 0 | 2.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1975 | 9 | 30 | 29 | 3.3 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 0
1976 | 50 | 125 | 113 | 4.7 | 12.6 | 0 | 0 | 0 | 0 | 8.3828 | 0 | 0 | 8.3828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 8.3828
1977 | 0 | 118 | 116 | 5.6 | 13 | 0 | 0 | 0 | 0 | 7.5305 | 0 | 0 | 7.5305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 7.5305
1978 | 30 | 243 | 218 | 5.4 | 13.9 | 0 | 0 | 0 | 0 | 17.1313 | 0 | 0 | 17.1313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 17.1313
1979 | 8 | 292 | 280 | 5.5 | 15 | 0 | 0 | 0 | 0 | 19.6212 | 0 | 0 | 19.6212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 25.9823 | 41.57% | 19.6212
1980 | 83 | 537 | 458 | 6.1 | 16.2 | 0 | 0 | 0 | 0 | 40.4715 | 0 | 4.2559 | 36.2156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 4.2559 | 0 | 29.8277 | 47.72% | 36.2156
1981 | 2 | 387 | 377 | 6.1 | 16.5 | 0 | 0 | 0 | 0 | 26.1752 | 0 | 0 | 26.1752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 29.8277 | 47.72% | 26.1752
1982 | 1 | 181 | 178 | 7 | 16 | 0 | 0 | 0 | 0 | 11.518 | 0 | 11.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 11.518 | 0 | 40.2349 | 64.38% | 0
1983 | 4 | 267 | 260 | 6.4 | 16 | 0 | 0 | 0 | 0 | 17.7245 | 0 | 17.7245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 17.7245 | 0 | 56.25 | 90% | 0
1984 | 16 | 256 | 244 | 6 | 16.2 | 0 | 0 | 0 | 0 | 17.4213 | 0 | 0 | 17.4213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 56.25 | 90% | 17.4213
1985 | 3 | 143 | 140 | 5.6 | 15.7 | 0 | 0 | 0 | 0 | 9.2062 | 0 | 0 | 9.2062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400.0752 | 31.37% | 0 | 0 | 56.25 | 90% | 9.2062
1986 | 0 | 52 | 51 | 4.9 | 14.8 | 0 | 0 | 0 | 0 | 2.9276 | 0 | 0 | 2.9276 | 0 | 0 | 0 | 94.0317 | 37.1931 | 0 | 94.0317 | 306.0436 | 23.99% | 0 | 0 | 56.25 | 90% | 40.1207
1987 | 0 | 4 | 4 | 3.8 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1274 | 40.338 | 0 | 101.1274 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 40.338
1988 | 0 | 0 | 0 | 3.3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 0
1989 | 0 | 0 | 0 | 3.2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 0
1990 | 0 | 0 | 0 | 1.7 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 0
1991 | 0 | 0 | 0 | 0.8 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 0
1992 | 0 | 0 | 0 | 1.4 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 0
1993 | 0 | 0 | 0 | 2.3 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8422e-14 | 0 | 0 | 2.8422e-14 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 0
1994 | 0 | 0 | 0 | 1.6 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 0
1995 | 0 | 0 | 0 | 1.4 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 0
1996 | 0 | 0 | 0 | 1.6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.9162 | 16.07% | 0 | 0 | 56.25 | 90% | 0
1997 | 0 | 0 | 0 | 1.9 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3886 | 39.2336 | 0 | 98.3886 | 106.5275 | 8.352% | 0 | 0 | 56.25 | 90% | 39.2336
1998 | 0 | 0 | 0 | 1.7 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.5275 | 42.7822 | 0 | 106.5275 | 0 | 0% | 0 | 0 | 56.25 | 90% | 42.7822
1999 | 177 | 57 | 36 | 1.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 28.5817 | 45.73% | 25
2000 | 590 | 236 | 70 | 2.6 | 13.4 | 0 | 0 | 0 | 76.5306 | 11.7727 | 0 | 0 | 11.7727 | 0 | 0 | 0 | 0 | 0 | 76.5306 | 0 | 76.5306 | 6% | 0 | 20.178 | 6.25 | 10% | 31.9507
2001 | 770 | 447 | 87 | 5.1 | 16.3 | 0 | 0 | 0 | 0 | 33.7906 | 0 | 2.0113 | 31.7793 | 0 | 0 | 0 | 38.2653 | 12.936 | 0 | 38.2653 | 38.2653 | 3% | 2.0113 | 0 | 8.0673 | 12.91% | 44.7152
2002 | 856 | 637 | 98 | 6.2 | 17.5 | 0 | 0 | 0 | 0 | 31.7287 | 20.6737 | 0 | 31.7287 | 0 | 0 | 0 | 38.2653 | 12.9155 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 8.0673 | 12.91% | 44.6442
2003 | 903 | 767 | 55 | 6 | 18.3 | 0 | 0 | 0 | 240.5933 | 44.4715 | 17.2426 | 0 | 44.4715 | 0 | 0 | 0 | 0 | 0 | 240.5933 | 0 | 240.5933 | 18.86% | 0 | 0 | 8.0673 | 12.91% | 44.4715
2004 | 924 | 741 | 75 | 5.4 | 19 | 0 | 0 | 0 | 255.4732 | 68.3142 | 3.0213 | 25 | 43.3142 | 0 | 0 | 0 | 0 | 0 | 255.4732 | 0 | 496.0665 | 38.89% | 25 | 0 | 30.6563 | 49.05% | 43.3142
2005 | 929 | 871 | 108 | 6.1 | 20.1 | 0 | 0 | 0 | 177.2537 | 42.3142 | 29.6858 | 0 | 42.3142 | 0 | 0 | 0 | 0 | 0 | 177.2537 | 0 | 673.3201 | 52.79% | 0 | 0 | 30.6563 | 49.05% | 42.3142
2006 | 912 | 824 | 111 | 6.6 | 20.2 | 0 | 0 | 0 | 0 | 66.707 | 5.293 | 25 | 41.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 673.3201 | 52.79% | 25 | 0 | 53.2453 | 85.19% | 41.707
2007 | 876 | 711 | 105 | 7.4 | 20.2 | 0 | 0 | 0 | 236.3798 | 44.4251 | 23.6185 | 3.3254 | 41.0998 | 0 | 0 | 0 | 0 | 0 | 236.3798 | 0 | 909.6999 | 71.32% | 3.3254 | 0 | 56.25 | 90% | 41.0998
2008 | 820 | 551 | 95 | 7.7 | 19.6 | 0 | 0 | 0 | 208.7969 | 40.7446 | 15.2669 | 0 | 40.7446 | 0 | 0 | 0 | 0 | 0 | 208.7969 | 0 | 1118.4968 | 87.69% | 0 | 0 | 56.25 | 90% | 40.7446
2009 | 696 | 349 | 79 | 7.2 | 18.7 | 0 | 0 | 0 | 157.0134 | 37.5356 | 0 | 0 | 37.5356 | 0 | 0 | 0 | 0 | 0 | 157.0134 | 0 | 1275.5102 | 100% | 0 | 5.5905 | 50.0628 | 80.1% | 43.1262
2010 | 398 | 135 | 55 | 7.2 | 16.6 | 0 | 0 | 0 | 0 | 13.8832 | 0 | 0 | 13.8832 | 0 | 0 | 0 | 83.259 | 32.4434 | 0 | 83.259 | 1192.2512 | 93.47% | 0 | 0 | 50.0628 | 80.1% | 46.3266
2011 | 26 | 8 | 6 | 5.1 | 14.5 | 0 | 0 | 0 | 0 | 0.034849 | 0 | 0 | 0.034849 | 0 | 0 | 0 | 112.3147 | 45.1525 | 0 | 112.3147 | 1079.9366 | 84.67% | 0 | 0 | 50.0628 | 80.1% | 45.1873
2012 | 0 | 0 | 0 | 3.4 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9023 | 41.5691 | 0 | 103.9023 | 976.0342 | 76.52% | 0 | 0 | 50.0628 | 80.1% | 41.5691
2013 | 0 | 0 | 0 | 3.8 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3296 | 37.8646 | 0 | 95.3296 | 880.7047 | 69.05% | 0 | 0 | 50.0628 | 80.1% | 37.8646
2014 | 0 | 0 | 0 | 3.4 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880.7047 | 69.05% | 0 | 0 | 50.0628 | 80.1% | 0
2015 | 0 | 0 | 0 | 1.9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880.7047 | 69.05% | 0 | 0 | 50.0628 | 80.1% | 0
2016 | 0 | 0 | 0 | 1.6 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880.7047 | 69.05% | 0 | 0 | 50.0628 | 80.1% | 0
2017 | 0 | 0 | 0 | 2.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880.7047 | 69.05% | 0 | 0 | 50.0628 | 80.1% | 0
2018 | 0 | 0 | 0 | 3.4 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880.7047 | 69.05% | 0 | 0 | 50.0628 | 80.1% | 0
2019 | 0 | 0 | 0 | 3.8 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880.7047 | 69.05% | 0 | 0 | 50.0628 | 80.1% | 0
2020 | 0 | 0 | 0 | 3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7177 | 36.3159 | 0 | 91.7177 | 788.987 | 61.86% | 0 | 0 | 50.0628 | 80.1% | 36.3159
2021 | 0 | 0 | 0 | 2.9 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1815 | 40.455 | 0 | 101.1815 | 687.8055 | 53.92% | 0 | 0 | 50.0628 | 80.1% | 40.455
2022 | 0 | 0 | 0 | 3.3 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.4186 | 43.6052 | 0 | 108.4186 | 579.3868 | 45.42% | 0 | 0 | 50.0628 | 80.1% | 43.6052
2023 | 38 | 52 | 46 | 3.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.8843 | 44.6748 | 0 | 110.8843 | 468.5026 | 36.73% | 0 | 0 | 50.0628 | 80.1% | 44.6748
2024 | 233 | 193 | 122 | 4.5 | 13.6 | 0 | 0 | 0 | 0 | 11.3236 | 0 | 0 | 11.3236 | 0 | 0 | 0 | 86.1259 | 33.7969 | 0 | 86.1259 | 382.3767 | 29.98% | 0 | 0 | 50.0628 | 80.1% | 45.1205
2025 | 275 | 323 | 200 | 6.9 | 16.1 | 0 | 0 | 0 | 42.8538 | 24.8265 | 0 | 0 | 24.8265 | 0 | 0 | 0 | 0 | 0 | 42.8538 | 0 | 425.2305 | 33.34% | 0 | 20.2115 | 27.6941 | 44.31% | 45.038
2026 | 69 | 348 | 301 | 7.6 | 16 | 0 | 0 | 0 | 0 | 25.7528 | 0 | 0 | 25.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425.2305 | 33.34% | 0 | 19.376 | 6.25 | 10% | 45.1288
2027 | 312 | 654 | 412 | 8.1 | 16.6 | 0 | 0 | 0 | 67.4599 | 44.75 | 6.9649 | 0 | 44.75 | 0 | 0 | 0 | 0 | 0 | 67.4599 | 0 | 492.6904 | 38.63% | 0 | 0 | 6.25 | 10% | 44.75
2028 | 377 | 754 | 439 | 9.8 | 18.1 | 0 | 0 | 0 | 88.3102 | 43.3532 | 18.7537 | 0 | 43.3532 | 0 | 0 | 0 | 0 | 0 | 88.3102 | 0 | 581.0006 | 45.55% | 0 | 0 | 6.25 | 10% | 43.3532
2029 | 565 | 906 | 432 | 10.7 | 18.1 | 0 | 0 | 0 | 145.751 | 67.5482 | 4.4518 | 25 | 42.5482 | 0 | 0 | 0 | 0 | 0 | 145.751 | 0 | 726.7517 | 56.98% | 25 | 0 | 28.839 | 46.14% | 42.5482
2030 | 437 | 746 | 398 | 9.7 | 17.5 | 0 | 0 | 0 | 107.4343 | 64.4432 | 0 | 22.5413 | 41.902 | 0 | 0 | 0 | 0 | 0 | 107.4343 | 0 | 834.186 | 65.4% | 22.5413 | 0 | 49.2064 | 78.73% | 41.902
2031 | 479 | 738 | 396 | 9.9 | 16.9 | 0 | 0 | 0 | 116.9611 | 49.196 | 15.2198 | 7.7954 | 41.4006 | 0 | 0 | 0 | 0 | 0 | 116.9611 | 0 | 951.1471 | 74.57% | 7.7954 | 0 | 56.25 | 90% | 41.4006
2032 | 191 | 428 | 312 | 9.2 | 15.8 | 0 | 0 | 0 | 28.8713 | 35.1172 | 0 | 0 | 35.1172 | 0 | 0 | 0 | 0 | 0 | 28.8713 | 0 | 980.0185 | 76.83% | 0 | 5.945 | 49.6705 | 79.47% | 41.0622
2033 | 12 | 148 | 142 | 9 | 14.1 | 0 | 0 | 0 | 0 | 9.8095 | 0 | 0 | 9.8095 | 0 | 0 | 0 | 86.012 | 33.7317 | 0 | 86.012 | 894.0064 | 70.09% | 0 | 0 | 49.6705 | 79.47% | 43.5412
2034 | 0 | 70 | 69 | 8.9 | 13.2 | 0 | 0 | 0 | 0 | 4.1931 | 0 | 0 | 4.1931 | 0 | 0 | 0 | 106.6575 | 42.7449 | 0 | 106.6575 | 787.3489 | 61.73% | 0 | 0 | 49.6705 | 79.47% | 46.938
2035 | 0 | 3 | 3 | 8.4 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.279 | 45.6525 | 0 | 113.279 | 674.07 | 52.85% | 0 | 0 | 49.6705 | 79.47% | 45.6525
2036 | 0 | 0 | 0 | 7.6 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5397 | 41.8435 | 0 | 104.5397 | 569.5303 | 44.65% | 0 | 0 | 49.6705 | 79.47% | 41.8435
2037 | 0 | 0 | 0 | 7.3 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.6129 | 37.962 | 0 | 95.6129 | 473.9174 | 37.16% | 0 | 0 | 49.6705 | 79.47% | 37.962
2038 | 0 | 0 | 0 | 5.6 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.7683 | 22.805 | 0 | 60.7683 | 413.1492 | 32.39% | 0 | 0 | 49.6705 | 79.47% | 22.805
2039 | 0 | 0 | 0 | 6.8 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.1492 | 32.39% | 0 | 0 | 49.6705 | 79.47% | 0
2040 | 0 | 0 | 0 | 7.6 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.1492 | 32.39% | 0 | 0 | 49.6705 | 79.47% | 0
2041 | 0 | 0 | 0 | 8.1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.1492 | 32.39% | 0 | 0 | 49.6705 | 79.47% | 0
2042 | 0 | 0 | 0 | 7.9 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.1492 | 32.39% | 0 | 0 | 49.6705 | 79.47% | 0
2043 | 0 | 0 | 0 | 6.7 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.1492 | 32.39% | 0 | 5.5969 | 43.4762 | 69.56% | 5.5969
2044 | 0 | 0 | 0 | 7.5 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5148 | 36.2379 | 0 | 91.5148 | 321.6343 | 25.22% | 0 | 0 | 43.4762 | 69.56% | 36.2379
2045 | 0 | 0 | 0 | 6.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.3665 | 40.5385 | 0 | 101.3665 | 220.2679 | 17.27% | 0 | 0 | 43.4762 | 69.56% | 40.5385
2046 | 0 | 0 | 0 | 6.4 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8743 | 43.8169 | 0 | 108.8743 | 111.3936 | 8.733% | 0 | 0 | 43.4762 | 69.56% | 43.8169
2047 | 210 | 51 | 24 | 7 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3936 | 44.9116 | 0 | 111.3936 | 0 | 0% | 0 | 0 | 43.4762 | 69.56% | 44.9116
2048 | 659 | 251 | 59 | 7.9 | 10.6 | 0 | 0 | 0 | 0 | 12.2275 | 0 | 0 | 12.2275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 15.8079 | 25.29% | 37.2275
2049 | 862 | 477 | 71 | 8.3 | 12 | 0 | 0 | 0 | 0 | 36.5248 | 0 | 0 | 36.5248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 8.6361 | 6.25 | 10% | 45.1609
2050 | 927 | 665 | 83 | 7.8 | 13.2 | 0 | 0 | 0 | 229.5862 | 45.1915 | 10.3517 | 0 | 45.1915 | 0 | 0 | 0 | 0 | 0 | 229.5862 | 0 | 229.5862 | 18% | 0 | 0 | 6.25 | 10% | 45.1915
2051 | 961 | 805 | 90 | 7.9 | 14.5 | 0 | 0 | 0 | 256.0714 | 45.0174 | 24.3595 | 0 | 45.0174 | 0 | 0 | 0 | 0 | 0 | 256.0714 | 0 | 485.6576 | 38.08% | 0 | 0 | 6.25 | 10% | 45.0174
2052 | 976 | 885 | 92 | 8.3 | 15.2 | 0 | 0 | 0 | 268.3271 | 43.6178 | 28.3822 | 0 | 43.6178 | 0 | 0 | 0 | 0 | 0 | 268.3271 | 0 | 753.9848 | 59.11% | 0 | 0 | 6.25 | 10% | 43.6178
2053 | 995 | 911 | 88 | 9 | 16.3 | 0 | 0 | 0 | 277.1427 | 42.5941 | 29.4059 | 0 | 42.5941 | 0 | 0 | 0 | 0 | 0 | 277.1427 | 0 | 1031.1275 | 80.84% | 0 | 0 | 6.25 | 10% | 42.5941
2054 | 959 | 860 | 103 | 9.6 | 16.3 | 0 | 0 | 0 | 244.3827 | 54.6308 | 17.3692 | 12.8988 | 41.7321 | 0 | 0 | 0 | 0 | 0 | 244.3827 | 0 | 1275.5102 | 100% | 12.8988 | 0 | 17.9048 | 28.65% | 41.7321
2055 | 898 | 752 | 124 | 8.8 | 15.9 | 0 | 0 | 0 | 0 | 66.2488 | 5.7512 | 25 | 41.2488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 25 | 0 | 40.4938 | 64.79% | 41.2488
2056 | 838 | 576 | 104 | 8.2 | 15.6 | 0 | 0 | 0 | 0 | 58.3775 | 0 | 17.4379 | 40.9396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 17.4379 | 0 | 56.25 | 90% | 40.9396
2057 | 736 | 367 | 78 | 8.4 | 14.6 | 0 | 0 | 0 | 0 | 39.6236 | 0 | 0 | 39.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 39.6236
2058 | 495 | 151 | 48 | 7.5 | 13.3 | 0 | 0 | 0 | 0 | 15.6203 | 0 | 0 | 15.6203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 40.6203
2059 | 45 | 10 | 7 | 7 | 11.4 | 0 | 0 | 0 | 0 | 0.14945 | 0 | 0 | 0.14945 | 0 | 0 | 0 | 112.8021 | 45.4794 | 0 | 112.8021 | 1162.7081 | 91.16% | 0 | 0 | 28.5817 | 45.73% | 45.6288
2060 | 0 | 0 | 0 | 5.2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.0702 | 42.1332 | 0 | 105.0702 | 1057.6379 | 82.92% | 0 | 0 | 28.5817 | 45.73% | 42.1332
2061 | 0 | 0 | 0 | 3.4 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.807 | 38.1027 | 0 | 95.807 | 961.8309 | 75.41% | 0 | 0 | 28.5817 | 45.73% | 38.1027
2062 | 0 | 0 | 0 | 1.8 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7578 | 35.9148 | 0 | 90.7578 | 871.0731 | 68.29% | 0 | 0 | 28.5817 | 45.73% | 35.9148
2063 | 0 | 0 | 0 | 1.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1077 | 43.9323 | 0 | 109.1077 | 761.9654 | 59.74% | 9.8754 | 0 | 37.5047 | 60.01% | 34.0569
2064 | 0 | 0 | 0 | 1.8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4911 | 32.7548 | 0 | 83.4911 | 678.4743 | 53.19% | 0 | 0 | 37.5047 | 60.01% | 32.7548
2065 | 0 | 0 | 0 | 1.3 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2436 | 32.2102 | 0 | 82.2436 | 596.2307 | 46.74% | 0 | 0 | 37.5047 | 60.01% | 32.2102
2066 | 0 | 0 | 0 | 2.3 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1119 | 32.1531 | 0 | 82.1119 | 514.1188 | 40.31% | 0 | 0 | 37.5047 | 60.01% | 32.1531
2067 | 0 | 0 | 0 | 2.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3303 | 33.121 | 0 | 84.3303 | 429.7885 | 33.7% | 0 | 0 | 37.5047 | 60.01% | 33.121
2068 | 0 | 0 | 0 | 2 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0118 | 36.4733 | 0 | 92.0118 | 337.7767 | 26.48% | 0 | 0 | 37.5047 | 60.01% | 36.4733
2069 | 0 | 0 | 0 | 1.1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5104 | 40.6151 | 0 | 101.5104 | 236.2663 | 18.52% | 0 | 0 | 37.5047 | 60.01% | 40.6151
2070 | 0 | 0 | 0 | 0.5 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7152 | 43.7501 | 0 | 108.7152 | 127.551 | 10% | 0 | 0 | 37.5047 | 60.01% | 43.7501
2071 | 323 | 61 | 21 | 1 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.985 | 0 | 127.551 | 0 | 0% | 7.1569 | 0 | 43.9714 | 70.35% | 44.828
2072 | 745 | 266 | 48 | 0.5 | 9.7 | 0 | 0 | 0 | 0 | 12.3506 | 0 | 0 | 12.3506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 24.6224 | 16.721 | 26.75% | 36.9729
2073 | 893 | 485 | 61 | 1.4 | 12.2 | 0 | 0 | 0 | 0 | 35.5507 | 0 | 0 | 35.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 9.4612 | 6.25 | 10% | 45.0119
2074 | 965 | 676 | 68 | 4.9 | 14.5 | 0 | 0 | 0 | 243.3582 | 45.0216 | 10.3536 | 0 | 45.0216 | 0 | 0 | 0 | 0 | 0 | 243.3582 | 0 | 243.3582 | 19.08% | 0 | 0 | 6.25 | 10% | 45.0216
2075 | 983 | 812 | 79 | 5.5 | 15.4 | 0 | 0 | 0 | 264.9272 | 44.9032 | 23.9546 | 0 | 44.9032 | 0 | 0 | 0 | 0 | 0 | 264.9272 | 0 | 508.2854 | 39.85% | 0 | 0 | 6.25 | 10% | 44.9032
2076 | 983 | 890 | 89 | 6.5 | 15.7 | 0 | 0 | 0 | 272.1756 | 43.4353 | 28.5647 | 0 | 43.4353 | 0 | 0 | 0 | 0 | 0 | 272.1756 | 0 | 780.4609 | 61.19% | 0 | 0 | 6.25 | 10% | 43.4353
2077 | 993 | 910 | 86 | 6 | 16.2 | 0 | 0 | 0 | 279.3882 | 42.5231 | 29.4769 | 0 | 42.5231 | 0 | 0 | 0 | 0 | 0 | 279.3882 | 0 | 1059.8491 | 83.09% | 0 | 0 | 6.25 | 10% | 42.5231
2078 | 988 | 862 | 82 | 6.9 | 16.2 | 0 | 0 | 0 | 0 | 54.0078 | 17.9922 | 12.2312 | 41.7766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1059.8491 | 83.09% | 12.2312 | 0 | 17.3016 | 27.68% | 41.7766
2079 | 965 | 751 | 77 | 7.3 | 15.9 | 0 | 0 | 0 | 215.6611 | 66.2321 | 5.7679 | 25 | 41.2321 | 0 | 0 | 0 | 0 | 0 | 215.6611 | 0 | 1275.5102 | 100% | 25 | 0 | 39.8906 | 63.82% | 41.2321
2080 | 900 | 582 | 74 | 7.4 | 15.7 | 0 | 0 | 0 | 0 | 58.8042 | 0 | 18.1055 | 40.6987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 18.1055 | 0 | 56.25 | 90% | 40.6987
2081 | 808 | 378 | 61 | 7.8 | 14.8 | 0 | 0 | 0 | 0 | 40.974 | 0 | 0 | 40.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 1.8848 | 54.1641 | 86.66% | 42.8588
2082 | 580 | 160 | 40 | 7.6 | 13.2 | 0 | 0 | 0 | 0 | 16.9166 | 0 | 0 | 16.9166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 26.4957 | 42.39% | 41.9166
2083 | 70 | 11 | 6 | 5.8 | 11.2 | 0 | 0 | 0 | 0 | 0.15451 | 0 | 0 | 0.15451 | 0 | 0 | 0 | 100.0876 | 39.943 | 0 | 100.0876 | 1175.4226 | 92.15% | 0 | 5.3516 | 20.5729 | 32.92% | 45.4492
2084 | 0 | 0 | 0 | 3.6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8658 | 42.044 | 0 | 104.8658 | 1070.5569 | 83.93% | 0 | 0 | 20.5729 | 32.92% | 42.044
2085 | 0 | 0 | 0 | 2.9 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.914 | 38.157 | 0 | 95.914 | 974.6429 | 76.41% | 0 | 0 | 20.5729 | 32.92% | 38.157
2086 | 0 | 0 | 0 | 3.1 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3178 | 36.1655 | 0 | 91.3178 | 883.3251 | 69.25% | 0 | 0 | 20.5729 | 32.92% | 36.1655
2087 | 0 | 0 | 0 | 2.3 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.798 | 34.1976 | 0 | 86.798 | 796.527 | 62.45% | 0 | 0 | 20.5729 | 32.92% | 34.1976
2088 | 0 | 0 | 0 | 2.1 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8959 | 32.9316 | 0 | 83.8959 | 712.6312 | 55.87% | 0 | 0 | 20.5729 | 32.92% | 32.9316
2089 | 0 | 0 | 0 | 0.8 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.3305 | 14.789 | 0 | 42.3305 | 670.3006 | 52.55% | 0 | 0 | 20.5729 | 32.92% | 14.789
2090 | 0 | 0 | 0 | 1.4 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7303 | 32.4233 | 0 | 82.7303 | 587.5703 | 46.07% | 0 | 0 | 20.5729 | 32.92% | 32.4233
2091 | 0 | 0 | 0 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6453 | 33.2547 | 0 | 84.6453 | 502.925 | 39.43% | 0 | 0 | 20.5729 | 32.92% | 33.2547
2092 | 0 | 0 | 0 | 1.9 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4451 | 36.6627 | 0 | 92.4451 | 410.4799 | 32.18% | 0 | 0 | 20.5729 | 32.92% | 36.6627
2093 | 0 | 0 | 0 | 2.6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8471 | 40.7669 | 0 | 101.8471 | 308.6328 | 24.2% | 0 | 0 | 20.5729 | 32.92% | 40.7669
2094 | 0 | 0 | 0 | 3.5 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7652 | 43.7835 | 0 | 108.7652 | 199.8676 | 15.67% | 0 | 0 | 20.5729 | 32.92% | 43.7835
2095 | 54 | 56 | 48 | 4.6 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.434 | 44.9241 | 0 | 111.434 | 88.4337 | 6.933% | 0 | 0 | 20.5729 | 32.92% | 44.9241
2096 | 74 | 159 | 138 | 5 | 10.7 | 0 | 0 | 0 | 0 | 10.4519 | 0 | 0 | 10.4519 | 0 | 0 | 0 | 88.4337 | 34.8733 | 0 | 88.4337 | 0 | 0% | 0 | 0 | 20.5729 | 32.92% | 45.3252
2097 | 502 | 437 | 188 | 6.2 | 12.1 | 0 | 0 | 0 | 99.264 | 32.417 | 0 | 0 | 32.417 | 0 | 0 | 0 | 0 | 0 | 99.264 | 0 | 99.264 | 7.782% | 0 | 12.9416 | 6.25 | 10% | 45.3586
2098 | 653 | 624 | 201 | 7 | 13.2 | 0 | 0 | 0 | 67.4566 | 45.2584 | 5.3632 | 0 | 45.2584 | 0 | 0 | 0 | 0 | 0 | 67.4566 | 0 | 166.7206 | 13.07% | 0 | 0 | 6.25 | 10% | 45.2584
2099 | 651 | 756 | 259 | 7.5 | 14.3 | 0 | 0 | 0 | 166.9836 | 44.75 | 18.5423 | 0 | 44.75 | 0 | 0 | 0 | 0 | 0 | 166.9836 | 0 | 333.7042 | 26.16% | 0 | 0 | 6.25 | 10% | 44.75
2100 | 760 | 850 | 220 | 7.5 | 15.5 | 0 | 0 | 0 | 204.6841 | 43.4701 | 28.5299 | 0 | 43.4701 | 0 | 0 | 0 | 0 | 0 | 204.6841 | 0 | 538.3882 | 42.21% | 0 | 0 | 6.25 | 10% | 43.4701
2101 | 828 | 914 | 219 | 7.7 | 15.8 | 0 | 0 | 0 | 227.9192 | 47.6565 | 24.3435 | 5.3367 | 42.3198 | 0 | 0 | 0 | 0 | 0 | 227.9192 | 0 | 766.3074 | 60.08% | 5.3367 | 0 | 11.072 | 17.72% | 42.3198
2102 | 729 | 837 | 250 | 7.6 | 16.1 | 0 | 0 | 0 | 197.1694 | 66.4897 | 5.5103 | 25 | 41.4897 | 0 | 0 | 0 | 0 | 0 | 197.1694 | 0 | 963.4768 | 75.54% | 25 | 0 | 33.661 | 53.86% | 41.4897
2103 | 770 | 736 | 189 | 8.4 | 15.7 | 0 | 0 | 0 | 204.0318 | 65.9703 | 3.4039 | 25 | 40.9703 | 0 | 0 | 0 | 0 | 0 | 204.0318 | 0 | 1167.5086 | 91.53% | 25 | 0 | 56.25 | 90% | 40.9703
2104 | 288 | 397 | 226 | 8 | 14.9 | 0 | 0 | 0 | 0 | 34.7648 | 0 | 0 | 34.7648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1167.5086 | 91.53% | 0 | 5.8573 | 49.7676 | 79.63% | 40.6221
2105 | 433 | 309 | 143 | 7.5 | 14.3 | 0 | 0 | 0 | 89.5201 | 30.8825 | 0 | 0 | 30.8825 | 0 | 0 | 0 | 0 | 0 | 89.5201 | 0 | 1257.0287 | 98.55% | 0 | 11.4359 | 37.1111 | 59.38% | 42.3184
2106 | 400 | 158 | 71 | 7.5 | 13.3 | 0 | 0 | 0 | 0 | 14.8074 | 0 | 0 | 14.8074 | 0 | 0 | 0 | 77.9403 | 30.2435 | 0 | 77.9403 | 1179.0884 | 92.44% | 0 | 0 | 37.1111 | 59.38% | 45.0509
2107 | 28 | 16 | 14 | 6.8 | 11.9 | 0 | 0 | 0 | 0 | 0.51423 | 0 | 0 | 0.51423 | 0 | 0 | 0 | 93.977 | 37.2629 | 0 | 93.977 | 1085.1115 | 85.07% | 0 | 6.3322 | 30.103 | 48.16% | 44.1094
2108 | 0 | 0 | 0 | 6.1 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8661 | 41.1541 | 0 | 102.8661 | 982.2454 | 77.01% | 0 | 0 | 30.103 | 48.16% | 41.1541
2109 | 0 | 0 | 0 | 6.1 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.64 | 38.0191 | 0 | 95.64 | 886.6054 | 69.51% | 0 | 0 | 30.103 | 48.16% | 38.0191
2110 | 0 | 0 | 0 | 5.1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6299 | 36.2838 | 0 | 91.6299 | 794.9755 | 62.33% | 0 | 0 | 30.103 | 48.16% | 36.2838
2111 | 0 | 0 | 0 | 3.7 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5402 | 34.0764 | 0 | 86.5402 | 708.4353 | 55.54% | 0 | 0 | 30.103 | 48.16% | 34.0764
2112 | 0 | 0 | 0 | 3.8 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.606 | 32.3648 | 0 | 82.606 | 625.8293 | 49.07% | 0 | 0 | 30.103 | 48.16% | 32.3648
2113 | 0 | 0 | 0 | 2.3 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7968 | 31.5779 | 0 | 80.7968 | 545.0325 | 42.73% | 0 | 0 | 30.103 | 48.16% | 31.5779
2114 | 0 | 0 | 0 | 3.1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7196 | 31.1086 | 0 | 79.7196 | 465.3129 | 36.48% | 0 | 0 | 30.103 | 48.16% | 31.1086
2115 | 0 | 0 | 0 | 2.6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3367 | 30.9415 | 0 | 79.3367 | 385.9761 | 30.26% | 0 | 0 | 30.103 | 48.16% | 30.9415
2116 | 0 | 0 | 0 | 2.2 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8464 | 31.5988 | 0 | 80.8464 | 305.1298 | 23.92% | 0 | 0 | 30.103 | 48.16% | 31.5988
2117 | 0 | 0 | 0 | 2.3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9396 | 32.5124 | 0 | 82.9396 | 222.1901 | 17.42% | 0 | 0 | 30.103 | 48.16% | 32.5124
2118 | 0 | 0 | 0 | 2.9 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8384 | 35.5234 | 0 | 89.8384 | 132.3517 | 10.38% | 0 | 0 | 30.103 | 48.16% | 35.5234
2119 | 188 | 58 | 31 | 2.9 | 7.9 | 0 | 0 | 0 | 0 | 1.1481 | 0 | 0 | 1.1481 | 0 | 0 | 0 | 94.0864 | 37.3752 | 0 | 94.0864 | 38.2653 | 3% | 0 | 0 | 30.103 | 48.16% | 38.5233
2120 | 520 | 239 | 80 | 4.5 | 10.6 | 0 | 0 | 0 | 0 | 12.0809 | 0 | 0 | 12.0809 | 0 | 0 | 0 | 38.2653 | 13.001 | 0 | 38.2653 | 0 | 0% | 0 | 15.114 | 13.3759 | 21.4% | 40.1959
2121 | 630 | 461 | 146 | 6.2 | 12.4 | 0 | 0 | 0 | 0 | 33.8548 | 0 | 0 | 33.8548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 6.4386 | 6.25 | 10% | 40.2934
2122 | 363 | 566 | 332 | 6.8 | 13.6 | 0 | 0 | 0 | 0 | 39.9787 | 4.8572 | 0 | 39.9787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 39.9787
2123 | 741 | 749 | 183 | 7 | 15.1 | 0 | 0 | 0 | 193.7283 | 39.8129 | 23.5708 | 0 | 39.8129 | 0 | 0 | 0 | 0 | 0 | 193.7283 | 0 | 193.7283 | 15.19% | 0 | 0 | 6.25 | 10% | 39.8129
2124 | 651 | 793 | 250 | 8.1 | 15.8 | 0 | 0 | 0 | 171.7782 | 38.9049 | 29.4651 | 0 | 38.9049 | 0 | 0 | 0 | 0 | 0 | 171.7782 | 0 | 365.5065 | 28.66% | 0 | 0 | 6.25 | 10% | 38.9049
2125 | 836 | 860 | 154 | 8.7 | 16 | 0 | 0 | 0 | 229.5264 | 37.1529 | 34.8471 | 0 | 37.1529 | 0 | 0 | 0 | 0 | 0 | 229.5264 | 0 | 595.0329 | 46.65% | 0 | 0 | 6.25 | 10% | 37.1529
2126 | 859 | 833 | 143 | 7.8 | 16.2 | 0 | 0 | 0 | 236.1347 | 51.6889 | 20.3111 | 15.6167 | 36.0722 | 0 | 0 | 0 | 0 | 0 | 236.1347 | 0 | 831.1676 | 65.16% | 15.6167 | 0 | 20.3607 | 32.58% | 36.0722
2127 | 823 | 721 | 136 | 7.6 | 16.2 | 0 | 0 | 0 | 220.3567 | 60.302 | 7.7877 | 25 | 35.302 | 0 | 0 | 0 | 0 | 0 | 220.3567 | 0 | 1051.5243 | 82.44% | 25 | 0 | 42.9497 | 68.72% | 35.302
2128 | 607 | 526 | 170 | 7.1 | 15.9 | 0 | 0 | 0 | 149.6129 | 50.0219 | 0 | 14.7199 | 35.302 | 0 | 0 | 0 | 0 | 0 | 149.6129 | 0 | 1201.1372 | 94.17% | 14.7199 | 0 | 56.25 | 90% | 35.302
2129 | 373 | 318 | 159 | 7 | 15.2 | 0 | 0 | 0 | 74.373 | 29.2733 | 0 | 0 | 29.2733 | 0 | 0 | 0 | 0 | 0 | 74.373 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 29.2733
2130 | 56 | 101 | 86 | 6.3 | 13.7 | 0 | 0 | 0 | 0 | 6.8422 | 0 | 0 | 6.8422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 6.8422
2131 | 0 | 7 | 7 | 6 | 12.1 | 0 | 0 | 0 | 0 | 0.035265 | 0 | 0 | 0.035265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0.035265
2132 | 0 | 0 | 0 | 5.5 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2133 | 0 | 0 | 0 | 4.7 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2134 | 0 | 0 | 0 | 4.9 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2135 | 0 | 0 | 0 | 3.9 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2136 | 0 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2137 | 0 | 0 | 0 | 2.6 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2138 | 0 | 0 | 0 | 3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2139 | 0 | 0 | 0 | 1.5 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2140 | 0 | 0 | 0 | 1.7 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2141 | 0 | 0 | 0 | 2.1 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2142 | 0 | 0 | 0 | 2.5 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
2143 | 0 | 8 | 8 | 2.2 | 9.5 | 0 | 0 | 0 | 0 | 0.021758 | 0 | 0 | 0.021758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0.021758
2144 | 0 | 22 | 22 | 2.9 | 9.5 | 0 | 0 | 0 | 0 | 1.0377 | 0 | 0 | 1.0377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 1.0377
2145 | 0 | 43 | 43 | 1.9 | 9.8 | 0 | 0 | 0 | 0 | 2.4321 | 0 | 0 | 2.4321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 2.4321
2146 | 0 | 59 | 57 | 1.5 | 10.1 | 0 | 0 | 0 | 0 | 3.325 | 0 | 0 | 3.325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 3.325
2147 | 0 | 84 | 81 | 1.3 | 10.5 | 0 | 0 | 0 | 0 | 4.8793 | 0 | 0 | 4.8793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 4.8793
2148 | 0 | 70 | 69 | 0.8 | 11 | 0 | 0 | 0 | 0 | 4.0521 | 0 | 0 | 4.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 4.0521
2149 | 0 | 89 | 88 | 0.9 | 11.5 | 0 | 0 | 0 | 0 | 5.2891 | 0 | 0 | 5.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 5.2891
2150 | 0 | 83 | 82 | 2.3 | 11.9 | 0 | 0 | 0 | 0 | 4.9009 | 0 | 0 | 4.9009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 4.9009
2151 | 0 | 65 | 63 | 1.8 | 12 | 0 | 0 | 0 | 0 | 3.6571 | 0 | 0 | 3.6571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 3.6571
2152 | 0 | 44 | 43 | 1.6 | 11.4 | 0 | 0 | 0 | 0 | 2.3722 | 0 | 0 | 2.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 2.3722
2153 | 0 | 41 | 40 | 1.1 | 11.4 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 2.2 | 0 | 0 | 0 | 79.5763 | 30.9991 | 0 | 79.5763 | 1195.9339 | 93.76% | 0 | 0 | 56.25 | 90% | 33.1991
2154 | 1 | 37 | 36 | 1.7 | 11.6 | 0 | 0 | 0 | 0 | 1.9799 | 0 | 0 | 1.9799 | 0 | 0 | 0 | 98.7455 | 39.3483 | 0 | 98.7455 | 1097.1883 | 86.02% | 0 | 0 | 56.25 | 90% | 41.3282
2155 | 0 | 3 | 3 | 1.1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5141 | 39.6806 | 0 | 99.5141 | 997.6742 | 78.22% | 0 | 0 | 56.25 | 90% | 39.6806
2156 | 0 | 0 | 0 | 0.7 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4655 | 37.0498 | 0 | 93.4655 | 904.2087 | 70.89% | 0 | 0 | 56.25 | 90% | 37.0498
2157 | 0 | 0 | 0 | 0.5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5114 | 34.0193 | 0 | 86.5114 | 817.6973 | 64.11% | 0 | 0 | 56.25 | 90% | 34.0193
2158 | 0 | 0 | 0 | 0.9 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3999 | 31.7938 | 0 | 81.3999 | 736.2974 | 57.73% | 0 | 0 | 56.25 | 90% | 31.7938
2159 | 0 | 0 | 0 | 0.7 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0639 | 30.3454 | 0 | 78.0639 | 658.2335 | 51.61% | 0 | 0 | 56.25 | 90% | 30.3454
2160 | 0 | 0 | 0 | 0.5 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7931 | 29.7897 | 0 | 76.7931 | 581.4404 | 45.58% | 0 | 0 | 56.25 | 90% | 29.7897
2161 | 0 | 0 | 0 | 0.1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.8036 | 29.7925 | 0 | 76.8036 | 504.6367 | 39.56% | 0 | 0 | 56.25 | 90% | 29.7925
2162 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0841 | 30.7883 | 0 | 79.0841 | 425.5526 | 33.36% | 0 | 0 | 56.25 | 90% | 30.7883
2163 | 0 | 0 | 0 | 0.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6623 | 34.9691 | 0 | 88.6623 | 336.8904 | 26.41% | 0 | 0 | 56.25 | 90% | 34.9691
2164 | 0 | 0 | 0 | 0.4 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.624 | 40.6304 | 0 | 101.624 | 235.2663 | 18.44% | 0 | 0 | 56.25 | 90% | 40.6304
2165 | 0 | 0 | 0 | 0.5 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.9405 | 43.8364 | 0 | 108.9405 | 126.3259 | 9.904% | 0 | 0 | 56.25 | 90% | 43.8364
2166 | 0 | 0 | 0 | 1.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.6158 | 45.4464 | 0 | 112.6158 | 13.71 | 1.075% | 0 | 0 | 56.25 | 90% | 45.4464
2167 | 195 | 67 | 34 | 1.8 | 10.1 | 0 | 0 | 0 | 0 | 1.2827 | 0 | 0 | 1.2827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.71 | 1.075% | 0 | 25 | 28.5817 | 45.73% | 26.2827
2168 | 523 | 272 | 106 | 1.2 | 11.6 | 0 | 0 | 0 | 80.4611 | 13.8322 | 0 | 0 | 13.8322 | 0 | 0 | 0 | 0 | 0 | 80.4611 | 0 | 94.1711 | 7.383% | 0 | 20.178 | 6.25 | 10% | 34.0102
2169 | 218 | 351 | 252 | 1.1 | 13.4 | 0 | 0 | 0 | 0 | 25.8164 | 3.5527e-15 | 0 | 25.8164 | 0 | 0 | 0 | 55.9058 | 20.6522 | 0 | 55.9058 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 46.4686
2170 | 311 | 482 | 266 | 1.5 | 14.8 | 0 | 0 | 0 | 0 | 32.9742 | 2.8579 | 0 | 32.9742 | 0 | 0 | 0 | 38.2653 | 12.9582 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 45.9324
2171 | 821 | 797 | 160 | 2.4 | 16.1 | 0 | 0 | 0 | 221.0137 | 44.6706 | 19.2192 | 0 | 44.6706 | 0 | 0 | 0 | 0 | 0 | 221.0137 | 0 | 221.0137 | 17.33% | 0 | 0 | 6.25 | 10% | 44.6706
2172 | 929 | 916 | 137 | 2.4 | 17.2 | 0 | 0 | 0 | 133.2619 | 43.7069 | 28.2931 | 0 | 43.7069 | 0 | 0 | 0 | 0 | 0 | 133.2619 | 0 | 354.2756 | 27.78% | 0 | 0 | 6.25 | 10% | 43.7069
2173 | 926 | 928 | 139 | 3.8 | 18.1 | 0 | 0 | 0 | 261.5512 | 57.3945 | 14.6055 | 14.4689 | 42.9256 | 0 | 0 | 0 | 0 | 0 | 261.5512 | 0 | 615.8268 | 48.28% | 14.4689 | 0 | 19.3236 | 30.92% | 42.9256
2174 | 918 | 874 | 130 | 5 | 18.5 | 0 | 0 | 0 | 256.6541 | 67.3198 | 4.6802 | 25 | 42.3198 | 0 | 0 | 0 | 0 | 0 | 256.6541 | 0 | 872.4809 | 68.4% | 25 | 0 | 41.9126 | 67.06% | 42.3198
2175 | 527 | 582 | 190 | 6.3 | 18.1 | 0 | 0 | 0 | 134.4346 | 52.2904 | 0 | 10.7868 | 41.5037 | 0 | 0 | 0 | 0 | 0 | 134.4346 | 0 | 1006.9155 | 78.94% | 10.7868 | 0 | 51.6591 | 82.65% | 41.5037
2176 | 545 | 503 | 197 | 4.3 | 18.1 | 0 | 0 | 0 | 134.7782 | 46.9954 | 0 | 5.0809 | 41.9145 | 0 | 0 | 0 | 0 | 0 | 134.7782 | 0 | 1141.6938 | 89.51% | 5.0809 | 0 | 56.25 | 90% | 41.9145
2177 | 587 | 406 | 158 | 2.8 | 18.3 | 0 | 0 | 0 | 133.8165 | 37.2708 | 0 | 0 | 37.2708 | 0 | 0 | 0 | 0 | 0 | 133.8165 | 0 | 1275.5102 | 100% | 0 | 7.3065 | 48.1636 | 77.06% | 44.5773
2178 | 23 | 63 | 56 | 5.1 | 16 | 0 | 0 | 0 | 0 | 3.8625 | 0 | 0 | 3.8625 | 0 | 0 | 0 | 106.9314 | 42.7412 | 0 | 106.9314 | 1168.5788 | 91.62% | 0 | 0 | 48.1636 | 77.06% | 46.6037
2179 | 0 | 7 | 7 | 3 | 14.5 | 0 | 0 | 0 | 0 | 0.038867 | 0 | 0 | 0.038867 | 0 | 0 | 0 | 107.5608 | 43.0859 | 0 | 107.5608 | 1061.0181 | 83.18% | 0 | 0 | 48.1636 | 77.06% | 43.1248
2180 | 0 | 0 | 0 | 1.9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4818 | 39.1584 | 0 | 98.4818 | 962.5362 | 75.46% | 0 | 0 | 48.1636 | 77.06% | 39.1584
2181 | 0 | 0 | 0 | 2.7 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0504 | 36.405 | 0 | 92.0504 | 870.4858 | 68.25% | 0 | 0 | 48.1636 | 77.06% | 36.405
2182 | 0 | 0 | 0 | 3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9338 | 34.192 | 0 | 86.9338 | 783.552 | 61.43% | 0 | 0 | 48.1636 | 77.06% | 34.192
2183 | 0 | 0 | 0 | 2.5 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8062 | 32.8425 | 0 | 83.8062 | 699.7458 | 54.86% | 0 | 0 | 48.1636 | 77.06% | 32.8425
2184 | 0 | 0 | 0 | 1.7 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2356 | 32.1657 | 0 | 82.2356 | 617.5102 | 48.41% | 0 | 0 | 48.1636 | 77.06% | 32.1657
2185 | 0 | 0 | 0 | 1.4 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8643 | 32.0125 | 0 | 81.8643 | 535.6459 | 41.99% | 0 | 0 | 48.1636 | 77.06% | 32.0125
2186 | 0 | 0 | 0 | 0.9 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5621 | 32.7575 | 0 | 83.5621 | 452.0838 | 35.44% | 0 | 0 | 48.1636 | 77.06% | 32.7575
2187 | 0 | 0 | 0 | 1.1 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6273 | 36.2797 | 0 | 91.6273 | 360.4565 | 28.26% | 0 | 0 | 48.1636 | 77.06% | 36.2797
2188 | 0 | 0 | 0 | 0.8 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6809 | 41.551 | 0 | 103.6809 | 256.7757 | 20.13% | 0 | 0 | 48.1636 | 77.06% | 41.551
2189 | 0 | 0 | 0 | 1.1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.0323 | 46.9468 | 0 | 116.0323 | 140.7433 | 11.03% | 2.538 | 0 | 50.4568 | 80.73% | 44.4088
2190 | 0 | 0 | 0 | 1.4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9791 | 0 | 127.551 | 13.1923 | 1.034% | 6.4115 | 0 | 56.25 | 90% | 45.5675
2191 | 134 | 73 | 31 | 1.2 | 8.4 | 0 | 0 | 0 | 0 | 1.1438 | 0 | 0 | 1.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1923 | 1.034% | 0 | 25 | 28.5817 | 45.73% | 26.1438
2192 | 570 | 283 | 60 | 0.5 | 11.4 | 0 | 0 | 0 | 90.7937 | 11.3901 | 0 | 0 | 11.3901 | 0 | 0 | 0 | 0 | 0 | 90.7937 | 0 | 103.986 | 8.152% | 0 | 20.178 | 6.25 | 10% | 31.5681
2193 | 768 | 500 | 119 | 1 | 14.2 | 0 | 0 | 0 | 0 | 33.2672 | 2.3417 | 0 | 33.2672 | 0 | 0 | 0 | 38.2653 | 12.9661 | 0 | 38.2653 | 65.7207 | 5.152% | 0 | 0 | 6.25 | 10% | 46.2333
2194 | 663 | 596 | 158 | 1.8 | 16.1 | 0 | 0 | 0 | 0 | 32.7802 | 13.4675 | 0 | 32.7802 | 0 | 0 | 0 | 38.2653 | 12.9391 | 0 | 38.2653 | 27.4554 | 2.152% | 0 | 0 | 6.25 | 10% | 45.7193
2195 | 868 | 810 | 141 | 2.9 | 17.9 | 0 | 0 | 0 | 234.5611 | 44.1916 | 20.7821 | 0 | 44.1916 | 0 | 0 | 0 | 0 | 0 | 234.5611 | 0 | 262.0165 | 20.54% | 0 | 0 | 6.25 | 10% | 44.1916
2196 | 968 | 942 | 132 | 3.1 | 19.6 | 0 | 0 | 0 | 271.2164 | 43.4813 | 28.5187 | 0 | 43.4813 | 0 | 0 | 0 | 0 | 0 | 271.2164 | 0 | 533.2329 | 41.81% | 0 | 0 | 6.25 | 10% | 43.4813
2197 | 910 | 957 | 183 | 2.8 | 20.7 | 0 | 0 | 0 | 257.5682 | 67.9061 | 4.0939 | 25 | 42.9061 | 0 | 0 | 0 | 0 | 0 | 257.5682 | 0 | 790.8011 | 62% | 25 | 0 | 28.839 | 46.14% | 42.9061
2198 | 938 | 914 | 153 | 2.7 | 21.6 | 0 | 0 | 0 | 264.5862 | 67.3852 | 4.6148 | 25 | 42.3852 | 0 | 0 | 0 | 0 | 0 | 264.5862 | 0 | 1055.3872 | 82.74% | 25 | 0 | 51.428 | 82.28% | 42.3852
2199 | 645 | 754 | 282 | 4.8 | 21.9 | 0 | 0 | 0 | 170.7211 | 47.0033 | 17.604 | 5.3367 | 41.6666 | 0 | 0 | 0 | 0 | 0 | 170.7211 | 0 | 1226.1084 | 96.13% | 5.3367 | 0 | 56.25 | 90% | 41.6666
2200 | 402 | 490 | 252 | 5.8 | 20.7 | 0 | 0 | 0 | 49.4018 | 42.0168 | 0 | 0 | 42.0168 | 0 | 0 | 0 | 0 | 0 | 49.4018 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 42.0168
2201 | 247 | 271 | 171 | 5.2 | 19.7 | 0 | 0 | 0 | 0 | 23.3039 | 0 | 0 | 23.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 21.2289 | 32.7552 | 52.41% | 44.5328
2202 | 206 | 130 | 76 | 3.9 | 18.9 | 0 | 0 | 0 | 0 | 9.8032 | 0 | 0 | 9.8032 | 0 | 0 | 0 | 93.582 | 36.7991 | 0 | 93.582 | 1181.9282 | 92.66% | 0 | 0 | 32.7552 | 52.41% | 46.6023
2203 | 1 | 10 | 10 | 2.5 | 17.1 | 0 | 0 | 0 | 0 | 0.20938 | 0 | 0 | 0.20938 | 0 | 0 | 0 | 107.5099 | 42.9321 | 0 | 107.5099 | 1074.4183 | 84.23% | 0 | 0 | 32.7552 | 52.41% | 43.1415
2204 | 0 | 0 | 0 | 1.8 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2998 | 39.4244 | 0 | 99.2998 | 975.1185 | 76.45% | 0 | 0 | 32.7552 | 52.41% | 39.4244
2205 | 0 | 0 | 0 | 1.1 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.211 | 36.8326 | 0 | 93.211 | 881.9075 | 69.14% | 0 | 0 | 32.7552 | 52.41% | 36.8326
2206 | 0 | 0 | 0 | 0.9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0077 | 34.6029 | 0 | 88.0077 | 793.8998 | 62.24% | 0 | 0 | 32.7552 | 52.41% | 34.6029
2207 | 0 | 0 | 0 | 1.5 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8168 | 33.2213 | 0 | 84.8168 | 709.083 | 55.59% | 0 | 0 | 32.7552 | 52.41% | 33.2213
2208 | 0 | 0 | 0 | 0.9 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.431 | 32.6615 | 0 | 83.431 | 625.6519 | 49.05% | 0 | 0 | 32.7552 | 52.41% | 32.6615
2209 | 0 | 0 | 0 | 0.5 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9749 | 32.4651 | 0 | 82.9749 | 542.6771 | 42.55% | 0 | 0 | 32.7552 | 52.41% | 32.4651
2210 | 0 | 0 | 0 | 0.8 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2679 | 36.0875 | 0 | 91.2679 | 451.4091 | 35.39% | 2.9149 | 0 | 35.3891 | 56.62% | 33.1726
2211 | 0 | 0 | 0 | 0.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2996 | 36.5568 | 0 | 92.2996 | 359.1096 | 28.15% | 0 | 0 | 35.3891 | 56.62% | 36.5568
2212 | 0 | 0 | 0 | 1.5 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0076 | 41.6541 | 0 | 104.0076 | 255.102 | 20% | 0 | 0 | 35.3891 | 56.62% | 41.6541
2213 | 0 | 0 | 0 | 2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9195 | 0 | 127.551 | 127.551 | 10% | 7.4035 | 0 | 42.0785 | 67.33% | 44.5161
2214 | 0 | 1 | 1 | 2 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9309 | 0 | 127.551 | 0 | 0% | 6.2268 | 0 | 47.7048 | 76.33% | 45.704
2215 | 368 | 82 | 30 | 1.6 | 11.1 | 0 | 0 | 0 | 0 | 1.0793 | 0 | 0 | 1.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 20.0365 | 32.06% | 26.0793
2216 | 727 | 289 | 56 | 0.6 | 15.1 | 0 | 0 | 0 | 121.4149 | 12.9703 | 0 | 0 | 12.9703 | 0 | 0 | 0 | 0 | 0 | 121.4149 | 0 | 121.4149 | 9.519% | 0 | 12.4569 | 6.25 | 10% | 25.4273
2217 | 874 | 502 | 63 | 0.7 | 16.9 | 0 | 0 | 0 | 0 | 33.2668 | 1.1983 | 0 | 33.2668 | 0 | 0 | 0 | 38.2653 | 12.926 | 0 | 38.2653 | 83.1496 | 6.519% | 0 | 0 | 6.25 | 10% | 46.1929
2218 | 948 | 690 | 67 | 1.7 | 19.1 | 0 | 0 | 0 | 0 | 32.9253 | 19.1585 | 0 | 32.9253 | 0 | 0 | 0 | 38.2653 | 12.8846 | 0 | 38.2653 | 44.8843 | 3.519% | 0 | 0 | 6.25 | 10% | 45.8099
2219 | 976 | 825 | 72 | 2.4 | 20.2 | 0 | 0 | 0 | 266.4259 | 44.3406 | 20.3951 | 0 | 44.3406 | 0 | 0 | 0 | 0 | 0 | 266.4259 | 0 | 311.3102 | 24.41% | 0 | 0 | 6.25 | 10% | 44.3406
2220 | 993 | 907 | 75 | 4.8 | 21.1 | 0 | 0 | 0 | 186.2262 | 43.3002 | 28.6998 | 0 | 43.3002 | 0 | 0 | 0 | 0 | 0 | 186.2262 | 0 | 497.5364 | 39.01% | 0 | 0 | 6.25 | 10% | 43.3002
2221 | 981 | 918 | 83 | 6.7 | 21 | 0 | 0 | 0 | 275.7759 | 42.8281 | 29.1719 | 0 | 42.8281 | 0 | 0 | 0 | 0 | 0 | 275.7759 | 0 | 773.3123 | 60.63% | 0 | 0 | 6.25 | 10% | 42.8281
2222 | 932 | 857 | 100 | 4.8 | 21.3 | 0 | 0 | 0 | 261.1738 | 48.9796 | 23.0204 | 6.5276 | 42.4521 | 0 | 0 | 0 | 0 | 0 | 261.1738 | 0 | 1034.4861 | 81.1% | 6.5276 | 0 | 12.148 | 19.44% | 42.4521
2223 | 858 | 735 | 117 | 5.3 | 21.9 | 0 | 0 | 0 | 232.994 | 65.8549 | 0 | 23.8638 | 41.9911 | 0 | 0 | 0 | 0 | 0 | 232.994 | 0 | 1267.4801 | 99.37% | 23.8638 | 0 | 33.7104 | 53.94% | 41.9911
2224 | 838 | 581 | 92 | 6.2 | 22.4 | 0 | 0 | 0 | 0 | 54.633 | 0 | 24.9453 | 29.6877 | 0 | 0 | 0 | 38.2653 | 12.8076 | 0 | 38.2653 | 1229.2148 | 96.37% | 24.9453 | 0 | 56.25 | 90% | 42.4953
2225 | 742 | 378 | 72 | 5.8 | 22.6 | 0 | 0 | 0 | 0 | 31.8307 | 5.5556 | 0 | 31.8307 | 0 | 0 | 0 | 38.2653 | 12.8024 | 0 | 38.2653 | 1190.9495 | 93.37% | 0 | 0 | 56.25 | 90% | 44.633
2226 | 484 | 159 | 48 | 5.5 | 21.5 | 0 | 0 | 0 | 84.5607 | 14.3061 | 0 | 0 | 14.3061 | 0 | 0 | 0 | 0 | 0 | 84.5607 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 39.3061
2227 | 78 | 15 | 9 | 5 | 19.9 | 0 | 0 | 0 | 0 | 0.30708 | 0 | 0 | 0.30708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 20.178 | 6.25 | 10% | 20.4851
2228 | 0 | 0 | 0 | 5.4 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 0
2229 | 0 | 0 | 0 | 4.2 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 0
2230 | 0 | 0 | 0 | 3.2 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 0
2231 | 0 | 0 | 0 | 2.5 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 0
2232 | 0 | 0 | 0 | 2.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 0
2233 | 0 | 0 | 0 | 1.5 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 0
2234 | 0 | 0 | 0 | 1.6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 0
2235 | 0 | 0 | 0 | 1.5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 0
2236 | 0 | 0 | 0 | 1.7 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8017 | 42.005 | 0 | 104.8017 | 1170.7085 | 91.78% | 0 | 0 | 6.25 | 10% | 42.005
2237 | 0 | 0 | 0 | 3.5 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.8076 | 45.0592 | 0 | 111.8076 | 1058.9009 | 83.02% | 0 | 0 | 6.25 | 10% | 45.0592
2238 | 0 | 1 | 1 | 2.8 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.4093 | 46.6525 | 0 | 115.4093 | 943.4916 | 73.97% | 0 | 0 | 6.25 | 10% | 46.6525
2239 | 41 | 47 | 38 | 3.3 | 10.5 | 0 | 0 | 0 | 0 | 1.4798 | 0 | 0 | 1.4798 | 0 | 0 | 0 | 112.5025 | 45.3718 | 0 | 112.5025 | 830.989 | 65.15% | 0 | 0 | 6.25 | 10% | 46.8516
2240 | 265 | 226 | 141 | 4.4 | 11.9 | 0 | 0 | 0 | 0 | 13.1563 | 0 | 0 | 13.1563 | 0 | 0 | 0 | 85.2896 | 33.4781 | 0 | 85.2896 | 745.6994 | 58.46% | 0 | 0 | 6.25 | 10% | 46.6343
2241 | 122 | 312 | 252 | 4.8 | 12.6 | 0 | 0 | 0 | 0 | 22.4825 | 0 | 0 | 22.4825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745.6994 | 58.46% | 0 | 0 | 6.25 | 10% | 22.4825
2242 | 24 | 331 | 310 | 4.4 | 13.1 | 0 | 0 | 0 | 0 | 22.684 | 0 | 0 | 22.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745.6994 | 58.46% | 0 | 0 | 6.25 | 10% | 22.684
2243 | 450 | 713 | 350 | 5.8 | 14 | 0 | 0 | 0 | 110.4333 | 56.0091 | 0 | 11.8941 | 44.115 | 0 | 0 | 0 | 0 | 0 | 110.4333 | 0 | 856.1327 | 67.12% | 11.8941 | 0 | 16.9971 | 27.2% | 44.115
2244 | 112 | 595 | 489 | 5.1 | 14.2 | 0 | 0 | 0 | 0 | 44.2634 | 0 | 1.0899 | 43.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856.1327 | 67.12% | 1.0899 | 0 | 17.9819 | 28.77% | 43.1735
2245 | 38 | 404 | 364 | 5 | 14.2 | 0 | 0 | 0 | 0 | 29.178 | 0 | 0 | 29.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856.1327 | 67.12% | 0 | 0 | 17.9819 | 28.77% | 29.178
2246 | 1 | 155 | 152 | 4.3 | 13.6 | 0 | 0 | 0 | 0 | 9.7099 | 0 | 0 | 9.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856.1327 | 67.12% | 0 | 0 | 17.9819 | 28.77% | 9.7099
2247 | 0 | 91 | 90 | 4.8 | 13.2 | 0 | 0 | 0 | 0 | 5.4301 | 0 | 0 | 5.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856.1327 | 67.12% | 0 | 0 | 17.9819 | 28.77% | 5.4301
2248 | 0 | 47 | 46 | 4.3 | 12.7 | 0 | 0 | 0 | 0 | 2.5576 | 0 | 0 | 2.5576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856.1327 | 67.12% | 0 | 0 | 17.9819 | 28.77% | 2.5576
2249 | 0 | 23 | 23 | 3.1 | 12.3 | 0 | 0 | 0 | 0 | 1.0846 | 0 | 0 | 1.0846 | 0 | 0 | 0 | 109.3887 | 43.9649 | 0 | 109.3887 | 746.744 | 58.54% | 0 | 0 | 17.9819 | 28.77% | 45.0495
2250 | 0 | 7 | 7 | 1.6 | 12.1 | 0 | 0 | 0 | 0 | 0.076462 | 0 | 0 | 0.076462 | 0 | 0 | 0 | 116.0651 | 46.8796 | 0 | 116.0651 | 630.6789 | 49.45% | 0 | 0 | 17.9819 | 28.77% | 46.9561
2251 | 0 | 0 | 0 | 2.6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.4065 | 43.1108 | 0 | 107.4065 | 523.2724 | 41.02% | 0 | 0 | 17.9819 | 28.77% | 43.1108
2252 | 0 | 0 | 0 | 3 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.2724 | 41.02% | 0 | 0 | 17.9819 | 28.77% | 0
2253 | 0 | 0 | 0 | 2.3 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.2724 | 41.02% | 0 | 0 | 17.9819 | 28.77% | 0
2254 | 0 | 0 | 0 | 2.4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 523.2724 | 41.02% | 0 | 0 | 17.9819 | 28.77% | 0
2255 | 0 | 0 | 0 | 2.5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.2724 | 41.02% | 0 | 0 | 17.9819 | 28.77% | 0
2256 | 0 | 0 | 0 | 2.9 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.2724 | 41.02% | 0 | 0 | 17.9819 | 28.77% | 0
2257 | 0 | 0 | 0 | 1.4 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.2724 | 41.02% | 0 | 0 | 17.9819 | 28.77% | 0
2258 | 0 | 0 | 0 | 1.1 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.2724 | 41.02% | 0 | 0 | 17.9819 | 28.77% | 0
2259 | 0 | 0 | 0 | 1.1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.2724 | 41.02% | 0 | 0 | 17.9819 | 28.77% | 0
2260 | 0 | 0 | 0 | 0.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9882 | 31.2247 | 0 | 79.9882 | 443.2842 | 34.75% | 0 | 0 | 17.9819 | 28.77% | 31.2247
2261 | 0 | 0 | 0 | 0.6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.4227 | 45.3767 | 0 | 112.4227 | 330.8615 | 25.94% | 0 | 0 | 17.9819 | 28.77% | 45.3767
2262 | 1 | 1 | 1 | 0.4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2082 | 47.0327 | 0 | 116.2082 | 214.6533 | 16.83% | 0 | 0 | 17.9819 | 28.77% | 47.0327
2263 | 64 | 58 | 49 | 0.4 | 7.9 | 0 | 0 | 0 | 0 | 2.0447 | 0 | 0 | 2.0447 | 0 | 0 | 0 | 113.4285 | 45.8166 | 0 | 113.4285 | 101.2248 | 7.936% | 0 | 0 | 17.9819 | 28.77% | 47.8613
2264 | 1 | 119 | 117 | 1.3 | 9.9 | 0 | 0 | 0 | 0 | 7.5377 | 0 | 0 | 7.5377 | 0 | 0 | 0 | 101.2248 | 40.4657 | 0 | 101.2248 | 0 | 0% | 0 | 0 | 17.9819 | 28.77% | 48.0034
2265 | 582 | 412 | 98 | 2.5 | 12.1 | 0 | 0 | 0 | 125.9376 | 28.6045 | 0 | 0 | 28.6045 | 0 | 0 | 0 | 0 | 0 | 125.9376 | 0 | 125.9376 | 9.874% | 0 | 10.6005 | 6.25 | 10% | 39.205
2266 | 804 | 694 | 151 | 5.8 | 14.7 | 0 | 0 | 0 | 201.0536 | 54.3856 | 0 | 6.7749 | 47.6106 | 0 | 0 | 0 | 0 | 0 | 201.0536 | 0 | 326.9912 | 25.64% | 6.7749 | 0 | 12.3716 | 19.79% | 47.6106
2267 | 722 | 767 | 204 | 8.2 | 15.2 | 0 | 0 | 0 | 187.5822 | 63.7717 | 0 | 17.9577 | 45.8141 | 0 | 0 | 0 | 0 | 0 | 187.5822 | 0 | 514.5734 | 40.34% | 17.9577 | 0 | 28.5974 | 45.76% | 45.8141
2268 | 458 | 794 | 392 | 9.6 | 14 | 0 | 0 | 0 | 112.9685 | 64.3171 | 0 | 19.5518 | 44.7654 | 0 | 0 | 0 | 0 | 0 | 112.9685 | 0 | 627.5419 | 49.2% | 19.5518 | 0 | 46.2637 | 74.02% | 44.7654
2269 | 75 | 360 | 291 | 8.1 | 13.8 | 0 | 0 | 0 | 0 | 26.5663 | 0 | 0 | 26.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627.5419 | 49.2% | 0 | 17.571 | 26.8173 | 42.91% | 44.1372
2270 | 1 | 230 | 226 | 7.4 | 12.9 | 0 | 0 | 0 | 0 | 14.9934 | 0 | 0 | 14.9934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627.5419 | 49.2% | 0 | 18.5838 | 6.25 | 10% | 33.5772
2271 | 1 | 141 | 139 | 6.5 | 10.1 | 0 | 0 | 0 | 0 | 8.9559 | 0 | 0 | 8.9559 | 0 | 0 | 0 | 94.4741 | 37.518 | 0 | 94.4741 | 533.0678 | 41.79% | 3.1667 | 0 | 9.1113 | 14.58% | 43.3072
2272 | 3 | 209 | 205 | 4.4 | 10.7 | 0 | 0 | 0 | 0 | 13.8062 | 0 | 0 | 13.8062 | 0 | 0 | 0 | 76.4694 | 29.657 | 0 | 76.4694 | 456.5985 | 35.8% | 0 | 0 | 9.1113 | 14.58% | 43.4632
2273 | 145 | 266 | 198 | 4.5 | 12 | 0 | 0 | 0 | 0 | 20.7172 | 0 | 0 | 20.7172 | 0 | 0 | 0 | 64.0486 | 24.2223 | 0 | 64.0486 | 392.5499 | 30.78% | 0 | 0 | 9.1113 | 14.58% | 44.9394
2274 | 214 | 137 | 80 | 5 | 12.6 | 0 | 0 | 0 | 0 | 10.3951 | 0 | 0 | 10.3951 | 0 | 0 | 0 | 91.2571 | 36.0595 | 0 | 91.2571 | 301.2928 | 23.62% | 0 | 0 | 9.1113 | 14.58% | 46.4547
2275 | 96 | 17 | 9 | 7.4 | 11.4 | 0 | 0 | 0 | 0 | 0.33898 | 0 | 0 | 0.33898 | 0 | 0 | 0 | 106.4075 | 42.6925 | 0 | 106.4075 | 194.8854 | 15.28% | 0 | 0 | 9.1113 | 14.58% | 43.0314
2276 | 0 | 0 | 0 | 8.6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.332 | 40.065 | 0 | 100.332 | 94.5534 | 7.413% | 0 | 0 | 9.1113 | 14.58% | 40.065
2277 | 0 | 0 | 0 | 5.6 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5534 | 37.5526 | 0 | 94.5534 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 37.5526
2278 | 0 | 0 | 0 | 4.6 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 0
2279 | 0 | 0 | 0 | 2.8 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 0
2280 | 0 | 0 | 0 | 1.6 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 0
2281 | 0 | 0 | 0 | 3.1 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 0
2282 | 0 | 0 | 0 | 6.1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 0
2283 | 0 | 0 | 0 | 5.9 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 0
2284 | 0 | 0 | 0 | 6.9 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 0
2285 | 0 | 0 | 0 | 6.6 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 0
2286 | 3 | 1 | 1 | 7.4 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 9.1113 | 14.58% | 0
2287 | 462 | 101 | 31 | 7.6 | 9.4 | 0 | 0 | 0 | 0 | 1.141 | 0 | 0 | 1.141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 2.5853 | 6.25 | 10% | 3.7264
2288 | 783 | 322 | 59 | 8.5 | 11.1 | 0 | 0 | 0 | 129.2595 | 14.604 | 0 | 0 | 14.604 | 0 | 0 | 0 | 0 | 0 | 129.2595 | 0 | 129.2595 | 10.13% | 0 | 0 | 6.25 | 10% | 14.604
2289 | 903 | 527 | 60 | 9.9 | 12.5 | 0 | 0 | 0 | 199.316 | 37.5074 | 0 | 0 | 37.5074 | 0 | 0 | 0 | 0 | 0 | 199.316 | 0 | 328.5755 | 25.76% | 0 | 0 | 6.25 | 10% | 37.5074
2290 | 961 | 710 | 65 | 8.8 | 14 | 0 | 0 | 0 | 241.9226 | 42.0426 | 13.9146 | 0 | 42.0426 | 0 | 0 | 0 | 0 | 0 | 241.9226 | 0 | 570.4981 | 44.73% | 0 | 0 | 6.25 | 10% | 42.0426
2291 | 896 | 813 | 109 | 6.9 | 15.3 | 0 | 0 | 0 | 239.4648 | 46.3423 | 19.9093 | 5.2327 | 41.1095 | 0 | 0 | 0 | 0 | 0 | 239.4648 | 0 | 809.963 | 63.5% | 5.2327 | 0 | 10.9781 | 17.56% | 41.1095
2292 | 677 | 774 | 196 | 4.9 | 15.7 | 0 | 0 | 0 | 182.8208 | 64.1974 | 0.75481 | 25 | 39.1974 | 0 | 0 | 0 | 0 | 0 | 182.8208 | 0 | 992.7838 | 77.83% | 25 | 0 | 33.5671 | 53.71% | 39.1974
2293 | 303 | 511 | 244 | 6.4 | 15.9 | 0 | 0 | 0 | 70.4329 | 43.6292 | 0 | 5.7855 | 37.8437 | 0 | 0 | 0 | 0 | 0 | 70.4329 | 0 | 1063.2167 | 83.36% | 5.7855 | 0 | 38.7946 | 62.07% | 37.8437
2294 | 552 | 619 | 170 | 8.9 | 15.7 | 0 | 0 | 0 | 142.9536 | 56.4881 | 0 | 19.3184 | 37.1696 | 0 | 0 | 0 | 0 | 0 | 142.9536 | 0 | 1206.1703 | 94.56% | 19.3184 | 0 | 56.25 | 90% | 37.1696
2295 | 193 | 287 | 137 | 7.5 | 14.8 | 0 | 0 | 0 | 34.6078 | 24.9606 | 0 | 0 | 24.9606 | 0 | 0 | 0 | 0 | 0 | 34.6078 | 0 | 1240.778 | 97.28% | 0 | 2.1694 | 53.8491 | 86.16% | 27.13
2296 | 35 | 259 | 233 | 8.1 | 13.2 | 0 | 0 | 0 | 0 | 18.3762 | 0 | 0 | 18.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.778 | 97.28% | 0 | 19.324 | 32.4626 | 51.94% | 37.7002
2297 | 6 | 71 | 68 | 6.9 | 11.2 | 0 | 0 | 0 | 0 | 4.3408 | 0 | 0 | 4.3408 | 0 | 0 | 0 | 89.1527 | 35.1768 | 0 | 89.1527 | 1151.6254 | 90.29% | 0 | 0 | 32.4626 | 51.94% | 39.5177
2298 | 70 | 67 | 54 | 7.6 | 9.8 | 0 | 0 | 0 | 0 | 5.0375 | 0 | 0 | 5.0375 | 0 | 0 | 0 | 93.4657 | 37.0831 | 0 | 93.4657 | 1058.1597 | 82.96% | 0 | 0 | 32.4626 | 51.94% | 42.1206
2299 | 5 | 11 | 10 | 5 | 9.2 | 0 | 0 | 0 | 0 | 0.25861 | 0 | 0 | 0.25861 | 0 | 0 | 0 | 99.4808 | 39.7159 | 0 | 99.4808 | 958.6789 | 75.16% | 0 | 0 | 32.4626 | 51.94% | 39.9745
2300 | 0 | 0 | 0 | 7.7 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5469 | 37.9969 | 0 | 95.5469 | 863.132 | 67.67% | 0 | 0 | 32.4626 | 51.94% | 37.9969
2301 | 0 | 0 | 0 | 6.8 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6927 | 35.0137 | 0 | 88.6927 | 774.4393 | 60.72% | 0 | 0 | 32.4626 | 51.94% | 35.0137
2302 | 0 | 0 | 0 | 6.6 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0049 | 32.5319 | 0 | 83.0049 | 691.4344 | 54.21% | 0 | 0 | 32.4626 | 51.94% | 32.5319
2303 | 0 | 0 | 0 | 7.8 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6022 | 30.6142 | 0 | 78.6022 | 612.8322 | 48.05% | 0 | 0 | 32.4626 | 51.94% | 30.6142
2304 | 0 | 0 | 0 | 8.1 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1703 | 29.546 | 0 | 76.1703 | 536.6619 | 42.07% | 0 | 0 | 32.4626 | 51.94% | 29.546
2305 | 0 | 0 | 0 | 7.5 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4224 | 18.3156 | 0 | 50.4224 | 486.2394 | 38.12% | 0 | 0 | 32.4626 | 51.94% | 18.3156
2306 | 0 | 0 | 0 | 6.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.9476 | 29.0154 | 0 | 74.9476 | 411.2919 | 32.25% | 0 | 0 | 32.4626 | 51.94% | 29.0154
2307 | 0 | 0 | 0 | 8.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1707 | 29.5418 | 0 | 76.1707 | 335.1211 | 26.27% | 0 | 0 | 32.4626 | 51.94% | 29.5418
2308 | 0 | 0 | 0 | 7.9 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0299 | 30.3552 | 0 | 78.0299 | 257.0912 | 20.16% | 0 | 0 | 32.4626 | 51.94% | 30.3552
2309 | 0 | 0 | 0 | 8.6 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8236 | 31.1365 | 0 | 79.8236 | 177.2676 | 13.9% | 0 | 0 | 32.4626 | 51.94% | 31.1365
2310 | 9 | 1 | 1 | 9.7 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5663 | 34.0778 | 0 | 86.5663 | 90.7013 | 7.111% | 0 | 0 | 32.4626 | 51.94% | 34.0778
2311 | 475 | 101 | 27 | 9.7 | 10 | 0 | 0 | 0 | 0 | 0.94022 | 0 | 0 | 0.94022 | 0 | 0 | 0 | 90.7013 | 35.8742 | 0 | 90.7013 | 0 | 0% | 0 | 0 | 32.4626 | 51.94% | 36.8145
2312 | 774 | 319 | 57 | 10.1 | 11.3 | 0 | 0 | 0 | 0 | 14.4181 | 0 | 0 | 14.4181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 23.6846 | 6.25 | 10% | 38.1027
2313 | 722 | 573 | 194 | 10.8 | 12.8 | 0 | 0 | 0 | 0 | 38.4885 | 2.4769 | 0 | 38.4885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.4885
2314 | 891 | 748 | 141 | 11.5 | 14 | 0 | 0 | 0 | 0 | 38.7016 | 20.3295 | 0 | 38.7016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.7016
2315 | 971 | 877 | 110 | 11.6 | 15.3 | 0 | 0 | 0 | 257.1114 | 38.4147 | 33.4425 | 0 | 38.4147 | 0 | 0 | 0 | 0 | 0 | 257.1114 | 0 | 257.1114 | 20.16% | 0 | 0 | 6.25 | 10% | 38.4147
2316 | 970 | 956 | 125 | 12 | 16.1 | 0 | 0 | 0 | 264.1699 | 36.4426 | 35.5574 | 0 | 36.4426 | 0 | 0 | 0 | 0 | 0 | 264.1699 | 0 | 521.2812 | 40.87% | 0 | 0 | 6.25 | 10% | 36.4426
2317 | 958 | 985 | 152 | 10.8 | 17 | 0 | 0 | 0 | 265.3419 | 35.3062 | 36.6938 | 0 | 35.3062 | 0 | 0 | 0 | 0 | 0 | 265.3419 | 0 | 786.6231 | 61.67% | 0 | 0 | 6.25 | 10% | 35.3062
2318 | 971 | 990 | 186 | 9.8 | 17.6 | 0 | 0 | 0 | 14.7874 | 40.4075 | 31.5925 | 5.3367 | 35.0708 | 0 | 0 | 0 | 0 | 0 | 14.7874 | 0 | 801.4105 | 62.83% | 5.3367 | 0 | 11.072 | 17.72% | 35.0708
2319 | 820 | 936 | 331 | 9.6 | 18.3 | 0 | 0 | 0 | 217.69 | 60.5388 | 11.4612 | 25 | 35.5388 | 0 | 0 | 0 | 0 | 0 | 217.69 | 0 | 1019.1006 | 79.9% | 25 | 0 | 33.661 | 53.86% | 35.5388
2320 | 839 | 797 | 293 | 8.3 | 18.9 | 0 | 0 | 0 | 214.556 | 61.7128 | 8.0749 | 25 | 36.7128 | 0 | 0 | 0 | 0 | 0 | 214.556 | 0 | 1233.6565 | 96.72% | 25 | 0 | 56.25 | 90% | 36.7128
2321 | 455 | 399 | 202 | 9 | 18 | 0 | 0 | 0 | 0 | 35.0804 | 0 | 0 | 35.0804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.6565 | 96.72% | 0 | 0 | 56.25 | 90% | 35.0804
2322 | 296 | 175 | 95 | 7.6 | 16.9 | 0 | 0 | 0 | 41.8537 | 13.4519 | 0 | 0 | 13.4519 | 0 | 0 | 0 | 0 | 0 | 41.8537 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 38.4519
2323 | 14 | 19 | 18 | 4.6 | 16 | 0 | 0 | 0 | 0 | 0.74484 | 0 | 0 | 0.74484 | 0 | 0 | 0 | 100.1397 | 39.7937 | 0 | 100.1397 | 1175.3705 | 92.15% | 0 | 0 | 28.5817 | 45.73% | 40.5385
2324 | 0 | 0 | 0 | 3.6 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3803 | 37.7545 | 0 | 95.3803 | 1079.9901 | 84.67% | 0 | 0 | 28.5817 | 45.73% | 37.7545
2325 | 0 | 0 | 0 | 1.6 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3181 | 34.699 | 0 | 88.3181 | 991.672 | 77.75% | 0 | 0 | 28.5817 | 45.73% | 34.699
2326 | 0 | 0 | 0 | 0.5 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5993 | 32.2381 | 0 | 82.5993 | 909.0727 | 71.27% | 0 | 0 | 28.5817 | 45.73% | 32.2381
2327 | 0 | 0 | 0 | 0.8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3619 | 30.8426 | 0 | 79.3619 | 829.7108 | 65.05% | 0 | 0 | 28.5817 | 45.73% | 30.8426
2328 | 0 | 0 | 0 | 0.9 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3488 | 36.0789 | 0 | 91.3488 | 738.362 | 57.89% | 7.4934 | 0 | 35.3524 | 56.56% | 28.5855
2329 | 0 | 0 | 0 | 1.2 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.9811 | 0 | 38.2653 | 700.0967 | 54.89% | 0 | 0 | 35.3524 | 56.56% | 12.9811
2330 | 0 | 0 | 0 | 1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5287 | 31.4038 | 0 | 80.5287 | 619.568 | 48.57% | 0 | 0 | 35.3524 | 56.56% | 31.4038
2331 | 0 | 0 | 0 | 1.4 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2441 | 35.646 | 0 | 90.2441 | 529.3239 | 41.5% | 0 | 0 | 35.3524 | 56.56% | 35.646
2332 | 0 | 0 | 0 | 1.2 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9295 | 41.6151 | 0 | 103.9295 | 425.3945 | 33.35% | 0 | 0 | 35.3524 | 56.56% | 41.6151
2333 | 0 | 0 | 0 | 0.7 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.9609 | 45.1261 | 0 | 111.9609 | 313.4335 | 24.57% | 0 | 0 | 35.3524 | 56.56% | 45.1261
2334 | 0 | 1 | 1 | 0.8 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.171 | 46.9561 | 0 | 116.171 | 197.2625 | 15.47% | 0 | 0 | 35.3524 | 56.56% | 46.9561
2335 | 35 | 65 | 58 | 1.3 | 12 | 0 | 0 | 0 | 0 | 2.4587 | 0 | 0 | 2.4587 | 0 | 0 | 0 | 112.4689 | 45.3162 | 0 | 112.4689 | 84.7936 | 6.648% | 0 | 0 | 35.3524 | 56.56% | 47.775
2336 | 208 | 263 | 182 | 1.3 | 15 | 0 | 0 | 0 | 0 | 14.715 | 0 | 0 | 14.715 | 0 | 0 | 0 | 84.7936 | 33.1714 | 0 | 84.7936 | 0 | 0% | 0 | 0 | 35.3524 | 56.56% | 47.8864
2337 | 167 | 425 | 333 | 4.5 | 17.7 | 0 | 0 | 0 | 0 | 29.6645 | 0 | 0 | 29.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 18.0241 | 15.4045 | 24.65% | 47.6886
2338 | 228 | 537 | 369 | 6.9 | 18.3 | 0 | 0 | 0 | 0 | 38.8655 | 0 | 0 | 38.8655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 8.2717 | 6.25 | 10% | 47.1371
2339 | 795 | 814 | 180 | 5.5 | 19.4 | 0 | 0 | 0 | 0 | 45.5258 | 19.1881 | 0 | 45.5258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 45.5258
2340 | 886 | 919 | 157 | 4.2 | 20.4 | 0 | 0 | 0 | 228.6267 | 44.4854 | 27.5146 | 0 | 44.4854 | 0 | 0 | 0 | 0 | 0 | 228.6267 | 0 | 228.6267 | 17.92% | 0 | 0 | 6.25 | 10% | 44.4854
2341 | 935 | 1028 | 213 | 4.3 | 21.4 | 0 | 0 | 0 | 264.4554 | 43.7821 | 28.2179 | 0 | 43.7821 | 0 | 0 | 0 | 0 | 0 | 264.4554 | 0 | 493.082 | 38.66% | 0 | 0 | 6.25 | 10% | 43.7821
2342 | 778 | 875 | 224 | 3.7 | 21.7 | 0 | 0 | 0 | 215.8294 | 68.0718 | 3.9282 | 25 | 43.0718 | 0 | 0 | 0 | 0 | 0 | 215.8294 | 0 | 708.9114 | 55.58% | 25 | 0 | 28.839 | 46.14% | 43.0718
2343 | 630 | 689 | 223 | 6.1 | 21.5 | 0 | 0 | 0 | 165.1201 | 59.9047 | 0 | 17.4527 | 42.4521 | 0 | 0 | 0 | 0 | 0 | 165.1201 | 0 | 874.0315 | 68.52% | 17.4527 | 0 | 44.6085 | 71.37% | 42.4521
2344 | 897 | 623 | 87 | 7.1 | 21.7 | 0 | 0 | 0 | 232.2815 | 55.8054 | 1.4115 | 12.884 | 42.9214 | 0 | 0 | 0 | 0 | 0 | 232.2815 | 0 | 1106.313 | 86.73% | 12.884 | 0 | 56.25 | 90% | 42.9214
2345 | 736 | 402 | 80 | 8.2 | 21.7 | 0 | 0 | 0 | 169.1972 | 37.5713 | 0 | 0 | 37.5713 | 0 | 0 | 0 | 0 | 0 | 169.1972 | 0 | 1275.5102 | 100% | 0 | 7.8611 | 47.5498 | 76.08% | 45.4325
2346 | 33 | 77 | 67 | 6.6 | 19.8 | 0 | 0 | 0 | 0 | 4.7378 | 0 | 0 | 4.7378 | 0 | 0 | 0 | 87.5711 | 34.1507 | 0 | 87.5711 | 1187.9391 | 93.13% | 0 | 8.8182 | 37.7904 | 60.46% | 47.7067
2347 | 3 | 10 | 10 | 4.2 | 17.7 | 0 | 0 | 0 | 0 | 0.2383 | 0 | 0 | 0.2383 | 0 | 0 | 0 | 108.9501 | 43.5201 | 0 | 108.9501 | 1078.989 | 84.59% | 0 | 0 | 37.7904 | 60.46% | 43.7584
2348 | 0 | 0 | 0 | 3.8 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.987 | 40.0943 | 0 | 100.987 | 978.002 | 76.68% | 0 | 0 | 37.7904 | 60.46% | 40.0943
2349 | 0 | 0 | 0 | 3.4 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9899 | 37.1111 | 0 | 93.9899 | 884.0121 | 69.31% | 0 | 0 | 37.7904 | 60.46% | 37.1111
2350 | 0 | 0 | 0 | 4.2 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.389 | 34.7143 | 0 | 88.389 | 795.6231 | 62.38% | 0 | 0 | 37.7904 | 60.46% | 34.7143
2351 | 0 | 0 | 0 | 4.4 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0054 | 33.245 | 0 | 85.0054 | 710.6177 | 55.71% | 0 | 0 | 37.7904 | 60.46% | 33.245
2352 | 0 | 0 | 0 | 4.9 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.6177 | 55.71% | 0 | 17.8876 | 17.9936 | 28.79% | 17.8876
2353 | 0 | 0 | 0 | 5.4 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.6177 | 55.71% | 0 | 0 | 17.9936 | 28.79% | 0
2354 | 0 | 0 | 0 | 3.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9561 | 33.2909 | 0 | 84.9561 | 625.6616 | 49.05% | 0 | 0 | 17.9936 | 28.79% | 33.2909
2355 | 0 | 0 | 0 | 2.5 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8832 | 36.7434 | 0 | 92.8832 | 532.7784 | 41.77% | 0 | 0 | 17.9936 | 28.79% | 36.7434
2356 | 0 | 0 | 0 | 4.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.852 | 41.9591 | 0 | 104.852 | 427.9264 | 33.55% | 0 | 0 | 17.9936 | 28.79% | 41.9591
2357 | 0 | 0 | 0 | 6.3 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.3885 | 45.243 | 0 | 112.3885 | 315.5379 | 24.74% | 0 | 0 | 17.9936 | 28.79% | 45.243
2358 | 15 | 3 | 2 | 4.3 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.7446 | 46.7263 | 0 | 115.7446 | 199.7933 | 15.66% | 0 | 0 | 17.9936 | 28.79% | 46.7263
2359 | 505 | 110 | 30 | 6.5 | 13.4 | 0 | 0 | 0 | 0 | 1.1605 | 0 | 0 | 1.1605 | 0 | 0 | 0 | 114.581 | 46.1856 | 0 | 114.581 | 85.2124 | 6.681% | 0 | 0 | 17.9936 | 28.79% | 47.346
2360 | 790 | 326 | 53 | 6.1 | 14.9 | 0 | 0 | 0 | 0 | 14.237 | 0 | 0 | 14.237 | 0 | 0 | 0 | 85.2124 | 33.3569 | 0 | 85.2124 | 0 | 0% | 0 | 0 | 17.9936 | 28.79% | 47.5939
2361 | 900 | 539 | 64 | 7.9 | 16 | 0 | 0 | 0 | 0 | 37.2878 | 0 | 0 | 37.2878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 10.6111 | 6.25 | 10% | 47.8989
2362 | 959 | 723 | 69 | 6.9 | 17 | 0 | 0 | 0 | 0 | 47.3599 | 7.9574 | 0 | 47.3599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 47.3599
2363 | 995 | 861 | 71 | 7.8 | 18 | 0 | 0 | 0 | 0 | 45.7458 | 23.1928 | 0 | 45.7458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 45.7458
2364 | 1011 | 941 | 73 | 7.3 | 18.9 | 0 | 0 | 0 | 278.0718 | 44.8406 | 27.1594 | 0 | 44.8406 | 0 | 0 | 0 | 0 | 0 | 278.0718 | 0 | 278.0718 | 21.8% | 0 | 0 | 6.25 | 10% | 44.8406
2365 | 991 | 970 | 108 | 6.8 | 19.6 | 0 | 0 | 0 | 279.1399 | 43.9799 | 28.0201 | 0 | 43.9799 | 0 | 0 | 0 | 0 | 0 | 279.1399 | 0 | 557.2116 | 43.69% | 0 | 0 | 6.25 | 10% | 43.9799
2366 | 830 | 927 | 237 | 6.8 | 20.4 | 0 | 0 | 0 | 228.7604 | 68.991 | 3.009 | 25 | 43.991 | 0 | 0 | 0 | 0 | 0 | 228.7604 | 0 | 785.972 | 61.62% | 25 | 0 | 28.839 | 46.14% | 43.991
2367 | 934 | 796 | 110 | 10.1 | 20.3 | 0 | 0 | 0 | 251.0986 | 59.0502 | 12.1753 | 15.3879 | 43.6623 | 0 | 0 | 0 | 0 | 0 | 251.0986 | 0 | 1037.0707 | 81.31% | 15.3879 | 0 | 42.7429 | 68.39% | 43.6623
2368 | 929 | 630 | 74 | 10.5 | 19.4 | 0 | 0 | 0 | 238.4395 | 58.827 | 0 | 14.9488 | 43.8782 | 0 | 0 | 0 | 0 | 0 | 238.4395 | 0 | 1275.5102 | 100% | 14.9488 | 0 | 56.25 | 90% | 43.8782
2369 | 835 | 425 | 68 | 8.7 | 18.6 | 0 | 0 | 0 | 0 | 40.9369 | 0 | 0 | 40.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 4.717 | 51.0295 | 81.65% | 45.6539
2370 | 662 | 200 | 43 | 6.8 | 17.7 | 0 | 0 | 0 | 0 | 17.5736 | 0 | 0 | 17.5736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 23.3612 | 37.38% | 42.5735
2371 | 135 | 23 | 10 | 5.7 | 15.8 | 0 | 0 | 0 | 0 | 0.39665 | 0 | 0 | 0.39665 | 0 | 0 | 0 | 108.7514 | 43.5414 | 0 | 108.7514 | 1166.7588 | 91.47% | 0 | 0 | 23.3612 | 37.38% | 43.9381
2372 | 0 | 0 | 0 | 5 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.823 | 40.1402 | 0 | 100.823 | 1065.9358 | 83.57% | 0 | 0 | 23.3612 | 37.38% | 40.1402
2373 | 0 | 0 | 0 | 4.6 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2647 | 40.7877 | 0 | 102.2647 | 963.6711 | 75.55% | 3.4775 | 0 | 26.5033 | 42.41% | 37.3103
2374 | 0 | 0 | 0 | 5.6 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.8013 | 0 | 127.551 | 836.1201 | 65.55% | 16.6539 | 0 | 41.5511 | 66.48% | 35.1474
2375 | 0 | 0 | 0 | 4.1 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6576 | 33.5932 | 0 | 85.6576 | 750.4625 | 58.84% | 0 | 0 | 41.5511 | 66.48% | 33.5932
2376 | 0 | 0 | 0 | 3.5 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750.4625 | 58.84% | 0 | 6.8967 | 33.9183 | 54.27% | 6.8967
2377 | 0 | 0 | 0 | 3.4 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 750.4625 | 58.84% | 0 | 25 | 6.25 | 10% | 25
2378 | 0 | 0 | 0 | 1.5 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5102 | 33.5695 | 0 | 85.5102 | 664.9524 | 52.13% | 0 | 0 | 6.25 | 10% | 33.5695
2379 | 0 | 0 | 0 | 1.6 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.375 | 37.015 | 0 | 93.375 | 571.5773 | 44.81% | 0 | 0 | 6.25 | 10% | 37.015
2380 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.4608 | 42.3114 | 0 | 105.4608 | 466.1166 | 36.54% | 0 | 0 | 6.25 | 10% | 42.3114
2381 | 0 | 0 | 0 | 2 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.9494 | 45.5815 | 0 | 112.9494 | 353.1672 | 27.69% | 0 | 0 | 6.25 | 10% | 45.5815
2382 | 16 | 3 | 2 | 5.4 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.0594 | 46.9101 | 0 | 116.0594 | 237.1078 | 18.59% | 0 | 0 | 6.25 | 10% | 46.9101
2383 | 534 | 116 | 27 | 8.2 | 12.4 | 0 | 0 | 0 | 0 | 1.0608 | 0 | 0 | 1.0608 | 0 | 0 | 0 | 114.7046 | 46.2768 | 0 | 114.7046 | 122.4032 | 9.596% | 0 | 0 | 6.25 | 10% | 47.3377
2384 | 820 | 334 | 46 | 7.2 | 13.9 | 0 | 0 | 0 | 0 | 14.2852 | 0 | 0 | 14.2852 | 0 | 0 | 0 | 84.1378 | 32.9229 | 0 | 84.1378 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 47.2081
2385 | 927 | 550 | 55 | 7.9 | 15.3 | 0 | 0 | 0 | 0 | 34.3224 | 3.3128 | 0 | 34.3224 | 0 | 0 | 0 | 38.2653 | 12.9512 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 47.2736
2386 | 970 | 729 | 63 | 7.8 | 16.6 | 0 | 0 | 0 | 246.2813 | 46.8878 | 8.7371 | 0 | 46.8878 | 0 | 0 | 0 | 0 | 0 | 246.2813 | 0 | 246.2813 | 19.31% | 0 | 0 | 6.25 | 10% | 46.8878
2387 | 994 | 931 | 135 | 6.4 | 17.9 | 0 | 0 | 0 | 268.7113 | 45.1539 | 26.8461 | 0 | 45.1539 | 0 | 0 | 0 | 0 | 0 | 268.7113 | 0 | 514.9926 | 40.38% | 0 | 0 | 6.25 | 10% | 45.1539
2388 | 935 | 994 | 184 | 5.5 | 19.2 | 0 | 0 | 0 | 259.8741 | 49.8416 | 22.1584 | 5.3367 | 44.5049 | 0 | 0 | 0 | 0 | 0 | 259.8741 | 0 | 774.8668 | 60.75% | 5.3367 | 0 | 11.072 | 17.72% | 44.5049
2389 | 993 | 1029 | 160 | 5.9 | 20.4 | 0 | 0 | 0 | 280.589 | 68.8921 | 3.1079 | 25 | 43.8921 | 0 | 0 | 0 | 0 | 0 | 280.589 | 0 | 1055.4558 | 82.75% | 25 | 0 | 33.661 | 53.86% | 43.8921
2390 | 664 | 879 | 317 | 5.7 | 19.3 | 0 | 0 | 0 | 179.811 | 68.349 | 3.651 | 25 | 43.349 | 0 | 0 | 0 | 0 | 0 | 179.811 | 0 | 1235.2668 | 96.84% | 25 | 0 | 56.25 | 90% | 43.349
2391 | 173 | 348 | 217 | 3.8 | 18.1 | 0 | 0 | 0 | 0 | 28.1119 | 0 | 0 | 28.1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1235.2668 | 96.84% | 0 | 14.6174 | 40.0725 | 64.12% | 42.7292
2392 | 797 | 578 | 104 | 5.7 | 18.8 | 0 | 0 | 0 | 0 | 47.63 | 5.8197 | 17.389 | 30.241 | 0 | 0 | 0 | 38.2653 | 12.8907 | 0 | 38.2653 | 1197.0015 | 93.84% | 17.389 | 0 | 55.7845 | 89.26% | 43.1317
2393 | 637 | 337 | 69 | 6.2 | 17.8 | 0 | 0 | 0 | 0 | 32.6561 | 0 | 0.51522 | 32.1408 | 0 | 0 | 0 | 38.2653 | 12.91 | 0 | 38.2653 | 1158.7362 | 90.84% | 0.51522 | 0 | 56.25 | 90% | 45.0509
2394 | 671 | 202 | 42 | 4.5 | 17.1 | 0 | 0 | 0 | 103.159 | 17.5733 | 0 | 0 | 17.5733 | 0 | 0 | 0 | 0 | 0 | 103.159 | 0 | 1261.8952 | 98.93% | 0 | 25 | 28.5817 | 45.73% | 42.5733
2395 | 66 | 19 | 13 | 3.1 | 15.4 | 0 | 0 | 0 | 0 | 0.48997 | 0 | 0 | 0.48997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.8952 | 98.93% | 0 | 20.178 | 6.25 | 10% | 20.668
2396 | 0 | 0 | 0 | 3.5 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.7811 | 0 | 127.551 | 1134.3442 | 88.93% | 11.627 | 0 | 16.7557 | 26.81% | 40.1541
2397 | 0 | 0 | 0 | 6.1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4338 | 37.437 | 0 | 94.4338 | 1039.9104 | 81.53% | 0 | 0 | 16.7557 | 26.81% | 37.437
2398 | 0 | 0 | 0 | 3.3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5137 | 34.9274 | 0 | 88.5137 | 951.3966 | 74.59% | 0 | 0 | 16.7557 | 26.81% | 34.9274
2399 | 0 | 0 | 0 | 2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9335 | 0 | 127.551 | 823.8456 | 64.59% | 18.3654 | 0 | 33.35 | 53.36% | 33.5681
2400 | 0 | 0 | 0 | 2.3 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8472 | 32.8787 | 0 | 83.8472 | 739.9984 | 58.02% | 0 | 0 | 33.35 | 53.36% | 32.8787
2401 | 0 | 0 | 0 | 3.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4636 | 32.7046 | 0 | 83.4636 | 656.5348 | 51.47% | 0 | 0 | 33.35 | 53.36% | 32.7046
2402 | 0 | 0 | 0 | 1.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3882 | 47.5045 | 0 | 117.3882 | 539.1466 | 42.27% | 13.9476 | 0 | 45.9524 | 73.52% | 33.557
2403 | 0 | 0 | 0 | 2 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2398 | 36.983 | 0 | 93.2398 | 445.9068 | 34.96% | 0 | 0 | 45.9524 | 73.52% | 36.983
2404 | 0 | 0 | 0 | 1.1 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.0183 | 42.1332 | 0 | 105.0183 | 340.8886 | 26.73% | 0 | 0 | 45.9524 | 73.52% | 42.1332
2405 | 0 | 0 | 0 | 1.1 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1335 | 45.2514 | 0 | 112.1335 | 228.755 | 17.93% | 0 | 0 | 45.9524 | 73.52% | 45.2514
2406 | 31 | 4 | 2 | 0.7 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.2173 | 46.5995 | 0 | 115.2173 | 113.5377 | 8.901% | 0 | 0 | 45.9524 | 73.52% | 46.5995
2407 | 558 | 119 | 27 | 0.8 | 10.4 | 0 | 0 | 0 | 0 | 1.0484 | 0 | 0 | 1.0484 | 0 | 0 | 0 | 113.5377 | 45.8255 | 0 | 113.5377 | 0 | 0% | 0 | 0 | 45.9524 | 73.52% | 46.8739
2408 | 821 | 336 | 43 | 1 | 13.7 | 0 | 0 | 0 | 0 | 13.9113 | 0 | 0 | 13.9113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 18.2841 | 29.25% | 38.9113
2409 | 927 | 550 | 51 | 1 | 16.2 | 0 | 0 | 0 | 0 | 35.8319 | 0 | 0 | 35.8319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 10.8735 | 6.25 | 10% | 46.7054
2410 | 980 | 735 | 59 | 1.5 | 17.2 | 0 | 0 | 0 | 254.2964 | 46.3572 | 6.7747 | 0 | 46.3572 | 0 | 0 | 0 | 0 | 0 | 254.2964 | 0 | 254.2964 | 19.94% | 0 | 0 | 6.25 | 10% | 46.3572
2411 | 895 | 881 | 162 | 1.8 | 18.4 | 0 | 0 | 0 | 243.5478 | 44.8712 | 21.2958 | 0 | 44.8712 | 0 | 0 | 0 | 0 | 0 | 243.5478 | 0 | 497.8442 | 39.03% | 0 | 0 | 6.25 | 10% | 44.8712
2412 | 893 | 977 | 201 | 3.7 | 19.2 | 0 | 0 | 0 | 91.5802 | 44.2598 | 27.7402 | 0 | 44.2598 | 0 | 0 | 0 | 0 | 0 | 91.5802 | 0 | 589.4244 | 46.21% | 0 | 0 | 6.25 | 10% | 44.2598
2413 | 998 | 1015 | 140 | 4.7 | 19.4 | 0 | 0 | 0 | 283.1852 | 63.7818 | 8.2182 | 20.0205 | 43.7612 | 0 | 0 | 0 | 0 | 0 | 283.1852 | 0 | 872.6097 | 68.41% | 20.0205 | 0 | 24.3398 | 38.94% | 43.7612
2414 | 939 | 950 | 163 | 4.2 | 20 | 0 | 0 | 0 | 264.1676 | 68.2988 | 3.7012 | 25 | 43.2988 | 0 | 0 | 0 | 0 | 0 | 264.1676 | 0 | 1136.7772 | 89.12% | 25 | 0 | 46.9288 | 75.09% | 43.2988
2415 | 534 | 618 | 221 | 3.8 | 19.9 | 0 | 0 | 0 | 138.733 | 52.9562 | 0 | 10.3161 | 42.6401 | 0 | 0 | 0 | 0 | 0 | 138.733 | 0 | 1275.5102 | 100% | 10.3161 | 0 | 56.25 | 90% | 42.6401
2416 | 848 | 712 | 197 | 4.5 | 20.5 | 0 | 0 | 0 | 0 | 29.8556 | 32.1314 | 0 | 29.8556 | 0 | 0 | 0 | 38.2653 | 12.8541 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 42.7097
2417 | 707 | 404 | 106 | 4.3 | 20.1 | 0 | 0 | 0 | 0 | 31.607 | 6.2022 | 0 | 31.607 | 0 | 0 | 0 | 38.2653 | 12.8631 | 0 | 38.2653 | 1198.9796 | 94% | 0 | 0 | 56.25 | 90% | 44.4701
2418 | 688 | 217 | 51 | 4.2 | 19.1 | 0 | 0 | 0 | 75.0175 | 18.3944 | 0 | 0 | 18.3944 | 0 | 0 | 0 | 0 | 0 | 75.0175 | 0 | 1273.9971 | 99.88% | 0 | 25 | 28.5817 | 45.73% | 43.3944
2419 | 160 | 26 | 10 | 3.9 | 17.1 | 0 | 0 | 0 | 0 | 0.43254 | 0 | 0 | 0.43254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.9971 | 99.88% | 0 | 20.178 | 6.25 | 10% | 20.6105
2420 | 0 | 0 | 0 | 2.3 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9225 | 40.1569 | 0 | 100.9225 | 1173.0746 | 91.97% | 0 | 0 | 6.25 | 10% | 40.1569
2421 | 0 | 0 | 0 | 1.8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6905 | 37.5094 | 0 | 94.6905 | 1078.3841 | 84.55% | 0 | 0 | 6.25 | 10% | 37.5094
2422 | 0 | 0 | 0 | 0.7 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9896 | 35.0638 | 0 | 88.9896 | 989.3945 | 77.57% | 0 | 0 | 6.25 | 10% | 35.0638
2423 | 0 | 0 | 0 | 1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0295 | 33.3648 | 0 | 85.0295 | 904.365 | 70.9% | 0 | 0 | 6.25 | 10% | 33.3648
2424 | 0 | 0 | 0 | 0.8 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7279 | 32.8063 | 0 | 83.7279 | 820.6371 | 64.34% | 0 | 1.605e-15 | 6.25 | 10% | 32.8063
2425 | 0 | 0 | 0 | 0.8 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4326 | 32.6893 | 0 | 83.4326 | 737.2045 | 57.8% | 0 | 0 | 6.25 | 10% | 32.6893
2426 | 0 | 0 | 0 | 0.9 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9922 | 33.3843 | 0 | 84.9922 | 652.2123 | 51.13% | 0 | 0 | 6.25 | 10% | 33.3843
2427 | 0 | 0 | 0 | 1.6 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.623 | 36.7239 | 0 | 92.623 | 559.5893 | 43.87% | 0 | 0 | 6.25 | 10% | 36.7239
2428 | 0 | 0 | 0 | 1.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.7703 | 41.59 | 0 | 103.7703 | 455.8191 | 35.74% | 0 | 0 | 6.25 | 10% | 41.59
2429 | 0 | 0 | 0 | 1.2 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.1678 | 44.3935 | 0 | 110.1678 | 345.6513 | 27.1% | 0 | 0 | 6.25 | 10% | 44.3935
2430 | 29 | 4 | 3 | 1.1 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.5038 | 45.8503 | 0 | 113.5038 | 232.1475 | 18.2% | 0 | 0 | 6.25 | 10% | 45.8503
2431 | 523 | 122 | 32 | 0.9 | 11 | 0 | 0 | 0 | 0 | 1.3298 | 0 | 0 | 1.3298 | 0 | 0 | 0 | 111.6703 | 44.9968 | 0 | 111.6703 | 120.4772 | 9.445% | 0 | 0 | 6.25 | 10% | 46.3266
2432 | 792 | 338 | 52 | 1 | 14 | 0 | 0 | 0 | 0 | 14.1985 | 0 | 0 | 14.1985 | 0 | 0 | 0 | 82.2119 | 32.0821 | 0 | 82.2119 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 46.2806
2433 | 905 | 553 | 62 | 2.5 | 17.1 | 0 | 0 | 0 | 0 | 33.1686 | 3.2918 | 0 | 33.1686 | 0 | 0 | 0 | 38.2653 | 12.9226 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.0912
2434 | 965 | 737 | 67 | 5.2 | 19.1 | 0 | 0 | 0 | 247.7379 | 45.4422 | 9.2011 | 0 | 45.4422 | 0 | 0 | 0 | 0 | 0 | 247.7379 | 0 | 247.7379 | 19.42% | 0 | 0 | 6.25 | 10% | 45.4422
2435 | 989 | 868 | 73 | 5.7 | 19.9 | 0 | 0 | 0 | 0 | 43.9757 | 23.5371 | 0 | 43.9757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247.7379 | 19.42% | 0 | 0 | 6.25 | 10% | 43.9757
2436 | 989 | 942 | 83 | 5 | 20 | 0 | 0 | 0 | 276.6424 | 42.92 | 29.08 | 0 | 42.92 | 0 | 0 | 0 | 0 | 0 | 276.6424 | 0 | 524.3802 | 41.11% | 0 | 0 | 6.25 | 10% | 42.92
2437 | 988 | 955 | 87 | 5.3 | 20.4 | 0 | 0 | 0 | 279.6175 | 42.1304 | 29.8696 | 0 | 42.1304 | 0 | 0 | 0 | 0 | 0 | 279.6175 | 0 | 803.9977 | 63.03% | 0 | 0 | 6.25 | 10% | 42.1304
2438 | 969 | 904 | 92 | 6.9 | 20.3 | 0 | 0 | 0 | 270.8027 | 56.5306 | 15.4694 | 15.1133 | 41.4173 | 0 | 0 | 0 | 0 | 0 | 270.8027 | 0 | 1074.8004 | 84.26% | 15.1133 | 0 | 19.9058 | 31.85% | 41.4173
2439 | 931 | 781 | 88 | 6.6 | 20 | 0 | 0 | 0 | 0 | 65.6917 | 2.5881 | 25 | 40.6917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.8004 | 84.26% | 25 | 0 | 42.4948 | 67.99% | 40.6917
2440 | 892 | 617 | 76 | 6 | 19.7 | 0 | 0 | 0 | 135.7931 | 55.7814 | 0 | 15.2234 | 40.558 | 0 | 0 | 0 | 0 | 0 | 135.7931 | 0 | 1210.5935 | 94.91% | 15.2234 | 0 | 56.25 | 90% | 40.558
2441 | 806 | 414 | 63 | 5.5 | 19.3 | 0 | 0 | 0 | 0 | 38.5901 | 0 | 0 | 38.5901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210.5935 | 94.91% | 0 | 3.3857 | 52.503 | 84% | 41.9758
2442 | 633 | 199 | 44 | 5.1 | 18.1 | 0 | 0 | 0 | 0 | 16.665 | 0 | 0 | 16.665 | 0 | 0 | 0 | 72.0459 | 27.5238 | 0 | 72.0459 | 1138.5475 | 89.26% | 0 | 0 | 52.503 | 84% | 44.1888
2443 | 147 | 26 | 11 | 4.8 | 16 | 0 | 0 | 0 | 0 | 0.4379 | 0 | 0 | 0.4379 | 0 | 0 | 0 | 102.9104 | 40.9961 | 0 | 102.9104 | 1035.6371 | 81.19% | 0 | 0 | 52.503 | 84% | 41.434
2444 | 0 | 0 | 0 | 3.7 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.4279 | 14.7702 | 0 | 42.4279 | 993.2093 | 77.87% | 0 | 24.0483 | 25.8879 | 41.42% | 38.8186
2445 | 0 | 0 | 0 | 3.2 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9551 | 36.7615 | 0 | 92.9551 | 900.2541 | 70.58% | 0 | 0 | 25.8879 | 41.42% | 36.7615
2446 | 0 | 0 | 0 | 0.8 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6669 | 34.504 | 0 | 87.6669 | 812.5873 | 63.71% | 0 | 0 | 25.8879 | 41.42% | 34.504
2447 | 0 | 0 | 0 | 1.2 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5316 | 32.7144 | 0 | 83.5316 | 729.0557 | 57.16% | 0 | 0 | 25.8879 | 41.42% | 32.7144
2448 | 0 | 0 | 0 | 1.3 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2014 | 31.7033 | 0 | 81.2014 | 647.8542 | 50.79% | 0 | 0 | 25.8879 | 41.42% | 31.7033
2449 | 0 | 0 | 0 | 0.7 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0012 | 31.2061 | 0 | 80.0012 | 567.853 | 44.52% | 0 | 0 | 25.8879 | 41.42% | 31.2061
2450 | 0 | 0 | 0 | 1.6 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5997 | 31.0376 | 0 | 79.5997 | 488.2533 | 38.28% | 0 | 0 | 25.8879 | 41.42% | 31.0376
2451 | 0 | 0 | 0 | 1.7 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4796 | 31.8537 | 0 | 81.4796 | 406.7737 | 31.89% | 0 | 0 | 25.8879 | 41.42% | 31.8537
2452 | 0 | 0 | 0 | 2.2 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4811 | 33.1628 | 0 | 84.4811 | 322.2926 | 25.27% | 0 | 0 | 25.8879 | 41.42% | 33.1628
2453 | 0 | 0 | 0 | 1.1 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4116 | 35.3229 | 0 | 89.4116 | 232.881 | 18.26% | 0 | 0 | 25.8879 | 41.42% | 35.3229
2454 | 34 | 5 | 3 | 0.8 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6025 | 38.4718 | 0 | 96.6025 | 136.2784 | 10.68% | 0 | 0 | 25.8879 | 41.42% | 38.4718
2455 | 529 | 126 | 33 | 0.6 | 11.3 | 0 | 0 | 0 | 0 | 1.3906 | 0 | 0 | 1.3906 | 0 | 0 | 0 | 98.0131 | 39.0365 | 0 | 98.0131 | 38.2653 | 3% | 0 | 0 | 25.8879 | 41.42% | 40.4271
2456 | 788 | 342 | 54 | 0.7 | 16.3 | 0 | 0 | 0 | 0 | 14.1988 | 0 | 0 | 14.1988 | 0 | 0 | 0 | 38.2653 | 12.936 | 0 | 38.2653 | 0 | 0% | 0 | 13.3272 | 11.1383 | 17.82% | 40.4619
2457 | 900 | 557 | 65 | 1.3 | 18.9 | 0 | 0 | 0 | 0 | 35.8585 | 0 | 0 | 35.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 4.4168 | 6.25 | 10% | 40.2753
2458 | 967 | 742 | 67 | 2.1 | 20.4 | 0 | 0 | 0 | 0 | 39.9243 | 13.097 | 0 | 39.9243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 39.9243
2459 | 996 | 876 | 69 | 3.1 | 21.6 | 0 | 0 | 0 | 0 | 38.8478 | 26.8431 | 0 | 38.8478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.8478
2460 | 1001 | 949 | 74 | 3.9 | 22.4 | 0 | 0 | 0 | 0 | 37.0484 | 34.9516 | 0 | 37.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 37.0484
2461 | 992 | 956 | 80 | 5.7 | 22.7 | 0 | 0 | 0 | 280.5265 | 35.9858 | 36.0142 | 0 | 35.9858 | 0 | 0 | 0 | 0 | 0 | 280.5265 | 0 | 280.5265 | 21.99% | 0 | 0 | 6.25 | 10% | 35.9858
2462 | 974 | 901 | 82 | 6.3 | 22.5 | 0 | 0 | 0 | 100.9949 | 43.7035 | 28.2965 | 8.3681 | 35.3354 | 0 | 0 | 0 | 0 | 0 | 100.9949 | 0 | 381.5214 | 29.91% | 8.3681 | 0 | 13.8111 | 22.1% | 35.3354
2463 | 942 | 786 | 81 | 5.8 | 22.4 | 0 | 0 | 0 | 257.2721 | 60.1168 | 7.3731 | 25 | 35.1168 | 0 | 0 | 0 | 0 | 0 | 257.2721 | 0 | 638.7935 | 50.08% | 25 | 0 | 36.4001 | 58.24% | 35.1168
2464 | 905 | 624 | 71 | 5.8 | 22.4 | 0 | 0 | 0 | 236.0694 | 55.4183 | 0 | 20.0898 | 35.3285 | 0 | 0 | 0 | 0 | 0 | 236.0694 | 0 | 874.8629 | 68.59% | 20.0898 | 0 | 54.5524 | 87.28% | 35.3285
2465 | 824 | 422 | 61 | 5.5 | 21.7 | 0 | 0 | 0 | 195.4636 | 38.742 | 0 | 1.8788 | 36.8632 | 0 | 0 | 0 | 0 | 0 | 195.4636 | 0 | 1070.3265 | 83.91% | 1.8788 | 0 | 56.25 | 90% | 36.8632
2466 | 644 | 202 | 41 | 5.3 | 20.3 | 0 | 0 | 0 | 0 | 16.4719 | 0 | 0 | 16.4719 | 0 | 0 | 0 | 38.2653 | 12.8586 | 0 | 38.2653 | 1032.0612 | 80.91% | 0 | 10.8891 | 44.1987 | 70.72% | 40.2196
2467 | 154 | 27 | 12 | 4.9 | 18.3 | 0 | 0 | 0 | 0 | 0.48642 | 0 | 0 | 0.48642 | 0 | 0 | 0 | 96.3065 | 38.0118 | 0 | 96.3065 | 935.7547 | 73.36% | 0 | 0 | 44.1987 | 70.72% | 38.4982
2468 | 0 | 0 | 0 | 3.4 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0152 | 36.2407 | 0 | 92.0152 | 843.7396 | 66.15% | 0 | 0 | 44.1987 | 70.72% | 36.2407
2469 | 0 | 0 | 0 | 1.2 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3568 | 33.8578 | 0 | 86.3568 | 757.3828 | 59.38% | 0 | 0 | 44.1987 | 70.72% | 33.8578
2470 | 0 | 0 | 0 | 1.5 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0866 | 31.6128 | 0 | 81.0866 | 676.2961 | 53.02% | 0 | 0 | 44.1987 | 70.72% | 31.6128
2471 | 0 | 0 | 0 | 1.4 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.1461 | 19.0241 | 0 | 52.1461 | 624.15 | 48.93% | 0 | 11.04 | 31.9804 | 51.17% | 30.0641
2472 | 0 | 0 | 0 | 1.4 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.5281 | 29.2104 | 0 | 75.5281 | 548.6219 | 43.01% | 0 | 0 | 31.9804 | 51.17% | 29.2104
2473 | 0 | 0 | 0 | 2.3 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.2742 | 28.6352 | 0 | 74.2742 | 474.3477 | 37.19% | 0 | 0 | 31.9804 | 51.17% | 28.6352
2474 | 0 | 0 | 0 | 1.4 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.999 | 28.5488 | 0 | 73.999 | 400.3488 | 31.39% | 0 | 0 | 31.9804 | 51.17% | 28.5488
2475 | 0 | 0 | 0 | 0.9 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.258 | 29.117 | 0 | 75.258 | 325.0908 | 25.49% | 0 | 0 | 31.9804 | 51.17% | 29.117
2476 | 0 | 0 | 0 | 0.4 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0027 | 29.436 | 0 | 76.0027 | 249.0881 | 19.53% | 0 | 0 | 31.9804 | 51.17% | 29.436
2477 | 0 | 0 | 0 | 1.6 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2077 | 30.4081 | 0 | 78.2077 | 170.8804 | 13.4% | 0 | 0 | 31.9804 | 51.17% | 30.4081
2478 | 37 | 6 | 4 | 2.4 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0896 | 33.3815 | 0 | 85.0896 | 85.7907 | 6.726% | 0 | 0 | 31.9804 | 51.17% | 33.3815
2479 | 493 | 132 | 44 | 1.2 | 14.5 | 0 | 0 | 0 | 0 | 1.8511 | 0 | 0 | 1.8511 | 0 | 0 | 0 | 85.7907 | 33.6222 | 0 | 85.7907 | 0 | 0% | 0 | 0 | 31.9804 | 51.17% | 35.4733
2480 | 709 | 331 | 65 | 0.8 | 17.9 | 0 | 0 | 0 | 128.2737 | 13.8398 | 0 | 0 | 13.8398 | 0 | 0 | 0 | 0 | 0 | 128.2737 | 0 | 128.2737 | 10.06% | 0 | 22.3591 | 7.2349 | 11.58% | 36.1989
2481 | 877 | 550 | 66 | 2.1 | 20.6 | 0 | 0 | 0 | 203.1685 | 35.3021 | 0 | 0 | 35.3021 | 0 | 0 | 0 | 0 | 0 | 203.1685 | 0 | 331.4422 | 25.99% | 0 | 0.88988 | 6.25 | 10% | 36.1919
2482 | 935 | 730 | 72 | 3.2 | 22.3 | 0 | 0 | 0 | 241.505 | 36.2643 | 15.9424 | 0 | 36.2643 | 0 | 0 | 0 | 0 | 0 | 241.505 | 0 | 572.9472 | 44.92% | 0 | 0 | 6.25 | 10% | 36.2643
2483 | 965 | 862 | 75 | 3.6 | 23.7 | 0 | 0 | 0 | 263.1216 | 35.8828 | 28.3604 | 0 | 35.8828 | 0 | 0 | 0 | 0 | 0 | 263.1216 | 0 | 836.0688 | 65.55% | 0 | 0 | 6.25 | 10% | 35.8828
2484 | 975 | 935 | 79 | 4.5 | 24.7 | 0 | 0 | 0 | 273.124 | 34.3313 | 37.6687 | 0 | 34.3313 | 0 | 0 | 0 | 0 | 0 | 273.124 | 0 | 1109.1928 | 86.96% | 0 | 0 | 6.25 | 10% | 34.3313
2485 | 973 | 946 | 81 | 4.1 | 25.2 | 0 | 0 | 0 | 166.3174 | 33.3007 | 38.6993 | 0 | 33.3007 | 0 | 0 | 0 | 0 | 0 | 166.3174 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 33.3007
2486 | 963 | 892 | 78 | 5.5 | 25.6 | 0 | 0 | 0 | 0 | 57.8383 | 14.1617 | 25 | 32.8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 25 | 0 | 28.839 | 46.14% | 32.8383
2487 | 940 | 780 | 74 | 5.6 | 25.6 | 0 | 0 | 0 | 0 | 57.8425 | 8.0948 | 25 | 32.8425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 25 | 0 | 51.428 | 82.28% | 32.8425
2488 | 892 | 616 | 68 | 5.5 | 25.8 | 0 | 0 | 0 | 0 | 38.7488 | 14.9329 | 5.3367 | 33.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 5.3367 | 0 | 56.25 | 90% | 33.4121
2489 | 805 | 414 | 58 | 5.9 | 24.7 | 0 | 0 | 0 | 0 | 35.3619 | 1.934 | 0 | 35.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 35.3619
2490 | 606 | 198 | 45 | 5.1 | 23.4 | 0 | 0 | 0 | 0 | 15.6872 | 0 | 0 | 15.6872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 23.2065 | 30.5666 | 48.91% | 38.8938
2491 | 67 | 22 | 14 | 3.1 | 20.9 | 0 | 0 | 0 | 0 | 0.50522 | 0 | 0 | 0.50522 | 0 | 0 | 0 | 95.2347 | 37.3858 | 0 | 95.2347 | 1180.2755 | 92.53% | 0 | 0 | 30.5666 | 48.91% | 37.891
2492 | 0 | 0 | 0 | 2.6 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3178 | 35.8535 | 0 | 91.3178 | 1088.9577 | 85.37% | 0 | 0 | 30.5666 | 48.91% | 35.8535
2493 | 0 | 0 | 0 | 0.9 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8151 | 33.5388 | 0 | 85.8151 | 1003.1425 | 78.65% | 0 | 0 | 30.5666 | 48.91% | 33.5388
2494 | 0 | 0 | 0 | 0.4 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1092 | 31.5111 | 0 | 81.1092 | 922.0334 | 72.29% | 0 | 0 | 30.5666 | 48.91% | 31.5111
2495 | 0 | 0 | 0 | 0.9 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922.0334 | 72.29% | 0 | 0 | 30.5666 | 48.91% | 0
2496 | 0 | 0 | 0 | 0.8 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922.0334 | 72.29% | 0 | 0 | 30.5666 | 48.91% | 0
2497 | 0 | 0 | 0 | 1.1 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922.0334 | 72.29% | 0 | 0 | 30.5666 | 48.91% | 0
2498 | 0 | 0 | 0 | 1.1 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922.0334 | 72.29% | 0 | 0 | 30.5666 | 48.91% | 0
2499 | 0 | 0 | 0 | 0.3 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922.0334 | 72.29% | 0 | 0 | 30.5666 | 48.91% | 0
2500 | 0 | 0 | 0 | 1.7 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1104 | 38.1083 | 0 | 96.1104 | 825.9229 | 64.75% | 0 | 0 | 30.5666 | 48.91% | 38.1083
2501 | 0 | 0 | 0 | 1.8 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4089 | 40.8421 | 0 | 102.4089 | 723.5141 | 56.72% | 0 | 0 | 30.5666 | 48.91% | 40.8421
2502 | 3 | 5 | 5 | 1.5 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.7006 | 46.656 | 0 | 115.7006 | 607.8135 | 47.65% | 3.7095 | 0 | 33.9183 | 54.27% | 42.9465
2503 | 158 | 83 | 53 | 2.2 | 16.3 | 0 | 0 | 0 | 0 | 1.7783 | 0 | 0 | 1.7783 | 0 | 0 | 0 | 105.8842 | 42.2712 | 0 | 105.8842 | 501.9293 | 39.35% | 0 | 0 | 33.9183 | 54.27% | 44.0495
2504 | 452 | 345 | 177 | 1.3 | 20.5 | 0 | 0 | 0 | 75.5439 | 17.4358 | 0 | 0 | 17.4358 | 0 | 0 | 0 | 0 | 0 | 75.5439 | 0 | 577.4732 | 45.27% | 0 | 25 | 6.25 | 10% | 42.4359
2505 | 390 | 459 | 233 | 1.2 | 23.7 | 0 | 0 | 0 | 80.9631 | 29.2262 | 0 | 0 | 29.2262 | 0 | 0 | 0 | 0 | 0 | 80.9631 | 0 | 658.4364 | 51.62% | 0 | 0 | 6.25 | 10% | 29.2262
2506 | 402 | 637 | 341 | 2.6 | 25.2 | 0 | 0 | 0 | 93.8034 | 43.8043 | 0 | 0 | 43.8043 | 0 | 0 | 0 | 0 | 0 | 93.8034 | 0 | 752.2398 | 58.98% | 0 | 0 | 6.25 | 10% | 43.8043
2507 | 560 | 793 | 331 | 3.4 | 26.3 | 0 | 0 | 0 | 145.1768 | 57.923 | 0 | 14.7258 | 43.1972 | 0 | 0 | 0 | 0 | 0 | 145.1768 | 0 | 897.4166 | 70.36% | 14.7258 | 0 | 19.5556 | 31.29% | 43.1972
2508 | 70 | 588 | 514 | 4.4 | 26.5 | 0 | 0 | 0 | 0 | 40.5067 | 0 | 0 | 40.5067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 897.4166 | 70.36% | 0 | 0 | 19.5556 | 31.29% | 40.5067
2509 | 88 | 517 | 429 | 4.2 | 25.6 | 0 | 0 | 0 | 0 | 35.8871 | 0 | 25 | 10.8871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 897.4166 | 70.36% | 25 | 0 | 42.1446 | 67.43% | 10.8871
2510 | 171 | 519 | 363 | 3.5 | 26.6 | 0 | 0 | 0 | 0 | 37.6012 | 0 | 10.1058 | 27.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 897.4166 | 70.36% | 10.1058 | 0 | 51.2758 | 82.04% | 27.4954
2511 | 212 | 526 | 366 | 5.3 | 27.5 | 0 | 0 | 0 | 42.0425 | 39.4195 | 0 | 0 | 39.4195 | 0 | 0 | 0 | 0 | 0 | 42.0425 | 0 | 939.4591 | 73.65% | 0 | 0 | 51.2758 | 82.04% | 39.4195
2512 | 515 | 568 | 245 | 5.2 | 27.9 | 0 | 0 | 0 | 126.1723 | 46.0116 | 0 | 5.5051 | 40.5065 | 0 | 0 | 0 | 0 | 0 | 126.1723 | 0 | 1065.6314 | 83.55% | 5.5051 | 0 | 56.25 | 90% | 40.5065
2513 | 397 | 373 | 191 | 3.6 | 25.8 | 0 | 0 | 0 | 85.5407 | 29.8712 | 0 | 0 | 29.8712 | 0 | 0 | 0 | 0 | 0 | 85.5407 | 0 | 1151.1721 | 90.25% | 0 | 2.3489 | 53.6504 | 85.84% | 32.2201
2514 | 211 | 166 | 109 | 3.2 | 23.4 | 0 | 0 | 0 | 0 | 11.5057 | 0 | 0 | 11.5057 | 0 | 0 | 0 | 84.9059 | 32.7722 | 0 | 84.9059 | 1066.2662 | 83.6% | 0 | 0 | 53.6504 | 85.84% | 44.2779
2515 | 24 | 22 | 20 | 2.5 | 20.4 | 0 | 0 | 0 | 0 | 0.8777 | 0 | 0 | 0.8777 | 0 | 0 | 0 | 101.5151 | 40.1274 | 0 | 101.5151 | 964.7511 | 75.64% | 0 | 0 | 53.6504 | 85.84% | 41.0051
2516 | 0 | 0 | 0 | 1.3 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9534 | 37.8868 | 0 | 95.9534 | 868.7976 | 68.11% | 0 | 0 | 53.6504 | 85.84% | 37.8868
2517 | 0 | 0 | 0 | 2.2 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6564 | 35.6989 | 0 | 90.6564 | 778.1412 | 61.01% | 0 | 0 | 53.6504 | 85.84% | 35.6989
2518 | 0 | 0 | 0 | 2 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.812 | 33.6447 | 0 | 85.812 | 692.3292 | 54.28% | 0 | 0 | 53.6504 | 85.84% | 33.6447
2519 | 0 | 0 | 0 | 1.7 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6867 | 32.3063 | 0 | 82.6867 | 609.6425 | 47.8% | 0 | 0 | 53.6504 | 85.84% | 32.3063
2520 | 0 | 0 | 0 | 1.5 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1249 | 31.6239 | 0 | 81.1249 | 528.5176 | 41.44% | 0 | 0 | 53.6504 | 85.84% | 31.6239
2521 | 0 | 0 | 0 | 2.2 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5304 | 34.4341 | 0 | 87.5304 | 440.9872 | 34.57% | 2.877 | 0 | 56.25 | 90% | 31.557
2522 | 0 | 0 | 0 | 1.2 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.611 | 32.2617 | 0 | 82.611 | 358.3762 | 28.1% | 0 | 0 | 56.25 | 90% | 32.2617
2523 | 0 | 0 | 0 | 1.8 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2189 | 35.1363 | 0 | 89.2189 | 269.1573 | 21.1% | 0 | 0 | 56.25 | 90% | 35.1363
2524 | 0 | 0 | 0 | 2.1 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.37 | 38.6821 | 0 | 97.37 | 171.7872 | 13.47% | 0 | 0 | 56.25 | 90% | 38.6821
2525 | 0 | 0 | 0 | 2.4 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7866 | 41.0636 | 0 | 102.7866 | 69.0006 | 5.41% | 0 | 0 | 56.25 | 90% | 41.0636
2526 | 13 | 4 | 4 | 1.4 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.0006 | 5.41% | 0 | 25 | 28.5817 | 45.73% | 25
2527 | 520 | 136 | 36 | 2.3 | 14.7 | 0 | 0 | 0 | 46.5556 | 1.5064 | 0 | 0 | 1.5064 | 0 | 0 | 0 | 0 | 0 | 46.5556 | 0 | 115.5562 | 9.06% | 0 | 20.178 | 6.25 | 10% | 21.6844
2528 | 785 | 353 | 57 | 1 | 17.6 | 0 | 0 | 0 | 0 | 14.4948 | 0 | 0 | 14.4948 | 0 | 0 | 0 | 77.2909 | 29.8151 | 0 | 77.2909 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 44.3099
2529 | 889 | 563 | 67 | 1.7 | 19.9 | 0 | 0 | 0 | 0 | 31.4967 | 4.2454 | 0 | 31.4967 | 0 | 0 | 0 | 38.2653 | 12.8676 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 44.3643
2530 | 926 | 737 | 80 | 1.7 | 21.5 | 0 | 0 | 0 | 240.1002 | 44.1372 | 7.341 | 0 | 44.1372 | 0 | 0 | 0 | 0 | 0 | 240.1002 | 0 | 240.1002 | 18.82% | 0 | 0 | 6.25 | 10% | 44.1372
2531 | 941 | 867 | 94 | 2.9 | 22.3 | 0 | 0 | 0 | 256.6978 | 42.8337 | 21.071 | 0 | 42.8337 | 0 | 0 | 0 | 0 | 0 | 256.6978 | 0 | 496.798 | 38.95% | 0 | 0 | 6.25 | 10% | 42.8337
2532 | 937 | 949 | 121 | 3.9 | 22.8 | 0 | 0 | 0 | 0 | 41.7307 | 30.2693 | 0 | 41.7307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496.798 | 38.95% | 0 | 0 | 6.25 | 10% | 41.7307
2533 | 583 | 762 | 235 | 3.7 | 22.9 | 0 | 0 | 0 | 105.1504 | 41.1109 | 19.3942 | 0 | 41.1109 | 0 | 0 | 0 | 0 | 0 | 105.1504 | 0 | 601.9484 | 47.19% | 0 | 0 | 6.25 | 10% | 41.1109
2534 | 917 | 892 | 114 | 5.2 | 23.2 | 0 | 0 | 0 | 256.7981 | 60.5888 | 11.4112 | 20.0461 | 40.5427 | 0 | 0 | 0 | 0 | 0 | 256.7981 | 0 | 858.7465 | 67.33% | 20.0461 | 0 | 24.3629 | 38.98% | 40.5427
2535 | 912 | 784 | 98 | 6.4 | 22.7 | 0 | 0 | 0 | 247.9129 | 64.8283 | 1.8578 | 25 | 39.8283 | 0 | 0 | 0 | 0 | 0 | 247.9129 | 0 | 1106.6594 | 86.76% | 25 | 0 | 46.9519 | 75.12% | 39.8283
2536 | 669 | 588 | 165 | 6.4 | 22.3 | 0 | 0 | 0 | 168.8508 | 50.0506 | 0 | 10.2906 | 39.76 | 0 | 0 | 0 | 4.3911e-13 | 0 | 168.8508 | 4.3911e-13 | 1275.5102 | 100% | 10.2906 | 0 | 56.25 | 90% | 39.76
2537 | 456 | 349 | 162 | 6.7 | 20.9 | 0 | 0 | 0 | 0 | 30.9649 | 3.5527e-14 | 0 | 30.9649 | 0 | 0 | 0 | 4.8723e-13 | 1.6355e-13 | 0 | 4.8723e-13 | 1275.5102 | 100% | 0 | 10.1781 | 44.9856 | 71.98% | 41.143
2538 | 621 | 211 | 54 | 6 | 20 | 0 | 0 | 0 | 0 | 16.7407 | 0 | 0 | 16.7407 | 0 | 0 | 0 | 69.0524 | 26.1489 | 0 | 69.0524 | 1206.4578 | 94.59% | 0 | 0.43156 | 44.508 | 71.21% | 43.3211
2539 | 143 | 28 | 14 | 5.6 | 17.6 | 0 | 0 | 0 | 0 | 0.56606 | 0 | 0 | 0.56606 | 0 | 0 | 0 | 100.7668 | 39.9822 | 0 | 100.7668 | 1105.6909 | 86.69% | 0 | 0 | 44.508 | 71.21% | 40.5483
2540 | 0 | 0 | 0 | 5.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5241 | 37.8534 | 0 | 95.5241 | 1010.1668 | 79.2% | 0 | 0 | 44.508 | 71.21% | 37.8534
2541 | 0 | 0 | 0 | 3.6 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7286 | 35.8089 | 0 | 90.7286 | 919.4382 | 72.08% | 0 | 0 | 44.508 | 71.21% | 35.8089
2542 | 0 | 0 | 0 | 3.4 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.1773 | 24.2749 | 0 | 64.1773 | 855.2609 | 67.05% | 0 | 0 | 44.508 | 71.21% | 24.2749
2543 | 0 | 0 | 0 | 3.5 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855.2609 | 67.05% | 0 | 0 | 44.508 | 71.21% | 0
2544 | 0 | 0 | 0 | 3.1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855.2609 | 67.05% | 0 | 0 | 44.508 | 71.21% | 0
2545 | 0 | 0 | 0 | 3.3 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855.2609 | 67.05% | 0 | 0 | 44.508 | 71.21% | 0
2546 | 0 | 0 | 0 | 2.7 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855.2609 | 67.05% | 0 | 0 | 44.508 | 71.21% | 0
2547 | 0 | 0 | 0 | 2.6 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1058 | 34.7185 | 0 | 88.1058 | 767.1551 | 60.14% | 0 | 0 | 44.508 | 71.21% | 34.7185
2548 | 0 | 0 | 0 | 2.5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.855 | 38.1069 | 0 | 95.855 | 671.3001 | 52.63% | 0 | 0 | 44.508 | 71.21% | 38.1069
2549 | 0 | 0 | 0 | 2.6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6113 | 40.6249 | 0 | 101.6113 | 569.6888 | 44.66% | 0 | 0 | 44.508 | 71.21% | 40.6249
2550 | 3 | 9 | 9 | 3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7614 | 42.8685 | 0 | 106.7614 | 462.9274 | 36.29% | 0 | 0 | 44.508 | 71.21% | 42.8685
2551 | 163 | 137 | 101 | 3.2 | 11.5 | 0 | 0 | 0 | 0 | 3.1018 | 0 | 0 | 3.1018 | 0 | 0 | 0 | 101.48 | 40.5424 | 0 | 101.48 | 361.4474 | 28.34% | 0 | 0 | 44.508 | 71.21% | 43.6442
2552 | 272 | 290 | 182 | 4.7 | 14 | 0 | 0 | 0 | 36.711 | 15.6979 | 0 | 0 | 15.6979 | 0 | 0 | 0 | 0 | 0 | 36.711 | 0 | 398.1584 | 31.22% | 0 | 25 | 16.8396 | 26.94% | 40.6979
2553 | 447 | 521 | 260 | 5.6 | 16.5 | 0 | 0 | 0 | 92.6865 | 34.5898 | 0 | 0 | 34.5898 | 0 | 0 | 0 | 0 | 0 | 92.6865 | 0 | 490.8449 | 38.48% | 0 | 9.5684 | 6.25 | 10% | 44.1581
2554 | 483 | 675 | 320 | 6 | 18.6 | 0 | 0 | 0 | 113.7777 | 43.888 | 4.338 | 0 | 43.888 | 0 | 0 | 0 | 0 | 0 | 113.7777 | 0 | 604.6227 | 47.4% | 0 | 0 | 6.25 | 10% | 43.888
2555 | 582 | 815 | 326 | 6.4 | 20.4 | 0 | 0 | 0 | 148.8426 | 42.5259 | 18.6738 | 0 | 42.5259 | 0 | 0 | 0 | 0 | 0 | 148.8426 | 0 | 753.4653 | 59.07% | 0 | 0 | 6.25 | 10% | 42.5259
2556 | 574 | 875 | 355 | 7 | 21.4 | 0 | 0 | 0 | 150.68 | 41.278 | 26.0915 | 0 | 41.278 | 0 | 0 | 0 | 0 | 0 | 150.68 | 0 | 904.1453 | 70.88% | 0 | 0 | 6.25 | 10% | 41.278
2557 | 458 | 829 | 407 | 7.7 | 21.7 | 0 | 0 | 0 | 116.7628 | 64.8197 | 0 | 24.0695 | 40.7502 | 0 | 0 | 0 | 0 | 0 | 116.7628 | 0 | 1020.9081 | 80.04% | 24.0695 | 0 | 27.9982 | 44.8% | 40.7502
2558 | 585 | 842 | 334 | 8.2 | 22.3 | 0 | 0 | 0 | 153.874 | 65.189 | 2.5382 | 25 | 40.189 | 0 | 0 | 0 | 0 | 0 | 153.874 | 0 | 1174.7821 | 92.1% | 25 | 0 | 50.5872 | 80.94% | 40.189
2559 | 286 | 612 | 385 | 8.4 | 22 | 0 | 0 | 0 | 61.4838 | 46.1038 | 1.4425 | 6.2672 | 39.8366 | 0 | 0 | 0 | 0 | 0 | 61.4838 | 0 | 1236.2659 | 96.92% | 6.2672 | 0 | 56.25 | 90% | 39.8366
2560 | 219 | 490 | 348 | 7.9 | 21.1 | 0 | 0 | 0 | 39.2443 | 37.009 | 0 | 0 | 37.009 | 0 | 0 | 0 | 0 | 0 | 39.2443 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 37.009
2561 | 188 | 350 | 262 | 7.6 | 19.6 | 0 | 0 | 0 | 0 | 26.1215 | 0 | 0 | 26.1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 14.878 | 39.784 | 63.65% | 40.9995
2562 | 45 | 123 | 108 | 7.3 | 18.2 | 0 | 0 | 0 | 0 | 7.7583 | 0 | 0 | 7.7583 | 0 | 0 | 0 | 88.9472 | 34.8331 | 0 | 88.9472 | 1186.563 | 93.03% | 0 | 0 | 39.784 | 63.65% | 42.5914
2563 | 0 | 16 | 16 | 6.3 | 17 | 0 | 0 | 0 | 0 | 0.60018 | 0 | 0 | 0.60018 | 0 | 0 | 0 | 98.3245 | 38.9565 | 0 | 98.3245 | 1088.2385 | 85.32% | 0 | 0 | 39.784 | 63.65% | 39.5567
2564 | 0 | 0 | 0 | 5.2 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1707 | 36.7323 | 0 | 93.1707 | 995.0678 | 78.01% | 0 | 0 | 39.784 | 63.65% | 36.7323
2565 | 0 | 0 | 0 | 3.5 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8067 | 34.3884 | 0 | 87.8067 | 907.261 | 71.13% | 0 | 0 | 39.784 | 63.65% | 34.3884
2566 | 0 | 0 | 0 | 1.2 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5575 | 32.1267 | 0 | 82.5575 | 824.7035 | 64.66% | 0 | 0 | 39.784 | 63.65% | 32.1267
2567 | 0 | 0 | 0 | 2 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 824.7035 | 64.66% | 0 | 5.3 | 33.9183 | 54.27% | 5.3
2568 | 0 | 0 | 0 | 1.3 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 824.7035 | 64.66% | 0 | 0 | 33.9183 | 54.27% | 0
2569 | 0 | 0 | 0 | 1.7 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 824.7035 | 64.66% | 0 | 0 | 33.9183 | 54.27% | 0
2570 | 0 | 0 | 0 | 1.6 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 824.7035 | 64.66% | 0 | 25 | 6.25 | 10% | 25
2571 | 0 | 0 | 0 | 2.1 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2134 | 30.3343 | 0 | 78.2134 | 746.4902 | 58.52% | 0 | 0 | 6.25 | 10% | 30.3343
2572 | 0 | 0 | 0 | 2.7 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1067 | 31.6295 | 0 | 81.1067 | 665.3835 | 52.17% | 0 | 0 | 6.25 | 10% | 31.6295
2573 | 0 | 0 | 0 | 1.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1557 | 32.9818 | 0 | 84.1557 | 581.2278 | 45.57% | 0 | 0 | 6.25 | 10% | 32.9818
2574 | 0 | 12 | 12 | 1.7 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2989 | 35.653 | 0 | 90.2989 | 490.9289 | 38.49% | 0 | 0 | 6.25 | 10% | 35.653
2575 | 4 | 31 | 30 | 1.7 | 13.2 | 0 | 0 | 0 | 0 | 1.2465 | 0 | 0 | 1.2465 | 0 | 0 | 0 | 91.931 | 36.3354 | 0 | 91.931 | 398.9978 | 31.28% | 0 | 0 | 6.25 | 10% | 37.5818
2576 | 0 | 41 | 41 | 1.4 | 13.8 | 0 | 0 | 0 | 0 | 2.2674 | 0 | 0 | 2.2674 | 0 | 0 | 0 | 92.1001 | 36.3896 | 0 | 92.1001 | 306.8977 | 24.06% | 0 | 0 | 6.25 | 10% | 38.657
2577 | 0 | 29 | 29 | 2.4 | 13.2 | 0 | 0 | 0 | 0 | 1.4681 | 0 | 0 | 1.4681 | 0 | 0 | 0 | 94.9063 | 37.6303 | 0 | 94.9063 | 211.9914 | 16.62% | 0 | 0 | 6.25 | 10% | 39.0985
2578 | 0 | 28 | 28 | 4.2 | 10.7 | 0 | 0 | 0 | 0 | 1.4035 | 0 | 0 | 1.4035 | 0 | 0 | 0 | 94.9215 | 37.7019 | 0 | 94.9215 | 117.0699 | 9.178% | 0 | 0 | 6.25 | 10% | 39.1054
2579 | 0 | 49 | 49 | 3.1 | 9.3 | 0 | 0 | 0 | 0 | 2.7729 | 0 | 0 | 2.7729 | 0 | 0 | 0 | 89.5421 | 35.3786 | 0 | 89.5421 | 27.5278 | 2.158% | 0 | 0 | 6.25 | 10% | 38.1514
2580 | 0 | 62 | 61 | 1.8 | 9.4 | 0 | 0 | 0 | 0 | 3.5479 | 0 | 0 | 3.5479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5278 | 2.158% | 0 | 0 | 6.25 | 10% | 3.5479
2581 | 0 | 109 | 107 | 2.8 | 10.7 | 0 | 0 | 0 | 0 | 6.6001 | 0 | 0 | 6.6001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5278 | 2.158% | 0 | 0 | 6.25 | 10% | 6.6001
2582 | 0 | 129 | 127 | 1.8 | 11.8 | 0 | 0 | 0 | 0 | 7.9104 | 0 | 0 | 7.9104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5278 | 2.158% | 0 | 0 | 6.25 | 10% | 7.9104
2583 | 225 | 532 | 354 | 4 | 13.2 | 0 | 0 | 0 | 46.6688 | 41.8432 | 0 | 7.2766 | 34.5667 | 0 | 0 | 0 | 0 | 0 | 46.6688 | 0 | 74.1965 | 5.817% | 7.2766 | 0 | 12.8248 | 20.52% | 34.5667
2584 | 574 | 555 | 193 | 4.1 | 14.5 | 0 | 0 | 0 | 143.8537 | 47.4419 | 0 | 12.3014 | 35.1404 | 0 | 0 | 0 | 0 | 0 | 143.8537 | 0 | 218.0502 | 17.1% | 12.3014 | 0 | 23.9399 | 38.3% | 35.1404
2585 | 274 | 281 | 170 | 4.8 | 14.2 | 0 | 0 | 0 | 51.7353 | 23.7794 | 0 | 0 | 23.7794 | 0 | 0 | 0 | 0 | 0 | 51.7353 | 0 | 269.7855 | 21.15% | 0 | 0 | 23.9399 | 38.3% | 23.7794
2586 | 578 | 209 | 60 | 3 | 14.5 | 0 | 0 | 0 | 111.2637 | 16.2486 | 0 | 0 | 16.2486 | 0 | 0 | 0 | 0 | 0 | 111.2637 | 0 | 381.0492 | 29.87% | 0 | 15.9839 | 6.25 | 10% | 32.2325
2587 | 55 | 20 | 13 | 2.9 | 13.3 | 0 | 0 | 0 | 0 | 0.44078 | 0 | 0 | 0.44078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0.44078
2588 | 0 | 0 | 0 | 2.3 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2589 | 0 | 0 | 0 | 1.9 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2590 | 0 | 0 | 0 | 1.5 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2591 | 0 | 0 | 0 | 0.9 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2592 | 0 | 0 | 0 | 1.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2593 | 0 | 0 | 0 | 2 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2594 | 0 | 0 | 0 | 1.2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2595 | 0 | 0 | 0 | 0.7 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2596 | 0 | 0 | 0 | 0.6 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2597 | 0 | 0 | 0 | 0.6 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2598 | 0 | 5 | 5 | 0.9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 0
2599 | 0 | 56 | 56 | 0.5 | 9 | 0 | 0 | 0 | 0 | 2.4638 | 0 | 0 | 2.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 2.4638
2600 | 8 | 136 | 132 | 0.6 | 10.4 | 0 | 0 | 0 | 0 | 8.4814 | 0 | 0 | 8.4814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.0492 | 29.87% | 0 | 0 | 6.25 | 10% | 8.4814
2601 | 297 | 366 | 181 | 1 | 12.4 | 0 | 0 | 0 | 58.0098 | 23.4142 | 0 | 0 | 23.4142 | 0 | 0 | 0 | 0 | 0 | 58.0098 | 0 | 439.059 | 34.42% | 0 | 0 | 6.25 | 10% | 23.4142
2602 | 148 | 422 | 309 | 2.8 | 13.8 | 0 | 0 | 0 | 0 | 29.7302 | 0 | 0 | 29.7302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 439.059 | 34.42% | 0 | 0 | 6.25 | 10% | 29.7302
2603 | 269 | 641 | 407 | 4 | 14.9 | 0 | 0 | 0 | 59.5254 | 46.4749 | 0 | 25 | 21.4749 | 0 | 0 | 0 | 0 | 0 | 59.5254 | 0 | 498.5844 | 39.09% | 25 | 0 | 28.839 | 46.14% | 21.4749
2604 | 179 | 672 | 501 | 4.8 | 15.2 | 0 | 0 | 0 | 31.6282 | 49.5001 | 0 | 25 | 24.5001 | 0 | 0 | 0 | 0 | 0 | 31.6282 | 0 | 530.2125 | 41.57% | 25 | 0 | 51.428 | 82.28% | 24.5001
2605 | 29 | 347 | 314 | 4.2 | 14.8 | 0 | 0 | 0 | 0 | 24.0661 | 8.8818e-16 | 4.776 | 19.2901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 4.776 | 0 | 55.7434 | 89.19% | 19.2901
2606 | 13 | 478 | 457 | 5.9 | 14.3 | 0 | 0 | 0 | 0 | 32.2347 | 0 | 0.56067 | 31.674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0.56067 | 0 | 56.25 | 90% | 31.674
2607 | 48 | 420 | 374 | 3.9 | 14.7 | 0 | 0 | 0 | 0 | 29.4635 | 0 | 0 | 29.4635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 56.25 | 90% | 29.4635
2608 | 1 | 267 | 263 | 2.9 | 15 | 0 | 0 | 0 | 0 | 17.3425 | 0 | 0 | 17.3425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 56.25 | 90% | 17.3425
2609 | 0 | 139 | 137 | 2.4 | 14.3 | 0 | 0 | 0 | 0 | 8.6701 | 0 | 0 | 8.6701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 56.25 | 90% | 8.6701
2610 | 0 | 70 | 69 | 1.2 | 14.2 | 0 | 0 | 0 | 0 | 4.124 | 0 | 0 | 4.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 25 | 28.5817 | 45.73% | 29.124
2611 | 26 | 8 | 4 | 2.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 20.178 | 6.25 | 10% | 20.178
2612 | 0 | 0 | 0 | 1.5 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2613 | 0 | 0 | 0 | 1.9 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2614 | 0 | 0 | 0 | 1.4 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2615 | 0 | 0 | 0 | 0.7 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2616 | 0 | 0 | 0 | 1.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2617 | 0 | 0 | 0 | 0.9 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2618 | 0 | 0 | 0 | 1.1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2619 | 0 | 0 | 0 | 0.8 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2620 | 0 | 0 | 0 | 0.7 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2621 | 0 | 0 | 0 | 0.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2622 | 0 | 1 | 1 | 1.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0
2623 | 0 | 17 | 17 | 3.8 | 9.9 | 0 | 0 | 0 | 0 | 0.62311 | 0 | 0 | 0.62311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 0.62311
2624 | 0 | 42 | 42 | 4.9 | 9.6 | 0 | 0 | 0 | 0 | 2.3823 | 0 | 0 | 2.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 2.3823
2625 | 0 | 83 | 82 | 3.5 | 9.8 | 0 | 0 | 0 | 0 | 5.0515 | 0 | 0 | 5.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 5.0515
2626 | 0 | 164 | 162 | 1.9 | 10.5 | 0 | 0 | 0 | 0 | 10.4352 | 0 | 0 | 10.4352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 10.4352
2627 | 1 | 360 | 353 | 0.8 | 11.6 | 0 | 0 | 0 | 0 | 23.5095 | 0 | 0 | 23.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 0 | 0 | 6.25 | 10% | 23.5095
2628 | 30 | 580 | 539 | 1 | 13.5 | 0 | 0 | 0 | 0 | 38.1435 | 1.7764e-15 | 5.3367 | 32.8068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530.2125 | 41.57% | 5.3367 | 0 | 11.072 | 17.72% | 32.8068
2629 | 650 | 969 | 373 | 1.8 | 15.6 | 0 | 0 | 0 | 179.6344 | 58.7129 | 13.2871 | 25 | 33.7129 | 0 | 0 | 0 | 0 | 0 | 179.6344 | 0 | 709.8469 | 55.65% | 25 | 0 | 33.661 | 53.86% | 33.7129
2630 | 810 | 949 | 247 | 4.9 | 17.7 | 0 | 0 | 0 | 224.4359 | 58.2352 | 13.7648 | 25 | 33.2352 | 0 | 0 | 0 | 0 | 0 | 224.4359 | 0 | 934.2828 | 73.25% | 25 | 0 | 56.25 | 90% | 33.2352
2631 | 73 | 313 | 250 | 4.4 | 17.2 | 0 | 0 | 0 | 0 | 22.7103 | 0 | 0 | 22.7103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 56.25 | 90% | 22.7103
2632 | 11 | 170 | 163 | 6.2 | 15.6 | 0 | 0 | 0 | 0 | 10.9881 | 0 | 0 | 10.9881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 56.25 | 90% | 10.9881
2633 | 2 | 78 | 77 | 4.8 | 13.8 | 0 | 0 | 0 | 0 | 4.7074 | 0 | 0 | 4.7074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 56.25 | 90% | 4.7074
2634 | 0 | 69 | 68 | 4.3 | 13.5 | 0 | 0 | 0 | 0 | 4.0823 | 0 | 0 | 4.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 25 | 28.5817 | 45.73% | 29.0823
2635 | 0 | 4 | 4 | 4.6 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2636 | 0 | 0 | 0 | 4.1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2637 | 0 | 0 | 0 | 3.8 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2638 | 0 | 0 | 0 | 3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2639 | 0 | 0 | 0 | 3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2640 | 0 | 0 | 0 | 2.8 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2641 | 0 | 0 | 0 | 3.2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2642 | 0 | 0 | 0 | 4.3 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2643 | 0 | 0 | 0 | 4.6 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2644 | 0 | 0 | 0 | 3.4 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2645 | 0 | 0 | 0 | 4.4 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2646 | 0 | 0 | 0 | 4.1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2647 | 0 | 4 | 4 | 2.9 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0
2648 | 0 | 19 | 19 | 3.8 | 11.3 | 0 | 0 | 0 | 0 | 0.84333 | 0 | 0 | 0.84333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 0.84333
2649 | 0 | 40 | 40 | 4.4 | 12.4 | 0 | 0 | 0 | 0 | 2.1945 | 0 | 0 | 2.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 2.1945
2650 | 0 | 68 | 68 | 3.3 | 12.5 | 0 | 0 | 0 | 0 | 4.0069 | 0 | 0 | 4.0069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 4.0069
2651 | 0 | 64 | 64 | 1.4 | 11.8 | 0 | 0 | 0 | 0 | 3.7183 | 0 | 0 | 3.7183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 3.7183
2652 | 0 | 147 | 145 | 1 | 11.9 | 0 | 0 | 0 | 0 | 9.0986 | 0 | 0 | 9.0986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 28.5817 | 45.73% | 9.0986
2653 | 0 | 335 | 327 | 0.9 | 13.6 | 0 | 0 | 0 | 0 | 21.4149 | 0 | 21.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 21.4149 | 0 | 47.9313 | 76.69% | 0
2654 | 1 | 325 | 319 | 0.9 | 14.7 | 0 | 0 | 0 | 0 | 20.8639 | 0 | 9.2066 | 11.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 9.2066 | 0 | 56.25 | 90% | 11.6574
2655 | 1 | 275 | 270 | 1.1 | 15.2 | 0 | 0 | 0 | 0 | 17.5443 | 0 | 0 | 17.5443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 56.25 | 90% | 17.5443
2656 | 1 | 241 | 237 | 0.9 | 15.4 | 0 | 0 | 0 | 0 | 15.329 | 0 | 0 | 15.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 56.25 | 90% | 15.329
2657 | 1 | 111 | 110 | 1.8 | 15.3 | 0 | 0 | 0 | 0 | 6.8295 | 0 | 0 | 6.8295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 934.2828 | 73.25% | 0 | 0 | 56.25 | 90% | 6.8295
2658 | 2 | 97 | 96 | 3 | 14 | 0 | 0 | 0 | 0 | 5.9902 | 0 | 0 | 5.9902 | 0 | 0 | 0 | 81.1032 | 31.6 | 0 | 81.1032 | 853.1796 | 66.89% | 0 | 0 | 56.25 | 90% | 37.5902
2659 | 0 | 14 | 14 | 1.6 | 13.7 | 0 | 0 | 0 | 0 | 0.49275 | 0 | 0 | 0.49275 | 0 | 0 | 0 | 91.1425 | 35.9763 | 0 | 91.1425 | 762.0371 | 59.74% | 0 | 0 | 56.25 | 90% | 36.4691
2660 | 0 | 0 | 0 | 0.7 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4308 | 33.9386 | 0 | 86.4308 | 675.6063 | 52.97% | 0 | 0 | 56.25 | 90% | 33.9386
2661 | 0 | 0 | 0 | 0.8 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9601 | 31.1378 | 0 | 79.9601 | 595.6462 | 46.7% | 0 | 0 | 56.25 | 90% | 31.1378
2662 | 0 | 0 | 0 | 0.3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.6462 | 46.7% | 0 | 11.4015 | 43.6316 | 69.81% | 11.4015
2663 | 0 | 0 | 0 | 0.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.6462 | 46.7% | 0 | 0 | 43.6316 | 69.81% | 0
2664 | 0 | 0 | 0 | 0.7 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.6462 | 46.7% | 0 | 0 | 43.6316 | 69.81% | 0
2665 | 0 | 0 | 0 | 0.3 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.6462 | 46.7% | 0 | 0 | 43.6316 | 69.81% | 0
2666 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.6462 | 46.7% | 0 | 0 | 43.6316 | 69.81% | 0
2667 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595.6462 | 46.7% | 0 | 0 | 43.6316 | 69.81% | 0
2668 | 0 | 0 | 0 | 0.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5095 | 31.415 | 0 | 80.5095 | 515.1367 | 40.39% | 0 | 0 | 43.6316 | 69.81% | 31.415
2669 | 0 | 0 | 0 | 0.5 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8425 | 33.7436 | 0 | 85.8425 | 429.2942 | 33.66% | 0 | 0 | 43.6316 | 69.81% | 33.7436
2670 | 0 | 5 | 6 | 0.9 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5936 | 36.249 | 0 | 91.5936 | 337.7006 | 26.48% | 0 | 0 | 43.6316 | 69.81% | 36.249
2671 | 5 | 79 | 76 | 1.1 | 11.3 | 0 | 0 | 0 | 0 | 3.4013 | 0 | 0 | 3.4013 | 0 | 0 | 0 | 87.4467 | 34.4312 | 0 | 87.4467 | 250.2539 | 19.62% | 0 | 0 | 43.6316 | 69.81% | 37.8325
2672 | 223 | 285 | 179 | 1 | 13.4 | 0 | 0 | 0 | 0 | 14.629 | 0 | 0 | 14.629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250.2539 | 19.62% | 0 | 23.7564 | 17.3396 | 27.74% | 38.3854
2673 | 572 | 594 | 251 | 1.2 | 15.6 | 0 | 0 | 0 | 128.6972 | 37.375 | 0 | 0 | 37.375 | 0 | 0 | 0 | 0 | 0 | 128.6972 | 0 | 378.9511 | 29.71% | 0 | 1.3141 | 15.8853 | 25.42% | 38.689
2674 | 475 | 711 | 350 | 1.8 | 16.4 | 0 | 0 | 0 | 115.1203 | 48.4133 | 0 | 9.3747 | 39.0386 | 0 | 0 | 0 | 0 | 0 | 115.1203 | 0 | 494.0714 | 38.74% | 9.3747 | 0 | 24.3559 | 38.97% | 39.0386
2675 | 102 | 627 | 526 | 2 | 16.9 | 0 | 0 | 0 | 0 | 42.8413 | 0 | 4.9643 | 37.8771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494.0714 | 38.74% | 4.9643 | 0 | 28.8415 | 46.15% | 37.8771
2676 | 37 | 549 | 501 | 3.8 | 17.9 | 0 | 0 | 0 | 0 | 36.3043 | 0 | 0 | 36.3043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494.0714 | 38.74% | 0 | 0 | 28.8415 | 46.15% | 36.3043
2677 | 194 | 558 | 371 | 5.3 | 18.7 | 0 | 0 | 0 | 38.4296 | 41.1923 | 0 | 5.6188 | 35.5736 | 0 | 0 | 0 | 0 | 0 | 38.4296 | 0 | 532.5011 | 41.75% | 5.6188 | 0 | 33.9183 | 54.27% | 35.5736
2678 | 0 | 166 | 163 | 3.4 | 17.5 | 0 | 0 | 0 | 0 | 10.1774 | 0 | 0 | 10.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.5011 | 41.75% | 0 | 0 | 33.9183 | 54.27% | 10.1774
2679 | 0 | 174 | 171 | 3.3 | 17.1 | 0 | 0 | 0 | 0 | 10.7474 | 0 | 0 | 10.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.5011 | 41.75% | 0 | 0 | 33.9183 | 54.27% | 10.7474
2680 | 21 | 219 | 202 | 2.6 | 17.8 | 0 | 0 | 0 | 0 | 14.5052 | 0 | 0 | 14.5052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.5011 | 41.75% | 0 | 0 | 33.9183 | 54.27% | 14.5052
2681 | 3 | 140 | 137 | 3.5 | 17.3 | 0 | 0 | 0 | 0 | 8.7011 | 0 | 0 | 8.7011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532.5011 | 41.75% | 0 | 0 | 33.9183 | 54.27% | 8.7011
2682 | 28 | 78 | 71 | 1.4 | 17.2 | 0 | 0 | 0 | 0 | 4.8401 | 0 | 0 | 4.8401 | 0 | 0 | 0 | 90.2353 | 35.4408 | 0 | 90.2353 | 442.2658 | 34.67% | 0 | 0 | 33.9183 | 54.27% | 40.2809
2683 | 15 | 23 | 21 | 1.2 | 16.2 | 0 | 0 | 0 | 0 | 0.9589 | 0 | 0 | 0.9589 | 0 | 0 | 0 | 93.4866 | 36.8973 | 0 | 93.4866 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 37.8562
2684 | 0 | 0 | 0 | 0.9 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 0
2685 | 0 | 0 | 0 | 1.3 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 0
2686 | 0 | 0 | 0 | 1.2 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 0
2687 | 0 | 0 | 0 | 0.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 0
2688 | 0 | 0 | 0 | 1.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 0
2689 | 0 | 0 | 0 | 0.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 0
2690 | 0 | 0 | 0 | 1.4 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 0
2691 | 0 | 0 | 0 | 0.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 0
2692 | 0 | 0 | 0 | 0.8 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7792 | 27.34% | 0 | 0 | 33.9183 | 54.27% | 0
2693 | 0 | 0 | 0 | 0.9 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5537 | 39.7127 | 0 | 99.5537 | 249.2255 | 19.54% | 0 | 0 | 33.9183 | 54.27% | 39.7127
2694 | 3 | 8 | 8 | 0.9 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7816 | 42.0009 | 0 | 104.7816 | 144.4439 | 11.32% | 0 | 0 | 33.9183 | 54.27% | 42.0009
2695 | 284 | 146 | 82 | 2.7 | 13.2 | 0 | 0 | 0 | 0 | 3.7867 | 0 | 0 | 3.7867 | 0 | 0 | 0 | 98.1389 | 39.0373 | 0 | 98.1389 | 46.305 | 3.63% | 0 | 0 | 33.9183 | 54.27% | 42.8239
2696 | 163 | 218 | 162 | 9.1 | 15.1 | 0 | 0 | 0 | 0 | 12.8301 | 0 | 0 | 12.8301 | 0 | 0 | 0 | 7.1054e-15 | 0 | 0 | 7.1054e-15 | 46.305 | 3.63% | 0 | 25 | 6.25 | 10% | 37.8301
2697 | 1 | 200 | 198 | 9 | 15.4 | 0 | 0 | 0 | 0 | 12.968 | 0 | 0 | 12.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.305 | 3.63% | 0 | 0 | 6.25 | 10% | 12.968
2698 | 35 | 328 | 299 | 7.4 | 16 | 0 | 0 | 0 | 0 | 22.4414 | 0 | 0 | 22.4414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.305 | 3.63% | 0 | 0 | 6.25 | 10% | 22.4414
2699 | 3 | 297 | 290 | 8.7 | 15.8 | 0 | 0 | 0 | 0 | 19.3928 | 0 | 0 | 19.3928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.305 | 3.63% | 0 | 0 | 6.25 | 10% | 19.3928
2700 | 2 | 144 | 141 | 6.7 | 14.1 | 0 | 0 | 0 | 0 | 8.9863 | 0 | 0 | 8.9863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.305 | 3.63% | 0 | 0 | 6.25 | 10% | 8.9863
2701 | 3 | 318 | 309 | 4.8 | 13.7 | 0 | 0 | 0 | 0 | 20.7421 | 0 | 0 | 20.7421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.305 | 3.63% | 0 | 0 | 6.25 | 10% | 20.7421
2702 | 28 | 403 | 371 | 5.7 | 14.8 | 0 | 0 | 0 | 0 | 28.1358 | 0 | 0 | 28.1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.305 | 3.63% | 0 | 0 | 6.25 | 10% | 28.1358
2703 | 35 | 290 | 260 | 5.9 | 14.4 | 0 | 0 | 0 | 0 | 20.195 | 0 | 0 | 20.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.305 | 3.63% | 0 | 0 | 6.25 | 10% | 20.195
2704 | 523 | 513 | 197 | 7.1 | 15.4 | 0 | 0 | 0 | 126.7098 | 44.5182 | 0 | 5.2108 | 39.3074 | 0 | 0 | 0 | 0 | 0 | 126.7098 | 0 | 173.0147 | 13.56% | 5.2108 | 0 | 10.9583 | 17.53% | 39.3074
2705 | 666 | 405 | 88 | 7.3 | 16 | 0 | 0 | 0 | 153.6427 | 34.3763 | 0 | 0 | 34.3763 | 0 | 0 | 0 | 0 | 0 | 153.6427 | 0 | 326.6575 | 25.61% | 0 | 0 | 10.9583 | 17.53% | 34.3763
2706 | 141 | 103 | 72 | 5.9 | 14.2 | 0 | 0 | 0 | 0 | 7.5355 | 0 | 0 | 7.5355 | 0 | 0 | 0 | 91.9695 | 36.319 | 0 | 91.9695 | 234.688 | 18.4% | 0 | 0 | 10.9583 | 17.53% | 43.8545
2707 | 66 | 27 | 22 | 6.6 | 12.8 | 0 | 0 | 0 | 0 | 1.0202 | 0 | 0 | 1.0202 | 0 | 0 | 0 | 100.1195 | 39.9124 | 0 | 100.1195 | 134.5685 | 10.55% | 0 | 0 | 10.9583 | 17.53% | 40.9327
2708 | 0 | 0 | 0 | 5.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0503 | 37.7253 | 0 | 95.0503 | 39.5182 | 3.098% | 0 | 0 | 10.9583 | 17.53% | 37.7253
2709 | 0 | 0 | 0 | 4.7 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 0 | 10.9583 | 17.53% | 0
2710 | 0 | 0 | 0 | 4.7 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 0 | 10.9583 | 17.53% | 0
2711 | 0 | 0 | 0 | 4.2 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 0 | 10.9583 | 17.53% | 0
2712 | 0 | 0 | 0 | 3.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 0 | 10.9583 | 17.53% | 0
2713 | 0 | 0 | 0 | 2.2 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 0 | 10.9583 | 17.53% | 0
2714 | 0 | 0 | 0 | 1.4 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 0 | 10.9583 | 17.53% | 0
2715 | 0 | 0 | 0 | 2 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 0 | 10.9583 | 17.53% | 0
2716 | 0 | 0 | 0 | 2 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 0 | 10.9583 | 17.53% | 0
2717 | 0 | 0 | 0 | 1.5 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 4.2542 | 6.25 | 10% | 4.2542
2718 | 115 | 19 | 9 | 0.7 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5182 | 3.098% | 0 | 0 | 6.25 | 10% | 0
2719 | 632 | 176 | 36 | 0.8 | 9.3 | 0 | 0 | 0 | 77.4152 | 1.9651 | 0 | 0 | 1.9651 | 0 | 0 | 0 | 0 | 0 | 77.4152 | 0 | 116.9334 | 9.168% | 0 | 0 | 6.25 | 10% | 1.9651
2720 | 826 | 391 | 51 | 0.9 | 12.1 | 0 | 0 | 0 | 0 | 15.2811 | 0 | 0 | 15.2811 | 0 | 0 | 0 | 78.6681 | 30.589 | 0 | 78.6681 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 45.8701
2721 | 914 | 598 | 59 | 3.4 | 13.3 | 0 | 0 | 0 | 0 | 33.2495 | 4.0863 | 0 | 33.2495 | 0 | 0 | 0 | 38.2653 | 12.9768 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.2263
2722 | 957 | 771 | 66 | 4.2 | 15 | 0 | 0 | 0 | 0 | 45.8349 | 8.4512 | 0 | 45.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 45.8349
2723 | 968 | 901 | 83 | 4 | 15.9 | 0 | 0 | 0 | 0 | 44.4534 | 21.9911 | 0 | 44.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 44.4534
2724 | 846 | 940 | 172 | 3.6 | 16.5 | 0 | 0 | 0 | 235.3601 | 43.4604 | 28.0217 | 0 | 43.4604 | 0 | 0 | 0 | 0 | 0 | 235.3601 | 0 | 235.3601 | 18.45% | 0 | 0 | 6.25 | 10% | 43.4604
2725 | 827 | 925 | 168 | 4.5 | 17.3 | 0 | 0 | 0 | 91.5738 | 42.9479 | 29.0521 | 0 | 42.9479 | 0 | 0 | 0 | 0 | 0 | 91.5738 | 0 | 326.934 | 25.63% | 0 | 0 | 6.25 | 10% | 42.9479
2726 | 955 | 928 | 100 | 5.9 | 18.3 | 0 | 0 | 0 | 267.3178 | 67.5148 | 4.4852 | 25 | 42.5148 | 0 | 0 | 0 | 0 | 0 | 267.3178 | 0 | 594.2517 | 46.59% | 25 | 0 | 28.839 | 46.14% | 42.5148
2727 | 932 | 810 | 92 | 5.8 | 19.1 | 0 | 0 | 0 | 254.0655 | 67.1443 | 0 | 24.9833 | 42.161 | 0 | 0 | 0 | 0 | 0 | 254.0655 | 0 | 848.3173 | 66.51% | 24.9833 | 0 | 51.4129 | 82.26% | 42.161
2728 | 891 | 638 | 74 | 6 | 18.8 | 0 | 0 | 0 | 232.3736 | 47.903 | 6.4525 | 5.3534 | 42.5496 | 0 | 0 | 0 | 0 | 0 | 232.3736 | 0 | 1080.6909 | 84.73% | 5.3534 | 0 | 56.25 | 90% | 42.5496
2729 | 812 | 438 | 63 | 4.7 | 18.8 | 0 | 0 | 0 | 194.8193 | 37.5341 | 0 | 0 | 37.5341 | 0 | 0 | 0 | 0 | 0 | 194.8193 | 0 | 1275.5102 | 100% | 0 | 6.6171 | 48.9266 | 78.28% | 44.1512
2730 | 653 | 224 | 46 | 4.3 | 18.2 | 0 | 0 | 0 | 0 | 16.1278 | 0 | 0 | 16.1278 | 0 | 0 | 0 | 60.424 | 22.4908 | 0 | 60.424 | 1215.0862 | 95.26% | 0 | 7.6968 | 40.4083 | 64.65% | 46.3154
2731 | 204 | 41 | 16 | 3.4 | 16.7 | 0 | 0 | 0 | 0 | 0.65666 | 0 | 0 | 0.65666 | 0 | 0 | 0 | 105.4626 | 42.067 | 0 | 105.4626 | 1109.6236 | 86.99% | 0 | 0 | 40.4083 | 64.65% | 42.7237
2732 | 0 | 0 | 0 | 3.5 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4516 | 39.0971 | 0 | 98.4516 | 1011.172 | 79.28% | 0 | 0 | 40.4083 | 64.65% | 39.0971
2733 | 0 | 0 | 0 | 4.8 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7854 | 36.2281 | 0 | 91.7854 | 919.3865 | 72.08% | 0 | 0 | 40.4083 | 64.65% | 36.2281
2734 | 0 | 0 | 0 | 3.2 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2818 | 33.8647 | 0 | 86.2818 | 833.1048 | 65.32% | 0 | 0 | 40.4083 | 64.65% | 33.8647
2735 | 0 | 0 | 0 | 1.8 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9795 | 32.4525 | 0 | 82.9795 | 750.1253 | 58.81% | 0 | 0 | 40.4083 | 64.65% | 32.4525
2736 | 0 | 0 | 0 | 3.7 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750.1253 | 58.81% | 0 | 24.0036 | 13.8427 | 22.15% | 24.0036
2737 | 0 | 0 | 0 | 6 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750.1253 | 58.81% | 0 | 0 | 13.8427 | 22.15% | 0
2738 | 0 | 0 | 0 | 5.9 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6314 | 32.252 | 0 | 82.6314 | 667.4939 | 52.33% | 0 | 0 | 13.8427 | 22.15% | 32.252
2739 | 0 | 0 | 0 | 4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5796 | 35.7282 | 0 | 90.5796 | 576.9143 | 45.23% | 0 | 0 | 13.8427 | 22.15% | 35.7282
2740 | 0 | 0 | 0 | 3 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4841 | 39.6193 | 0 | 99.4841 | 477.4303 | 37.43% | 0 | 0 | 13.8427 | 22.15% | 39.6193
2741 | 0 | 0 | 0 | 3.4 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.6816 | 43.2014 | 0 | 107.6816 | 369.7487 | 28.99% | 0 | 0 | 13.8427 | 22.15% | 43.2014
2742 | 15 | 15 | 14 | 4.5 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.2882 | 45.2068 | 0 | 112.2882 | 257.4605 | 20.18% | 0 | 0 | 13.8427 | 22.15% | 45.2068
2743 | 109 | 112 | 85 | 4.1 | 13.7 | 0 | 0 | 0 | 0 | 3.7545 | 0 | 0 | 3.7545 | 0 | 0 | 0 | 104.8117 | 41.9231 | 0 | 104.8117 | 152.6488 | 11.97% | 0 | 0 | 13.8427 | 22.15% | 45.6776
2744 | 29 | 158 | 145 | 3.9 | 14.8 | 0 | 0 | 0 | 0 | 9.6091 | 0 | 0 | 9.6091 | 0 | 0 | 0 | 91.7994 | 36.223 | 0 | 91.7994 | 60.8494 | 4.771% | 0 | 0 | 13.8427 | 22.15% | 45.8322
2745 | 170 | 355 | 244 | 7.5 | 15.8 | 0 | 0 | 0 | 0 | 23.0179 | 0 | 0 | 23.0179 | 0 | 0 | 0 | 60.8494 | 22.7474 | 0 | 60.8494 | 1.1369e-12 | 8.913e-14% | 0 | 0 | 13.8427 | 22.15% | 45.7653
2746 | 280 | 548 | 328 | 8.4 | 17 | 0 | 0 | 0 | 55.3806 | 38.5177 | 0 | 0 | 38.5177 | 0 | 0 | 0 | 0 | 0 | 55.3806 | 0 | 55.3806 | 4.342% | 0 | 6.8605 | 6.25 | 10% | 45.3781
2747 | 685 | 876 | 287 | 8.9 | 18.7 | 0 | 0 | 0 | 176.8638 | 44.3726 | 20.8086 | 0.52224 | 43.8504 | 0 | 0 | 0 | 0 | 0 | 176.8638 | 0 | 232.2444 | 18.21% | 0.52224 | 0 | 6.7219 | 10.75% | 43.8504
2748 | 885 | 986 | 178 | 9.4 | 20.1 | 0 | 0 | 0 | 242.0576 | 67.8253 | 4.1747 | 25 | 42.8253 | 0 | 0 | 0 | 0 | 0 | 242.0576 | 0 | 474.302 | 37.19% | 25 | 0 | 29.3109 | 46.9% | 42.8253
2749 | 824 | 978 | 218 | 8.3 | 20.8 | 0 | 0 | 0 | 227.1009 | 67.3128 | 4.6872 | 25 | 42.3128 | 0 | 0 | 0 | 0 | 0 | 227.1009 | 0 | 701.4029 | 54.99% | 25 | 0 | 51.8999 | 83.04% | 42.3128
2750 | 350 | 595 | 277 | 5.7 | 20.2 | 0 | 0 | 0 | 85.1631 | 46.6885 | 0 | 4.8144 | 41.8741 | 0 | 0 | 0 | 0 | 0 | 85.1631 | 0 | 786.5659 | 61.67% | 4.8144 | 0 | 56.25 | 90% | 41.8741
2751 | 146 | 391 | 274 | 6.1 | 20.2 | 0 | 0 | 0 | 0 | 28.9473 | 0 | 0 | 28.9473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786.5659 | 61.67% | 0 | 12.2945 | 42.6432 | 68.23% | 41.2418
2752 | 773 | 659 | 165 | 6.2 | 21.9 | 0 | 0 | 0 | 166.6016 | 54.5061 | 1.7764e-14 | 12.9871 | 41.519 | 0 | 0 | 0 | 0 | 0 | 166.6016 | 0 | 953.1675 | 74.73% | 12.9871 | 0 | 54.3779 | 87% | 41.519
2753 | 794 | 460 | 92 | 7.5 | 22.4 | 0 | 0 | 0 | 187.777 | 38.8454 | 0 | 0 | 38.8454 | 0 | 0 | 0 | 0 | 0 | 187.777 | 0 | 1140.9445 | 89.45% | 0 | 3.8797 | 50.0841 | 80.13% | 42.7251
2754 | 690 | 232 | 43 | 7.8 | 20.7 | 0 | 0 | 0 | 134.5657 | 16.5753 | 0 | 0 | 16.5753 | 0 | 0 | 0 | 1.2993e-12 | 3.9913e-13 | 134.5657 | 1.2993e-12 | 1275.5102 | 100% | 0 | 25 | 22.4157 | 35.87% | 41.5753
2755 | 223 | 42 | 16 | 7.7 | 18.8 | 0 | 0 | 0 | 0 | 0.71315 | 0 | 0 | 0.71315 | 0 | 0 | 0 | 87.4871 | 34.17 | 0 | 87.4871 | 1188.0231 | 93.14% | 0 | 7.4157 | 14.2085 | 22.73% | 42.2989
2756 | 0 | 0 | 0 | 6.4 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9422 | 39.2029 | 0 | 98.9422 | 1089.0809 | 85.38% | 0 | 0 | 14.2085 | 22.73% | 39.2029
2757 | 0 | 0 | 0 | 4.9 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4876 | 36.4593 | 0 | 92.4876 | 996.5934 | 78.13% | 0 | 0 | 14.2085 | 22.73% | 36.4593
2758 | 0 | 0 | 0 | 3.3 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6715 | 33.9567 | 0 | 86.6715 | 909.9219 | 71.34% | 0 | 0 | 14.2085 | 22.73% | 33.9567
2759 | 0 | 0 | 0 | 2.3 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1739 | 32.4846 | 0 | 83.1739 | 826.748 | 64.82% | 0 | 0 | 14.2085 | 22.73% | 32.4846
2760 | 0 | 0 | 0 | 1.4 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.322 | 31.7283 | 0 | 81.322 | 745.426 | 58.44% | 0 | 0 | 14.2085 | 22.73% | 31.7283
2761 | 0 | 0 | 0 | 1.7 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6222 | 28.8265 | 0 | 74.6222 | 670.8038 | 52.59% | 0 | 0 | 14.2085 | 22.73% | 28.8265
2762 | 0 | 0 | 0 | 2.2 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1 | 32.5347 | 0 | 83.1 | 587.7038 | 46.08% | 0 | 0 | 14.2085 | 22.73% | 32.5347
2763 | 0 | 0 | 0 | 2.2 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4211 | 35.7254 | 0 | 90.4211 | 497.2827 | 38.99% | 0 | 0 | 14.2085 | 22.73% | 35.7254
2764 | 0 | 0 | 0 | 0.7 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1407 | 40.0023 | 0 | 100.1407 | 397.142 | 31.14% | 0 | 0 | 14.2085 | 22.73% | 40.0023
2765 | 0 | 0 | 0 | 1.4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.8317 | 42.9284 | 0 | 106.8317 | 290.3103 | 22.76% | 0 | 0 | 14.2085 | 22.73% | 42.9284
2766 | 111 | 22 | 10 | 1.8 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.011 | 44.3099 | 0 | 110.011 | 180.2993 | 14.14% | 0 | 0 | 14.2085 | 22.73% | 44.3099
2767 | 620 | 184 | 42 | 1.7 | 11.5 | 0 | 0 | 0 | 0 | 2.4024 | 0 | 0 | 2.4024 | 0 | 0 | 0 | 105.1749 | 42.1527 | 0 | 105.1749 | 75.1244 | 5.89% | 0 | 0 | 14.2085 | 22.73% | 44.5551
2768 | 801 | 400 | 63 | 0.9 | 14.7 | 0 | 0 | 0 | 0 | 15.6146 | 0 | 0 | 15.6146 | 0 | 0 | 0 | 75.1244 | 28.9794 | 0 | 75.1244 | 0 | 0% | 0 | 0 | 14.2085 | 22.73% | 44.5941
2769 | 876 | 603 | 81 | 3 | 16.1 | 0 | 0 | 0 | 0 | 37.2248 | 0 | 0 | 37.2248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 7.191 | 6.25 | 10% | 44.4158
2770 | 909 | 783 | 105 | 3.8 | 17.2 | 0 | 0 | 0 | 0 | 43.9367 | 10.1628 | 0 | 43.9367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 43.9367
2771 | 939 | 915 | 114 | 3.6 | 18.3 | 0 | 0 | 0 | 0 | 42.3003 | 23.6531 | 0 | 42.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 42.3003
2772 | 948 | 997 | 132 | 2.6 | 19 | 0 | 0 | 0 | 261.6474 | 41.2906 | 30.7094 | 0 | 41.2906 | 0 | 0 | 0 | 0 | 0 | 261.6474 | 0 | 261.6474 | 20.51% | 0 | 0 | 6.25 | 10% | 41.2906
2773 | 719 | 879 | 211 | 2.1 | 19.9 | 0 | 0 | 0 | 0 | 40.3881 | 25.7155 | 0 | 40.3881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261.6474 | 20.51% | 0 | 0 | 6.25 | 10% | 40.3881
2774 | 867 | 929 | 173 | 4.8 | 20.2 | 0 | 0 | 0 | 241.8334 | 56.3529 | 15.6471 | 16.4759 | 39.877 | 0 | 0 | 0 | 0 | 0 | 241.8334 | 0 | 503.4808 | 39.47% | 16.4759 | 0 | 21.1369 | 33.82% | 39.877
2775 | 897 | 827 | 130 | 4.2 | 20 | 0 | 0 | 0 | 245.2087 | 64.3909 | 2.0157 | 25 | 39.3909 | 0 | 0 | 0 | 0 | 0 | 245.2087 | 0 | 748.6895 | 58.7% | 25 | 0 | 43.7259 | 69.96% | 39.3909
2776 | 855 | 645 | 99 | 4.2 | 19.7 | 0 | 0 | 0 | 223.8268 | 53.3729 | 0 | 13.8608 | 39.5121 | 0 | 0 | 0 | 0 | 0 | 223.8268 | 0 | 972.5163 | 76.25% | 13.8608 | 0 | 56.25 | 90% | 39.5121
2777 | 780 | 442 | 76 | 4.2 | 19.4 | 0 | 0 | 0 | 187.0712 | 36.9712 | 0 | 0 | 36.9712 | 0 | 0 | 0 | 0 | 0 | 187.0712 | 0 | 1159.5874 | 90.91% | 0 | 3.35 | 52.5424 | 84.07% | 40.3213
2778 | 603 | 225 | 57 | 3.9 | 18.7 | 0 | 0 | 0 | 0 | 15.7848 | 0 | 0 | 15.7848 | 0 | 0 | 0 | 71.5078 | 27.2661 | 0 | 71.5078 | 1088.0797 | 85.31% | 0 | 0 | 52.5424 | 84.07% | 43.0509
2779 | 196 | 44 | 20 | 2.2 | 17.5 | 0 | 0 | 0 | 0 | 0.86057 | 0 | 0 | 0.86057 | 0 | 0 | 0 | 65.1523 | 24.5615 | 0 | 65.1523 | 1022.9273 | 80.2% | 0 | 15.5941 | 35.2839 | 56.45% | 41.0162
2780 | 0 | 0 | 0 | 1.2 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4867 | 38.235 | 0 | 96.4867 | 926.4407 | 72.63% | 0 | 0 | 35.2839 | 56.45% | 38.235
2781 | 0 | 0 | 0 | 1.2 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4259 | 36.0861 | 0 | 91.4259 | 835.0148 | 65.47% | 0 | 0 | 35.2839 | 56.45% | 36.0861
2782 | 0 | 0 | 0 | 1.7 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7842 | 33.66 | 0 | 85.7842 | 749.2306 | 58.74% | 0 | 0 | 35.2839 | 56.45% | 33.66
2783 | 0 | 0 | 0 | 0.8 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7897 | 31.9345 | 0 | 81.7897 | 667.441 | 52.33% | 0 | 0 | 35.2839 | 56.45% | 31.9345
2784 | 0 | 0 | 0 | 2.3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3108 | 30.8551 | 0 | 79.3108 | 588.1302 | 46.11% | 0 | 0 | 35.2839 | 56.45% | 30.8551
2785 | 0 | 0 | 0 | 2.4 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3972 | 30.4666 | 0 | 78.3972 | 509.733 | 39.96% | 0 | 0 | 35.2839 | 56.45% | 30.4666
2786 | 0 | 0 | 0 | 1.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0002 | 30.2981 | 0 | 78.0002 | 431.7328 | 33.85% | 0 | 0 | 35.2839 | 56.45% | 30.2981
2787 | 0 | 0 | 0 | 1.1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7498 | 31.0766 | 0 | 79.7498 | 351.983 | 27.6% | 0 | 0 | 35.2839 | 56.45% | 31.0766
2788 | 0 | 0 | 0 | 1.2 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4958 | 31.8467 | 0 | 81.4958 | 270.4872 | 21.21% | 0 | 0 | 35.2839 | 56.45% | 31.8467
2789 | 0 | 0 | 0 | 1.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1548 | 33.8898 | 0 | 86.1548 | 184.3323 | 14.45% | 0 | 0 | 35.2839 | 56.45% | 33.8898
2790 | 110 | 23 | 11 | 1.8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6699 | 36.7142 | 0 | 92.6699 | 91.6624 | 7.186% | 0 | 0 | 35.2839 | 56.45% | 36.7142
2791 | 623 | 186 | 40 | 0.1 | 14 | 0 | 0 | 0 | 0 | 2.2097 | 0 | 0 | 2.2097 | 0 | 0 | 0 | 91.6624 | 36.1924 | 0 | 91.6624 | 0 | 0% | 0 | 0 | 35.2839 | 56.45% | 38.4021
2792 | 815 | 401 | 55 | 1 | 16.8 | 0 | 0 | 0 | 0 | 15.1444 | 0 | 0 | 15.1444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 23.6909 | 9.0644 | 14.5% | 38.8353
2793 | 902 | 607 | 64 | 1.9 | 18.9 | 0 | 0 | 0 | 0 | 36.1252 | 0 | 0 | 36.1252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 2.543 | 6.25 | 10% | 38.6681
2794 | 953 | 782 | 68 | 2.4 | 19.9 | 0 | 0 | 0 | 0 | 38.3785 | 13.9594 | 0 | 38.3785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.3785
2795 | 984 | 909 | 68 | 2.5 | 20.6 | 0 | 0 | 0 | 0 | 37.3186 | 26.5816 | 0 | 37.3186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 37.3186
2796 | 992 | 977 | 70 | 2.6 | 21.3 | 0 | 0 | 0 | 0 | 35.5262 | 35.2346 | 0 | 35.5262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 35.5262
2797 | 988 | 981 | 72 | 2.7 | 21.7 | 0 | 0 | 0 | 0 | 34.2784 | 37.7216 | 0 | 34.2784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 34.2784
2798 | 977 | 926 | 72 | 3.9 | 22.2 | 0 | 0 | 0 | 147.2388 | 41.5626 | 30.3842 | 7.9137 | 33.6489 | 0 | 0 | 0 | 0 | 0 | 147.2388 | 0 | 147.2388 | 11.54% | 7.9137 | 0 | 13.4005 | 21.44% | 33.6489
2799 | 958 | 814 | 68 | 4.9 | 22.4 | 0 | 0 | 0 | 262.5072 | 58.5932 | 6.9385 | 25 | 33.5932 | 0 | 0 | 0 | 0 | 0 | 262.5072 | 0 | 409.746 | 32.12% | 25 | 0 | 35.9895 | 57.58% | 33.5932
2800 | 923 | 653 | 61 | 4.6 | 22 | 0 | 0 | 0 | 242.9732 | 53.7322 | 0 | 19.7825 | 33.9497 | 0 | 0 | 0 | 0 | 0 | 242.9732 | 0 | 652.7192 | 51.17% | 19.7825 | 0 | 53.8642 | 86.18% | 33.9497
2801 | 848 | 453 | 54 | 5.7 | 20.8 | 0 | 0 | 0 | 203.8111 | 37.8338 | 0 | 2.6405 | 35.1934 | 0 | 0 | 0 | 0 | 0 | 203.8111 | 0 | 856.5303 | 67.15% | 2.6405 | 0 | 56.25 | 90% | 35.1934
2802 | 690 | 236 | 43 | 5.4 | 19.6 | 0 | 0 | 0 | 137.2632 | 16.4356 | 0 | 0 | 16.4356 | 0 | 0 | 0 | 0 | 0 | 137.2632 | 0 | 993.7935 | 77.91% | 0 | 21.851 | 32.0668 | 51.31% | 38.2865
2803 | 256 | 48 | 17 | 5.2 | 17.6 | 0 | 0 | 0 | 0 | 0.78476 | 0 | 0 | 0.78476 | 0 | 0 | 0 | 79.1466 | 30.6188 | 0 | 79.1466 | 914.6469 | 71.71% | 0 | 5.8761 | 25.5636 | 40.9% | 37.2796
2804 | 0 | 0 | 0 | 2.8 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2353 | 35.0778 | 0 | 89.2353 | 825.4116 | 64.71% | 0 | 0 | 25.5636 | 40.9% | 35.0778
2805 | 0 | 0 | 0 | 2.1 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6952 | 32.7241 | 0 | 83.6952 | 741.7164 | 58.15% | 0 | 0 | 25.5636 | 40.9% | 32.7241
2806 | 0 | 0 | 0 | 1.7 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2536 | 30.39 | 0 | 78.2536 | 663.4628 | 52.02% | 0 | 0 | 25.5636 | 40.9% | 30.39
2807 | 0 | 0 | 0 | 0.8 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8093 | 28.8928 | 0 | 74.8093 | 588.6535 | 46.15% | 0 | 0 | 25.5636 | 40.9% | 28.8928
2808 | 0 | 0 | 0 | 1.4 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.3412 | 27.8204 | 0 | 72.3412 | 516.3123 | 40.48% | 0 | 0 | 25.5636 | 40.9% | 27.8204
2809 | 0 | 0 | 0 | 1.6 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4216 | 27.4263 | 0 | 71.4216 | 444.8907 | 34.88% | 0 | 0 | 25.5636 | 40.9% | 27.4263
2810 | 0 | 0 | 0 | 0.9 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.0104 | 27.2675 | 0 | 71.0104 | 373.8803 | 29.31% | 0 | 0 | 25.5636 | 40.9% | 27.2675
2811 | 0 | 0 | 0 | 0.9 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.7905 | 27.6213 | 0 | 71.7905 | 302.0898 | 23.68% | 0 | 0 | 25.5636 | 40.9% | 27.6213
2812 | 0 | 0 | 0 | 1.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.5765 | 27.5266 | 0 | 71.5765 | 230.5133 | 18.07% | 0 | 0 | 25.5636 | 40.9% | 27.5266
2813 | 0 | 0 | 0 | 1.7 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5909 | 28.8315 | 0 | 74.5909 | 155.9223 | 12.22% | 0 | 0 | 25.5636 | 40.9% | 28.8315
2814 | 125 | 32 | 17 | 1.6 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3899 | 30.9178 | 0 | 79.3899 | 76.5325 | 6% | 0 | 0 | 25.5636 | 40.9% | 30.9178
2815 | 409 | 160 | 61 | 1.5 | 13.4 | 0 | 0 | 0 | 0 | 3.0416 | 0 | 0 | 3.0416 | 0 | 0 | 0 | 76.5325 | 29.6282 | 0 | 76.5325 | 0 | 0% | 0 | 0 | 25.5636 | 40.9% | 32.6698
2816 | 777 | 403 | 69 | 3 | 16.4 | 0 | 0 | 0 | 0 | 15.8163 | 0 | 0 | 15.8163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 17.451 | 6.25 | 10% | 33.2673
2817 | 865 | 605 | 80 | 4.3 | 18.7 | 0 | 0 | 0 | 203.4709 | 33.1586 | 3.5062 | 0 | 33.1586 | 0 | 0 | 0 | 0 | 0 | 203.4709 | 0 | 203.4709 | 15.95% | 0 | 0 | 6.25 | 10% | 33.1586
2818 | 963 | 791 | 67 | 4.3 | 20.6 | 0 | 0 | 0 | 250.7209 | 33.1085 | 20.381 | 0 | 33.1085 | 0 | 0 | 0 | 0 | 0 | 250.7209 | 0 | 454.1917 | 35.61% | 0 | 0 | 6.25 | 10% | 33.1085
2819 | 948 | 902 | 87 | 4.6 | 22 | 0 | 0 | 0 | 257.7782 | 32.8954 | 31.3741 | 0 | 32.8954 | 0 | 0 | 0 | 0 | 0 | 257.7782 | 0 | 711.9699 | 55.82% | 0 | 0 | 6.25 | 10% | 32.8954
2820 | 964 | 976 | 92 | 5.6 | 22.3 | 0 | 0 | 0 | 0 | 31.4596 | 40.5404 | 0 | 31.4596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711.9699 | 55.82% | 0 | 0 | 6.25 | 10% | 31.4596
2821 | 908 | 958 | 118 | 6.6 | 22.3 | 0 | 0 | 0 | 254.3132 | 30.5195 | 41.4805 | 0 | 30.5195 | 0 | 0 | 0 | 0 | 0 | 254.3132 | 0 | 966.2831 | 75.76% | 0 | 0 | 6.25 | 10% | 30.5195
2822 | 923 | 932 | 121 | 7.2 | 22.7 | 0 | 0 | 0 | 256.5457 | 34.4922 | 37.5078 | 4.4086 | 30.0836 | 0 | 0 | 0 | 0 | 0 | 256.5457 | 0 | 1222.8288 | 95.87% | 4.4086 | 0 | 10.2334 | 16.37% | 30.0836
2823 | 937 | 829 | 96 | 7.1 | 22.9 | 0 | 0 | 0 | 52.6814 | 55.6588 | 11.1777 | 25 | 30.6588 | 0 | 0 | 0 | 0 | 0 | 52.6814 | 0 | 1275.5102 | 100% | 25 | 0 | 32.8224 | 52.52% | 30.6588
2824 | 886 | 657 | 86 | 6.8 | 22.6 | 0 | 0 | 0 | 0 | 54.0123 | 0 | 22.3216 | 31.6907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 22.3216 | 0 | 52.9913 | 84.79% | 31.6907
2825 | 789 | 453 | 79 | 6.5 | 21.6 | 0 | 0 | 0 | 0 | 37.364 | 0 | 3.6065 | 33.7575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 3.6065 | 0 | 56.25 | 90% | 33.7575
2826 | 661 | 241 | 52 | 5.5 | 20.3 | 0 | 0 | 0 | 0 | 16.3526 | 0 | 0 | 16.3526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 11.977 | 42.9946 | 68.79% | 28.3296
2827 | 227 | 50 | 21 | 5.1 | 18 | 0 | 0 | 0 | 0 | 0.91984 | 0 | 0 | 0.91984 | 0 | 0 | 0 | 91.183 | 35.8111 | 0 | 91.183 | 1184.3272 | 92.85% | 0 | 0 | 42.9946 | 68.79% | 36.7309
2828 | 0 | 0 | 0 | 4.6 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8476 | 34.4831 | 0 | 87.8476 | 1096.4796 | 85.96% | 0 | 0 | 42.9946 | 68.79% | 34.4831
2829 | 0 | 0 | 0 | 2.4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.865 | 31.9373 | 0 | 81.865 | 1014.6146 | 79.55% | 0 | 0 | 42.9946 | 68.79% | 31.9373
2830 | 0 | 0 | 0 | 2.8 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6102 | 30.0891 | 0 | 77.6102 | 937.0043 | 73.46% | 0 | 0 | 42.9946 | 68.79% | 30.0891
2831 | 0 | 0 | 0 | 2.4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.9745 | 0 | 38.2653 | 898.739 | 70.46% | 0 | 0 | 42.9946 | 68.79% | 12.9745
2832 | 0 | 0 | 0 | 1.4 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2788 | 27.7866 | 0 | 72.2788 | 826.4602 | 64.79% | 0 | 0 | 42.9946 | 68.79% | 27.7866
2833 | 0 | 0 | 0 | 1.4 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.5564 | 28.3427 | 0 | 73.5564 | 752.9038 | 59.03% | 0 | 0 | 42.9946 | 68.79% | 28.3427
2834 | 0 | 0 | 0 | 0.8 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0975 | 29.4847 | 0 | 76.0975 | 676.8064 | 53.06% | 0 | 0 | 42.9946 | 68.79% | 29.4847
2835 | 0 | 0 | 0 | 1.4 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4786 | 33.1224 | 0 | 84.4786 | 592.3278 | 46.44% | 0 | 0 | 42.9946 | 68.79% | 33.1224
2836 | 0 | 0 | 0 | 2.4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4578 | 36.9802 | 0 | 93.4578 | 498.87 | 39.11% | 0 | 0 | 42.9946 | 68.79% | 36.9802
2837 | 0 | 0 | 0 | 1.7 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1905 | 39.9369 | 0 | 100.1905 | 398.6795 | 31.26% | 0 | 0 | 42.9946 | 68.79% | 39.9369
2838 | 0 | 15 | 15 | 2.3 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3818 | 41.3156 | 0 | 103.3818 | 295.2977 | 23.15% | 0 | 0 | 42.9946 | 68.79% | 41.3156
2839 | 72 | 122 | 102 | 2.3 | 15.1 | 0 | 0 | 0 | 0 | 4.3901 | 0 | 0 | 4.3901 | 0 | 0 | 0 | 94.5364 | 37.4004 | 0 | 94.5364 | 200.7613 | 15.74% | 0 | 0 | 42.9946 | 68.79% | 41.7906
2840 | 246 | 318 | 207 | 3.7 | 16.9 | 0 | 0 | 0 | 25.9807 | 16.59 | 0 | 0 | 16.59 | 0 | 0 | 0 | 0 | 0 | 25.9807 | 0 | 226.7421 | 17.78% | 0 | 25 | 15.3263 | 24.52% | 41.59
2841 | 521 | 548 | 220 | 4.5 | 18.7 | 0 | 0 | 0 | 114.9983 | 34.0004 | 0 | 0 | 34.0004 | 0 | 0 | 0 | 0 | 0 | 114.9983 | 0 | 341.7403 | 26.79% | 0 | 8.201 | 6.25 | 10% | 42.2014
2842 | 597 | 739 | 283 | 5.1 | 20.1 | 0 | 0 | 0 | 147.4278 | 42.0078 | 8.7318 | 0 | 42.0078 | 0 | 0 | 0 | 0 | 0 | 147.4278 | 0 | 489.1682 | 38.35% | 0 | 0 | 6.25 | 10% | 42.0078
2843 | 298 | 698 | 434 | 5.2 | 20.6 | 0 | 0 | 0 | 66.9871 | 49.6265 | 0 | 8.5184 | 41.1081 | 0 | 0 | 0 | 0 | 0 | 66.9871 | 0 | 556.1553 | 43.6% | 8.5184 | 0 | 13.9469 | 22.31% | 41.1081
2844 | 520 | 819 | 329 | 5.8 | 20.7 | 0 | 0 | 0 | 135.6016 | 46.3093 | 14.5118 | 6.1426 | 40.1667 | 0 | 0 | 0 | 0 | 0 | 135.6016 | 0 | 691.7569 | 54.23% | 6.1426 | 0 | 19.4971 | 31.2% | 40.1667
2845 | 756 | 945 | 240 | 5.3 | 21.7 | 0 | 0 | 0 | 209.2004 | 64.5609 | 7.4391 | 25 | 39.5609 | 0 | 0 | 0 | 0 | 0 | 209.2004 | 0 | 900.9574 | 70.64% | 25 | 0 | 42.0861 | 67.34% | 39.5609
2846 | 317 | 674 | 385 | 4.5 | 21.9 | 0 | 0 | 0 | 75.9578 | 50.0839 | 0 | 10.9896 | 39.0943 | 0 | 0 | 0 | 0 | 0 | 75.9578 | 0 | 976.9151 | 76.59% | 10.9896 | 0 | 52.0158 | 83.23% | 39.0943
2847 | 291 | 579 | 341 | 4.3 | 21.8 | 0 | 0 | 0 | 66.4249 | 43.1161 | 0 | 4.6861 | 38.43 | 0 | 0 | 0 | 0 | 0 | 66.4249 | 0 | 1043.34 | 81.8% | 4.6861 | 0 | 56.25 | 90% | 38.43
2848 | 167 | 417 | 309 | 4.1 | 21.4 | 0 | 0 | 0 | 0 | 30.2477 | 0 | 0 | 30.2477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1043.34 | 81.8% | 0 | 2.0178 | 54.0169 | 86.43% | 32.2655
2849 | 404 | 362 | 179 | 4.6 | 20.7 | 0 | 0 | 0 | 87.67 | 28.8751 | 0 | 0 | 28.8751 | 0 | 0 | 0 | 0 | 0 | 87.67 | 0 | 1131.01 | 88.67% | 0 | 10.7721 | 42.095 | 67.35% | 39.6472
2850 | 547 | 226 | 64 | 4.7 | 19.9 | 0 | 0 | 0 | 105.591 | 14.8503 | 0 | 0 | 14.8503 | 0 | 0 | 0 | 0 | 0 | 105.591 | 0 | 1236.601 | 96.95% | 0 | 25 | 14.4267 | 23.08% | 39.8503
2851 | 247 | 58 | 27 | 4.4 | 18.1 | 0 | 0 | 0 | 0 | 1.2751 | 0 | 0 | 1.2751 | 0 | 0 | 0 | 97.3189 | 38.4613 | 0 | 97.3189 | 1139.2821 | 89.32% | 0 | 0 | 14.4267 | 23.08% | 39.7363
2852 | 0 | 0 | 0 | 4.3 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1036 | 36.3396 | 0 | 92.1036 | 1047.1785 | 82.1% | 0 | 0 | 14.4267 | 23.08% | 36.3396
2853 | 0 | 0 | 0 | 3.1 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1379 | 34.231 | 0 | 87.1379 | 960.0406 | 75.27% | 0 | 0 | 14.4267 | 23.08% | 34.231
2854 | 0 | 0 | 0 | 2.1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2488 | 32.1267 | 0 | 82.2488 | 877.7917 | 68.82% | 0 | 0 | 14.4267 | 23.08% | 32.1267
2855 | 0 | 0 | 0 | 1.9 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.416 | 30.9081 | 0 | 79.416 | 798.3757 | 62.59% | 0 | 0 | 14.4267 | 23.08% | 30.9081
2856 | 0 | 0 | 0 | 0.8 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2482 | 30.4039 | 0 | 78.2482 | 720.1275 | 56.46% | 0 | 0 | 14.4267 | 23.08% | 30.4039
2857 | 0 | 0 | 0 | 1.2 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1991 | 30.3969 | 0 | 78.1991 | 641.9284 | 50.33% | 0 | 0 | 14.4267 | 23.08% | 30.3969
2858 | 0 | 0 | 0 | 1 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6174 | 31.0278 | 0 | 79.6174 | 562.3109 | 44.09% | 0 | 0 | 14.4267 | 23.08% | 31.0278
2859 | 0 | 0 | 0 | 1.4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.184 | 34.3146 | 0 | 87.184 | 475.127 | 37.25% | 0 | 0 | 14.4267 | 23.08% | 34.3146
2860 | 0 | 0 | 0 | 1.8 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3566 | 37.8715 | 0 | 95.3566 | 379.7704 | 29.77% | 0 | 0 | 14.4267 | 23.08% | 37.8715
2861 | 0 | 0 | 0 | 1.3 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5169 | 41.0218 | 0 | 102.5169 | 277.2535 | 21.74% | 0 | 0 | 14.4267 | 23.08% | 41.0218
2862 | 99 | 26 | 14 | 1.4 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.7635 | 42.4312 | 0 | 105.7635 | 171.49 | 13.44% | 0 | 0 | 14.4267 | 23.08% | 42.4312
2863 | 572 | 187 | 48 | 0.5 | 14.3 | 0 | 0 | 0 | 0 | 2.5017 | 0 | 0 | 2.5017 | 0 | 0 | 0 | 100.3647 | 39.9657 | 0 | 100.3647 | 71.1252 | 5.576% | 0 | 0 | 14.4267 | 23.08% | 42.4674
2864 | 760 | 398 | 69 | 0.6 | 16.7 | 0 | 0 | 0 | 0 | 15.362 | 0 | 0 | 15.362 | 0 | 0 | 0 | 71.1252 | 27.1779 | 0 | 71.1252 | 0 | 0% | 0 | 0 | 14.4267 | 23.08% | 42.5398
2865 | 848 | 600 | 84 | 1.6 | 18.7 | 0 | 0 | 0 | 0 | 35.6029 | 0 | 0 | 35.6029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 7.3881 | 6.25 | 10% | 42.9911
2866 | 898 | 771 | 92 | 2.3 | 20 | 0 | 0 | 0 | 233.9811 | 42.9493 | 8.2568 | 0 | 42.9493 | 0 | 0 | 0 | 0 | 0 | 233.9811 | 0 | 233.9811 | 18.34% | 0 | 0 | 6.25 | 10% | 42.9493
2867 | 924 | 894 | 99 | 2.6 | 21.3 | 0 | 0 | 0 | 252.3731 | 41.9117 | 20.4914 | 0 | 41.9117 | 0 | 0 | 0 | 0 | 0 | 252.3731 | 0 | 486.3542 | 38.13% | 0 | 0 | 6.25 | 10% | 41.9117
2868 | 938 | 965 | 102 | 2.6 | 22.5 | 0 | 0 | 0 | 263.7155 | 41.0106 | 28.0365 | 0 | 41.0106 | 0 | 0 | 0 | 0 | 0 | 263.7155 | 0 | 750.0697 | 58.81% | 0 | 0 | 6.25 | 10% | 41.0106
2869 | 929 | 969 | 109 | 3.5 | 23.1 | 0 | 0 | 0 | 0 | 40.3867 | 31.5831 | 0 | 40.3867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750.0697 | 58.81% | 0 | 0 | 6.25 | 10% | 40.3867
2870 | 905 | 911 | 114 | 4.7 | 23.5 | 0 | 0 | 0 | 253.3512 | 65.0051 | 5.0859 | 25 | 40.0051 | 0 | 0 | 0 | 0 | 0 | 253.3512 | 0 | 1003.4209 | 78.67% | 25 | 0 | 28.839 | 46.14% | 40.0051
2871 | 864 | 797 | 118 | 5.1 | 23.5 | 0 | 0 | 0 | 39.7405 | 58.0865 | 4.8223 | 18.8961 | 39.1904 | 0 | 0 | 0 | 0 | 0 | 39.7405 | 0 | 1043.1614 | 81.78% | 18.8961 | 0 | 45.9128 | 73.46% | 39.1904
2872 | 795 | 628 | 112 | 3.5 | 23.8 | 0 | 0 | 0 | 0 | 50.1198 | 0 | 11.4405 | 38.6793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1043.1614 | 81.78% | 11.4405 | 0 | 56.25 | 90% | 38.6793
2873 | 713 | 439 | 98 | 3.5 | 23.6 | 0 | 0 | 0 | 0 | 34.9447 | 0 | 0 | 34.9447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1043.1614 | 81.78% | 0 | 4.3725 | 51.4109 | 82.26% | 39.3171
2874 | 501 | 273 | 124 | 5 | 21.4 | 0 | 0 | 0 | 0 | 17.8026 | 0 | 0 | 17.8026 | 0 | 0 | 0 | 62.8421 | 23.41 | 0 | 62.8421 | 980.3193 | 76.86% | 0 | 0 | 51.4109 | 82.26% | 41.2126
2875 | 93 | 54 | 42 | 4.7 | 18.4 | 0 | 0 | 0 | 0 | 2.156 | 0 | 0 | 2.156 | 0 | 0 | 0 | 90.5634 | 35.5218 | 0 | 90.5634 | 889.7559 | 69.76% | 0 | 1.2982 | 49.9741 | 79.96% | 38.9759
2876 | 0 | 0 | 0 | 3.7 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3299 | 35.9788 | 0 | 91.3299 | 798.426 | 62.6% | 0 | 0 | 49.9741 | 79.96% | 35.9788
2877 | 0 | 0 | 0 | 3.8 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.9635 | 0 | 38.2653 | 760.1607 | 59.6% | 0 | 20.982 | 26.7527 | 42.8% | 33.9455
2878 | 0 | 0 | 0 | 3.9 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6691 | 31.8662 | 0 | 81.6691 | 678.4916 | 53.19% | 0 | 0 | 26.7527 | 42.8% | 31.8662
2879 | 0 | 0 | 0 | 2.8 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6806 | 30.1476 | 0 | 77.6806 | 600.811 | 47.1% | 0 | 0 | 26.7527 | 42.8% | 30.1476
2880 | 0 | 0 | 0 | 2.7 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.6506 | 29.2786 | 0 | 75.6506 | 525.1605 | 41.17% | 0 | 0 | 26.7527 | 42.8% | 29.2786
2881 | 0 | 0 | 0 | 2.8 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6422 | 28.8469 | 0 | 74.6422 | 450.5183 | 35.32% | 0 | 0 | 26.7527 | 42.8% | 28.8469
2882 | 0 | 0 | 0 | 2.9 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2708 | 28.2578 | 0 | 73.2708 | 377.2475 | 29.58% | 0 | 0 | 26.7527 | 42.8% | 28.2578
2883 | 0 | 0 | 0 | 2.2 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5512 | 27.9472 | 0 | 72.5512 | 304.6962 | 23.89% | 0 | 0 | 26.7527 | 42.8% | 27.9472
2884 | 0 | 0 | 0 | 2.4 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2953 | 27.8386 | 0 | 72.2953 | 232.401 | 18.22% | 0 | 0 | 26.7527 | 42.8% | 27.8386
2885 | 0 | 0 | 0 | 3.8 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2342 | 29.1184 | 0 | 75.2342 | 157.1668 | 12.32% | 0 | 0 | 26.7527 | 42.8% | 29.1184
2886 | 51 | 22 | 16 | 2.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.375 | 31.3509 | 0 | 80.375 | 76.7918 | 6.02% | 0 | 0 | 26.7527 | 42.8% | 31.3509
2887 | 430 | 182 | 70 | 2.9 | 12.9 | 0 | 0 | 0 | 0 | 3.5917 | 0 | 0 | 3.5917 | 0 | 0 | 0 | 76.7918 | 29.7536 | 0 | 76.7918 | 0 | 0% | 0 | 0 | 26.7527 | 42.8% | 33.3453
2888 | 729 | 398 | 78 | 3 | 15 | 0 | 0 | 0 | 140.8752 | 15.7126 | 0 | 0 | 15.7126 | 0 | 0 | 0 | 0 | 0 | 140.8752 | 0 | 140.8752 | 11.04% | 0 | 18.5254 | 6.25 | 10% | 34.238
2889 | 845 | 604 | 85 | 3.9 | 17.9 | 0 | 0 | 0 | 0 | 34.6544 | 1.6191 | 0 | 34.6544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.8752 | 11.04% | 0 | 0 | 6.25 | 10% | 34.6544
2890 | 891 | 779 | 101 | 4.8 | 20 | 0 | 0 | 0 | 230.2386 | 34.9608 | 17.5825 | 0 | 34.9608 | 0 | 0 | 0 | 0 | 0 | 230.2386 | 0 | 371.1139 | 29.1% | 0 | 0 | 6.25 | 10% | 34.9608
2891 | 810 | 869 | 164 | 5.2 | 21.5 | 0 | 0 | 0 | 0 | 34.2603 | 27.8639 | 0 | 34.2603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371.1139 | 29.1% | 0 | 0 | 6.25 | 10% | 34.2603
2892 | 815 | 965 | 208 | 5.9 | 22.6 | 0 | 0 | 0 | 223.9579 | 32.4275 | 38.5732 | 0 | 32.4275 | 0 | 0 | 0 | 0 | 0 | 223.9579 | 0 | 595.0718 | 46.65% | 0 | 0 | 6.25 | 10% | 32.4275
2893 | 826 | 952 | 181 | 6 | 23.2 | 0 | 0 | 0 | 229.8513 | 31.4373 | 40.5627 | 0 | 31.4373 | 0 | 0 | 0 | 0 | 0 | 229.8513 | 0 | 824.9231 | 64.67% | 0 | 0 | 6.25 | 10% | 31.4373
2894 | 862 | 906 | 143 | 5.7 | 23.8 | 0 | 0 | 0 | 220.0362 | 38.2073 | 31.3165 | 7.1558 | 31.0515 | 0 | 0 | 0 | 0 | 0 | 220.0362 | 0 | 1044.9593 | 81.92% | 7.1558 | 0 | 12.7157 | 20.35% | 31.0515
2895 | 852 | 796 | 125 | 5.6 | 24.3 | 0 | 0 | 0 | 230.5509 | 56.2033 | 6.3688 | 25 | 31.2033 | 0 | 0 | 0 | 0 | 0 | 230.5509 | 0 | 1275.5102 | 100% | 25 | 0 | 35.3047 | 56.49% | 31.2033
2896 | 875 | 651 | 82 | 5.6 | 24.3 | 0 | 0 | 0 | 0 | 52.2731 | 0 | 20.3721 | 31.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 20.3721 | 0 | 53.7121 | 85.94% | 31.901
2897 | 815 | 457 | 66 | 5.8 | 23.7 | 0 | 0 | 0 | 0 | 36.7055 | 0 | 2.8088 | 33.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 2.8088 | 0 | 56.25 | 90% | 33.8968
2898 | 645 | 241 | 52 | 5.4 | 21.8 | 0 | 0 | 0 | 0 | 15.7486 | 0 | 0 | 15.7486 | 0 | 0 | 0 | 53.8723 | 19.5346 | 0 | 53.8723 | 1221.6379 | 95.78% | 0 | 1.6259 | 54.4505 | 87.12% | 36.9092
2899 | 80 | 34 | 22 | 5 | 19.1 | 0 | 0 | 0 | 0 | 0.89242 | 0 | 0 | 0.89242 | 0 | 0 | 0 | 89.6036 | 35.0683 | 0 | 89.6036 | 1132.0343 | 88.75% | 0 | 0 | 54.4505 | 87.12% | 35.9607
2900 | 0 | 0 | 0 | 5.6 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8167 | 33.5653 | 0 | 85.8167 | 1046.2176 | 82.02% | 0 | 0 | 54.4505 | 87.12% | 33.5653
2901 | 0 | 0 | 0 | 5.2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.2176 | 82.02% | 0 | 0 | 54.4505 | 87.12% | 0
2902 | 0 | 0 | 0 | 4.4 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.2176 | 82.02% | 0 | 0 | 54.4505 | 87.12% | 0
2903 | 0 | 0 | 0 | 4.4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.2176 | 82.02% | 0 | 0 | 54.4505 | 87.12% | 0
2904 | 0 | 0 | 0 | 3.1 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.2176 | 82.02% | 0 | 0 | 54.4505 | 87.12% | 0
2905 | 0 | 0 | 0 | 2.1 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.2176 | 82.02% | 0 | 0 | 54.4505 | 87.12% | 0
2906 | 0 | 0 | 0 | 2.1 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.2176 | 82.02% | 0 | 0 | 54.4505 | 87.12% | 0
2907 | 0 | 0 | 0 | 2.3 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.2176 | 82.02% | 0 | 0 | 54.4505 | 87.12% | 0
2908 | 0 | 0 | 0 | 2.4 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1069 | 35.529 | 0 | 90.1069 | 956.1107 | 74.96% | 0 | 0 | 54.4505 | 87.12% | 35.529
2909 | 0 | 0 | 0 | 2.4 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8664 | 38.4801 | 0 | 96.8664 | 859.2443 | 67.36% | 0 | 0 | 54.4505 | 87.12% | 38.4801
2910 | 23 | 25 | 22 | 2.7 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4514 | 39.9954 | 0 | 100.4514 | 758.7929 | 59.49% | 0 | 0 | 54.4505 | 87.12% | 39.9954
2911 | 218 | 165 | 103 | 4.1 | 15.2 | 0 | 0 | 0 | 0 | 4.9732 | 0 | 0 | 4.9732 | 0 | 0 | 0 | 91.937 | 36.2672 | 0 | 91.937 | 666.8558 | 52.28% | 0 | 0 | 54.4505 | 87.12% | 41.2404
2912 | 426 | 335 | 138 | 2.2 | 18.3 | 0 | 0 | 0 | 75.1867 | 14.9772 | 0 | 0 | 14.9772 | 0 | 0 | 0 | 0 | 0 | 75.1867 | 0 | 742.0425 | 58.18% | 0 | 25 | 26.7822 | 42.85% | 39.9772
2913 | 574 | 547 | 193 | 6.1 | 20.1 | 0 | 0 | 0 | 127.6603 | 33.9714 | 0 | 0 | 33.9714 | 0 | 0 | 0 | 0 | 0 | 127.6603 | 0 | 869.7028 | 68.18% | 0 | 8.2425 | 17.6599 | 28.26% | 42.2139
2914 | 762 | 771 | 190 | 6.7 | 21.5 | 0 | 0 | 0 | 192.6611 | 52.8618 | 0 | 10.6855 | 42.1763 | 0 | 0 | 0 | 0 | 0 | 192.6611 | 0 | 1062.3639 | 83.29% | 10.6855 | 0 | 27.3149 | 43.7% | 42.1763
2915 | 522 | 745 | 290 | 7.2 | 22.3 | 0 | 0 | 0 | 130.8869 | 53.9397 | 0 | 12.6115 | 41.3282 | 0 | 0 | 0 | 0 | 0 | 130.8869 | 0 | 1193.2508 | 93.55% | 12.6115 | 0 | 38.7101 | 61.94% | 41.3282
2916 | 326 | 752 | 435 | 6.8 | 22.9 | 0 | 0 | 0 | 76.2855 | 53.8963 | 0 | 13.5514 | 40.3449 | 0 | 0 | 0 | 0 | 0 | 76.2855 | 0 | 1269.5363 | 99.53% | 13.5514 | 0 | 50.9546 | 81.53% | 40.3449
2917 | 141 | 589 | 446 | 7.1 | 23.2 | 0 | 0 | 0 | 0 | 41.7915 | 0 | 2.0371 | 39.7544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.5363 | 99.53% | 2.0371 | 0 | 52.7952 | 84.47% | 39.7544
2918 | 27 | 415 | 384 | 7.3 | 21.8 | 0 | 0 | 0 | 0 | 27.0476 | 0 | 0 | 27.0476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.5363 | 99.53% | 0 | 12.5369 | 38.9202 | 62.27% | 39.5845
2919 | 13 | 312 | 298 | 8.3 | 20.8 | 0 | 0 | 0 | 0 | 20.1371 | 0 | 0 | 20.1371 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 1269.5363 | 99.53% | 0 | 18.8263 | 18.0846 | 28.94% | 38.9634
2920 | 23 | 281 | 263 | 8.5 | 19.7 | 0 | 0 | 0 | 0 | 18.2623 | 0 | 0 | 18.2623 | 0 | 0 | 0 | 56.4437 | 20.7192 | 0 | 56.4437 | 1213.0926 | 95.11% | 0 | 0 | 18.0846 | 28.94% | 38.9815
2921 | 110 | 272 | 220 | 7.1 | 19.2 | 0 | 0 | 0 | 0 | 19.2541 | 0 | 0 | 19.2541 | 0 | 0 | 0 | 56.5776 | 20.7941 | 0 | 56.5776 | 1156.515 | 90.67% | 0 | 0 | 18.0846 | 28.94% | 40.0483
2922 | 93 | 161 | 134 | 5.7 | 18.5 | 0 | 0 | 0 | 0 | 10.36 | 0 | 0 | 10.36 | 0 | 0 | 0 | 81.941 | 31.787 | 0 | 81.941 | 1074.5741 | 84.25% | 0 | 0 | 18.0846 | 28.94% | 42.1471
2923 | 38 | 40 | 34 | 4.8 | 17.3 | 0 | 0 | 0 | 0 | 1.7553 | 0 | 0 | 1.7553 | 0 | 0 | 0 | 96.055 | 37.9574 | 0 | 96.055 | 978.5191 | 76.72% | 0 | 0 | 18.0846 | 28.94% | 39.7127
2924 | 0 | 0 | 0 | 3.4 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2826 | 36.4092 | 0 | 92.2826 | 886.2365 | 69.48% | 0 | 0 | 18.0846 | 28.94% | 36.4092
2925 | 0 | 0 | 0 | 3.8 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4592 | 34.3369 | 0 | 87.4592 | 798.7773 | 62.62% | 0 | 0 | 18.0846 | 28.94% | 34.3369
2926 | 0 | 0 | 0 | 4.4 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8543 | 32.777 | 0 | 83.8543 | 714.923 | 56.05% | 0 | 0 | 18.0846 | 28.94% | 32.777
2927 | 0 | 0 | 0 | 3.1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.923 | 56.05% | 0 | 0 | 18.0846 | 28.94% | 0
2928 | 0 | 0 | 0 | 2.3 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.923 | 56.05% | 0 | 3.5064 | 14.204 | 22.73% | 3.5064
2929 | 0 | 0 | 0 | 1.5 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2491 | 30.383 | 0 | 78.2491 | 636.6739 | 49.92% | 0 | 0 | 14.204 | 22.73% | 30.383
2930 | 0 | 0 | 0 | 1.2 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8724 | 31.1114 | 0 | 79.8724 | 556.8015 | 43.65% | 0 | 0 | 14.204 | 22.73% | 31.1114
2931 | 0 | 0 | 0 | 0.8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2496 | 33.894 | 0 | 86.2496 | 470.5518 | 36.89% | 0 | 0 | 14.204 | 22.73% | 33.894
2932 | 0 | 0 | 0 | 1.2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9925 | 37.2671 | 0 | 93.9925 | 376.5594 | 29.52% | 0 | 0 | 14.204 | 22.73% | 37.2671
2933 | 0 | 0 | 0 | 1.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6901 | 40.2307 | 0 | 100.6901 | 275.8693 | 21.63% | 0 | 0 | 14.204 | 22.73% | 40.2307
2934 | 105 | 27 | 15 | 2.4 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5995 | 41.9145 | 0 | 104.5995 | 171.2698 | 13.43% | 0 | 0 | 14.204 | 22.73% | 41.9145
2935 | 540 | 190 | 49 | 2.9 | 13.3 | 0 | 0 | 0 | 0 | 2.5579 | 0 | 0 | 2.5579 | 0 | 0 | 0 | 100.8069 | 40.195 | 0 | 100.8069 | 70.4629 | 5.524% | 0 | 0 | 14.204 | 22.73% | 42.7529
2936 | 788 | 419 | 71 | 4.2 | 15.4 | 0 | 0 | 0 | 0 | 16.2461 | 0 | 0 | 16.2461 | 0 | 0 | 0 | 70.4629 | 26.933 | 0 | 70.4629 | 0 | 0% | 0 | 0 | 14.204 | 22.73% | 43.1791
2937 | 814 | 611 | 104 | 3.3 | 17.5 | 0 | 0 | 0 | 0 | 36.4086 | 0 | 0 | 36.4086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 7.1869 | 6.25 | 10% | 43.5955
2938 | 924 | 797 | 91 | 1.4 | 19.7 | 0 | 0 | 0 | 0 | 43.3629 | 8.1204 | 0 | 43.3629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 43.3629
2939 | 948 | 925 | 101 | 1.7 | 21.4 | 0 | 0 | 0 | 259.8146 | 42.1234 | 20.4522 | 0 | 42.1234 | 0 | 0 | 0 | 0 | 0 | 259.8146 | 0 | 259.8146 | 20.37% | 0 | 0 | 6.25 | 10% | 42.1234
2940 | 861 | 956 | 157 | 2.2 | 22.3 | 0 | 0 | 0 | 240.744 | 40.8978 | 26.8838 | 0 | 40.8978 | 0 | 0 | 0 | 0 | 0 | 240.744 | 0 | 500.5586 | 39.24% | 0 | 0 | 6.25 | 10% | 40.8978
2941 | 860 | 953 | 150 | 4.1 | 22.5 | 0 | 0 | 0 | 201.174 | 61.5902 | 8.8486 | 21.3205 | 40.2697 | 0 | 0 | 0 | 0 | 0 | 201.174 | 0 | 701.7326 | 55.02% | 21.3205 | 0 | 25.5143 | 40.82% | 40.2697
2942 | 902 | 937 | 138 | 5.9 | 22.1 | 0 | 0 | 0 | 251.2661 | 64.8422 | 7.1578 | 25 | 39.8422 | 0 | 0 | 0 | 0 | 0 | 251.2661 | 0 | 952.9988 | 74.72% | 25 | 0 | 48.1033 | 76.97% | 39.8422
2943 | 481 | 603 | 222 | 7.1 | 19.9 | 0 | 0 | 0 | 119.9082 | 48.4127 | 0 | 9.0162 | 39.3965 | 0 | 0 | 0 | 0 | 0 | 119.9082 | 0 | 1072.907 | 84.12% | 9.0162 | 0 | 56.25 | 90% | 39.3965
2944 | 427 | 436 | 162 | 6.9 | 18.9 | 0 | 0 | 0 | 99.579 | 35.4227 | 0 | 0 | 35.4227 | 0 | 0 | 0 | 0 | 0 | 99.579 | 0 | 1172.486 | 91.92% | 0 | 3.861 | 51.9769 | 83.16% | 39.2837
2945 | 433 | 332 | 114 | 5.3 | 18.6 | 0 | 0 | 0 | 94.8044 | 25.7001 | 0 | 0 | 25.7001 | 0 | 0 | 0 | 0 | 0 | 94.8044 | 0 | 1267.2904 | 99.36% | 0 | 14.0864 | 36.3871 | 58.22% | 39.7865
2946 | 449 | 225 | 86 | 4 | 18.8 | 0 | 0 | 0 | 0 | 14.3569 | 0 | 0 | 14.3569 | 0 | 0 | 0 | 70.9387 | 27.0159 | 0 | 70.9387 | 1196.3517 | 93.79% | 0 | 0 | 36.3871 | 58.22% | 41.3728
2947 | 1 | 11 | 11 | 4.8 | 16.1 | 0 | 0 | 0 | 0 | 0.30866 | 0 | 0 | 0.30866 | 0 | 0 | 0 | 98.5788 | 39.1115 | 0 | 98.5788 | 1097.7729 | 86.07% | 0 | 0 | 36.3871 | 58.22% | 39.4202
2948 | 0 | 0 | 0 | 4.2 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6528 | 36.6125 | 0 | 92.6528 | 1005.1201 | 78.8% | 0 | 0 | 36.3871 | 58.22% | 36.6125
2949 | 0 | 0 | 0 | 3.6 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2426 | 34.7017 | 0 | 88.2426 | 916.8775 | 71.88% | 0 | 0 | 36.3871 | 58.22% | 34.7017
2950 | 0 | 0 | 0 | 3.4 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9706 | 32.8439 | 0 | 83.9706 | 832.9069 | 65.3% | 0 | 0 | 36.3871 | 58.22% | 32.8439
2951 | 0 | 0 | 0 | 5.2 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3475 | 31.2771 | 0 | 80.3475 | 752.5594 | 59% | 0 | 0 | 36.3871 | 58.22% | 31.2771
2952 | 0 | 0 | 0 | 4.4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2409 | 30.3607 | 0 | 78.2409 | 674.3185 | 52.87% | 0 | 0 | 36.3871 | 58.22% | 30.3607
2953 | 0 | 0 | 0 | 4.1 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1398 | 29.8872 | 0 | 77.1398 | 597.1787 | 46.82% | 0 | 0 | 36.3871 | 58.22% | 29.8872
2954 | 0 | 0 | 0 | 4.1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0549 | 29.8705 | 0 | 77.0549 | 520.1238 | 40.78% | 0 | 0 | 36.3871 | 58.22% | 29.8705
2955 | 0 | 0 | 0 | 3.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7675 | 30.6323 | 0 | 78.7675 | 441.3563 | 34.6% | 0 | 0 | 36.3871 | 58.22% | 30.6323
2956 | 0 | 0 | 0 | 2.7 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7273 | 31.0459 | 0 | 79.7273 | 361.6289 | 28.35% | 0 | 0 | 36.3871 | 58.22% | 31.0459
2957 | 0 | 0 | 0 | 3 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7828 | 33.6809 | 0 | 85.7828 | 275.8461 | 21.63% | 0 | 0 | 36.3871 | 58.22% | 33.6809
2958 | 0 | 7 | 7 | 3 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8627 | 36.7615 | 0 | 92.8627 | 182.9834 | 14.35% | 0 | 0 | 36.3871 | 58.22% | 36.7615
2959 | 16 | 90 | 84 | 2.8 | 13 | 0 | 0 | 0 | 0 | 4.2879 | 0 | 0 | 4.2879 | 0 | 0 | 0 | 71.46 | 27.4302 | 0 | 71.46 | 111.5234 | 8.743% | 0 | 7.0783 | 28.5533 | 45.69% | 38.7963
2960 | 4 | 174 | 171 | 2.2 | 13.9 | 0 | 0 | 0 | 0 | 10.7798 | 0 | 0 | 10.7798 | 0 | 0 | 0 | 73.2581 | 28.1905 | 0 | 73.2581 | 38.2653 | 3% | 0 | 0 | 28.5533 | 45.69% | 38.9704
2961 | 53 | 313 | 278 | 1.9 | 15.2 | 0 | 0 | 0 | 0 | 20.2475 | 0 | 0 | 20.2475 | 0 | 0 | 0 | 38.2653 | 12.9526 | 0 | 38.2653 | 0 | 0% | 0 | 5.6838 | 22.2628 | 35.62% | 38.884
2962 | 18 | 372 | 352 | 2.8 | 15.8 | 0 | 0 | 0 | 0 | 24.0645 | 0 | 0 | 24.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 14.4685 | 6.25 | 10% | 38.533
2963 | 398 | 769 | 408 | 4.4 | 18 | 0 | 0 | 0 | 0 | 37.8242 | 15.8502 | 0 | 37.8242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 37.8242
2964 | 843 | 1004 | 217 | 6.5 | 18.8 | 0 | 0 | 0 | 231.756 | 36.1376 | 35.8624 | 0 | 36.1376 | 0 | 0 | 0 | 0 | 0 | 231.756 | 0 | 231.756 | 18.17% | 0 | 0 | 6.25 | 10% | 36.1376
2965 | 898 | 992 | 150 | 6 | 19.3 | 0 | 0 | 0 | 251.7796 | 35.0625 | 36.9375 | 0 | 35.0625 | 0 | 0 | 0 | 0 | 0 | 251.7796 | 0 | 483.5356 | 37.91% | 0 | 0 | 6.25 | 10% | 35.0625
2966 | 918 | 935 | 117 | 6.3 | 19.6 | 0 | 0 | 0 | 255.5984 | 45.6735 | 26.3265 | 11.2015 | 34.472 | 0 | 0 | 0 | 0 | 0 | 255.5984 | 0 | 739.134 | 57.95% | 11.2015 | 0 | 16.3712 | 26.19% | 34.472
2967 | 895 | 824 | 112 | 7.2 | 19 | 0 | 0 | 0 | 241.7819 | 59.2477 | 6.3654 | 25 | 34.2477 | 0 | 0 | 0 | 0 | 0 | 241.7819 | 0 | 980.9159 | 76.9% | 25 | 0 | 38.9602 | 62.34% | 34.2477
2968 | 839 | 659 | 107 | 6.8 | 18.5 | 0 | 0 | 0 | 58.1096 | 53.1799 | 0 | 18.5882 | 34.5917 | 0 | 0 | 0 | 0 | 0 | 58.1096 | 0 | 1039.0255 | 81.46% | 18.5882 | 0 | 55.7558 | 89.21% | 34.5917
2969 | 718 | 454 | 101 | 6.7 | 17.8 | 0 | 0 | 0 | 0 | 36.1192 | 0 | 0.54699 | 35.5722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1039.0255 | 81.46% | 0.54699 | 0 | 56.25 | 90% | 35.5722
2970 | 70 | 123 | 97 | 6 | 15.9 | 0 | 0 | 0 | 0 | 7.5013 | 0 | 0 | 7.5013 | 0 | 0 | 0 | 38.2653 | 12.9422 | 0 | 38.2653 | 1000.7602 | 78.46% | 0 | 17.9461 | 36.3885 | 58.22% | 38.3896
2971 | 0 | 27 | 27 | 4.3 | 15.1 | 0 | 0 | 0 | 0 | 1.3239 | 0 | 0 | 1.3239 | 0 | 0 | 0 | 74.2043 | 28.5674 | 0 | 74.2043 | 926.5559 | 72.64% | 0 | 7.3772 | 28.2239 | 45.16% | 37.2685
2972 | 0 | 0 | 0 | 2.4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.662 | 34.8522 | 0 | 88.662 | 837.8939 | 65.69% | 0 | 0 | 28.2239 | 45.16% | 34.8522
2973 | 0 | 0 | 0 | 1.5 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2038 | 32.5041 | 0 | 83.2038 | 754.6901 | 59.17% | 0 | 0 | 28.2239 | 45.16% | 32.5041
2974 | 0 | 0 | 0 | 1.3 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4334 | 30.4554 | 0 | 78.4334 | 676.2567 | 53.02% | 0 | 0 | 28.2239 | 45.16% | 30.4554
2975 | 0 | 0 | 0 | 0.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2465 | 29.0808 | 0 | 75.2465 | 601.0101 | 47.12% | 0 | 0 | 28.2239 | 45.16% | 29.0808
2976 | 0 | 0 | 0 | 0.9 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.0556 | 28.138 | 0 | 73.0556 | 527.9545 | 41.39% | 0 | 0 | 28.2239 | 45.16% | 28.138
2977 | 0 | 0 | 0 | 1.2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.9692 | 27.6728 | 0 | 71.9692 | 455.9853 | 35.75% | 0 | 0 | 28.2239 | 45.16% | 27.6728
2978 | 0 | 0 | 0 | 1.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0843 | 27.723 | 0 | 72.0843 | 383.901 | 30.1% | 0 | 0 | 28.2239 | 45.16% | 27.723
2979 | 0 | 0 | 0 | 1.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9283 | 28.0906 | 0 | 72.9283 | 310.9727 | 24.38% | 0 | 0 | 28.2239 | 45.16% | 28.0906
2980 | 0 | 0 | 0 | 1.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.3318 | 27.8288 | 0 | 72.3318 | 238.6409 | 18.71% | 0 | 0 | 28.2239 | 45.16% | 27.8288
2981 | 0 | 0 | 0 | 1.4 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.6264 | 29.2661 | 0 | 75.6264 | 163.0145 | 12.78% | 0 | 0 | 28.2239 | 45.16% | 29.2661
2982 | 143 | 36 | 15 | 2.1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6866 | 31.8537 | 0 | 81.6866 | 81.3278 | 6.376% | 0 | 0 | 28.2239 | 45.16% | 31.8537
2983 | 647 | 212 | 44 | 1.1 | 17.4 | 0 | 0 | 0 | 0 | 2.4248 | 0 | 0 | 2.4248 | 0 | 0 | 0 | 81.3278 | 31.5723 | 0 | 81.3278 | 0 | 0% | 0 | 0 | 28.2239 | 45.16% | 33.997
2984 | 810 | 425 | 60 | 0.8 | 20.4 | 0 | 0 | 0 | 0 | 15.234 | 0 | 0 | 15.234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 19.6975 | 6.424 | 10.28% | 34.9315
2985 | 897 | 628 | 67 | 0.8 | 22.8 | 0 | 0 | 0 | 0 | 34.9122 | 0 | 0 | 34.9122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0.15722 | 6.25 | 10% | 35.0694
2986 | 931 | 793 | 76 | 3.1 | 23.9 | 0 | 0 | 0 | 0 | 35.0569 | 16.0686 | 0 | 35.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 35.0569
2987 | 920 | 908 | 103 | 6.6 | 22.9 | 0 | 0 | 0 | 0 | 34.4135 | 29.3606 | 0 | 34.4135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 34.4135
2988 | 910 | 980 | 130 | 5.9 | 23 | 0 | 0 | 0 | 252.639 | 32.8829 | 37.9524 | 0 | 32.8829 | 0 | 0 | 0 | 0 | 0 | 252.639 | 0 | 252.639 | 19.81% | 0 | 0 | 6.25 | 10% | 32.8829
2989 | 903 | 997 | 149 | 6 | 23.6 | 0 | 0 | 0 | 167.8185 | 32.0723 | 39.9277 | 0 | 32.0723 | 0 | 0 | 0 | 0 | 0 | 167.8185 | 0 | 420.4576 | 32.96% | 0 | 0 | 6.25 | 10% | 32.0723
2990 | 700 | 848 | 218 | 5.6 | 23.8 | 0 | 0 | 0 | 190.6494 | 43.5018 | 21.2538 | 11.6649 | 31.837 | 0 | 0 | 0 | 0 | 0 | 190.6494 | 0 | 611.107 | 47.91% | 11.6649 | 0 | 16.7899 | 26.86% | 31.837
2991 | 860 | 820 | 131 | 4.1 | 25.1 | 0 | 0 | 0 | 234.2408 | 57.018 | 5.1372 | 25 | 32.018 | 0 | 0 | 0 | 0 | 0 | 234.2408 | 0 | 845.3478 | 66.28% | 25 | 0 | 39.3789 | 63.01% | 32.018
2992 | 829 | 658 | 109 | 5.4 | 25 | 0 | 0 | 0 | 215.1353 | 51.253 | 0 | 18.4383 | 32.8146 | 0 | 0 | 0 | 0 | 0 | 215.1353 | 0 | 1060.4831 | 83.14% | 18.4383 | 0 | 56.039 | 89.66% | 32.8146
2993 | 724 | 449 | 92 | 4.8 | 23.9 | 0 | 0 | 0 | 0 | 34.6734 | 0 | 0.23348 | 34.4399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060.4831 | 83.14% | 0.23348 | 0 | 56.25 | 90% | 34.4399
2994 | 578 | 239 | 63 | 4.9 | 22.2 | 0 | 0 | 0 | 114.172 | 14.8937 | 0 | 0 | 14.8937 | 0 | 0 | 0 | 0 | 0 | 114.172 | 0 | 1174.6551 | 92.09% | 0 | 22.794 | 31.0232 | 49.64% | 37.6877
2995 | 222 | 56 | 26 | 3.2 | 20 | 0 | 0 | 0 | 0 | 1.1401 | 0 | 0 | 1.1401 | 0 | 0 | 0 | 55.6382 | 20.3611 | 0 | 55.6382 | 1119.0169 | 87.73% | 0 | 15.809 | 13.5268 | 21.64% | 37.3103
2996 | 0 | 0 | 0 | 2.4 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5858 | 34.7212 | 0 | 88.5858 | 1030.4311 | 80.79% | 0 | 0 | 13.5268 | 21.64% | 34.7212
2997 | 0 | 0 | 0 | 1 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.893 | 32.3202 | 0 | 82.893 | 947.538 | 74.29% | 0 | 0 | 13.5268 | 21.64% | 32.3202
2998 | 0 | 0 | 0 | 1.1 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8432 | 30.5989 | 0 | 78.8432 | 868.6948 | 68.11% | 0 | 0 | 13.5268 | 21.64% | 30.5989
2999 | 0 | 0 | 0 | 0.4 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.366 | 29.5251 | 0 | 76.366 | 792.3288 | 62.12% | 0 | 0 | 13.5268 | 21.64% | 29.5251
3000 | 0 | 0 | 0 | 0.7 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4334 | 29.1045 | 0 | 75.4334 | 716.8954 | 56.2% | 0 | 0 | 13.5268 | 21.64% | 29.1045
3001 | 0 | 0 | 0 | 1 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7266 | 29.209 | 0 | 75.7266 | 641.1688 | 50.27% | 0 | 0 | 13.5268 | 21.64% | 29.209
3002 | 0 | 0 | 0 | 0.5 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8969 | 30.1616 | 0 | 77.8969 | 563.2719 | 44.16% | 0 | 0 | 13.5268 | 21.64% | 30.1616
3003 | 0 | 0 | 0 | 1.3 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2774 | 33.7895 | 0 | 86.2774 | 476.9945 | 37.4% | 0 | 0 | 13.5268 | 21.64% | 33.7895
3004 | 0 | 0 | 0 | 0.7 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.674 | 37.9147 | 0 | 95.674 | 381.3205 | 29.9% | 0 | 0 | 13.5268 | 21.64% | 37.9147
3005 | 0 | 0 | 0 | 2 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.346 | 41.214 | 0 | 103.346 | 277.9745 | 21.79% | 0 | 0 | 13.5268 | 21.64% | 41.214
3006 | 121 | 36 | 18 | 2 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3524 | 42.505 | 0 | 106.3524 | 171.6222 | 13.46% | 0 | 0 | 13.5268 | 21.64% | 42.505
3007 | 594 | 209 | 52 | 1.2 | 18.8 | 0 | 0 | 0 | 0 | 2.6821 | 0 | 0 | 2.6821 | 0 | 0 | 0 | 100.9496 | 39.99 | 0 | 100.9496 | 70.6726 | 5.541% | 0 | 0 | 13.5268 | 21.64% | 42.6721
3008 | 779 | 423 | 72 | 1.6 | 18.4 | 0 | 0 | 0 | 0 | 15.8369 | 0 | 0 | 15.8369 | 0 | 0 | 0 | 70.6726 | 26.9174 | 0 | 70.6726 | 0 | 0% | 0 | 0 | 13.5268 | 21.64% | 42.7543
3009 | 860 | 623 | 86 | 1.9 | 19.3 | 0 | 0 | 0 | 0 | 35.9509 | 0 | 0 | 35.9509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 6.575 | 6.25 | 10% | 42.5259
3010 | 904 | 791 | 96 | 3 | 20.7 | 0 | 0 | 0 | 0 | 42.888 | 8.7958 | 0 | 42.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 42.888
3011 | 937 | 917 | 97 | 3 | 23.6 | 0 | 0 | 0 | 255.9838 | 42.0273 | 20.3257 | 0 | 42.0273 | 0 | 0 | 0 | 0 | 0 | 255.9838 | 0 | 255.9838 | 20.07% | 0 | 0 | 6.25 | 10% | 42.0273
3012 | 941 | 986 | 108 | 2.7 | 25.6 | 0 | 0 | 0 | 97.9861 | 41.0817 | 27.3144 | 0 | 41.0817 | 0 | 0 | 0 | 0 | 0 | 97.9861 | 0 | 353.9699 | 27.75% | 0 | 0 | 6.25 | 10% | 41.0817
3013 | 935 | 999 | 122 | 5.6 | 26.2 | 0 | 0 | 0 | 263.4385 | 44.7341 | 27.2659 | 4.2889 | 40.4452 | 0 | 0 | 0 | 0 | 0 | 263.4385 | 0 | 617.4084 | 48.4% | 4.2889 | 0 | 10.1253 | 16.2% | 40.4452
3014 | 869 | 929 | 151 | 5.7 | 26.4 | 0 | 0 | 0 | 241.4752 | 65.2781 | 4.0122 | 25 | 40.2781 | 0 | 0 | 0 | 0 | 0 | 241.4752 | 0 | 858.8836 | 67.34% | 25 | 0 | 32.7143 | 52.34% | 40.2781
3015 | 635 | 760 | 248 | 6.4 | 25.9 | 0 | 0 | 0 | 166.1334 | 58.0472 | 0 | 18.3958 | 39.6514 | 0 | 0 | 0 | 0 | 0 | 166.1334 | 0 | 1025.017 | 80.36% | 18.3958 | 0 | 49.3359 | 78.94% | 39.6514
3016 | 611 | 617 | 209 | 5.5 | 25 | 0 | 0 | 0 | 153.2445 | 47.3354 | 0 | 7.652 | 39.6834 | 0 | 0 | 0 | 0 | 0 | 153.2445 | 0 | 1178.2614 | 92.38% | 7.652 | 0 | 56.25 | 90% | 39.6834
3017 | 440 | 394 | 174 | 5 | 23.9 | 0 | 0 | 0 | 97.2488 | 29.1554 | 0 | 0 | 29.1554 | 0 | 0 | 0 | 0 | 0 | 97.2488 | 0 | 1275.5102 | 100% | 0 | 11.7118 | 43.2882 | 69.26% | 40.8672
3018 | 377 | 243 | 126 | 4 | 22.4 | 0 | 0 | 0 | 0 | 15.1831 | 0 | 0 | 15.1831 | 0 | 0 | 0 | 73.4961 | 27.9402 | 0 | 73.4961 | 1202.0141 | 94.24% | 0 | 0 | 43.2882 | 69.26% | 43.1234
3019 | 66 | 50 | 38 | 3 | 19.8 | 0 | 0 | 0 | 0 | 1.9876 | 0 | 0 | 1.9876 | 0 | 0 | 0 | 90.7258 | 35.5123 | 0 | 90.7258 | 1111.2883 | 87.13% | 0 | 3.1347 | 39.8189 | 63.71% | 40.6346
3020 | 0 | 0 | 0 | 1.7 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0474 | 37.0721 | 0 | 94.0474 | 1017.2409 | 79.75% | 0 | 0 | 39.8189 | 63.71% | 37.0721
3021 | 0 | 0 | 0 | 1 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7941 | 34.8438 | 0 | 88.7941 | 928.4468 | 72.79% | 0 | 0 | 39.8189 | 63.71% | 34.8438
3022 | 0 | 0 | 0 | 0.5 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6657 | 33.082 | 0 | 84.6657 | 843.7811 | 66.15% | 0 | 0 | 39.8189 | 63.71% | 33.082
3023 | 0 | 0 | 0 | 0.3 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0461 | 31.9707 | 0 | 82.0461 | 761.735 | 59.72% | 0 | 0 | 39.8189 | 63.71% | 31.9707
3024 | 0 | 0 | 0 | 0.5 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.94 | 31.5167 | 0 | 80.94 | 680.795 | 53.37% | 0 | 0 | 39.8189 | 63.71% | 31.5167
3025 | 0 | 0 | 0 | 0.7 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6194 | 31.4094 | 0 | 80.6194 | 600.1755 | 47.05% | 0 | 0 | 39.8189 | 63.71% | 31.4094
3026 | 0 | 0 | 0 | 0.9 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0839 | 32.0626 | 0 | 82.0839 | 518.0916 | 40.62% | 0 | 0 | 39.8189 | 63.71% | 32.0626
3027 | 0 | 0 | 0 | 0.9 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5082 | 34.8396 | 0 | 88.5082 | 429.5834 | 33.68% | 0 | 0 | 39.8189 | 63.71% | 34.8396
3028 | 0 | 0 | 0 | 1.2 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3196 | 38.6807 | 0 | 97.3196 | 332.2638 | 26.05% | 0 | 0 | 39.8189 | 63.71% | 38.6807
3029 | 0 | 0 | 0 | 1.8 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9345 | 41.6067 | 0 | 103.9345 | 228.3293 | 17.9% | 0 | 0 | 39.8189 | 63.71% | 41.6067
3030 | 68 | 36 | 18 | 1.3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.5325 | 43.1596 | 0 | 107.5325 | 120.7969 | 9.47% | 0 | 0 | 39.8189 | 63.71% | 43.1596
3031 | 577 | 219 | 56 | 0.7 | 13.4 | 0 | 0 | 0 | 0 | 3.013 | 0 | 0 | 3.013 | 0 | 0 | 0 | 48.8823 | 17.5958 | 0 | 48.8823 | 71.9145 | 5.638% | 0 | 22.7318 | 14.6609 | 23.46% | 43.3406
3032 | 768 | 429 | 79 | 0.7 | 17.3 | 0 | 0 | 0 | 0 | 15.9428 | 0 | 0 | 15.9428 | 0 | 0 | 0 | 71.9145 | 27.4982 | 0 | 71.9145 | 0 | 0% | 0 | 0 | 14.6609 | 23.46% | 43.4409
3033 | 914 | 643 | 70 | 1.9 | 21 | 0 | 0 | 0 | 220.0747 | 36.3565 | 0 | 0 | 36.3565 | 0 | 0 | 0 | 0 | 0 | 220.0747 | 0 | 220.0747 | 17.25% | 0 | 7.5997 | 6.25 | 10% | 43.9562
3034 | 941 | 810 | 86 | 3.3 | 22.6 | 0 | 0 | 0 | 246.4059 | 43.5454 | 8.9296 | 0 | 43.5454 | 0 | 0 | 0 | 0 | 0 | 246.4059 | 0 | 466.4806 | 36.57% | 0 | 0 | 6.25 | 10% | 43.5454
3035 | 925 | 923 | 111 | 3.7 | 24.1 | 0 | 0 | 0 | 252.0028 | 42.5148 | 20.3761 | 0 | 42.5148 | 0 | 0 | 0 | 0 | 0 | 252.0028 | 0 | 718.4834 | 56.33% | 0 | 0 | 6.25 | 10% | 42.5148
3036 | 948 | 994 | 109 | 4.1 | 25 | 0 | 0 | 0 | 265.5896 | 41.6346 | 28.5314 | 0 | 41.6346 | 0 | 0 | 0 | 0 | 0 | 265.5896 | 0 | 984.073 | 77.15% | 0 | 0 | 6.25 | 10% | 41.6346
3037 | 935 | 995 | 116 | 4.5 | 25 | 0 | 0 | 0 | 0 | 42.1839 | 29.8161 | 1.08 | 41.104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 984.073 | 77.15% | 1.08 | 0 | 7.2258 | 11.56% | 41.104
3038 | 940 | 937 | 98 | 4.6 | 25.8 | 0 | 0 | 0 | 0 | 66.2154 | 3.6626 | 25 | 41.2154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 984.073 | 77.15% | 25 | 0 | 29.8148 | 47.7% | 41.2154
3039 | 887 | 825 | 116 | 4.1 | 26.4 | 0 | 0 | 0 | 123.5387 | 62.2696 | 0 | 21.2813 | 40.9884 | 0 | 0 | 0 | 0 | 0 | 123.5387 | 0 | 1107.6117 | 86.84% | 21.2813 | 0 | 49.0438 | 78.47% | 40.9884
3040 | 776 | 638 | 121 | 4.7 | 25.5 | 0 | 0 | 0 | 0 | 49.252 | 0 | 7.9754 | 41.2767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107.6117 | 86.84% | 7.9754 | 0 | 56.25 | 90% | 41.2767
3041 | 704 | 450 | 102 | 4.9 | 23.8 | 0 | 0 | 0 | 167.8985 | 34.4903 | 0 | 0 | 34.4903 | 0 | 0 | 0 | 0 | 0 | 167.8985 | 0 | 1275.5102 | 100% | 0 | 8.3852 | 46.9698 | 75.15% | 42.8755
3042 | 507 | 235 | 77 | 4.6 | 21.4 | 0 | 0 | 0 | 0 | 14.497 | 0 | 0 | 14.497 | 0 | 0 | 0 | 77.1276 | 29.5581 | 0 | 77.1276 | 1198.3826 | 93.95% | 0 | 0 | 46.9698 | 75.15% | 44.0551
3043 | 120 | 49 | 30 | 2.9 | 19 | 0 | 0 | 0 | 0 | 1.3427 | 0 | 0 | 1.3427 | 0 | 0 | 0 | 100.1626 | 39.6373 | 0 | 100.1626 | 1098.22 | 86.1% | 0 | 0 | 46.9698 | 75.15% | 40.98
3044 | 0 | 0 | 0 | 2 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.6277 | 37.7671 | 0 | 95.6277 | 1002.5923 | 78.6% | 0 | 0 | 46.9698 | 75.15% | 37.7671
3045 | 0 | 0 | 0 | 0.8 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3835 | 35.9621 | 0 | 91.3835 | 911.2088 | 71.44% | 0 | 0 | 46.9698 | 75.15% | 35.9621
3046 | 0 | 0 | 0 | 0.7 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6291 | 33.9135 | 0 | 86.6291 | 824.5797 | 64.65% | 0 | 0 | 46.9698 | 75.15% | 33.9135
3047 | 0 | 0 | 0 | 0.8 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6145 | 32.6099 | 0 | 83.6145 | 740.9652 | 58.09% | 0 | 0 | 46.9698 | 75.15% | 32.6099
3048 | 0 | 0 | 0 | 0.9 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3415 | 32.0918 | 0 | 82.3415 | 658.6237 | 51.64% | 0 | 0 | 46.9698 | 75.15% | 32.0918
3049 | 0 | 0 | 0 | 1.5 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.009 | 31.9846 | 0 | 82.009 | 576.6147 | 45.21% | 0 | 0 | 46.9698 | 75.15% | 31.9846
3050 | 0 | 0 | 0 | 1.5 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3415 | 32.564 | 0 | 83.3415 | 493.2732 | 38.67% | 0 | 0 | 46.9698 | 75.15% | 32.564
3051 | 0 | 0 | 0 | 0.7 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5303 | 32.6461 | 0 | 83.5303 | 409.7429 | 32.12% | 0 | 0 | 46.9698 | 75.15% | 32.6461
3052 | 0 | 0 | 0 | 1 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2341 | 39.0651 | 0 | 98.2341 | 311.5088 | 24.42% | 0 | 0 | 46.9698 | 75.15% | 39.0651
3053 | 0 | 0 | 0 | 1.3 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4725 | 41.8142 | 0 | 104.4725 | 207.0363 | 16.23% | 0 | 0 | 46.9698 | 75.15% | 41.8142
3054 | 117 | 42 | 25 | 1.2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7056 | 43.2153 | 0 | 107.7056 | 99.3307 | 7.788% | 0 | 0 | 46.9698 | 75.15% | 43.2153
3055 | 326 | 173 | 92 | 0.7 | 17.7 | 0 | 0 | 0 | 0 | 4.5528 | 0 | 0 | 4.5528 | 0 | 0 | 0 | 99.3307 | 39.3547 | 0 | 99.3307 | 0 | 0% | 0 | 0 | 46.9698 | 75.15% | 43.9075
3056 | 653 | 437 | 136 | 3.1 | 22.5 | 0 | 0 | 0 | 0 | 17.7682 | 0 | 0 | 17.7682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 19.3015 | 30.88% | 42.7683
3057 | 227 | 435 | 291 | 4.2 | 24.4 | 0 | 0 | 0 | 0 | 26.8068 | 0 | 0 | 26.8068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 11.7928 | 6.25 | 10% | 38.5996
3058 | 423 | 594 | 248 | 4.2 | 25.1 | 0 | 0 | 0 | 0 | 38.511 | 0 | 0 | 38.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.511
3059 | 939 | 927 | 101 | 5.6 | 26.7 | 0 | 0 | 0 | 254.423 | 43.0231 | 20.2783 | 0 | 43.0231 | 0 | 0 | 0 | 0 | 0 | 254.423 | 0 | 254.423 | 19.95% | 0 | 0 | 6.25 | 10% | 43.0231
3060 | 820 | 929 | 159 | 6.4 | 28.2 | 0 | 0 | 0 | 225.0745 | 65.1955 | 1.2098 | 23.0833 | 42.1123 | 0 | 0 | 0 | 0 | 0 | 225.0745 | 0 | 479.4976 | 37.59% | 23.0833 | 0 | 27.1071 | 43.37% | 42.1123
3061 | 703 | 895 | 226 | 6.4 | 29.1 | 0 | 0 | 0 | 187.5915 | 65.5541 | 0 | 23.6159 | 41.9382 | 0 | 0 | 0 | 0 | 0 | 187.5915 | 0 | 667.0891 | 52.3% | 23.6159 | 0 | 48.4455 | 77.51% | 41.9382
3062 | 401 | 703 | 332 | 5 | 29.3 | 0 | 0 | 0 | 0 | 41.5441 | 9.5272 | 0 | 41.5441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667.0891 | 52.3% | 0 | 0 | 48.4455 | 77.51% | 41.5441
3063 | 867 | 830 | 131 | 5.1 | 30.1 | 0 | 0 | 0 | 235.5143 | 41.0984 | 20.5501 | 0 | 41.0984 | 0 | 0 | 0 | 0 | 0 | 235.5143 | 0 | 902.6034 | 70.76% | 0 | 0 | 48.4455 | 77.51% | 41.0984
3064 | 789 | 657 | 129 | 6.8 | 30.4 | 0 | 0 | 0 | 202.6789 | 49.9838 | 0 | 8.6375 | 41.3463 | 0 | 0 | 0 | 0 | 0 | 202.6789 | 0 | 1105.2823 | 86.65% | 8.6375 | 0 | 56.25 | 90% | 41.3463
3065 | 723 | 453 | 94 | 8.2 | 30.1 | 0 | 0 | 0 | 170.2279 | 34.1137 | 0 | 0 | 34.1137 | 0 | 0 | 0 | 0 | 0 | 170.2279 | 0 | 1275.5102 | 100% | 0 | 8.2284 | 47.1434 | 75.43% | 42.3421
3066 | 445 | 216 | 65 | 8.6 | 28.6 | 0 | 0 | 0 | 0 | 12.1745 | 0 | 0 | 12.1745 | 0 | 0 | 0 | 79.4662 | 30.0456 | 0 | 79.4662 | 1196.044 | 93.77% | 0 | 1.7194 | 45.2405 | 72.38% | 43.9395
3067 | 180 | 70 | 45 | 7.3 | 26.8 | 0 | 0 | 0 | 0 | 2.1481 | 0 | 0 | 2.1481 | 0 | 0 | 0 | 100.2641 | 39.0367 | 0 | 100.2641 | 1095.7798 | 85.91% | 0 | 0 | 45.2405 | 72.38% | 41.1847
3068 | 0 | 0 | 0 | 4.3 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.881 | 37.7587 | 0 | 96.881 | 998.8988 | 78.31% | 0 | 0 | 45.2405 | 72.38% | 37.7587
3069 | 0 | 0 | 0 | 3.3 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7339 | 35.6989 | 0 | 91.7339 | 907.1649 | 71.12% | 0 | 0 | 45.2405 | 72.38% | 35.6989
3070 | 0 | 0 | 0 | 4.7 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2566 | 33.8438 | 0 | 87.2566 | 819.9083 | 64.28% | 0 | 0 | 45.2405 | 72.38% | 33.8438
3071 | 0 | 0 | 0 | 5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.7188 | 26.3389 | 0 | 69.7188 | 750.1895 | 58.81% | 0 | 0 | 45.2405 | 72.38% | 26.3389
3072 | 0 | 0 | 0 | 4.1 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0871 | 32.135 | 0 | 83.0871 | 667.1024 | 52.3% | 0 | 0 | 45.2405 | 72.38% | 32.135
3073 | 0 | 0 | 0 | 5.1 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7546 | 32.0097 | 0 | 82.7546 | 584.3478 | 45.81% | 0 | 0 | 45.2405 | 72.38% | 32.0097
3074 | 0 | 0 | 0 | 3.3 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.954 | 32.5264 | 0 | 83.954 | 500.3938 | 39.23% | 0 | 0 | 45.2405 | 72.38% | 32.5264
3075 | 0 | 0 | 0 | 3 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5287 | 35.3842 | 0 | 90.5287 | 409.8651 | 32.13% | 0 | 0 | 45.2405 | 72.38% | 35.3842
3076 | 0 | 0 | 0 | 2.1 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5935 | 38.9146 | 0 | 98.5935 | 311.2716 | 24.4% | 0 | 0 | 45.2405 | 72.38% | 38.9146
3077 | 0 | 0 | 0 | 3.1 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3267 | 41.8142 | 0 | 105.3267 | 205.9449 | 16.15% | 0 | 0 | 45.2405 | 72.38% | 41.8142
3078 | 9 | 26 | 25 | 1.8 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7697 | 43.3002 | 0 | 108.7697 | 97.1752 | 7.619% | 0 | 0 | 45.2405 | 72.38% | 43.3002
3079 | 86 | 158 | 129 | 1.5 | 20.5 | 0 | 0 | 0 | 0 | 5.5397 | 0 | 0 | 5.5397 | 0 | 0 | 0 | 97.1752 | 38.2494 | 0 | 97.1752 | 0 | 0% | 0 | 0 | 45.2405 | 72.38% | 43.7891
3080 | 401 | 405 | 215 | 1.2 | 22.9 | 0 | 0 | 0 | 0 | 18.6902 | 0 | 0 | 18.6902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 17.5721 | 28.12% | 43.6902
3081 | 657 | 601 | 176 | 2 | 24.1 | 0 | 0 | 0 | 0 | 34.3847 | 0 | 0 | 34.3847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 10.2302 | 6.25 | 10% | 44.6149
3082 | 809 | 766 | 136 | 1.7 | 25.2 | 0 | 0 | 0 | 201.6767 | 44.3573 | 3.9988 | 0 | 44.3573 | 0 | 0 | 0 | 0 | 0 | 201.6767 | 0 | 201.6767 | 15.81% | 0 | 0 | 6.25 | 10% | 44.3573
3083 | 904 | 900 | 102 | 1.9 | 26.7 | 0 | 0 | 0 | 0 | 43.1401 | 15.8245 | 0 | 43.1401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.6767 | 15.81% | 0 | 0 | 6.25 | 10% | 43.1401
3084 | 947 | 977 | 89 | 2.1 | 28 | 0 | 0 | 0 | 0 | 63.4743 | 2.5407 | 21.2186 | 42.2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.6767 | 15.81% | 21.2186 | 0 | 25.4223 | 40.68% | 42.2557
3085 | 777 | 937 | 201 | 3.7 | 28.4 | 0 | 0 | 0 | 217.0853 | 66.8074 | 0 | 24.9917 | 41.8156 | 0 | 0 | 0 | 0 | 0 | 217.0853 | 0 | 418.762 | 32.83% | 24.9917 | 0 | 48.0038 | 76.81% | 41.8156
3086 | 778 | 886 | 189 | 3.9 | 28.8 | 0 | 0 | 0 | 215.467 | 41.7307 | 23.1692 | 0 | 41.7307 | 0 | 0 | 0 | 0 | 0 | 215.467 | 0 | 634.229 | 49.72% | 0 | 0 | 48.0038 | 76.81% | 41.7307
3087 | 868 | 831 | 134 | 5.6 | 28.1 | 0 | 0 | 0 | 235.3281 | 41.3087 | 21.1227 | 0 | 41.3087 | 0 | 0 | 0 | 0 | 0 | 235.3281 | 0 | 869.5571 | 68.17% | 0 | 0 | 48.0038 | 76.81% | 41.3087
3088 | 839 | 662 | 102 | 5.2 | 28.3 | 0 | 0 | 0 | 218.1004 | 50.2971 | 0 | 9.1263 | 41.1708 | 0 | 0 | 0 | 0 | 0 | 218.1004 | 0 | 1087.6575 | 85.27% | 9.1263 | 0 | 56.25 | 90% | 41.1708
3089 | 775 | 460 | 74 | 3.8 | 28.3 | 0 | 0 | 0 | 187.8527 | 34.2634 | 0 | 0 | 34.2634 | 0 | 0 | 0 | 0 | 0 | 187.8527 | 0 | 1275.5102 | 100% | 0 | 7.7988 | 47.6189 | 76.19% | 42.0621
3090 | 639 | 251 | 53 | 3.5 | 28.2 | 0 | 0 | 0 | 0 | 14.857 | 0 | 0 | 14.857 | 0 | 0 | 0 | 71.2495 | 26.5996 | 0 | 71.2495 | 1204.2607 | 94.41% | 0 | 2.0748 | 45.3226 | 72.52% | 43.5314
3091 | 271 | 63 | 25 | 4 | 26.5 | 0 | 0 | 0 | 0 | 1.0509 | 0 | 0 | 1.0509 | 0 | 0 | 0 | 102.1199 | 39.8567 | 0 | 102.1199 | 1102.1407 | 86.41% | 0 | 0 | 45.3226 | 72.52% | 40.9076
3092 | 0 | 0 | 0 | 1.9 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8497 | 37.4467 | 0 | 95.8497 | 1006.291 | 78.89% | 0 | 0 | 45.3226 | 72.52% | 37.4467
3093 | 0 | 0 | 0 | 0.9 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1967 | 35.6265 | 0 | 91.1967 | 915.0944 | 71.74% | 0 | 0 | 45.3226 | 72.52% | 35.6265
3094 | 0 | 0 | 0 | 0.9 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2761 | 33.9386 | 0 | 87.2761 | 827.8182 | 64.9% | 0 | 0 | 45.3226 | 72.52% | 33.9386
3095 | 0 | 0 | 0 | 1 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7772 | 32.4679 | 0 | 83.7772 | 744.041 | 58.33% | 0 | 0 | 45.3226 | 72.52% | 32.4679
3096 | 0 | 0 | 0 | 0.6 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4239 | 31.9345 | 0 | 82.4239 | 661.6172 | 51.87% | 0 | 0 | 45.3226 | 72.52% | 31.9345
3097 | 0 | 0 | 0 | 0.5 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.3857 | 27.6414 | 0 | 72.3857 | 589.2315 | 46.2% | 0 | 0 | 45.3226 | 72.52% | 27.6414
3098 | 0 | 0 | 0 | 0.7 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4012 | 32.4428 | 0 | 83.4012 | 505.8303 | 39.66% | 0 | 0 | 45.3226 | 72.52% | 32.4428
3099 | 0 | 0 | 0 | 1.8 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7775 | 35.1711 | 0 | 89.7775 | 416.0527 | 32.62% | 0 | 0 | 45.3226 | 72.52% | 35.1711
3100 | 0 | 0 | 0 | 2.4 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.723 | 39.0275 | 0 | 98.723 | 317.3297 | 24.88% | 0 | 0 | 45.3226 | 72.52% | 39.0275
3101 | 0 | 0 | 0 | 1.7 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3995 | 41.9521 | 0 | 105.3995 | 211.9302 | 16.62% | 0 | 0 | 45.3226 | 72.52% | 41.9521
3102 | 168 | 42 | 19 | 1.4 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.1422 | 43.1944 | 0 | 108.1422 | 103.788 | 8.137% | 0 | 0 | 45.3226 | 72.52% | 43.1944
3103 | 647 | 223 | 47 | 0.9 | 20.9 | 0 | 0 | 0 | 0 | 2.5683 | 0 | 0 | 2.5683 | 0 | 0 | 0 | 103.788 | 41.0703 | 0 | 103.788 | 0 | 0% | 0 | 0 | 45.3226 | 72.52% | 43.6387
3104 | 804 | 429 | 58 | 0.5 | 23.9 | 0 | 0 | 0 | 0 | 14.7021 | 0 | 0 | 14.7021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 17.6542 | 28.25% | 39.7021
3105 | 893 | 629 | 63 | 1 | 25.7 | 0 | 0 | 0 | 0 | 34.0515 | 0 | 0 | 34.0515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 10.3044 | 6.25 | 10% | 44.3559
3106 | 940 | 797 | 66 | 1.3 | 27.2 | 0 | 0 | 0 | 247.3657 | 44.484 | 4.2099 | 0 | 44.484 | 0 | 0 | 0 | 0 | 0 | 247.3657 | 0 | 247.3657 | 19.39% | 0 | 0 | 6.25 | 10% | 44.484
3107 | 958 | 916 | 71 | 2.3 | 28.4 | 0 | 0 | 0 | 262.4543 | 42.9911 | 16.8318 | 0 | 42.9911 | 0 | 0 | 0 | 0 | 0 | 262.4543 | 0 | 509.8201 | 39.97% | 0 | 0 | 6.25 | 10% | 42.9911
3108 | 965 | 982 | 75 | 2.9 | 29.1 | 0 | 0 | 0 | 271.5939 | 41.8992 | 24.8535 | 0 | 41.8992 | 0 | 0 | 0 | 0 | 0 | 271.5939 | 0 | 781.414 | 61.26% | 0 | 0 | 6.25 | 10% | 41.8992
3109 | 947 | 980 | 84 | 3.7 | 29.8 | 0 | 0 | 0 | 268.8059 | 43.8013 | 25.2101 | 2.2447 | 41.5566 | 0 | 0 | 0 | 0 | 0 | 268.8059 | 0 | 1050.2199 | 82.34% | 2.2447 | 0 | 8.2783 | 13.25% | 41.5566
3110 | 930 | 924 | 87 | 4.4 | 29.7 | 0 | 0 | 0 | 0 | 66.3491 | 0.84478 | 25 | 41.3491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050.2199 | 82.34% | 25 | 0 | 30.8673 | 49.39% | 41.3491
3111 | 894 | 812 | 92 | 4.4 | 29.9 | 0 | 0 | 0 | 131.6858 | 60.2443 | 0 | 19.6946 | 40.5497 | 0 | 0 | 0 | 0 | 0 | 131.6858 | 0 | 1181.9057 | 92.66% | 19.6946 | 0 | 48.6625 | 77.86% | 40.5497
3112 | 845 | 652 | 86 | 3.9 | 29.9 | 0 | 0 | 0 | 0 | 48.7576 | 0 | 8.3973 | 40.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1181.9057 | 92.66% | 8.3973 | 0 | 56.25 | 90% | 40.3603
3113 | 652 | 429 | 96 | 4.9 | 28.8 | 0 | 0 | 0 | 0 | 31.3346 | 0 | 0 | 31.3346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1181.9057 | 92.66% | 0 | 9.0577 | 46.2255 | 73.96% | 40.3923
3114 | 455 | 238 | 90 | 3.9 | 27.7 | 0 | 0 | 0 | 0 | 13.965 | 0 | 0 | 13.965 | 0 | 0 | 0 | 72.3192 | 27.0902 | 0 | 72.3192 | 1109.5865 | 86.99% | 0 | 0 | 46.2255 | 73.96% | 41.0552
3115 | 225 | 68 | 37 | 3.1 | 26.1 | 0 | 0 | 0 | 0 | 1.726 | 0 | 0 | 1.726 | 0 | 0 | 0 | 82.0882 | 31.3654 | 0 | 82.0882 | 1027.4983 | 80.56% | 0 | 6.5878 | 38.9346 | 62.3% | 39.6792
3116 | 0 | 1 | 1 | 1.8 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0936 | 37.139 | 0 | 95.0936 | 932.4047 | 73.1% | 0 | 0 | 38.9346 | 62.3% | 37.139
3117 | 0 | 0 | 0 | 0.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3729 | 35.6474 | 0 | 91.3729 | 841.0318 | 65.94% | 0 | 0 | 38.9346 | 62.3% | 35.6474
3118 | 0 | 0 | 0 | 1 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6665 | 33.6698 | 0 | 86.6665 | 754.3653 | 59.14% | 0 | 0 | 38.9346 | 62.3% | 33.6698
3119 | 0 | 0 | 0 | 1.7 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6196 | 31.9916 | 0 | 82.6196 | 671.7457 | 52.66% | 0 | 0 | 38.9346 | 62.3% | 31.9916
3120 | 0 | 0 | 0 | 1.3 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2293 | 30.9819 | 0 | 80.2293 | 591.5164 | 46.37% | 0 | 0 | 38.9346 | 62.3% | 30.9819
3121 | 0 | 0 | 0 | 0.3 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1979 | 30.5571 | 0 | 79.1979 | 512.3185 | 40.17% | 0 | 0 | 38.9346 | 62.3% | 30.5571
3122 | 0 | 0 | 0 | 2.1 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.744 | 30.3357 | 0 | 78.744 | 433.5745 | 33.99% | 0 | 0 | 38.9346 | 62.3% | 30.3357
3123 | 0 | 0 | 0 | 2.2 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4839 | 30.6602 | 0 | 79.4839 | 354.0906 | 27.76% | 0 | 0 | 38.9346 | 62.3% | 30.6602
3124 | 0 | 0 | 0 | 1.6 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6287 | 31.2242 | 0 | 80.6287 | 273.4619 | 21.44% | 0 | 0 | 38.9346 | 62.3% | 31.2242
3125 | 0 | 0 | 0 | 2 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6612 | 33.8076 | 0 | 86.6612 | 186.8007 | 14.65% | 0 | 0 | 38.9346 | 62.3% | 33.8076
3126 | 166 | 42 | 19 | 1.9 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8389 | 36.9217 | 0 | 93.8389 | 92.9619 | 7.288% | 0 | 0 | 38.9346 | 62.3% | 36.9217
3127 | 644 | 224 | 46 | 0.5 | 23.3 | 0 | 0 | 0 | 0 | 2.4601 | 0 | 0 | 2.4601 | 0 | 0 | 0 | 92.9619 | 36.2331 | 0 | 92.9619 | 0 | 0% | 0 | 0 | 38.9346 | 62.3% | 38.6932
3128 | 807 | 435 | 60 | 0.6 | 25.2 | 0 | 0 | 0 | 163.5188 | 14.8008 | 0 | 0 | 14.8008 | 0 | 0 | 0 | 0 | 0 | 163.5188 | 0 | 163.5188 | 12.82% | 0 | 24.2935 | 12.0481 | 19.28% | 39.0943
3129 | 887 | 634 | 68 | 1.1 | 27.2 | 0 | 0 | 0 | 214.3085 | 34.0155 | 0 | 0 | 34.0155 | 0 | 0 | 0 | 0 | 0 | 214.3085 | 0 | 377.8273 | 29.62% | 0 | 5.239 | 6.25 | 10% | 39.2545
3130 | 929 | 800 | 74 | 2.2 | 28.7 | 0 | 0 | 0 | 243.8273 | 39.4285 | 9.7124 | 0 | 39.4285 | 0 | 0 | 0 | 0 | 0 | 243.8273 | 0 | 621.6545 | 48.74% | 0 | 0 | 6.25 | 10% | 39.4285
3131 | 952 | 922 | 78 | 2.5 | 29.6 | 0 | 0 | 0 | 0 | 38.4007 | 21.4016 | 0 | 38.4007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621.6545 | 48.74% | 0 | 0 | 6.25 | 10% | 38.4007
3132 | 944 | 987 | 97 | 3.7 | 30.5 | 0 | 0 | 0 | 0 | 36.6111 | 30.5529 | 0 | 36.6111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621.6545 | 48.74% | 0 | 0 | 6.25 | 10% | 36.6111
3133 | 752 | 892 | 175 | 2.6 | 30.6 | 0 | 0 | 0 | 0 | 35.3577 | 26.7612 | 0 | 35.3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621.6545 | 48.74% | 0 | 0 | 6.25 | 10% | 35.3577
3134 | 874 | 912 | 125 | 4.2 | 30.3 | 0 | 0 | 0 | 244.2816 | 50.8398 | 14.9533 | 16.042 | 34.7978 | 0 | 0 | 0 | 0 | 0 | 244.2816 | 0 | 865.9361 | 67.89% | 16.042 | 0 | 20.7449 | 33.19% | 34.7978
3135 | 891 | 813 | 93 | 4.4 | 30.2 | 0 | 0 | 0 | 0 | 59.5834 | 0.40283 | 25 | 34.5834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.9361 | 67.89% | 25 | 0 | 43.3339 | 69.33% | 34.5834
3136 | 848 | 657 | 87 | 4.3 | 29.7 | 0 | 0 | 0 | 0 | 49.0647 | 0 | 14.2947 | 34.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 865.9361 | 67.89% | 14.2947 | 0 | 56.25 | 90% | 34.77
3137 | 776 | 464 | 74 | 5.4 | 28.9 | 0 | 0 | 0 | 140.3179 | 34.3265 | 0 | 0 | 34.3265 | 0 | 0 | 0 | 0 | 0 | 140.3179 | 0 | 1006.2541 | 78.89% | 0 | 1.2095 | 54.9114 | 87.86% | 35.536
3138 | 645 | 258 | 55 | 6.7 | 25.9 | 0 | 0 | 0 | 0 | 15.2471 | 0 | 0 | 15.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006.2541 | 78.89% | 0 | 22.1356 | 30.4132 | 48.66% | 37.3827
3139 | 307 | 71 | 26 | 6.5 | 22.2 | 0 | 0 | 0 | 0 | 1.1452 | 0 | 0 | 1.1452 | 0 | 0 | 0 | 90.9188 | 35.4381 | 0 | 90.9188 | 915.3352 | 71.76% | 0 | 0 | 30.4132 | 48.66% | 36.5833
3140 | 0 | 1 | 1 | 5.7 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2386 | 34.433 | 0 | 88.2386 | 827.0966 | 64.84% | 0 | 0 | 30.4132 | 48.66% | 34.433
3141 | 0 | 0 | 0 | 4.6 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3205 | 32.3787 | 0 | 83.3205 | 743.7761 | 58.31% | 0 | 0 | 30.4132 | 48.66% | 32.3787
3142 | 0 | 0 | 0 | 4.3 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8465 | 30.4888 | 0 | 78.8465 | 664.9296 | 52.13% | 0 | 0 | 30.4132 | 48.66% | 30.4888
3143 | 0 | 0 | 0 | 3.2 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2713 | 28.9485 | 0 | 75.2713 | 589.6583 | 46.23% | 0 | 0 | 30.4132 | 48.66% | 28.9485
3144 | 0 | 0 | 0 | 3.4 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2057 | 28.0614 | 0 | 73.2057 | 516.4526 | 40.49% | 0 | 0 | 30.4132 | 48.66% | 28.0614
3145 | 0 | 0 | 0 | 2.7 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1593 | 27.6004 | 0 | 72.1593 | 444.2933 | 34.83% | 0 | 0 | 30.4132 | 48.66% | 27.6004
3146 | 0 | 0 | 0 | 3.9 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.936 | 27.4639 | 0 | 71.936 | 372.3573 | 29.19% | 0 | 0 | 30.4132 | 48.66% | 27.4639
3147 | 0 | 0 | 0 | 4.5 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0471 | 27.482 | 0 | 72.0471 | 300.3102 | 23.54% | 0 | 0 | 30.4132 | 48.66% | 27.482
3148 | 0 | 0 | 0 | 4.7 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8333 | 27.4026 | 0 | 71.8333 | 228.4768 | 17.91% | 0 | 0 | 30.4132 | 48.66% | 27.4026
3149 | 0 | 0 | 0 | 3.8 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2933 | 28.9249 | 0 | 75.2933 | 153.1836 | 12.01% | 0 | 0 | 30.4132 | 48.66% | 28.9249
3150 | 158 | 40 | 19 | 2.8 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1562 | 31.5473 | 0 | 81.1562 | 72.0274 | 5.647% | 0 | 0 | 30.4132 | 48.66% | 31.5473
3151 | 587 | 218 | 52 | 4.1 | 17.3 | 0 | 0 | 0 | 0 | 2.6574 | 0 | 0 | 2.6574 | 0 | 0 | 0 | 72.0274 | 27.5471 | 0 | 72.0274 | 0 | 0% | 0 | 3.1896 | 26.8832 | 43.01% | 33.394
3152 | 766 | 432 | 72 | 5.2 | 19.1 | 0 | 0 | 0 | 0 | 15.6796 | 0 | 0 | 15.6796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 18.6434 | 6.25 | 10% | 34.3229
3153 | 847 | 629 | 84 | 6.1 | 20.4 | 0 | 0 | 0 | 0 | 35.7336 | 0 | 1.0486 | 34.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1.0486 | 0 | 7.1974 | 11.52% | 34.685
3154 | 892 | 793 | 92 | 6.2 | 21.5 | 0 | 0 | 0 | 0 | 51.334 | 0 | 16.3022 | 35.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 16.3022 | 0 | 21.9274 | 35.08% | 35.0318
3155 | 920 | 914 | 94 | 6.2 | 22.7 | 0 | 0 | 0 | 0 | 34.8368 | 27.6478 | 0 | 34.8368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 21.9274 | 35.08% | 34.8368
3156 | 929 | 978 | 98 | 5.9 | 23.6 | 0 | 0 | 0 | 175.1226 | 33.4845 | 35.6514 | 0 | 33.4845 | 0 | 0 | 0 | 0 | 0 | 175.1226 | 0 | 175.1226 | 13.73% | 0 | 0 | 21.9274 | 35.08% | 33.4845
3157 | 927 | 982 | 99 | 5.3 | 24.6 | 0 | 0 | 0 | 261.2533 | 32.4818 | 38.361 | 0 | 32.4818 | 0 | 0 | 0 | 0 | 0 | 261.2533 | 0 | 436.3759 | 34.21% | 0 | 0 | 21.9274 | 35.08% | 32.4818
3158 | 914 | 926 | 98 | 5.1 | 25.4 | 0 | 0 | 0 | 255.4193 | 57.1615 | 10.977 | 25 | 32.1615 | 0 | 0 | 0 | 0 | 0 | 255.4193 | 0 | 691.7953 | 54.24% | 25 | 0 | 44.5164 | 71.23% | 32.1615
3159 | 889 | 816 | 95 | 5.5 | 25.4 | 0 | 0 | 0 | 241.5867 | 32.2492 | 29.1514 | 0 | 32.2492 | 0 | 0 | 0 | 0 | 0 | 241.5867 | 0 | 933.3819 | 73.18% | 0 | 0 | 44.5164 | 71.23% | 32.2492
3160 | 853 | 662 | 86 | 5.5 | 25.1 | 0 | 0 | 0 | 221.6586 | 45.8619 | 4.4391 | 12.9859 | 32.8759 | 0 | 0 | 0 | 0 | 0 | 221.6586 | 0 | 1155.0405 | 90.56% | 12.9859 | 0 | 56.25 | 90% | 32.8759
3161 | 779 | 469 | 74 | 5.4 | 24.2 | 0 | 0 | 0 | 0 | 34.3118 | 0.63086 | 0 | 34.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1155.0405 | 90.56% | 0 | 0 | 56.25 | 90% | 34.3118
3162 | 635 | 261 | 58 | 5.3 | 22.5 | 0 | 0 | 0 | 0 | 15.4 | 0 | 0 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1155.0405 | 90.56% | 0 | 21.5649 | 32.3834 | 51.81% | 36.9649
3163 | 291 | 72 | 29 | 4.6 | 20.2 | 0 | 0 | 0 | 0 | 1.3143 | 0 | 0 | 1.3143 | 0 | 0 | 0 | 91.2741 | 35.7244 | 0 | 91.2741 | 1063.7664 | 83.4% | 0 | 0 | 32.3834 | 51.81% | 37.0387
3164 | 0 | 1 | 1 | 3.9 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.1749 | 17.6284 | 0 | 49.1749 | 1014.5915 | 79.54% | 0 | 16.8686 | 13.7143 | 21.94% | 34.497
3165 | 0 | 0 | 0 | 1.9 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7502 | 32.2228 | 0 | 82.7502 | 931.8413 | 73.06% | 0 | 0 | 13.7143 | 21.94% | 32.2228
3166 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4557 | 30.383 | 0 | 78.4557 | 853.3856 | 66.91% | 0 | 0 | 13.7143 | 21.94% | 30.383
3167 | 0 | 0 | 0 | 1.6 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.9369 | 29.3037 | 0 | 75.9369 | 777.4487 | 60.95% | 0 | 0 | 13.7143 | 21.94% | 29.3037
3168 | 0 | 0 | 0 | 1.5 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1154 | 28.9694 | 0 | 75.1154 | 702.3333 | 55.06% | 0 | 0 | 13.7143 | 21.94% | 28.9694
3169 | 0 | 0 | 0 | 1 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3994 | 29.0989 | 0 | 75.3994 | 626.9339 | 49.15% | 0 | 0 | 13.7143 | 21.94% | 29.0989
3170 | 0 | 0 | 0 | 1 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0339 | 29.8329 | 0 | 77.0339 | 549.9 | 43.11% | 0 | 0 | 13.7143 | 21.94% | 29.8329
3171 | 0 | 0 | 0 | 2.5 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8096 | 33.2088 | 0 | 84.8096 | 465.0904 | 36.46% | 0 | 0 | 13.7143 | 21.94% | 33.2088
3172 | 0 | 0 | 0 | 2.3 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2384 | 36.8743 | 0 | 93.2384 | 371.852 | 29.15% | 0 | 0 | 13.7143 | 21.94% | 36.8743
3173 | 0 | 0 | 0 | 1.8 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1581 | 39.9355 | 0 | 100.1581 | 271.6939 | 21.3% | 0 | 0 | 13.7143 | 21.94% | 39.9355
3174 | 204 | 48 | 21 | 3 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3801 | 41.2808 | 0 | 103.3801 | 168.3138 | 13.2% | 0 | 0 | 13.7143 | 21.94% | 41.2808
3175 | 649 | 231 | 50 | 3.5 | 16.8 | 0 | 0 | 0 | 0 | 2.5358 | 0 | 0 | 2.5358 | 0 | 0 | 0 | 99.0017 | 39.2604 | 0 | 99.0017 | 69.3121 | 5.434% | 0 | 0 | 13.7143 | 21.94% | 41.7961
3176 | 818 | 446 | 64 | 4.4 | 17.9 | 0 | 0 | 0 | 0 | 15.8642 | 0 | 0 | 15.8642 | 0 | 0 | 0 | 69.3121 | 26.3483 | 0 | 69.3121 | 0 | 0% | 0 | 0 | 13.7143 | 21.94% | 42.2125
3177 | 896 | 646 | 72 | 4.2 | 19.2 | 0 | 0 | 0 | 0 | 36.3956 | 0 | 0 | 36.3956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 6.7445 | 6.25 | 10% | 43.1401
3178 | 945 | 815 | 75 | 3.9 | 20.5 | 0 | 0 | 0 | 70.6287 | 43.5384 | 8.5913 | 0 | 43.5384 | 0 | 0 | 0 | 0 | 0 | 70.6287 | 0 | 70.6287 | 5.537% | 0 | 0 | 6.25 | 10% | 43.5384
3179 | 962 | 934 | 81 | 3.7 | 21.6 | 0 | 0 | 0 | 262.6496 | 42.4744 | 20.5482 | 0 | 42.4744 | 0 | 0 | 0 | 0 | 0 | 262.6496 | 0 | 333.2783 | 26.13% | 0 | 0 | 6.25 | 10% | 42.4744
3180 | 968 | 998 | 84 | 2.7 | 23.5 | 0 | 0 | 0 | 272.4766 | 41.6193 | 26.7523 | 0 | 41.6193 | 0 | 0 | 0 | 0 | 0 | 272.4766 | 0 | 605.7548 | 47.49% | 0 | 0 | 6.25 | 10% | 41.6193
3181 | 960 | 1000 | 89 | 4.5 | 24 | 0 | 0 | 0 | 0 | 41.3338 | 30.5398 | 0 | 41.3338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605.7548 | 47.49% | 0 | 0 | 6.25 | 10% | 41.3338
3182 | 937 | 940 | 94 | 5.2 | 24.1 | 0 | 0 | 0 | 0 | 63.7233 | 5.8531 | 22.3659 | 41.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605.7548 | 47.49% | 22.3659 | 0 | 26.4589 | 42.33% | 41.3574
3183 | 907 | 828 | 94 | 6.2 | 23.6 | 0 | 0 | 0 | 246.2975 | 62.9158 | 0 | 22.0097 | 40.9062 | 0 | 0 | 0 | 0 | 0 | 246.2975 | 0 | 852.0523 | 66.8% | 22.0097 | 0 | 46.346 | 74.15% | 40.9062
3184 | 854 | 668 | 92 | 7.5 | 22.3 | 0 | 0 | 0 | 220.0596 | 51.5679 | 0 | 10.9611 | 40.6068 | 0 | 0 | 0 | 0 | 0 | 220.0596 | 0 | 1072.1119 | 84.05% | 10.9611 | 0 | 56.25 | 90% | 40.6068
3185 | 760 | 471 | 86 | 7.3 | 21.2 | 0 | 0 | 0 | 180.7558 | 35.5939 | 0 | 0 | 35.5939 | 0 | 0 | 0 | 0 | 0 | 180.7558 | 0 | 1252.8677 | 98.22% | 0 | 5.4933 | 50.1704 | 80.27% | 41.0872
3186 | 592 | 259 | 69 | 6.9 | 19.9 | 0 | 0 | 0 | 0 | 15.3939 | 0 | 0 | 15.3939 | 0 | 0 | 0 | 38.2653 | 12.8676 | 0 | 38.2653 | 1214.6024 | 95.22% | 0 | 13.8355 | 34.8582 | 55.77% | 42.097
3187 | 239 | 70 | 33 | 5.4 | 18.2 | 0 | 0 | 0 | 0 | 1.5266 | 0 | 0 | 1.5266 | 0 | 0 | 0 | 98.006 | 38.7529 | 0 | 98.006 | 1116.5963 | 87.54% | 0 | 0 | 34.8582 | 55.77% | 40.2795
3188 | 0 | 1 | 1 | 3.7 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2087 | 18.1196 | 0 | 50.2087 | 1066.3876 | 83.6% | 0 | 18.8856 | 13.9568 | 22.33% | 37.0053
3189 | 0 | 0 | 0 | 4 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4227 | 35.1864 | 0 | 89.4227 | 976.965 | 76.59% | 0 | 0 | 13.9568 | 22.33% | 35.1864
3190 | 0 | 0 | 0 | 4.3 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7744 | 33.1935 | 0 | 84.7744 | 892.1906 | 69.95% | 0 | 0 | 13.9568 | 22.33% | 33.1935
3191 | 0 | 0 | 0 | 3.7 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.172 | 32.0737 | 0 | 82.172 | 810.0186 | 63.51% | 0 | 0 | 13.9568 | 22.33% | 32.0737
3192 | 0 | 0 | 0 | 3.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0292 | 31.5905 | 0 | 81.0292 | 728.9893 | 57.15% | 0 | 0 | 13.9568 | 22.33% | 31.5905
3193 | 0 | 0 | 0 | 3.9 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9819 | 31.5752 | 0 | 80.9819 | 648.0074 | 50.8% | 0 | 0 | 13.9568 | 22.33% | 31.5752
3194 | 0 | 0 | 0 | 1.7 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.262 | 32.135 | 0 | 82.262 | 565.7454 | 44.35% | 0 | 0 | 13.9568 | 22.33% | 32.135
3195 | 0 | 0 | 0 | 2 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1195 | 34.6906 | 0 | 88.1195 | 477.6258 | 37.45% | 0 | 0 | 13.9568 | 22.33% | 34.6906
3196 | 0 | 0 | 0 | 2.2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.262 | 38.2448 | 0 | 96.262 | 381.3638 | 29.9% | 0 | 0 | 13.9568 | 22.33% | 38.2448
3197 | 0 | 0 | 0 | 2 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7024 | 41.0803 | 0 | 102.7024 | 278.6614 | 21.85% | 0 | 0 | 13.9568 | 22.33% | 41.0803
3198 | 242 | 50 | 20 | 1.9 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.9994 | 42.512 | 0 | 105.9994 | 172.662 | 13.54% | 0 | 0 | 13.9568 | 22.33% | 42.512
3199 | 682 | 239 | 47 | 2.2 | 14.1 | 0 | 0 | 0 | 0 | 2.6322 | 0 | 0 | 2.6322 | 0 | 0 | 0 | 101.062 | 40.2767 | 0 | 101.062 | 71.5999 | 5.613% | 0 | 0 | 13.9568 | 22.33% | 42.9089
3200 | 840 | 454 | 60 | 3.3 | 16.2 | 0 | 0 | 0 | 0 | 15.909 | 0 | 0 | 15.909 | 0 | 0 | 0 | 71.5999 | 27.401 | 0 | 71.5999 | 0 | 0% | 0 | 0 | 13.9568 | 22.33% | 43.31
3201 | 922 | 656 | 66 | 4.4 | 18.1 | 0 | 0 | 0 | 221.7648 | 36.9606 | 0 | 0 | 36.9606 | 0 | 0 | 0 | 0 | 0 | 221.7648 | 0 | 221.7648 | 17.39% | 0 | 6.9636 | 6.25 | 10% | 43.9242
3202 | 966 | 825 | 68 | 4.5 | 19.8 | 0 | 0 | 0 | 252.4845 | 44.2473 | 8.6475 | 0 | 44.2473 | 0 | 0 | 0 | 0 | 0 | 252.4845 | 0 | 474.2493 | 37.18% | 0 | 0 | 6.25 | 10% | 44.2473
3203 | 985 | 945 | 71 | 4.3 | 21.1 | 0 | 0 | 0 | 268.7856 | 43.122 | 20.8715 | 0 | 43.122 | 0 | 0 | 0 | 0 | 0 | 268.7856 | 0 | 743.0349 | 58.25% | 0 | 0 | 6.25 | 10% | 43.122
3204 | 991 | 1010 | 74 | 2.9 | 22.1 | 0 | 0 | 0 | 279.2473 | 42.5398 | 27.0085 | 0 | 42.5398 | 0 | 0 | 0 | 0 | 0 | 279.2473 | 0 | 1022.2821 | 80.15% | 0 | 0 | 6.25 | 10% | 42.5398
3205 | 986 | 1012 | 76 | 2.7 | 23.2 | 0 | 0 | 0 | 243.7416 | 42.4047 | 28.7625 | 0 | 42.4047 | 0 | 0 | 0 | 0 | 0 | 243.7416 | 0 | 1266.0237 | 99.26% | 0 | 0 | 6.25 | 10% | 42.4047
3206 | 975 | 956 | 75 | 3.7 | 24.3 | 0 | 0 | 0 | 0 | 66.3733 | 3.2118 | 23.9644 | 42.4089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0237 | 99.26% | 23.9644 | 0 | 27.9032 | 44.65% | 42.4089
3207 | 952 | 844 | 73 | 4.5 | 24.8 | 0 | 0 | 0 | 0 | 63.0692 | 0 | 21.216 | 41.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0237 | 99.26% | 21.216 | 0 | 47.0732 | 75.32% | 41.8532
3208 | 916 | 686 | 68 | 4.2 | 24.5 | 0 | 0 | 0 | 0 | 51.7268 | 0 | 10.1563 | 41.5705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0237 | 99.26% | 10.1563 | 0 | 56.25 | 90% | 41.5705
3209 | 853 | 492 | 59 | 3 | 24.4 | 0 | 0 | 0 | 0 | 36.0395 | 0 | 0 | 36.0395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.0237 | 99.26% | 0 | 5.8638 | 49.7603 | 79.62% | 41.9034
3210 | 703 | 274 | 49 | 2.3 | 24.2 | 0 | 0 | 0 | 0 | 15.8336 | 0 | 0 | 15.8336 | 0 | 0 | 0 | 71.9579 | 27.1741 | 0 | 71.9579 | 1194.0658 | 93.61% | 0 | 0 | 49.7603 | 79.62% | 43.0078
3211 | 360 | 79 | 26 | 3.6 | 21.9 | 0 | 0 | 0 | 0 | 1.2725 | 0 | 0 | 1.2725 | 0 | 0 | 0 | 101.1105 | 39.8412 | 0 | 101.1105 | 1092.9553 | 85.69% | 0 | 0 | 49.7603 | 79.62% | 41.1137
3212 | 0 | 1 | 1 | 2.4 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.8783 | 0 | 38.2653 | 1054.69 | 82.69% | 0 | 24.7746 | 22.3415 | 35.75% | 37.6529
3213 | 0 | 0 | 0 | 2.2 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9666 | 35.7226 | 0 | 90.9666 | 963.7233 | 75.56% | 0 | 0 | 22.3415 | 35.75% | 35.7226
3214 | 0 | 0 | 0 | 0.9 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4525 | 33.8369 | 0 | 86.4525 | 877.2709 | 68.78% | 0 | 0 | 22.3415 | 35.75% | 33.8369
3215 | 0 | 0 | 0 | 1.1 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6992 | 32.6851 | 0 | 83.6992 | 793.5717 | 62.22% | 0 | 0 | 22.3415 | 35.75% | 32.6851
3216 | 0 | 0 | 0 | 0.4 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1568 | 32.0612 | 0 | 82.1568 | 711.4149 | 55.77% | 0 | 0 | 22.3415 | 35.75% | 32.0612
3217 | 0 | 0 | 0 | 0.6 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7459 | 31.8996 | 0 | 81.7459 | 629.669 | 49.37% | 0 | 0 | 22.3415 | 35.75% | 31.8996
3218 | 0 | 0 | 0 | 0.5 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7423 | 32.3467 | 0 | 82.7423 | 546.9267 | 42.88% | 0 | 0 | 22.3415 | 35.75% | 32.3467
3219 | 0 | 0 | 0 | 0.7 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8345 | 34.582 | 0 | 87.8345 | 459.0922 | 35.99% | 0 | 0 | 22.3415 | 35.75% | 34.582
3220 | 0 | 0 | 0 | 0.8 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6982 | 37.5846 | 0 | 94.6982 | 364.394 | 28.57% | 0 | 0 | 22.3415 | 35.75% | 37.5846
3221 | 0 | 0 | 0 | 0.6 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6361 | 34.505 | 0 | 87.6361 | 276.7579 | 21.7% | 0 | 5.6046 | 16.1387 | 25.82% | 40.1096
3222 | 241 | 51 | 21 | 0.5 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0315 | 41.6123 | 0 | 104.0315 | 172.7265 | 13.54% | 0 | 0 | 16.1387 | 25.82% | 41.6123
3223 | 659 | 235 | 49 | 1.2 | 16.1 | 0 | 0 | 0 | 0 | 2.7407 | 0 | 0 | 2.7407 | 0 | 0 | 0 | 99.884 | 39.6779 | 0 | 99.884 | 72.8424 | 5.711% | 0 | 0 | 16.1387 | 25.82% | 42.4187
3224 | 816 | 447 | 63 | 1.4 | 19.1 | 0 | 0 | 0 | 0 | 15.4537 | 0 | 0 | 15.4537 | 0 | 0 | 0 | 72.8424 | 27.8257 | 0 | 72.8424 | 0 | 0% | 0 | 0 | 16.1387 | 25.82% | 43.2793
3225 | 892 | 646 | 72 | 1.7 | 22.2 | 0 | 0 | 0 | 58.1152 | 35.1172 | 0 | 0 | 35.1172 | 0 | 0 | 0 | 0 | 0 | 58.1152 | 0 | 58.1152 | 4.556% | 0 | 8.935 | 6.25 | 10% | 44.0523
3226 | 914 | 807 | 88 | 3.1 | 24.1 | 0 | 0 | 0 | 0 | 44.1233 | 6.3194 | 0 | 44.1233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1152 | 4.556% | 0 | 0 | 6.25 | 10% | 44.1233
3227 | 887 | 921 | 130 | 4 | 26.3 | 0 | 0 | 0 | 0 | 43.1498 | 17.859 | 0 | 43.1498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1152 | 4.556% | 0 | 0 | 6.25 | 10% | 43.1498
3228 | 897 | 978 | 126 | 4 | 28.8 | 0 | 0 | 0 | 0 | 42.4284 | 23.9816 | 0 | 42.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1152 | 4.556% | 0 | 0 | 6.25 | 10% | 42.4284
3229 | 951 | 999 | 92 | 5.8 | 31.3 | 0 | 0 | 0 | 268.209 | 42.7644 | 27.438 | 0.61726 | 42.1471 | 0 | 0 | 0 | 0 | 0 | 268.209 | 0 | 326.3242 | 25.58% | 0.61726 | 0 | 6.8077 | 10.89% | 42.1471
3230 | 948 | 947 | 86 | 6.7 | 32.4 | 0 | 0 | 0 | 264.2979 | 67.0663 | 1.1229 | 25 | 42.0663 | 0 | 0 | 0 | 0 | 0 | 264.2979 | 0 | 590.6221 | 46.3% | 25 | 0 | 29.3967 | 47.03% | 42.0663
3231 | 936 | 842 | 79 | 7.5 | 32.5 | 0 | 0 | 0 | 253.8147 | 61.8517 | 0 | 20.394 | 41.4577 | 0 | 0 | 0 | 0 | 0 | 253.8147 | 0 | 844.4368 | 66.2% | 20.394 | 0 | 47.8239 | 76.52% | 41.4577
3232 | 905 | 685 | 70 | 7 | 32.4 | 0 | 0 | 0 | 235.293 | 50.5617 | 0 | 9.3254 | 41.2363 | 0 | 0 | 0 | 0 | 0 | 235.293 | 0 | 1079.7299 | 84.65% | 9.3254 | 0 | 56.25 | 90% | 41.2363
3233 | 809 | 481 | 68 | 5.5 | 32 | 0 | 0 | 0 | 195.7803 | 34.5058 | 0 | 0 | 34.5058 | 0 | 0 | 0 | 0 | 0 | 195.7803 | 0 | 1275.5102 | 100% | 0 | 7.3558 | 48.1091 | 76.97% | 41.8616
3234 | 640 | 281 | 70 | 4.6 | 28.6 | 0 | 0 | 0 | 0 | 15.8704 | 0 | 0 | 15.8704 | 0 | 0 | 0 | 38.2653 | 12.6149 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 14.3818 | 32.1923 | 51.51% | 42.8671
3235 | 328 | 97 | 48 | 3 | 24.9 | 0 | 0 | 0 | 0 | 2.3994 | 0 | 0 | 2.3994 | 0 | 0 | 0 | 64.2635 | 23.8433 | 0 | 64.2635 | 1172.9814 | 91.96% | 0 | 14.6301 | 16.0006 | 25.6% | 40.8728
3236 | 0 | 1 | 1 | 2.1 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1162 | 35.1002 | 0 | 90.1162 | 1082.8652 | 84.9% | 0 | 0 | 16.0006 | 25.6% | 35.1002
3237 | 0 | 0 | 0 | 1.4 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4343 | 35.6808 | 0 | 91.4343 | 991.4309 | 77.73% | 0 | 0 | 16.0006 | 25.6% | 35.6808
3238 | 0 | 0 | 0 | 5.8 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4169 | 34.0305 | 0 | 87.4169 | 904.014 | 70.87% | 0 | 0 | 16.0006 | 25.6% | 34.0305
3239 | 0 | 0 | 0 | 6.8 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7842 | 32.6364 | 0 | 83.7842 | 820.2299 | 64.31% | 0 | 0 | 16.0006 | 25.6% | 32.6364
3240 | 0 | 0 | 0 | 6.2 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7777 | 32.2548 | 0 | 82.7777 | 737.4522 | 57.82% | 0 | 0 | 16.0006 | 25.6% | 32.2548
3241 | 0 | 0 | 0 | 5.2 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5456 | 32.1657 | 0 | 82.5456 | 654.9066 | 51.34% | 0 | 0 | 16.0006 | 25.6% | 32.1657
3242 | 0 | 0 | 0 | 4.1 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8044 | 32.738 | 0 | 83.8044 | 571.1021 | 44.77% | 0 | 0 | 16.0006 | 25.6% | 32.738
3243 | 0 | 0 | 0 | 3.7 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1022 | 35.4928 | 0 | 90.1022 | 481 | 37.71% | 0 | 0 | 16.0006 | 25.6% | 35.4928
3244 | 0 | 0 | 0 | 3.2 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3965 | 38.6751 | 0 | 97.3965 | 383.6034 | 30.07% | 0 | 0 | 16.0006 | 25.6% | 38.6751
3245 | 0 | 0 | 0 | 3.4 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.5375 | 41.3533 | 0 | 103.5375 | 280.0659 | 21.96% | 0 | 0 | 16.0006 | 25.6% | 41.3533
3246 | 154 | 47 | 26 | 3.9 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.0889 | 42.8936 | 0 | 107.0889 | 172.977 | 13.56% | 0 | 0 | 16.0006 | 25.6% | 42.8936
3247 | 540 | 224 | 68 | 4.3 | 16 | 0 | 0 | 0 | 0 | 3.7518 | 0 | 0 | 3.7518 | 0 | 0 | 0 | 99.9372 | 39.7058 | 0 | 99.9372 | 73.0398 | 5.726% | 0 | 0 | 16.0006 | 25.6% | 43.4576
3248 | 739 | 435 | 84 | 5.1 | 18.1 | 0 | 0 | 0 | 0 | 15.87 | 0 | 0 | 15.87 | 0 | 0 | 0 | 73.0398 | 27.9539 | 0 | 73.0398 | 0 | 0% | 0 | 0 | 16.0006 | 25.6% | 43.8239
3249 | 848 | 636 | 88 | 5.1 | 19.8 | 0 | 0 | 0 | 0 | 35.7587 | 0 | 0 | 35.7587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 8.8103 | 6.25 | 10% | 44.569
3250 | 900 | 803 | 91 | 4.4 | 21.7 | 0 | 0 | 0 | 233.8345 | 44.7083 | 6.1464 | 0 | 44.7083 | 0 | 0 | 0 | 0 | 0 | 233.8345 | 0 | 233.8345 | 18.33% | 0 | 0 | 6.25 | 10% | 44.7083
3251 | 923 | 921 | 96 | 2.5 | 23.7 | 0 | 0 | 0 | 252.0608 | 43.3378 | 16.9379 | 0 | 43.3378 | 0 | 0 | 0 | 0 | 0 | 252.0608 | 0 | 485.8952 | 38.09% | 0 | 0 | 6.25 | 10% | 43.3378
3252 | 926 | 983 | 101 | 1.5 | 26.1 | 0 | 0 | 0 | 260.4804 | 42.6777 | 21.8336 | 0 | 42.6777 | 0 | 0 | 0 | 0 | 0 | 260.4804 | 0 | 746.3756 | 58.52% | 0 | 0 | 6.25 | 10% | 42.6777
3253 | 925 | 987 | 103 | 4.6 | 26.6 | 0 | 0 | 0 | 261.3058 | 45.0156 | 24.6777 | 2.6192 | 42.3964 | 0 | 0 | 0 | 0 | 0 | 261.3058 | 0 | 1007.6814 | 79% | 2.6192 | 0 | 8.6166 | 13.79% | 42.3964
3254 | 907 | 932 | 106 | 5.4 | 26.3 | 0 | 0 | 0 | 32.2064 | 67.3435 | 0.42489 | 25 | 42.3435 | 0 | 0 | 0 | 0 | 0 | 32.2064 | 0 | 1039.8878 | 81.53% | 25 | 0 | 31.2056 | 49.93% | 42.3435
3255 | 871 | 820 | 108 | 6.1 | 25.2 | 0 | 0 | 0 | 235.6224 | 61.1119 | 0 | 19.3171 | 41.7947 | 0 | 0 | 0 | 0 | 0 | 235.6224 | 0 | 1275.5102 | 100% | 19.3171 | 0 | 48.6598 | 77.86% | 41.7947
3256 | 830 | 663 | 98 | 6.3 | 23.7 | 0 | 0 | 0 | 0 | 50.1004 | 0 | 8.4003 | 41.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 8.4003 | 0 | 56.25 | 90% | 41.7
3257 | 722 | 470 | 96 | 6.1 | 22 | 0 | 0 | 0 | 0 | 34.495 | 7.1054e-15 | 0 | 34.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 7.7078 | 47.7195 | 76.35% | 42.2028
3258 | 527 | 264 | 92 | 6 | 20.5 | 0 | 0 | 0 | 0 | 15.6566 | 0 | 0 | 15.6566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 20.0512 | 32.08% | 40.6566
3259 | 178 | 62 | 35 | 4.9 | 18.5 | 0 | 0 | 0 | 0 | 1.6389 | 0 | 0 | 1.6389 | 0 | 0 | 0 | 98.6627 | 39.0194 | 0 | 98.6627 | 1176.8475 | 92.26% | 0 | 0 | 20.0512 | 32.08% | 40.6583
3260 | 0 | 1 | 1 | 3 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0907 | 37.5498 | 0 | 95.0907 | 1081.7568 | 84.81% | 0 | 0 | 20.0512 | 32.08% | 37.5498
3261 | 0 | 0 | 0 | 2.5 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081.7568 | 84.81% | 0 | 0 | 20.0512 | 32.08% | 0
3262 | 0 | 0 | 0 | 1.7 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081.7568 | 84.81% | 0 | 0 | 20.0512 | 32.08% | 0
3263 | 0 | 0 | 0 | 0.7 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081.7568 | 84.81% | 0 | 0 | 20.0512 | 32.08% | 0
3264 | 0 | 0 | 0 | 2.4 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081.7568 | 84.81% | 0 | 0 | 20.0512 | 32.08% | 0
3265 | 0 | 0 | 0 | 4.3 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081.7568 | 84.81% | 0 | 0 | 20.0512 | 32.08% | 0
3266 | 0 | 0 | 0 | 9 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081.7568 | 84.81% | 0 | 0 | 20.0512 | 32.08% | 0
3267 | 0 | 0 | 0 | 9.7 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081.7568 | 84.81% | 0 | 3.5096 | 16.1669 | 25.87% | 3.5096
3268 | 0 | 0 | 0 | 6.9 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1215 | 38.2531 | 0 | 97.1215 | 984.6353 | 77.2% | 0 | 0 | 16.1669 | 25.87% | 38.2531
3269 | 0 | 0 | 0 | 4.4 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8589 | 40.7628 | 0 | 102.8589 | 881.7764 | 69.13% | 0 | 0 | 16.1669 | 25.87% | 40.7628
3270 | 101 | 55 | 43 | 9.7 | 18.5 | 0 | 0 | 0 | 0 | 1.6678 | 0 | 0 | 1.6678 | 0 | 0 | 0 | 102.2988 | 40.5921 | 0 | 102.2988 | 779.4776 | 61.11% | 0 | 0 | 16.1669 | 25.87% | 42.2599
3271 | 20 | 141 | 135 | 11.6 | 17.7 | 0 | 0 | 0 | 0 | 6.568 | 0 | 0 | 6.568 | 0 | 0 | 0 | 93.043 | 36.632 | 0 | 93.043 | 686.4346 | 53.82% | 0 | 0 | 16.1669 | 25.87% | 43.2
3272 | 74 | 291 | 248 | 9.8 | 18.1 | 0 | 0 | 0 | 0 | 16.191 | 0 | 0 | 16.191 | 0 | 0 | 0 | 71.9891 | 27.4992 | 0 | 71.9891 | 614.4455 | 48.17% | 0 | 0 | 16.1669 | 25.87% | 43.6902
3273 | 342 | 582 | 346 | 8.8 | 20.5 | 0 | 0 | 0 | 66.2307 | 34.9497 | 0 | 0 | 34.9497 | 0 | 0 | 0 | 0 | 0 | 66.2307 | 0 | 680.6762 | 53.37% | 0 | 8.9605 | 6.25 | 10% | 43.9102
3274 | 426 | 753 | 407 | 10.9 | 23.2 | 0 | 0 | 0 | 94.7855 | 49.1356 | 0 | 5.6111 | 43.5245 | 0 | 0 | 0 | 0 | 0 | 94.7855 | 0 | 775.4616 | 60.8% | 5.6111 | 0 | 11.32 | 18.11% | 43.5245
3275 | 281 | 717 | 453 | 11.6 | 24.2 | 0 | 0 | 0 | 56.8344 | 48.8563 | 0 | 6.7079 | 42.1485 | 0 | 0 | 0 | 0 | 0 | 56.8344 | 0 | 832.2961 | 65.25% | 6.7079 | 0 | 17.3809 | 27.81% | 42.1485
3276 | 176 | 678 | 495 | 10 | 25.2 | 0 | 0 | 0 | 0 | 46.1453 | 0 | 5.2781 | 40.8672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 832.2961 | 65.25% | 5.2781 | 0 | 22.15 | 35.44% | 40.8672
3277 | 658 | 1037 | 395 | 5.2 | 26.1 | 0 | 0 | 0 | 179.751 | 63.3243 | 8.6757 | 23.1033 | 40.221 | 0 | 0 | 0 | 0 | 0 | 179.751 | 0 | 1012.0471 | 79.34% | 23.1033 | 0 | 43.0253 | 68.84% | 40.221
3278 | 262 | 717 | 467 | 4.6 | 24.8 | 0 | 0 | 0 | 59.4934 | 50.1458 | 0 | 10.1894 | 39.9564 | 0 | 0 | 0 | 0 | 0 | 59.4934 | 0 | 1071.5405 | 84.01% | 10.1894 | 0 | 52.232 | 83.57% | 39.9564
3279 | 88 | 475 | 393 | 3.7 | 25.2 | 0 | 0 | 0 | 0 | 31.1609 | 0 | 4.4468 | 26.7141 | 0 | 0 | 0 | 38.2653 | 12.7284 | 0 | 38.2653 | 1033.2752 | 81.01% | 4.4468 | 0 | 56.25 | 90% | 39.4425
3280 | 6 | 229 | 222 | 4.5 | 23.5 | 0 | 0 | 0 | 0 | 14.1453 | 0 | 0 | 14.1453 | 0 | 0 | 0 | 67.2517 | 25.1997 | 0 | 67.2517 | 966.0235 | 75.74% | 0 | 0 | 56.25 | 90% | 39.345
3281 | 2 | 187 | 184 | 3.7 | 22 | 0 | 0 | 0 | 0 | 11.4961 | 0 | 0 | 11.4961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 966.0235 | 75.74% | 0 | 0.66247 | 55.5168 | 88.83% | 12.1585
3282 | 298 | 205 | 109 | 2.5 | 22.5 | 0 | 0 | 0 | 51.9573 | 12.2215 | 0 | 0 | 12.2215 | 0 | 0 | 0 | 0 | 0 | 51.9573 | 0 | 1017.9808 | 79.81% | 0 | 25 | 27.8485 | 44.56% | 37.2215
3283 | 64 | 48 | 41 | 4.1 | 20.9 | 0 | 0 | 0 | 0 | 2.1658 | 0 | 0 | 2.1658 | 0 | 0 | 0 | 94.0503 | 36.8756 | 0 | 94.0503 | 923.9305 | 72.44% | 0 | 0 | 27.8485 | 44.56% | 39.0414
3284 | 0 | 2 | 2 | 3 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3949 | 36.2449 | 0 | 92.3949 | 831.5357 | 65.19% | 0 | 0 | 27.8485 | 44.56% | 36.2449
3285 | 0 | 0 | 0 | 1.3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9033 | 34.8243 | 0 | 88.9033 | 742.6324 | 58.22% | 0 | 0 | 27.8485 | 44.56% | 34.8243
3286 | 0 | 0 | 0 | 1.5 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7702 | 33.0988 | 0 | 84.7702 | 657.8622 | 51.58% | 0 | 0 | 27.8485 | 44.56% | 33.0988
3287 | 0 | 0 | 0 | 3.3 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5632 | 31.6699 | 0 | 81.5632 | 576.299 | 45.18% | 0 | 0 | 27.8485 | 44.56% | 31.6699
3288 | 0 | 0 | 0 | 1.8 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4666 | 30.766 | 0 | 79.4666 | 496.8323 | 38.95% | 0 | 0 | 27.8485 | 44.56% | 30.766
3289 | 0 | 0 | 0 | 2.2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2215 | 30.2813 | 0 | 78.2215 | 418.6108 | 32.82% | 0 | 0 | 27.8485 | 44.56% | 30.2813
3290 | 0 | 0 | 0 | 2 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5022 | 29.9833 | 0 | 77.5022 | 341.1086 | 26.74% | 0 | 0 | 27.8485 | 44.56% | 29.9833
3291 | 0 | 0 | 0 | 1.4 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8856 | 30.2033 | 0 | 77.8856 | 263.2231 | 20.64% | 0 | 0 | 27.8485 | 44.56% | 30.2033
3292 | 0 | 0 | 0 | 1.8 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3693 | 43.4747 | 0 | 108.3693 | 154.8538 | 12.14% | 12.7658 | 0 | 39.3832 | 63.01% | 30.7089
3293 | 0 | 0 | 0 | 1.1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.8717 | 0 | 127.551 | 27.3028 | 2.141% | 18.6671 | 0 | 56.25 | 90% | 33.2046
3294 | 68 | 43 | 37 | 1.6 | 13.4 | 0 | 0 | 0 | 0 | 1.4083 | 0 | 0 | 1.4083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3028 | 2.141% | 0 | 25 | 28.5817 | 45.73% | 26.4083
3295 | 529 | 218 | 53 | 1 | 16.4 | 0 | 0 | 0 | 72.8418 | 2.6754 | 4.4409e-16 | 0 | 2.6754 | 0 | 0 | 0 | 0 | 0 | 72.8418 | 0 | 100.1446 | 7.851% | 0 | 20.178 | 6.25 | 10% | 22.8534
3296 | 803 | 455 | 69 | 1 | 18.8 | 0 | 0 | 0 | 0 | 15.5506 | 0 | 0 | 15.5506 | 0 | 0 | 0 | 61.8793 | 23.0994 | 0 | 61.8793 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 38.65
3297 | 857 | 660 | 101 | 1.5 | 20.5 | 0 | 0 | 0 | 0 | 25.9074 | 9.9469 | 0 | 25.9074 | 0 | 0 | 0 | 38.2653 | 12.8541 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.7614
3298 | 864 | 791 | 102 | 2.1 | 21.3 | 0 | 0 | 0 | 0 | 38.7656 | 10.0228 | 0 | 38.7656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.7656
3299 | 896 | 946 | 141 | 3.8 | 21.8 | 0 | 0 | 0 | 0 | 37.6389 | 25.1268 | 0 | 37.6389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 37.6389
3300 | 745 | 925 | 211 | 3.6 | 22.5 | 0 | 0 | 0 | 0 | 35.7477 | 28.7282 | 0 | 35.7477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 35.7477
3301 | 651 | 884 | 252 | 3.8 | 22.9 | 0 | 0 | 0 | 72.4598 | 34.6516 | 28.4476 | 0 | 34.6516 | 0 | 0 | 0 | 0 | 0 | 72.4598 | 0 | 72.4598 | 5.681% | 0 | 0 | 6.25 | 10% | 34.6516
3302 | 599 | 789 | 238 | 4.5 | 22.9 | 0 | 0 | 0 | 160.9507 | 43.9466 | 14.1673 | 9.6209 | 34.3257 | 0 | 0 | 0 | 0 | 0 | 160.9507 | 0 | 233.4105 | 18.3% | 9.6209 | 0 | 14.9431 | 23.91% | 34.3257
3303 | 669 | 808 | 255 | 2.8 | 23.4 | 0 | 0 | 0 | 178.886 | 58.295 | 0 | 24.057 | 34.238 | 0 | 0 | 0 | 0 | 0 | 178.886 | 0 | 412.2965 | 32.32% | 24.057 | 0 | 36.68 | 58.69% | 34.238
3304 | 895 | 737 | 125 | 5 | 24.7 | 0 | 0 | 0 | 233.9409 | 54.7202 | 0 | 20.1327 | 34.5875 | 0 | 0 | 0 | 0 | 0 | 233.9409 | 0 | 646.2373 | 50.67% | 20.1327 | 0 | 54.8711 | 87.79% | 34.5875
3305 | 827 | 504 | 78 | 6.1 | 23.9 | 0 | 0 | 0 | 199.9336 | 36.7933 | 0 | 1.5261 | 35.2672 | 0 | 0 | 0 | 0 | 0 | 199.9336 | 0 | 846.171 | 66.34% | 1.5261 | 0 | 56.25 | 90% | 35.2672
3306 | 705 | 288 | 55 | 6.5 | 22.7 | 0 | 0 | 0 | 145.6427 | 16.301 | 0 | 0 | 16.301 | 0 | 0 | 0 | 0 | 0 | 145.6427 | 0 | 991.8137 | 77.76% | 0 | 20.6862 | 33.3559 | 53.37% | 36.9872
3307 | 389 | 89 | 29 | 5.8 | 21.3 | 0 | 0 | 0 | 0 | 1.4705 | 0 | 0 | 1.4705 | 0 | 0 | 0 | 88.8799 | 34.6225 | 0 | 88.8799 | 902.9338 | 70.79% | 0 | 0 | 33.3559 | 53.37% | 36.093
3308 | 0 | 1 | 1 | 5.4 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6946 | 30.7511 | 0 | 79.6946 | 823.2392 | 64.54% | 0 | 3.1443 | 29.876 | 47.8% | 33.8954
3309 | 0 | 0 | 0 | 2.8 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8605 | 32.1698 | 0 | 82.8605 | 740.3787 | 58.05% | 0 | 0 | 29.876 | 47.8% | 32.1698
3310 | 0 | 0 | 0 | 3.4 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3195 | 30.2298 | 0 | 78.3195 | 662.0593 | 51.91% | 0 | 0 | 29.876 | 47.8% | 30.2298
3311 | 0 | 0 | 0 | 2.5 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8944 | 28.7772 | 0 | 74.8944 | 587.1649 | 46.03% | 0 | 0 | 29.876 | 47.8% | 28.7772
3312 | 0 | 0 | 0 | 1.9 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8981 | 27.9319 | 0 | 72.8981 | 514.2668 | 40.32% | 0 | 0 | 29.876 | 47.8% | 27.9319
3313 | 0 | 0 | 0 | 1.5 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.0728 | 27.6227 | 0 | 72.0728 | 442.194 | 34.67% | 0 | 0 | 29.876 | 47.8% | 27.6227
3314 | 0 | 0 | 0 | 1.5 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.6998 | 27.4639 | 0 | 71.6998 | 370.4942 | 29.05% | 0 | 0 | 29.876 | 47.8% | 27.4639
3315 | 0 | 0 | 0 | 1.1 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8707 | 27.5349 | 0 | 71.8707 | 298.6235 | 23.41% | 0 | 0 | 29.876 | 47.8% | 27.5349
3316 | 0 | 0 | 0 | 0.8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.0613 | 27.2049 | 0 | 71.0613 | 227.5622 | 17.84% | 0 | 0 | 29.876 | 47.8% | 27.2049
3317 | 0 | 0 | 0 | 1.1 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.9094 | 28.8705 | 0 | 74.9094 | 152.6528 | 11.97% | 0 | 0 | 29.876 | 47.8% | 28.8705
3318 | 0 | 21 | 21 | 1.8 | 15.3 | 0 | 0 | 0 | 0 | 0.62323 | 0 | 0 | 0.62323 | 0 | 0 | 0 | 79.0643 | 30.672 | 0 | 79.0643 | 73.5885 | 5.769% | 0 | 0 | 29.876 | 47.8% | 31.2952
3319 | 1 | 102 | 101 | 1.5 | 15.5 | 0 | 0 | 0 | 0 | 5.3171 | 0 | 0 | 5.3171 | 0 | 0 | 0 | 73.5885 | 28.2872 | 0 | 73.5885 | 0 | 0% | 0 | 0 | 29.876 | 47.8% | 33.6043
3320 | 347 | 367 | 196 | 1 | 18.1 | 0 | 0 | 0 | 0 | 16.838 | 0 | 0 | 16.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 17.8582 | 10.1118 | 16.18% | 34.6962
3321 | 555 | 572 | 193 | 1.5 | 19.7 | 0 | 0 | 0 | 0 | 31.6747 | 0 | 0 | 31.6747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.4894 | 6.25 | 10% | 35.1641
3322 | 935 | 830 | 86 | 2.3 | 21.1 | 0 | 0 | 0 | 96.1284 | 35.6335 | 15.414 | 0 | 35.6335 | 0 | 0 | 0 | 0 | 0 | 96.1284 | 0 | 96.1284 | 7.536% | 0 | 0 | 6.25 | 10% | 35.6335
3323 | 971 | 952 | 80 | 3.2 | 22.3 | 0 | 0 | 0 | 0 | 35.2936 | 27.1456 | 0 | 35.2936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1284 | 7.536% | 0 | 0 | 6.25 | 10% | 35.2936
3324 | 974 | 1021 | 91 | 2.8 | 23.2 | 0 | 0 | 0 | 274.1101 | 33.6252 | 35.1592 | 0 | 33.6252 | 0 | 0 | 0 | 0 | 0 | 274.1101 | 0 | 370.2386 | 29.03% | 0 | 0 | 6.25 | 10% | 33.6252
3325 | 970 | 1037 | 106 | 3.1 | 23.5 | 0 | 0 | 0 | 276.1318 | 32.3356 | 39.5876 | 0 | 32.3356 | 0 | 0 | 0 | 0 | 0 | 276.1318 | 0 | 646.3704 | 50.68% | 0 | 0 | 6.25 | 10% | 32.3356
3326 | 947 | 983 | 116 | 4 | 23.8 | 0 | 0 | 0 | 266.1389 | 44.162 | 26.1865 | 12.1871 | 31.9749 | 0 | 0 | 0 | 0 | 0 | 266.1389 | 0 | 912.5093 | 71.54% | 12.1871 | 0 | 17.2618 | 27.62% | 31.9749
3327 | 916 | 852 | 98 | 5.8 | 23.9 | 0 | 0 | 0 | 249.2148 | 57.2687 | 5.733 | 25 | 32.2687 | 0 | 0 | 0 | 0 | 0 | 249.2148 | 0 | 1161.7241 | 91.08% | 25 | 0 | 39.8508 | 63.76% | 32.2687
3328 | 839 | 681 | 104 | 4.9 | 23.3 | 0 | 0 | 0 | 0 | 50.5006 | 0 | 17.3684 | 33.1322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1161.7241 | 91.08% | 17.3684 | 0 | 55.5442 | 88.87% | 33.1322
3329 | 790 | 491 | 79 | 3.9 | 23.5 | 0 | 0 | 0 | 0 | 35.1918 | 0 | 0.78113 | 34.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1161.7241 | 91.08% | 0.78113 | 0 | 56.25 | 90% | 34.4107
3330 | 686 | 290 | 60 | 4.5 | 23.6 | 0 | 0 | 0 | 0 | 16.1833 | 0 | 0 | 16.1833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1161.7241 | 91.08% | 0 | 20.3749 | 33.7004 | 53.92% | 36.5582
3331 | 112 | 67 | 47 | 5.6 | 21.9 | 0 | 0 | 0 | 0 | 2.3982 | 0 | 0 | 2.3982 | 0 | 0 | 0 | 87.949 | 34.1823 | 0 | 87.949 | 1073.775 | 84.18% | 0 | 0 | 33.7004 | 53.92% | 36.5805
3332 | 0 | 1 | 1 | 3.3 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.7615 | 18.2475 | 0 | 50.7615 | 1023.0136 | 80.2% | 0 | 15.8721 | 16.1342 | 25.81% | 34.1196
3333 | 0 | 0 | 0 | 0.6 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4192 | 32.0361 | 0 | 82.4192 | 940.5943 | 73.74% | 0 | 0 | 16.1342 | 25.81% | 32.0361
3334 | 0 | 0 | 0 | 0.9 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2028 | 30.1838 | 0 | 78.2028 | 862.3915 | 67.61% | 0 | 0 | 16.1342 | 25.81% | 30.1838
3335 | 0 | 0 | 0 | 1.6 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.6145 | 29.0767 | 0 | 75.6145 | 786.777 | 61.68% | 0 | 0 | 16.1342 | 25.81% | 29.0767
3336 | 0 | 0 | 0 | 2.1 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.0632 | 28.8817 | 0 | 75.0632 | 711.7138 | 55.8% | 0 | 0 | 16.1342 | 25.81% | 28.8817
3337 | 0 | 0 | 0 | 2.2 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.2956 | 28.9973 | 0 | 75.2956 | 636.4182 | 49.9% | 0 | 0 | 16.1342 | 25.81% | 28.9973
3338 | 0 | 0 | 0 | 1.3 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1914 | 29.8552 | 0 | 77.1914 | 559.2268 | 43.84% | 0 | 0 | 16.1342 | 25.81% | 29.8552
3339 | 0 | 0 | 0 | 1.2 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7726 | 33.1586 | 0 | 84.7726 | 474.4542 | 37.2% | 0 | 0 | 16.1342 | 25.81% | 33.1586
3340 | 0 | 0 | 0 | 1.8 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7229 | 37.022 | 0 | 93.7229 | 380.7313 | 29.85% | 0 | 0 | 16.1342 | 25.81% | 37.022
3341 | 0 | 0 | 0 | 1.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.647 | 40.494 | 0 | 101.647 | 279.0843 | 21.88% | 0 | 0 | 16.1342 | 25.81% | 40.494
3342 | 284 | 58 | 23 | 1.3 | 14.9 | 0 | 0 | 0 | 0 | 0.72031 | 0 | 0 | 0.72031 | 0 | 0 | 0 | 104.0818 | 41.5563 | 0 | 104.0818 | 175.0025 | 13.72% | 0 | 0 | 16.1342 | 25.81% | 42.2766
3343 | 672 | 247 | 50 | 0.9 | 18.5 | 0 | 0 | 0 | 0 | 2.7583 | 0 | 0 | 2.7583 | 0 | 0 | 0 | 101.5904 | 40.2857 | 0 | 101.5904 | 73.412 | 5.756% | 0 | 0 | 16.1342 | 25.81% | 43.044
3344 | 824 | 459 | 64 | 0.7 | 21.2 | 0 | 0 | 0 | 0 | 15.2332 | 0 | 0 | 15.2332 | 0 | 0 | 0 | 73.412 | 27.9696 | 0 | 73.412 | 0 | 0% | 0 | 0 | 16.1342 | 25.81% | 43.2027
3345 | 893 | 657 | 76 | 1.2 | 22.8 | 0 | 0 | 0 | 217.0996 | 34.7968 | 0 | 0 | 34.7968 | 0 | 0 | 0 | 0 | 0 | 217.0996 | 0 | 217.0996 | 17.02% | 0 | 8.9309 | 6.25 | 10% | 43.7278
3346 | 930 | 832 | 95 | 2.2 | 23.5 | 0 | 0 | 0 | 243.8054 | 43.5649 | 7.2644 | 0 | 43.5649 | 0 | 0 | 0 | 0 | 0 | 243.8054 | 0 | 460.9051 | 36.13% | 0 | 0 | 6.25 | 10% | 43.5649
3347 | 940 | 953 | 110 | 3.6 | 24.2 | 0 | 0 | 0 | 112.6624 | 42.2418 | 20.201 | 0 | 42.2418 | 0 | 0 | 0 | 0 | 0 | 112.6624 | 0 | 573.5674 | 44.97% | 0 | 0 | 6.25 | 10% | 42.2418
3348 | 952 | 1046 | 137 | 4.6 | 24.6 | 0 | 0 | 0 | 266.1114 | 41.5148 | 29.7686 | 0 | 41.5148 | 0 | 0 | 0 | 0 | 0 | 266.1114 | 0 | 839.6789 | 65.83% | 0 | 0 | 6.25 | 10% | 41.5148
3349 | 480 | 728 | 263 | 4 | 24.1 | 0 | 0 | 0 | 126.6865 | 45.5804 | 6.7116 | 4.5656 | 41.0148 | 0 | 0 | 0 | 0 | 0 | 126.6865 | 0 | 966.3654 | 75.76% | 4.5656 | 0 | 10.3753 | 16.6% | 41.0148
3350 | 406 | 691 | 315 | 3 | 24.1 | 0 | 0 | 0 | 103.943 | 49.5949 | 0 | 8.8084 | 40.7864 | 0 | 0 | 0 | 0 | 0 | 103.943 | 0 | 1070.3084 | 83.91% | 8.8084 | 0 | 18.3342 | 29.33% | 40.7864
3351 | 760 | 842 | 219 | 3.5 | 24.8 | 0 | 0 | 0 | 205.2018 | 61.2183 | 0 | 21.0307 | 40.1876 | 0 | 0 | 0 | 0 | 0 | 205.2018 | 0 | 1275.5102 | 100% | 21.0307 | 0 | 37.3368 | 59.74% | 40.1876
3352 | 739 | 652 | 141 | 5.1 | 24.5 | 0 | 0 | 0 | 0 | 48.0791 | 0 | 20.9319 | 27.1471 | 0 | 0 | 0 | 38.2653 | 12.7494 | 0 | 38.2653 | 1237.2449 | 97% | 20.9319 | 0 | 56.25 | 90% | 39.8965
3353 | 82 | 270 | 224 | 4.9 | 23.7 | 0 | 0 | 0 | 0 | 17.2965 | 0 | 0 | 17.2965 | 0 | 0 | 0 | 62.9933 | 23.3646 | 0 | 62.9933 | 1174.2516 | 92.06% | 0 | 0 | 56.25 | 90% | 40.6611
3354 | 522 | 271 | 99 | 3.6 | 24 | 0 | 0 | 0 | 101.2586 | 15.6748 | 0 | 0 | 15.6748 | 0 | 0 | 0 | 0 | 0 | 101.2586 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 40.6748
3355 | 178 | 85 | 52 | 3.9 | 21.7 | 0 | 0 | 0 | 0 | 2.5566 | 0 | 0 | 2.5566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 20.178 | 6.25 | 10% | 22.7346
3356 | 0 | 2 | 2 | 2.6 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2845 | 36.6042 | 0 | 93.2845 | 1182.2257 | 92.69% | 0 | 0 | 6.25 | 10% | 36.6042
3357 | 0 | 0 | 0 | 1.7 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8241 | 34.7031 | 0 | 88.8241 | 1093.4017 | 85.72% | 0 | 0 | 6.25 | 10% | 34.7031
3358 | 0 | 0 | 0 | 1.6 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5141 | 32.8899 | 0 | 84.5141 | 1008.8875 | 79.1% | 0 | 0 | 6.25 | 10% | 32.8899
3359 | 0 | 0 | 0 | 2.2 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8489 | 31.798 | 0 | 81.8489 | 927.0387 | 72.68% | 0 | 0 | 6.25 | 10% | 31.798
3360 | 0 | 0 | 0 | 2.9 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8359 | 31.3885 | 0 | 80.8359 | 846.2028 | 66.34% | 0 | 0 | 6.25 | 10% | 31.3885
3361 | 0 | 0 | 0 | 2.8 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0543 | 31.4832 | 0 | 81.0543 | 765.1485 | 59.99% | 0 | 0 | 6.25 | 10% | 31.4832
3362 | 0 | 0 | 0 | 2.7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9536 | 31.901 | 0 | 81.9536 | 683.195 | 53.56% | 0 | 0 | 6.25 | 10% | 31.901
3363 | 0 | 0 | 0 | 1 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1761 | 34.6335 | 0 | 88.1761 | 595.0188 | 46.65% | 0 | 0 | 6.25 | 10% | 34.6335
3364 | 0 | 0 | 0 | 0.7 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2874 | 38.1891 | 0 | 96.2874 | 498.7314 | 39.1% | 0 | 0 | 6.25 | 10% | 38.1891
3365 | 0 | 0 | 0 | 1.1 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.6284 | 45.7372 | 0 | 113.6284 | 385.1031 | 30.19% | 4.3241 | 0 | 10.157 | 16.25% | 41.4131
3366 | 0 | 28 | 28 | 1.3 | 14 | 0 | 0 | 0 | 0 | 0.96563 | 0 | 0.96563 | 0 | 0 | 0 | 0 | 127.551 | 51.8013 | 0 | 127.551 | 257.552 | 20.19% | 10.0684 | 0 | 19.2544 | 30.81% | 42.6986
3367 | 113 | 160 | 125 | 1.3 | 16 | 0 | 0 | 0 | 0 | 5.9898 | 0 | 0 | 5.9898 | 0 | 0 | 0 | 94.4179 | 37.3105 | 0 | 94.4179 | 163.1341 | 12.79% | 0 | 0 | 19.2544 | 30.81% | 43.3002
3368 | 22 | 260 | 246 | 2.1 | 18.1 | 0 | 0 | 0 | 0 | 15.2068 | 0 | 0 | 15.2068 | 0 | 0 | 0 | 74.4949 | 28.5836 | 0 | 74.4949 | 88.6392 | 6.949% | 0 | 0 | 19.2544 | 30.81% | 43.7905
3369 | 390 | 566 | 295 | 3.1 | 20.4 | 0 | 0 | 0 | 84.1079 | 32.5527 | 0 | 0 | 32.5527 | 0 | 0 | 0 | 0 | 0 | 84.1079 | 0 | 172.7472 | 13.54% | 0 | 11.7503 | 6.25 | 10% | 44.303
3370 | 794 | 811 | 177 | 3.8 | 22.3 | 0 | 0 | 0 | 204.4443 | 51.1516 | 0 | 6.9238 | 44.2278 | 0 | 0 | 0 | 0 | 0 | 204.4443 | 0 | 377.1915 | 29.57% | 6.9238 | 0 | 12.5061 | 20.01% | 44.2278
3371 | 921 | 966 | 138 | 4.5 | 23.6 | 0 | 0 | 0 | 249.9033 | 63.6838 | 0 | 20.7025 | 42.9813 | 0 | 0 | 0 | 0 | 0 | 249.9033 | 0 | 627.0948 | 49.16% | 20.7025 | 0 | 31.212 | 49.94% | 42.9813
3372 | 287 | 490 | 214 | 6.6 | 23.3 | 0 | 0 | 0 | 64.7819 | 35.4853 | 0 | 0 | 35.4853 | 0 | 0 | 0 | 0 | 0 | 64.7819 | 0 | 691.8767 | 54.24% | 0 | 6.5281 | 23.9871 | 38.38% | 42.0134
3373 | 2 | 80 | 77 | 4.4 | 16.5 | 0 | 0 | 0 | 0 | 4.6313 | 0 | 0 | 4.6313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.8767 | 54.24% | 0 | 0 | 23.9871 | 38.38% | 4.6313
3374 | 365 | 634 | 301 | 3.3 | 18.8 | 0 | 0 | 0 | 91.5181 | 47.0129 | 0 | 5.5761 | 41.4368 | 0 | 0 | 0 | 0 | 0 | 91.5181 | 0 | 783.3948 | 61.42% | 5.5761 | 0 | 29.0255 | 46.44% | 41.4368
3375 | 651 | 852 | 308 | 3.6 | 20.8 | 0 | 0 | 0 | 173.047 | 61.2124 | 0 | 20.4274 | 40.785 | 0 | 0 | 0 | 0 | 0 | 173.047 | 0 | 956.4419 | 74.99% | 20.4274 | 0 | 47.4829 | 75.97% | 40.785
3376 | 443 | 599 | 286 | 3.7 | 21.4 | 0 | 0 | 0 | 106.824 | 42.7501 | 0 | 2.2033 | 40.5469 | 0 | 0 | 0 | 0 | 0 | 106.824 | 0 | 1063.2659 | 83.36% | 2.2033 | 0 | 49.4736 | 79.16% | 40.5469
3377 | 24 | 162 | 149 | 3.8 | 20.4 | 0 | 0 | 0 | 0 | 10.2565 | 0 | 0 | 10.2565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063.2659 | 83.36% | 0 | 5.6814 | 43.1858 | 69.1% | 15.9379
3378 | 252 | 228 | 139 | 3.9 | 20.7 | 0 | 0 | 0 | 40.6699 | 13.2686 | 0 | 0 | 13.2686 | 0 | 0 | 0 | 0 | 0 | 40.6699 | 0 | 1103.9358 | 86.55% | 0 | 25 | 15.5175 | 24.83% | 38.2686
3379 | 21 | 44 | 40 | 3.8 | 19.3 | 0 | 0 | 0 | 0 | 2.1822 | 0 | 0 | 2.1822 | 0 | 0 | 0 | 96.5998 | 38.0792 | 0 | 96.5998 | 1007.336 | 78.98% | 0 | 0 | 15.5175 | 24.83% | 40.2614
3380 | 0 | 2 | 2 | 3.8 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7749 | 36.9593 | 0 | 93.7749 | 913.5611 | 71.62% | 0 | 0 | 15.5175 | 24.83% | 36.9593
3381 | 0 | 0 | 0 | 3.9 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3409 | 35.1028 | 0 | 89.3409 | 824.2202 | 64.62% | 0 | 0 | 15.5175 | 24.83% | 35.1028
3382 | 0 | 0 | 0 | 3 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1325 | 33.3077 | 0 | 85.1325 | 739.0877 | 57.94% | 0 | 0 | 15.5175 | 24.83% | 33.3077
3383 | 0 | 0 | 0 | 2.5 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3395 | 32.1086 | 0 | 82.3395 | 656.7482 | 51.49% | 0 | 0 | 15.5175 | 24.83% | 32.1086
3384 | 0 | 0 | 0 | 1.9 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4344 | 31.7186 | 0 | 81.4344 | 575.3138 | 45.1% | 0 | 0 | 15.5175 | 24.83% | 31.7186
3385 | 0 | 0 | 0 | 1.3 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5186 | 31.7618 | 0 | 81.5186 | 493.7952 | 38.71% | 0 | 0 | 15.5175 | 24.83% | 31.7618
3386 | 0 | 0 | 0 | 1.9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7404 | 36.2264 | 0 | 91.7404 | 402.0548 | 31.52% | 3.8407 | 0 | 18.9877 | 30.38% | 32.3857
3387 | 0 | 0 | 0 | 2.1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.8472 | 0 | 127.551 | 274.5038 | 21.52% | 16.9798 | 0 | 34.33 | 54.93% | 34.8675
3388 | 0 | 0 | 0 | 2.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.8866 | 0 | 127.551 | 146.9527 | 11.52% | 13.6948 | 0 | 46.704 | 74.73% | 38.1918
3389 | 0 | 0 | 0 | 1.1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.8972 | 0 | 127.551 | 19.4017 | 1.521% | 10.5648 | 0 | 56.25 | 90% | 41.3324
3390 | 264 | 58 | 25 | 1.9 | 13.1 | 0 | 0 | 0 | 0 | 0.8253 | 0 | 0 | 0.8253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.4017 | 1.521% | 0 | 25 | 28.5817 | 45.73% | 25.8253
3391 | 640 | 243 | 53 | 0.6 | 16.7 | 0 | 0 | 0 | 93.4849 | 2.6767 | 0 | 0 | 2.6767 | 0 | 0 | 0 | 0 | 0 | 93.4849 | 0 | 112.8867 | 8.85% | 0 | 20.178 | 6.25 | 10% | 22.8547
3392 | 797 | 453 | 68 | 0.7 | 19.2 | 0 | 0 | 0 | 2.0249e-12 | 15.1617 | 0 | 0 | 15.1617 | 0 | 0 | 0 | 74.6213 | 28.5898 | 2.0249e-12 | 74.6213 | 38.2653 | 3% | 0 | 3.4817e-13 | 6.25 | 10% | 43.7515
3393 | 871 | 646 | 77 | 1.2 | 21.1 | 0 | 0 | 0 | 0 | 31.112 | 3.1264 | 0 | 31.112 | 0 | 0 | 0 | 38.2653 | 12.84 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 43.952
3394 | 914 | 811 | 83 | 1.7 | 22.5 | 0 | 0 | 0 | 0 | 44.4186 | 4.5962 | 0 | 44.4186 | 0 | 0 | 0 | 4.7156e-13 | 0 | 0 | 4.7156e-13 | 0 | 0% | 0 | 0 | 6.25 | 10% | 44.4186
3395 | 939 | 932 | 89 | 2.4 | 24.2 | 0 | 0 | 0 | 256.613 | 43.5272 | 16.4656 | 0 | 43.5272 | 0 | 0 | 0 | 0 | 0 | 256.613 | 0 | 256.613 | 20.12% | 0 | 0 | 6.25 | 10% | 43.5272
3396 | 942 | 1000 | 102 | 3.1 | 25.3 | 0 | 0 | 0 | 264.341 | 42.9061 | 24.2143 | 0 | 42.9061 | 0 | 0 | 0 | 0 | 0 | 264.341 | 0 | 520.954 | 40.84% | 0 | 0 | 6.25 | 10% | 42.9061
3397 | 921 | 1006 | 122 | 4.7 | 25.8 | 0 | 0 | 0 | 0 | 67.5635 | 2.751 | 25 | 42.5635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520.954 | 40.84% | 25 | 0 | 28.839 | 46.14% | 42.5635
3398 | 720 | 851 | 187 | 6.3 | 25.9 | 0 | 0 | 0 | 147.4831 | 44.113 | 17.6473 | 1.6372 | 42.4758 | 0 | 0 | 0 | 0 | 0 | 147.4831 | 0 | 668.4371 | 52.41% | 1.6372 | 0 | 30.3183 | 48.51% | 42.4758
3399 | 830 | 866 | 181 | 4.2 | 26.6 | 0 | 0 | 0 | 225.1063 | 62.3321 | 0 | 20.5401 | 41.792 | 0 | 0 | 0 | 0 | 0 | 225.1063 | 0 | 893.5434 | 70.05% | 20.5401 | 0 | 48.8775 | 78.2% | 41.792
3400 | 775 | 683 | 148 | 4.5 | 26.2 | 0 | 0 | 0 | 200.4037 | 49.7299 | 0 | 8.1594 | 41.5705 | 0 | 0 | 0 | 0 | 0 | 200.4037 | 0 | 1093.9471 | 85.77% | 8.1594 | 0 | 56.25 | 90% | 41.5705
3401 | 754 | 487 | 92 | 5.1 | 25.6 | 0 | 0 | 0 | 181.5631 | 34.5909 | 0 | 0 | 34.5909 | 0 | 0 | 0 | 0 | 0 | 181.5631 | 0 | 1275.5102 | 100% | 0 | 7.1198 | 48.3703 | 77.39% | 41.7107
3402 | 613 | 271 | 67 | 3.5 | 24.9 | 0 | 0 | 0 | 0 | 15.2065 | 0 | 0 | 15.2065 | 0 | 0 | 0 | 38.2653 | 12.7375 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 14.7407 | 32.0563 | 51.29% | 42.6847
3403 | 277 | 81 | 31 | 4.1 | 22.7 | 0 | 0 | 0 | 0 | 1.384 | 0 | 0 | 1.384 | 0 | 0 | 0 | 71.5569 | 27.0906 | 0 | 71.5569 | 1165.688 | 91.39% | 0 | 12.4943 | 18.2284 | 29.17% | 40.9689
3404 | 0 | 2 | 2 | 3.4 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2664 | 37.4398 | 0 | 95.2664 | 1070.4216 | 83.92% | 0 | 0 | 18.2284 | 29.17% | 37.4398
3405 | 0 | 0 | 0 | 3.4 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1225 | 35.3257 | 0 | 90.1225 | 980.2991 | 76.86% | 0 | 0 | 18.2284 | 29.17% | 35.3257
3406 | 0 | 0 | 0 | 2 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5032 | 33.3857 | 0 | 85.5032 | 894.7959 | 70.15% | 0 | 0 | 18.2284 | 29.17% | 33.3857
3407 | 0 | 0 | 0 | 1.8 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4809 | 32.1141 | 0 | 82.4809 | 812.315 | 63.69% | 0 | 0 | 18.2284 | 29.17% | 32.1141
3408 | 0 | 0 | 0 | 1 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2466 | 31.6128 | 0 | 81.2466 | 731.0683 | 57.32% | 0 | 0 | 18.2284 | 29.17% | 31.6128
3409 | 0 | 0 | 0 | 0.4 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.989 | 31.525 | 0 | 80.989 | 650.0794 | 50.97% | 0 | 0 | 18.2284 | 29.17% | 31.525
3410 | 0 | 0 | 0 | 0.6 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3078 | 32.1113 | 0 | 82.3078 | 567.7716 | 44.51% | 0 | 0 | 18.2284 | 29.17% | 32.1113
3411 | 0 | 0 | 0 | 1.5 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0053 | 34.5778 | 0 | 88.0053 | 479.7662 | 37.61% | 0 | 0 | 18.2284 | 29.17% | 34.5778
3412 | 0 | 0 | 0 | 1.6 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8086 | 37.9732 | 0 | 95.8086 | 383.9577 | 30.1% | 0 | 0 | 18.2284 | 29.17% | 37.9732
3413 | 0 | 0 | 0 | 1 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.3782 | 40.8644 | 0 | 102.3782 | 281.5794 | 22.08% | 0 | 0 | 18.2284 | 29.17% | 40.8644
3414 | 279 | 59 | 25 | 2.2 | 16 | 0 | 0 | 0 | 0 | 0.81166 | 0 | 0 | 0.81166 | 0 | 0 | 0 | 104.2089 | 41.5597 | 0 | 104.2089 | 177.3706 | 13.91% | 0 | 0 | 18.2284 | 29.17% | 42.3713
3415 | 645 | 246 | 54 | 1.3 | 18.2 | 0 | 0 | 0 | 0 | 2.7243 | 0 | 0 | 2.7243 | 0 | 0 | 0 | 102.071 | 40.5119 | 0 | 102.071 | 75.2996 | 5.903% | 0 | 0 | 18.2284 | 29.17% | 43.2362
3416 | 797 | 455 | 68 | 1 | 21.5 | 0 | 0 | 0 | 0 | 15.0246 | 0 | 0 | 15.0246 | 0 | 0 | 0 | 75.2996 | 28.7659 | 0 | 75.2996 | 0 | 0% | 0 | 0 | 18.2284 | 29.17% | 43.7905
3417 | 867 | 651 | 83 | 1 | 24.6 | 0 | 0 | 0 | 0 | 33.9046 | 0 | 0 | 33.9046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 10.8232 | 6.25 | 10% | 44.7277
3418 | 892 | 806 | 93 | 1.2 | 26.6 | 0 | 0 | 0 | 233.4155 | 44.9172 | 2.5428 | 0 | 44.9172 | 0 | 0 | 0 | 0 | 0 | 233.4155 | 0 | 233.4155 | 18.3% | 0 | 0 | 6.25 | 10% | 44.9172
3419 | 941 | 936 | 89 | 1.6 | 27.7 | 0 | 0 | 0 | 257.5819 | 43.6721 | 14.7215 | 0 | 43.6721 | 0 | 0 | 0 | 0 | 0 | 257.5819 | 0 | 490.9974 | 38.49% | 0 | 0 | 6.25 | 10% | 43.6721
3420 | 870 | 977 | 143 | 2.4 | 28.7 | 0 | 0 | 0 | 243.1115 | 42.9409 | 20.8428 | 0 | 42.9409 | 0 | 0 | 0 | 0 | 0 | 243.1115 | 0 | 734.1089 | 57.55% | 0 | 0 | 6.25 | 10% | 42.9409
3421 | 922 | 997 | 111 | 4.7 | 29.2 | 0 | 0 | 0 | 260.3504 | 67.654 | 1.1408 | 25 | 42.654 | 0 | 0 | 0 | 0 | 0 | 260.3504 | 0 | 994.4594 | 77.97% | 25 | 0 | 28.839 | 46.14% | 42.654
3422 | 931 | 951 | 98 | 5.3 | 29.4 | 0 | 0 | 0 | 0 | 54.204 | 13.1606 | 11.7157 | 42.4883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 994.4594 | 77.97% | 11.7157 | 0 | 39.4249 | 63.08% | 42.4883
3423 | 896 | 834 | 96 | 6.2 | 29.3 | 0 | 0 | 0 | 55.2798 | 60.4198 | 0 | 18.6209 | 41.7989 | 0 | 0 | 0 | 0 | 0 | 55.2798 | 0 | 1049.7391 | 82.3% | 18.6209 | 0 | 56.25 | 90% | 41.7989
3424 | 870 | 685 | 85 | 6.2 | 29 | 0 | 0 | 0 | 225.7711 | 41.6193 | 8.2335 | 0 | 41.6193 | 0 | 0 | 0 | 0 | 0 | 225.7711 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 41.6193
3425 | 779 | 491 | 81 | 6 | 28.3 | 0 | 0 | 0 | 0 | 29.3069 | 5.1724 | 0 | 29.3069 | 0 | 0 | 0 | 38.2653 | 12.6257 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 41.9326
3426 | 626 | 282 | 69 | 5.5 | 27 | 0 | 0 | 0 | 0 | 15.5177 | 0 | 0 | 15.5177 | 0 | 0 | 0 | 72.3598 | 27.1586 | 0 | 72.3598 | 1164.8851 | 91.33% | 0 | 0 | 56.25 | 90% | 42.6763
3427 | 304 | 94 | 41 | 4.6 | 25.5 | 0 | 0 | 0 | 37.2071 | 1.946 | 0 | 0 | 1.946 | 0 | 0 | 0 | 0 | 0 | 37.2071 | 0 | 1202.0923 | 94.24% | 0 | 25 | 28.5817 | 45.73% | 26.946
3428 | 0 | 1 | 1 | 3.7 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202.0923 | 94.24% | 0 | 20.178 | 6.25 | 10% | 20.178
3429 | 0 | 0 | 0 | 3.2 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5459 | 35.6488 | 0 | 91.5459 | 1110.5464 | 87.07% | 0 | 0 | 6.25 | 10% | 35.6488
3430 | 0 | 0 | 0 | 2.2 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.393 | 33.9093 | 0 | 87.393 | 1023.1534 | 80.22% | 0 | 0 | 6.25 | 10% | 33.9093
3431 | 0 | 0 | 0 | 2.1 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1746 | 32.6392 | 0 | 84.1746 | 938.9788 | 73.62% | 0 | 0 | 6.25 | 10% | 32.6392
3432 | 0 | 0 | 0 | 1.1 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.7015 | 26.9299 | 0 | 70.7015 | 868.2773 | 68.07% | 0 | 0 | 6.25 | 10% | 26.9299
3433 | 0 | 0 | 0 | 0.1 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3118 | 31.9985 | 0 | 82.3118 | 785.9655 | 61.62% | 0 | 0 | 6.25 | 10% | 31.9985
3434 | 0 | 0 | 0 | 0.8 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4965 | 32.5027 | 0 | 83.4965 | 702.469 | 55.07% | 0 | 0 | 6.25 | 10% | 32.5027
3435 | 0 | 0 | 0 | 1.6 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9471 | 34.919 | 0 | 88.9471 | 613.5219 | 48.1% | 0 | 0 | 6.25 | 10% | 34.919
3436 | 0 | 0 | 0 | 0.5 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6877 | 38.3046 | 0 | 96.6877 | 516.8342 | 40.52% | 0 | 0 | 6.25 | 10% | 38.3046
3437 | 0 | 0 | 0 | 0.7 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2824 | 41.2001 | 0 | 103.2824 | 413.5518 | 32.42% | 0 | 0 | 6.25 | 10% | 41.2001
3438 | 93 | 65 | 50 | 0.8 | 16.9 | 0 | 0 | 0 | 0 | 2.0135 | 0 | 0 | 2.0135 | 0 | 0 | 0 | 102.7082 | 40.862 | 0 | 102.7082 | 310.8436 | 24.37% | 0 | 0 | 6.25 | 10% | 42.8755
3439 | 145 | 182 | 137 | 0.6 | 20.2 | 0 | 0 | 0 | 0 | 6.3385 | 0 | 0 | 6.3385 | 0 | 0 | 0 | 94.5949 | 37.1567 | 0 | 94.5949 | 216.2487 | 16.95% | 0 | 0 | 6.25 | 10% | 43.4952
3440 | 61 | 250 | 219 | 0.4 | 22 | 0 | 0 | 0 | 0 | 13.7089 | 0 | 0 | 13.7089 | 0 | 0 | 0 | 78.8627 | 30.2696 | 0 | 78.8627 | 137.386 | 10.77% | 0 | 0 | 6.25 | 10% | 43.9785
3441 | 33 | 299 | 273 | 1.1 | 23.8 | 0 | 0 | 0 | 0 | 17.9024 | 0 | 0 | 17.9024 | 0 | 0 | 0 | 70.9564 | 26.7696 | 0 | 70.9564 | 66.4296 | 5.208% | 0 | 0 | 6.25 | 10% | 44.672
3442 | 15 | 325 | 309 | 1.8 | 24.8 | 0 | 0 | 0 | 0 | 19.9367 | 0 | 0 | 19.9367 | 0 | 0 | 0 | 66.4296 | 24.7744 | 0 | 66.4296 | 0 | 0% | 0 | 0 | 6.25 | 10% | 44.711
3443 | 190 | 611 | 426 | 2.1 | 26.2 | 0 | 0 | 0 | 37.8211 | 38.835 | 0 | 0 | 38.835 | 0 | 0 | 0 | 0 | 0 | 37.8211 | 0 | 37.8211 | 2.965% | 0 | 0 | 6.25 | 10% | 38.835
3444 | 298 | 751 | 452 | 2.3 | 27.6 | 0 | 0 | 0 | 71.39 | 49.2002 | 0 | 7.191 | 42.0092 | 0 | 0 | 0 | 0 | 0 | 71.39 | 0 | 109.2111 | 8.562% | 7.191 | 0 | 12.7475 | 20.4% | 42.0092
3445 | 208 | 727 | 513 | 2.1 | 28.3 | 0 | 0 | 0 | 44.9661 | 47.3211 | 0 | 5.8453 | 41.4758 | 0 | 0 | 0 | 0 | 0 | 44.9661 | 0 | 154.1772 | 12.09% | 5.8453 | 0 | 18.0291 | 28.85% | 41.4758
3446 | 52 | 492 | 438 | 7.7 | 25.9 | 0 | 0 | 0 | 0 | 32.6436 | 0 | 0 | 32.6436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.1772 | 12.09% | 0 | 0 | 18.0291 | 28.85% | 32.6436
3447 | 107 | 467 | 374 | 8.2 | 23.4 | 0 | 0 | 0 | 0 | 32.1623 | 0 | 0 | 32.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.1772 | 12.09% | 0 | 0 | 18.0291 | 28.85% | 32.1623
3448 | 463 | 597 | 281 | 7.6 | 23.3 | 0 | 0 | 0 | 109.2182 | 43.7107 | 0 | 3.3602 | 40.3505 | 0 | 0 | 0 | 0 | 0 | 109.2182 | 0 | 263.3954 | 20.65% | 3.3602 | 0 | 21.0653 | 33.7% | 40.3505
3449 | 235 | 338 | 206 | 7.6 | 21.4 | 0 | 0 | 0 | 40.1309 | 22.694 | 0 | 0 | 22.694 | 0 | 0 | 0 | 0 | 0 | 40.1309 | 0 | 303.5263 | 23.8% | 0 | 13.3865 | 6.25 | 10% | 36.0804
3450 | 2 | 69 | 68 | 6.8 | 19.1 | 0 | 0 | 0 | 0 | 4.011 | 0 | 0 | 4.011 | 0 | 0 | 0 | 93.6927 | 36.8353 | 0 | 93.6927 | 209.8336 | 16.45% | 0 | 0 | 6.25 | 10% | 40.8463
3451 | 10 | 46 | 44 | 7.2 | 18.2 | 0 | 0 | 0 | 0 | 2.437 | 0 | 0 | 2.437 | 0 | 0 | 0 | 93.6105 | 36.8509 | 0 | 93.6105 | 116.2231 | 9.112% | 0 | 0 | 6.25 | 10% | 39.2879
3452 | 0 | 2 | 2 | 6.4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2231 | 46.6826 | 0 | 116.2231 | 0 | 0% | 10.1537 | 0 | 15.4245 | 24.68% | 36.529
3453 | 0 | 0 | 0 | 5.7 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0
3454 | 0 | 0 | 0 | 4.4 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0
3455 | 0 | 0 | 0 | 3.2 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0
3456 | 0 | 0 | 0 | 3 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0
3457 | 0 | 0 | 0 | 3.1 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0
3458 | 0 | 0 | 0 | 2.2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0
3459 | 0 | 0 | 0 | 2 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0
3460 | 0 | 0 | 0 | 1.5 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0
3461 | 0 | 0 | 0 | 1.2 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0
3462 | 325 | 62 | 23 | 0.4 | 13.4 | 0 | 0 | 0 | 0 | 0.72615 | 0 | 0 | 0.72615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.4245 | 24.68% | 0.72615
3463 | 625 | 245 | 60 | 0.6 | 17.1 | 0 | 0 | 0 | 91.7178 | 3.116 | 0 | 0 | 3.116 | 0 | 0 | 0 | 0 | 0 | 91.7178 | 0 | 91.7178 | 7.191% | 0 | 0 | 15.4245 | 24.68% | 3.116
3464 | 770 | 479 | 103 | 1.2 | 19.2 | 0 | 0 | 0 | 158.3956 | 16.8449 | 0 | 0 | 16.8449 | 0 | 0 | 0 | 0 | 0 | 158.3956 | 0 | 250.1134 | 19.61% | 0 | 3.9048 | 11.1029 | 17.76% | 20.7497
3465 | 888 | 658 | 75 | 1.7 | 20.6 | 0 | 0 | 0 | 215.8839 | 34.7094 | 0 | 0 | 34.7094 | 0 | 0 | 0 | 0 | 0 | 215.8839 | 0 | 465.9973 | 36.53% | 0 | 4.3849 | 6.25 | 10% | 39.0943
3466 | 937 | 840 | 91 | 2.6 | 22.1 | 0 | 0 | 0 | 245.3951 | 51.0094 | 0 | 11.7396 | 39.2698 | 0 | 0 | 0 | 0 | 0 | 245.3951 | 0 | 711.3924 | 55.77% | 11.7396 | 0 | 16.8574 | 26.97% | 39.2698
3467 | 126 | 365 | 250 | 2.3 | 22 | 0 | 0 | 0 | 0 | 24.2007 | 0 | 0 | 24.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711.3924 | 55.77% | 0 | 9.5844 | 6.25 | 10% | 33.7851
3468 | 9 | 291 | 278 | 4.2 | 21.8 | 0 | 0 | 0 | 0 | 18.1802 | 0 | 0 | 18.1802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711.3924 | 55.77% | 0 | 0 | 6.25 | 10% | 18.1802
3469 | 27 | 312 | 280 | 3.7 | 21.6 | 0 | 0 | 0 | 0 | 20.2681 | 0 | 0 | 20.2681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711.3924 | 55.77% | 0 | 0 | 6.25 | 10% | 20.2681
3470 | 52 | 322 | 268 | 1.7 | 21.5 | 0 | 0 | 0 | 0 | 20.8831 | 0 | 0 | 20.8831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711.3924 | 55.77% | 0 | 0 | 6.25 | 10% | 20.8831
3471 | 31 | 266 | 237 | 2.1 | 21.7 | 0 | 0 | 0 | 0 | 17.137 | 0 | 0 | 17.137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711.3924 | 55.77% | 0 | 0 | 6.25 | 10% | 17.137
3472 | 14 | 184 | 172 | 3.2 | 20.9 | 0 | 0 | 0 | 0 | 11.3369 | 0 | 0 | 11.3369 | 0 | 0 | 0 | 63.2104 | 23.5905 | 0 | 63.2104 | 648.182 | 50.82% | 0 | 0 | 6.25 | 10% | 34.9274
3473 | 83 | 177 | 127 | 2.9 | 20.6 | 0 | 0 | 0 | 0 | 11.2352 | 0 | 0 | 11.2352 | 0 | 0 | 0 | 64.6412 | 24.22 | 0 | 64.6412 | 583.5408 | 45.75% | 0 | 0 | 6.25 | 10% | 35.4552
3474 | 100 | 144 | 105 | 4.1 | 19.1 | 0 | 0 | 0 | 0 | 8.3027 | 0 | 0 | 8.3027 | 0 | 0 | 0 | 74.5526 | 28.5647 | 0 | 74.5526 | 508.9882 | 39.9% | 0 | 0 | 6.25 | 10% | 36.8674
3475 | 122 | 59 | 39 | 3 | 18.7 | 0 | 0 | 0 | 0 | 1.9836 | 0 | 0 | 1.9836 | 0 | 0 | 0 | 88.2529 | 34.5064 | 0 | 88.2529 | 420.7354 | 32.99% | 0 | 0 | 6.25 | 10% | 36.49
3476 | 0 | 2 | 2 | 2.3 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4152 | 34.6614 | 0 | 88.4152 | 332.3202 | 26.05% | 0 | 0 | 6.25 | 10% | 34.6614
3477 | 0 | 0 | 0 | 2.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3591 | 32.511 | 0 | 83.3591 | 248.9611 | 19.52% | 0 | 0 | 6.25 | 10% | 32.511
3478 | 0 | 0 | 0 | 1.5 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9894 | 30.6462 | 0 | 78.9894 | 169.9716 | 13.33% | 0 | 0 | 6.25 | 10% | 30.6462
3479 | 0 | 0 | 0 | 0.6 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9716 | 13.33% | 0 | 0 | 6.25 | 10% | 0
3480 | 0 | 0 | 0 | 1.1 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9716 | 13.33% | 0 | 0 | 6.25 | 10% | 0
3481 | 0 | 0 | 0 | 1.2 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9716 | 13.33% | 0 | 0 | 6.25 | 10% | 0
3482 | 0 | 0 | 0 | 1.6 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9716 | 13.33% | 0 | 0 | 6.25 | 10% | 0
3483 | 0 | 0 | 0 | 0.8 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.9716 | 13.33% | 0 | 0 | 6.25 | 10% | 0
3484 | 0 | 0 | 0 | 0.6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.2107 | 27.326 | 0 | 71.2107 | 98.7609 | 7.743% | 0 | 0 | 6.25 | 10% | 27.326
3485 | 0 | 1 | 1 | 0.9 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7609 | 39.336 | 0 | 98.7609 | 0 | 0% | 10.3708 | 0 | 15.6206 | 24.99% | 28.9652
3486 | 318 | 62 | 24 | 0.8 | 13.7 | 0 | 0 | 0 | 0 | 0.77337 | 0 | 0 | 0.77337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 15.6206 | 24.99% | 0.77337
3487 | 664 | 250 | 49 | 0.8 | 17.9 | 0 | 0 | 0 | 91.3341 | 2.6675 | 0 | 0 | 2.6675 | 0 | 0 | 0 | 0 | 0 | 91.3341 | 0 | 91.3341 | 7.161% | 0 | 8.4669 | 6.25 | 10% | 11.1344
3488 | 799 | 455 | 64 | 0.8 | 20.6 | 0 | 0 | 0 | 0 | 14.6478 | 0 | 0 | 14.6478 | 0 | 0 | 0 | 53.0688 | 19.2323 | 0 | 53.0688 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 33.8801
3489 | 869 | 649 | 75 | 1 | 22.2 | 0 | 0 | 0 | 0 | 21.3333 | 12.1957 | 0 | 21.3333 | 0 | 0 | 0 | 38.2653 | 12.8128 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 34.1461
3490 | 883 | 822 | 114 | 1.4 | 23.2 | 0 | 0 | 0 | 230.6408 | 38.3702 | 10.5409 | 3.8662 | 34.504 | 0 | 0 | 0 | 0 | 0 | 230.6408 | 0 | 230.6408 | 18.08% | 3.8662 | 0 | 9.7433 | 15.59% | 34.504
3491 | 161 | 475 | 325 | 2.6 | 23 | 0 | 0 | 0 | 0 | 31.1734 | 0 | 0 | 31.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230.6408 | 18.08% | 0 | 3.1564 | 6.25 | 10% | 34.3299
3492 | 458 | 751 | 302 | 4.6 | 23.7 | 0 | 0 | 0 | 117.8791 | 32.8495 | 19.0942 | 0 | 32.8495 | 0 | 0 | 0 | 0 | 0 | 117.8791 | 0 | 348.5199 | 27.32% | 0 | 0 | 6.25 | 10% | 32.8495
3493 | 763 | 988 | 249 | 6.4 | 24.1 | 0 | 0 | 0 | 210.366 | 31.8829 | 38.4722 | 0 | 31.8829 | 0 | 0 | 0 | 0 | 0 | 210.366 | 0 | 558.8859 | 43.82% | 0 | 0 | 6.25 | 10% | 31.8829
3494 | 902 | 950 | 119 | 6.5 | 24.4 | 0 | 0 | 0 | 250.4185 | 43.9627 | 24.3871 | 12.4113 | 31.5515 | 0 | 0 | 0 | 0 | 0 | 250.4185 | 0 | 809.3044 | 63.45% | 12.4113 | 0 | 17.4643 | 27.94% | 31.5515
3495 | 870 | 830 | 109 | 6.9 | 24.3 | 0 | 0 | 0 | 234.428 | 57.0347 | 3.7978 | 25 | 32.0347 | 0 | 0 | 0 | 0 | 0 | 234.428 | 0 | 1043.7324 | 81.83% | 25 | 0 | 40.0533 | 64.09% | 32.0347
3496 | 849 | 680 | 89 | 6.9 | 23.8 | 0 | 0 | 0 | 0 | 49.986 | 0 | 17.248 | 32.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1043.7324 | 81.83% | 17.248 | 0 | 55.6379 | 89.02% | 32.738
3497 | 786 | 492 | 74 | 6.5 | 23.3 | 0 | 0 | 0 | 122.3245 | 34.8221 | 0 | 0.67745 | 34.1447 | 0 | 0 | 0 | 0 | 0 | 122.3245 | 0 | 1166.0569 | 91.42% | 0.67745 | 0 | 56.25 | 90% | 34.1447
3498 | 661 | 287 | 58 | 5.1 | 22.8 | 0 | 0 | 0 | 0 | 15.5904 | 0 | 0 | 15.5904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.0569 | 91.42% | 0 | 20.4024 | 33.67 | 53.87% | 35.9928
3499 | 414 | 99 | 31 | 4.3 | 21.5 | 0 | 0 | 0 | 0 | 1.6172 | 0 | 0 | 1.6172 | 0 | 0 | 0 | 56.0073 | 20.4646 | 0 | 56.0073 | 1110.0496 | 87.03% | 0 | 14.7188 | 17.3802 | 27.81% | 36.8005
3500 | 1 | 3 | 3 | 3.2 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6854 | 34.6433 | 0 | 88.6854 | 1021.3642 | 80.07% | 0 | 0 | 17.3802 | 27.81% | 34.6433
3501 | 0 | 0 | 0 | 2.3 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3524 | 32.4024 | 0 | 83.3524 | 938.0118 | 73.54% | 0 | 0 | 17.3802 | 27.81% | 32.4024
3502 | 0 | 0 | 0 | 1.6 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8019 | 30.4986 | 0 | 78.8019 | 859.21 | 67.36% | 0 | 0 | 17.3802 | 27.81% | 30.4986
3503 | 0 | 0 | 0 | 0.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1645 | 29.3886 | 0 | 76.1645 | 783.0455 | 61.39% | 0 | 0 | 17.3802 | 27.81% | 29.3886
3504 | 0 | 0 | 0 | 0.8 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.0688 | 28.943 | 0 | 75.0688 | 707.9767 | 55.51% | 0 | 0 | 17.3802 | 27.81% | 28.943
3505 | 0 | 0 | 0 | 1 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.0263 | 28.9485 | 0 | 75.0263 | 632.9503 | 49.62% | 0 | 0 | 17.3802 | 27.81% | 28.9485
3506 | 0 | 0 | 0 | 1 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7752 | 29.7089 | 0 | 76.7752 | 556.1751 | 43.6% | 0 | 0 | 17.3802 | 27.81% | 29.7089
3507 | 0 | 0 | 0 | 0.7 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7594 | 32.7673 | 0 | 83.7594 | 472.4157 | 37.04% | 0 | 0 | 17.3802 | 27.81% | 32.7673
3508 | 0 | 0 | 0 | 0.8 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4685 | 36.5499 | 0 | 92.4685 | 379.9472 | 29.79% | 0 | 0 | 17.3802 | 27.81% | 36.5499
3509 | 0 | 1 | 1 | 2.1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5279 | 40.1026 | 0 | 100.5279 | 279.4194 | 21.91% | 0 | 0 | 17.3802 | 27.81% | 40.1026
3510 | 359 | 65 | 22 | 2.5 | 14.5 | 0 | 0 | 0 | 0 | 0.67466 | 0 | 0 | 0.67466 | 0 | 0 | 0 | 103.3654 | 41.2621 | 0 | 103.3654 | 176.0539 | 13.8% | 0 | 0 | 17.3802 | 27.81% | 41.9368
3511 | 706 | 258 | 43 | 1.6 | 17.3 | 0 | 0 | 0 | 0 | 2.2721 | 0 | 0 | 2.2721 | 0 | 0 | 0 | 101.8244 | 40.4571 | 0 | 101.8244 | 74.2295 | 5.82% | 0 | 0 | 17.3802 | 27.81% | 42.7292
3512 | 850 | 467 | 52 | 1.6 | 20.3 | 0 | 0 | 0 | 0 | 14.7402 | 0 | 0 | 14.7402 | 0 | 0 | 0 | 74.2295 | 28.3678 | 0 | 74.2295 | 0 | 0% | 0 | 0 | 17.3802 | 27.81% | 43.108
3513 | 911 | 660 | 61 | 1.3 | 22.9 | 0 | 0 | 0 | 0 | 33.898 | 0 | 0 | 33.898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 10.0568 | 6.25 | 10% | 43.9548
3514 | 937 | 821 | 72 | 1.9 | 24.4 | 0 | 0 | 0 | 141.878 | 44.2473 | 4.5167 | 0 | 44.2473 | 0 | 0 | 0 | 0 | 0 | 141.878 | 0 | 141.878 | 11.12% | 0 | 0 | 6.25 | 10% | 44.2473
3515 | 829 | 907 | 155 | 2.1 | 26.6 | 0 | 0 | 0 | 0 | 43.2209 | 14.2418 | 0 | 43.2209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.878 | 11.12% | 0 | 0 | 6.25 | 10% | 43.2209
3516 | 932 | 999 | 104 | 3.6 | 27.8 | 0 | 0 | 0 | 0 | 44.0298 | 22.0389 | 1.7142 | 42.3156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.878 | 11.12% | 1.7142 | 0 | 7.7989 | 12.48% | 42.3156
3517 | 911 | 993 | 113 | 5.7 | 28.3 | 0 | 0 | 0 | 256.1343 | 67.2641 | 1.3898 | 25 | 42.2641 | 0 | 0 | 0 | 0 | 0 | 256.1343 | 0 | 398.0123 | 31.2% | 25 | 0 | 30.3879 | 48.62% | 42.2641
3518 | 729 | 843 | 169 | 5.9 | 28 | 0 | 0 | 0 | 198.8984 | 42.1164 | 18.1557 | 0 | 42.1164 | 0 | 0 | 0 | 0 | 0 | 198.8984 | 0 | 596.9106 | 46.8% | 0 | 0 | 30.3879 | 48.62% | 42.1164
3519 | 927 | 847 | 78 | 6.2 | 28.9 | 0 | 0 | 0 | 252.0248 | 60.8494 | 0 | 19.1773 | 41.6722 | 0 | 0 | 0 | 0 | 0 | 252.0248 | 0 | 848.9354 | 66.56% | 19.1773 | 0 | 47.7157 | 76.35% | 41.6722
3520 | 895 | 712 | 87 | 5.8 | 28.5 | 0 | 0 | 0 | 233.2339 | 51.0283 | 0 | 9.4452 | 41.583 | 0 | 0 | 0 | 0 | 0 | 233.2339 | 0 | 1082.1694 | 84.84% | 9.4452 | 0 | 56.25 | 90% | 41.583
3521 | 784 | 504 | 85 | 4.7 | 28.1 | 0 | 0 | 0 | 190.2574 | 34.699 | 0 | 0 | 34.699 | 0 | 0 | 0 | 0 | 0 | 190.2574 | 0 | 1272.4268 | 99.76% | 0 | 7.2058 | 48.2751 | 77.24% | 41.9048
3522 | 543 | 315 | 119 | 4.6 | 26.5 | 0 | 0 | 0 | 0 | 17.1919 | 0 | 0 | 17.1919 | 0 | 0 | 0 | 68.1255 | 25.3924 | 0 | 68.1255 | 1204.3013 | 94.42% | 0 | 0 | 48.2751 | 77.24% | 42.5844
3523 | 247 | 100 | 60 | 3.8 | 24.4 | 0 | 0 | 0 | 0 | 3.0194 | 0 | 0 | 3.0194 | 0 | 0 | 0 | 38.2653 | 12.7523 | 0 | 38.2653 | 1166.036 | 91.42% | 0 | 24.9256 | 20.6891 | 33.1% | 40.6973
3524 | 2 | 6 | 6 | 2.8 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0198 | 35.1521 | 0 | 90.0198 | 1076.0162 | 84.36% | 0 | 1.991 | 18.4856 | 29.58% | 37.1431
3525 | 0 | 0 | 0 | 1.6 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2119 | 35.348 | 0 | 90.2119 | 985.8043 | 77.29% | 0 | 0 | 18.4856 | 29.58% | 35.348
3526 | 0 | 0 | 0 | 0.6 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5636 | 33.3689 | 0 | 85.5636 | 900.2407 | 70.58% | 0 | 0 | 18.4856 | 29.58% | 33.3689
3527 | 0 | 0 | 0 | 0.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0054 | 32.2715 | 0 | 83.0054 | 817.2353 | 64.07% | 0 | 0 | 18.4856 | 29.58% | 32.2715
3528 | 0 | 0 | 0 | 0.5 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8574 | 31.8147 | 0 | 81.8574 | 735.3779 | 57.65% | 0 | 0 | 18.4856 | 29.58% | 31.8147
3529 | 0 | 0 | 0 | 0.7 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7838 | 31.7785 | 0 | 81.7838 | 653.5941 | 51.24% | 0 | 0 | 18.4856 | 29.58% | 31.7785
3530 | 0 | 0 | 0 | 1 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9629 | 32.3272 | 0 | 82.9629 | 570.6313 | 44.74% | 0 | 0 | 18.4856 | 29.58% | 32.3272
3531 | 0 | 0 | 0 | 0.9 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3243 | 34.6265 | 0 | 88.3243 | 482.307 | 37.81% | 0 | 0 | 18.4856 | 29.58% | 34.6265
3532 | 0 | 0 | 0 | 1.1 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2591 | 38.086 | 0 | 96.2591 | 386.0479 | 30.27% | 0 | 0 | 18.4856 | 29.58% | 38.086
3533 | 0 | 1 | 1 | 4.8 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2302 | 41.1095 | 0 | 103.2302 | 282.8176 | 22.17% | 0 | 0 | 18.4856 | 29.58% | 41.1095
3534 | 243 | 59 | 28 | 5.3 | 16.8 | 0 | 0 | 0 | 0 | 0.95274 | 0 | 0 | 0.95274 | 0 | 0 | 0 | 104.6221 | 41.6971 | 0 | 104.6221 | 178.1956 | 13.97% | 0 | 0 | 18.4856 | 29.58% | 42.6499
3535 | 598 | 243 | 59 | 5.2 | 18.2 | 0 | 0 | 0 | 0 | 3.0295 | 0 | 0 | 3.0295 | 0 | 0 | 0 | 102.061 | 40.5075 | 0 | 102.061 | 76.1346 | 5.969% | 0 | 0 | 18.4856 | 29.58% | 43.537
3536 | 767 | 450 | 73 | 4.6 | 20.4 | 0 | 0 | 0 | 0 | 14.9739 | 0 | 0 | 14.9739 | 0 | 0 | 0 | 76.1346 | 29.1842 | 0 | 76.1346 | 0 | 0% | 0 | 0 | 18.4856 | 29.58% | 44.1581
3537 | 856 | 645 | 78 | 4.1 | 23.5 | 0 | 0 | 0 | 206.1461 | 33.9005 | 0 | 0 | 33.9005 | 0 | 0 | 0 | 0 | 0 | 206.1461 | 0 | 206.1461 | 16.16% | 0 | 11.0556 | 6.25 | 10% | 44.9562
3538 | 907 | 812 | 83 | 3.9 | 25.7 | 0 | 0 | 0 | 186.1922 | 48.8706 | 0 | 3.8281 | 45.0425 | 0 | 0 | 0 | 0 | 0 | 186.1922 | 0 | 392.3383 | 30.76% | 3.8281 | 0 | 9.7089 | 15.53% | 45.0425
3539 | 882 | 932 | 130 | 3.6 | 27.4 | 0 | 0 | 0 | 239.0356 | 59.2062 | 0 | 15.1873 | 44.0189 | 0 | 0 | 0 | 0 | 0 | 239.0356 | 0 | 631.3739 | 49.5% | 15.1873 | 0 | 23.4316 | 37.49% | 44.0189
3540 | 763 | 962 | 225 | 4 | 28.6 | 0 | 0 | 0 | 209.744 | 64.4457 | 0 | 21.4936 | 42.9521 | 0 | 0 | 0 | 0 | 0 | 209.744 | 0 | 841.1179 | 65.94% | 21.4936 | 0 | 42.8524 | 68.56% | 42.9521
3541 | 767 | 924 | 179 | 5.6 | 28.4 | 0 | 0 | 0 | 212.3751 | 57.4774 | 6.7746 | 14.8276 | 42.6499 | 0 | 0 | 0 | 0 | 0 | 212.3751 | 0 | 1053.493 | 82.59% | 14.8276 | 0 | 56.25 | 90% | 42.6499
3542 | 806 | 904 | 158 | 5.8 | 28.4 | 0 | 0 | 0 | 222.0172 | 42.5482 | 21.6169 | 0 | 42.5482 | 0 | 0 | 0 | 0 | 0 | 222.0172 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 42.5482
3543 | 492 | 671 | 250 | 5.9 | 28 | 0 | 0 | 0 | 0 | 29.5066 | 17.9481 | 0 | 29.5066 | 0 | 0 | 0 | 38.2653 | 12.6363 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 42.1429
3544 | 327 | 439 | 205 | 5.3 | 26.9 | 0 | 0 | 0 | 0 | 29.0706 | 1.8901 | 0 | 29.0706 | 0 | 0 | 0 | 38.2653 | 12.674 | 0 | 38.2653 | 1198.9796 | 94% | 0 | 0 | 56.25 | 90% | 41.7446
3545 | 225 | 279 | 162 | 5.1 | 26.1 | 0 | 0 | 0 | 4.622 | 18.8741 | 0 | 0 | 18.8741 | 0 | 0 | 0 | 0 | 0 | 4.622 | 0 | 1203.6016 | 94.36% | 0 | 12.4879 | 42.4293 | 67.89% | 31.3619
3546 | 382 | 247 | 107 | 4.3 | 26.1 | 0 | 0 | 0 | 71.9087 | 13.3662 | 0 | 0 | 13.3662 | 0 | 0 | 0 | 0 | 0 | 71.9087 | 0 | 1275.5102 | 100% | 0 | 25 | 14.7609 | 23.62% | 38.3662
3547 | 308 | 111 | 59 | 4 | 24.9 | 0 | 0 | 0 | 0 | 3.0024 | 0 | 0 | 3.0024 | 0 | 0 | 0 | 96.931 | 37.798 | 0 | 96.931 | 1178.5792 | 92.4% | 0 | 0 | 14.7609 | 23.62% | 40.8004
3548 | 2 | 6 | 5 | 3.9 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5977 | 37.4259 | 0 | 95.5977 | 1082.9815 | 84.91% | 0 | 0 | 14.7609 | 23.62% | 37.4259
3549 | 0 | 0 | 0 | 4.7 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3396 | 35.3396 | 0 | 90.3396 | 992.6419 | 77.82% | 0 | 0 | 14.7609 | 23.62% | 35.3396
3550 | 0 | 0 | 0 | 5.6 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1669 | 33.6349 | 0 | 86.1669 | 906.475 | 71.07% | 0 | 0 | 14.7609 | 23.62% | 33.6349
3551 | 0 | 0 | 0 | 4.8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3481 | 32.4651 | 0 | 83.3481 | 823.1269 | 64.53% | 0 | 0 | 14.7609 | 23.62% | 32.4651
3552 | 0 | 0 | 0 | 4.1 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2334 | 31.9776 | 0 | 82.2334 | 740.8935 | 58.09% | 0 | 0 | 14.7609 | 23.62% | 31.9776
3553 | 0 | 0 | 0 | 3.6 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8641 | 31.8133 | 0 | 81.8641 | 659.0295 | 51.67% | 0 | 0 | 14.7609 | 23.62% | 31.8133
3554 | 0 | 0 | 0 | 4.7 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0056 | 32.3035 | 0 | 83.0056 | 576.0239 | 45.16% | 0 | 0 | 14.7609 | 23.62% | 32.3035
3555 | 0 | 0 | 0 | 4.6 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5354 | 34.7226 | 0 | 88.5354 | 487.4885 | 38.22% | 0 | 0 | 14.7609 | 23.62% | 34.7226
3556 | 0 | 0 | 0 | 5.2 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7591 | 38.3172 | 0 | 96.7591 | 390.7294 | 30.63% | 0 | 0 | 14.7609 | 23.62% | 38.3172
3557 | 0 | 1 | 1 | 4 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.9347 | 44.0654 | 0 | 109.9347 | 280.7946 | 22.01% | 2.7456 | 0 | 17.2417 | 27.59% | 41.3198
3558 | 292 | 66 | 29 | 3 | 16.1 | 0 | 0 | 0 | 0 | 1.0038 | 0 | 0 | 1.0038 | 0 | 0 | 0 | 104.4548 | 41.6614 | 0 | 104.4548 | 176.3398 | 13.83% | 0 | 0 | 17.2417 | 27.59% | 42.6652
3559 | 650 | 254 | 55 | 4.8 | 18.8 | 0 | 0 | 0 | 0 | 2.7697 | 0 | 0 | 2.7697 | 0 | 0 | 0 | 102.3062 | 40.5765 | 0 | 102.3062 | 74.0336 | 5.804% | 0 | 0 | 17.2417 | 27.59% | 43.3462
3560 | 767 | 458 | 82 | 6.3 | 19.8 | 0 | 0 | 0 | 0 | 15.6192 | 0 | 0 | 15.6192 | 0 | 0 | 0 | 74.0336 | 28.3078 | 0 | 74.0336 | 0 | 0% | 0 | 0 | 17.2417 | 27.59% | 43.927
3561 | 859 | 649 | 81 | 6 | 20.8 | 0 | 0 | 0 | 0 | 34.6846 | 0 | 0 | 34.6846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 9.9317 | 6.25 | 10% | 44.6163
3562 | 899 | 810 | 88 | 6.2 | 21.5 | 0 | 0 | 0 | 102.2423 | 44.8865 | 5.1955 | 0 | 44.8865 | 0 | 0 | 0 | 0 | 0 | 102.2423 | 0 | 102.2423 | 8.016% | 0 | 0 | 6.25 | 10% | 44.8865
3563 | 924 | 930 | 92 | 5.5 | 21.9 | 0 | 0 | 0 | 0 | 43.6164 | 17.4339 | 0 | 43.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2423 | 8.016% | 0 | 0 | 6.25 | 10% | 43.6164
3564 | 931 | 992 | 96 | 6 | 22.8 | 0 | 0 | 0 | 0 | 42.771 | 25.0554 | 0 | 42.771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2423 | 8.016% | 0 | 0 | 6.25 | 10% | 42.771
3565 | 926 | 997 | 99 | 6.4 | 23.2 | 0 | 0 | 0 | 259.9123 | 45.5745 | 24.5223 | 2.9943 | 42.5802 | 0 | 0 | 0 | 0 | 0 | 259.9123 | 0 | 362.1546 | 28.39% | 2.9943 | 0 | 8.9555 | 14.33% | 42.5802
3566 | 916 | 946 | 99 | 6.3 | 23.8 | 0 | 0 | 0 | 254.7478 | 67.5356 | 0.2915 | 25 | 42.5356 | 0 | 0 | 0 | 0 | 0 | 254.7478 | 0 | 616.9024 | 48.37% | 25 | 0 | 31.5445 | 50.47% | 42.5356
3567 | 884 | 838 | 101 | 6.5 | 23.6 | 0 | 0 | 0 | 238.8926 | 61.004 | 0 | 19.1355 | 41.8685 | 0 | 0 | 0 | 0 | 0 | 238.8926 | 0 | 855.795 | 67.09% | 19.1355 | 0 | 48.8346 | 78.14% | 41.8685
3568 | 837 | 683 | 96 | 6.7 | 22.9 | 0 | 0 | 0 | 215.7986 | 49.8777 | 0 | 8.2069 | 41.6708 | 0 | 0 | 0 | 0 | 0 | 215.7986 | 0 | 1071.5936 | 84.01% | 8.2069 | 0 | 56.25 | 90% | 41.6708
3569 | 768 | 498 | 85 | 6.7 | 22 | 0 | 0 | 0 | 184.1643 | 35.0389 | 0 | 0 | 35.0389 | 0 | 0 | 0 | 0 | 0 | 184.1643 | 0 | 1255.758 | 98.45% | 0 | 6.8199 | 48.7022 | 77.92% | 41.8588
3570 | 629 | 293 | 70 | 6.4 | 20.5 | 0 | 0 | 0 | 0 | 16.0302 | 0 | 0 | 16.0302 | 0 | 0 | 0 | 38.2653 | 12.8541 | 0 | 38.2653 | 1217.4927 | 95.45% | 0 | 13.2879 | 33.9961 | 54.39% | 42.1722
3571 | 348 | 100 | 40 | 6.4 | 18.5 | 0 | 0 | 0 | 0 | 1.9958 | 0 | 0 | 1.9958 | 0 | 0 | 0 | 97.4607 | 38.4996 | 0 | 97.4607 | 1120.0319 | 87.81% | 0 | 0 | 33.9961 | 54.39% | 40.4954
3572 | 3 | 4 | 4 | 5.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9995 | 37.0819 | 0 | 93.9995 | 1026.0324 | 80.44% | 0 | 0 | 33.9961 | 54.39% | 37.0819
3573 | 0 | 0 | 0 | 4.3 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3476 | 35.1015 | 0 | 89.3476 | 936.6848 | 73.44% | 0 | 0 | 33.9961 | 54.39% | 35.1015
3574 | 0 | 0 | 0 | 2.6 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2982 | 33.3759 | 0 | 85.2982 | 851.3866 | 66.75% | 0 | 0 | 33.9961 | 54.39% | 33.3759
3575 | 0 | 0 | 0 | 2.7 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1166 | 32.025 | 0 | 82.1166 | 769.27 | 60.31% | 0 | 0 | 33.9961 | 54.39% | 32.025
3576 | 0 | 0 | 0 | 2.2 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6776 | 31.4178 | 0 | 80.6776 | 688.5924 | 53.99% | 0 | 0 | 33.9961 | 54.39% | 31.4178
3577 | 0 | 0 | 0 | 2.7 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5492 | 31.3649 | 0 | 80.5492 | 608.0432 | 47.67% | 0 | 0 | 33.9961 | 54.39% | 31.3649
3578 | 0 | 0 | 0 | 2.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.746 | 31.9024 | 0 | 81.746 | 526.2972 | 41.26% | 0 | 0 | 33.9961 | 54.39% | 31.9024
3579 | 0 | 0 | 0 | 1.2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.227 | 34.2937 | 0 | 87.227 | 439.0702 | 34.42% | 0 | 0 | 33.9961 | 54.39% | 34.2937
3580 | 0 | 0 | 0 | 0.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.863 | 37.6208 | 0 | 94.863 | 344.2072 | 26.99% | 0 | 0 | 33.9961 | 54.39% | 37.6208
3581 | 0 | 1 | 1 | 0.9 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.2271 | 24.7285 | 0 | 65.2271 | 278.9801 | 21.87% | 0 | 15.8769 | 16.4247 | 26.28% | 40.6054
3582 | 356 | 69 | 24 | 0.6 | 13.2 | 0 | 0 | 0 | 0 | 0.77546 | 0 | 0 | 0.77546 | 0 | 0 | 0 | 103.3231 | 41.2936 | 0 | 103.3231 | 175.657 | 13.77% | 0 | 0 | 16.4247 | 26.28% | 42.0691
3583 | 705 | 262 | 46 | 2.3 | 16.6 | 0 | 0 | 0 | 0 | 2.479 | 0 | 0 | 2.479 | 0 | 0 | 0 | 101.3828 | 40.3031 | 0 | 101.3828 | 74.2743 | 5.823% | 0 | 0 | 16.4247 | 26.28% | 42.7822
3584 | 846 | 472 | 57 | 3.9 | 19.3 | 0 | 0 | 0 | 0 | 15.0377 | 0 | 0 | 15.0377 | 0 | 0 | 0 | 74.2743 | 28.4352 | 0 | 74.2743 | 0 | 0% | 0 | 0 | 16.4247 | 26.28% | 43.4729
3585 | 922 | 671 | 62 | 6.2 | 21 | 0 | 0 | 0 | 221.4972 | 35.3533 | 0 | 0 | 35.3533 | 0 | 0 | 0 | 0 | 0 | 221.4972 | 0 | 221.4972 | 17.37% | 0 | 9.1934 | 6.25 | 10% | 44.5467
3586 | 959 | 835 | 67 | 6.6 | 21.6 | 0 | 0 | 0 | 248.0848 | 44.7988 | 6.6256 | 0 | 44.7988 | 0 | 0 | 0 | 0 | 0 | 248.0848 | 0 | 469.582 | 36.82% | 0 | 0 | 6.25 | 10% | 44.7988
3587 | 962 | 948 | 78 | 6 | 22 | 0 | 0 | 0 | 0 | 43.544 | 18.7597 | 0 | 43.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 469.582 | 36.82% | 0 | 0 | 6.25 | 10% | 43.544
3588 | 980 | 1016 | 74 | 7.3 | 22.5 | 0 | 0 | 0 | 271.7131 | 42.7515 | 27.1024 | 0 | 42.7515 | 0 | 0 | 0 | 0 | 0 | 271.7131 | 0 | 741.2951 | 58.12% | 0 | 0 | 6.25 | 10% | 42.7515
3589 | 986 | 1023 | 70 | 7.7 | 23.4 | 0 | 0 | 0 | 276.9267 | 42.6178 | 29.3822 | 0 | 42.6178 | 0 | 0 | 0 | 0 | 0 | 276.9267 | 0 | 1018.2218 | 79.83% | 0 | 0 | 6.25 | 10% | 42.6178
3590 | 978 | 970 | 69 | 8 | 23.9 | 0 | 0 | 0 | 247.2363 | 66.6133 | 3.5921 | 24.0414 | 42.5719 | 0 | 0 | 0 | 0 | 0 | 247.2363 | 0 | 1265.4581 | 99.21% | 24.0414 | 0 | 27.9729 | 44.76% | 42.5719
3591 | 961 | 865 | 66 | 7.7 | 23.9 | 0 | 0 | 0 | 0 | 63.3171 | 0 | 21.3176 | 41.9995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.4581 | 99.21% | 21.3176 | 0 | 47.2346 | 75.58% | 41.9995
3592 | 916 | 707 | 66 | 7.7 | 23.5 | 0 | 0 | 0 | 0 | 51.7654 | 0 | 9.9776 | 41.7878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.4581 | 99.21% | 9.9776 | 0 | 56.25 | 90% | 41.7878
3593 | 850 | 516 | 61 | 7.7 | 22.7 | 0 | 0 | 0 | 0 | 36.3907 | 0 | 0 | 36.3907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.4581 | 99.21% | 0 | 5.3484 | 50.3308 | 80.53% | 41.739
3594 | 736 | 310 | 50 | 6.9 | 21.5 | 0 | 0 | 0 | 0 | 16.716 | 0 | 0 | 16.716 | 0 | 0 | 0 | 67.4265 | 25.3782 | 0 | 67.4265 | 1198.0316 | 93.93% | 0 | 0 | 50.3308 | 80.53% | 42.0942
3595 | 474 | 111 | 30 | 6.3 | 19.7 | 0 | 0 | 0 | 0 | 1.635 | 0 | 0 | 1.635 | 0 | 0 | 0 | 98.6483 | 38.9383 | 0 | 98.6483 | 1099.3833 | 86.19% | 0 | 0 | 50.3308 | 80.53% | 40.5733
3596 | 6 | 3 | 3 | 5.6 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.9137 | 0 | 38.2653 | 1061.118 | 83.19% | 0 | 24.508 | 23.207 | 37.13% | 37.4217
3597 | 0 | 0 | 0 | 4.6 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4413 | 35.5889 | 0 | 90.4413 | 970.6767 | 76.1% | 0 | 0 | 23.207 | 37.13% | 35.5889
3598 | 0 | 0 | 0 | 3.9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1895 | 33.7742 | 0 | 86.1895 | 884.4872 | 69.34% | 0 | 0 | 23.207 | 37.13% | 33.7742
3599 | 0 | 0 | 0 | 1.6 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0235 | 32.4289 | 0 | 83.0235 | 801.4638 | 62.83% | 0 | 0 | 23.207 | 37.13% | 32.4289
3600 | 0 | 0 | 0 | 1.3 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6569 | 31.8467 | 0 | 81.6569 | 719.8068 | 56.43% | 0 | 0 | 23.207 | 37.13% | 31.8467
3601 | 0 | 0 | 0 | 1.6 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0999 | 31.6044 | 0 | 81.0999 | 638.707 | 50.07% | 0 | 0 | 23.207 | 37.13% | 31.6044
3602 | 0 | 0 | 0 | 1.4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3348 | 32.1587 | 0 | 82.3348 | 556.3722 | 43.62% | 0 | 0 | 23.207 | 37.13% | 32.1587
3603 | 0 | 0 | 0 | 2 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2399 | 34.2965 | 0 | 87.2399 | 469.1323 | 36.78% | 0 | 0 | 23.207 | 37.13% | 34.2965
3604 | 0 | 0 | 0 | 1.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9782 | 37.671 | 0 | 94.9782 | 374.1541 | 29.33% | 0 | 0 | 23.207 | 37.13% | 37.671
3605 | 0 | 1 | 1 | 2.2 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0678 | 40.3408 | 0 | 101.0678 | 273.0863 | 21.41% | 0 | 0 | 23.207 | 37.13% | 40.3408
3606 | 389 | 72 | 22 | 1.4 | 13.6 | 0 | 0 | 0 | 0 | 0.67795 | 0 | 0 | 0.67795 | 0 | 0 | 0 | 103.3723 | 41.3006 | 0 | 103.3723 | 169.714 | 13.31% | 0 | 0 | 23.207 | 37.13% | 41.9786
3607 | 732 | 266 | 41 | 1.9 | 17.5 | 0 | 0 | 0 | 0 | 2.137 | 0 | 0 | 2.137 | 0 | 0 | 0 | 103.6895 | 41.2538 | 0 | 103.6895 | 66.0245 | 5.176% | 0 | 0 | 23.207 | 37.13% | 43.3908
3608 | 854 | 474 | 52 | 4.5 | 20.7 | 0 | 0 | 0 | 0 | 14.6824 | 0 | 0 | 14.6824 | 0 | 0 | 0 | 66.0245 | 24.8118 | 0 | 66.0245 | 0 | 0% | 0 | 4.9174 | 17.7648 | 28.42% | 44.4116
3609 | 919 | 669 | 59 | 5.4 | 22.2 | 0 | 0 | 0 | 41.5448 | 34.7273 | 0 | 0 | 34.7273 | 0 | 0 | 0 | 0 | 0 | 41.5448 | 0 | 41.5448 | 3.257% | 0 | 10.4043 | 6.25 | 10% | 45.1316
3610 | 960 | 836 | 62 | 6.6 | 23.6 | 0 | 0 | 0 | 0 | 45.3266 | 5.3645 | 0 | 45.3266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5448 | 3.257% | 0 | 0 | 6.25 | 10% | 45.3266
3611 | 975 | 952 | 66 | 6.5 | 24.2 | 0 | 0 | 0 | 0 | 44.1707 | 17.6487 | 0 | 44.1707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5448 | 3.257% | 0 | 0 | 6.25 | 10% | 44.1707
3612 | 980 | 1014 | 70 | 7 | 24.7 | 0 | 0 | 0 | 0 | 43.0899 | 25.8029 | 0 | 43.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5448 | 3.257% | 0 | 0 | 6.25 | 10% | 43.0899
3613 | 984 | 1022 | 69 | 7.6 | 25.3 | 0 | 0 | 0 | 0 | 43.0912 | 28.5295 | 0.47474 | 42.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5448 | 3.257% | 0.47474 | 0 | 6.679 | 10.69% | 42.6164
3614 | 977 | 971 | 67 | 7.5 | 25.4 | 0 | 0 | 0 | 272.0012 | 67.3713 | 2.0761 | 25 | 42.3713 | 0 | 0 | 0 | 0 | 0 | 272.0012 | 0 | 313.546 | 24.58% | 25 | 0 | 29.268 | 46.83% | 42.3713
3615 | 952 | 863 | 68 | 6.8 | 25.7 | 0 | 0 | 0 | 258.6577 | 62.2738 | 0 | 20.3258 | 41.9479 | 0 | 0 | 0 | 0 | 0 | 258.6577 | 0 | 572.2037 | 44.86% | 20.3258 | 0 | 47.6336 | 76.21% | 41.9479
3616 | 914 | 708 | 65 | 7.2 | 25.6 | 0 | 0 | 0 | 237.3951 | 51.1205 | 0 | 9.5361 | 41.5844 | 0 | 0 | 0 | 0 | 0 | 237.3951 | 0 | 809.5988 | 63.47% | 9.5361 | 0 | 56.25 | 90% | 41.5844
3617 | 849 | 518 | 61 | 7.5 | 24.7 | 0 | 0 | 0 | 205.1821 | 36.0837 | 0 | 0 | 36.0837 | 0 | 0 | 0 | 0 | 0 | 205.1821 | 0 | 1014.7809 | 79.56% | 0 | 5.1679 | 50.5305 | 80.85% | 41.2516
3618 | 734 | 312 | 50 | 6.7 | 23.6 | 0 | 0 | 0 | 154.4218 | 16.566 | 0 | 0 | 16.566 | 0 | 0 | 0 | 0 | 0 | 154.4218 | 0 | 1169.2027 | 91.67% | 0 | 24.5519 | 23.3581 | 37.37% | 41.1179
3619 | 474 | 113 | 31 | 6.1 | 21.5 | 0 | 0 | 0 | 0 | 1.6882 | 0 | 0 | 1.6882 | 0 | 0 | 0 | 74.452 | 28.4012 | 0 | 74.452 | 1094.7508 | 85.83% | 0 | 9.9994 | 12.2915 | 19.67% | 40.0887
3620 | 9 | 4 | 3 | 5 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0141 | 37.4356 | 0 | 95.0141 | 999.7367 | 78.38% | 0 | 0 | 12.2915 | 19.67% | 37.4356
3621 | 0 | 0 | 0 | 4.6 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7393 | 36.107 | 0 | 91.7393 | 907.9974 | 71.19% | 0 | 0 | 12.2915 | 19.67% | 36.107
3622 | 0 | 0 | 0 | 5.3 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9698 | 34.0862 | 0 | 86.9698 | 821.0275 | 64.37% | 0 | 0 | 12.2915 | 19.67% | 34.0862
3623 | 0 | 0 | 0 | 3.4 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3101 | 32.5013 | 0 | 83.3101 | 737.7175 | 57.84% | 0 | 0 | 12.2915 | 19.67% | 32.5013
3624 | 0 | 0 | 0 | 2.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1481 | 31.5515 | 0 | 81.1481 | 656.5694 | 51.48% | 0 | 0 | 12.2915 | 19.67% | 31.5515
3625 | 0 | 0 | 0 | 2.2 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9367 | 31.0404 | 0 | 79.9367 | 576.6327 | 45.21% | 0 | 0 | 12.2915 | 19.67% | 31.0404
3626 | 0 | 0 | 0 | 3 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9433 | 30.6295 | 0 | 78.9433 | 497.6893 | 39.02% | 0 | 0 | 12.2915 | 19.67% | 30.6295
3627 | 0 | 0 | 0 | 2.2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5172 | 30.454 | 0 | 78.5172 | 419.1721 | 32.86% | 0 | 0 | 12.2915 | 19.67% | 30.454
3628 | 0 | 0 | 0 | 1 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2549 | 31.2339 | 0 | 80.2549 | 338.9172 | 26.57% | 0 | 0 | 12.2915 | 19.67% | 31.2339
3629 | 0 | 1 | 1 | 1.2 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2322 | 33.855 | 0 | 86.2322 | 252.685 | 19.81% | 0 | 0 | 12.2915 | 19.67% | 33.855
3630 | 373 | 73 | 23 | 1.2 | 14 | 0 | 0 | 0 | 0 | 0.7242 | 0 | 0 | 0.7242 | 0 | 0 | 0 | 92.3145 | 36.476 | 0 | 92.3145 | 160.3705 | 12.57% | 0 | 0 | 12.2915 | 19.67% | 37.2002
3631 | 718 | 266 | 43 | 3.2 | 18.1 | 0 | 0 | 0 | 0 | 2.2613 | 0 | 0 | 2.2613 | 0 | 0 | 0 | 93.4471 | 36.7856 | 0 | 93.4471 | 66.9234 | 5.247% | 0 | 0 | 12.2915 | 19.67% | 39.047
3632 | 855 | 476 | 52 | 6.2 | 21.2 | 0 | 0 | 0 | 0 | 14.6481 | 0 | 0 | 14.6481 | 0 | 0 | 0 | 66.9234 | 25.176 | 0 | 66.9234 | 0 | 0% | 0 | 0 | 12.2915 | 19.67% | 39.8241
3633 | 930 | 676 | 55 | 6.4 | 22.8 | 0 | 0 | 0 | 0 | 34.7496 | 0 | 0 | 34.7496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 5.4589 | 6.25 | 10% | 40.2085
3634 | 968 | 841 | 59 | 6.7 | 24.1 | 0 | 0 | 0 | 153.247 | 40.6653 | 10.0387 | 0 | 40.6653 | 0 | 0 | 0 | 0 | 0 | 153.247 | 0 | 153.247 | 12.01% | 0 | 0 | 6.25 | 10% | 40.6653
3635 | 989 | 961 | 61 | 7.3 | 25.3 | 0 | 0 | 0 | 0 | 39.7461 | 22.4108 | 0 | 39.7461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.247 | 12.01% | 0 | 0 | 6.25 | 10% | 39.7461
3636 | 997 | 1026 | 63 | 7.7 | 25.7 | 0 | 0 | 0 | 0 | 38.2364 | 31.1351 | 0 | 38.2364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.247 | 12.01% | 0 | 0 | 6.25 | 10% | 38.2364
3637 | 996 | 1030 | 63 | 8.3 | 25.9 | 0 | 0 | 0 | 0 | 37.2058 | 34.7751 | 0 | 37.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.247 | 12.01% | 0 | 0 | 6.25 | 10% | 37.2058
3638 | 988 | 979 | 63 | 8.7 | 26.2 | 0 | 0 | 0 | 0 | 52.2842 | 17.6631 | 15.4502 | 36.834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.247 | 12.01% | 15.4502 | 0 | 20.2102 | 32.34% | 36.834
3639 | 968 | 871 | 62 | 8.5 | 25.9 | 0 | 0 | 0 | 261.8266 | 61.7393 | 1.3685 | 25 | 36.7393 | 0 | 0 | 0 | 0 | 0 | 261.8266 | 0 | 415.0737 | 32.54% | 25 | 0 | 42.7992 | 68.48% | 36.7393
3640 | 936 | 718 | 58 | 8.2 | 25.6 | 0 | 0 | 0 | 242.8629 | 51.8458 | 0 | 14.8865 | 36.9593 | 0 | 0 | 0 | 0 | 0 | 242.8629 | 0 | 657.9366 | 51.58% | 14.8865 | 0 | 56.25 | 90% | 36.9593
3641 | 878 | 528 | 53 | 8.4 | 24.8 | 0 | 0 | 0 | 212.1489 | 36.6311 | 0 | 0 | 36.6311 | 0 | 0 | 0 | 0 | 0 | 212.1489 | 0 | 870.0855 | 68.21% | 0 | 0.77384 | 55.3936 | 88.63% | 37.405
3642 | 773 | 320 | 44 | 7.8 | 23.5 | 0 | 0 | 0 | 163.0073 | 16.8952 | 0 | 0 | 16.8952 | 0 | 0 | 0 | 0 | 0 | 163.0073 | 0 | 1033.0928 | 80.99% | 0 | 21.0293 | 32.1198 | 51.39% | 37.9244
3643 | 531 | 119 | 27 | 6.3 | 22.1 | 0 | 0 | 0 | 0 | 1.747 | 0 | 0 | 1.747 | 0 | 0 | 0 | 91.9065 | 35.8696 | 0 | 91.9065 | 941.1863 | 73.79% | 0 | 0 | 32.1198 | 51.39% | 37.6167
3644 | 14 | 4 | 3 | 4.9 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7677 | 34.2471 | 0 | 87.7677 | 853.4186 | 66.91% | 0 | 1.2736 | 30.7102 | 49.14% | 35.5207
3645 | 0 | 0 | 0 | 4.8 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6601 | 33.4302 | 0 | 85.6601 | 767.7585 | 60.19% | 0 | 0 | 30.7102 | 49.14% | 33.4302
3646 | 0 | 0 | 0 | 2.3 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8999 | 31.4122 | 0 | 80.8999 | 686.8586 | 53.85% | 0 | 0 | 30.7102 | 49.14% | 31.4122
3647 | 0 | 0 | 0 | 2.1 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6915 | 30.0251 | 0 | 77.6915 | 609.1671 | 47.76% | 0 | 0 | 30.7102 | 49.14% | 30.0251
3648 | 0 | 0 | 0 | 1.2 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3679 | 29.0599 | 0 | 75.3679 | 533.7992 | 41.85% | 0 | 0 | 30.7102 | 49.14% | 29.0599
3649 | 0 | 0 | 0 | 1.3 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.4878 | 28.6937 | 0 | 74.4878 | 459.3113 | 36.01% | 0 | 0 | 30.7102 | 49.14% | 28.6937
3650 | 0 | 0 | 0 | 2.2 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7597 | 28.3803 | 0 | 73.7597 | 385.5517 | 30.23% | 0 | 0 | 30.7102 | 49.14% | 28.3803
3651 | 0 | 0 | 0 | 1.9 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.64 | 27.9082 | 0 | 72.64 | 312.9116 | 24.53% | 0 | 0 | 30.7102 | 49.14% | 27.9082
3652 | 0 | 0 | 0 | 1.4 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5063 | 27.8762 | 0 | 72.5063 | 240.4053 | 18.85% | 0 | 0 | 30.7102 | 49.14% | 27.8762
3653 | 0 | 1 | 1 | 2.4 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5541 | 29.6323 | 0 | 76.5541 | 163.8513 | 12.85% | 0 | 0 | 30.7102 | 49.14% | 29.6323
3654 | 420 | 77 | 21 | 2 | 15.4 | 0 | 0 | 0 | 0 | 0.62291 | 0 | 0 | 0.62291 | 0 | 0 | 0 | 81.1317 | 31.5664 | 0 | 81.1317 | 82.7196 | 6.485% | 0 | 0 | 30.7102 | 49.14% | 32.1893
3655 | 760 | 275 | 39 | 1.1 | 19.1 | 0 | 0 | 0 | 0 | 2.1889 | 0 | 0 | 2.1889 | 0 | 0 | 0 | 82.7196 | 32.0937 | 0 | 82.7196 | 0 | 0% | 0 | 0 | 30.7102 | 49.14% | 34.2825
3656 | 883 | 487 | 48 | 1.8 | 21.5 | 0 | 0 | 0 | 94.6184 | 14.4817 | 0 | 0 | 14.4817 | 0 | 0 | 0 | 0 | 0 | 94.6184 | 0 | 94.6184 | 7.418% | 0 | 20.8468 | 7.6384 | 12.22% | 35.3285
3657 | 946 | 686 | 54 | 3.4 | 23.8 | 0 | 0 | 0 | 230.3122 | 34.5795 | 0 | 0 | 34.5795 | 0 | 0 | 0 | 0 | 0 | 230.3122 | 0 | 324.9306 | 25.47% | 0 | 1.2545 | 6.25 | 10% | 35.834
3658 | 978 | 850 | 58 | 5.4 | 25.2 | 0 | 0 | 0 | 0 | 36.6042 | 13.9432 | 0 | 36.6042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.9306 | 25.47% | 0 | 0 | 6.25 | 10% | 36.6042
3659 | 993 | 967 | 61 | 5.2 | 26.4 | 0 | 0 | 0 | 0 | 36.5777 | 24.8267 | 0 | 36.5777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.9306 | 25.47% | 0 | 0 | 6.25 | 10% | 36.5777
3660 | 1001 | 1031 | 63 | 4.4 | 27.1 | 0 | 0 | 0 | 0 | 35.2992 | 32.5108 | 0 | 35.2992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.9306 | 25.47% | 0 | 0 | 6.25 | 10% | 35.2992
3661 | 1001 | 1037 | 63 | 4.5 | 27.9 | 0 | 0 | 0 | 0 | 34.5722 | 35.5423 | 0 | 34.5722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.9306 | 25.47% | 0 | 0 | 6.25 | 10% | 34.5722
3662 | 991 | 985 | 64 | 4.8 | 28.6 | 0 | 0 | 0 | 0 | 48.9723 | 19.1468 | 14.6577 | 34.3146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.9306 | 25.47% | 14.6577 | 0 | 19.4941 | 31.19% | 34.3146
3663 | 967 | 874 | 63 | 5.3 | 28.7 | 0 | 0 | 0 | 264.424 | 59.4552 | 2.1102 | 25 | 34.4552 | 0 | 0 | 0 | 0 | 0 | 264.424 | 0 | 589.3546 | 46.21% | 25 | 0 | 42.0831 | 67.33% | 34.4552
3664 | 931 | 718 | 60 | 5.1 | 27.9 | 0 | 0 | 0 | 244.2115 | 50.6968 | 0 | 15.679 | 35.0179 | 0 | 0 | 0 | 0 | 0 | 244.2115 | 0 | 833.566 | 65.35% | 15.679 | 0 | 56.25 | 90% | 35.0179
3665 | 871 | 528 | 55 | 4.8 | 27.8 | 0 | 0 | 0 | 213.5947 | 35.7776 | 0 | 0 | 35.7776 | 0 | 0 | 0 | 0 | 0 | 213.5947 | 0 | 1047.1607 | 82.1% | 0 | 0.18033 | 56.0504 | 89.68% | 35.958
3666 | 760 | 320 | 46 | 4.9 | 26.6 | 0 | 0 | 0 | 162.5848 | 16.5623 | 0 | 0 | 16.5623 | 0 | 0 | 0 | 0 | 0 | 162.5848 | 0 | 1209.7455 | 94.84% | 0 | 21.0975 | 32.7011 | 52.32% | 37.6598
3667 | 485 | 115 | 30 | 4.9 | 24.6 | 0 | 0 | 0 | 0 | 1.6267 | 0 | 0 | 1.6267 | 0 | 0 | 0 | 94.2095 | 36.6612 | 0 | 94.2095 | 1115.536 | 87.46% | 0 | 0 | 32.7011 | 52.32% | 38.2879
3668 | 15 | 5 | 4 | 3.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.9781 | 24.301 | 0 | 64.9781 | 1050.5579 | 82.36% | 0 | 11.6375 | 19.8215 | 31.71% | 35.9385
3669 | 0 | 0 | 0 | 2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3253 | 33.6015 | 0 | 86.3253 | 964.2326 | 75.6% | 0 | 0 | 19.8215 | 31.71% | 33.6015
3670 | 0 | 0 | 0 | 1.5 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8688 | 31.7158 | 0 | 81.8688 | 882.3638 | 69.18% | 0 | 0 | 19.8215 | 31.71% | 31.7158
3671 | 0 | 0 | 0 | 1.3 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0364 | 30.5446 | 0 | 79.0364 | 803.3274 | 62.98% | 0 | 0 | 19.8215 | 31.71% | 30.5446
3672 | 0 | 0 | 0 | 1 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3858 | 29.9151 | 0 | 77.3858 | 725.9416 | 56.91% | 0 | 0 | 19.8215 | 31.71% | 29.9151
3673 | 0 | 0 | 0 | 0.6 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2407 | 29.8663 | 0 | 77.2407 | 648.7009 | 50.86% | 0 | 0 | 19.8215 | 31.71% | 29.8663
3674 | 0 | 0 | 0 | 1 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1337 | 30.7089 | 0 | 79.1337 | 569.5672 | 44.65% | 0 | 0 | 19.8215 | 31.71% | 30.7089
3675 | 0 | 0 | 0 | 1.7 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1672 | 33.7533 | 0 | 86.1672 | 483.4 | 37.9% | 0 | 0 | 19.8215 | 31.71% | 33.7533
3676 | 0 | 0 | 0 | 0.6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1722 | 37.6807 | 0 | 95.1722 | 388.2278 | 30.44% | 0 | 0 | 19.8215 | 31.71% | 37.6807
3677 | 0 | 2 | 2 | 1.7 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9157 | 40.636 | 0 | 101.9157 | 286.3121 | 22.45% | 0 | 0 | 19.8215 | 31.71% | 40.636
3678 | 347 | 76 | 28 | 1.3 | 17.2 | 0 | 0 | 0 | 0 | 0.94862 | 0 | 0 | 0.94862 | 0 | 0 | 0 | 103.9629 | 41.3893 | 0 | 103.9629 | 182.3492 | 14.3% | 0 | 0 | 19.8215 | 31.71% | 42.3379
3679 | 694 | 267 | 51 | 0.6 | 21.8 | 0 | 0 | 0 | 0 | 2.7467 | 0 | 0 | 2.7467 | 0 | 0 | 0 | 103.6621 | 40.9463 | 0 | 103.6621 | 78.6871 | 6.169% | 0 | 0 | 19.8215 | 31.71% | 43.693
3680 | 813 | 476 | 71 | 0.9 | 23.7 | 0 | 0 | 0 | 0 | 14.6645 | 0 | 0 | 14.6645 | 0 | 0 | 0 | 78.6871 | 30.087 | 0 | 78.6871 | 0 | 0% | 0 | 0 | 19.8215 | 31.71% | 44.7514
3681 | 811 | 652 | 114 | 1.5 | 25.4 | 0 | 0 | 0 | 0 | 33.472 | 0 | 0 | 33.472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 12.2627 | 6.25 | 10% | 45.7347
3682 | 874 | 819 | 115 | 1.7 | 26.8 | 0 | 0 | 0 | 187.0955 | 46.2959 | 1.354 | 0 | 46.2959 | 0 | 0 | 0 | 0 | 0 | 187.0955 | 0 | 187.0955 | 14.67% | 0 | 0 | 6.25 | 10% | 46.2959
3683 | 933 | 942 | 96 | 1.6 | 28.8 | 0 | 0 | 0 | 254.8824 | 57.3735 | 0 | 12.0107 | 45.3628 | 0 | 0 | 0 | 0 | 0 | 254.8824 | 0 | 441.9779 | 34.65% | 12.0107 | 0 | 17.1024 | 27.36% | 45.3628
3684 | 948 | 1012 | 99 | 2.1 | 30.2 | 0 | 0 | 0 | 266.2797 | 53.0349 | 11.1036 | 8.0704 | 44.9645 | 0 | 0 | 0 | 0 | 0 | 266.2797 | 0 | 708.2576 | 55.53% | 8.0704 | 0 | 24.3945 | 39.03% | 44.9645
3685 | 914 | 1013 | 125 | 3.9 | 30.1 | 0 | 0 | 0 | 258.5979 | 67.6039 | 0 | 22.7132 | 44.8907 | 0 | 0 | 0 | 0 | 0 | 258.5979 | 0 | 966.8555 | 75.8% | 22.7132 | 0 | 44.9172 | 71.87% | 44.8907
3686 | 577 | 844 | 300 | 3.7 | 30.2 | 0 | 0 | 0 | 155.078 | 57.6281 | 0 | 12.5424 | 45.0857 | 0 | 0 | 0 | 0 | 0 | 155.078 | 0 | 1121.9335 | 87.96% | 12.5424 | 0 | 56.25 | 90% | 45.0857
3687 | 162 | 585 | 441 | 5 | 29 | 0 | 0 | 0 | 0 | 38.6855 | 0 | 0 | 38.6855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1121.9335 | 87.96% | 0 | 1.6669 | 54.4052 | 87.05% | 40.3524
3688 | 249 | 522 | 339 | 4.3 | 29.1 | 0 | 0 | 0 | 0 | 34.74 | 1.4211e-14 | 0 | 34.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1121.9335 | 87.96% | 0 | 8.8973 | 44.5583 | 71.29% | 43.6373
3689 | 644 | 499 | 152 | 4.1 | 29 | 0 | 0 | 0 | 153.5767 | 33.7532 | 0 | 0 | 33.7532 | 0 | 0 | 0 | 0 | 0 | 153.5767 | 0 | 1275.5102 | 100% | 0 | 9.6139 | 33.9183 | 54.27% | 43.3671
3690 | 499 | 266 | 92 | 4.2 | 28.2 | 0 | 0 | 0 | 0 | 14.5539 | 0 | 0 | 14.5539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 6.25 | 10% | 39.5539
3691 | 376 | 110 | 43 | 3.8 | 26.8 | 0 | 0 | 0 | 0 | 2.1348 | 0 | 0 | 2.1348 | 0 | 0 | 0 | 101.694 | 39.6446 | 0 | 101.694 | 1173.8162 | 92.03% | 0 | 0 | 6.25 | 10% | 41.7794
3692 | 11 | 5 | 5 | 1.8 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1663 | 38.3966 | 0 | 98.1663 | 1075.65 | 84.33% | 0 | 0 | 6.25 | 10% | 38.3966
3693 | 0 | 0 | 0 | 1.4 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.846 | 36.7671 | 0 | 93.846 | 981.804 | 76.97% | 0 | 0 | 6.25 | 10% | 36.7671
3694 | 0 | 0 | 0 | 0.6 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1977 | 34.8104 | 0 | 89.1977 | 892.6063 | 69.98% | 0 | 0 | 6.25 | 10% | 34.8104
3695 | 0 | 0 | 0 | 1 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9388 | 33.4901 | 0 | 85.9388 | 806.6675 | 63.24% | 0 | 0 | 6.25 | 10% | 33.4901
3696 | 0 | 0 | 0 | 0.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2737 | 32.8439 | 0 | 84.2737 | 722.3937 | 56.64% | 0 | 0 | 6.25 | 10% | 32.8439
3697 | 0 | 0 | 0 | 0.6 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.3256 | 22.4921 | 0 | 60.3256 | 662.0681 | 51.91% | 0 | 0 | 6.25 | 10% | 22.4921
3698 | 0 | 0 | 0 | 0.2 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.9343 | 0 | 38.2653 | 623.8028 | 48.91% | 0 | 0 | 6.25 | 10% | 12.9343
3699 | 0 | 0 | 0 | 0.4 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6712 | 35.6669 | 0 | 90.6712 | 533.1316 | 41.8% | 0 | 0 | 6.25 | 10% | 35.6669
3700 | 0 | 0 | 0 | 0.2 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5572 | 39.1208 | 0 | 98.5572 | 434.5744 | 34.07% | 0 | 0 | 6.25 | 10% | 39.1208
3701 | 0 | 1 | 1 | 1 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7038 | 41.7989 | 0 | 104.7038 | 329.8707 | 25.86% | 0 | 0 | 6.25 | 10% | 41.7989
3702 | 369 | 75 | 26 | 0.6 | 17 | 0 | 0 | 0 | 0 | 0.85333 | 0 | 0 | 0.85333 | 0 | 0 | 0 | 106.4865 | 42.4943 | 0 | 106.4865 | 223.3841 | 17.51% | 0 | 0 | 6.25 | 10% | 43.3476
3703 | 711 | 271 | 50 | 0.9 | 20.8 | 0 | 0 | 0 | 0 | 2.6944 | 0 | 0 | 2.6944 | 0 | 0 | 0 | 105.4109 | 41.7771 | 0 | 105.4109 | 117.9733 | 9.249% | 0 | 0 | 6.25 | 10% | 44.4715
3704 | 831 | 478 | 68 | 1.2 | 21.8 | 0 | 0 | 0 | 0 | 14.7624 | 0 | 0 | 14.7624 | 0 | 0 | 0 | 79.708 | 30.645 | 0 | 79.708 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 45.4074
3705 | 905 | 675 | 76 | 1.7 | 24.8 | 0 | 0 | 0 | 0 | 34.0262 | 0 | 0 | 34.0262 | 0 | 0 | 0 | 38.2653 | 12.7405 | 0 | 38.2653 | 0 | 0% | 0.38999 | 0 | 6.6024 | 10.56% | 46.3767
3706 | 941 | 839 | 83 | 2.3 | 25.8 | 0 | 0 | 0 | 0 | 46.5327 | 2.5541 | 0 | 46.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.6024 | 10.56% | 46.5327
3707 | 958 | 955 | 87 | 2.3 | 27.7 | 0 | 0 | 0 | 18.3595 | 48.8346 | 10.186 | 3.3743 | 45.4603 | 0 | 0 | 0 | 0 | 0 | 18.3595 | 0 | 18.3595 | 1.439% | 3.3743 | 0 | 9.6513 | 15.44% | 45.4603
3708 | 962 | 1017 | 90 | 4 | 29.7 | 0 | 0 | 0 | 269.2458 | 44.9255 | 21.2927 | 0 | 44.9255 | 0 | 0 | 0 | 0 | 0 | 269.2458 | 0 | 287.6053 | 22.55% | 0 | 0 | 9.6513 | 15.44% | 44.9255
3709 | 954 | 1019 | 94 | 4.9 | 30.1 | 0 | 0 | 0 | 269.7783 | 68.7682 | 0 | 24.0098 | 44.7584 | 0 | 0 | 0 | 0 | 0 | 269.7783 | 0 | 557.3836 | 43.7% | 24.0098 | 0 | 31.3455 | 50.15% | 44.7584
3710 | 933 | 961 | 96 | 5.6 | 30.8 | 0 | 0 | 0 | 260.6152 | 66.4406 | 0 | 21.6738 | 44.7667 | 0 | 0 | 0 | 0 | 0 | 260.6152 | 0 | 817.9988 | 64.13% | 21.6738 | 0 | 50.9291 | 81.49% | 44.7667
3711 | 897 | 856 | 104 | 5.1 | 30.9 | 0 | 0 | 0 | 244.1254 | 43.9395 | 15.7601 | 0 | 43.9395 | 0 | 0 | 0 | 0 | 0 | 244.1254 | 0 | 1062.1242 | 83.27% | 0 | 0 | 50.9291 | 81.49% | 43.9395
3712 | 823 | 701 | 118 | 5.2 | 30.2 | 0 | 0 | 0 | 213.386 | 49.1556 | 0 | 5.8888 | 43.2668 | 0 | 0 | 0 | 0 | 0 | 213.386 | 0 | 1275.5102 | 100% | 5.8888 | 0 | 56.25 | 90% | 43.2668
3713 | 722 | 506 | 112 | 4.2 | 29.6 | 0 | 0 | 0 | 0 | 33.9665 | 0 | 0 | 33.9665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 9.15 | 46.1234 | 73.8% | 43.1164
3714 | 571 | 301 | 93 | 4.3 | 26.6 | 0 | 0 | 0 | 0 | 16.0241 | 0 | 0 | 16.0241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 18.4551 | 29.53% | 41.0241
3715 | 255 | 103 | 52 | 3.6 | 23.9 | 0 | 0 | 0 | 0 | 2.6216 | 0 | 0 | 2.6216 | 0 | 0 | 0 | 95.9306 | 37.4566 | 0 | 95.9306 | 1179.5796 | 92.48% | 0 | 1.509 | 16.7851 | 26.86% | 41.5872
3716 | 3 | 4 | 4 | 2.7 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3569 | 38.2643 | 0 | 97.3569 | 1082.2226 | 84.85% | 0 | 0 | 16.7851 | 26.86% | 38.2643
3717 | 0 | 0 | 0 | 1.9 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4768 | 36.7058 | 0 | 93.4768 | 988.7458 | 77.52% | 0 | 0 | 16.7851 | 26.86% | 36.7058
3718 | 0 | 0 | 0 | 1.2 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9845 | 34.8173 | 0 | 88.9845 | 899.7613 | 70.54% | 0 | 0 | 16.7851 | 26.86% | 34.8173
3719 | 0 | 0 | 0 | 1.1 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.149 | 33.6071 | 0 | 86.149 | 813.6123 | 63.79% | 0 | 0 | 16.7851 | 26.86% | 33.6071
3720 | 0 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9276 | 32.9985 | 0 | 84.9276 | 728.6847 | 57.13% | 0 | 0 | 16.7851 | 26.86% | 32.9985
3721 | 0 | 0 | 0 | 0.9 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.3163 | 25.3776 | 0 | 67.3163 | 661.3684 | 51.85% | 0 | 0 | 16.7851 | 26.86% | 25.3776
3722 | 0 | 0 | 0 | 1.7 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8307 | 33.4107 | 0 | 85.8307 | 575.5377 | 45.12% | 0 | 0 | 16.7851 | 26.86% | 33.4107
3723 | 0 | 0 | 0 | 3.9 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3958 | 35.692 | 0 | 91.3958 | 484.1419 | 37.96% | 0 | 0 | 16.7851 | 26.86% | 35.692
3724 | 0 | 0 | 0 | 4.6 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1807 | 39.0999 | 0 | 99.1807 | 384.9612 | 30.18% | 0 | 0 | 16.7851 | 26.86% | 39.0999
3725 | 0 | 1 | 1 | 4.6 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.0105 | 41.597 | 0 | 105.0105 | 279.9507 | 21.95% | 0 | 0 | 16.7851 | 26.86% | 41.597
3726 | 119 | 54 | 38 | 7.8 | 21.4 | 0 | 0 | 0 | 0 | 1.4043 | 0 | 0 | 1.4043 | 0 | 0 | 0 | 104.5432 | 41.357 | 0 | 104.5432 | 175.4075 | 13.75% | 0 | 0 | 16.7851 | 26.86% | 42.7613
3727 | 509 | 237 | 75 | 8.5 | 22 | 0 | 0 | 0 | 0 | 4.021 | 0 | 0 | 4.021 | 0 | 0 | 0 | 100.8485 | 39.7207 | 0 | 100.8485 | 74.559 | 5.845% | 0 | 0 | 16.7851 | 26.86% | 43.7417
3728 | 685 | 453 | 115 | 9.1 | 22.8 | 0 | 0 | 0 | 0 | 15.9727 | 1.7764e-15 | 0 | 15.9727 | 0 | 0 | 0 | 74.559 | 28.3734 | 0 | 74.559 | 0 | 0% | 0 | 0 | 16.7851 | 26.86% | 44.3462
3729 | 882 | 678 | 91 | 10.1 | 24 | 0 | 0 | 0 | 0 | 35.426 | 0 | 0 | 35.426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 9.5191 | 6.25 | 10% | 44.945
3730 | 858 | 855 | 165 | 10.7 | 25.3 | 0 | 0 | 0 | 215.7139 | 45.3531 | 7.5321 | 0 | 45.3531 | 0 | 0 | 0 | 0 | 0 | 215.7139 | 0 | 215.7139 | 16.91% | 0 | 0 | 6.25 | 10% | 45.3531
3731 | 481 | 811 | 369 | 10.3 | 26.1 | 0 | 0 | 0 | 115.9619 | 44.0843 | 9.8126 | 0 | 44.0843 | 0 | 0 | 0 | 0 | 0 | 115.9619 | 0 | 331.6758 | 26% | 0 | 0 | 6.25 | 10% | 44.0843
3732 | 778 | 1045 | 288 | 6.9 | 27.6 | 0 | 0 | 0 | 211.4357 | 42.9075 | 27.2218 | 0 | 42.9075 | 0 | 0 | 0 | 0 | 0 | 211.4357 | 0 | 543.1115 | 42.58% | 0 | 0 | 6.25 | 10% | 42.9075
3733 | 947 | 1051 | 129 | 3.5 | 28 | 0 | 0 | 0 | 268.8229 | 67.7529 | 2.1145 | 25 | 42.7529 | 0 | 0 | 0 | 0 | 0 | 268.8229 | 0 | 811.9344 | 63.66% | 25 | 0 | 28.839 | 46.14% | 42.7529
3734 | 935 | 980 | 109 | 2.4 | 28.5 | 0 | 0 | 0 | 263.6165 | 65.5391 | 0 | 22.9491 | 42.59 | 0 | 0 | 0 | 0 | 0 | 263.6165 | 0 | 1075.5508 | 84.32% | 22.9491 | 0 | 49.5749 | 79.32% | 42.59
3735 | 740 | 841 | 213 | 4.8 | 28.5 | 0 | 0 | 0 | 198.1333 | 49.1907 | 9.6009 | 7.3876 | 41.8031 | 0 | 0 | 0 | 0 | 0 | 198.1333 | 0 | 1273.6841 | 99.86% | 7.3876 | 0 | 56.25 | 90% | 41.8031
3736 | 376 | 586 | 309 | 5.8 | 27.5 | 0 | 0 | 0 | 1.8261 | 39.5078 | 0 | 0 | 39.5078 | 0 | 0 | 0 | 0 | 0 | 1.8261 | 0 | 1275.5102 | 100% | 0 | 1.865 | 54.1859 | 86.7% | 41.3728
3737 | 296 | 409 | 244 | 4.4 | 26.6 | 0 | 0 | 0 | 0 | 26.6894 | 0 | 0 | 26.6894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 15.083 | 37.4931 | 59.99% | 41.7725
3738 | 27 | 154 | 142 | 3.4 | 25.4 | 0 | 0 | 0 | 0 | 9.0098 | 0 | 0 | 9.0098 | 0 | 0 | 0 | 80.9983 | 30.9548 | 0 | 80.9983 | 1194.5119 | 93.65% | 0 | 2.1281 | 35.1378 | 56.22% | 42.0928
3739 | 37 | 67 | 59 | 2.1 | 24.4 | 0 | 0 | 0 | 0 | 3.2806 | 0 | 0 | 3.2806 | 0 | 0 | 0 | 95.9136 | 37.407 | 0 | 95.9136 | 1098.5983 | 86.13% | 0 | 0 | 35.1378 | 56.22% | 40.6875
3740 | 2 | 6 | 6 | 1.6 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8237 | 37.476 | 0 | 95.8237 | 1002.7746 | 78.62% | 0 | 0 | 35.1378 | 56.22% | 37.476
3741 | 0 | 0 | 0 | 1.9 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5584 | 35.7755 | 0 | 91.5584 | 911.2161 | 71.44% | 0 | 0 | 35.1378 | 56.22% | 35.7755
3742 | 0 | 0 | 0 | 1 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2693 | 33.997 | 0 | 87.2693 | 823.9469 | 64.6% | 0 | 0 | 35.1378 | 56.22% | 33.997
3743 | 0 | 0 | 0 | 1.8 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5048 | 32.816 | 0 | 84.5048 | 739.4421 | 57.97% | 0 | 0 | 35.1378 | 56.22% | 32.816
3744 | 0 | 0 | 0 | 1.7 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0016 | 32.2409 | 0 | 83.0016 | 656.4405 | 51.46% | 0 | 0 | 35.1378 | 56.22% | 32.2409
3745 | 0 | 0 | 0 | 1.6 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8651 | 32.206 | 0 | 82.8651 | 573.5753 | 44.97% | 0 | 0 | 35.1378 | 56.22% | 32.206
3746 | 0 | 0 | 0 | 2.1 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6004 | 32.5431 | 0 | 83.6004 | 489.9749 | 38.41% | 0 | 0 | 35.1378 | 56.22% | 32.5431
3747 | 0 | 0 | 0 | 1.5 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5225 | 34.7561 | 0 | 88.5225 | 401.4524 | 31.47% | 0 | 0 | 35.1378 | 56.22% | 34.7561
3748 | 0 | 0 | 0 | 0.8 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9438 | 38.0359 | 0 | 95.9438 | 305.5086 | 23.95% | 0 | 0 | 35.1378 | 56.22% | 38.0359
3749 | 0 | 1 | 1 | 0.7 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.1445 | 40.7628 | 0 | 102.1445 | 203.3641 | 15.94% | 0 | 0 | 35.1378 | 56.22% | 40.7628
3750 | 303 | 73 | 30 | 0.7 | 15.6 | 0 | 0 | 0 | 0 | 1.0528 | 0 | 0 | 1.0528 | 0 | 0 | 0 | 102.7392 | 40.9411 | 0 | 102.7392 | 100.6248 | 7.889% | 0 | 0 | 35.1378 | 56.22% | 41.9939
3751 | 642 | 260 | 61 | 0.2 | 20.3 | 0 | 0 | 0 | 0 | 3.104 | 0 | 0 | 3.104 | 0 | 0 | 0 | 100.6248 | 39.7505 | 0 | 100.6248 | 0 | 0% | 0 | 0 | 35.1378 | 56.22% | 42.8546
3752 | 791 | 469 | 78 | 1.1 | 22.5 | 0 | 0 | 0 | 0 | 14.7496 | 0 | 0 | 14.7496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 7.4695 | 11.95% | 39.7496
3753 | 872 | 665 | 87 | 3.3 | 23.7 | 0 | 0 | 0 | 210.7899 | 34.1476 | 0 | 0 | 34.1476 | 0 | 0 | 0 | 0 | 0 | 210.7899 | 0 | 210.7899 | 16.53% | 0 | 1.1019 | 6.25 | 10% | 35.2495
3754 | 926 | 833 | 88 | 3.7 | 24.5 | 0 | 0 | 0 | 0 | 44.3698 | 5.1545 | 0 | 44.3698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.7899 | 16.53% | 0 | 0 | 6.25 | 10% | 44.3698
3755 | 951 | 951 | 88 | 3 | 25.6 | 0 | 0 | 0 | 0 | 43.2181 | 16.4037 | 0 | 43.2181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.7899 | 16.53% | 0 | 0 | 6.25 | 10% | 43.2181
3756 | 944 | 1013 | 102 | 3.6 | 26.4 | 0 | 0 | 0 | 0 | 42.5315 | 23.7485 | 0 | 42.5315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.7899 | 16.53% | 0 | 0 | 6.25 | 10% | 42.5315
3757 | 946 | 1019 | 99 | 4.3 | 26.7 | 0 | 0 | 0 | 96.8725 | 43.5358 | 25.4105 | 0.996 | 42.5398 | 0 | 0 | 0 | 0 | 0 | 96.8725 | 0 | 307.6624 | 24.12% | 0.996 | 0 | 7.1499 | 11.44% | 42.5398
3758 | 950 | 974 | 93 | 5.2 | 26.4 | 0 | 0 | 0 | 265.9795 | 67.3184 | 0.73369 | 25 | 42.3184 | 0 | 0 | 0 | 0 | 0 | 265.9795 | 0 | 573.6419 | 44.97% | 25 | 0 | 29.7389 | 47.58% | 42.3184
3759 | 937 | 872 | 87 | 4.9 | 26.9 | 0 | 0 | 0 | 255.9644 | 61.5679 | 0 | 19.6631 | 41.9048 | 0 | 0 | 0 | 0 | 0 | 255.9644 | 0 | 829.6063 | 65.04% | 19.6631 | 0 | 47.5058 | 76.01% | 41.9048
3760 | 915 | 724 | 77 | 5.7 | 26.7 | 0 | 0 | 0 | 239.114 | 51.4082 | 0 | 9.6776 | 41.7307 | 0 | 0 | 0 | 0 | 0 | 239.114 | 0 | 1068.7203 | 83.79% | 9.6776 | 0 | 56.25 | 90% | 41.7307
3761 | 850 | 533 | 69 | 6.4 | 26.1 | 0 | 0 | 0 | 206.7899 | 36.4423 | 0 | 0 | 36.4423 | 0 | 0 | 0 | 0 | 0 | 206.7899 | 0 | 1275.5102 | 100% | 0 | 5.4096 | 50.2631 | 80.42% | 41.8518
3762 | 732 | 323 | 57 | 5.7 | 25.4 | 0 | 0 | 0 | 0 | 17.0328 | 0 | 0 | 17.0328 | 0 | 0 | 0 | 38.2653 | 12.7222 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 12.5188 | 36.4081 | 58.25% | 42.2738
3763 | 479 | 121 | 34 | 4.2 | 24.5 | 0 | 0 | 0 | 0 | 1.9015 | 0 | 0 | 1.9015 | 0 | 0 | 0 | 62.1309 | 22.9537 | 0 | 62.1309 | 1175.114 | 92.13% | 0 | 16.0468 | 18.6485 | 29.84% | 40.902
3764 | 17 | 5 | 4 | 2.4 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1831 | 37.6849 | 0 | 96.1831 | 1078.9309 | 84.59% | 0 | 0 | 18.6485 | 29.84% | 37.6849
3765 | 0 | 0 | 0 | 1.1 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2743 | 36.1237 | 0 | 92.2743 | 986.6566 | 77.35% | 0 | 0 | 18.6485 | 29.84% | 36.1237
3766 | 0 | 0 | 0 | 1.3 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7551 | 34.2965 | 0 | 87.7551 | 898.9015 | 70.47% | 0 | 0 | 18.6485 | 29.84% | 34.2965
3767 | 0 | 0 | 0 | 0.5 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.706 | 33.0709 | 0 | 84.706 | 814.1956 | 63.83% | 0 | 0 | 18.6485 | 29.84% | 33.0709
3768 | 0 | 0 | 0 | 0.8 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6905 | 31.3603 | 0 | 80.6905 | 733.5051 | 57.51% | 0 | 0 | 18.6485 | 29.84% | 31.3603
3769 | 0 | 0 | 0 | 1 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0651 | 32.447 | 0 | 83.0651 | 650.44 | 50.99% | 0 | 0 | 18.6485 | 29.84% | 32.447
3770 | 0 | 0 | 0 | 0.7 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1419 | 32.9247 | 0 | 84.1419 | 566.2981 | 44.4% | 0 | 0 | 18.6485 | 29.84% | 32.9247
3771 | 0 | 0 | 0 | 1.5 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3739 | 35.2101 | 0 | 89.3739 | 476.9242 | 37.39% | 0 | 0 | 18.6485 | 29.84% | 35.2101
3772 | 0 | 0 | 0 | 1.3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3302 | 38.2657 | 0 | 96.3302 | 380.594 | 29.84% | 0 | 0 | 18.6485 | 29.84% | 38.2657
3773 | 0 | 1 | 1 | 1.9 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4459 | 40.9048 | 0 | 102.4459 | 278.1481 | 21.81% | 0 | 0 | 18.6485 | 29.84% | 40.9048
3774 | 185 | 66 | 38 | 1.7 | 16.2 | 0 | 0 | 0 | 0 | 1.4375 | 0 | 0 | 1.4375 | 0 | 0 | 0 | 102.748 | 40.9157 | 0 | 102.748 | 175.4001 | 13.75% | 0 | 0 | 18.6485 | 29.84% | 42.3532
3775 | 455 | 220 | 77 | 0.8 | 18.6 | 0 | 0 | 0 | 0 | 3.8619 | 0 | 0 | 3.8619 | 0 | 0 | 0 | 99.1653 | 39.2308 | 0 | 99.1653 | 76.2349 | 5.977% | 0 | 0 | 18.6485 | 29.84% | 43.0927
3776 | 731 | 457 | 93 | 0.9 | 21.6 | 0 | 0 | 0 | 0 | 14.7266 | 0 | 0 | 14.7266 | 0 | 0 | 0 | 76.2349 | 29.1627 | 0 | 76.2349 | 1.4211e-14 | 1.114e-15% | 0 | 0 | 18.6485 | 29.84% | 43.8893
3777 | 829 | 654 | 103 | 1.5 | 23.2 | 0 | 0 | 0 | 0 | 33.2854 | 0 | 0 | 33.2854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 11.2028 | 6.25 | 10% | 44.4882
3778 | 877 | 817 | 110 | 1.9 | 25.1 | 0 | 0 | 0 | 228.1897 | 44.5676 | 3.0886 | 0 | 44.5676 | 0 | 0 | 0 | 0 | 0 | 228.1897 | 0 | 228.1897 | 17.89% | 0 | 0 | 6.25 | 10% | 44.5676
3779 | 908 | 936 | 112 | 2.4 | 26.5 | 0 | 0 | 0 | 247.0361 | 45.7055 | 12.4184 | 2.4958 | 43.2097 | 0 | 0 | 0 | 0 | 0 | 247.0361 | 0 | 475.2258 | 37.26% | 2.4958 | 0 | 8.5051 | 13.61% | 43.2097
3780 | 908 | 997 | 120 | 4.7 | 27 | 0 | 0 | 0 | 252.4163 | 42.1652 | 23.5876 | 0 | 42.1652 | 0 | 0 | 0 | 0 | 0 | 252.4163 | 0 | 727.6421 | 57.05% | 0 | 0 | 8.5051 | 13.61% | 42.1652
3781 | 899 | 1000 | 124 | 3.6 | 27.5 | 0 | 0 | 0 | 254.1982 | 66.8502 | 0 | 24.8939 | 41.9563 | 0 | 0 | 0 | 0 | 0 | 254.1982 | 0 | 981.8403 | 76.98% | 24.8939 | 0 | 30.9983 | 49.6% | 41.9563
3782 | 890 | 949 | 119 | 2.3 | 28.1 | 0 | 0 | 0 | 0 | 63.4849 | 0 | 21.6833 | 41.8017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 981.8403 | 76.98% | 21.6833 | 0 | 50.5904 | 80.94% | 41.8017
3783 | 864 | 845 | 117 | 3.1 | 28.4 | 0 | 0 | 0 | 0 | 41.3338 | 16.7646 | 0 | 41.3338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 981.8403 | 76.98% | 0 | 0 | 50.5904 | 80.94% | 41.3338
3784 | 813 | 690 | 111 | 2.5 | 29 | 0 | 0 | 0 | 182.7256 | 47.1922 | 0 | 6.2637 | 40.9285 | 0 | 0 | 0 | 0 | 0 | 182.7256 | 0 | 1164.5658 | 91.3% | 6.2637 | 0 | 56.25 | 90% | 40.9285
3785 | 733 | 502 | 100 | 3.9 | 28.7 | 0 | 0 | 0 | 0 | 33.6479 | 0 | 0 | 33.6479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1164.5658 | 91.3% | 0 | 7.0271 | 48.4729 | 77.56% | 40.675
3786 | 596 | 298 | 79 | 4.6 | 27.9 | 0 | 0 | 0 | 0 | 15.5489 | 0 | 0 | 15.5489 | 0 | 0 | 0 | 67.7012 | 25.1177 | 0 | 67.7012 | 1096.8646 | 85.99% | 0 | 0 | 48.4729 | 77.56% | 40.6667
3787 | 358 | 112 | 46 | 4.1 | 26.6 | 0 | 0 | 0 | 0 | 2.3261 | 0 | 0 | 2.3261 | 0 | 0 | 0 | 78.8483 | 29.9472 | 0 | 78.8483 | 1018.0163 | 79.81% | 0 | 7.2639 | 40.4337 | 64.69% | 39.5372
3788 | 15 | 7 | 6 | 4.1 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0503 | 36.6515 | 0 | 94.0503 | 923.966 | 72.44% | 0 | 0 | 40.4337 | 64.69% | 36.6515
3789 | 0 | 0 | 0 | 3.4 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6379 | 35.3925 | 0 | 90.6379 | 833.3281 | 65.33% | 0 | 0 | 40.4337 | 64.69% | 35.3925
3790 | 0 | 0 | 0 | 3.7 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2017 | 33.582 | 0 | 86.2017 | 747.1264 | 58.57% | 0 | 0 | 40.4337 | 64.69% | 33.582
3791 | 0 | 0 | 0 | 3.4 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5842 | 32.0403 | 0 | 82.5842 | 664.5421 | 52.1% | 0 | 0 | 40.4337 | 64.69% | 32.0403
3792 | 0 | 0 | 0 | 4.4 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3931 | 31.1128 | 0 | 80.3931 | 584.1491 | 45.8% | 0 | 0 | 40.4337 | 64.69% | 31.1128
3793 | 0 | 0 | 0 | 4.8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0393 | 30.5975 | 0 | 79.0393 | 505.1097 | 39.6% | 0 | 0 | 40.4337 | 64.69% | 30.5975
3794 | 0 | 0 | 0 | 3.8 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8843 | 30.5501 | 0 | 78.8843 | 426.2254 | 33.42% | 0 | 0 | 40.4337 | 64.69% | 30.5501
3795 | 0 | 0 | 0 | 3.8 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7374 | 30.4902 | 0 | 78.7374 | 347.4881 | 27.24% | 0 | 0 | 40.4337 | 64.69% | 30.4902
3796 | 0 | 0 | 0 | 1.4 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5394 | 31.291 | 0 | 80.5394 | 266.9487 | 20.93% | 0 | 0 | 40.4337 | 64.69% | 31.291
3797 | 0 | 1 | 1 | 1.3 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.392 | 33.8313 | 0 | 86.392 | 180.5567 | 14.16% | 0 | 0 | 40.4337 | 64.69% | 33.8313
3798 | 264 | 70 | 32 | 1.4 | 17 | 0 | 0 | 0 | 0 | 1.1418 | 0 | 0 | 1.1418 | 0 | 0 | 0 | 90.4913 | 35.5612 | 0 | 90.4913 | 90.0654 | 7.061% | 0 | 0 | 40.4337 | 64.69% | 36.703
3799 | 589 | 252 | 67 | 2 | 20.2 | 0 | 0 | 0 | 0 | 3.4985 | 0 | 0 | 3.4985 | 0 | 0 | 0 | 90.0654 | 35.2031 | 0 | 90.0654 | 0 | 0% | 0 | 0 | 40.4337 | 64.69% | 38.7016
3800 | 740 | 457 | 88 | 5.6 | 23.1 | 0 | 0 | 0 | 0 | 14.6187 | 0 | 0 | 14.6187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 24.8614 | 12.9188 | 20.67% | 39.4801
3801 | 815 | 647 | 103 | 7.1 | 24.2 | 0 | 0 | 0 | 0 | 33.6285 | 0 | 0 | 33.6285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 6.0257 | 6.25 | 10% | 39.6542
3802 | 850 | 807 | 118 | 6.9 | 24.9 | 0 | 0 | 0 | 0 | 39.8951 | 8.9009 | 0 | 39.8951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 39.8951
3803 | 870 | 924 | 130 | 7.1 | 25.1 | 0 | 0 | 0 | 0 | 38.8367 | 20.7274 | 0 | 38.8367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.8367
3804 | 875 | 989 | 140 | 7.2 | 25.6 | 0 | 0 | 0 | 240.2326 | 37.3451 | 28.8729 | 0 | 37.3451 | 0 | 0 | 0 | 0 | 0 | 240.2326 | 0 | 240.2326 | 18.83% | 0 | 0 | 6.25 | 10% | 37.3451
3805 | 851 | 990 | 158 | 7.7 | 25.8 | 0 | 0 | 0 | 91.1263 | 36.4788 | 31.6388 | 0 | 36.4788 | 0 | 0 | 0 | 0 | 0 | 91.1263 | 0 | 331.359 | 25.98% | 0 | 0 | 6.25 | 10% | 36.4788
3806 | 846 | 947 | 157 | 7.9 | 25.9 | 0 | 0 | 0 | 232.2491 | 61.1209 | 5.4231 | 25 | 36.1209 | 0 | 0 | 0 | 0 | 0 | 232.2491 | 0 | 563.6081 | 44.19% | 25 | 0 | 28.839 | 46.14% | 36.1209
3807 | 817 | 837 | 147 | 8.4 | 25.6 | 0 | 0 | 0 | 217.3717 | 60.2482 | 0 | 24.5535 | 35.6947 | 0 | 0 | 0 | 0 | 0 | 217.3717 | 0 | 780.9798 | 61.23% | 24.5535 | 0 | 51.0246 | 81.64% | 35.6947
3808 | 769 | 686 | 136 | 8.3 | 25.3 | 0 | 0 | 0 | 195.4648 | 41.6269 | 7.4494 | 5.7832 | 35.8438 | 0 | 0 | 0 | 0 | 0 | 195.4648 | 0 | 976.4446 | 76.55% | 5.7832 | 0 | 56.25 | 90% | 35.8438
3809 | 681 | 500 | 124 | 8 | 24.4 | 0 | 0 | 0 | 160.2762 | 34.2301 | 0 | 0 | 34.2301 | 0 | 0 | 0 | 0 | 0 | 160.2762 | 0 | 1136.7208 | 89.12% | 0 | 1.8477 | 54.2051 | 86.73% | 36.0777
3810 | 519 | 295 | 101 | 7.3 | 22.7 | 0 | 0 | 0 | 0 | 15.9892 | 0 | 0 | 15.9892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1136.7208 | 89.12% | 0 | 21.2654 | 30.67 | 49.07% | 37.2546
3811 | 211 | 100 | 56 | 6.6 | 20.8 | 0 | 0 | 0 | 0 | 2.8747 | 0 | 0 | 2.8747 | 0 | 0 | 0 | 56.0098 | 20.4924 | 0 | 56.0098 | 1080.711 | 84.73% | 0 | 13.7886 | 15.4098 | 24.66% | 37.1557
3812 | 2 | 5 | 4 | 5.6 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4546 | 35.004 | 0 | 89.4546 | 991.2564 | 77.71% | 0 | 0 | 15.4098 | 24.66% | 35.004
3813 | 0 | 0 | 0 | 5 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8836 | 32.6322 | 0 | 83.8836 | 907.3728 | 71.14% | 0 | 0 | 15.4098 | 24.66% | 32.6322
3814 | 0 | 0 | 0 | 4.4 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9592 | 30.9484 | 0 | 79.9592 | 827.4136 | 64.87% | 0 | 0 | 15.4098 | 24.66% | 30.9484
3815 | 0 | 0 | 0 | 3.2 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.869 | 29.624 | 0 | 76.869 | 750.5446 | 58.84% | 0 | 0 | 15.4098 | 24.66% | 29.624
3816 | 0 | 0 | 0 | 1.9 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.9541 | 28.819 | 0 | 74.9541 | 675.5905 | 52.97% | 0 | 0 | 15.4098 | 24.66% | 28.819
3817 | 0 | 0 | 0 | 1.4 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9209 | 28.3789 | 0 | 73.9209 | 601.6696 | 47.17% | 0 | 0 | 15.4098 | 24.66% | 28.3789
3818 | 0 | 0 | 0 | 1.1 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2536 | 28.0934 | 0 | 73.2536 | 528.4161 | 41.43% | 0 | 0 | 15.4098 | 24.66% | 28.0934
3819 | 0 | 0 | 0 | 1.1 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2463 | 28.0976 | 0 | 73.2463 | 455.1698 | 35.69% | 0 | 0 | 15.4098 | 24.66% | 28.0976
3820 | 0 | 0 | 0 | 1 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2116 | 28.1171 | 0 | 73.2116 | 381.9582 | 29.95% | 0 | 0 | 15.4098 | 24.66% | 28.1171
3821 | 0 | 1 | 1 | 0.6 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7948 | 29.6727 | 0 | 76.7948 | 305.1633 | 23.92% | 0 | 0 | 15.4098 | 24.66% | 29.6727
3822 | 3 | 34 | 33 | 0.4 | 15.4 | 0 | 0 | 0 | 0 | 1.1983 | 0 | 0 | 1.1983 | 0 | 0 | 0 | 78.9571 | 30.622 | 0 | 78.9571 | 226.2062 | 17.73% | 0 | 0 | 15.4098 | 24.66% | 31.8203
3823 | 169 | 198 | 141 | 2 | 18 | 0 | 0 | 0 | 0 | 6.7164 | 0 | 0 | 6.7164 | 0 | 0 | 0 | 71.1949 | 27.1595 | 0 | 71.1949 | 155.0113 | 12.15% | 0 | 0 | 15.4098 | 24.66% | 33.8759
3824 | 72 | 342 | 303 | 2.1 | 19.7 | 0 | 0 | 0 | 0 | 18.2604 | 0 | 0 | 18.2604 | 0 | 0 | 0 | 47.2986 | 16.7714 | 0 | 47.2986 | 107.7127 | 8.445% | 0 | 0 | 15.4098 | 24.66% | 35.0318
3825 | 28 | 342 | 319 | 1.9 | 20.7 | 0 | 0 | 0 | 0 | 20.736 | 0 | 0 | 20.736 | 0 | 0 | 0 | 42.7786 | 14.7944 | 0 | 42.7786 | 64.9341 | 5.091% | 0 | 0 | 15.4098 | 24.66% | 35.5304
3826 | 165 | 454 | 311 | 1.7 | 22 | 0 | 0 | 0 | 0 | 27.8835 | 0 | 0 | 27.8835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.9341 | 5.091% | 0 | 8.2764 | 6.25 | 10% | 36.1599
3827 | 441 | 731 | 315 | 1.2 | 24.4 | 0 | 0 | 0 | 0 | 35.7908 | 9.9064 | 0 | 35.7908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.9341 | 5.091% | 0 | 0 | 6.25 | 10% | 35.7908
3828 | 516 | 855 | 344 | 2.2 | 26.6 | 0 | 0 | 0 | 136.6883 | 34.1182 | 21.3242 | 0 | 34.1182 | 0 | 0 | 0 | 0 | 0 | 136.6883 | 0 | 201.6224 | 15.81% | 0 | 0 | 6.25 | 10% | 34.1182
3829 | 750 | 978 | 242 | 4 | 27.4 | 0 | 0 | 0 | 208.4721 | 33.1559 | 33.0896 | 0 | 33.1559 | 0 | 0 | 0 | 0 | 0 | 208.4721 | 0 | 410.0945 | 32.15% | 0 | 0 | 6.25 | 10% | 33.1559
3830 | 768 | 916 | 195 | 4.4 | 28.3 | 0 | 0 | 0 | 211.8691 | 49.2115 | 13.7373 | 16.3119 | 32.8996 | 0 | 0 | 0 | 0 | 0 | 211.8691 | 0 | 621.9636 | 48.76% | 16.3119 | 0 | 20.9888 | 33.58% | 32.8996
3831 | 763 | 838 | 188 | 5.1 | 28.3 | 0 | 0 | 0 | 204.5601 | 57.8341 | 0.46185 | 25 | 32.8341 | 0 | 0 | 0 | 0 | 0 | 204.5601 | 0 | 826.5237 | 64.8% | 25 | 0 | 43.5778 | 69.72% | 32.8341
3832 | 715 | 677 | 164 | 5.2 | 28.1 | 0 | 0 | 0 | 182.9328 | 47.3352 | 0 | 14.0248 | 33.3104 | 0 | 0 | 0 | 0 | 0 | 182.9328 | 0 | 1009.4565 | 79.14% | 14.0248 | 0 | 56.25 | 90% | 33.3104
3833 | 647 | 495 | 134 | 5.4 | 27.4 | 0 | 0 | 0 | 153.4913 | 33.0873 | 0 | 0 | 33.0873 | 0 | 0 | 0 | 0 | 0 | 153.4913 | 0 | 1162.9478 | 91.18% | 0 | 1.2217 | 54.8979 | 87.84% | 34.309
3834 | 468 | 284 | 108 | 5.5 | 25.7 | 0 | 0 | 0 | 0 | 15.3228 | 0 | 0 | 15.3228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1162.9478 | 91.18% | 0 | 20.9026 | 31.7643 | 50.82% | 36.2254
3835 | 169 | 90 | 53 | 4.9 | 23.3 | 0 | 0 | 0 | 0 | 2.6414 | 0 | 0 | 2.6414 | 0 | 0 | 0 | 57.9542 | 21.2246 | 0 | 57.9542 | 1104.9936 | 86.63% | 0 | 13.3093 | 17.0345 | 27.26% | 37.1752
3836 | 6 | 5 | 5 | 3 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1211 | 34.7394 | 0 | 89.1211 | 1015.8726 | 79.64% | 0 | 0 | 17.0345 | 27.26% | 34.7394
3837 | 0 | 0 | 0 | 1.8 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4824 | 32.8286 | 0 | 84.4824 | 931.3902 | 73.02% | 0 | 0 | 17.0345 | 27.26% | 32.8286
3838 | 0 | 0 | 0 | 0.7 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0529 | 30.9512 | 0 | 80.0529 | 851.3373 | 66.74% | 0 | 0 | 17.0345 | 27.26% | 30.9512
3839 | 0 | 0 | 0 | 0.5 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5581 | 29.8914 | 0 | 77.5581 | 773.7792 | 60.66% | 0 | 0 | 17.0345 | 27.26% | 29.8914
3840 | 0 | 0 | 0 | 1 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.39 | 29.3817 | 0 | 76.39 | 697.3892 | 54.68% | 0 | 0 | 17.0345 | 27.26% | 29.3817
3841 | 0 | 0 | 0 | 0.8 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1844 | 29.3148 | 0 | 76.1844 | 621.2048 | 48.7% | 0 | 0 | 17.0345 | 27.26% | 29.3148
3842 | 0 | 0 | 0 | 1.2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0214 | 30.1142 | 0 | 78.0214 | 543.1834 | 42.59% | 0 | 0 | 17.0345 | 27.26% | 30.1142
3843 | 0 | 0 | 0 | 1.2 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0003 | 32.7116 | 0 | 84.0003 | 459.183 | 36% | 0 | 0 | 17.0345 | 27.26% | 32.7116
3844 | 0 | 0 | 0 | 0.6 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5434 | 36.022 | 0 | 91.5434 | 367.6397 | 28.82% | 0 | 0 | 17.0345 | 27.26% | 36.022
3845 | 0 | 1 | 1 | 1.4 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0472 | 38.8311 | 0 | 98.0472 | 269.5925 | 21.14% | 0 | 0 | 17.0345 | 27.26% | 38.8311
3846 | 44 | 51 | 45 | 1.3 | 17.7 | 0 | 0 | 0 | 0 | 1.7649 | 0 | 0 | 1.7649 | 0 | 0 | 0 | 97.9021 | 38.7361 | 0 | 97.9021 | 171.6904 | 13.46% | 0 | 0 | 17.0345 | 27.26% | 40.5009
3847 | 514 | 240 | 70 | 0.7 | 21.3 | 0 | 0 | 0 | 0 | 3.6547 | 0 | 0 | 3.6547 | 0 | 0 | 0 | 96.7506 | 38.0105 | 0 | 96.7506 | 74.9398 | 5.875% | 0 | 0 | 17.0345 | 27.26% | 41.6652
3848 | 809 | 472 | 71 | 0.6 | 24.6 | 0 | 0 | 0 | 0 | 14.07 | 0 | 0 | 14.07 | 0 | 0 | 0 | 74.9398 | 28.4239 | 0 | 74.9398 | 0 | 0% | 0 | 0 | 17.0345 | 27.26% | 42.4939
3849 | 873 | 662 | 83 | 3 | 25.6 | 0 | 0 | 0 | 0 | 33.3232 | 0 | 0 | 33.3232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 9.7445 | 6.25 | 10% | 43.0677
3850 | 916 | 827 | 88 | 4.8 | 26.9 | 0 | 0 | 0 | 0 | 43.4924 | 5.2618 | 0 | 43.4924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 43.4924
3851 | 950 | 951 | 88 | 4 | 27.5 | 0 | 0 | 0 | 0 | 42.4841 | 17.0567 | 0 | 42.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 42.4841
3852 | 953 | 1013 | 92 | 2.5 | 28.2 | 0 | 0 | 0 | 267.3428 | 41.6499 | 22.9229 | 0 | 41.6499 | 0 | 0 | 0 | 0 | 0 | 267.3428 | 0 | 267.3428 | 20.96% | 0 | 0 | 6.25 | 10% | 41.6499
3853 | 934 | 1016 | 106 | 3.9 | 28.7 | 0 | 0 | 0 | 0 | 44.0008 | 23.7022 | 2.6253 | 41.3755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267.3428 | 20.96% | 2.6253 | 0 | 8.6221 | 13.8% | 41.3755
3854 | 911 | 965 | 116 | 5.1 | 28.7 | 0 | 0 | 0 | 199.334 | 66.1081 | 0.28194 | 25 | 41.1081 | 0 | 0 | 0 | 0 | 0 | 199.334 | 0 | 466.6769 | 36.59% | 25 | 0 | 31.2111 | 49.94% | 41.1081
3855 | 887 | 853 | 105 | 4.3 | 28.8 | 0 | 0 | 0 | 241.8213 | 59.1867 | 0 | 18.6468 | 40.5399 | 0 | 0 | 0 | 0 | 0 | 241.8213 | 0 | 708.4981 | 55.55% | 18.6468 | 0 | 48.0596 | 76.9% | 40.5399
3856 | 854 | 705 | 95 | 5.3 | 28.7 | 0 | 0 | 0 | 222.1565 | 49.209 | 0 | 9.0646 | 40.1444 | 0 | 0 | 0 | 0 | 0 | 222.1565 | 0 | 930.6547 | 72.96% | 9.0646 | 0 | 56.25 | 90% | 40.1444
3857 | 801 | 522 | 80 | 6 | 28.1 | 0 | 0 | 0 | 194.45 | 35.1865 | 0 | 0 | 35.1865 | 0 | 0 | 0 | 0 | 0 | 194.45 | 0 | 1125.1047 | 88.21% | 0 | 5.5066 | 50.1556 | 80.25% | 40.6931
3858 | 644 | 316 | 76 | 5.8 | 27.6 | 0 | 0 | 0 | 134.8108 | 16.5401 | 0 | 0 | 16.5401 | 0 | 0 | 0 | 0 | 0 | 134.8108 | 0 | 1259.9155 | 98.78% | 0 | 24.7812 | 22.7295 | 36.37% | 41.3212
3859 | 418 | 127 | 49 | 4.6 | 26.4 | 0 | 0 | 0 | 0 | 2.5883 | 0 | 0 | 2.5883 | 0 | 0 | 0 | 87.5252 | 33.6555 | 0 | 87.5252 | 1172.3903 | 91.92% | 0 | 3.9103 | 18.4018 | 29.44% | 40.1541
3860 | 25 | 9 | 7 | 2.8 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.522 | 36.8033 | 0 | 94.522 | 1077.8683 | 84.5% | 0 | 0 | 18.4018 | 29.44% | 36.8033
3861 | 0 | 0 | 0 | 1.9 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5699 | 35.2226 | 0 | 90.5699 | 987.2984 | 77.4% | 0 | 0 | 18.4018 | 29.44% | 35.2226
3862 | 0 | 0 | 0 | 1.3 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2916 | 33.5695 | 0 | 86.2916 | 901.0068 | 70.64% | 0 | 0 | 18.4018 | 29.44% | 33.5695
3863 | 0 | 0 | 0 | 0.9 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3075 | 32.3105 | 0 | 83.3075 | 817.6992 | 64.11% | 0 | 0 | 18.4018 | 29.44% | 32.3105
3864 | 0 | 0 | 0 | 1 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9517 | 31.7465 | 0 | 81.9517 | 735.7475 | 57.68% | 0 | 0 | 18.4018 | 29.44% | 31.7465
3865 | 0 | 0 | 0 | 1.8 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6528 | 31.6225 | 0 | 81.6528 | 654.0947 | 51.28% | 0 | 0 | 18.4018 | 29.44% | 31.6225
3866 | 0 | 0 | 0 | 0.9 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6329 | 32.096 | 0 | 82.6329 | 571.4618 | 44.8% | 0 | 0 | 18.4018 | 29.44% | 32.096
3867 | 0 | 0 | 0 | 1.8 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1761 | 34.4942 | 0 | 88.1761 | 483.2857 | 37.89% | 0 | 0 | 18.4018 | 29.44% | 34.4942
3868 | 0 | 0 | 0 | 0.6 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9897 | 37.9133 | 0 | 95.9897 | 387.2961 | 30.36% | 0 | 0 | 18.4018 | 29.44% | 37.9133
3869 | 0 | 1 | 1 | 0.8 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8064 | 40.877 | 0 | 102.8064 | 284.4896 | 22.3% | 0 | 0 | 18.4018 | 29.44% | 40.877
3870 | 339 | 75 | 26 | 0.7 | 18.7 | 0 | 0 | 0 | 0 | 0.84502 | 0 | 0 | 0.84502 | 0 | 0 | 0 | 104.0856 | 41.3522 | 0 | 104.0856 | 180.404 | 14.14% | 0 | 0 | 18.4018 | 29.44% | 42.1972
3871 | 689 | 265 | 49 | 1.1 | 22.2 | 0 | 0 | 0 | 0 | 2.5994 | 0 | 0 | 2.5994 | 0 | 0 | 0 | 102.6963 | 40.4989 | 0 | 102.6963 | 77.7077 | 6.092% | 0 | 0 | 18.4018 | 29.44% | 43.0983
3872 | 831 | 473 | 60 | 3.1 | 24.4 | 0 | 0 | 0 | 0 | 13.9511 | 0 | 0 | 13.9511 | 0 | 0 | 0 | 77.7077 | 29.6208 | 0 | 77.7077 | 0 | 0% | 0 | 0 | 18.4018 | 29.44% | 43.5718
3873 | 905 | 666 | 66 | 3.4 | 26.4 | 0 | 0 | 0 | 219.1404 | 33.0947 | 0 | 0 | 33.0947 | 0 | 0 | 0 | 0 | 0 | 219.1404 | 0 | 219.1404 | 17.18% | 0 | 10.9799 | 6.25 | 10% | 44.0746
3874 | 948 | 831 | 68 | 2.7 | 27.2 | 0 | 0 | 0 | 247.7342 | 44.0286 | 3.9148 | 0 | 44.0286 | 0 | 0 | 0 | 0 | 0 | 247.7342 | 0 | 466.8747 | 36.6% | 0 | 0 | 6.25 | 10% | 44.0286
3875 | 956 | 943 | 75 | 3.1 | 28.5 | 0 | 0 | 0 | 260.4966 | 42.6053 | 15.6222 | 0 | 42.6053 | 0 | 0 | 0 | 0 | 0 | 260.4966 | 0 | 727.3712 | 57.03% | 0 | 0 | 6.25 | 10% | 42.6053
3876 | 955 | 1005 | 83 | 4.7 | 28.9 | 0 | 0 | 0 | 266.3086 | 41.8616 | 23.7426 | 0 | 41.8616 | 0 | 0 | 0 | 0 | 0 | 266.3086 | 0 | 993.6798 | 77.9% | 0 | 0 | 6.25 | 10% | 41.8616
3877 | 950 | 1014 | 90 | 4.9 | 29.4 | 0 | 0 | 0 | 107.945 | 49.5648 | 18.5704 | 7.9093 | 41.6555 | 0 | 0 | 0 | 0 | 0 | 107.945 | 0 | 1101.6249 | 86.37% | 7.9093 | 0 | 13.3966 | 21.43% | 41.6555
3878 | 935 | 962 | 90 | 3.1 | 29.7 | 0 | 0 | 0 | 0 | 64.683 | 0 | 23.1167 | 41.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101.6249 | 86.37% | 23.1167 | 0 | 34.2839 | 54.85% | 41.5663
3879 | 909 | 857 | 90 | 3.9 | 30.2 | 0 | 0 | 0 | 0 | 58.9536 | 0 | 17.7995 | 41.1541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101.6249 | 86.37% | 17.7995 | 0 | 50.3668 | 80.59% | 41.1541
3880 | 768 | 691 | 140 | 4.7 | 30.5 | 0 | 0 | 0 | 0 | 47.7391 | 0 | 6.5112 | 41.2279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101.6249 | 86.37% | 6.5112 | 0 | 56.25 | 90% | 41.2279
3881 | 720 | 519 | 122 | 4.7 | 30 | 0 | 0 | 0 | 173.8853 | 34.585 | 0 | 0 | 34.585 | 0 | 0 | 0 | 0 | 0 | 173.8853 | 0 | 1275.5102 | 100% | 0 | 7.0301 | 48.4695 | 77.55% | 41.6151
3882 | 657 | 315 | 69 | 4.3 | 28.9 | 0 | 0 | 0 | 0 | 16.208 | 0 | 0 | 16.208 | 0 | 0 | 0 | 68.7651 | 25.4963 | 0 | 68.7651 | 1206.7451 | 94.61% | 0 | 0 | 48.4695 | 77.55% | 41.7042
3883 | 310 | 108 | 52 | 4.1 | 24.9 | 0 | 0 | 0 | 0 | 2.688 | 0 | 0 | 2.688 | 0 | 0 | 0 | 96.8746 | 37.7739 | 0 | 96.8746 | 1109.8705 | 87.01% | 0 | 0 | 48.4695 | 77.55% | 40.4619
3884 | 9 | 7 | 6 | 5.8 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1719 | 37.3924 | 0 | 95.1719 | 1014.6986 | 79.55% | 0 | 0 | 48.4695 | 77.55% | 37.3924
3885 | 0 | 0 | 0 | 7.9 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1758 | 35.7867 | 0 | 91.1758 | 923.5229 | 72.4% | 0 | 0 | 48.4695 | 77.55% | 35.7867
3886 | 0 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1851 | 34.0806 | 0 | 87.1851 | 836.3378 | 65.57% | 0 | 0 | 48.4695 | 77.55% | 34.0806
3887 | 0 | 0 | 0 | 7.4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8783 | 32.6726 | 0 | 83.8783 | 752.4595 | 58.99% | 0 | 0 | 48.4695 | 77.55% | 32.6726
3888 | 0 | 0 | 0 | 6.9 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0298 | 32.3314 | 0 | 83.0298 | 669.4298 | 52.48% | 0 | 0 | 48.4695 | 77.55% | 32.3314
3889 | 0 | 0 | 0 | 6.6 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.177 | 35.8817 | 0 | 91.177 | 578.2528 | 45.34% | 3.6562 | 0 | 51.7731 | 82.84% | 32.2255
3890 | 0 | 0 | 0 | 5.1 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1673 | 32.8578 | 0 | 84.1673 | 494.0855 | 38.74% | 0 | 0 | 51.7731 | 82.84% | 32.8578
3891 | 0 | 0 | 0 | 4.7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.283 | 35.082 | 0 | 89.283 | 404.8024 | 31.74% | 0 | 0 | 51.7731 | 82.84% | 35.082
3892 | 0 | 0 | 0 | 5.3 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0762 | 38.4996 | 0 | 97.0762 | 307.7262 | 24.13% | 0 | 0 | 51.7731 | 82.84% | 38.4996
3893 | 0 | 1 | 1 | 4.1 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6178 | 41.3546 | 0 | 103.6178 | 204.1085 | 16% | 0 | 0 | 51.7731 | 82.84% | 41.3546
3894 | 9 | 42 | 41 | 3.5 | 15.5 | 0 | 0 | 0 | 0 | 1.5909 | 0 | 0 | 1.5909 | 0 | 0 | 0 | 102.8201 | 40.9809 | 0 | 102.8201 | 101.2884 | 7.941% | 0 | 0 | 51.7731 | 82.84% | 42.5719
3895 | 495 | 258 | 100 | 4.7 | 17 | 0 | 0 | 0 | 0 | 5.2399 | 0 | 0 | 5.2399 | 0 | 0 | 0 | 96.2603 | 38.0618 | 0 | 96.2603 | 5.0281 | 0.3942% | 0 | 0 | 51.7731 | 82.84% | 43.3016
3896 | 495 | 443 | 203 | 5.2 | 18 | 0 | 0 | 0 | 0 | 18.5091 | 0 | 0 | 18.5091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0281 | 0.3942% | 0 | 25 | 24.1048 | 38.57% | 43.5091
3897 | 358 | 499 | 256 | 5.3 | 18.9 | 0 | 0 | 0 | 0 | 28.4096 | 0 | 0 | 28.4096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0281 | 0.3942% | 0 | 16.1329 | 6.25 | 10% | 44.5425
3898 | 708 | 752 | 175 | 5.1 | 20.2 | 0 | 0 | 0 | 178.374 | 44.4868 | 1.7381 | 0 | 44.4868 | 0 | 0 | 0 | 0 | 0 | 178.374 | 0 | 183.4022 | 14.38% | 0 | 0 | 6.25 | 10% | 44.4868
3899 | 924 | 938 | 106 | 5.1 | 21.2 | 0 | 0 | 0 | 249.3934 | 43.0022 | 17.987 | 0 | 43.0022 | 0 | 0 | 0 | 0 | 0 | 249.3934 | 0 | 432.7956 | 33.93% | 0 | 0 | 6.25 | 10% | 43.0022
3900 | 943 | 999 | 99 | 5.7 | 21.8 | 0 | 0 | 0 | 261.6712 | 42.2891 | 25.6837 | 0 | 42.2891 | 0 | 0 | 0 | 0 | 0 | 261.6712 | 0 | 694.4667 | 54.45% | 0 | 0 | 6.25 | 10% | 42.2891
3901 | 942 | 1006 | 101 | 6.1 | 22.7 | 0 | 0 | 0 | 264.742 | 43.6908 | 26.7862 | 1.5966 | 42.0942 | 0 | 0 | 0 | 0 | 0 | 264.742 | 0 | 959.2087 | 75.2% | 1.5966 | 0 | 7.6927 | 12.31% | 42.0942
3902 | 930 | 956 | 102 | 6.5 | 23.2 | 0 | 0 | 0 | 120.0583 | 67.097 | 1.4216 | 25 | 42.097 | 0 | 0 | 0 | 0 | 0 | 120.0583 | 0 | 1079.267 | 84.61% | 25 | 0 | 30.2817 | 48.45% | 42.097
3903 | 900 | 858 | 100 | 6 | 23.7 | 0 | 0 | 0 | 0 | 61.324 | 0 | 19.7771 | 41.5468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1079.267 | 84.61% | 19.7771 | 0 | 48.1515 | 77.04% | 41.5468
3904 | 850 | 705 | 97 | 6.4 | 23.2 | 0 | 0 | 0 | 0 | 50.3482 | 0 | 8.9629 | 41.3853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1079.267 | 84.61% | 8.9629 | 0 | 56.25 | 90% | 41.3853
3905 | 784 | 518 | 84 | 6.3 | 22.5 | 0 | 0 | 0 | 189.5905 | 35.5993 | 0 | 0 | 35.5993 | 0 | 0 | 0 | 0 | 0 | 189.5905 | 0 | 1268.8576 | 99.48% | 0 | 6.0409 | 49.5644 | 79.3% | 41.6401
3906 | 653 | 312 | 68 | 6.7 | 21.5 | 0 | 0 | 0 | 0 | 16.6138 | 0 | 0 | 16.6138 | 0 | 0 | 0 | 67.4017 | 25.3675 | 0 | 67.4017 | 1201.4558 | 94.19% | 0 | 0 | 49.5644 | 79.3% | 41.9814
3907 | 373 | 115 | 42 | 6.8 | 19.8 | 0 | 0 | 0 | 0 | 2.2344 | 0 | 0 | 2.2344 | 0 | 0 | 0 | 97.9782 | 38.6425 | 0 | 97.9782 | 1103.4776 | 86.51% | 0 | 0 | 49.5644 | 79.3% | 40.877
3908 | 13 | 6 | 5 | 6.4 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.9082 | 0 | 38.2653 | 1065.2123 | 83.51% | 0 | 24.6611 | 22.2711 | 35.63% | 37.5693
3909 | 0 | 0 | 0 | 5.3 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5913 | 36.0234 | 0 | 91.5913 | 973.6211 | 76.33% | 0 | 0 | 22.2711 | 35.63% | 36.0234
3910 | 0 | 0 | 0 | 4 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5295 | 30.7803 | 0 | 79.5295 | 894.0916 | 70.1% | 0 | 3.4452 | 18.4582 | 29.53% | 34.2254
3911 | 0 | 0 | 0 | 3.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5953 | 32.9832 | 0 | 84.5953 | 809.4963 | 63.46% | 0 | 0 | 18.4582 | 29.53% | 32.9832
3912 | 0 | 0 | 0 | 3.1 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2929 | 32.4539 | 0 | 83.2929 | 726.2034 | 56.93% | 0 | 0 | 18.4582 | 29.53% | 32.4539
3913 | 0 | 0 | 0 | 3.6 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9077 | 32.2952 | 0 | 82.9077 | 643.2957 | 50.43% | 0 | 0 | 18.4582 | 29.53% | 32.2952
3914 | 0 | 0 | 0 | 1.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2191 | 32.8843 | 0 | 84.2191 | 559.0766 | 43.83% | 0 | 0 | 18.4582 | 29.53% | 32.8843
3915 | 0 | 0 | 0 | 1.5 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2041 | 35.0722 | 0 | 89.2041 | 469.8725 | 36.84% | 0 | 0 | 18.4582 | 29.53% | 35.0722
3916 | 0 | 0 | 0 | 2 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1954 | 38.5428 | 0 | 97.1954 | 372.6771 | 29.22% | 0 | 0 | 18.4582 | 29.53% | 38.5428
3917 | 0 | 1 | 1 | 1.7 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.5012 | 41.2906 | 0 | 103.5012 | 269.1759 | 21.1% | 0 | 0 | 18.4582 | 29.53% | 41.2906
3918 | 7 | 37 | 36 | 1.4 | 15.5 | 0 | 0 | 0 | 0 | 1.3448 | 0 | 0 | 1.3448 | 0 | 0 | 0 | 103.002 | 41.0599 | 0 | 103.002 | 166.1739 | 13.03% | 0 | 0 | 18.4582 | 29.53% | 42.4047
3919 | 117 | 147 | 109 | 2.1 | 18.1 | 0 | 0 | 0 | 0 | 5.5037 | 0 | 0 | 5.5037 | 0 | 0 | 0 | 95.4869 | 37.6684 | 0 | 95.4869 | 70.687 | 5.542% | 0 | 0 | 18.4582 | 29.53% | 43.1721
3920 | 479 | 424 | 182 | 5.3 | 20.7 | 0 | 0 | 0 | 0 | 16.9319 | 0 | 0 | 16.9319 | 0 | 0 | 0 | 70.687 | 26.821 | 0 | 70.687 | 0 | 0% | 0 | 0 | 18.4582 | 29.53% | 43.7529
3921 | 695 | 630 | 164 | 6.3 | 21.9 | 0 | 0 | 0 | 0 | 33.5632 | 0 | 0 | 33.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 11.0308 | 6.25 | 10% | 44.5941
3922 | 741 | 796 | 194 | 6.8 | 23.5 | 0 | 0 | 0 | 135.3417 | 48.7121 | 0 | 3.898 | 44.8141 | 0 | 0 | 0 | 0 | 0 | 135.3417 | 0 | 135.3417 | 10.61% | 3.898 | 0 | 9.7721 | 15.64% | 44.8141
3923 | 828 | 918 | 162 | 6.8 | 25 | 0 | 0 | 0 | 219.7131 | 43.5384 | 15.8408 | 0 | 43.5384 | 0 | 0 | 0 | 0 | 0 | 219.7131 | 0 | 355.0548 | 27.84% | 0 | 0 | 9.7721 | 15.64% | 43.5384
3924 | 845 | 982 | 162 | 6.8 | 25.9 | 0 | 0 | 0 | 231.364 | 42.8225 | 23.1436 | 0 | 42.8225 | 0 | 0 | 0 | 0 | 0 | 231.364 | 0 | 586.4188 | 45.98% | 0 | 0 | 9.7721 | 15.64% | 42.8225
3925 | 848 | 989 | 159 | 7.1 | 25.4 | 0 | 0 | 0 | 235.3943 | 64.5817 | 3.1317 | 21.8567 | 42.7251 | 0 | 0 | 0 | 0 | 0 | 235.3943 | 0 | 821.8131 | 64.43% | 21.8567 | 0 | 29.5209 | 47.23% | 42.7251
3926 | 856 | 944 | 143 | 6.9 | 25.4 | 0 | 0 | 0 | 236.2159 | 66.0459 | 0 | 23.3 | 42.7459 | 0 | 0 | 0 | 0 | 0 | 236.2159 | 0 | 1058.029 | 82.95% | 23.3 | 0 | 50.5738 | 80.92% | 42.7459
3927 | 810 | 839 | 152 | 6 | 25.2 | 0 | 0 | 0 | 217.4812 | 42.3086 | 17.3143 | 0 | 42.3086 | 0 | 0 | 0 | 0 | 0 | 217.4812 | 0 | 1275.5102 | 100% | 0 | 0 | 50.5738 | 80.92% | 42.3086
3928 | 715 | 685 | 170 | 5.7 | 25.1 | 0 | 0 | 0 | 0 | 48.3525 | 0 | 6.282 | 42.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 6.282 | 0 | 56.25 | 90% | 42.0705
3929 | 545 | 475 | 167 | 5.8 | 24.1 | 0 | 0 | 0 | 0 | 31.9645 | 0 | 0 | 31.9645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 7.8011 | 47.6162 | 76.19% | 39.7656
3930 | 306 | 245 | 121 | 5.2 | 22.7 | 0 | 0 | 0 | 0 | 13.2144 | 0 | 0 | 13.2144 | 0 | 0 | 0 | 75.7379 | 28.8853 | 0 | 75.7379 | 1199.7723 | 94.06% | 0 | 0 | 47.6162 | 76.19% | 42.0997
3931 | 1 | 41 | 41 | 5.4 | 20.6 | 0 | 0 | 0 | 0 | 2.2048 | 0 | 0 | 2.2048 | 0 | 0 | 0 | 98.2268 | 38.6958 | 0 | 98.2268 | 1101.5455 | 86.36% | 0 | 0 | 47.6162 | 76.19% | 40.9006
3932 | 0 | 3 | 3 | 4.7 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.9705 | 37.7949 | 0 | 95.9705 | 1005.575 | 78.84% | 0 | 0 | 47.6162 | 76.19% | 37.7949
3933 | 0 | 0 | 0 | 4.2 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2095 | 36.2059 | 0 | 92.2095 | 913.3656 | 71.61% | 0 | 0 | 47.6162 | 76.19% | 36.2059
3934 | 0 | 0 | 0 | 3.1 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1615 | 34.4775 | 0 | 88.1615 | 825.204 | 64.7% | 0 | 0 | 47.6162 | 76.19% | 34.4775
3935 | 0 | 0 | 0 | 2.2 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0952 | 33.1712 | 0 | 85.0952 | 740.1088 | 58.02% | 0 | 0 | 47.6162 | 76.19% | 33.1712
3936 | 0 | 0 | 0 | 3.3 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.038 | 32.7088 | 0 | 84.038 | 656.0707 | 51.44% | 0 | 0 | 47.6162 | 76.19% | 32.7088
3937 | 0 | 0 | 0 | 3.1 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7822 | 30.0151 | 0 | 77.7822 | 578.2885 | 45.34% | 0 | 0 | 47.6162 | 76.19% | 30.0151
3938 | 0 | 0 | 0 | 3.5 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7994 | 33.0528 | 0 | 84.7994 | 493.4891 | 38.69% | 0 | 0 | 47.6162 | 76.19% | 33.0528
3939 | 0 | 0 | 0 | 3.2 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.909 | 35.2059 | 0 | 89.909 | 403.5801 | 31.64% | 0 | 0 | 47.6162 | 76.19% | 35.2059
3940 | 0 | 0 | 0 | 2.3 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4336 | 38.5052 | 0 | 97.4336 | 306.1466 | 24% | 0 | 0 | 47.6162 | 76.19% | 38.5052
3941 | 0 | 1 | 1 | 2.4 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3664 | 41.0845 | 0 | 103.3664 | 202.7802 | 15.9% | 0 | 0 | 47.6162 | 76.19% | 41.0845
3942 | 83 | 50 | 36 | 2.7 | 17.6 | 0 | 0 | 0 | 0 | 1.3321 | 0 | 0 | 1.3321 | 0 | 0 | 0 | 103.7766 | 41.2857 | 0 | 103.7766 | 99.0036 | 7.762% | 0 | 0 | 47.6162 | 76.19% | 42.6178
3943 | 455 | 233 | 88 | 2.2 | 18.9 | 0 | 0 | 0 | 0 | 4.4891 | 0 | 0 | 4.4891 | 0 | 0 | 0 | 99.0036 | 39.1426 | 0 | 99.0036 | 0 | 0% | 0 | 0 | 47.6162 | 76.19% | 43.6317
3944 | 672 | 443 | 108 | 2.6 | 20.7 | 0 | 0 | 0 | 0 | 14.7401 | 0 | 0 | 14.7401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 19.9479 | 31.92% | 39.74
3945 | 804 | 644 | 109 | 1.9 | 23.3 | 0 | 0 | 0 | 0 | 32.5514 | 7.1054e-15 | 0 | 32.5514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 12.3769 | 6.25 | 10% | 44.9283
3946 | 876 | 814 | 108 | 4 | 24.9 | 0 | 0 | 0 | 226.2791 | 48.1167 | 0 | 3.3541 | 44.7626 | 0 | 0 | 0 | 0 | 0 | 226.2791 | 0 | 226.2791 | 17.74% | 3.3541 | 0 | 9.2807 | 14.85% | 44.7626
3947 | 918 | 938 | 105 | 3 | 26.4 | 0 | 0 | 0 | 249.41 | 46.8161 | 11.5177 | 3.2792 | 43.537 | 0 | 0 | 0 | 0 | 0 | 249.41 | 0 | 475.6891 | 37.29% | 3.2792 | 0 | 12.2436 | 19.59% | 43.537
3948 | 935 | 1006 | 103 | 5.2 | 27.5 | 0 | 0 | 0 | 259.8006 | 66.1165 | 0 | 23.7034 | 42.4131 | 0 | 0 | 0 | 0 | 0 | 259.8006 | 0 | 735.4897 | 57.66% | 23.7034 | 0 | 33.661 | 53.86% | 42.4131
3949 | 934 | 1014 | 104 | 5.3 | 28.4 | 0 | 0 | 0 | 263.1331 | 67.2488 | 1.1206 | 25 | 42.2488 | 0 | 0 | 0 | 0 | 0 | 263.1331 | 0 | 998.6229 | 78.29% | 25 | 0 | 56.25 | 90% | 42.2488
3950 | 920 | 961 | 103 | 6 | 28.9 | 0 | 0 | 0 | 0 | 42.0385 | 24.379 | 0 | 42.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 998.6229 | 78.29% | 0 | 0 | 56.25 | 90% | 42.0385
3951 | 913 | 867 | 94 | 4.3 | 29.2 | 0 | 0 | 0 | 177.7302 | 41.4675 | 18.3661 | 0 | 41.4675 | 0 | 0 | 0 | 0 | 0 | 177.7302 | 0 | 1176.353 | 92.23% | 0 | 0 | 56.25 | 90% | 41.4675
3952 | 869 | 715 | 92 | 5.6 | 28.8 | 0 | 0 | 0 | 0 | 41.1249 | 8.7093 | 0 | 41.1249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1176.353 | 92.23% | 0 | 0 | 56.25 | 90% | 41.1249
3953 | 745 | 518 | 100 | 5.3 | 28 | 0 | 0 | 0 | 0 | 34.5192 | 0 | 0 | 34.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1176.353 | 92.23% | 0 | 6.2101 | 49.377 | 79% | 40.7293
3954 | 585 | 309 | 90 | 5.3 | 26.6 | 0 | 0 | 0 | 0 | 16.3884 | 0 | 0 | 16.3884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1176.353 | 92.23% | 0 | 24.249 | 22.5399 | 36.06% | 40.6374
3955 | 288 | 102 | 45 | 4.2 | 25.5 | 0 | 0 | 0 | 0 | 2.2796 | 0 | 0 | 2.2796 | 0 | 0 | 0 | 96.4513 | 37.5389 | 0 | 96.4513 | 1079.9018 | 84.66% | 0 | 0 | 22.5399 | 36.06% | 39.8185
3956 | 19 | 9 | 8 | 3.7 | 23.4 | 0 | 0 | 0 | 0 | 0.035418 | 0 | 0 | 0.035418 | 0 | 0 | 0 | 77.6512 | 29.6627 | 0 | 77.6512 | 1002.2505 | 78.58% | 0 | 7.5035 | 14.2354 | 22.78% | 37.2016
3957 | 0 | 0 | 0 | 1.7 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7554 | 35.8535 | 0 | 91.7554 | 910.4951 | 71.38% | 0 | 0 | 14.2354 | 22.78% | 35.8535
3958 | 0 | 0 | 0 | 0.9 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4403 | 33.6851 | 0 | 86.4403 | 824.0548 | 64.61% | 0 | 0 | 14.2354 | 22.78% | 33.6851
3959 | 0 | 0 | 0 | 0.3 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9262 | 32.2033 | 0 | 82.9262 | 741.1286 | 58.1% | 0 | 0 | 14.2354 | 22.78% | 32.2033
3960 | 0 | 0 | 0 | 0.8 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5573 | 31.6114 | 0 | 81.5573 | 659.5714 | 51.71% | 0 | 0 | 14.2354 | 22.78% | 31.6114
3961 | 0 | 0 | 0 | 1.9 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3413 | 31.0807 | 0 | 80.3413 | 579.2301 | 45.41% | 0 | 0 | 14.2354 | 22.78% | 31.0807
3962 | 0 | 0 | 0 | 1.9 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3418 | 30.7033 | 0 | 79.3418 | 499.8883 | 39.19% | 0 | 0 | 14.2354 | 22.78% | 30.7033
3963 | 0 | 0 | 0 | 1.8 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0597 | 30.6184 | 0 | 79.0597 | 420.8286 | 32.99% | 0 | 0 | 14.2354 | 22.78% | 30.6184
3964 | 0 | 0 | 0 | 1.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9331 | 31.4582 | 0 | 80.9331 | 339.8955 | 26.65% | 0 | 0 | 14.2354 | 22.78% | 31.4582
3965 | 0 | 1 | 1 | 1.8 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7302 | 33.9901 | 0 | 86.7302 | 253.1653 | 19.85% | 0 | 0 | 14.2354 | 22.78% | 33.9901
3966 | 384 | 78 | 25 | 1.3 | 16 | 0 | 0 | 0 | 0 | 0.81108 | 0 | 0 | 0.81108 | 0 | 0 | 0 | 91.3291 | 35.97 | 0 | 91.3291 | 161.8361 | 12.69% | 0 | 0 | 14.2354 | 22.78% | 36.781
3967 | 729 | 272 | 45 | 0.6 | 19.9 | 0 | 0 | 0 | 0 | 2.3652 | 0 | 0 | 2.3652 | 0 | 0 | 0 | 93.1721 | 36.562 | 0 | 93.1721 | 68.664 | 5.383% | 0 | 0 | 14.2354 | 22.78% | 38.9272
3968 | 860 | 482 | 56 | 1 | 22.4 | 0 | 0 | 0 | 0 | 13.7268 | 0 | 0 | 13.7268 | 0 | 0 | 0 | 68.664 | 25.8647 | 0 | 68.664 | 0 | 0% | 0 | 0 | 14.2354 | 22.78% | 39.5915
3969 | 926 | 678 | 62 | 1.4 | 24.3 | 0 | 0 | 0 | 44.2151 | 32.8552 | 0 | 0 | 32.8552 | 0 | 0 | 0 | 0 | 0 | 44.2151 | 0 | 44.2151 | 3.466% | 0 | 7.2153 | 6.25 | 10% | 40.0706
3970 | 962 | 842 | 66 | 2.4 | 26.6 | 0 | 0 | 0 | 0 | 40.2321 | 7.8865 | 0 | 40.2321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.2151 | 3.466% | 0 | 0 | 6.25 | 10% | 40.2321
3971 | 970 | 957 | 75 | 5.1 | 27.7 | 0 | 0 | 0 | 0 | 39.072 | 20.8889 | 0 | 39.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.2151 | 3.466% | 0 | 0 | 6.25 | 10% | 39.072
3972 | 965 | 1025 | 90 | 5 | 27.9 | 0 | 0 | 0 | 0 | 37.3214 | 29.528 | 0 | 37.3214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.2151 | 3.466% | 0 | 0 | 6.25 | 10% | 37.3214
3973 | 963 | 1028 | 87 | 4.2 | 28.4 | 0 | 0 | 0 | 272.8567 | 36.3396 | 32.0962 | 0 | 36.3396 | 0 | 0 | 0 | 0 | 0 | 272.8567 | 0 | 317.0718 | 24.86% | 0 | 0 | 6.25 | 10% | 36.3396
3974 | 950 | 975 | 86 | 3.1 | 28.8 | 0 | 0 | 0 | 267.8845 | 60.9858 | 4.4721 | 25 | 35.9858 | 0 | 0 | 0 | 0 | 0 | 267.8845 | 0 | 584.9563 | 45.86% | 25 | 0 | 28.839 | 46.14% | 35.9858
3975 | 927 | 869 | 82 | 4.2 | 28.4 | 0 | 0 | 0 | 253.7844 | 52.9271 | 7.0454 | 17.075 | 35.8521 | 0 | 0 | 0 | 0 | 0 | 253.7844 | 0 | 838.7407 | 65.76% | 17.075 | 0 | 44.2673 | 70.83% | 35.8521
3976 | 889 | 718 | 78 | 3.4 | 28.6 | 0 | 0 | 0 | 233.9384 | 49.221 | 0 | 13.2616 | 35.9594 | 0 | 0 | 0 | 0 | 0 | 233.9384 | 0 | 1072.6791 | 84.1% | 13.2616 | 0 | 56.25 | 90% | 35.9594
3977 | 826 | 532 | 71 | 4.3 | 28.3 | 0 | 0 | 0 | 202.8311 | 35.3843 | 0 | 0 | 35.3843 | 0 | 0 | 0 | 0 | 0 | 202.8311 | 0 | 1275.5102 | 100% | 0 | 0.94966 | 55.199 | 88.32% | 36.334
3978 | 710 | 327 | 59 | 4.2 | 27.1 | 0 | 0 | 0 | 0 | 16.7692 | 4.6185e-14 | 0 | 16.7692 | 0 | 0 | 0 | 55.9473 | 20.179 | 0 | 55.9473 | 1219.5629 | 95.61% | 0 | 0 | 55.199 | 88.32% | 36.9482
3979 | 440 | 125 | 39 | 3.5 | 25.8 | 0 | 0 | 0 | 0 | 2.1095 | 0 | 0 | 2.1095 | 0 | 0 | 0 | 90.7466 | 35.0796 | 0 | 90.7466 | 1128.8163 | 88.5% | 0 | 0 | 55.199 | 88.32% | 37.1891
3980 | 26 | 8 | 6 | 2.3 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5809 | 35.2198 | 0 | 90.5809 | 1038.2354 | 81.4% | 0 | 0 | 55.199 | 88.32% | 35.2198
3981 | 0 | 0 | 0 | 1.7 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6199 | 33.2255 | 0 | 85.6199 | 952.6155 | 74.69% | 0 | 0 | 55.199 | 88.32% | 33.2255
3982 | 0 | 0 | 0 | 3.2 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0753 | 31.3523 | 0 | 81.0753 | 871.5402 | 68.33% | 0 | 0 | 55.199 | 88.32% | 31.3523
3983 | 0 | 0 | 0 | 2.1 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8034 | 29.9499 | 0 | 77.8034 | 793.7368 | 62.23% | 0 | 0 | 55.199 | 88.32% | 29.9499
3984 | 0 | 0 | 0 | 1.8 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.5559 | 29.021 | 0 | 75.5559 | 718.1809 | 56.31% | 0 | 0 | 55.199 | 88.32% | 29.021
3985 | 0 | 0 | 0 | 2.4 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5871 | 28.5976 | 0 | 74.5871 | 643.5938 | 50.46% | 0 | 0 | 55.199 | 88.32% | 28.5976
3986 | 0 | 0 | 0 | 2.7 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.763 | 28.2369 | 0 | 73.763 | 569.8308 | 44.67% | 0 | 0 | 55.199 | 88.32% | 28.2369
3987 | 0 | 0 | 0 | 2.5 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2656 | 28.0516 | 0 | 73.2656 | 496.5652 | 38.93% | 0 | 0 | 55.199 | 88.32% | 28.0516
3988 | 0 | 0 | 0 | 3.4 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.936 | 27.9291 | 0 | 72.936 | 423.6292 | 33.21% | 0 | 0 | 55.199 | 88.32% | 27.9291
3989 | 0 | 1 | 1 | 1.8 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7543 | 29.6337 | 0 | 76.7543 | 346.8748 | 27.19% | 0 | 0 | 55.199 | 88.32% | 29.6337
3990 | 255 | 87 | 56 | 2.1 | 17.5 | 0 | 0 | 0 | 0 | 2.3048 | 0 | 0 | 2.3048 | 0 | 0 | 0 | 77.1585 | 29.762 | 0 | 77.1585 | 269.7163 | 21.15% | 0 | 0 | 55.199 | 88.32% | 32.0668
3991 | 349 | 235 | 118 | 2.4 | 20.1 | 0 | 0 | 0 | 43.2209 | 5.9358 | 0 | 0 | 5.9358 | 0 | 0 | 0 | 0 | 0 | 43.2209 | 0 | 312.9371 | 24.53% | 0 | 24.8867 | 27.6561 | 44.25% | 30.8225
3992 | 331 | 378 | 215 | 4 | 22.4 | 0 | 0 | 0 | 56.538 | 16.7036 | 0 | 0 | 16.7036 | 0 | 0 | 0 | 0 | 0 | 56.538 | 0 | 369.4751 | 28.97% | 0 | 18.6624 | 7.0017 | 11.2% | 35.3661
3993 | 572 | 653 | 266 | 5.1 | 24.4 | 0 | 0 | 0 | 130.0809 | 35.2133 | 0 | 0 | 35.2133 | 0 | 0 | 0 | 0 | 0 | 130.0809 | 0 | 499.556 | 39.17% | 0 | 0.67925 | 6.25 | 10% | 35.8925
3994 | 265 | 590 | 366 | 5.8 | 24.7 | 0 | 0 | 0 | 53.3472 | 36.6196 | 0 | 0.4179 | 36.2017 | 0 | 0 | 0 | 0 | 0 | 53.3472 | 0 | 552.9033 | 43.35% | 0.4179 | 0 | 6.6276 | 10.6% | 36.2017
3995 | 126 | 568 | 445 | 4.6 | 25.3 | 0 | 0 | 0 | 0 | 36.5729 | 0 | 13.3514 | 23.2215 | 0 | 0 | 0 | 38.2653 | 12.7253 | 0 | 38.2653 | 514.638 | 40.35% | 13.3514 | 0 | 18.6914 | 29.91% | 35.9468
3996 | 2 | 283 | 275 | 5.3 | 24.4 | 0 | 0 | 0 | 0 | 17.3221 | 0 | 0 | 17.3221 | 0 | 0 | 0 | 39.8364 | 13.4242 | 0 | 39.8364 | 474.8016 | 37.22% | 0 | 3.6115 | 14.6944 | 23.51% | 34.3578
3997 | 135 | 477 | 336 | 5.2 | 24.4 | 0 | 0 | 0 | 0 | 31.9447 | 0 | 0 | 31.9447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474.8016 | 37.22% | 0 | 1.4103 | 13.1336 | 21.01% | 33.355
3998 | 566 | 816 | 277 | 5.6 | 26.1 | 0 | 0 | 0 | 150.13 | 56.889 | 0 | 23.729 | 33.16 | 0 | 0 | 0 | 0 | 0 | 150.13 | 0 | 624.9316 | 48.99% | 23.729 | 0 | 34.5741 | 55.32% | 33.16
3999 | 250 | 587 | 372 | 6.2 | 25.6 | 0 | 0 | 0 | 52.3554 | 40.4983 | 0 | 7.2742 | 33.2241 | 0 | 0 | 0 | 0 | 0 | 52.3554 | 0 | 677.2869 | 53.1% | 7.2742 | 0 | 41.1468 | 65.83% | 33.2241
4000 | 785 | 718 | 151 | 6.3 | 25.5 | 0 | 0 | 0 | 201.8826 | 50.5633 | 0 | 16.7152 | 33.848 | 0 | 0 | 0 | 0 | 0 | 201.8826 | 0 | 879.1696 | 68.93% | 16.7152 | 0 | 56.25 | 90% | 33.848
4001 | 468 | 406 | 146 | 6 | 24.7 | 0 | 0 | 0 | 105.0644 | 27.7022 | 0 | 0 | 27.7022 | 0 | 0 | 0 | 0 | 0 | 105.0644 | 0 | 984.2339 | 77.16% | 0 | 5.9197 | 49.6985 | 79.52% | 33.6219
4002 | 311 | 214 | 87 | 5.4 | 23.8 | 0 | 0 | 0 | 54.8008 | 11.119 | 0 | 0 | 11.119 | 0 | 0 | 0 | 0 | 0 | 54.8008 | 0 | 1039.0347 | 81.46% | 0 | 25 | 22.0301 | 35.25% | 36.119
4003 | 221 | 117 | 68 | 4.9 | 22.8 | 0 | 0 | 0 | 0 | 3.598 | 0 | 0 | 3.598 | 0 | 0 | 0 | 87.0508 | 33.7345 | 0 | 87.0508 | 951.9839 | 74.64% | 0 | 0 | 22.0301 | 35.25% | 37.3325
4004 | 5 | 10 | 9 | 3.4 | 21.5 | 0 | 0 | 0 | 0 | 0.11862 | 0 | 0 | 0.11862 | 0 | 0 | 0 | 90.133 | 35.1486 | 0 | 90.133 | 861.8509 | 67.57% | 0 | 0 | 22.0301 | 35.25% | 35.2672
4005 | 0 | 0 | 0 | 2.4 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8674 | 32.9553 | 0 | 84.8674 | 776.9836 | 60.92% | 0 | 0 | 22.0301 | 35.25% | 32.9553
4006 | 0 | 0 | 0 | 1.3 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8908 | 31.2883 | 0 | 80.8908 | 696.0927 | 54.57% | 0 | 0 | 22.0301 | 35.25% | 31.2883
4007 | 0 | 0 | 0 | 1.1 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8435 | 30.0056 | 0 | 77.8435 | 618.2492 | 48.47% | 0 | 0 | 22.0301 | 35.25% | 30.0056
4008 | 0 | 0 | 0 | 1 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.9297 | 29.2173 | 0 | 75.9297 | 542.3195 | 42.52% | 0 | 0 | 22.0301 | 35.25% | 29.2173
4009 | 0 | 0 | 0 | 1.1 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7806 | 29.1811 | 0 | 75.7806 | 466.5389 | 36.58% | 0 | 0 | 22.0301 | 35.25% | 29.1811
4010 | 0 | 0 | 0 | 0.8 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.914 | 30.5668 | 0 | 78.914 | 387.6249 | 30.39% | 0 | 0 | 22.0301 | 35.25% | 30.5668
4011 | 0 | 0 | 0 | 0.4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.7489 | 0 | 127.551 | 260.0739 | 20.39% | 18.3298 | 0 | 38.5922 | 61.75% | 33.4191
4012 | 0 | 0 | 0 | 0.1 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.7544 | 0 | 127.551 | 132.5229 | 10.39% | 14.5988 | 0 | 51.7831 | 82.85% | 37.1557
4013 | 0 | 1 | 1 | 0.9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7352 | 45.3067 | 0 | 112.7352 | 19.7876 | 1.551% | 4.9437 | 0 | 56.25 | 90% | 40.363
4014 | 308 | 74 | 30 | 0.3 | 16.1 | 0 | 0 | 0 | 0 | 1.0492 | 0 | 0 | 1.0492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.7876 | 1.551% | 0 | 25 | 28.5817 | 45.73% | 26.0492
4015 | 652 | 261 | 58 | 0.2 | 21.2 | 0 | 0 | 0 | 98.0263 | 2.9006 | 0 | 0 | 2.9006 | 0 | 0 | 0 | 0 | 0 | 98.0263 | 0 | 117.814 | 9.237% | 0 | 20.178 | 6.25 | 10% | 23.0786
4016 | 795 | 465 | 72 | 1.1 | 23 | 0 | 0 | 0 | 0 | 13.6603 | 1.7764e-15 | 0 | 13.6603 | 0 | 0 | 0 | 79.5487 | 30.502 | 0 | 79.5487 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 44.1623
4017 | 882 | 662 | 77 | 1.9 | 24.3 | 0 | 0 | 0 | 0 | 32.1995 | 0.37567 | 0 | 32.1995 | 0 | 0 | 0 | 38.2653 | 12.7552 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 44.9548
4018 | 928 | 827 | 80 | 1.4 | 26.9 | 0 | 0 | 0 | 0 | 45.335 | 1.3789 | 0 | 45.335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 45.335
4019 | 942 | 942 | 86 | 2.3 | 28.6 | 0 | 0 | 0 | 231.4737 | 44.2654 | 12.9993 | 0 | 44.2654 | 0 | 0 | 0 | 0 | 0 | 231.4737 | 0 | 231.4737 | 18.15% | 0 | 0 | 6.25 | 10% | 44.2654
4020 | 943 | 1004 | 92 | 3.9 | 29.4 | 0 | 0 | 0 | 263.2764 | 52.2832 | 12.3641 | 8.9509 | 43.3323 | 0 | 0 | 0 | 0 | 0 | 263.2764 | 0 | 494.75 | 38.79% | 8.9509 | 0 | 14.3377 | 22.94% | 43.3323
4021 | 945 | 1016 | 94 | 4.9 | 29.6 | 0 | 0 | 0 | 266.7979 | 67.8734 | 0 | 24.7221 | 43.1512 | 0 | 0 | 0 | 0 | 0 | 266.7979 | 0 | 761.5479 | 59.71% | 24.7221 | 0 | 36.6756 | 58.68% | 43.1512
4022 | 930 | 963 | 93 | 3.6 | 30.3 | 0 | 0 | 0 | 261.5814 | 64.7633 | 0 | 21.6636 | 43.0997 | 0 | 0 | 0 | 0 | 0 | 261.5814 | 0 | 1023.1294 | 80.21% | 21.6636 | 0 | 56.25 | 90% | 43.0997
4023 | 924 | 867 | 84 | 4.9 | 30.7 | 0 | 0 | 0 | 252.3808 | 42.6359 | 17.1506 | 0 | 42.6359 | 0 | 0 | 0 | 0 | 0 | 252.3808 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 42.6359
4024 | 896 | 721 | 76 | 5.2 | 30.2 | 0 | 0 | 0 | 0 | 42.4855 | 7.3091 | 0 | 42.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 42.4855
4025 | 832 | 534 | 69 | 3.7 | 29.9 | 0 | 0 | 0 | 0 | 35.2318 | 7.1054e-15 | 0 | 35.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 7.3401 | 48.1265 | 77% | 42.5719
4026 | 709 | 328 | 60 | 3 | 29.4 | 0 | 0 | 0 | 0 | 16.7065 | 0 | 0 | 16.7065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 20.4581 | 32.73% | 41.7065
4027 | 470 | 131 | 39 | 1.6 | 27.6 | 0 | 0 | 0 | 0 | 2.3096 | 0 | 0 | 2.3096 | 0 | 0 | 0 | 74.3471 | 27.958 | 0 | 74.3471 | 1201.1631 | 94.17% | 0 | 10.9715 | 8.3156 | 13.3% | 41.2391
4028 | 36 | 9 | 6 | 1.6 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4166 | 38.0233 | 0 | 97.4166 | 1103.7465 | 86.53% | 0 | 0 | 8.3156 | 13.3% | 38.0233
4029 | 0 | 0 | 0 | 2.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0122 | 36.3521 | 0 | 93.0122 | 1010.7343 | 79.24% | 0 | 0 | 8.3156 | 13.3% | 36.3521
4030 | 0 | 0 | 0 | 0.8 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7777 | 34.6293 | 0 | 88.7777 | 921.9566 | 72.28% | 0 | 0 | 8.3156 | 13.3% | 34.6293
4031 | 0 | 0 | 0 | 1 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2214 | 33.1586 | 0 | 85.2214 | 836.7351 | 65.6% | 0 | 0 | 8.3156 | 13.3% | 33.1586
4032 | 0 | 0 | 0 | 1.7 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.934 | 32.6782 | 0 | 83.934 | 752.8011 | 59.02% | 0 | 0 | 8.3156 | 13.3% | 32.6782
4033 | 0 | 0 | 0 | 1 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.655 | 32.5431 | 0 | 83.655 | 669.1461 | 52.46% | 0 | 0 | 8.3156 | 13.3% | 32.5431
4034 | 0 | 0 | 0 | 0.8 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.786 | 33.0612 | 0 | 84.786 | 584.3601 | 45.81% | 0 | 0 | 8.3156 | 13.3% | 33.0612
4035 | 0 | 0 | 0 | 0.7 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6091 | 35.2017 | 0 | 89.6091 | 494.751 | 38.79% | 0 | 0 | 8.3156 | 13.3% | 35.2017
4036 | 0 | 0 | 0 | 0.4 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6506 | 38.3019 | 0 | 96.6506 | 398.1004 | 31.21% | 0 | 0 | 8.3156 | 13.3% | 38.3019
4037 | 0 | 1 | 1 | 0.6 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6441 | 41.3045 | 0 | 103.6441 | 294.4562 | 23.09% | 0 | 0 | 8.3156 | 13.3% | 41.3045
4038 | 341 | 75 | 27 | 0.4 | 17.8 | 0 | 0 | 0 | 0 | 0.89668 | 0 | 0 | 0.89668 | 0 | 0 | 0 | 106.4081 | 42.4133 | 0 | 106.4081 | 188.0482 | 14.74% | 0 | 0 | 8.3156 | 13.3% | 43.31
4039 | 681 | 262 | 50 | 0.9 | 22 | 0 | 0 | 0 | 0 | 2.67 | 0 | 0 | 2.67 | 0 | 0 | 0 | 105.7472 | 41.8265 | 0 | 105.7472 | 82.3009 | 6.452% | 0 | 0 | 8.3156 | 13.3% | 44.4966
4040 | 825 | 469 | 62 | 2 | 23.9 | 0 | 0 | 0 | 0 | 13.3032 | 0 | 0 | 13.3032 | 0 | 0 | 0 | 82.3009 | 31.6209 | 0 | 82.3009 | 0 | 0% | 0 | 0 | 8.3156 | 13.3% | 44.9241
4041 | 880 | 657 | 75 | 3.2 | 23.7 | 0 | 0 | 0 | 0 | 32.7158 | 0 | 0 | 32.7158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 1.8664 | 6.25 | 10% | 34.5822
4042 | 909 | 817 | 86 | 2.6 | 25.7 | 0 | 0 | 0 | 236.3847 | 47.2478 | 0 | 1.133 | 46.1149 | 0 | 0 | 0 | 0 | 0 | 236.3847 | 0 | 236.3847 | 18.53% | 1.133 | 0 | 7.2737 | 11.64% | 46.1149
4043 | 922 | 932 | 95 | 3 | 27.4 | 0 | 0 | 0 | 250.424 | 52.5562 | 5.0031 | 7.582 | 44.9743 | 0 | 0 | 0 | 0 | 0 | 250.424 | 0 | 486.8087 | 38.17% | 7.582 | 0 | 14.1245 | 22.6% | 44.9743
4044 | 916 | 992 | 105 | 3.4 | 28.9 | 0 | 0 | 0 | 255.6587 | 63.6215 | 0 | 19.5428 | 44.0788 | 0 | 0 | 0 | 0 | 0 | 255.6587 | 0 | 742.4673 | 58.21% | 19.5428 | 0 | 31.7825 | 50.85% | 44.0788
4045 | 916 | 1001 | 106 | 3 | 30.4 | 0 | 0 | 0 | 259.5916 | 65.3016 | 0 | 21.4276 | 43.874 | 0 | 0 | 0 | 0 | 0 | 259.5916 | 0 | 1002.059 | 78.56% | 21.4276 | 0 | 51.1436 | 81.83% | 43.874
4046 | 899 | 949 | 109 | 6.4 | 31.1 | 0 | 0 | 0 | 249.9208 | 43.7626 | 21.3654 | 0 | 43.7626 | 0 | 0 | 0 | 0 | 0 | 249.9208 | 0 | 1251.9798 | 98.16% | 0 | 0 | 51.1436 | 81.83% | 43.7626
4047 | 870 | 845 | 107 | 6.2 | 30 | 0 | 0 | 0 | 0 | 43.3295 | 15.5145 | 0 | 43.3295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.9798 | 98.16% | 0 | 0 | 51.1436 | 81.83% | 43.3295
4048 | 828 | 697 | 100 | 6 | 29.6 | 0 | 0 | 0 | 23.5304 | 48.4071 | 0 | 5.6514 | 42.7557 | 0 | 0 | 0 | 0 | 0 | 23.5304 | 0 | 1275.5102 | 100% | 5.6514 | 0 | 56.25 | 90% | 42.7557
4049 | 769 | 517 | 86 | 4.5 | 29.4 | 0 | 0 | 0 | 0 | 34.3279 | 0 | 0 | 34.3279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 8.4599 | 46.8872 | 75.02% | 42.7877
4050 | 680 | 323 | 66 | 3.9 | 29 | 0 | 0 | 0 | 0 | 16.6963 | 0 | 0 | 16.6963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 19.2189 | 30.75% | 41.6964
4051 | 455 | 130 | 39 | 4.5 | 27 | 0 | 0 | 0 | 0 | 2.3213 | 0 | 0 | 2.3213 | 0 | 0 | 0 | 75.8234 | 28.6304 | 0 | 75.8234 | 1199.6868 | 94.06% | 0 | 10.492 | 7.607 | 12.17% | 41.4438
4052 | 26 | 8 | 6 | 3.3 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1006 | 38.132 | 0 | 97.1006 | 1102.5862 | 86.44% | 0 | 0 | 7.607 | 12.17% | 38.132
4053 | 0 | 0 | 0 | 1.9 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2771 | 36.6557 | 0 | 93.2771 | 1009.3091 | 79.13% | 0 | 0 | 7.607 | 12.17% | 36.6557
4054 | 0 | 0 | 0 | 0.8 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6686 | 34.7073 | 0 | 88.6686 | 920.6405 | 72.18% | 0 | 0 | 7.607 | 12.17% | 34.7073
4055 | 0 | 0 | 0 | 0.5 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8821 | 33.5263 | 0 | 85.8821 | 834.7585 | 65.45% | 0 | 0 | 7.607 | 12.17% | 33.5263
4056 | 0 | 0 | 0 | 0.3 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.8964 | 13.6276 | 0 | 39.8964 | 794.862 | 62.32% | 0 | 0 | 7.607 | 12.17% | 13.6276
4057 | 0 | 0 | 0 | 0.8 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9548 | 32.7575 | 0 | 83.9548 | 710.9072 | 55.74% | 0 | 0 | 7.607 | 12.17% | 32.7575
4058 | 0 | 0 | 0 | 0.5 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1393 | 33.2993 | 0 | 85.1393 | 625.7679 | 49.06% | 0 | 0 | 7.607 | 12.17% | 33.2993
4059 | 0 | 0 | 0 | 0.9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3954 | 35.6014 | 0 | 90.3954 | 535.3725 | 41.97% | 0 | 0 | 7.607 | 12.17% | 35.6014
4060 | 0 | 0 | 0 | 1.2 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0003 | 38.8924 | 0 | 98.0003 | 437.3722 | 34.29% | 0 | 0 | 7.607 | 12.17% | 38.8924
4061 | 0 | 1 | 1 | 1.2 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4748 | 41.7042 | 0 | 104.4748 | 332.8974 | 26.1% | 0 | 0 | 7.607 | 12.17% | 41.7042
4062 | 253 | 70 | 33 | 1.5 | 19.1 | 0 | 0 | 0 | 0 | 1.177 | 0 | 0 | 1.177 | 0 | 0 | 0 | 107.0326 | 42.5996 | 0 | 107.0326 | 225.8648 | 17.71% | 0 | 0 | 7.607 | 12.17% | 43.7765
4063 | 626 | 259 | 64 | 0.9 | 22.9 | 0 | 0 | 0 | 0 | 3.2681 | 0 | 0 | 3.2681 | 0 | 0 | 0 | 105.1586 | 41.4973 | 0 | 105.1586 | 120.7063 | 9.463% | 0 | 0 | 7.607 | 12.17% | 44.7654
4064 | 741 | 458 | 91 | 0.8 | 25.4 | 0 | 0 | 0 | 0 | 13.7744 | 0 | 0 | 13.7744 | 0 | 0 | 0 | 82.441 | 31.5704 | 0 | 82.441 | 38.2653 | 3% | 0 | 0 | 7.607 | 12.17% | 45.3447
4065 | 873 | 669 | 90 | 1.8 | 27.8 | 0 | 0 | 0 | 0 | 32.5142 | 0 | 0 | 32.5142 | 0 | 0 | 0 | 38.2653 | 12.6433 | 0 | 38.2653 | 0 | 0% | 0 | 1.2261 | 6.25 | 10% | 46.3837
4066 | 927 | 835 | 89 | 3.2 | 28.9 | 0 | 0 | 0 | 241.1838 | 46.4644 | 1.4451 | 0 | 46.4644 | 0 | 0 | 0 | 0 | 0 | 241.1838 | 0 | 241.1838 | 18.91% | 0 | 0 | 6.25 | 10% | 46.4644
4067 | 958 | 958 | 89 | 3.7 | 30.1 | 0 | 0 | 0 | 260.3322 | 58.8835 | 0 | 13.6627 | 45.2208 | 0 | 0 | 0 | 0 | 0 | 260.3322 | 0 | 501.516 | 39.32% | 13.6627 | 0 | 18.5951 | 29.75% | 45.2208
4068 | 917 | 1051 | 164 | 4.5 | 31.2 | 0 | 0 | 0 | 255.0119 | 44.374 | 22.821 | 0 | 44.374 | 0 | 0 | 0 | 0 | 0 | 255.0119 | 0 | 756.5279 | 59.31% | 0 | 0 | 18.5951 | 29.75% | 44.374
4069 | 962 | 1041 | 103 | 5.2 | 32.1 | 0 | 0 | 0 | 271.7162 | 45.3845 | 23.5716 | 1.2166 | 44.1679 | 0 | 0 | 0 | 0 | 0 | 271.7162 | 0 | 1028.2441 | 80.61% | 1.2166 | 0 | 19.6944 | 31.51% | 44.1679
4070 | 942 | 983 | 101 | 6 | 32.5 | 0 | 0 | 0 | 247.2662 | 66.7471 | 0 | 22.653 | 44.0941 | 0 | 0 | 0 | 0 | 0 | 247.2662 | 0 | 1275.5102 | 100% | 22.653 | 0 | 40.1627 | 64.26% | 44.0941
4071 | 862 | 899 | 161 | 5.9 | 33.2 | 0 | 0 | 0 | 0 | 61.411 | 0 | 17.8043 | 43.6066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 17.8043 | 0 | 56.25 | 90% | 43.6066
4072 | 272 | 527 | 318 | 5.8 | 32.4 | 0 | 0 | 0 | 0 | 34.285 | 0 | 0 | 34.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 34.285
4073 | 353 | 440 | 246 | 4.8 | 31.9 | 0 | 0 | 0 | 0 | 28.5413 | 0 | 0 | 28.5413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 7.0853 | 48.4085 | 77.45% | 35.6266
4074 | 627 | 355 | 117 | 3.9 | 31.7 | 0 | 0 | 0 | 0 | 18.7341 | 0 | 0 | 18.7341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 23.9325 | 21.9216 | 35.07% | 42.6666
4075 | 416 | 143 | 64 | 2.8 | 30.5 | 0 | 0 | 0 | 0 | 3.5385 | 0 | 0 | 3.5385 | 0 | 0 | 0 | 98.5952 | 37.922 | 0 | 98.5952 | 1176.915 | 92.27% | 0 | 0 | 21.9216 | 35.07% | 41.4605
4076 | 41 | 15 | 12 | 2.8 | 25.2 | 0 | 0 | 0 | 0 | 0.24377 | 0 | 0 | 0.24377 | 0 | 0 | 0 | 97.4404 | 37.9885 | 0 | 97.4404 | 1079.4745 | 84.63% | 0 | 0 | 21.9216 | 35.07% | 38.2322
4077 | 0 | 0 | 0 | 1.8 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4882 | 36.9718 | 0 | 94.4882 | 984.9863 | 77.22% | 0 | 0 | 21.9216 | 35.07% | 36.9718
4078 | 0 | 0 | 0 | 0.5 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7523 | 34.9914 | 0 | 89.7523 | 895.234 | 70.19% | 0 | 0 | 21.9216 | 35.07% | 34.9914
4079 | 0 | 0 | 0 | 0.5 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4473 | 33.6127 | 0 | 86.4473 | 808.7867 | 63.41% | 0 | 0 | 21.9216 | 35.07% | 33.6127
4080 | 0 | 0 | 0 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1792 | 33.1127 | 0 | 85.1792 | 723.6075 | 56.73% | 0 | 0 | 21.9216 | 35.07% | 33.1127
4081 | 0 | 0 | 0 | 0.5 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.202 | 21.0501 | 0 | 57.202 | 666.4055 | 52.25% | 0 | 0 | 21.9216 | 35.07% | 21.0501
4082 | 0 | 0 | 0 | 1.2 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6566 | 33.3411 | 0 | 85.6566 | 580.7489 | 45.53% | 0 | 0 | 21.9216 | 35.07% | 33.3411
4083 | 0 | 0 | 0 | 0.8 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9386 | 35.2017 | 0 | 89.9386 | 490.8103 | 38.48% | 0 | 0 | 21.9216 | 35.07% | 35.2017
4084 | 0 | 0 | 0 | 0.8 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2121 | 38.3436 | 0 | 97.2121 | 393.5983 | 30.86% | 0 | 0 | 21.9216 | 35.07% | 38.3436
4085 | 0 | 1 | 1 | 1.2 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3164 | 40.8672 | 0 | 103.3164 | 290.2818 | 22.76% | 0 | 0 | 21.9216 | 35.07% | 40.8672
4086 | 241 | 83 | 48 | 1.5 | 22.4 | 0 | 0 | 0 | 0 | 1.869 | 0 | 0 | 1.869 | 0 | 0 | 0 | 103.9453 | 41.019 | 0 | 103.9453 | 186.3365 | 14.61% | 0 | 0 | 21.9216 | 35.07% | 42.888
4087 | 610 | 255 | 65 | 1 | 24.5 | 0 | 0 | 0 | 0 | 3.3095 | 0 | 0 | 3.3095 | 0 | 0 | 0 | 103.6117 | 40.6898 | 0 | 103.6117 | 82.7248 | 6.486% | 0 | 0 | 21.9216 | 35.07% | 43.9994
4088 | 779 | 459 | 74 | 0.8 | 26.5 | 0 | 0 | 0 | 0 | 13.2209 | 0 | 0 | 13.2209 | 0 | 0 | 0 | 82.7248 | 31.6043 | 0 | 82.7248 | 0 | 0% | 0 | 0 | 21.9216 | 35.07% | 44.8252
4089 | 858 | 653 | 84 | 1.5 | 28.4 | 0 | 0 | 0 | 0 | 31.5173 | 0 | 0 | 31.5173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 14.1602 | 6.25 | 10% | 45.6776
4090 | 902 | 817 | 92 | 2.1 | 29.9 | 0 | 0 | 0 | 58.0417 | 46.2482 | 0 | 0.40485 | 45.8433 | 0 | 0 | 0 | 0 | 0 | 58.0417 | 0 | 58.0417 | 4.55% | 0.40485 | 0 | 6.6158 | 10.59% | 45.8433
4091 | 925 | 934 | 93 | 2 | 31.3 | 0 | 0 | 0 | 0 | 44.5592 | 11.331 | 0 | 44.5592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0417 | 4.55% | 0 | 0 | 6.6158 | 10.59% | 44.5592
4092 | 939 | 1004 | 94 | 3.3 | 32.1 | 0 | 0 | 0 | 0 | 43.5816 | 19.828 | 0 | 43.5816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.0417 | 4.55% | 0 | 0 | 6.6158 | 10.59% | 43.5816
4093 | 970 | 1031 | 85 | 5.3 | 32.8 | 0 | 0 | 0 | 274.0643 | 68.2303 | 0 | 24.9635 | 43.2668 | 0 | 0 | 0 | 0 | 0 | 274.0643 | 0 | 332.106 | 26.04% | 24.9635 | 0 | 29.1718 | 46.67% | 43.2668
4094 | 975 | 988 | 77 | 6.3 | 32.8 | 0 | 0 | 0 | 272.8457 | 63.9688 | 3.3215 | 20.8997 | 43.0691 | 0 | 0 | 0 | 0 | 0 | 272.8457 | 0 | 604.9517 | 47.43% | 20.8997 | 0 | 48.0559 | 76.89% | 43.0691
4095 | 967 | 890 | 70 | 6.1 | 32.9 | 0 | 0 | 0 | 264.0273 | 42.4396 | 18.8495 | 0 | 42.4396 | 0 | 0 | 0 | 0 | 0 | 264.0273 | 0 | 868.9791 | 68.13% | 0 | 0 | 48.0559 | 76.89% | 42.4396
4096 | 945 | 745 | 64 | 6.5 | 32.9 | 0 | 0 | 0 | 247.5909 | 51.2492 | 0 | 9.0686 | 42.1805 | 0 | 0 | 0 | 0 | 0 | 247.5909 | 0 | 1116.57 | 87.54% | 9.0686 | 0 | 56.25 | 90% | 42.1805
4097 | 871 | 550 | 62 | 6 | 31.8 | 0 | 0 | 0 | 0 | 36.4125 | 0 | 0 | 36.4125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116.57 | 87.54% | 0 | 0 | 56.25 | 90% | 36.4125
4098 | 734 | 336 | 56 | 4.2 | 31.5 | 0 | 0 | 0 | 158.9402 | 17.1664 | 0 | 0 | 17.1664 | 0 | 0 | 0 | 0 | 0 | 158.9402 | 0 | 1275.5102 | 100% | 0 | 24.6599 | 28.9581 | 46.33% | 41.8263
4099 | 455 | 130 | 39 | 3 | 30.6 | 0 | 0 | 0 | 0 | 2.3121 | 0 | 0 | 2.3121 | 0 | 0 | 0 | 100.2218 | 38.5941 | 0 | 100.2218 | 1175.2884 | 92.14% | 0 | 0 | 28.9581 | 46.33% | 40.9062
4100 | 31 | 9 | 6 | 2.1 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0074 | 37.9328 | 0 | 98.0074 | 1077.281 | 84.46% | 0 | 0 | 28.9581 | 46.33% | 37.9328
4101 | 0 | 0 | 0 | 3 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4507 | 36.7643 | 0 | 94.4507 | 982.8303 | 77.05% | 0 | 0 | 28.9581 | 46.33% | 36.7643
4102 | 0 | 0 | 0 | 2.3 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6009 | 34.8925 | 0 | 89.6009 | 893.2293 | 70.03% | 0 | 0 | 28.9581 | 46.33% | 34.8925
4103 | 0 | 0 | 0 | 3 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0781 | 33.4414 | 0 | 86.0781 | 807.1512 | 63.28% | 0 | 0 | 28.9581 | 46.33% | 33.4414
4104 | 0 | 0 | 0 | 3.8 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6861 | 32.8829 | 0 | 84.6861 | 722.4651 | 56.64% | 0 | 0 | 28.9581 | 46.33% | 32.8829
4105 | 0 | 0 | 0 | 3.1 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3221 | 32.7144 | 0 | 84.3221 | 638.1431 | 50.03% | 0 | 0 | 28.9581 | 46.33% | 32.7144
4106 | 0 | 0 | 0 | 2.2 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3466 | 33.2394 | 0 | 85.3466 | 552.7964 | 43.34% | 0 | 0 | 28.9581 | 46.33% | 33.2394
4107 | 0 | 0 | 0 | 1.6 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0809 | 35.334 | 0 | 90.0809 | 462.7155 | 36.28% | 0 | 0 | 28.9581 | 46.33% | 35.334
4108 | 0 | 0 | 0 | 1.2 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.5674 | 0 | 127.551 | 335.1645 | 26.28% | 13.0358 | 0 | 40.7367 | 65.18% | 38.5317
4109 | 0 | 1 | 1 | 1.1 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.777 | 50.7621 | 0 | 125.777 | 209.3875 | 16.42% | 9.6498 | 0 | 49.4558 | 79.13% | 41.1123
4110 | 57 | 41 | 32 | 0.9 | 18.9 | 0 | 0 | 0 | 0 | 1.1296 | 0 | 0 | 1.1296 | 0 | 0 | 0 | 105.5739 | 41.9826 | 0 | 105.5739 | 103.8136 | 8.139% | 0 | 0 | 49.4558 | 79.13% | 43.1122
4111 | 524 | 234 | 63 | 2 | 21.3 | 0 | 0 | 0 | 0 | 3.2076 | 0 | 0 | 3.2076 | 0 | 0 | 0 | 103.8136 | 41.0508 | 0 | 103.8136 | 0 | 0% | 0 | 0 | 49.4558 | 79.13% | 44.2584
4112 | 763 | 453 | 74 | 1.1 | 24.1 | 0 | 0 | 0 | 0 | 13.1325 | 0 | 0 | 13.1325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 21.7875 | 34.86% | 38.1325
4113 | 847 | 646 | 82 | 2.4 | 25.8 | 0 | 0 | 0 | 0 | 31.58 | 3.5527e-15 | 0 | 31.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 14.039 | 6.25 | 10% | 45.6191
4114 | 881 | 809 | 97 | 2.9 | 27.3 | 0 | 0 | 0 | 228.2478 | 46.4896 | 0 | 0.80087 | 45.6887 | 0 | 0 | 0 | 0 | 0 | 228.2478 | 0 | 228.2478 | 17.89% | 0.80087 | 0 | 6.9736 | 11.16% | 45.6887
4115 | 769 | 865 | 158 | 3.5 | 27.8 | 0 | 0 | 0 | 205.3243 | 53.926 | 0 | 9.6286 | 44.2974 | 0 | 0 | 0 | 0 | 0 | 205.3243 | 0 | 433.5721 | 33.99% | 9.6286 | 0 | 15.6737 | 25.08% | 44.2974
4116 | 586 | 788 | 210 | 5.2 | 28.3 | 0 | 0 | 0 | 155.2866 | 52.4246 | 0 | 9.2009 | 43.2236 | 0 | 0 | 0 | 0 | 0 | 155.2866 | 0 | 588.8586 | 46.17% | 9.2009 | 0 | 23.9873 | 38.38% | 43.2236
4117 | 878 | 995 | 131 | 4.9 | 29 | 0 | 0 | 0 | 246.5842 | 42.8393 | 23.2669 | 0 | 42.8393 | 0 | 0 | 0 | 0 | 0 | 246.5842 | 0 | 835.4428 | 65.5% | 0 | 0 | 23.9873 | 38.38% | 42.8393
4118 | 852 | 943 | 140 | 4.8 | 29.6 | 0 | 0 | 0 | 0 | 57.2982 | 6.529 | 14.6344 | 42.6638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 835.4428 | 65.5% | 14.6344 | 0 | 37.2103 | 59.54% | 42.6638
4119 | 821 | 841 | 138 | 4.8 | 29.5 | 0 | 0 | 0 | 222.0161 | 57.6604 | 0 | 15.5927 | 42.0677 | 0 | 0 | 0 | 0 | 0 | 222.0161 | 0 | 1057.4589 | 82.9% | 15.5927 | 0 | 51.2992 | 82.08% | 42.0677
4120 | 757 | 655 | 136 | 4.6 | 29.2 | 0 | 0 | 0 | 0 | 47.3324 | 0 | 5.4792 | 41.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1057.4589 | 82.9% | 5.4792 | 0 | 56.25 | 90% | 41.8532
4121 | 698 | 509 | 114 | 5.4 | 28.4 | 0 | 0 | 0 | 145.4677 | 33.9502 | 0 | 0 | 33.9502 | 0 | 0 | 0 | 0 | 0 | 145.4677 | 0 | 1202.9266 | 94.31% | 0 | 7.4546 | 47.9997 | 76.8% | 41.4048
4122 | 582 | 312 | 88 | 5.3 | 27.1 | 0 | 0 | 0 | 0 | 16.4555 | 0 | 0 | 16.4555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202.9266 | 94.31% | 0 | 24.4576 | 20.9317 | 33.49% | 40.9132
4123 | 327 | 119 | 52 | 4.7 | 25.6 | 0 | 0 | 0 | 0 | 2.8171 | 0 | 0 | 2.8171 | 0 | 0 | 0 | 86.5215 | 33.2951 | 0 | 86.5215 | 1116.4051 | 87.53% | 0 | 3.8456 | 16.6756 | 26.68% | 39.9578
4124 | 3 | 5 | 5 | 3.8 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8427 | 37.4272 | 0 | 95.8427 | 1020.5624 | 80.01% | 0 | 0 | 16.6756 | 26.68% | 37.4272
4125 | 0 | 0 | 0 | 3.1 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1849 | 36.3897 | 0 | 93.1849 | 927.3775 | 72.71% | 0 | 0 | 16.6756 | 26.68% | 36.3897
4126 | 0 | 0 | 0 | 2.7 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7033 | 34.5722 | 0 | 88.7033 | 838.6742 | 65.75% | 0 | 0 | 16.6756 | 26.68% | 34.5722
4127 | 0 | 0 | 0 | 2.9 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1177 | 33.0918 | 0 | 85.1177 | 753.5565 | 59.08% | 0 | 0 | 16.6756 | 26.68% | 33.0918
4128 | 0 | 0 | 0 | 3.6 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.914 | 32.1879 | 0 | 82.914 | 670.6425 | 52.58% | 0 | 0 | 16.6756 | 26.68% | 32.1879
4129 | 0 | 0 | 0 | 3.5 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8165 | 31.7283 | 0 | 81.8165 | 588.8259 | 46.16% | 0 | 0 | 16.6756 | 26.68% | 31.7283
4130 | 0 | 0 | 0 | 3.2 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1639 | 31.4651 | 0 | 81.1639 | 507.6621 | 39.8% | 0 | 0 | 16.6756 | 26.68% | 31.4651
4131 | 0 | 0 | 0 | 3.1 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.857 | 31.3551 | 0 | 80.857 | 426.8051 | 33.46% | 0 | 0 | 16.6756 | 26.68% | 31.3551
4132 | 0 | 0 | 0 | 1.8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4773 | 32.0877 | 0 | 82.4773 | 344.3278 | 27% | 0 | 0 | 16.6756 | 26.68% | 32.0877
4133 | 0 | 1 | 1 | 1.6 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1813 | 34.5736 | 0 | 88.1813 | 256.1464 | 20.08% | 0 | 0 | 16.6756 | 26.68% | 34.5736
4134 | 214 | 64 | 33 | 1.3 | 18 | 0 | 0 | 0 | 0 | 1.1836 | 0 | 0 | 1.1836 | 0 | 0 | 0 | 92.4399 | 36.3551 | 0 | 92.4399 | 163.7065 | 12.83% | 0 | 0 | 16.6756 | 26.68% | 37.5387
4135 | 521 | 238 | 74 | 1.3 | 20.6 | 0 | 0 | 0 | 0 | 3.9657 | 0 | 0 | 3.9657 | 0 | 0 | 0 | 91.8116 | 35.9308 | 0 | 91.8116 | 71.8949 | 5.637% | 0 | 0 | 16.6756 | 26.68% | 39.8965
4136 | 698 | 442 | 94 | 2.9 | 22.9 | 0 | 0 | 0 | 0 | 13.5899 | 0 | 0 | 13.5899 | 0 | 0 | 0 | 71.8949 | 27.2244 | 0 | 71.8949 | 0 | 0% | 0 | 0 | 16.6756 | 26.68% | 40.8143
4137 | 788 | 632 | 105 | 4.5 | 24.8 | 0 | 0 | 0 | 0 | 31.6782 | 0 | 0 | 31.6782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 9.4202 | 6.25 | 10% | 41.0984
4138 | 842 | 794 | 111 | 5.8 | 25.8 | 0 | 0 | 0 | 0 | 41.487 | 5.2415 | 0 | 41.487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 41.487
4139 | 867 | 910 | 116 | 5.4 | 27 | 0 | 0 | 0 | 0 | 40.6708 | 16.3841 | 0 | 40.6708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 40.6708
4140 | 881 | 978 | 119 | 5.2 | 27.7 | 0 | 0 | 0 | 0 | 38.9996 | 24.6533 | 0 | 38.9996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.9996
4141 | 890 | 991 | 115 | 5.7 | 28.5 | 0 | 0 | 0 | 249.5007 | 37.8896 | 28.4978 | 0 | 37.8896 | 0 | 0 | 0 | 0 | 0 | 249.5007 | 0 | 249.5007 | 19.56% | 0 | 0 | 6.25 | 10% | 37.8896
4142 | 891 | 948 | 108 | 6 | 29.2 | 0 | 0 | 0 | 201.7602 | 62.8242 | 2.0751 | 25 | 37.8242 | 0 | 0 | 0 | 0 | 0 | 201.7602 | 0 | 451.2608 | 35.38% | 25 | 0 | 28.839 | 46.14% | 37.8242
4143 | 874 | 850 | 102 | 6.5 | 29 | 0 | 0 | 0 | 236.2512 | 59.1253 | 0 | 21.5824 | 37.5428 | 0 | 0 | 0 | 0 | 0 | 236.2512 | 0 | 687.512 | 53.9% | 21.5824 | 0 | 48.34 | 77.34% | 37.5428
4144 | 825 | 701 | 100 | 6.8 | 28.5 | 0 | 0 | 0 | 212.9679 | 46.3458 | 2.3746 | 8.7542 | 37.5916 | 0 | 0 | 0 | 0 | 0 | 212.9679 | 0 | 900.48 | 70.6% | 8.7542 | 0 | 56.25 | 90% | 37.5916
4145 | 749 | 520 | 94 | 7.4 | 27.3 | 0 | 0 | 0 | 179.8303 | 34.8657 | 0 | 0 | 34.8657 | 0 | 0 | 0 | 0 | 0 | 179.8303 | 0 | 1080.3103 | 84.7% | 0 | 2.9752 | 52.9573 | 84.73% | 37.8409
4146 | 613 | 318 | 81 | 7 | 25.9 | 0 | 0 | 0 | 0 | 16.7487 | 0 | 0 | 16.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.3103 | 84.7% | 0 | 21.7398 | 28.8971 | 46.24% | 38.4885
4147 | 345 | 123 | 52 | 5.8 | 24.1 | 0 | 0 | 0 | 0 | 2.8758 | 0 | 0 | 2.8758 | 0 | 0 | 0 | 91.9706 | 35.745 | 0 | 91.9706 | 988.3397 | 77.49% | 0 | 0 | 28.8971 | 46.24% | 38.6208
4148 | 14 | 9 | 8 | 4.6 | 22 | 0 | 0 | 0 | 0 | 0.08446 | 0 | 0 | 0.08446 | 0 | 0 | 0 | 92.3849 | 36.0824 | 0 | 92.3849 | 895.9548 | 70.24% | 0 | 0 | 28.8971 | 46.24% | 36.1669
4149 | 0 | 0 | 0 | 3.8 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2561 | 33.9734 | 0 | 87.2561 | 808.6988 | 63.4% | 0 | 0 | 28.8971 | 46.24% | 33.9734
4150 | 0 | 0 | 0 | 2.5 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9852 | 32.1768 | 0 | 82.9852 | 725.7136 | 56.9% | 0 | 0 | 28.8971 | 46.24% | 32.1768
4151 | 0 | 0 | 0 | 1.3 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3471 | 30.6114 | 0 | 79.3471 | 646.3664 | 50.68% | 0 | 0 | 28.8971 | 46.24% | 30.6114
4152 | 0 | 0 | 0 | 1.3 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2763 | 29.7173 | 0 | 77.2763 | 569.0902 | 44.62% | 0 | 0 | 28.8971 | 46.24% | 29.7173
4153 | 0 | 0 | 0 | 1.5 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1023 | 29.2006 | 0 | 76.1023 | 492.9879 | 38.65% | 0 | 0 | 28.8971 | 46.24% | 29.2006
4154 | 0 | 0 | 0 | 1.4 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.5763 | 29.007 | 0 | 75.5763 | 417.4116 | 32.73% | 0 | 0 | 28.8971 | 46.24% | 29.007
4155 | 0 | 0 | 0 | 1.5 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.944 | 28.7563 | 0 | 74.944 | 342.4676 | 26.85% | 0 | 0 | 28.8971 | 46.24% | 28.7563
4156 | 0 | 0 | 0 | 1.7 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6659 | 28.6491 | 0 | 74.6659 | 267.8017 | 21% | 0 | 0 | 28.8971 | 46.24% | 28.6491
4157 | 0 | 1 | 1 | 1.5 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.8868 | 25.2835 | 0 | 66.8868 | 200.9149 | 15.75% | 0 | 5.1788 | 23.1655 | 37.06% | 30.4624
4158 | 249 | 68 | 33 | 0.8 | 17.8 | 0 | 0 | 0 | 0 | 1.1841 | 0 | 0 | 1.1841 | 0 | 0 | 0 | 81.5196 | 31.6375 | 0 | 81.5196 | 119.3952 | 9.361% | 0 | 0 | 23.1655 | 37.06% | 32.8216
4159 | 569 | 247 | 69 | 0.6 | 20.6 | 0 | 0 | 0 | 0 | 3.6297 | 0 | 0 | 3.6297 | 0 | 0 | 0 | 81.1299 | 31.3269 | 0 | 81.1299 | 38.2653 | 3% | 0 | 0 | 23.1655 | 37.06% | 34.9566
4160 | 732 | 451 | 86 | 1.3 | 23.2 | 0 | 0 | 0 | 0 | 13.2944 | 0 | 0 | 13.2944 | 0 | 0 | 0 | 38.2653 | 12.7863 | 0 | 38.2653 | 0 | 0% | 0 | 10.1683 | 11.9119 | 19.06% | 36.249
4161 | 822 | 646 | 95 | 4 | 26 | 0 | 0 | 0 | 196.3501 | 31.7961 | 0 | 0 | 31.7961 | 0 | 0 | 0 | 0 | 0 | 196.3501 | 0 | 196.3501 | 15.39% | 0 | 5.1159 | 6.25 | 10% | 36.912
4162 | 857 | 806 | 109 | 5.8 | 27.2 | 0 | 0 | 0 | 219.0482 | 37.7629 | 9.2469 | 0 | 37.7629 | 0 | 0 | 0 | 0 | 0 | 219.0482 | 0 | 415.3983 | 32.57% | 0 | 0 | 6.25 | 10% | 37.7629
4163 | 890 | 927 | 111 | 6 | 28.6 | 0 | 0 | 0 | 238.338 | 37.9314 | 19.8891 | 0 | 37.9314 | 0 | 0 | 0 | 0 | 0 | 238.338 | 0 | 653.7363 | 51.25% | 0 | 0 | 6.25 | 10% | 37.9314
4164 | 905 | 995 | 112 | 6.4 | 29.6 | 0 | 0 | 0 | 249.6903 | 36.4928 | 28.1811 | 0 | 36.4928 | 0 | 0 | 0 | 0 | 0 | 249.6903 | 0 | 903.4266 | 70.83% | 0 | 0 | 6.25 | 10% | 36.4928
4165 | 901 | 1006 | 118 | 6.1 | 30.4 | 0 | 0 | 0 | 0 | 35.7602 | 31.2027 | 0 | 35.7602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 903.4266 | 70.83% | 0 | 0 | 6.25 | 10% | 35.7602
4166 | 872 | 955 | 132 | 6 | 30.9 | 0 | 0 | 0 | 0 | 60.568 | 4.2444 | 25 | 35.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 903.4266 | 70.83% | 25 | 0 | 28.839 | 46.14% | 35.568
4167 | 822 | 848 | 142 | 6.3 | 30.4 | 0 | 0 | 0 | 221.0707 | 58.3208 | 0 | 22.8656 | 35.4552 | 0 | 0 | 0 | 0 | 0 | 221.0707 | 0 | 1124.4973 | 88.16% | 22.8656 | 0 | 49.4995 | 79.2% | 35.4552
4168 | 776 | 703 | 136 | 6.4 | 30.1 | 0 | 0 | 0 | 0 | 43.2772 | 5.3042 | 7.471 | 35.8062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1124.4973 | 88.16% | 7.471 | 0 | 56.25 | 90% | 35.8062
4169 | 668 | 518 | 136 | 6.4 | 29.5 | 0 | 0 | 0 | 0 | 34.2747 | 0 | 0 | 34.2747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1124.4973 | 88.16% | 0 | 2.0746 | 53.954 | 86.33% | 36.3493
4170 | 473 | 309 | 123 | 6.7 | 27.9 | 0 | 0 | 0 | 33.592 | 16.5619 | 0 | 0 | 16.5619 | 0 | 0 | 0 | 0 | 0 | 33.592 | 0 | 1158.0892 | 90.79% | 0 | 20.6091 | 31.1452 | 49.83% | 37.171
4171 | 219 | 119 | 72 | 6.3 | 25.1 | 0 | 0 | 0 | 0 | 4.0411 | 0 | 0 | 4.0411 | 0 | 0 | 0 | 59.4175 | 21.7628 | 0 | 59.4175 | 1098.6717 | 86.14% | 0 | 12.2139 | 17.6277 | 28.2% | 38.0178
4172 | 2 | 6 | 5 | 4.6 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5331 | 36.1098 | 0 | 92.5331 | 1006.1387 | 78.88% | 0 | 0 | 17.6277 | 28.2% | 36.1098
4173 | 0 | 0 | 0 | 4 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7124 | 34.1391 | 0 | 87.7124 | 918.4263 | 72% | 0 | 0 | 17.6277 | 28.2% | 34.1391
4174 | 0 | 0 | 0 | 2 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2571 | 32.3049 | 0 | 83.2571 | 835.1692 | 65.48% | 0 | 0 | 17.6277 | 28.2% | 32.3049
4175 | 0 | 0 | 0 | 1.1 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2922 | 31.0348 | 0 | 80.2922 | 754.8769 | 59.18% | 0 | 0 | 17.6277 | 28.2% | 31.0348
4176 | 0 | 0 | 0 | 1.4 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4259 | 30.2187 | 0 | 78.4259 | 676.451 | 53.03% | 0 | 0 | 17.6277 | 28.2% | 30.2187
4177 | 0 | 0 | 0 | 1.3 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7254 | 29.9499 | 0 | 77.7254 | 598.7256 | 46.94% | 0 | 0 | 17.6277 | 28.2% | 29.9499
4178 | 0 | 0 | 0 | 1 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4637 | 30.3273 | 0 | 78.4637 | 520.2619 | 40.79% | 0 | 0 | 17.6277 | 28.2% | 30.3273
4179 | 0 | 0 | 0 | 0.2 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1723 | 31.9512 | 0 | 82.1723 | 438.0896 | 34.35% | 0 | 0 | 17.6277 | 28.2% | 31.9512
4180 | 0 | 0 | 0 | 0.9 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2494 | 34.1739 | 0 | 87.2494 | 350.8402 | 27.51% | 0 | 0 | 17.6277 | 28.2% | 34.1739
4181 | 0 | 1 | 1 | 1.1 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2295 | 36.3242 | 0 | 92.2295 | 258.6107 | 20.28% | 0 | 0 | 17.6277 | 28.2% | 36.3242
4182 | 123 | 56 | 37 | 1.4 | 18.5 | 0 | 0 | 0 | 0 | 1.3725 | 0 | 0 | 1.3725 | 0 | 0 | 0 | 95.1698 | 37.5087 | 0 | 95.1698 | 163.4409 | 12.81% | 0 | 0 | 17.6277 | 28.2% | 38.8812
4183 | 473 | 237 | 87 | 1.1 | 21.4 | 0 | 0 | 0 | 0 | 4.3901 | 0 | 0 | 4.3901 | 0 | 0 | 0 | 91.9909 | 35.9549 | 0 | 91.9909 | 71.45 | 5.602% | 0 | 0 | 17.6277 | 28.2% | 40.3449
4184 | 656 | 442 | 112 | 3.2 | 23.9 | 0 | 0 | 0 | 0 | 14.1442 | 0 | 0 | 14.1442 | 0 | 0 | 0 | 71.45 | 26.975 | 0 | 71.45 | 0 | 0% | 0 | 0 | 17.6277 | 28.2% | 41.1193
4185 | 766 | 633 | 125 | 3 | 25.3 | 0 | 0 | 0 | 182.2872 | 31.8026 | 0 | 0 | 31.8026 | 0 | 0 | 0 | 0 | 0 | 182.2872 | 0 | 182.2872 | 14.29% | 0 | 10.2804 | 6.25 | 10% | 42.083
4186 | 828 | 800 | 133 | 2.5 | 26.8 | 0 | 0 | 0 | 213.5137 | 46.3939 | 0 | 3.7413 | 42.6526 | 0 | 0 | 0 | 0 | 0 | 213.5137 | 0 | 395.8009 | 31.03% | 3.7413 | 0 | 9.6305 | 15.41% | 42.6526
4187 | 875 | 921 | 124 | 2.9 | 28.2 | 0 | 0 | 0 | 236.4411 | 42.1248 | 14.3628 | 0 | 42.1248 | 0 | 0 | 0 | 0 | 0 | 236.4411 | 0 | 632.242 | 49.57% | 0 | 0 | 9.6305 | 15.41% | 42.1248
4188 | 884 | 985 | 128 | 2.4 | 29.6 | 0 | 0 | 0 | 246.4963 | 62.014 | 0 | 21.1315 | 40.8825 | 0 | 0 | 0 | 0 | 0 | 246.4963 | 0 | 878.7383 | 68.89% | 21.1315 | 0 | 28.7241 | 45.96% | 40.8825
4189 | 864 | 986 | 141 | 2.5 | 29.9 | 0 | 0 | 0 | 244.0569 | 42.1491 | 21.6993 | 1.761 | 40.3881 | 0 | 0 | 0 | 0 | 0 | 244.0569 | 0 | 1122.7952 | 88.03% | 1.761 | 0 | 30.3153 | 48.5% | 40.3881
4190 | 863 | 957 | 146 | 2.2 | 31 | 0 | 0 | 0 | 152.715 | 62.5309 | 0 | 22.0467 | 40.4842 | 0 | 0 | 0 | 0 | 0 | 152.715 | 0 | 1275.5102 | 100% | 22.0467 | 0 | 50.2358 | 80.38% | 40.4842
4191 | 789 | 832 | 156 | 2.3 | 31.1 | 0 | 0 | 0 | 0 | 40.3046 | 15.44 | 0 | 40.3046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.2358 | 80.38% | 40.3046
4192 | 771 | 689 | 130 | 3.2 | 30.3 | 0 | 0 | 0 | 0 | 47.0498 | 0 | 6.6561 | 40.3937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 6.6561 | 0 | 56.25 | 90% | 40.3937
4193 | 723 | 517 | 107 | 4.1 | 29.8 | 0 | 0 | 0 | 0 | 34.1956 | 0 | 0 | 34.1956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 34.1956
4194 | 539 | 299 | 91 | 3.9 | 28.7 | 0 | 0 | 0 | 0 | 15.8202 | 0 | 0 | 15.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 24.6247 | 28.997 | 46.4% | 40.4449
4195 | 199 | 90 | 46 | 3.7 | 26.9 | 0 | 0 | 0 | 0 | 2.3637 | 0 | 0 | 2.3637 | 0 | 0 | 0 | 98.3752 | 38.2236 | 0 | 98.3752 | 1177.135 | 92.29% | 0 | 0 | 28.997 | 46.4% | 40.5873
4196 | 15 | 9 | 8 | 2.3 | 24.6 | 0 | 0 | 0 | 0 | 0.081436 | 0 | 0 | 0.081436 | 0 | 0 | 0 | 57.0942 | 20.7953 | 0 | 57.0942 | 1120.0408 | 87.81% | 0 | 0 | 28.997 | 46.4% | 20.8768
4197 | 0 | 0 | 0 | 2.3 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5262 | 36.4983 | 0 | 93.5262 | 1026.5145 | 80.48% | 0 | 0 | 28.997 | 46.4% | 36.4983
4198 | 0 | 0 | 0 | 1 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6121 | 34.433 | 0 | 88.6121 | 937.9024 | 73.53% | 0 | 0 | 28.997 | 46.4% | 34.433
4199 | 0 | 0 | 0 | 0.5 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 33.3508 | 0 | 86 | 851.9024 | 66.79% | 0 | 0 | 28.997 | 46.4% | 33.3508
4200 | 0 | 0 | 0 | 0.3 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3907 | 32.6963 | 0 | 84.3907 | 767.5117 | 60.17% | 0 | 0 | 28.997 | 46.4% | 32.6963
4201 | 0 | 0 | 0 | 1.2 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0346 | 32.5904 | 0 | 84.0346 | 683.4772 | 53.58% | 0 | 0 | 28.997 | 46.4% | 32.5904
4202 | 0 | 0 | 0 | 1.4 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4372 | 33.2297 | 0 | 85.4372 | 598.04 | 46.89% | 0 | 0 | 28.997 | 46.4% | 33.2297
4203 | 0 | 0 | 0 | 1.2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3316 | 35.7616 | 0 | 91.3316 | 506.7083 | 39.73% | 0 | 0 | 28.997 | 46.4% | 35.7616
4204 | 0 | 0 | 0 | 1 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9152 | 39.047 | 0 | 98.9152 | 407.7931 | 31.97% | 0 | 0 | 28.997 | 46.4% | 39.047
4205 | 0 | 1 | 1 | 0.6 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3648 | 41.8922 | 0 | 105.3648 | 302.4283 | 23.71% | 0 | 0 | 28.997 | 46.4% | 41.8922
4206 | 188 | 62 | 35 | 0.6 | 20 | 0 | 0 | 0 | 0 | 1.2652 | 0 | 0 | 1.2652 | 0 | 0 | 0 | 109.1802 | 43.4626 | 0 | 109.1802 | 193.2481 | 15.15% | 0 | 0 | 28.997 | 46.4% | 44.7277
4207 | 506 | 233 | 76 | 1.8 | 22.5 | 0 | 0 | 0 | 0 | 4.087 | 0 | 0 | 4.087 | 0 | 0 | 0 | 106.3628 | 42.0488 | 0 | 106.3628 | 86.8853 | 6.812% | 0 | 0 | 28.997 | 46.4% | 46.1358
4208 | 670 | 431 | 101 | 2.8 | 25.3 | 0 | 0 | 0 | 0 | 13.4535 | 0 | 0 | 13.4535 | 0 | 0 | 0 | 86.8853 | 33.4747 | 0 | 86.8853 | 0 | 0% | 0 | 0 | 28.997 | 46.4% | 46.9282
4209 | 767 | 623 | 115 | 2.1 | 27.1 | 0 | 0 | 0 | 0 | 30.7339 | 0 | 0 | 30.7339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 17.4046 | 9.7348 | 15.58% | 48.1385
4210 | 831 | 788 | 120 | 2.1 | 28.6 | 0 | 0 | 0 | 214.5264 | 45.168 | 0 | 0 | 45.168 | 0 | 0 | 0 | 0 | 0 | 214.5264 | 0 | 214.5264 | 16.82% | 0 | 3.1487 | 6.25 | 10% | 48.3167
4211 | 872 | 911 | 119 | 2 | 30.2 | 0 | 0 | 0 | 235.9766 | 54.8971 | 0 | 7.3338 | 47.5633 | 0 | 0 | 0 | 0 | 0 | 235.9766 | 0 | 450.5029 | 35.32% | 7.3338 | 0 | 12.8765 | 20.6% | 47.5633
4212 | 888 | 980 | 120 | 3.2 | 31.1 | 0 | 0 | 0 | 247.3375 | 62.1628 | 0 | 15.2067 | 46.9561 | 0 | 0 | 0 | 0 | 0 | 247.3375 | 0 | 697.8405 | 54.71% | 15.2067 | 0 | 26.6167 | 42.59% | 46.9561
4213 | 898 | 995 | 117 | 3.8 | 31 | 0 | 0 | 0 | 253.6121 | 47.2494 | 18.127 | 0.24319 | 47.0062 | 0 | 0 | 0 | 0 | 0 | 253.6121 | 0 | 951.4525 | 74.59% | 0.24319 | 0 | 26.8364 | 42.94% | 47.0062
4214 | 889 | 949 | 115 | 4.8 | 31.5 | 0 | 0 | 0 | 0 | 64.201 | 0 | 17.1446 | 47.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 951.4525 | 74.59% | 17.1446 | 0 | 42.3277 | 67.72% | 47.0563
4215 | 868 | 851 | 111 | 5.7 | 30.5 | 0 | 0 | 0 | 106.6176 | 58.886 | 0 | 12.5371 | 46.3488 | 0 | 0 | 0 | 0 | 0 | 106.6176 | 0 | 1058.0701 | 82.95% | 12.5371 | 0 | 53.6557 | 85.85% | 46.3488
4216 | 835 | 706 | 102 | 5.1 | 30.5 | 0 | 0 | 0 | 217.4401 | 48.7493 | 0 | 2.8712 | 45.8781 | 0 | 0 | 0 | 0 | 0 | 217.4401 | 0 | 1275.5102 | 100% | 2.8712 | 0 | 56.25 | 90% | 45.8781
4217 | 777 | 526 | 87 | 4.5 | 30.4 | 0 | 0 | 0 | 0 | 32.8017 | 2.0896 | 0 | 32.8017 | 0 | 0 | 0 | 38.2653 | 12.5472 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 45.3489
4218 | 658 | 325 | 72 | 4.5 | 29.7 | 0 | 0 | 0 | 0 | 17.0235 | 2.8422e-14 | 0 | 17.0235 | 0 | 0 | 0 | 74.2134 | 27.7335 | 0 | 74.2134 | 1163.0315 | 91.18% | 0 | 0 | 56.25 | 90% | 44.757
4219 | 387 | 130 | 50 | 3.3 | 26.3 | 0 | 0 | 0 | 58.2535 | 2.8308 | 0 | 0 | 2.8308 | 0 | 0 | 0 | 0 | 0 | 58.2535 | 0 | 1221.285 | 95.75% | 0 | 25 | 28.5817 | 45.73% | 27.8308
4220 | 22 | 10 | 8 | 2.9 | 22.9 | 0 | 0 | 0 | 0 | 0.05658 | 0 | 0 | 0.05658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1221.285 | 95.75% | 0 | 20.178 | 6.25 | 10% | 20.2346
4221 | 0 | 0 | 0 | 1.1 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7774 | 38.838 | 0 | 98.7774 | 1122.5075 | 88% | 0 | 0 | 6.25 | 10% | 38.838
4222 | 0 | 0 | 0 | 3 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7294 | 36.703 | 0 | 93.7294 | 1028.7782 | 80.66% | 0 | 0 | 6.25 | 10% | 36.703
4223 | 0 | 0 | 0 | 2.2 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4497 | 35.3438 | 0 | 90.4497 | 938.3285 | 73.56% | 0 | 0 | 6.25 | 10% | 35.3438
4224 | 0 | 0 | 0 | 1.9 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.0058 | 24.7901 | 0 | 66.0058 | 872.3227 | 68.39% | 0 | 0 | 6.25 | 10% | 24.7901
4225 | 0 | 0 | 0 | 0.9 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0909 | 34.3633 | 0 | 88.0909 | 784.2318 | 61.48% | 0 | 0 | 6.25 | 10% | 34.3633
4226 | 0 | 0 | 0 | 1.3 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0361 | 34.8062 | 0 | 89.0361 | 695.1957 | 54.5% | 0 | 0 | 6.25 | 10% | 34.8062
4227 | 0 | 0 | 0 | 1.9 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7985 | 36.8869 | 0 | 93.7985 | 601.3972 | 47.15% | 0 | 0 | 6.25 | 10% | 36.8869
4228 | 0 | 0 | 0 | 3.7 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.3564 | 40.1207 | 0 | 101.3564 | 500.0407 | 39.2% | 0 | 0 | 6.25 | 10% | 40.1207
4229 | 0 | 0 | 0 | 2.9 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.6245 | 43.2376 | 0 | 108.6245 | 391.4163 | 30.69% | 0 | 0 | 6.25 | 10% | 43.2376
4230 | 0 | 17 | 17 | 2.3 | 20.2 | 0 | 0 | 0 | 0 | 0.41702 | 0 | 0 | 0.41702 | 0 | 0 | 0 | 114.4782 | 45.7327 | 0 | 114.4782 | 276.9381 | 21.71% | 0 | 0 | 6.25 | 10% | 46.1497
4231 | 0 | 66 | 66 | 1.4 | 20.9 | 0 | 0 | 0 | 0 | 3.6069 | 0 | 0 | 3.6069 | 0 | 0 | 0 | 110.8013 | 44.0915 | 0 | 110.8013 | 166.1368 | 13.03% | 0 | 0 | 6.25 | 10% | 47.6984
4232 | 0 | 154 | 152 | 2.8 | 22.1 | 0 | 0 | 0 | 0 | 9.1048 | 0 | 0 | 9.1048 | 0 | 0 | 0 | 100.315 | 39.4835 | 0 | 100.315 | 65.8218 | 5.16% | 0 | 0 | 6.25 | 10% | 48.5883
4233 | 126 | 437 | 342 | 3.7 | 23.7 | 0 | 0 | 0 | 0 | 25.1082 | 0 | 0 | 25.1082 | 0 | 0 | 0 | 65.8218 | 24.5761 | 0 | 65.8218 | 0 | 0% | 0 | 0 | 6.25 | 10% | 49.6843
4234 | 798 | 798 | 158 | 4.2 | 25.6 | 0 | 0 | 0 | 203.9336 | 47.5117 | 0 | 0 | 47.5117 | 0 | 0 | 0 | 0 | 0 | 203.9336 | 0 | 203.9336 | 15.99% | 0 | 0 | 6.25 | 10% | 47.5117
4235 | 849 | 913 | 143 | 3.9 | 27.3 | 0 | 0 | 0 | 214.7301 | 57.4017 | 0 | 8.0168 | 49.3849 | 0 | 0 | 0 | 0 | 0 | 214.7301 | 0 | 418.6637 | 32.82% | 8.0168 | 0 | 13.4936 | 21.59% | 49.3849
4236 | 853 | 980 | 153 | 3.1 | 28.8 | 0 | 0 | 0 | 236.7387 | 62.4811 | 0 | 13.8831 | 48.598 | 0 | 0 | 0 | 0 | 0 | 236.7387 | 0 | 655.4024 | 51.38% | 13.8831 | 0 | 26.0379 | 41.66% | 48.598
4237 | 854 | 990 | 154 | 4 | 29.8 | 0 | 0 | 0 | 240.0108 | 65.2712 | 0 | 16.6969 | 48.5744 | 0 | 0 | 0 | 0 | 0 | 240.0108 | 0 | 895.4132 | 70.2% | 16.6969 | 0 | 41.1245 | 65.8% | 48.5744
4238 | 856 | 949 | 144 | 3.9 | 30.9 | 0 | 0 | 0 | 239.1557 | 63.5682 | 0 | 14.9562 | 48.612 | 0 | 0 | 0 | 0 | 0 | 239.1557 | 0 | 1134.5689 | 88.95% | 14.9562 | 0 | 54.6383 | 87.42% | 48.612
4239 | 500 | 667 | 239 | 4.4 | 30.7 | 0 | 0 | 0 | 128.0556 | 46.3588 | 0 | 0 | 46.3588 | 0 | 0 | 0 | 0 | 0 | 128.0556 | 0 | 1262.6245 | 98.99% | 0 | 1.4162 | 53.071 | 84.91% | 47.775
4240 | 772 | 718 | 156 | 5.8 | 30.5 | 0 | 0 | 0 | 0 | 37.5276 | 12.0584 | 2.8015 | 34.7261 | 0 | 0 | 0 | 38.2653 | 12.5433 | 0 | 38.2653 | 1224.3592 | 95.99% | 2.8015 | 0 | 55.6023 | 88.96% | 47.2694
4241 | 627 | 516 | 161 | 6.8 | 28.9 | 0 | 0 | 0 | 0 | 34.626 | 0 | 0 | 34.626 | 0 | 0 | 0 | 38.2653 | 12.604 | 0 | 38.2653 | 1186.0939 | 92.99% | 0.71683 | 0 | 56.25 | 90% | 46.5132
4242 | 455 | 309 | 132 | 6.7 | 27.6 | 0 | 0 | 0 | 89.4163 | 16.9208 | 0 | 0 | 16.9208 | 0 | 0 | 0 | 0 | 0 | 89.4163 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 41.9208
4243 | 142 | 100 | 65 | 5.4 | 26.7 | 0 | 0 | 0 | 0 | 3.541 | 0 | 0 | 3.541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 20.178 | 6.25 | 10% | 23.719
4244 | 4 | 5 | 5 | 4.2 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.9906 | 41.707 | 0 | 105.9906 | 1169.5196 | 91.69% | 0 | 0 | 6.25 | 10% | 41.707
4245 | 0 | 0 | 0 | 2.1 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1309 | 39.6653 | 0 | 101.1309 | 1068.3887 | 83.76% | 0 | 0 | 6.25 | 10% | 39.6653
4246 | 0 | 0 | 0 | 1.5 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5568 | 37.313 | 0 | 95.5568 | 972.832 | 76.27% | 0 | 0 | 6.25 | 10% | 37.313
4247 | 0 | 0 | 0 | 1.8 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.409 | 35.5596 | 0 | 91.409 | 881.423 | 69.1% | 0 | 0 | 6.25 | 10% | 35.5596
4248 | 0 | 0 | 0 | 1.7 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1761 | 34.6892 | 0 | 89.1761 | 792.2469 | 62.11% | 0 | 0 | 6.25 | 10% | 34.6892
4249 | 0 | 0 | 0 | 1.8 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5116 | 34.3898 | 0 | 88.5116 | 703.7353 | 55.17% | 0 | 0 | 6.25 | 10% | 34.3898
4250 | 0 | 0 | 0 | 2.8 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6108 | 34.8619 | 0 | 89.6108 | 614.1245 | 48.15% | 0 | 0 | 6.25 | 10% | 34.8619
4251 | 0 | 0 | 0 | 2.5 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7915 | 37.1459 | 0 | 94.7915 | 519.3331 | 40.72% | 0 | 0 | 6.25 | 10% | 37.1459
4252 | 0 | 0 | 0 | 1.1 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3712 | 0 | 127.551 | 391.782 | 30.72% | 11.0987 | 0 | 16.2783 | 26.05% | 40.2725
4253 | 0 | 1 | 1 | 2.3 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3801 | 0 | 127.551 | 264.231 | 20.72% | 7.8751 | 0 | 23.394 | 37.43% | 43.505
4254 | 19 | 49 | 46 | 4.7 | 20.9 | 0 | 0 | 0 | 0 | 1.7908 | 0 | 1.7908 | 0 | 0 | 0 | 0 | 124.234 | 49.878 | 0 | 124.234 | 139.997 | 10.98% | 5.1806 | 0 | 28.075 | 44.92% | 46.4881
4255 | 88 | 161 | 133 | 6.1 | 23.1 | 0 | 0 | 0 | 0 | 6.2465 | 0 | 0 | 6.2465 | 0 | 0 | 0 | 106.2365 | 41.9421 | 0 | 106.2365 | 33.7605 | 2.647% | 0 | 0 | 28.075 | 44.92% | 48.1886
4256 | 252 | 359 | 226 | 6 | 24.8 | 0 | 0 | 0 | 36.3748 | 15.8955 | 0 | 0 | 15.8955 | 0 | 0 | 0 | 0 | 0 | 36.3748 | 0 | 70.1353 | 5.499% | 0 | 0 | 28.075 | 44.92% | 15.8955
4257 | 391 | 549 | 277 | 6.7 | 27.2 | 0 | 0 | 0 | 80.8774 | 29.5706 | 0 | 0 | 29.5706 | 0 | 0 | 0 | 0 | 0 | 80.8774 | 0 | 151.0127 | 11.84% | 0 | 6.5246 | 20.8539 | 33.37% | 36.0952
4258 | 570 | 811 | 345 | 7.5 | 29.2 | 0 | 0 | 0 | 137.5346 | 48.7474 | 0 | 0 | 48.7474 | 0 | 0 | 0 | 0 | 0 | 137.5346 | 0 | 288.5472 | 22.62% | 0 | 0 | 20.8539 | 33.37% | 48.7474
4259 | 347 | 697 | 372 | 7.3 | 30.3 | 0 | 0 | 0 | 79.151 | 44.4199 | 0 | 0 | 44.4199 | 0 | 0 | 0 | 0 | 0 | 79.151 | 0 | 367.6982 | 28.83% | 0 | 0 | 20.8539 | 33.37% | 44.4199
4260 | 570 | 939 | 374 | 7.2 | 31 | 0 | 0 | 0 | 148.7844 | 61.517 | 0 | 11.5169 | 50 | 0 | 0 | 0 | 0 | 0 | 148.7844 | 0 | 516.4826 | 40.49% | 11.5169 | 0 | 31.2602 | 50.02% | 50
4261 | 552 | 949 | 394 | 7.4 | 31.8 | 0 | 0 | 0 | 145.6324 | 63.3854 | 0 | 13.3854 | 50 | 0 | 0 | 0 | 0 | 0 | 145.6324 | 0 | 662.1149 | 51.91% | 13.3854 | 0 | 43.3546 | 69.37% | 50
4262 | 439 | 831 | 409 | 8 | 31.1 | 0 | 0 | 0 | 110.1422 | 56.7568 | 0 | 6.7568 | 50 | 0 | 0 | 0 | 0 | 0 | 110.1422 | 0 | 772.2572 | 60.54% | 6.7568 | 0 | 49.4598 | 79.14% | 50
4263 | 658 | 825 | 255 | 8.4 | 31.5 | 0 | 0 | 0 | 171.2952 | 57.1965 | 0 | 7.5149 | 49.6816 | 0 | 0 | 0 | 0 | 0 | 171.2952 | 0 | 943.5523 | 73.97% | 7.5149 | 0 | 56.25 | 90% | 49.6816
4264 | 624 | 677 | 217 | 8.3 | 32.2 | 0 | 0 | 0 | 154.9616 | 46.4843 | 0 | 0 | 46.4843 | 0 | 0 | 0 | 0 | 0 | 154.9616 | 0 | 1098.514 | 86.12% | 0 | 0 | 56.25 | 90% | 46.4843
4265 | 536 | 496 | 188 | 7.6 | 30.6 | 0 | 0 | 0 | 122.538 | 32.6275 | 0 | 0 | 32.6275 | 0 | 0 | 0 | 0 | 0 | 122.538 | 0 | 1221.052 | 95.73% | 0 | 0.11461 | 56.1232 | 89.8% | 32.7421
4266 | 313 | 282 | 155 | 7 | 28.7 | 0 | 0 | 0 | 54.4582 | 15.4639 | 0 | 0 | 15.4639 | 0 | 0 | 0 | 0 | 0 | 54.4582 | 0 | 1275.5102 | 100% | 0 | 25 | 28.4548 | 45.53% | 40.4639
4267 | 77 | 102 | 84 | 5.8 | 27.1 | 0 | 0 | 0 | 0 | 4.6592 | 0 | 0 | 4.6592 | 0 | 0 | 0 | 106.2047 | 41.5295 | 0 | 106.2047 | 1169.3055 | 91.67% | 0 | 0 | 28.4548 | 45.53% | 46.1887
4268 | 2 | 9 | 9 | 5.1 | 25.3 | 0 | 0 | 0 | 0 | 0.11784 | 0 | 0 | 0.11784 | 0 | 0 | 0 | 108.6174 | 42.7493 | 0 | 108.6174 | 1060.6881 | 83.16% | 0 | 0 | 28.4548 | 45.53% | 42.8671
4269 | 0 | 0 | 0 | 3.8 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2768 | 40.6109 | 0 | 103.2768 | 957.4113 | 75.06% | 0 | 0 | 28.4548 | 45.53% | 40.6109
4270 | 0 | 0 | 0 | 3.4 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3761 | 38.0498 | 0 | 97.3761 | 860.0352 | 67.43% | 0 | 0 | 28.4548 | 45.53% | 38.0498
4271 | 0 | 0 | 0 | 3.5 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.505 | 36.1724 | 0 | 93.505 | 766.5301 | 60.1% | 0 | 0 | 28.4548 | 45.53% | 36.1724
4272 | 0 | 0 | 0 | 2.8 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2796 | 35.2714 | 0 | 91.2796 | 675.2505 | 52.94% | 0 | 0 | 28.4548 | 45.53% | 35.2714
4273 | 0 | 0 | 0 | 2.3 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2934 | 35.043 | 0 | 90.2934 | 584.9571 | 45.86% | 0 | 0 | 28.4548 | 45.53% | 35.043
4274 | 0 | 0 | 0 | 2.1 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7332 | 35.3076 | 0 | 90.7332 | 494.2239 | 38.75% | 0 | 0 | 28.4548 | 45.53% | 35.3076
4275 | 0 | 0 | 0 | 1.3 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2295 | 0 | 127.551 | 366.6729 | 28.75% | 13.7368 | 0 | 40.8668 | 65.39% | 37.4927
4276 | 0 | 0 | 0 | 1.7 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2095 | 0 | 127.551 | 239.1219 | 18.75% | 10.5275 | 0 | 50.379 | 80.61% | 40.682
4277 | 0 | 1 | 1 | 1.1 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.1641 | 50.1432 | 0 | 125.1641 | 113.9577 | 8.934% | 6.4976 | 0 | 56.25 | 90% | 43.6456
4278 | 79 | 55 | 43 | 1.7 | 22.4 | 0 | 0 | 0 | 0 | 1.6309 | 0 | 0 | 1.6309 | 0 | 0 | 0 | 113.9577 | 45.3196 | 0 | 113.9577 | 0 | 0% | 0 | 0 | 56.25 | 90% | 46.9505
4279 | 350 | 220 | 110 | 0.7 | 26 | 0 | 0 | 0 | 43.3482 | 5.3834 | 0 | 0 | 5.3834 | 0 | 0 | 0 | 0 | 0 | 43.3482 | 0 | 43.3482 | 3.398% | 0 | 20.178 | 33.9183 | 54.27% | 25.5614
4280 | 539 | 421 | 155 | 3.1 | 28.3 | 0 | 0 | 0 | 71.0215 | 14.8649 | 0 | 0 | 14.8649 | 0 | 0 | 0 | 0 | 0 | 71.0215 | 0 | 114.3697 | 8.967% | 0 | 25 | 6.25 | 10% | 39.8649
4281 | 656 | 616 | 181 | 5 | 31.4 | 0 | 0 | 0 | 0 | 31.4993 | 0 | 0 | 31.4993 | 0 | 0 | 0 | 52.5536 | 18.5007 | 0 | 52.5536 | 61.8161 | 4.846% | 0 | 0 | 6.25 | 10% | 50
4282 | 731 | 784 | 195 | 6 | 33.3 | 0 | 0 | 0 | 0 | 37.5729 | 8.4501 | 0 | 37.5729 | 0 | 0 | 0 | 38.2653 | 12.4271 | 0 | 38.2653 | 23.5508 | 1.846% | 0 | 0 | 6.25 | 10% | 50
4283 | 771 | 909 | 206 | 6.6 | 34.1 | 0 | 0 | 0 | 203.1618 | 56.9625 | 0 | 6.9625 | 50 | 0 | 0 | 0 | 0 | 0 | 203.1618 | 0 | 226.7126 | 17.77% | 6.9625 | 0 | 12.541 | 20.07% | 50
4284 | 789 | 979 | 211 | 7.1 | 34.6 | 0 | 0 | 0 | 214.2446 | 58.0986 | 5.3534 | 8.0986 | 50 | 0 | 0 | 0 | 0 | 0 | 214.2446 | 0 | 440.9572 | 34.57% | 8.0986 | 0 | 19.8586 | 31.77% | 50
4285 | 798 | 992 | 206 | 7.3 | 34.6 | 0 | 0 | 0 | 220.1802 | 66.0751 | 0 | 16.0752 | 50 | 0 | 0 | 0 | 0 | 0 | 220.1802 | 0 | 661.1374 | 51.83% | 16.0752 | 0 | 34.3834 | 55.01% | 50
4286 | 800 | 951 | 196 | 7.8 | 34.5 | 0 | 0 | 0 | 218.9193 | 64.8322 | 0 | 14.8322 | 50 | 0 | 0 | 0 | 0 | 0 | 218.9193 | 0 | 880.0567 | 69% | 14.8322 | 0 | 47.7852 | 76.46% | 50
4287 | 789 | 857 | 181 | 9 | 34.2 | 0 | 0 | 0 | 209.2906 | 59.3683 | 0 | 9.3683 | 50 | 0 | 0 | 0 | 0 | 0 | 209.2906 | 0 | 1089.3473 | 85.4% | 9.3683 | 0 | 56.25 | 90% | 50
4288 | 733 | 704 | 168 | 8.2 | 33.8 | 0 | 0 | 0 | 186.1629 | 48.4898 | 0 | 1.6769e-12 | 48.4898 | 0 | 0 | 0 | 5.7117e-12 | 1.8516e-12 | 186.1629 | 5.7117e-12 | 1275.5102 | 100% | 1.6769e-12 | 1.097 | 55.0359 | 88.06% | 49.5869
4289 | 636 | 516 | 153 | 7.4 | 32.8 | 0 | 0 | 0 | 0 | 34.1215 | 0 | 0 | 34.1215 | 0 | 0 | 0 | 42.9022 | 14.3847 | 0 | 42.9022 | 1232.608 | 96.64% | 0 | 0 | 55.0359 | 88.06% | 48.5061
4290 | 478 | 312 | 126 | 6.8 | 31.6 | 0 | 0 | 0 | 5.5224e-12 | 16.829 | 0 | 0 | 16.829 | 0 | 0 | 0 | 80.8962 | 30.3694 | 5.5224e-12 | 80.8962 | 1151.7118 | 90.29% | 0 | 0 | 55.0359 | 88.06% | 47.1984
4291 | 221 | 120 | 73 | 7.4 | 29.4 | 0 | 0 | 0 | 0 | 4.0815 | 0 | 0 | 4.0815 | 0 | 0 | 0 | 107.473 | 41.7966 | 0 | 107.473 | 1044.2388 | 81.87% | 0 | 0 | 55.0359 | 88.06% | 45.8781
4292 | 8 | 10 | 9 | 6.1 | 26.9 | 0 | 0 | 0 | 0 | 0.1253 | 0 | 0 | 0.1253 | 0 | 0 | 0 | 109.2313 | 42.8379 | 0 | 109.2313 | 935.0075 | 73.3% | 0 | 0 | 55.0359 | 88.06% | 42.9632
4293 | 0 | 0 | 0 | 6.5 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5789 | 41.3811 | 0 | 105.5789 | 829.4286 | 65.03% | 0 | 0 | 55.0359 | 88.06% | 41.3811
4294 | 0 | 0 | 0 | 5.1 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4838 | 38.8325 | 0 | 99.4838 | 729.9448 | 57.23% | 0 | 0 | 55.0359 | 88.06% | 38.8325
4295 | 0 | 0 | 0 | 4.4 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.3009 | 36.7003 | 0 | 94.3009 | 635.6439 | 49.83% | 0 | 0 | 55.0359 | 88.06% | 36.7003
4296 | 0 | 0 | 0 | 3 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1103 | 35.4468 | 0 | 91.1103 | 544.5336 | 42.69% | 0 | 0 | 55.0359 | 88.06% | 35.4468
4297 | 0 | 0 | 0 | 1.9 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1282 | 34.6405 | 0 | 89.1282 | 455.4054 | 35.7% | 0 | 0 | 55.0359 | 88.06% | 34.6405
4298 | 0 | 0 | 0 | 1.1 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9052 | 34.1224 | 0 | 87.9052 | 367.5002 | 28.81% | 0 | 0 | 55.0359 | 88.06% | 34.1224
4299 | 0 | 0 | 0 | 1.1 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6455 | 33.6349 | 0 | 86.6455 | 280.8547 | 22.02% | 0 | 0 | 55.0359 | 88.06% | 33.6349
4300 | 0 | 0 | 0 | 1.5 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0415 | 34.2616 | 0 | 88.0415 | 192.8132 | 15.12% | 0.032 | 0 | 55.0648 | 88.1% | 34.2296
4301 | 0 | 1 | 1 | 2.5 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2636 | 36.8604 | 0 | 94.2636 | 98.5497 | 7.726% | 0 | 0 | 55.0648 | 88.1% | 36.8604
4302 | 102 | 60 | 44 | 3 | 23.3 | 0 | 0 | 0 | 0 | 1.6731 | 0 | 0 | 1.6731 | 0 | 0 | 0 | 98.5497 | 38.6287 | 0 | 98.5497 | 0 | 0% | 0 | 0 | 55.0648 | 88.1% | 40.3018
4303 | 363 | 229 | 116 | 1.8 | 26 | 0 | 0 | 0 | 44.8508 | 5.6689 | 0 | 0 | 5.6689 | 0 | 0 | 0 | 0 | 0 | 44.8508 | 0 | 44.8508 | 3.516% | 0 | 19.1071 | 33.9183 | 54.27% | 24.776
4304 | 541 | 428 | 160 | 3.4 | 28.5 | 0 | 0 | 0 | 35.6262 | 15.151 | 0 | 0 | 15.151 | 0 | 0 | 0 | 0 | 0 | 35.6262 | 0 | 80.477 | 6.309% | 0 | 25 | 6.25 | 10% | 40.151
4305 | 666 | 622 | 179 | 5.2 | 30.4 | 0 | 0 | 0 | 0 | 31.7803 | 0 | 0 | 31.7803 | 0 | 0 | 0 | 42.2117 | 14.2079 | 0 | 42.2117 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 45.9881
4306 | 734 | 787 | 194 | 5.8 | 32.5 | 0 | 0 | 0 | 0 | 34.4819 | 11.6873 | 0 | 34.4819 | 0 | 0 | 0 | 38.2653 | 12.4616 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.9435
4307 | 774 | 911 | 204 | 6.2 | 34 | 0 | 0 | 0 | 204.3402 | 56.9062 | 0 | 10.1786 | 46.7277 | 0 | 0 | 0 | 0 | 0 | 204.3402 | 0 | 204.3402 | 16.02% | 10.1786 | 0 | 15.447 | 24.72% | 46.7277
4308 | 785 | 979 | 213 | 6.7 | 34.5 | 0 | 0 | 0 | 85.2126 | 63.2424 | 0 | 17.4144 | 45.828 | 0 | 0 | 0 | 0 | 0 | 85.2126 | 0 | 289.5528 | 22.7% | 17.4144 | 0 | 31.1819 | 49.89% | 45.828
4309 | 789 | 994 | 215 | 7.2 | 34.8 | 0 | 0 | 0 | 217.5525 | 44.8433 | 21.144 | 0 | 44.8433 | 0 | 0 | 0 | 0 | 0 | 217.5525 | 0 | 507.1054 | 39.76% | 0 | 0 | 31.1819 | 49.89% | 44.8433
4310 | 779 | 949 | 211 | 7.3 | 35.2 | 0 | 0 | 0 | 213.0676 | 64.1717 | 0 | 19.5596 | 44.6122 | 0 | 0 | 0 | 0 | 0 | 213.0676 | 0 | 720.173 | 56.46% | 19.5596 | 0 | 48.8552 | 78.17% | 44.6122
4311 | 744 | 847 | 206 | 6.8 | 35.5 | 0 | 0 | 0 | 198.1211 | 52.618 | 5.3559 | 8.1841 | 44.4339 | 0 | 0 | 0 | 0 | 0 | 198.1211 | 0 | 918.2941 | 71.99% | 8.1841 | 0 | 56.25 | 90% | 44.4339
4312 | 695 | 699 | 189 | 7.1 | 35 | 0 | 0 | 0 | 176.3277 | 44.2111 | 3.4452 | 0 | 44.2111 | 0 | 0 | 0 | 0 | 0 | 176.3277 | 0 | 1094.6218 | 85.82% | 0 | 0 | 56.25 | 90% | 44.2111
4313 | 614 | 513 | 162 | 6.9 | 34.1 | 0 | 0 | 0 | 144.4004 | 33.7332 | 0 | 0 | 33.7332 | 0 | 0 | 0 | 0 | 0 | 144.4004 | 0 | 1239.0222 | 97.14% | 0 | 10.0392 | 45.1393 | 72.22% | 43.7724
4314 | 462 | 308 | 128 | 6.7 | 32.6 | 0 | 0 | 0 | 0 | 16.6212 | 0 | 0 | 16.6212 | 0 | 0 | 0 | 72.8964 | 26.9255 | 0 | 72.8964 | 1166.1258 | 91.42% | 0 | 0 | 45.1393 | 72.22% | 43.5467
4315 | 229 | 122 | 73 | 5.6 | 30.5 | 0 | 0 | 0 | 0 | 3.916 | 0 | 0 | 3.916 | 0 | 0 | 0 | 101.7767 | 39.2603 | 0 | 101.7767 | 1064.3491 | 83.44% | 0 | 0 | 45.1393 | 72.22% | 43.1763
4316 | 10 | 11 | 10 | 5.8 | 28.1 | 0 | 0 | 0 | 0 | 0.17707 | 0 | 0 | 0.17707 | 0 | 0 | 0 | 104.8653 | 40.8489 | 0 | 104.8653 | 959.4838 | 75.22% | 0 | 0 | 45.1393 | 72.22% | 41.026
4317 | 0 | 0 | 0 | 3.1 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6231 | 38.359 | 0 | 98.6231 | 860.8606 | 67.49% | 0 | 0 | 45.1393 | 72.22% | 38.359
4318 | 0 | 0 | 0 | 1.1 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6283 | 35.9343 | 0 | 92.6283 | 768.2324 | 60.23% | 0 | 0 | 45.1393 | 72.22% | 35.9343
4319 | 0 | 0 | 0 | 1.1 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.6385 | 21.9371 | 0 | 59.6385 | 708.5939 | 55.55% | 0 | 12.0418 | 31.8123 | 50.9% | 33.9789
4320 | 0 | 0 | 0 | 2.2 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0691 | 32.784 | 0 | 85.0691 | 623.5248 | 48.88% | 0 | 0 | 31.8123 | 50.9% | 32.784
4321 | 0 | 0 | 0 | 1.5 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6969 | 31.8857 | 0 | 82.6969 | 540.8279 | 42.4% | 0 | 0 | 31.8123 | 50.9% | 31.8857
4322 | 0 | 0 | 0 | 2.1 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0234 | 31.5835 | 0 | 82.0234 | 458.8044 | 35.97% | 0 | 0 | 31.8123 | 50.9% | 31.5835
4323 | 0 | 0 | 0 | 1.8 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9648 | 31.1546 | 0 | 80.9648 | 377.8396 | 29.62% | 0 | 0 | 31.8123 | 50.9% | 31.1546
4324 | 0 | 0 | 0 | 1.5 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6203 | 31.0612 | 0 | 80.6203 | 297.2193 | 23.3% | 0 | 0 | 31.8123 | 50.9% | 31.0612
4325 | 0 | 1 | 0 | 1.1 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.318 | 32.7241 | 0 | 84.318 | 212.9013 | 16.69% | 0 | 0 | 31.8123 | 50.9% | 32.7241
4326 | 177 | 62 | 36 | 0.4 | 21.6 | 0 | 0 | 0 | 0 | 1.3015 | 0 | 0 | 1.3015 | 0 | 0 | 0 | 87.2406 | 33.8975 | 0 | 87.2406 | 125.6607 | 9.852% | 0 | 0 | 31.8123 | 50.9% | 35.1989
4327 | 524 | 241 | 80 | 1.4 | 25.5 | 0 | 0 | 0 | 0 | 3.9504 | 0 | 0 | 3.9504 | 0 | 0 | 0 | 87.3954 | 33.676 | 0 | 87.3954 | 38.2653 | 3% | 0 | 0 | 31.8123 | 50.9% | 37.6264
4328 | 692 | 443 | 103 | 1.1 | 27.8 | 0 | 0 | 0 | 0 | 13.3677 | 0 | 0 | 13.3677 | 0 | 0 | 0 | 38.2653 | 12.6433 | 0 | 38.2653 | 0 | 0% | 0 | 13.4746 | 16.8994 | 27.04% | 39.4857
4329 | 781 | 637 | 120 | 2.8 | 30.4 | 0 | 0 | 0 | 0 | 31.0777 | 0 | 0 | 31.0777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 9.6224 | 6.25 | 10% | 40.7001
4330 | 832 | 801 | 131 | 4.4 | 32.6 | 0 | 0 | 0 | 213.1974 | 46.0837 | 0 | 4.2068 | 41.8769 | 0 | 0 | 0 | 0 | 0 | 213.1974 | 0 | 213.1974 | 16.71% | 4.2068 | 0 | 10.0511 | 16.08% | 41.8769
4331 | 856 | 921 | 140 | 5.3 | 34.1 | 0 | 0 | 0 | 228.8784 | 48.4814 | 8.2777 | 5.8566 | 42.6248 | 0 | 0 | 0 | 0 | 0 | 228.8784 | 0 | 442.0758 | 34.66% | 5.8566 | 0 | 15.3429 | 24.55% | 42.6248
4332 | 854 | 987 | 154 | 5.6 | 35 | 0 | 0 | 0 | 235.0121 | 62.6422 | 0 | 20.6595 | 41.9828 | 0 | 0 | 0 | 0 | 0 | 235.0121 | 0 | 677.0879 | 53.08% | 20.6595 | 0 | 34.01 | 54.42% | 41.9828
4333 | 842 | 1000 | 169 | 6.1 | 35.7 | 0 | 0 | 0 | 16.8031 | 65.9336 | 0 | 24.6138 | 41.3198 | 0 | 0 | 0 | 0 | 0 | 16.8031 | 0 | 693.891 | 54.4% | 24.6138 | 0 | 56.25 | 90% | 41.3198
4334 | 752 | 928 | 213 | 6.3 | 35.6 | 0 | 0 | 0 | 205.8669 | 41.2488 | 21.5253 | 0 | 41.2488 | 0 | 0 | 0 | 0 | 0 | 205.8669 | 0 | 899.7579 | 70.54% | 0 | 0 | 56.25 | 90% | 41.2488
4335 | 713 | 834 | 219 | 5.6 | 35.4 | 0 | 0 | 0 | 190.0763 | 41.253 | 15.5043 | 0 | 41.253 | 0 | 0 | 0 | 0 | 0 | 190.0763 | 0 | 1089.8342 | 85.44% | 0 | 0 | 56.25 | 90% | 41.253
4336 | 723 | 696 | 166 | 5.5 | 34.6 | 0 | 0 | 0 | 185.676 | 41.5705 | 5.7893 | 0 | 41.5705 | 0 | 0 | 0 | 0 | 0 | 185.676 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 41.5705
4337 | 648 | 516 | 145 | 5.5 | 34.1 | 0 | 0 | 0 | 0 | 29.7236 | 4.0955 | 0 | 29.7236 | 0 | 0 | 0 | 38.2653 | 12.3915 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 42.1151
4338 | 491 | 311 | 119 | 5.5 | 33.1 | 0 | 0 | 0 | 0 | 16.6026 | 0 | 0 | 16.6026 | 0 | 0 | 0 | 71.4531 | 26.277 | 0 | 71.4531 | 1165.7918 | 91.4% | 0 | 0 | 56.25 | 90% | 42.8796
4339 | 215 | 118 | 71 | 5.1 | 31.1 | 0 | 0 | 0 | 0 | 3.9495 | 0 | 0 | 3.9495 | 0 | 0 | 0 | 103.6524 | 39.9733 | 0 | 103.6524 | 1062.1394 | 83.27% | 0 | 0 | 56.25 | 90% | 43.9228
4340 | 10 | 10 | 9 | 4.2 | 28.8 | 0 | 0 | 0 | 0 | 0.12743 | 0 | 0 | 0.12743 | 0 | 0 | 0 | 106.3211 | 41.3832 | 0 | 106.3211 | 955.8182 | 74.94% | 0 | 0 | 56.25 | 90% | 41.5106
4341 | 0 | 0 | 0 | 2.1 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.771 | 38.4119 | 0 | 98.771 | 857.0473 | 67.19% | 0 | 0 | 56.25 | 90% | 38.4119
4342 | 0 | 0 | 0 | 1.9 | 25.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6942 | 35.9538 | 0 | 92.6942 | 764.353 | 59.93% | 0 | 0 | 56.25 | 90% | 35.9538
4343 | 0 | 0 | 0 | 0.6 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1286 | 34.1085 | 0 | 88.1286 | 676.2244 | 53.02% | 0 | 0 | 56.25 | 90% | 34.1085
4344 | 0 | 0 | 0 | 0.6 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2646 | 33.3689 | 0 | 86.2646 | 589.9599 | 46.25% | 0 | 0 | 56.25 | 90% | 33.3689
4345 | 0 | 0 | 0 | 1.4 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7254 | 33.1378 | 0 | 85.7254 | 504.2344 | 39.53% | 0 | 0 | 56.25 | 90% | 33.1378
4346 | 0 | 0 | 0 | 1.2 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8129 | 33.667 | 0 | 86.8129 | 417.4215 | 32.73% | 0 | 0 | 56.25 | 90% | 33.667
4347 | 0 | 0 | 0 | 1.2 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1929 | 36.4928 | 0 | 93.1929 | 324.2286 | 25.42% | 0 | 0 | 56.25 | 90% | 36.4928
4348 | 0 | 0 | 0 | 1.8 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4065 | 39.9285 | 0 | 101.4065 | 222.8221 | 17.47% | 0 | 0 | 56.25 | 90% | 39.9285
4349 | 1 | 1 | 0 | 1.3 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8933 | 43.1874 | 0 | 108.8933 | 113.9288 | 8.932% | 0 | 0 | 56.25 | 90% | 43.1874
4350 | 154 | 53 | 31 | 1.9 | 22.2 | 0 | 0 | 0 | 0 | 1.0636 | 0 | 0 | 1.0636 | 0 | 0 | 0 | 112.3766 | 44.6585 | 0 | 112.3766 | 1.5522 | 0.1217% | 0 | 0 | 56.25 | 90% | 45.7221
4351 | 540 | 235 | 71 | 1.2 | 26 | 0 | 0 | 0 | 75.6428 | 3.7167 | 0 | 0 | 3.7167 | 0 | 0 | 0 | 0 | 0 | 75.6428 | 0 | 77.195 | 6.052% | 0 | 20.178 | 33.9183 | 54.27% | 23.8947
4352 | 715 | 439 | 91 | 1.6 | 29.2 | 0 | 0 | 0 | 144.0851 | 12.7857 | 0 | 0 | 12.7857 | 0 | 0 | 0 | 0 | 0 | 144.0851 | 0 | 221.2801 | 17.35% | 0 | 25 | 6.25 | 10% | 37.7857
4353 | 817 | 635 | 100 | 1.7 | 30.5 | 0 | 0 | 0 | 0 | 30.6341 | 0 | 0 | 30.6341 | 0 | 0 | 0 | 54.4838 | 19.3659 | 0 | 54.4838 | 166.7963 | 13.08% | 0 | 0 | 6.25 | 10% | 50
4354 | 876 | 802 | 102 | 2 | 32.3 | 0 | 0 | 0 | 0 | 37.5299 | 7.4888 | 0 | 37.5299 | 0 | 0 | 0 | 38.2653 | 12.4701 | 0 | 38.2653 | 128.531 | 10.08% | 0 | 0 | 6.25 | 10% | 50
4355 | 905 | 923 | 104 | 2.2 | 33.8 | 0 | 0 | 0 | 245.4572 | 55.0685 | 0 | 5.0685 | 50 | 0 | 0 | 0 | 0 | 0 | 245.4572 | 0 | 373.9881 | 29.32% | 5.0685 | 0 | 10.8297 | 17.33% | 50
4356 | 924 | 996 | 104 | 4.8 | 34.2 | 0 | 0 | 0 | 256.6743 | 57.8115 | 5.7925 | 7.8115 | 50 | 0 | 0 | 0 | 0 | 0 | 256.6743 | 0 | 630.6624 | 49.44% | 7.8115 | 0 | 17.8879 | 28.62% | 50
4357 | 940 | 1015 | 97 | 5.7 | 34.7 | 0 | 0 | 0 | 264.754 | 67.0125 | 0 | 17.0125 | 50 | 0 | 0 | 0 | 0 | 0 | 264.754 | 0 | 895.4164 | 70.2% | 17.0125 | 0 | 33.2597 | 53.22% | 50
4358 | 921 | 965 | 100 | 6.9 | 34.7 | 0 | 0 | 0 | 141.93 | 65.5112 | 0 | 15.5112 | 50 | 0 | 0 | 0 | 0 | 0 | 141.93 | 0 | 1037.3465 | 81.33% | 15.5112 | 0 | 47.2751 | 75.64% | 50
4359 | 881 | 861 | 108 | 7.2 | 34.4 | 0 | 0 | 0 | 238.1637 | 59.2913 | 0 | 9.9329 | 49.3585 | 0 | 0 | 0 | 0 | 0 | 238.1637 | 0 | 1275.5102 | 100% | 9.9329 | 0 | 56.25 | 90% | 49.3585
4360 | 739 | 670 | 133 | 6.9 | 34 | 0 | 0 | 0 | 0 | 36.1825 | 10.1841 | 0 | 36.1825 | 0 | 0 | 0 | 38.2653 | 12.396 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 48.5785
4361 | 703 | 514 | 114 | 6.7 | 33.9 | 0 | 0 | 0 | 0 | 34.1153 | 4.9738e-14 | 0 | 34.1153 | 0 | 0 | 0 | 41.0387 | 13.5539 | 0 | 41.0387 | 1196.2062 | 93.78% | 0 | 0 | 56.25 | 90% | 47.6691
4362 | 537 | 304 | 95 | 5.8 | 33 | 0 | 0 | 0 | 79.304 | 16.1766 | 0 | 0 | 16.1766 | 0 | 0 | 0 | 0 | 0 | 79.304 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 41.1766
4363 | 245 | 110 | 56 | 3.7 | 31.5 | 0 | 0 | 0 | 0 | 3.0043 | 0 | 0 | 3.0043 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 1275.5102 | 100% | 0 | 17.0479 | 9.7142 | 15.54% | 20.0522
4364 | 1 | 7 | 7 | 3.6 | 28.1 | 0 | 0 | 0 | 0 | 0.007051 | 0 | 0 | 0.007051 | 0 | 0 | 0 | 107.8898 | 42.1303 | 0 | 107.8898 | 1167.6204 | 91.54% | 0 | 0 | 9.7142 | 15.54% | 42.1373
4365 | 0 | 0 | 0 | 4.9 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8297 | 39.8812 | 0 | 101.8297 | 1065.7906 | 83.56% | 0 | 0 | 9.7142 | 15.54% | 39.8812
4366 | 0 | 0 | 0 | 3.8 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0716 | 37.5582 | 0 | 96.0716 | 969.719 | 76.03% | 0 | 0 | 9.7142 | 15.54% | 37.5582
4367 | 0 | 0 | 0 | 2.5 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3553 | 35.9496 | 0 | 92.3553 | 877.3637 | 68.79% | 0 | 0 | 9.7142 | 15.54% | 35.9496
4368 | 0 | 0 | 0 | 3.9 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.8024 | 0 | 38.2653 | 839.0984 | 65.79% | 0 | 0 | 9.7142 | 15.54% | 12.8024
4369 | 0 | 0 | 0 | 4 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7189 | 28.0964 | 0 | 73.7189 | 765.3795 | 60.01% | 0 | 0 | 9.7142 | 15.54% | 28.0964
4370 | 0 | 0 | 0 | 3.2 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.1686 | 35.2226 | 0 | 90.1686 | 675.2109 | 52.94% | 0 | 0 | 9.7142 | 15.54% | 35.2226
4371 | 0 | 0 | 0 | 2.4 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5039 | 37.5289 | 0 | 95.5039 | 579.707 | 45.45% | 0 | 0 | 9.7142 | 15.54% | 37.5289
4372 | 0 | 0 | 0 | 2.1 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8633 | 40.7015 | 0 | 102.8633 | 476.8436 | 37.38% | 0 | 0 | 9.7142 | 15.54% | 40.7015
4373 | 0 | 1 | 1 | 2.6 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.0529 | 43.9047 | 0 | 110.0529 | 366.7908 | 28.76% | 0 | 0 | 9.7142 | 15.54% | 43.9047
4374 | 118 | 51 | 34 | 3.3 | 18.8 | 0 | 0 | 0 | 0 | 1.2284 | 0 | 0 | 1.2284 | 0 | 0 | 0 | 114.0411 | 45.6497 | 0 | 114.0411 | 252.7496 | 19.82% | 0 | 0 | 9.7142 | 15.54% | 46.8781
4375 | 391 | 213 | 94 | 4.3 | 20.8 | 0 | 0 | 0 | 0 | 4.8117 | 0 | 0 | 4.8117 | 0 | 0 | 0 | 110.1132 | 43.8031 | 0 | 110.1132 | 142.6365 | 11.18% | 0 | 0 | 9.7142 | 15.54% | 48.6148
4376 | 621 | 421 | 119 | 6.2 | 23.4 | 0 | 0 | 0 | 0 | 14.0034 | 0 | 0 | 14.0034 | 0 | 0 | 0 | 91.4905 | 35.5946 | 0 | 91.4905 | 51.1459 | 4.01% | 0 | 0 | 9.7142 | 15.54% | 49.598
4377 | 749 | 621 | 130 | 6.5 | 25.2 | 0 | 0 | 0 | 0 | 31.7733 | 0 | 0 | 31.7733 | 0 | 0 | 0 | 51.1459 | 18.2267 | 0 | 51.1459 | 0 | 0% | 0 | 0 | 9.7142 | 15.54% | 50
4378 | 814 | 786 | 135 | 6.1 | 26.8 | 0 | 0 | 0 | 0 | 46.8699 | 0 | 0 | 46.8699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.1301 | 6.25 | 10% | 50
4379 | 830 | 904 | 151 | 5.4 | 28.1 | 0 | 0 | 0 | 221.0361 | 57.3317 | 0 | 7.3317 | 50 | 0 | 0 | 0 | 0 | 0 | 221.0361 | 0 | 221.0361 | 17.33% | 7.3317 | 0 | 12.8747 | 20.6% | 50
4380 | 839 | 974 | 161 | 4.5 | 29.2 | 0 | 0 | 0 | 231.3064 | 63.66 | 0 | 13.66 | 50 | 0 | 0 | 0 | 0 | 0 | 231.3064 | 0 | 452.3425 | 35.46% | 13.66 | 0 | 25.2173 | 40.35% | 50
4381 | 865 | 993 | 145 | 3.4 | 30.4 | 0 | 0 | 0 | 243.9904 | 60.9979 | 3.9891 | 10.9979 | 50 | 0 | 0 | 0 | 0 | 0 | 243.9904 | 0 | 696.3329 | 54.59% | 10.9979 | 0 | 35.1545 | 56.25% | 50
4382 | 845 | 948 | 152 | 4.4 | 31.3 | 0 | 0 | 0 | 235.4868 | 63.7741 | 0 | 13.7741 | 50 | 0 | 0 | 0 | 0 | 0 | 235.4868 | 0 | 931.8198 | 73.05% | 13.7741 | 0 | 47.6002 | 76.16% | 50
4383 | 808 | 845 | 154 | 5.3 | 31 | 0 | 0 | 0 | 218.103 | 58.6822 | 0 | 9.573 | 49.1092 | 0 | 0 | 0 | 0 | 0 | 218.103 | 0 | 1149.9228 | 90.15% | 9.573 | 0 | 56.25 | 90% | 49.1092
4384 | 772 | 699 | 138 | 4.9 | 30.9 | 0 | 0 | 0 | 125.5874 | 48.417 | 0.03173 | 0 | 48.417 | 0 | 0 | 0 | 0 | 0 | 125.5874 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 48.417
4385 | 613 | 479 | 127 | 5 | 30.3 | 0 | 0 | 0 | 0 | 31.8451 | 0 | 0 | 31.8451 | 0 | 0 | 0 | 45.8158 | 15.7293 | 0 | 45.8158 | 1229.6944 | 96.41% | 0 | 8.4555e-13 | 56.25 | 90% | 47.5744
4386 | 524 | 302 | 99 | 5.2 | 28.7 | 0 | 0 | 0 | 0 | 16.4739 | 0 | 0 | 16.4739 | 0 | 0 | 0 | 80.9336 | 30.6576 | 0 | 80.9336 | 1148.7608 | 90.06% | 0 | 0 | 56.25 | 90% | 47.1315
4387 | 236 | 106 | 56 | 5.1 | 26.7 | 0 | 0 | 0 | 0 | 3.0704 | 0 | 0 | 3.0704 | 0 | 0 | 0 | 109.3892 | 42.9275 | 0 | 109.3892 | 1039.3716 | 81.49% | 0 | 0 | 56.25 | 90% | 45.9979
4388 | 6 | 7 | 6 | 4.4 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3387 | 42.661 | 0 | 108.3387 | 931.0329 | 72.99% | 0 | 0 | 56.25 | 90% | 42.661
4389 | 0 | 0 | 0 | 4.4 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7309 | 40.4299 | 0 | 102.7309 | 828.302 | 64.94% | 0 | 0 | 56.25 | 90% | 40.4299
4390 | 0 | 0 | 0 | 4.5 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9085 | 38.0345 | 0 | 96.9085 | 731.3936 | 57.34% | 0 | 0 | 56.25 | 90% | 38.0345
4391 | 0 | 0 | 0 | 2.7 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6421 | 36.2351 | 0 | 92.6421 | 638.7515 | 50.08% | 0 | 0 | 56.25 | 90% | 36.2351
4392 | 0 | 0 | 0 | 1.6 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3884 | 27.9541 | 0 | 73.3884 | 565.3631 | 44.32% | 0 | 0 | 56.25 | 90% | 27.9541
4393 | 0 | 0 | 0 | 2.7 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8892 | 35.0959 | 0 | 89.8892 | 475.4739 | 37.28% | 0 | 0 | 56.25 | 90% | 35.0959
4394 | 0 | 0 | 0 | 2.8 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8208 | 35.458 | 0 | 90.8208 | 384.6532 | 30.16% | 0 | 0 | 56.25 | 90% | 35.458
4395 | 0 | 0 | 0 | 3.1 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1912 | 37.7768 | 0 | 96.1912 | 288.4619 | 22.62% | 0 | 0 | 56.25 | 90% | 37.7768
4396 | 0 | 0 | 0 | 2.2 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3964 | 40.9313 | 0 | 103.3964 | 185.0655 | 14.51% | 0 | 0 | 56.25 | 90% | 40.9313
4397 | 0 | 1 | 1 | 1.3 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.9278 | 44.2166 | 0 | 110.9278 | 74.1377 | 5.812% | 0 | 0 | 56.25 | 90% | 44.2166
4398 | 160 | 54 | 31 | 1.5 | 20.4 | 0 | 0 | 0 | 0 | 1.0738 | 0 | 0 | 1.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.1377 | 5.812% | 0 | 16.3576 | 38.1465 | 61.03% | 17.4314
4399 | 522 | 228 | 71 | 1.8 | 22.2 | 0 | 0 | 0 | 71.8502 | 3.7894 | 7.3719e-14 | 0 | 3.7894 | 0 | 0 | 0 | 0 | 0 | 71.8502 | 0 | 145.988 | 11.45% | 0 | 25 | 10.4782 | 16.77% | 28.7894
4400 | 684 | 428 | 98 | 3.2 | 24 | 0 | 0 | 0 | 0 | 13.168 | 0 | 0 | 13.168 | 0 | 0 | 0 | 93.3404 | 36.3394 | 0 | 93.3404 | 52.6476 | 4.128% | 0 | 0 | 10.4782 | 16.77% | 49.5075
4401 | 758 | 616 | 120 | 4.6 | 25.5 | 0 | 0 | 0 | 0 | 31.146 | 0 | 0 | 31.146 | 0 | 0 | 0 | 52.6476 | 18.854 | 0 | 52.6476 | 0 | 0% | 0 | 0 | 10.4782 | 16.77% | 50
4402 | 805 | 777 | 135 | 4.7 | 26.7 | 0 | 0 | 0 | 205.276 | 46.1796 | 0 | 0 | 46.1796 | 0 | 0 | 0 | 0 | 0 | 205.276 | 0 | 205.276 | 16.09% | 0 | 3.8204 | 6.25 | 10% | 50
4403 | 846 | 902 | 137 | 4.2 | 28.3 | 0 | 0 | 0 | 226.737 | 56.4052 | 0 | 6.4052 | 50 | 0 | 0 | 0 | 0 | 0 | 226.737 | 0 | 432.013 | 33.87% | 6.4052 | 0 | 12.0375 | 19.26% | 50
4404 | 828 | 961 | 159 | 3.9 | 29.7 | 0 | 0 | 0 | 228.5247 | 59.6521 | 2.8161 | 9.7254 | 49.9267 | 0 | 0 | 0 | 0 | 0 | 228.5247 | 0 | 660.5378 | 51.79% | 9.7254 | 0 | 20.825 | 33.32% | 49.9267
4405 | 833 | 975 | 159 | 4.5 | 30.5 | 0 | 0 | 0 | 152.7295 | 65.3458 | 0 | 15.6907 | 49.6551 | 0 | 0 | 0 | 0 | 0 | 152.7295 | 0 | 813.2672 | 63.76% | 15.6907 | 0 | 35.0024 | 56% | 49.6551
4406 | 816 | 927 | 161 | 5.2 | 31.1 | 0 | 0 | 0 | 226.0025 | 63.7597 | 0 | 14.3079 | 49.4518 | 0 | 0 | 0 | 0 | 0 | 226.0025 | 0 | 1039.2697 | 81.48% | 14.3079 | 0 | 47.9305 | 76.69% | 49.4518
4407 | 770 | 823 | 165 | 6.4 | 30.9 | 0 | 0 | 0 | 206.0373 | 57.6384 | 0 | 9.2075 | 48.4309 | 0 | 0 | 0 | 0 | 0 | 206.0373 | 0 | 1245.3071 | 97.63% | 9.2075 | 0 | 56.25 | 90% | 48.4309
4408 | 733 | 682 | 149 | 6.1 | 30.6 | 0 | 0 | 0 | 0 | 35.3721 | 12.2578 | 0 | 35.3721 | 0 | 0 | 0 | 38.2653 | 12.5394 | 0 | 38.2653 | 1207.0418 | 94.63% | 0 | 0 | 56.25 | 90% | 47.9114
4409 | 653 | 499 | 129 | 5.6 | 30 | 0 | 0 | 0 | 0 | 33.6397 | 0 | 0 | 33.6397 | 0 | 0 | 0 | 40.6952 | 13.5865 | 0 | 40.6952 | 1166.3466 | 91.44% | 0 | 0 | 56.25 | 90% | 47.2262
4410 | 530 | 304 | 99 | 5.2 | 28.9 | 0 | 0 | 0 | 109.1636 | 16.6294 | 0 | 0 | 16.6294 | 0 | 0 | 0 | 0 | 0 | 109.1636 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 41.6294
4411 | 289 | 117 | 56 | 4.5 | 27.5 | 0 | 0 | 0 | 0 | 3.16 | 0 | 0 | 3.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 20.178 | 6.25 | 10% | 23.338
4412 | 14 | 9 | 8 | 3.3 | 25.8 | 0 | 0 | 0 | 0 | 0.080233 | 0 | 0 | 0.080233 | 0 | 0 | 0 | 107.2634 | 42.1198 | 0 | 107.2634 | 1168.2468 | 91.59% | 0 | 0 | 6.25 | 10% | 42.2
4413 | 0 | 0 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.239 | 40.1486 | 0 | 102.239 | 1066.0079 | 83.58% | 0 | 0 | 6.25 | 10% | 40.1486
4414 | 0 | 0 | 0 | 4.8 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.1892 | 0 | 127.551 | 938.4568 | 73.58% | 13.5127 | 0 | 18.4595 | 29.54% | 37.6765
4415 | 0 | 0 | 0 | 3.5 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.383 | 36.1167 | 0 | 92.383 | 846.0738 | 66.33% | 0 | 0 | 18.4595 | 29.54% | 36.1167
4416 | 0 | 0 | 0 | 1.9 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5144 | 35.2853 | 0 | 90.5144 | 755.5594 | 59.24% | 0 | 0 | 18.4595 | 29.54% | 35.2853
4417 | 0 | 0 | 0 | 1 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9102 | 35.0792 | 0 | 89.9102 | 665.6492 | 52.19% | 0 | 0 | 18.4595 | 29.54% | 35.0792
4418 | 0 | 0 | 0 | 1.5 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7454 | 38.9123 | 0 | 98.7454 | 566.9038 | 44.45% | 3.5267 | 0 | 21.6461 | 34.63% | 35.3856
4419 | 0 | 0 | 0 | 0.5 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3531 | 0 | 127.551 | 439.3528 | 34.45% | 13.873 | 0 | 34.1812 | 54.69% | 37.4802
4420 | 0 | 0 | 0 | 1.6 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3801 | 0 | 127.551 | 311.8018 | 24.45% | 10.7343 | 0 | 43.8803 | 70.21% | 40.6458
4421 | 0 | 0 | 0 | 1.8 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4982 | 0 | 127.551 | 184.2508 | 14.45% | 7.6451 | 0 | 50.7881 | 81.26% | 43.8531
4422 | 54 | 46 | 37 | 1.6 | 19.2 | 0 | 0 | 0 | 0 | 1.368 | 0 | 1.368 | 0 | 0 | 0 | 0 | 127.551 | 51.4575 | 0 | 127.551 | 56.6997 | 4.445% | 6.0449 | 0 | 56.25 | 90% | 46.7806
4423 | 336 | 207 | 104 | 2.6 | 21.4 | 0 | 0 | 0 | 39.3892 | 5.1991 | 0 | 0 | 5.1991 | 0 | 0 | 0 | 0 | 0 | 39.3892 | 0 | 96.089 | 7.533% | 0 | 25 | 28.5817 | 45.73% | 30.1991
4424 | 502 | 397 | 152 | 1.5 | 24.3 | 0 | 0 | 0 | 95.4871 | 14.2322 | 0 | 0 | 14.2322 | 0 | 0 | 0 | 0 | 0 | 95.4871 | 0 | 191.576 | 15.02% | 0 | 20.178 | 6.25 | 10% | 34.4102
4425 | 597 | 584 | 192 | 2.9 | 26.4 | 0 | 0 | 0 | 0 | 30.3199 | 0 | 0 | 30.3199 | 0 | 0 | 0 | 54.6884 | 19.6801 | 0 | 54.6884 | 136.8877 | 10.73% | 0 | 0 | 6.25 | 10% | 50
4426 | 631 | 739 | 231 | 4.4 | 27.4 | 0 | 0 | 0 | 0 | 43.0513 | 1.3268 | 5.7084 | 37.3429 | 0 | 0 | 0 | 38.2653 | 12.6571 | 0 | 38.2653 | 98.6224 | 7.732% | 5.7084 | 0 | 11.4079 | 18.25% | 50
4427 | 700 | 867 | 229 | 4.8 | 28.4 | 0 | 0 | 0 | 183.9003 | 50 | 5.2159 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 183.9003 | 0 | 282.5227 | 22.15% | 0 | 0 | 11.4079 | 18.25% | 50
4428 | 726 | 939 | 233 | 5.8 | 29.5 | 0 | 0 | 0 | 196.5504 | 62.3406 | 0 | 12.6674 | 49.6732 | 0 | 0 | 0 | 0 | 0 | 196.5504 | 0 | 479.0731 | 37.56% | 12.6674 | 0 | 22.8536 | 36.57% | 49.6732
4429 | 738 | 956 | 228 | 5.5 | 30.2 | 0 | 0 | 0 | 203.6075 | 64.7916 | 0 | 15.1713 | 49.6203 | 0 | 0 | 0 | 0 | 0 | 203.6075 | 0 | 682.6805 | 53.52% | 15.1713 | 0 | 36.5618 | 58.5% | 49.6203
4430 | 744 | 916 | 213 | 5.2 | 30.5 | 0 | 0 | 0 | 204.3753 | 63.181 | 0 | 13.6053 | 49.5757 | 0 | 0 | 0 | 0 | 0 | 204.3753 | 0 | 887.0559 | 69.55% | 13.6053 | 0 | 48.8551 | 78.17% | 49.5757
4431 | 750 | 825 | 183 | 4.6 | 31 | 0 | 0 | 0 | 201.7951 | 57.0344 | 0 | 8.1842 | 48.8501 | 0 | 0 | 0 | 0 | 0 | 201.7951 | 0 | 1088.851 | 85.37% | 8.1842 | 0 | 56.25 | 90% | 48.8501
4432 | 757 | 691 | 140 | 5.6 | 30.7 | 0 | 0 | 0 | 186.6592 | 48.1651 | 0 | 0 | 48.1651 | 0 | 0 | 0 | 0 | 0 | 186.6592 | 0 | 1275.5102 | 100% | 0 | 6.4202e-15 | 56.25 | 90% | 48.1651
4433 | 703 | 515 | 115 | 5.1 | 30.4 | 0 | 0 | 0 | 0 | 34.6163 | 0 | 0 | 34.6163 | 0 | 0 | 0 | 39.3145 | 12.9887 | 0 | 39.3145 | 1236.1957 | 96.92% | 0 | 0 | 56.25 | 90% | 47.6051
4434 | 579 | 316 | 91 | 5.6 | 29.4 | 0 | 0 | 0 | 0 | 17.1111 | 0 | 0 | 17.1111 | 0 | 0 | 0 | 79.3779 | 29.9383 | 0 | 79.3779 | 1156.8178 | 90.69% | 0 | 0 | 56.25 | 90% | 47.0494
4435 | 361 | 131 | 57 | 5.6 | 27.4 | 0 | 0 | 0 | 51.0022 | 3.3528 | 0 | 0 | 3.3528 | 0 | 0 | 0 | 0 | 0 | 51.0022 | 0 | 1207.82 | 94.69% | 0 | 24.8394 | 28.7594 | 46.02% | 28.1922
4436 | 19 | 11 | 9 | 5.5 | 24.8 | 0 | 0 | 0 | 0 | 0.13527 | 0 | 0 | 0.13527 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 1207.82 | 94.69% | 0 | 0 | 28.7594 | 46.02% | 0.13527
4437 | 0 | 0 | 0 | 4.4 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4779 | 40.7502 | 0 | 103.4779 | 1104.3421 | 86.58% | 0 | 0 | 28.7594 | 46.02% | 40.7502
4438 | 0 | 0 | 0 | 3.3 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9431 | 38.3604 | 0 | 97.9431 | 1006.399 | 78.9% | 0 | 0 | 28.7594 | 46.02% | 38.3604
4439 | 0 | 0 | 0 | 1.4 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5375 | 36.5109 | 0 | 93.5375 | 912.8615 | 71.57% | 0 | 0 | 28.7594 | 46.02% | 36.5109
4440 | 0 | 0 | 0 | 1.1 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.662 | 35.7574 | 0 | 91.662 | 821.1994 | 64.38% | 0 | 0 | 28.7594 | 46.02% | 35.7574
4441 | 0 | 0 | 0 | 0.9 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5957 | 35.334 | 0 | 90.5957 | 730.6038 | 57.28% | 0 | 0 | 28.7594 | 46.02% | 35.334
4442 | 0 | 0 | 0 | 1 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5221 | 35.7463 | 0 | 91.5221 | 639.0817 | 50.1% | 0 | 0 | 28.7594 | 46.02% | 35.7463
4443 | 0 | 0 | 0 | 1.3 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6483 | 37.9593 | 0 | 96.6483 | 542.4335 | 42.53% | 0 | 0 | 28.7594 | 46.02% | 37.9593
4444 | 0 | 0 | 0 | 1.3 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4675 | 40.9619 | 0 | 103.4675 | 438.966 | 34.41% | 0 | 0 | 28.7594 | 46.02% | 40.9619
4445 | 0 | 0 | 0 | 1.1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8621 | 45.0512 | 0 | 112.8621 | 326.1038 | 25.57% | 0.9112 | 0 | 29.5827 | 47.33% | 44.14
4446 | 36 | 45 | 40 | 1.6 | 20 | 0 | 0 | 0 | 0 | 1.506 | 0 | 1.506 | 0 | 0 | 0 | 0 | 127.551 | 51.389 | 0 | 127.551 | 198.5528 | 15.57% | 5.7203 | 0 | 34.7514 | 55.6% | 47.1747
4447 | 220 | 189 | 121 | 1.7 | 22.6 | 0 | 0 | 0 | 0 | 5.7398 | 0 | 0 | 5.7398 | 0 | 0 | 0 | 109.0888 | 43.2106 | 0 | 109.0888 | 89.4641 | 7.014% | 0 | 0 | 34.7514 | 55.6% | 48.9504
4448 | 387 | 380 | 190 | 2.8 | 24.6 | 0 | 0 | 0 | 0 | 15.2147 | 0 | 0 | 15.2147 | 0 | 0 | 0 | 89.4641 | 34.6326 | 0 | 89.4641 | 0 | 0% | 0 | 0 | 34.7514 | 55.6% | 49.8473
4449 | 537 | 576 | 222 | 2.7 | 26 | 0 | 0 | 0 | 121.7087 | 30.3566 | 0 | 0 | 30.3566 | 0 | 0 | 0 | 0 | 0 | 121.7087 | 0 | 121.7087 | 9.542% | 0 | 19.6434 | 13.0114 | 20.82% | 50
4450 | 634 | 745 | 237 | 2 | 27.7 | 0 | 0 | 0 | 159.3919 | 43.8907 | 0 | 0 | 43.8907 | 0 | 0 | 0 | 0 | 0 | 159.3919 | 0 | 281.1007 | 22.04% | 0 | 6.1093 | 6.25 | 10% | 50
4451 | 668 | 866 | 258 | 2 | 29.4 | 0 | 0 | 0 | 176.5228 | 53.4769 | 0 | 3.4769 | 50 | 0 | 0 | 0 | 0 | 0 | 176.5228 | 0 | 457.6235 | 35.88% | 3.4769 | 0 | 9.3916 | 15.03% | 50
4452 | 691 | 936 | 264 | 3.6 | 30.5 | 0 | 0 | 0 | 187.9869 | 60.8809 | 0 | 11.3763 | 49.5047 | 0 | 0 | 0 | 0 | 0 | 187.9869 | 0 | 645.6104 | 50.62% | 11.3763 | 0 | 19.6707 | 31.47% | 49.5047
4453 | 698 | 948 | 261 | 3.4 | 31.2 | 0 | 0 | 0 | 193.4367 | 62.9586 | 0 | 13.7714 | 49.1872 | 0 | 0 | 0 | 0 | 0 | 193.4367 | 0 | 839.0471 | 65.78% | 13.7714 | 0 | 32.114 | 51.38% | 49.1872
4454 | 683 | 910 | 262 | 3.2 | 32.7 | 0 | 0 | 0 | 187.79 | 60.8843 | 0 | 11.8392 | 49.0451 | 0 | 0 | 0 | 0 | 0 | 187.79 | 0 | 1026.8371 | 80.5% | 11.8392 | 0 | 42.8115 | 68.5% | 49.0451
4455 | 647 | 811 | 254 | 4.7 | 32.9 | 0 | 0 | 0 | 171.4754 | 55.6039 | 1.0658e-14 | 7.3582 | 48.2457 | 0 | 0 | 0 | 0 | 0 | 171.4754 | 0 | 1198.3125 | 93.95% | 7.3582 | 0 | 49.46 | 79.14% | 48.2457
4456 | 589 | 656 | 224 | 4.8 | 31.9 | 0 | 0 | 0 | 77.1977 | 45.0161 | 0 | 0 | 45.0161 | 0 | 0 | 0 | 0 | 0 | 77.1977 | 0 | 1275.5102 | 100% | 0 | 2.5848 | 46.5994 | 74.56% | 47.6009
4457 | 535 | 491 | 183 | 4.6 | 32.4 | 0 | 0 | 0 | 0 | 32.1684 | 0 | 0 | 32.1684 | 0 | 0 | 0 | 42.9996 | 14.4451 | 0 | 42.9996 | 1232.5107 | 96.63% | 0 | 0 | 46.5994 | 74.56% | 46.6135
4458 | 58 | 154 | 127 | 4.6 | 30.2 | 0 | 0 | 0 | 0 | 8.6374 | 0 | 0 | 8.6374 | 0 | 0 | 0 | 96.2847 | 36.9845 | 0 | 96.2847 | 1136.226 | 89.08% | 0 | 0 | 46.5994 | 74.56% | 45.6219
4459 | 19 | 52 | 49 | 4.7 | 26.9 | 0 | 0 | 0 | 0 | 2.6956 | 0 | 0 | 2.6956 | 0 | 0 | 0 | 106.7294 | 41.7745 | 0 | 106.7294 | 1029.4966 | 80.71% | 0 | 0 | 46.5994 | 74.56% | 44.4701
4460 | 4 | 9 | 9 | 5.1 | 25.2 | 0 | 0 | 0 | 0 | 0.12588 | 0 | 0 | 0.12588 | 0 | 0 | 0 | 106.1797 | 41.719 | 0 | 106.1797 | 923.3169 | 72.39% | 0 | 0 | 46.5994 | 74.56% | 41.8449
4461 | 0 | 0 | 0 | 3.9 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5315 | 40.228 | 0 | 102.5315 | 820.7854 | 64.35% | 0 | 0 | 46.5994 | 74.56% | 40.228
4462 | 0 | 0 | 0 | 1.8 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4141 | 38.0832 | 0 | 97.4141 | 723.3714 | 56.71% | 0 | 0 | 46.5994 | 74.56% | 38.0832
4463 | 0 | 0 | 0 | 2.4 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0349 | 36.3103 | 0 | 93.0349 | 630.3365 | 49.42% | 0 | 0 | 46.5994 | 74.56% | 36.3103
4464 | 0 | 0 | 0 | 1.8 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7044 | 35.2031 | 0 | 90.7044 | 539.6321 | 42.31% | 0 | 0 | 46.5994 | 74.56% | 35.2031
4465 | 0 | 0 | 0 | 1.1 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9224 | 34.4636 | 0 | 88.9224 | 450.7098 | 35.34% | 0 | 0 | 46.5994 | 74.56% | 34.4636
4466 | 0 | 0 | 0 | 1 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9741 | 34.0346 | 0 | 87.9741 | 362.7357 | 28.44% | 0 | 0 | 46.5994 | 74.56% | 34.0346
4467 | 0 | 0 | 0 | 0.4 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362.7357 | 28.44% | 0 | 0 | 46.5994 | 74.56% | 0
4468 | 0 | 0 | 0 | 1.5 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362.7357 | 28.44% | 0 | 0 | 46.5994 | 74.56% | 0
4469 | 0 | 0 | 0 | 0.9 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6323 | 36.6543 | 0 | 93.6323 | 269.1034 | 21.1% | 0 | 0 | 46.5994 | 74.56% | 36.6543
4470 | 42 | 46 | 39 | 1.4 | 21.3 | 0 | 0 | 0 | 0 | 1.4482 | 0 | 1.4482 | 0 | 0 | 0 | 0 | 121.865 | 48.8211 | 0 | 121.865 | 147.2384 | 11.54% | 10.6806 | 0 | 56.25 | 90% | 39.5887
4471 | 246 | 197 | 121 | 0.7 | 24.4 | 0 | 0 | 0 | 0 | 5.8376 | 0 | 0 | 5.8376 | 0 | 0 | 0 | 93.4127 | 36.3374 | 0 | 93.4127 | 53.8257 | 4.22% | 0 | 0 | 56.25 | 90% | 42.1749
4472 | 421 | 391 | 184 | 0.9 | 27.8 | 0 | 0 | 0 | 77.1449 | 14.8805 | 0 | 0 | 14.8805 | 0 | 0 | 0 | 0 | 0 | 77.1449 | 0 | 130.9706 | 10.27% | 0 | 17.9812 | 36.3496 | 58.16% | 32.8617
4473 | 511 | 576 | 237 | 3 | 34.1 | 0 | 0 | 0 | 114.9113 | 29.6554 | 0 | 0 | 29.6554 | 0 | 0 | 0 | 0 | 0 | 114.9113 | 0 | 245.8819 | 19.28% | 0 | 0 | 36.3496 | 58.16% | 29.6554
4474 | 521 | 735 | 312 | 4.9 | 35.8 | 0 | 0 | 0 | 125.9385 | 43.1056 | 0 | 0 | 43.1056 | 0 | 0 | 0 | 0 | 0 | 125.9385 | 0 | 371.8204 | 29.15% | 0 | 0 | 36.3496 | 58.16% | 43.1056
4475 | 212 | 625 | 426 | 5.9 | 35.9 | 0 | 0 | 0 | 40.8455 | 38.9311 | 0 | 0 | 38.9311 | 0 | 0 | 0 | 0 | 0 | 40.8455 | 0 | 412.6659 | 32.35% | 0 | 0 | 36.3496 | 58.16% | 38.9311
4476 | 332 | 752 | 421 | 2.7 | 36.6 | 0 | 0 | 0 | 81.1453 | 47.1808 | 0 | 3.2469 | 43.9339 | 0 | 0 | 0 | 0 | 0 | 81.1453 | 0 | 493.8113 | 38.71% | 3.2469 | 0 | 39.2834 | 62.85% | 43.9339
4477 | 273 | 703 | 424 | 4.4 | 37.5 | 0 | 0 | 0 | 63.8012 | 45.4846 | 0 | 2.215 | 43.2696 | 0 | 0 | 0 | 0 | 0 | 63.8012 | 0 | 557.6125 | 43.72% | 2.215 | 0 | 41.2847 | 66.06% | 43.2696
4478 | 3 | 232 | 226 | 6.6 | 35.7 | 0 | 0 | 0 | 0 | 13.6336 | 0 | 0 | 13.6336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557.6125 | 43.72% | 0 | 0 | 41.2847 | 66.06% | 13.6336
4479 | 17 | 336 | 318 | 8.9 | 36.5 | 0 | 0 | 0 | 0 | 20.2947 | 0 | 0 | 20.2947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557.6125 | 43.72% | 0 | 0 | 41.2847 | 66.06% | 20.2947
4480 | 165 | 433 | 310 | 7.4 | 37.7 | 0 | 0 | 0 | 0 | 27.8524 | 0 | 0 | 27.8524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557.6125 | 43.72% | 0 | 0 | 41.2847 | 66.06% | 27.8524
4481 | 63 | 204 | 172 | 4.6 | 37.7 | 0 | 0 | 0 | 0 | 12.4988 | 0 | 0 | 12.4988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557.6125 | 43.72% | 0 | 0 | 41.2847 | 66.06% | 12.4988
4482 | 35 | 149 | 134 | 5.6 | 36.6 | 0 | 0 | 0 | 0 | 8.4064 | 0 | 0 | 8.4064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557.6125 | 43.72% | 0 | 0 | 41.2847 | 66.06% | 8.4064
4483 | 1 | 43 | 43 | 6.4 | 29.3 | 0 | 0 | 0 | 0 | 2.2443 | 0 | 0 | 2.2443 | 0 | 0 | 0 | 101.9618 | 39.4822 | 0 | 101.9618 | 455.6507 | 35.72% | 0 | 0 | 41.2847 | 66.06% | 41.7265
4484 | 0 | 6 | 6 | 4.2 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4904 | 39.4843 | 0 | 101.4904 | 354.1604 | 27.77% | 0 | 0 | 41.2847 | 66.06% | 39.4843
4485 | 0 | 0 | 0 | 1.5 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.985 | 37.2559 | 0 | 95.985 | 258.1754 | 20.24% | 0 | 0 | 41.2847 | 66.06% | 37.2559
4486 | 0 | 0 | 0 | 3.7 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1936 | 38.7087 | 0 | 99.1936 | 158.9818 | 12.46% | 3.6323 | 0 | 44.5667 | 71.31% | 35.0764
4487 | 0 | 0 | 0 | 2.4 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7733 | 33.2116 | 0 | 86.7733 | 72.2086 | 5.661% | 0 | 0 | 44.5667 | 71.31% | 33.2116
4488 | 0 | 0 | 0 | 0.8 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2086 | 5.661% | 0 | 0 | 44.5667 | 71.31% | 0
4489 | 0 | 0 | 0 | 1.4 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2086 | 5.661% | 0 | 0 | 44.5667 | 71.31% | 0
4490 | 0 | 0 | 0 | 1.1 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2086 | 5.661% | 0 | 0 | 44.5667 | 71.31% | 0
4491 | 0 | 0 | 0 | 1.9 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2086 | 5.661% | 0 | 0 | 44.5667 | 71.31% | 0
4492 | 0 | 0 | 0 | 3.9 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2086 | 5.661% | 0 | 0 | 44.5667 | 71.31% | 0
4493 | 0 | 0 | 0 | 1.9 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2086 | 5.661% | 0 | 0 | 44.5667 | 71.31% | 0
4494 | 0 | 18 | 18 | 1.4 | 24 | 0 | 0 | 0 | 0 | 0.44994 | 0 | 0 | 0.44994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2086 | 5.661% | 0 | 0 | 44.5667 | 71.31% | 0.44994
4495 | 34 | 97 | 85 | 1.1 | 26.1 | 0 | 0 | 0 | 0 | 4.2636 | 0 | 0 | 4.2636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2086 | 5.661% | 0 | 0 | 44.5667 | 71.31% | 4.2636
4496 | 242 | 328 | 210 | 3.4 | 30.9 | 0 | 0 | 0 | 36.0858 | 14.3593 | 0 | 0 | 14.3593 | 0 | 0 | 0 | 0 | 0 | 36.0858 | 0 | 108.2943 | 8.49% | 0 | 0 | 44.5667 | 71.31% | 14.3593
4497 | 262 | 463 | 279 | 3.8 | 32 | 0 | 0 | 0 | 48.9185 | 24.8104 | 0 | 0 | 24.8104 | 0 | 0 | 0 | 0 | 0 | 48.9185 | 0 | 157.2128 | 12.33% | 0 | 0 | 44.5667 | 71.31% | 24.8104
4498 | 455 | 695 | 332 | 5.4 | 34.5 | 0 | 0 | 0 | 107.0522 | 41.4627 | 0 | 0.35038 | 41.1123 | 0 | 0 | 0 | 0 | 0 | 107.0522 | 0 | 264.265 | 20.72% | 0.35038 | 0 | 44.8833 | 71.81% | 41.1123
4499 | 70 | 483 | 411 | 6.6 | 34.7 | 0 | 0 | 0 | 0 | 29.8324 | 0 | 0 | 29.8324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264.265 | 20.72% | 0 | 0 | 44.8833 | 71.81% | 29.8324
4500 | 299 | 788 | 484 | 5.2 | 35.9 | 0 | 0 | 0 | 69.4106 | 50.1884 | 0 | 9.3616 | 40.8268 | 0 | 0 | 0 | 0 | 0 | 69.4106 | 0 | 333.6756 | 26.16% | 9.3616 | 0 | 53.3421 | 85.35% | 40.8268
4501 | 121 | 593 | 462 | 5.1 | 35.8 | 0 | 0 | 0 | 0 | 38.007 | 0 | 0 | 38.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6756 | 26.16% | 0 | 0 | 53.3421 | 85.35% | 38.007
4502 | 33 | 423 | 383 | 5.4 | 35.4 | 0 | 0 | 0 | 0 | 26.3432 | 0 | 0 | 26.3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6756 | 26.16% | 0 | 0 | 53.3421 | 85.35% | 26.3432
4503 | 88 | 464 | 384 | 4.1 | 35.3 | 0 | 0 | 0 | 0 | 29.235 | 0 | 0 | 29.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333.6756 | 26.16% | 0 | 0 | 53.3421 | 85.35% | 29.235
4504 | 411 | 657 | 353 | 4.2 | 36.6 | 0 | 0 | 0 | 98.078 | 42.8195 | 0 | 3.2183 | 39.6012 | 0 | 0 | 0 | 0 | 0 | 98.078 | 0 | 431.7536 | 33.85% | 3.2183 | 0 | 56.25 | 90% | 39.6012
4505 | 239 | 432 | 291 | 5.4 | 36.5 | 0 | 0 | 0 | 44.1181 | 26.8938 | 0 | 0 | 26.8938 | 0 | 0 | 0 | 0 | 0 | 44.1181 | 0 | 475.8718 | 37.31% | 0 | 0 | 56.25 | 90% | 26.8938
4506 | 79 | 178 | 145 | 3.9 | 34.4 | 0 | 0 | 0 | 0 | 10.0808 | 0 | 0 | 10.0808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 56.25 | 90% | 10.0808
4507 | 37 | 78 | 69 | 5 | 32.1 | 0 | 0 | 0 | 0 | 3.813 | 0 | 0 | 3.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 24.4146 | 29.2295 | 46.77% | 28.2276
4508 | 1 | 2 | 2 | 4.8 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 29.2295 | 46.77% | 0
4509 | 0 | 0 | 0 | 1.6 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 29.2295 | 46.77% | 0
4510 | 0 | 0 | 0 | 0.7 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 29.2295 | 46.77% | 0
4511 | 0 | 0 | 0 | 1 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 29.2295 | 46.77% | 0
4512 | 0 | 0 | 0 | 0.9 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 29.2295 | 46.77% | 0
4513 | 0 | 0 | 0 | 1.3 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 29.2295 | 46.77% | 0
4514 | 0 | 0 | 0 | 1.8 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 29.2295 | 46.77% | 0
4515 | 0 | 0 | 0 | 2.9 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 29.2295 | 46.77% | 0
4516 | 0 | 0 | 0 | 1.8 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475.8718 | 37.31% | 0 | 0 | 29.2295 | 46.77% | 0
4517 | 0 | 0 | 0 | 0.7 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4152 | 0 | 127.551 | 348.3207 | 27.31% | 7.789 | 0 | 36.2674 | 58.03% | 43.6261
4518 | 0 | 23 | 23 | 0.7 | 19.7 | 0 | 0 | 0 | 0 | 0.69869 | 0 | 0.69869 | 0 | 0 | 0 | 0 | 127.551 | 51.4152 | 0 | 127.551 | 220.7697 | 17.31% | 5.5422 | 0 | 41.2751 | 66.04% | 46.5717
4519 | 2 | 99 | 98 | 0.9 | 21.6 | 0 | 0 | 0 | 0 | 5.0553 | 0 | 5.0553 | 0 | 0 | 0 | 0 | 127.551 | 51.2394 | 0 | 127.551 | 93.2187 | 7.308% | 8.3943 | 0 | 48.8599 | 78.18% | 47.9003
4520 | 140 | 262 | 190 | 1.7 | 24.2 | 0 | 0 | 0 | 0 | 12.4858 | 0 | 0 | 12.4858 | 0 | 0 | 0 | 93.2187 | 36.271 | 0 | 93.2187 | 0 | 0% | 0 | 0 | 48.8599 | 78.18% | 48.7568
4521 | 257 | 392 | 215 | 2.6 | 27.6 | 0 | 0 | 0 | 48.285 | 21.2221 | 0 | 0 | 21.2221 | 0 | 0 | 0 | 0 | 0 | 48.285 | 0 | 48.285 | 3.786% | 0 | 25 | 21.1915 | 33.91% | 46.2221
4522 | 389 | 617 | 297 | 2.7 | 30.3 | 0 | 0 | 0 | 90.7302 | 36.4303 | 7.1054e-15 | 0 | 36.4303 | 0 | 0 | 0 | 0 | 0 | 90.7302 | 0 | 139.0152 | 10.9% | 0 | 13.5006 | 6.25 | 10% | 49.9309
4523 | 577 | 833 | 306 | 3 | 32.6 | 0 | 0 | 0 | 103.3816 | 48.7067 | 2.9953 | 0 | 48.7067 | 0 | 0 | 0 | 0 | 0 | 103.3816 | 0 | 242.3967 | 19% | 0 | 0 | 6.25 | 10% | 48.7067
4524 | 542 | 872 | 340 | 3 | 33.9 | 0 | 0 | 0 | 143.944 | 55.7237 | 0 | 8.1994 | 47.5243 | 0 | 0 | 0 | 0 | 0 | 143.944 | 0 | 386.3408 | 30.29% | 8.1994 | 0 | 13.6587 | 21.85% | 47.5243
4525 | 661 | 958 | 306 | 5.6 | 34.2 | 0 | 0 | 0 | 180.3898 | 54.5056 | 9.4792 | 7.505 | 47.0006 | 0 | 0 | 0 | 0 | 0 | 180.3898 | 0 | 566.7306 | 44.43% | 7.505 | 0 | 20.4399 | 32.7% | 47.0006
4526 | 833 | 961 | 177 | 5.7 | 34.2 | 0 | 0 | 0 | 230.8841 | 65.505 | 0 | 18.7565 | 46.7485 | 0 | 0 | 0 | 0 | 0 | 230.8841 | 0 | 797.6146 | 62.53% | 18.7565 | 0 | 37.3875 | 59.82% | 46.7485
4527 | 887 | 880 | 124 | 7.2 | 34.2 | 0 | 0 | 0 | 240.2255 | 61.0522 | 0 | 15.1796 | 45.8725 | 0 | 0 | 0 | 0 | 0 | 240.2255 | 0 | 1037.8402 | 81.37% | 15.1796 | 0 | 51.1032 | 81.77% | 45.8725
4528 | 903 | 742 | 89 | 4.9 | 34.5 | 0 | 0 | 0 | 237.67 | 51.1189 | 0 | 5.6962 | 45.4227 | 0 | 0 | 0 | 0 | 0 | 237.67 | 0 | 1275.5102 | 100% | 5.6962 | 0 | 56.25 | 90% | 45.4227
4529 | 860 | 561 | 75 | 5.4 | 34.3 | 0 | 0 | 0 | 0 | 32.5472 | 5.0631 | 0 | 32.5472 | 0 | 0 | 0 | 38.2653 | 12.3824 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 44.9297
4530 | 713 | 342 | 67 | 4.3 | 33.2 | 0 | 0 | 0 | 0 | 18.2638 | 0 | 0 | 18.2638 | 0 | 0 | 0 | 71.8233 | 26.4222 | 0 | 71.8233 | 1165.4216 | 91.37% | 0 | 0 | 56.25 | 90% | 44.686
4531 | 426 | 129 | 42 | 4 | 31.8 | 0 | 0 | 0 | 0 | 2.5943 | 0 | 0 | 2.5943 | 0 | 0 | 0 | 105.8286 | 40.7937 | 0 | 105.8286 | 1059.593 | 83.07% | 0 | 0 | 56.25 | 90% | 43.388
4532 | 32 | 9 | 6 | 2.2 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3393 | 40.0399 | 0 | 103.3393 | 956.2537 | 74.97% | 0 | 0 | 56.25 | 90% | 40.0399
4533 | 0 | 0 | 0 | 1.7 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5469 | 38.1932 | 0 | 98.5469 | 857.7068 | 67.24% | 0 | 0 | 56.25 | 90% | 38.1932
4534 | 0 | 0 | 0 | 3.9 | 27.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5091 | 36.1265 | 0 | 93.5091 | 764.1977 | 59.91% | 0 | 0 | 56.25 | 90% | 36.1265
4535 | 0 | 0 | 0 | 4.6 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3445 | 34.8995 | 0 | 90.3445 | 673.8532 | 52.83% | 0 | 0 | 56.25 | 90% | 34.8995
4536 | 0 | 0 | 0 | 3.7 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3086 | 34.1307 | 0 | 88.3086 | 585.5446 | 45.91% | 0 | 0 | 56.25 | 90% | 34.1307
4537 | 0 | 0 | 0 | 3 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1406 | 33.2942 | 0 | 86.1406 | 499.404 | 39.15% | 0 | 0 | 56.25 | 90% | 33.2942
4538 | 0 | 0 | 0 | 3.5 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.801 | 34.4928 | 0 | 88.801 | 410.6031 | 32.19% | 0 | 0 | 56.25 | 90% | 34.4928
4539 | 0 | 0 | 0 | 2.9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6699 | 36.6348 | 0 | 93.6699 | 316.9331 | 24.85% | 0 | 0 | 56.25 | 90% | 36.6348
4540 | 0 | 0 | 0 | 1.3 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1658 | 39.5386 | 0 | 100.1658 | 216.7674 | 16.99% | 0 | 0 | 56.25 | 90% | 39.5386
4541 | 0 | 0 | 0 | 1.3 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8797 | 42.1081 | 0 | 105.8797 | 110.8877 | 8.694% | 0 | 0 | 56.25 | 90% | 42.1081
4542 | 296 | 57 | 21 | 2.3 | 19.8 | 0 | 0 | 0 | 0 | 0.60525 | 0 | 0 | 0.60525 | 0 | 0 | 0 | 110.8877 | 44.2144 | 0 | 110.8877 | 0 | 0% | 0 | 0 | 56.25 | 90% | 44.8197
4543 | 674 | 240 | 47 | 1.2 | 23 | 0 | 0 | 0 | 96.6065 | 2.504 | 0 | 0 | 2.504 | 0 | 0 | 0 | 0 | 0 | 96.6065 | 0 | 96.6065 | 7.574% | 0 | 20.178 | 33.9183 | 54.27% | 22.682
4544 | 827 | 449 | 57 | 0.8 | 25.3 | 0 | 0 | 0 | 167.8364 | 12.0211 | 0 | 0 | 12.0211 | 0 | 0 | 0 | 0 | 0 | 167.8364 | 0 | 264.4428 | 20.73% | 0 | 25 | 6.25 | 10% | 37.0211
4545 | 907 | 647 | 62 | 1.4 | 26.8 | 0 | 0 | 0 | 0 | 30.9685 | 0 | 0 | 30.9685 | 0 | 0 | 0 | 49.1369 | 17.2995 | 0 | 49.1369 | 215.3059 | 16.88% | 0 | 0 | 6.25 | 10% | 48.268
4546 | 940 | 813 | 70 | 2.1 | 28.4 | 0 | 0 | 0 | 0 | 46.3786 | 0 | 10.2564 | 36.1222 | 0 | 0 | 0 | 38.2653 | 12.6221 | 0 | 38.2653 | 177.0406 | 13.88% | 10.2564 | 0 | 15.5173 | 24.83% | 48.7443
4547 | 960 | 936 | 75 | 2.1 | 29.8 | 0 | 0 | 0 | 0 | 56.8862 | 0 | 9.1349 | 47.7513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177.0406 | 13.88% | 9.1349 | 0 | 23.7713 | 38.03% | 47.7513
4548 | 966 | 1005 | 78 | 2.9 | 30.6 | 0 | 0 | 0 | 270.5426 | 56.3403 | 7.8253 | 9.8634 | 46.477 | 0 | 0 | 0 | 0 | 0 | 270.5426 | 0 | 447.5832 | 35.09% | 9.8634 | 0 | 32.6834 | 52.29% | 46.477
4549 | 978 | 1025 | 77 | 5.3 | 30.8 | 0 | 0 | 0 | 276.6904 | 46.2625 | 22.9153 | 0 | 46.2625 | 0 | 0 | 0 | 0 | 0 | 276.6904 | 0 | 724.2736 | 56.78% | 0 | 0 | 32.6834 | 52.29% | 46.2625
4550 | 968 | 979 | 76 | 6.1 | 30.3 | 0 | 0 | 0 | 271.237 | 68.0231 | 0 | 21.8957 | 46.1274 | 0 | 0 | 0 | 0 | 0 | 271.237 | 0 | 995.5106 | 78.05% | 21.8957 | 0 | 52.4675 | 83.95% | 46.1274
4551 | 934 | 873 | 80 | 6 | 30.1 | 0 | 0 | 0 | 255.0754 | 45.5369 | 16.009 | 0 | 45.5369 | 0 | 0 | 0 | 0 | 0 | 255.0754 | 0 | 1250.586 | 98.05% | 0 | 0 | 52.4675 | 83.95% | 45.5369
4552 | 881 | 719 | 82 | 6.2 | 29.3 | 0 | 0 | 0 | 0 | 32.5145 | 18.4264 | 0 | 32.5145 | 0 | 0 | 0 | 38.2653 | 12.5892 | 0 | 38.2653 | 1212.3207 | 95.05% | 0 | 0 | 52.4675 | 83.95% | 45.1038
4553 | 804 | 531 | 79 | 4.7 | 29.8 | 0 | 0 | 0 | 0 | 36.3408 | 0 | 0 | 36.3408 | 0 | 0 | 0 | 38.2653 | 12.5704 | 0 | 38.2653 | 1174.0554 | 92.05% | 4.1862 | 0 | 56.25 | 90% | 44.725
4554 | 680 | 327 | 67 | 5.1 | 28.5 | 0 | 0 | 0 | 35.6886 | 18.0088 | 0 | 0 | 18.0088 | 0 | 0 | 0 | 0 | 0 | 35.6886 | 0 | 1209.744 | 94.84% | 0 | 25 | 28.5817 | 45.73% | 43.0089
4555 | 428 | 129 | 43 | 4.3 | 27.2 | 0 | 0 | 0 | 65.7662 | 2.7301 | 0 | 0 | 2.7301 | 0 | 0 | 0 | 0 | 0 | 65.7662 | 0 | 1275.5102 | 100% | 0 | 17.1061 | 9.6497 | 15.44% | 19.8363
4556 | 30 | 8 | 6 | 2 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4994 | 40.5552 | 0 | 103.4994 | 1172.0108 | 91.89% | 0 | 0 | 9.6497 | 15.44% | 40.5552
4557 | 0 | 0 | 0 | 0.5 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.722 | 38.6431 | 0 | 98.722 | 1073.2888 | 84.15% | 0 | 0 | 9.6497 | 15.44% | 38.6431
4558 | 0 | 0 | 0 | 1.4 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7528 | 36.5721 | 0 | 93.7528 | 979.5361 | 76.8% | 0 | 0 | 9.6497 | 15.44% | 36.5721
4559 | 0 | 0 | 0 | 1 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.392 | 35.1237 | 0 | 90.392 | 889.1441 | 69.71% | 0 | 0 | 9.6497 | 15.44% | 35.1237
4560 | 0 | 0 | 0 | 0.8 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.1439 | 17.9062 | 0 | 50.1439 | 839.0001 | 65.78% | 0 | 0 | 9.6497 | 15.44% | 17.9062
4561 | 0 | 0 | 0 | 1.4 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2889 | 33.9051 | 0 | 87.2889 | 751.7112 | 58.93% | 0 | 0 | 9.6497 | 15.44% | 33.9051
4562 | 0 | 0 | 0 | 1 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1754 | 34.3257 | 0 | 88.1754 | 663.5358 | 52.02% | 0 | 0 | 9.6497 | 15.44% | 34.3257
4563 | 0 | 0 | 0 | 1.7 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5689 | 36.6682 | 0 | 93.5689 | 569.9668 | 44.69% | 0 | 0 | 9.6497 | 15.44% | 36.6682
4564 | 0 | 0 | 0 | 1.3 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.3857 | 39.6263 | 0 | 100.3857 | 469.5811 | 36.82% | 0 | 0 | 9.6497 | 15.44% | 39.6263
4565 | 0 | 0 | 0 | 1.7 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9923 | 42.3866 | 0 | 106.9923 | 362.5888 | 28.43% | 0 | 0 | 9.6497 | 15.44% | 42.3866
4566 | 223 | 51 | 24 | 1.8 | 22.5 | 0 | 0 | 0 | 0 | 0.73367 | 0 | 0 | 0.73367 | 0 | 0 | 0 | 111.1131 | 44.0888 | 0 | 111.1131 | 251.4757 | 19.72% | 0 | 0 | 9.6497 | 15.44% | 44.8225
4567 | 597 | 228 | 57 | 2.7 | 24.4 | 0 | 0 | 0 | 0 | 2.8667 | 0 | 0 | 2.8667 | 0 | 0 | 0 | 110.4771 | 43.6354 | 0 | 110.4771 | 140.9986 | 11.05% | 0 | 0 | 9.6497 | 15.44% | 46.502
4568 | 728 | 428 | 83 | 5.3 | 25.9 | 0 | 0 | 0 | 0 | 12.4315 | 0 | 0 | 12.4315 | 0 | 0 | 0 | 90.9811 | 35.1708 | 0 | 90.9811 | 50.0175 | 3.921% | 0 | 0 | 9.6497 | 15.44% | 47.6023
4569 | 811 | 624 | 100 | 5.9 | 27.8 | 0 | 0 | 0 | 0 | 31.3225 | 0 | 0 | 31.3225 | 0 | 0 | 0 | 50.0175 | 17.6265 | 0 | 50.0175 | 0 | 0% | 0 | 0 | 9.6497 | 15.44% | 48.949
4570 | 840 | 785 | 120 | 6.4 | 28.7 | 0 | 0 | 0 | 0 | 46.8186 | 0 | 0 | 46.8186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.0719 | 6.25 | 10% | 49.8905
4571 | 864 | 907 | 129 | 6.9 | 29.5 | 0 | 0 | 0 | 229.553 | 57.6647 | 0 | 8.4636 | 49.2011 | 0 | 0 | 0 | 0 | 0 | 229.553 | 0 | 229.553 | 18% | 8.4636 | 0 | 13.8974 | 22.24% | 49.2011
4572 | 862 | 974 | 143 | 6.9 | 30.1 | 0 | 0 | 0 | 236.1402 | 58.8374 | 5.4963 | 10.3759 | 48.4616 | 0 | 0 | 0 | 0 | 0 | 236.1402 | 0 | 465.6931 | 36.51% | 10.3759 | 0 | 23.2726 | 37.24% | 48.4616
4573 | 863 | 990 | 147 | 7.3 | 30.6 | 0 | 0 | 0 | 240.127 | 67.213 | 0 | 18.9562 | 48.2568 | 0 | 0 | 0 | 0 | 0 | 240.127 | 0 | 705.8201 | 55.34% | 18.9562 | 0 | 40.4007 | 64.64% | 48.2568
4574 | 858 | 948 | 143 | 7.3 | 31.2 | 0 | 0 | 0 | 237.0881 | 65.6641 | 0 | 17.5409 | 48.1231 | 0 | 0 | 0 | 0 | 0 | 237.0881 | 0 | 942.9082 | 73.92% | 17.5409 | 0 | 56.25 | 90% | 48.1231
4575 | 831 | 848 | 139 | 7.3 | 31.7 | 0 | 0 | 0 | 223.4628 | 47.5117 | 11.9462 | 0 | 47.5117 | 0 | 0 | 0 | 0 | 0 | 223.4628 | 0 | 1166.371 | 91.44% | 0 | 0 | 56.25 | 90% | 47.5117
4576 | 784 | 701 | 131 | 7.3 | 31.2 | 0 | 0 | 0 | 0 | 46.9769 | 2.5465 | 0 | 46.9769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.371 | 91.44% | 0 | 0 | 56.25 | 90% | 46.9769
4577 | 711 | 516 | 114 | 7.3 | 30.6 | 0 | 0 | 0 | 0 | 35.4365 | 0 | 0 | 35.4365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.371 | 91.44% | 0 | 4.5357 | 51.2302 | 81.97% | 39.9723
4578 | 620 | 321 | 83 | 6.7 | 29.7 | 0 | 0 | 0 | 109.1392 | 17.7389 | 0 | 0 | 17.7389 | 0 | 0 | 0 | 0 | 0 | 109.1392 | 0 | 1275.5102 | 100% | 0 | 25 | 23.5618 | 37.7% | 42.7389
4579 | 376 | 126 | 50 | 6.1 | 27.7 | 0 | 0 | 0 | 0 | 3.0582 | 0 | 0 | 3.0582 | 0 | 0 | 0 | 106.805 | 41.7169 | 0 | 106.805 | 1168.7052 | 91.63% | 0 | 0 | 23.5618 | 37.7% | 44.7751
4580 | 23 | 10 | 8 | 4.8 | 25.4 | 0 | 0 | 0 | 0 | 0.043712 | 0 | 0 | 0.043712 | 0 | 0 | 0 | 106.0572 | 41.6466 | 0 | 106.0572 | 1062.6479 | 83.31% | 0 | 0 | 23.5618 | 37.7% | 41.6903
4581 | 0 | 0 | 0 | 2.9 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2519 | 39.7349 | 0 | 101.2519 | 961.396 | 75.37% | 0 | 0 | 23.5618 | 37.7% | 39.7349
4582 | 0 | 0 | 0 | 2 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7968 | 37.4565 | 0 | 95.7968 | 865.5992 | 67.86% | 0 | 0 | 23.5618 | 37.7% | 37.4565
4583 | 0 | 0 | 0 | 1.9 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1887 | 35.9245 | 0 | 92.1887 | 773.4105 | 60.64% | 0 | 0 | 23.5618 | 37.7% | 35.9245
4584 | 0 | 0 | 0 | 2.1 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4541 | 35.1878 | 0 | 90.4541 | 682.9564 | 53.54% | 0 | 0 | 23.5618 | 37.7% | 35.1878
4585 | 0 | 0 | 0 | 1.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.1634 | 34.6976 | 0 | 89.1634 | 593.793 | 46.55% | 0 | 0 | 23.5618 | 37.7% | 34.6976
4586 | 0 | 0 | 0 | 2.4 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0962 | 35.0416 | 0 | 90.0962 | 503.6968 | 39.49% | 0 | 0 | 23.5618 | 37.7% | 35.0416
4587 | 0 | 0 | 0 | 1.7 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.3516 | 48.114 | 0 | 120.3516 | 383.3452 | 30.05% | 10.9194 | 0 | 33.4281 | 53.48% | 37.1947
4588 | 0 | 0 | 0 | 1 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3348 | 0 | 127.551 | 255.7942 | 20.05% | 11.2211 | 0 | 43.567 | 69.71% | 40.1138
4589 | 0 | 0 | 0 | 0.9 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3622 | 0 | 127.551 | 128.2432 | 10.05% | 8.0633 | 0 | 50.8527 | 81.36% | 43.2988
4590 | 66 | 44 | 35 | 1.2 | 21.2 | 0 | 0 | 0 | 0 | 1.2583 | 0 | 0 | 1.2583 | 0 | 0 | 0 | 127.551 | 51.2783 | 0 | 127.551 | 0.69215 | 0.05426% | 5.9733 | 0 | 56.25 | 90% | 46.5633
4591 | 340 | 202 | 102 | 1 | 24.3 | 0 | 0 | 0 | 39.841 | 4.989 | 0 | 0 | 4.989 | 0 | 0 | 0 | 0 | 0 | 39.841 | 0 | 40.5332 | 3.178% | 0 | 25 | 28.5817 | 45.73% | 29.989
4592 | 535 | 401 | 146 | 2.1 | 27.5 | 0 | 0 | 0 | 101.4531 | 13.9733 | 0 | 0 | 13.9733 | 0 | 0 | 0 | 0 | 0 | 101.4531 | 0 | 141.9863 | 11.13% | 0 | 20.178 | 6.25 | 10% | 34.1513
4593 | 643 | 594 | 176 | 3 | 29.4 | 0 | 0 | 0 | 0 | 30.5612 | 0 | 0 | 30.5612 | 0 | 0 | 0 | 57.4986 | 20.7035 | 0 | 57.4986 | 84.4877 | 6.624% | 1.2647 | 0 | 7.3927 | 11.83% | 50
4594 | 719 | 762 | 191 | 4.6 | 31.4 | 0 | 0 | 0 | 0 | 37.4927 | 7.7899 | 0 | 37.4927 | 0 | 0 | 0 | 38.2653 | 12.5073 | 0 | 38.2653 | 46.2224 | 3.624% | 0 | 0 | 7.3927 | 11.83% | 50
4595 | 734 | 880 | 217 | 5.3 | 32.3 | 0 | 0 | 0 | 193.4237 | 55.8704 | 1.7764e-15 | 5.8704 | 50 | 0 | 0 | 0 | 0 | 0 | 193.4237 | 0 | 239.6461 | 18.79% | 5.8704 | 0 | 12.6969 | 20.32% | 50
4596 | 734 | 952 | 241 | 6 | 32.7 | 0 | 0 | 0 | 198.7928 | 62.9342 | 0 | 12.9342 | 50 | 0 | 0 | 0 | 0 | 0 | 198.7928 | 0 | 438.4388 | 34.37% | 12.9342 | 0 | 24.3838 | 39.01% | 50
4597 | 730 | 967 | 250 | 5.9 | 33.2 | 0 | 0 | 0 | 201.011 | 65.4511 | 0 | 15.4511 | 50 | 0 | 0 | 0 | 0 | 0 | 201.011 | 0 | 639.4498 | 50.13% | 15.4511 | 0 | 38.3448 | 61.35% | 50
4598 | 689 | 917 | 266 | 6.1 | 33.5 | 0 | 0 | 0 | 187.2906 | 63.1392 | 0 | 13.1392 | 50 | 0 | 0 | 0 | 0 | 0 | 187.2906 | 0 | 826.7404 | 64.82% | 13.1392 | 0 | 50.2168 | 80.35% | 50
4599 | 641 | 816 | 264 | 6.8 | 33.8 | 0 | 0 | 0 | 168.137 | 56.6771 | 0 | 6.6771 | 50 | 0 | 0 | 0 | 0 | 0 | 168.137 | 0 | 994.8774 | 78% | 6.6771 | 0 | 56.25 | 90% | 50
4600 | 555 | 662 | 255 | 7.2 | 33.6 | 0 | 0 | 0 | 136.7528 | 45.585 | 0 | 0 | 45.585 | 0 | 0 | 0 | 0 | 0 | 136.7528 | 0 | 1131.6302 | 88.72% | 0 | 0 | 56.25 | 90% | 45.585
4601 | 445 | 478 | 222 | 7.1 | 32.9 | 0 | 0 | 0 | 98.7168 | 31.6962 | 0 | 0 | 31.6962 | 0 | 0 | 0 | 0 | 0 | 98.7168 | 0 | 1230.3469 | 96.46% | 0 | 0 | 56.25 | 90% | 31.6962
4602 | 274 | 279 | 170 | 6.6 | 32 | 0 | 0 | 0 | 45.1633 | 15.829 | 0 | 0 | 15.829 | 0 | 0 | 0 | 0 | 0 | 45.1633 | 0 | 1275.5102 | 100% | 0 | 22.9684 | 30.8301 | 49.33% | 38.7974
4603 | 75 | 100 | 83 | 6.2 | 29.8 | 0 | 0 | 0 | 0 | 4.6175 | 0 | 0 | 4.6175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 30.8301 | 49.33% | 4.6175
4604 | 1 | 8 | 8 | 4.6 | 27.5 | 0 | 0 | 0 | 0 | 0.048236 | 0 | 0 | 0.048236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 30.8301 | 49.33% | 0.048236
4605 | 0 | 0 | 0 | 5 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.9486 | 41.5594 | 0 | 105.9486 | 1169.5616 | 91.69% | 0 | 0 | 30.8301 | 49.33% | 41.5594
4606 | 0 | 0 | 0 | 4.5 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.8124 | 39.0288 | 0 | 99.8124 | 1069.7492 | 83.87% | 0 | 0 | 30.8301 | 49.33% | 39.0288
4607 | 0 | 0 | 0 | 3.3 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.756 | 36.9454 | 0 | 94.756 | 974.9933 | 76.44% | 0 | 0 | 30.8301 | 49.33% | 36.9454
4608 | 0 | 0 | 0 | 2.1 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5718 | 36.0889 | 0 | 92.5718 | 882.4215 | 69.18% | 0 | 0 | 30.8301 | 49.33% | 36.0889
4609 | 0 | 0 | 0 | 1.9 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6246 | 35.6975 | 0 | 91.6246 | 790.7969 | 62% | 0 | 0 | 30.8301 | 49.33% | 35.6975
4610 | 0 | 0 | 0 | 1.6 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.0471 | 50.9522 | 0 | 127.0471 | 663.7498 | 52.04% | 15.0917 | 0 | 44.4664 | 71.15% | 35.8605
4611 | 0 | 0 | 0 | 1.7 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2095 | 0 | 127.551 | 536.1987 | 42.04% | 13.0413 | 0 | 56.25 | 90% | 38.1682
4612 | 0 | 0 | 0 | 2.2 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5585 | 41.1959 | 0 | 104.5585 | 431.6403 | 33.84% | 0 | 0 | 56.25 | 90% | 41.1959
4613 | 0 | 0 | 0 | 2.2 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.2408 | 44.42 | 0 | 112.2408 | 319.3995 | 25.04% | 0 | 0 | 56.25 | 90% | 44.42
4614 | 7 | 41 | 39 | 1.2 | 23.5 | 0 | 0 | 0 | 0 | 1.4317 | 0 | 0 | 1.4317 | 0 | 0 | 0 | 116.3992 | 46.2611 | 0 | 116.3992 | 203.0003 | 15.92% | 0 | 0 | 56.25 | 90% | 47.6928
4615 | 104 | 156 | 122 | 1.2 | 26.9 | 0 | 0 | 0 | 0 | 5.5037 | 0 | 0 | 5.5037 | 0 | 0 | 0 | 112.8195 | 44.363 | 0 | 112.8195 | 90.1808 | 7.07% | 0 | 0 | 56.25 | 90% | 49.8668
4616 | 314 | 373 | 221 | 1.8 | 30 | 0 | 0 | 0 | 51.8631 | 15.7186 | 0 | 0 | 15.7186 | 0 | 0 | 0 | 0 | 0 | 51.8631 | 0 | 142.0439 | 11.14% | 0 | 18.2018 | 36.1054 | 57.77% | 33.9204
4617 | 432 | 564 | 280 | 2.7 | 32.1 | 0 | 0 | 0 | 94.0076 | 29.897 | 0 | 0 | 29.897 | 0 | 0 | 0 | 0 | 0 | 94.0076 | 0 | 236.0515 | 18.51% | 0 | 20.103 | 13.8568 | 22.17% | 50
4618 | 531 | 731 | 305 | 3.9 | 34.8 | 0 | 0 | 0 | 129.5129 | 43.1268 | 0 | 0 | 43.1268 | 0 | 0 | 0 | 0 | 0 | 129.5129 | 0 | 365.5644 | 28.66% | 0 | 6.8732 | 6.25 | 10% | 50
4619 | 491 | 849 | 397 | 4.6 | 35.6 | 0 | 0 | 0 | 123.3634 | 52.7529 | 0 | 2.7529 | 50 | 0 | 0 | 0 | 0 | 0 | 123.3634 | 0 | 488.9278 | 38.33% | 2.7529 | 0 | 8.7374 | 13.98% | 50
4620 | 505 | 895 | 400 | 4.4 | 36.6 | 0 | 0 | 0 | 131.7724 | 57.4284 | 0 | 7.4284 | 50 | 0 | 0 | 0 | 0 | 0 | 131.7724 | 0 | 620.7002 | 48.66% | 7.4284 | 0 | 15.4494 | 24.72% | 50
4621 | 357 | 862 | 500 | 5.7 | 36.5 | 0 | 0 | 0 | 88.2508 | 56.189 | 0 | 6.189 | 50 | 0 | 0 | 0 | 0 | 0 | 88.2508 | 0 | 708.951 | 55.58% | 6.189 | 0 | 21.0416 | 33.67% | 50
4622 | 226 | 698 | 474 | 6.5 | 36.2 | 0 | 0 | 0 | 46.7733 | 45.5466 | 0 | 0 | 45.5466 | 0 | 0 | 0 | 0 | 0 | 46.7733 | 0 | 755.7243 | 59.25% | 0 | 4.4534 | 16.1128 | 25.78% | 50
4623 | 19 | 416 | 393 | 6 | 35.2 | 0 | 0 | 0 | 0 | 25.2457 | 0 | 0 | 25.2457 | 0 | 0 | 0 | 66.2575 | 23.9262 | 0 | 66.2575 | 689.4668 | 54.05% | 0 | 0 | 16.1128 | 25.78% | 49.1718
4624 | 16 | 356 | 341 | 5.9 | 34.4 | 0 | 0 | 0 | 0 | 21.6247 | 0 | 0 | 21.6247 | 0 | 0 | 0 | 73.5895 | 27.0415 | 0 | 73.5895 | 615.8774 | 48.28% | 0 | 0 | 16.1128 | 25.78% | 48.6663
4625 | 3 | 177 | 174 | 6 | 32.8 | 0 | 0 | 0 | 0 | 10.4394 | 0 | 0 | 10.4394 | 0 | 0 | 0 | 97.8853 | 37.3397 | 0 | 97.8853 | 517.9921 | 40.61% | 0 | 0 | 16.1128 | 25.78% | 47.7791
4626 | 5 | 146 | 143 | 5.6 | 31.3 | 0 | 0 | 0 | 0 | 8.5232 | 0 | 0 | 8.5232 | 0 | 0 | 0 | 99.5647 | 38.2323 | 0 | 99.5647 | 418.4274 | 32.8% | 0 | 0 | 16.1128 | 25.78% | 46.7555
4627 | 3 | 73 | 72 | 6.1 | 29.7 | 0 | 0 | 0 | 0 | 4.0112 | 0 | 0 | 4.0112 | 0 | 0 | 0 | 106.5265 | 41.3599 | 0 | 106.5265 | 311.9009 | 24.45% | 0 | 0 | 16.1128 | 25.78% | 45.3712
4628 | 0 | 5 | 5 | 3.3 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5164 | 42.3838 | 0 | 108.5164 | 203.3845 | 15.95% | 0 | 0 | 16.1128 | 25.78% | 42.3838
4629 | 0 | 0 | 0 | 1.8 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6999 | 40.8352 | 0 | 104.6999 | 98.6846 | 7.737% | 0 | 0 | 16.1128 | 25.78% | 40.8352
4630 | 0 | 0 | 0 | 1.4 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6846 | 38.4049 | 0 | 98.6846 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 38.4049
4631 | 0 | 0 | 0 | 0.7 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 0
4632 | 0 | 0 | 0 | 2.3 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 0
4633 | 0 | 0 | 0 | 2.5 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 0
4634 | 0 | 0 | 0 | 2 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 0
4635 | 0 | 0 | 0 | 1.5 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 0
4636 | 0 | 0 | 0 | 1.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 0
4637 | 0 | 0 | 0 | 1.5 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 0
4638 | 1 | 30 | 30 | 1.4 | 23.3 | 0 | 0 | 0 | 0 | 1.0098 | 0 | 0 | 1.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 1.0098
4639 | 103 | 158 | 126 | 1 | 26.6 | 0 | 0 | 0 | 0 | 5.5931 | 0 | 0 | 5.5931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 5.5931
4640 | 285 | 351 | 210 | 1.5 | 28.9 | 0 | 0 | 0 | 0 | 14.7435 | 0 | 0 | 14.7435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 16.1128 | 25.78% | 14.7435
4641 | 432 | 544 | 260 | 2.4 | 32.1 | 0 | 0 | 0 | 0 | 28.6698 | 0 | 0 | 28.6698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 8.9117 | 6.25 | 10% | 37.5815
4642 | 529 | 707 | 290 | 2.2 | 33.9 | 0 | 0 | 0 | 113.4105 | 41.6912 | 0 | 0 | 41.6912 | 0 | 0 | 0 | 0 | 0 | 113.4105 | 0 | 113.4105 | 8.891% | 0 | 0 | 6.25 | 10% | 41.6912
4643 | 593 | 828 | 303 | 2.4 | 35.4 | 0 | 0 | 0 | 154.4952 | 51.5682 | 0 | 6.1956 | 45.3726 | 0 | 0 | 0 | 0 | 0 | 154.4952 | 0 | 267.9057 | 21% | 6.1956 | 0 | 11.8481 | 18.96% | 45.3726
4644 | 635 | 920 | 307 | 2.6 | 36.4 | 0 | 0 | 0 | 171.9363 | 58.3698 | 0 | 13.9248 | 44.445 | 0 | 0 | 0 | 0 | 0 | 171.9363 | 0 | 439.842 | 34.48% | 13.9248 | 0 | 24.43 | 39.09% | 44.445
4645 | 621 | 939 | 328 | 3.5 | 37 | 0 | 0 | 0 | 170.1399 | 61.2739 | 0 | 17.7746 | 43.4994 | 0 | 0 | 0 | 0 | 0 | 170.1399 | 0 | 609.9819 | 47.82% | 17.7746 | 0 | 40.4904 | 64.78% | 43.4994
4646 | 666 | 897 | 273 | 3.2 | 36.9 | 0 | 0 | 0 | 182.8246 | 60.0226 | 0 | 17.0873 | 42.9354 | 0 | 0 | 0 | 0 | 0 | 182.8246 | 0 | 792.8065 | 62.16% | 17.0873 | 0 | 55.9298 | 89.49% | 42.9354
4647 | 524 | 701 | 249 | 4.8 | 36.5 | 0 | 0 | 0 | 135.3211 | 42.9486 | 5.2377 | 0.35441 | 42.5941 | 0 | 0 | 0 | 0 | 0 | 135.3211 | 0 | 928.1275 | 72.77% | 0.35441 | 0 | 56.25 | 90% | 42.5941
4648 | 515 | 612 | 235 | 6 | 36.1 | 0 | 0 | 0 | 126.3569 | 41.8785 | 0 | 0 | 41.8785 | 0 | 0 | 0 | 0 | 0 | 126.3569 | 0 | 1054.4845 | 82.67% | 0 | 0.31872 | 55.8973 | 89.44% | 42.1972
4649 | 406 | 437 | 201 | 5.8 | 35.5 | 0 | 0 | 0 | 89.5231 | 28.5969 | 0 | 0 | 28.5969 | 0 | 0 | 0 | 0 | 0 | 89.5231 | 0 | 1144.0076 | 89.69% | 0 | 13.2243 | 41.2615 | 66.02% | 41.8212
4650 | 331 | 282 | 154 | 3.9 | 34.9 | 0 | 0 | 0 | 62.1205 | 15.8109 | 0 | 0 | 15.8109 | 0 | 0 | 0 | 0 | 0 | 62.1205 | 0 | 1206.128 | 94.56% | 0 | 25 | 13.5932 | 21.75% | 40.8109
4651 | 132 | 105 | 77 | 2.5 | 32.1 | 0 | 0 | 0 | 0 | 4.2174 | 0 | 2.4665 | 1.7509 | 0 | 0 | 0 | 102.8328 | 39.4993 | 0 | 102.8328 | 1103.2952 | 86.5% | 2.4665 | 0 | 15.8217 | 25.31% | 41.2502
4652 | 2 | 8 | 8 | 2 | 29.5 | 0 | 0 | 0 | 0 | 0.038356 | 0 | 0 | 0.038356 | 0 | 0 | 0 | 100.7103 | 38.9306 | 0 | 100.7103 | 1002.5849 | 78.6% | 0 | 0 | 15.8217 | 25.31% | 38.969
4653 | 0 | 0 | 0 | 2 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1649 | 36.8493 | 0 | 95.1649 | 907.42 | 71.14% | 0 | 0 | 15.8217 | 25.31% | 36.8493
4654 | 0 | 0 | 0 | 2.6 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.464 | 34.5499 | 0 | 89.464 | 817.956 | 64.13% | 0 | 0 | 15.8217 | 25.31% | 34.5499
4655 | 0 | 0 | 0 | 2.6 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7422 | 33.0417 | 0 | 85.7422 | 732.2138 | 57.41% | 0 | 0 | 15.8217 | 25.31% | 33.0417
4656 | 0 | 0 | 0 | 1.7 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0784 | 31.9609 | 0 | 83.0784 | 649.1354 | 50.89% | 0 | 0 | 15.8217 | 25.31% | 31.9609
4657 | 0 | 0 | 0 | 0.7 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3511 | 31.3078 | 0 | 81.3511 | 567.7843 | 44.51% | 0 | 0 | 15.8217 | 25.31% | 31.3078
4658 | 0 | 0 | 0 | 1.6 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.254 | 30.8175 | 0 | 80.254 | 487.5303 | 38.22% | 0 | 0 | 15.8217 | 25.31% | 30.8175
4659 | 0 | 0 | 0 | 1.1 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6603 | 30.6003 | 0 | 79.6603 | 407.87 | 31.98% | 0 | 0 | 15.8217 | 25.31% | 30.6003
4660 | 0 | 0 | 0 | 1.2 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8169 | 30.2256 | 0 | 78.8169 | 329.0532 | 25.8% | 0 | 0 | 15.8217 | 25.31% | 30.2256
4661 | 0 | 0 | 0 | 1.3 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3227 | 31.7506 | 0 | 82.3227 | 246.7305 | 19.34% | 0 | 0 | 15.8217 | 25.31% | 31.7506
4662 | 230 | 48 | 20 | 1.4 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3334 | 34.3271 | 0 | 88.3334 | 158.3971 | 12.42% | 0 | 0 | 15.8217 | 25.31% | 34.3271
4663 | 645 | 230 | 47 | 1.6 | 25.9 | 0 | 0 | 0 | 0 | 2.486 | 0 | 0 | 2.486 | 0 | 0 | 0 | 88.3344 | 34.0429 | 0 | 88.3344 | 70.0627 | 5.493% | 0 | 0 | 15.8217 | 25.31% | 36.529
4664 | 780 | 435 | 66 | 2.2 | 28.3 | 0 | 0 | 0 | 0 | 11.7903 | 0 | 0 | 11.7903 | 0 | 0 | 0 | 70.0627 | 26.0896 | 0 | 70.0627 | 0 | 0% | 0 | 0 | 15.8217 | 25.31% | 37.8799
4665 | 851 | 627 | 79 | 2 | 30.5 | 0 | 0 | 0 | 67.8583 | 30.2618 | 0 | 0 | 30.2618 | 0 | 0 | 0 | 0 | 0 | 67.8583 | 0 | 67.8583 | 5.32% | 0 | 8.6486 | 6.25 | 10% | 38.9105
4666 | 884 | 779 | 91 | 5.1 | 31.5 | 0 | 0 | 0 | 0 | 39.8408 | 6.2415 | 0 | 39.8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.8583 | 5.32% | 0 | 0 | 6.25 | 10% | 39.8408
4667 | 894 | 888 | 105 | 3.4 | 31.8 | 0 | 0 | 0 | 241.4247 | 40.2238 | 15.9166 | 0 | 40.2238 | 0 | 0 | 0 | 0 | 0 | 241.4247 | 0 | 309.283 | 24.25% | 0 | 0 | 6.25 | 10% | 40.2238
4668 | 892 | 964 | 115 | 2.9 | 33.2 | 0 | 0 | 0 | 248.607 | 39.1876 | 22.6748 | 0 | 39.1876 | 0 | 0 | 0 | 0 | 0 | 248.607 | 0 | 557.89 | 43.74% | 0 | 0 | 6.25 | 10% | 39.1876
4669 | 885 | 981 | 122 | 3.1 | 34.1 | 0 | 0 | 0 | 250.4656 | 50.7726 | 13.5436 | 12.3509 | 38.4216 | 0 | 0 | 0 | 0 | 0 | 250.4656 | 0 | 808.3556 | 63.38% | 12.3509 | 0 | 17.4098 | 27.86% | 38.4216
4670 | 865 | 930 | 126 | 3.2 | 34.8 | 0 | 0 | 0 | 242.8616 | 62.521 | 0 | 24.286 | 38.235 | 0 | 0 | 0 | 0 | 0 | 242.8616 | 0 | 1051.2172 | 82.42% | 24.286 | 0 | 39.3536 | 62.97% | 38.235
4671 | 824 | 835 | 131 | 4.2 | 35.3 | 0 | 0 | 0 | 224.293 | 57.0462 | 0 | 18.6998 | 38.3464 | 0 | 0 | 0 | 0 | 0 | 224.293 | 0 | 1275.5102 | 100% | 18.6998 | 0 | 56.25 | 90% | 38.3464
4672 | 767 | 684 | 127 | 4.7 | 35 | 0 | 0 | 0 | 0 | 38.5776 | 8.8954 | 0 | 38.5776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 38.5776
4673 | 693 | 508 | 112 | 4.1 | 34.5 | 0 | 0 | 0 | 0 | 33.9833 | 0 | 0 | 33.9833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 5.0107 | 50.7045 | 81.13% | 38.994
4674 | 576 | 304 | 86 | 2 | 34 | 0 | 0 | 0 | 0 | 16.7347 | 0 | 0 | 16.7347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 23.3512 | 24.861 | 39.78% | 40.0859
4675 | 335 | 116 | 50 | 2.9 | 30.9 | 0 | 0 | 0 | 0 | 2.987 | 0 | 0 | 2.987 | 0 | 0 | 0 | 100.0915 | 38.5028 | 0 | 100.0915 | 1175.4187 | 92.15% | 0 | 0 | 24.861 | 39.78% | 41.4897
4676 | 22 | 8 | 7 | 1.6 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.3548 | 39.416 | 0 | 101.3548 | 1074.0639 | 84.21% | 0 | 0 | 24.861 | 39.78% | 39.416
4677 | 0 | 0 | 0 | 0.6 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0844 | 36.8632 | 0 | 95.0844 | 978.9795 | 76.75% | 0 | 0 | 24.861 | 39.78% | 36.8632
4678 | 0 | 0 | 0 | 1.3 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2566 | 34.7728 | 0 | 90.2566 | 888.7228 | 69.68% | 0 | 0 | 24.861 | 39.78% | 34.7728
4679 | 0 | 0 | 0 | 0.8 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.4789 | 26.8534 | 0 | 71.4789 | 817.2439 | 64.07% | 0 | 0 | 24.861 | 39.78% | 26.8534
4680 | 0 | 0 | 0 | 1.1 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.7191 | 0 | 38.2653 | 778.9786 | 61.07% | 0 | 0 | 24.861 | 39.78% | 12.7191
4681 | 0 | 0 | 0 | 1.2 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.7191 | 0 | 38.2653 | 740.7133 | 58.07% | 0 | 0 | 24.861 | 39.78% | 12.7191
4682 | 0 | 0 | 0 | 0.7 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1902 | 32.7826 | 0 | 85.1902 | 655.5231 | 51.39% | 0 | 0 | 24.861 | 39.78% | 32.7826
4683 | 0 | 0 | 0 | 0.9 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2691 | 35.8646 | 0 | 92.2691 | 563.254 | 44.16% | 0 | 0 | 24.861 | 39.78% | 35.8646
4684 | 0 | 0 | 0 | 1.3 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0951 | 39.1862 | 0 | 100.0951 | 463.159 | 36.31% | 0 | 0 | 24.861 | 39.78% | 39.1862
4685 | 0 | 0 | 0 | 1.4 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3746 | 42.7557 | 0 | 108.3746 | 354.7844 | 27.82% | 0 | 0 | 24.861 | 39.78% | 42.7557
4686 | 141 | 41 | 25 | 1.3 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.6133 | 45.8001 | 0 | 115.6133 | 239.1711 | 18.75% | 0 | 0 | 24.861 | 39.78% | 45.8001
4687 | 479 | 204 | 69 | 0.8 | 28.2 | 0 | 0 | 0 | 0 | 3.6311 | 0 | 0 | 3.6311 | 0 | 0 | 0 | 112.8856 | 44.2344 | 0 | 112.8856 | 126.2855 | 9.901% | 0 | 0 | 24.861 | 39.78% | 47.8655
4688 | 661 | 405 | 96 | 1.6 | 31 | 0 | 0 | 0 | 0 | 12.1549 | 0 | 0 | 12.1549 | 0 | 0 | 0 | 88.0202 | 33.4205 | 0 | 88.0202 | 38.2653 | 3% | 0 | 3.3401 | 21.1644 | 33.86% | 48.9156
4689 | 764 | 601 | 111 | 2.4 | 33.2 | 0 | 0 | 0 | 0 | 29.4885 | 0 | 0 | 29.4885 | 0 | 0 | 0 | 38.2653 | 12.4314 | 0 | 38.2653 | 0 | 0% | 0 | 8.0801 | 12.2219 | 19.56% | 50
4690 | 807 | 772 | 136 | 2.9 | 34.6 | 0 | 0 | 0 | 0 | 44.604 | 0 | 0 | 44.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 5.396 | 6.25 | 10% | 50
4691 | 841 | 915 | 159 | 3.1 | 35.5 | 0 | 0 | 0 | 226.1294 | 56.1369 | 0 | 6.1369 | 50 | 0 | 0 | 0 | 0 | 0 | 226.1294 | 0 | 226.1294 | 17.73% | 6.1369 | 0 | 11.7951 | 18.87% | 50
4692 | 847 | 1020 | 204 | 3.5 | 36.4 | 0 | 0 | 0 | 234.6917 | 64.7742 | 0 | 14.7742 | 50 | 0 | 0 | 0 | 0 | 0 | 234.6917 | 0 | 460.8211 | 36.13% | 14.7742 | 0 | 25.1444 | 40.23% | 50
4693 | 831 | 1041 | 231 | 7.5 | 36.7 | 0 | 0 | 0 | 176.4667 | 69.8745 | 0 | 19.8745 | 50 | 0 | 0 | 0 | 0 | 0 | 176.4667 | 0 | 637.2878 | 49.96% | 19.8745 | 0 | 43.1022 | 68.96% | 50
4694 | 822 | 948 | 178 | 7.5 | 36.6 | 0 | 0 | 0 | 226.1902 | 54.3278 | 11.1155 | 4.4289 | 49.8988 | 0 | 0 | 0 | 0 | 0 | 226.1902 | 0 | 863.4781 | 67.7% | 4.4289 | 0 | 47.1041 | 75.37% | 49.8988
4695 | 808 | 847 | 156 | 7.1 | 36.2 | 0 | 0 | 0 | 217.1459 | 59.0809 | 0 | 10.1221 | 48.9588 | 0 | 0 | 0 | 0 | 0 | 217.1459 | 0 | 1080.6239 | 84.72% | 10.1221 | 0 | 56.25 | 90% | 48.9588
4696 | 759 | 690 | 139 | 7.4 | 35.8 | 0 | 0 | 0 | 194.8863 | 48.2791 | 0.077582 | 0 | 48.2791 | 0 | 0 | 0 | 0 | 0 | 194.8863 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 48.2791
4697 | 633 | 488 | 128 | 6.5 | 35.8 | 0 | 0 | 0 | 0 | 32.9069 | 4.2633e-13 | 0 | 32.9069 | 0 | 0 | 0 | 43.5133 | 14.4795 | 0 | 43.5133 | 1231.9969 | 96.59% | 0 | 0 | 56.25 | 90% | 47.3864
4698 | 503 | 288 | 98 | 5.7 | 35 | 0 | 0 | 0 | 0 | 16.2172 | 0 | 0 | 16.2172 | 0 | 0 | 0 | 82.2315 | 30.5605 | 0 | 82.2315 | 1149.7654 | 90.14% | 0 | 0 | 56.25 | 90% | 46.7778
4699 | 256 | 108 | 59 | 4.5 | 33.5 | 0 | 0 | 0 | 0 | 3.327 | 0 | 0 | 3.327 | 0 | 0 | 0 | 110.4544 | 42.4829 | 0 | 110.4544 | 1039.3111 | 81.48% | 0 | 0 | 56.25 | 90% | 45.8099
4700 | 16 | 8 | 7 | 2.4 | 30.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.4021 | 42.4145 | 0 | 109.4021 | 929.909 | 72.9% | 0 | 0 | 56.25 | 90% | 42.4145
4701 | 0 | 0 | 0 | 1.7 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.5251 | 40.3477 | 0 | 103.5251 | 826.3839 | 64.79% | 0 | 0 | 56.25 | 90% | 40.3477
4702 | 0 | 0 | 0 | 0.7 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6881 | 38.0289 | 0 | 97.6881 | 728.6958 | 57.13% | 0 | 0 | 56.25 | 90% | 38.0289
4703 | 0 | 0 | 0 | 0.5 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3432 | 36.1864 | 0 | 93.3432 | 635.3526 | 49.81% | 0 | 0 | 56.25 | 90% | 36.1864
4704 | 0 | 0 | 0 | 1.1 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.7065 | 0 | 38.2653 | 597.0873 | 46.81% | 0 | 0 | 56.25 | 90% | 12.7065
4705 | 0 | 0 | 0 | 2.8 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5292 | 32.0502 | 0 | 83.5292 | 513.5581 | 40.26% | 0 | 0 | 56.25 | 90% | 32.0502
4706 | 0 | 0 | 0 | 5.3 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.665 | 35.2254 | 0 | 90.665 | 422.8931 | 33.15% | 0 | 0 | 56.25 | 90% | 35.2254
4707 | 0 | 0 | 0 | 5.1 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8331 | 37.5721 | 0 | 95.8331 | 327.06 | 25.64% | 0 | 0 | 56.25 | 90% | 37.5721
4708 | 0 | 0 | 0 | 5.5 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8065 | 40.1792 | 0 | 101.8065 | 225.2536 | 17.66% | 0 | 0 | 56.25 | 90% | 40.1792
4709 | 0 | 0 | 0 | 4.3 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.2076 | 43.3727 | 0 | 109.2076 | 116.046 | 9.098% | 0 | 0 | 56.25 | 90% | 43.3727
4710 | 75 | 37 | 27 | 3.2 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.046 | 46.2987 | 0 | 116.046 | 0 | 0% | 0 | 0 | 56.25 | 90% | 46.2987
4711 | 432 | 199 | 76 | 4.6 | 23.9 | 0 | 0 | 0 | 51.5781 | 3.7662 | 0 | 0 | 3.7662 | 0 | 0 | 0 | 0 | 0 | 51.5781 | 0 | 51.5781 | 4.044% | 0 | 20.178 | 33.9183 | 54.27% | 23.9442
4712 | 629 | 399 | 105 | 6.6 | 26.6 | 0 | 0 | 0 | 82.8787 | 12.7727 | 0 | 0 | 12.7727 | 0 | 0 | 0 | 0 | 0 | 82.8787 | 0 | 134.4569 | 10.54% | 0 | 25 | 6.25 | 10% | 37.7727
4713 | 737 | 595 | 123 | 7 | 28 | 0 | 0 | 0 | 0 | 30.6311 | 0 | 0 | 30.6311 | 0 | 0 | 0 | 54.1521 | 19.3689 | 0 | 54.1521 | 80.3048 | 6.296% | 0 | 0 | 6.25 | 10% | 50
4714 | 803 | 763 | 131 | 6.8 | 29.9 | 0 | 0 | 0 | 0 | 45.9306 | 0 | 0 | 45.9306 | 0 | 0 | 0 | 38.2653 | 12.5666 | 0 | 38.2653 | 42.0395 | 3.296% | 8.4972 | 0 | 13.9277 | 22.28% | 50
4715 | 833 | 887 | 141 | 7.3 | 30.7 | 0 | 0 | 0 | 220.1613 | 57.2561 | 0 | 7.2561 | 50 | 0 | 0 | 0 | 0 | 0 | 220.1613 | 0 | 262.2008 | 20.56% | 7.2561 | 0 | 20.484 | 32.77% | 50
4716 | 855 | 963 | 142 | 7.2 | 30.7 | 0 | 0 | 0 | 233.8136 | 64.1325 | 0 | 14.1325 | 50 | 0 | 0 | 0 | 0 | 0 | 233.8136 | 0 | 496.0144 | 38.89% | 14.1325 | 0 | 33.2535 | 53.21% | 50
4717 | 874 | 985 | 132 | 6.3 | 31.5 | 0 | 0 | 0 | 244.3986 | 59.8746 | 6.9748 | 9.9465 | 49.9281 | 0 | 0 | 0 | 0 | 0 | 244.3986 | 0 | 740.413 | 58.05% | 9.9465 | 0 | 42.2408 | 67.59% | 49.9281
4718 | 867 | 941 | 129 | 5.8 | 32 | 0 | 0 | 0 | 241.2712 | 65.0996 | 0 | 15.5044 | 49.5952 | 0 | 0 | 0 | 0 | 0 | 241.2712 | 0 | 981.6842 | 76.96% | 15.5044 | 0 | 56.25 | 90% | 49.5952
4719 | 832 | 837 | 127 | 6 | 32.2 | 0 | 0 | 0 | 225.1285 | 48.5061 | 10.2377 | 0 | 48.5061 | 0 | 0 | 0 | 0 | 0 | 225.1285 | 0 | 1206.8127 | 94.61% | 0 | 0 | 56.25 | 90% | 48.5061
4720 | 756 | 681 | 133 | 6.4 | 31.7 | 0 | 0 | 0 | 0 | 35.1741 | 13.2438 | 0 | 35.1741 | 0 | 0 | 0 | 38.2653 | 12.4951 | 0 | 38.2653 | 1168.5474 | 91.61% | 0 | 0 | 56.25 | 90% | 47.6691
4721 | 656 | 493 | 124 | 6.7 | 30.7 | 0 | 0 | 0 | 0 | 34.2103 | 0 | 0 | 34.2103 | 0 | 0 | 0 | 38.4077 | 12.5953 | 0 | 38.4077 | 1130.1397 | 88.6% | 0 | 0 | 56.25 | 90% | 46.8056
4722 | 523 | 296 | 96 | 6.6 | 29 | 0 | 0 | 0 | 106.2049 | 16.9356 | 0 | 0 | 16.9356 | 0 | 0 | 0 | 0 | 0 | 106.2049 | 0 | 1236.3446 | 96.93% | 0 | 25 | 28.5817 | 45.73% | 41.9356
4723 | 305 | 114 | 53 | 6.1 | 27.1 | 0 | 0 | 0 | 39.1657 | 3.193 | 0 | 0 | 3.193 | 0 | 0 | 0 | 0 | 0 | 39.1657 | 0 | 1275.5102 | 100% | 0 | 8.6335 | 19.0266 | 30.44% | 11.8266
4724 | 12 | 8 | 7 | 5.6 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7235 | 42.0009 | 0 | 106.7235 | 1168.7867 | 91.63% | 0 | 0 | 19.0266 | 30.44% | 42.0009
4725 | 0 | 0 | 0 | 4.9 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2301 | 39.7948 | 0 | 101.2301 | 1067.5566 | 83.7% | 0 | 0 | 19.0266 | 30.44% | 39.7948
4726 | 0 | 0 | 0 | 3.7 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7393 | 37.5094 | 0 | 95.7393 | 971.8173 | 76.19% | 0 | 0 | 19.0266 | 30.44% | 37.5094
4727 | 0 | 0 | 0 | 2.9 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6415 | 35.7839 | 0 | 91.6415 | 880.1758 | 69.01% | 0 | 0 | 19.0266 | 30.44% | 35.7839
4728 | 0 | 0 | 0 | 2.8 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.908 | 35.0847 | 0 | 89.908 | 790.2678 | 61.96% | 0 | 0 | 19.0266 | 30.44% | 35.0847
4729 | 0 | 0 | 0 | 2.1 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5844 | 39.2739 | 0 | 99.5844 | 690.6834 | 54.15% | 4.6543 | 0 | 23.2321 | 37.17% | 34.6196
4730 | 0 | 0 | 0 | 0.8 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3531 | 0 | 127.551 | 563.1323 | 44.15% | 16.3185 | 0 | 37.9768 | 60.76% | 35.0346
4731 | 0 | 0 | 0 | 1.3 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.389 | 0 | 127.551 | 435.5813 | 34.15% | 13.9283 | 0 | 50.5619 | 80.9% | 37.4607
4732 | 0 | 0 | 0 | 1.4 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.1838 | 40.4299 | 0 | 102.1838 | 333.3975 | 26.14% | 0 | 0 | 50.5619 | 80.9% | 40.4299
4733 | 0 | 0 | 0 | 2.2 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3134 | 43.5495 | 0 | 109.3134 | 224.0842 | 17.57% | 0 | 0 | 50.5619 | 80.9% | 43.5495
4734 | 168 | 45 | 26 | 1.4 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.167 | 46.3419 | 0 | 116.167 | 107.9171 | 8.461% | 0 | 0 | 50.5619 | 80.9% | 46.3419
4735 | 245 | 172 | 112 | 0.7 | 24.1 | 0 | 0 | 0 | 0 | 5.3558 | 0 | 0 | 5.3558 | 0 | 0 | 0 | 107.9171 | 42.5696 | 0 | 107.9171 | 0 | 0% | 0 | 0 | 50.5619 | 80.9% | 47.9254
4736 | 171 | 281 | 192 | 1.3 | 25.1 | 0 | 0 | 0 | 0 | 12.8258 | 0 | 0 | 12.8258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 22.8936 | 36.63% | 37.8258
4737 | 641 | 675 | 259 | 1.5 | 28.1 | 0 | 0 | 0 | 148.259 | 34.9616 | 0 | 0 | 34.9616 | 0 | 0 | 0 | 0 | 0 | 148.259 | 0 | 148.259 | 11.62% | 0 | 15.0384 | 6.25 | 10% | 50
4738 | 557 | 676 | 234 | 1.2 | 29.8 | 0 | 0 | 0 | 0 | 37.4296 | 2.3356 | 0 | 37.4296 | 0 | 0 | 0 | 38.2653 | 12.5704 | 0 | 38.2653 | 109.9937 | 8.624% | 0 | 0 | 6.25 | 10% | 50
4739 | 842 | 958 | 206 | 3.8 | 30.6 | 0 | 0 | 0 | 0 | 37.4606 | 23.3198 | 0 | 37.4606 | 0 | 0 | 0 | 38.2653 | 12.5394 | 0 | 38.2653 | 71.7284 | 5.624% | 0 | 0 | 6.25 | 10% | 50
4740 | 812 | 995 | 216 | 3.9 | 31.3 | 0 | 0 | 0 | 223.7754 | 58.0833 | 7.0301 | 8.8725 | 49.2108 | 0 | 0 | 0 | 0 | 0 | 223.7754 | 0 | 295.5038 | 23.17% | 8.8725 | 0 | 14.2668 | 22.83% | 49.2108
4741 | 913 | 994 | 111 | 3.9 | 31.9 | 0 | 0 | 0 | 258.2514 | 66.7031 | 0 | 17.8279 | 48.8752 | 0 | 0 | 0 | 0 | 0 | 258.2514 | 0 | 553.7552 | 43.41% | 17.8279 | 0 | 30.3754 | 48.6% | 48.8752
4742 | 905 | 950 | 108 | 4.4 | 32.5 | 0 | 0 | 0 | 254.0046 | 65.4036 | 0 | 16.8181 | 48.5855 | 0 | 0 | 0 | 0 | 0 | 254.0046 | 0 | 807.7598 | 63.33% | 16.8181 | 0 | 45.5716 | 72.91% | 48.5855
4743 | 852 | 840 | 119 | 5.8 | 32.1 | 0 | 0 | 0 | 231.2833 | 59.4246 | 0 | 11.8182 | 47.6064 | 0 | 0 | 0 | 0 | 0 | 231.2833 | 0 | 1039.0431 | 81.46% | 11.8182 | 0 | 56.25 | 90% | 47.6064
4744 | 801 | 690 | 115 | 6.1 | 30.9 | 0 | 0 | 0 | 64.6771 | 46.665 | 2.6941 | 0 | 46.665 | 0 | 0 | 0 | 9.3063e-13 | 0 | 64.6771 | 9.3063e-13 | 1103.7203 | 86.53% | 0 | 0 | 56.25 | 90% | 46.665
4745 | 712 | 508 | 111 | 6.1 | 28.8 | 0 | 0 | 0 | 171.7899 | 35.7968 | 0 | 0 | 35.7968 | 0 | 0 | 0 | 9.3063e-13 | 0 | 171.7899 | 9.3063e-13 | 1275.5102 | 100% | 0 | 5.9979 | 49.6119 | 79.38% | 41.7947
4746 | 443 | 282 | 111 | 4.9 | 27.4 | 0 | 0 | 0 | 0 | 16.1713 | 0 | 0 | 16.1713 | 0 | 0 | 0 | 76.9057 | 29.0592 | 0 | 76.9057 | 1198.6045 | 93.97% | 0 | 2.1067e-13 | 49.6119 | 79.38% | 45.2305
4747 | 137 | 77 | 44 | 2.7 | 26.1 | 0 | 0 | 0 | 0 | 2.4735 | 0 | 0 | 2.4735 | 0 | 0 | 0 | 106.1264 | 41.6039 | 0 | 106.1264 | 1092.4781 | 85.65% | 0 | 0 | 49.6119 | 79.38% | 44.0774
4748 | 1 | 6 | 6 | 4.4 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2693 | 40.9424 | 0 | 104.2693 | 988.2088 | 77.48% | 0 | 0 | 49.6119 | 79.38% | 40.9424
4749 | 0 | 0 | 0 | 3.7 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7497 | 39.1347 | 0 | 99.7497 | 888.4591 | 69.66% | 0 | 0 | 49.6119 | 79.38% | 39.1347
4750 | 0 | 0 | 0 | 2.3 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6879 | 37.0122 | 0 | 94.6879 | 793.7712 | 62.23% | 0 | 0 | 49.6119 | 79.38% | 37.0122
4751 | 0 | 0 | 0 | 1.2 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9325 | 35.451 | 0 | 90.9325 | 702.8387 | 55.1% | 0 | 0 | 49.6119 | 79.38% | 35.451
4752 | 0 | 0 | 0 | 0.7 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0734 | 34.6725 | 0 | 89.0734 | 613.7653 | 48.12% | 0 | 0 | 49.6119 | 79.38% | 34.6725
4753 | 0 | 0 | 0 | 0.7 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1796 | 34.3146 | 0 | 88.1796 | 525.5857 | 41.21% | 0 | 0 | 49.6119 | 79.38% | 34.3146
4754 | 0 | 0 | 0 | 1.3 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2202 | 34.8076 | 0 | 89.2202 | 436.3655 | 34.21% | 0 | 0 | 49.6119 | 79.38% | 34.8076
4755 | 0 | 0 | 0 | 0.9 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5566 | 37.1139 | 0 | 94.5566 | 341.8089 | 26.8% | 0 | 0 | 49.6119 | 79.38% | 37.1139
4756 | 0 | 0 | 0 | 1 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.1645 | 47.3309 | 0 | 118.1645 | 223.6444 | 17.53% | 7.3466 | 0 | 56.25 | 90% | 39.9842
4757 | 0 | 0 | 0 | 2.3 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3567 | 43.0384 | 0 | 108.3567 | 115.2877 | 9.039% | 0 | 0 | 56.25 | 90% | 43.0384
4758 | 150 | 39 | 23 | 1.6 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.2877 | 45.9547 | 0 | 115.2877 | 0 | 0% | 0 | 0 | 56.25 | 90% | 45.9547
4759 | 515 | 204 | 62 | 1.4 | 23.6 | 0 | 0 | 0 | 67.2592 | 3.2462 | 0 | 0 | 3.2462 | 0 | 0 | 0 | 0 | 0 | 67.2592 | 0 | 67.2592 | 5.273% | 0 | 20.178 | 33.9183 | 54.27% | 23.4242
4760 | 704 | 408 | 83 | 2 | 26.3 | 0 | 0 | 0 | 137.6495 | 11.9903 | 0 | 0 | 11.9903 | 0 | 0 | 0 | 0 | 0 | 137.6495 | 0 | 204.9087 | 16.06% | 0 | 25 | 6.25 | 10% | 36.9903
4761 | 789 | 601 | 100 | 3.5 | 26.8 | 0 | 0 | 0 | 0 | 30.5816 | 0 | 0 | 30.5816 | 0 | 0 | 0 | 54.1207 | 19.4184 | 0 | 54.1207 | 150.788 | 11.82% | 0 | 0 | 6.25 | 10% | 50
4762 | 831 | 762 | 115 | 4.1 | 28 | 0 | 0 | 0 | 0 | 42.1888 | 3.7304 | 0 | 42.1888 | 0 | 0 | 0 | 38.2653 | 12.6363 | 0 | 38.2653 | 112.5227 | 8.822% | 4.8251 | 0 | 10.6098 | 16.98% | 50
4763 | 874 | 893 | 116 | 5.6 | 29.4 | 0 | 0 | 0 | 233.5942 | 50 | 7.406 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 233.5942 | 0 | 346.117 | 27.14% | 0 | 0 | 10.6098 | 16.98% | 50
4764 | 905 | 974 | 110 | 5.7 | 30.9 | 0 | 0 | 0 | 250.2236 | 50 | 14.7519 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 250.2236 | 0 | 596.3406 | 46.75% | 0 | 0 | 10.6098 | 16.98% | 50
4765 | 919 | 994 | 104 | 5.8 | 31.8 | 0 | 0 | 0 | 168.2599 | 67.8196 | 0 | 17.8637 | 49.9559 | 0 | 0 | 0 | 0 | 0 | 168.2599 | 0 | 764.6005 | 59.94% | 17.8637 | 0 | 26.7507 | 42.8% | 49.9559
4766 | 928 | 960 | 95 | 6 | 32.3 | 0 | 0 | 0 | 259.5255 | 66.9118 | 0 | 17.2817 | 49.63 | 0 | 0 | 0 | 0 | 0 | 259.5255 | 0 | 1024.1261 | 80.29% | 17.2817 | 0 | 42.3658 | 67.79% | 49.63
4767 | 919 | 864 | 87 | 5.7 | 32.7 | 0 | 0 | 0 | 251.3841 | 61.1311 | 0 | 12.3952 | 48.7359 | 0 | 0 | 0 | 0 | 0 | 251.3841 | 0 | 1275.5102 | 100% | 12.3952 | 0 | 53.5655 | 85.7% | 48.7359
4768 | 887 | 716 | 81 | 6 | 32.7 | 0 | 0 | 0 | 0 | 51.1401 | 0 | 2.971 | 48.1691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 2.971 | 0 | 56.25 | 90% | 48.1691
4769 | 821 | 529 | 73 | 5.7 | 32.4 | 0 | 0 | 0 | 0 | 36.928 | 0 | 0 | 36.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 36.928
4770 | 695 | 321 | 61 | 5.6 | 30.8 | 0 | 0 | 0 | 0 | 18.2404 | 0 | 0 | 18.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 43.2405
4771 | 442 | 121 | 38 | 4 | 29.3 | 0 | 0 | 0 | 0 | 2.7175 | 0 | 0 | 2.7175 | 0 | 0 | 0 | 110.3774 | 43.0353 | 0 | 110.3774 | 1165.1328 | 91.35% | 0 | 0 | 28.5817 | 45.73% | 45.7528
4772 | 23 | 6 | 4 | 3.5 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.976 | 42.7181 | 0 | 108.976 | 1056.1569 | 82.8% | 0 | 0 | 28.5817 | 45.73% | 42.7181
4773 | 0 | 0 | 0 | 3.3 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.3013 | 40.5288 | 0 | 103.3013 | 952.8556 | 74.7% | 0 | 0 | 28.5817 | 45.73% | 40.5288
4774 | 0 | 0 | 0 | 2.8 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1698 | 38.0289 | 0 | 97.1698 | 855.6858 | 67.09% | 0 | 0 | 28.5817 | 45.73% | 38.0289
4775 | 0 | 0 | 0 | 1.8 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0006 | 36.3326 | 0 | 93.0006 | 762.6852 | 59.79% | 0 | 0 | 28.5817 | 45.73% | 36.3326
4776 | 0 | 0 | 0 | 2.3 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9712 | 35.4747 | 0 | 90.9712 | 671.714 | 52.66% | 0 | 0 | 28.5817 | 45.73% | 35.4747
4777 | 0 | 0 | 0 | 2 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0633 | 35.0054 | 0 | 90.0633 | 581.6507 | 45.6% | 0 | 0 | 28.5817 | 45.73% | 35.0054
4778 | 0 | 0 | 0 | 1.7 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6897 | 35.3396 | 0 | 90.6897 | 490.961 | 38.49% | 0 | 0 | 28.5817 | 45.73% | 35.3396
4779 | 0 | 0 | 0 | 2.9 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3079 | 42.9935 | 0 | 108.3079 | 382.6531 | 30% | 5.2821 | 0 | 33.3544 | 53.37% | 37.7114
4780 | 0 | 0 | 0 | 3.2 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3256 | 0 | 127.551 | 255.102 | 20% | 10.8441 | 0 | 43.1527 | 69.04% | 40.4814
4781 | 0 | 0 | 0 | 3.5 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3531 | 0 | 127.551 | 127.551 | 10% | 7.6991 | 0 | 50.1094 | 80.17% | 43.654
4782 | 152 | 41 | 25 | 2.7 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.344 | 0 | 127.551 | 0 | 0% | 4.5648 | 0 | 54.234 | 86.77% | 46.7792
4783 | 501 | 204 | 67 | 2.1 | 22.4 | 0 | 0 | 0 | 0 | 3.63 | 0 | 0 | 3.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 26.5656 | 42.51% | 28.63
4784 | 658 | 404 | 100 | 3.1 | 26.3 | 0 | 0 | 0 | 126.6946 | 12.6819 | 0 | 0 | 12.6819 | 0 | 0 | 0 | 0 | 0 | 126.6946 | 0 | 126.6946 | 9.933% | 0 | 18.3564 | 6.25 | 10% | 31.0383
4785 | 758 | 603 | 119 | 4.4 | 29.8 | 0 | 0 | 0 | 0 | 30.6362 | 0 | 0 | 30.6362 | 0 | 0 | 0 | 54.3799 | 19.3638 | 0 | 54.3799 | 72.3147 | 5.669% | 0 | 0 | 6.25 | 10% | 50
4786 | 830 | 774 | 125 | 6 | 31.9 | 0 | 0 | 0 | 0 | 37.5132 | 8.8787 | 0 | 37.5132 | 0 | 0 | 0 | 38.2653 | 12.4868 | 0 | 38.2653 | 34.0494 | 2.669% | 0 | 0 | 6.25 | 10% | 50
4787 | 843 | 894 | 143 | 6.7 | 32.8 | 0 | 0 | 0 | 223.6568 | 57.5268 | 0 | 7.5268 | 50 | 0 | 0 | 0 | 0 | 0 | 223.6568 | 0 | 257.7062 | 20.2% | 7.5268 | 0 | 13.0509 | 20.88% | 50
4788 | 837 | 961 | 159 | 8.3 | 32.7 | 0 | 0 | 0 | 227.5252 | 64.7775 | 0 | 14.7775 | 50 | 0 | 0 | 0 | 0 | 0 | 227.5252 | 0 | 485.2314 | 38.04% | 14.7775 | 0 | 26.4033 | 42.25% | 50
4789 | 828 | 975 | 168 | 8.7 | 32.7 | 0 | 0 | 0 | 228.2163 | 67.5727 | 0 | 17.5727 | 50 | 0 | 0 | 0 | 0 | 0 | 228.2163 | 0 | 713.4476 | 55.93% | 17.5727 | 0 | 42.2812 | 67.65% | 50
4790 | 784 | 921 | 186 | 7.9 | 33 | 0 | 0 | 0 | 214.3272 | 64.8466 | 0 | 14.8467 | 50 | 0 | 0 | 0 | 0 | 0 | 214.3272 | 0 | 927.7748 | 72.74% | 14.8467 | 0 | 55.6961 | 89.11% | 50
4791 | 660 | 806 | 240 | 7.4 | 33.1 | 0 | 0 | 0 | 156.6226 | 49.8489 | 7.305 | 0.61304 | 49.2359 | 0 | 0 | 0 | 0 | 0 | 156.6226 | 0 | 1084.3975 | 85.02% | 0.61304 | 0 | 56.25 | 90% | 49.2359
4792 | 493 | 634 | 274 | 7.4 | 32.7 | 0 | 0 | 0 | 118.9811 | 44.3053 | 0 | 0 | 44.3053 | 0 | 0 | 0 | 0 | 0 | 118.9811 | 0 | 1203.3785 | 94.34% | 0 | 4.1744 | 51.6301 | 82.61% | 48.4797
4793 | 349 | 446 | 246 | 7.7 | 31.9 | 0 | 0 | 0 | 72.1317 | 29.642 | 0 | 0 | 29.642 | 0 | 0 | 0 | 0 | 0 | 72.1317 | 0 | 1275.5102 | 100% | 0 | 17.931 | 31.7852 | 50.86% | 47.573
4794 | 174 | 248 | 178 | 7.1 | 30.8 | 0 | 0 | 0 | 0 | 14.4296 | 0 | 0 | 14.4296 | 0 | 0 | 0 | 84.9705 | 32.1602 | 0 | 84.9705 | 1190.5397 | 93.34% | 0 | 0 | 31.7852 | 50.86% | 46.5898
4795 | 28 | 81 | 74 | 7.3 | 29.6 | 0 | 0 | 0 | 0 | 4.129 | 0 | 0 | 4.129 | 0 | 0 | 0 | 106.1947 | 41.2324 | 0 | 106.1947 | 1084.345 | 85.01% | 0 | 0 | 31.7852 | 50.86% | 45.3614
4796 | 0 | 5 | 5 | 6 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.0392 | 42.6053 | 0 | 109.0392 | 975.3058 | 76.46% | 0 | 0 | 31.7852 | 50.86% | 42.6053
4797 | 0 | 0 | 0 | 5.7 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6624 | 41.0009 | 0 | 104.6624 | 870.6434 | 68.26% | 0 | 0 | 31.7852 | 50.86% | 41.0009
4798 | 0 | 0 | 0 | 4.9 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4396 | 38.5136 | 0 | 98.4396 | 772.2038 | 60.54% | 0 | 0 | 31.7852 | 50.86% | 38.5136
4799 | 0 | 0 | 0 | 4.3 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5214 | 36.4412 | 0 | 93.5214 | 678.6823 | 53.21% | 0 | 0 | 31.7852 | 50.86% | 36.4412
4800 | 0 | 0 | 0 | 3.7 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.399 | 35.1418 | 0 | 90.399 | 588.2833 | 46.12% | 0 | 0 | 31.7852 | 50.86% | 35.1418
4801 | 0 | 0 | 0 | 1.4 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.283 | 39.826 | 0 | 101.283 | 487.0003 | 38.18% | 5.2426 | 0 | 36.5222 | 58.44% | 34.5834
4802 | 0 | 0 | 0 | 0.7 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9112 | 34.075 | 0 | 87.9112 | 399.0891 | 31.29% | 0 | 0 | 36.5222 | 58.44% | 34.075
4803 | 0 | 0 | 0 | 1 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.0891 | 31.29% | 0 | 16.2035 | 18.5893 | 29.74% | 16.2035
4804 | 0 | 0 | 0 | 1.2 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 399.0891 | 31.29% | 0 | 0 | 18.5893 | 29.74% | 0
4805 | 0 | 0 | 0 | 1.1 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8839 | 36.6362 | 0 | 93.8839 | 305.2053 | 23.93% | 0 | 0 | 18.5893 | 29.74% | 36.6362
4806 | 9 | 29 | 28 | 1 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.1162 | 0 | 127.551 | 177.6542 | 13.93% | 11.2253 | 0 | 28.732 | 45.97% | 39.8909
4807 | 103 | 148 | 117 | 0.9 | 26.7 | 0 | 0 | 0 | 0 | 5.1396 | 0 | 0 | 5.1396 | 0 | 0 | 0 | 97.0701 | 37.6886 | 0 | 97.0701 | 80.5841 | 6.318% | 0 | 0 | 28.732 | 45.97% | 42.8281
4808 | 141 | 290 | 221 | 0.6 | 29.6 | 0 | 0 | 0 | 0 | 13.7443 | 0 | 0 | 13.7443 | 0 | 0 | 0 | 80.5841 | 30.4292 | 0 | 80.5841 | 0 | 0% | 0 | 0 | 28.732 | 45.97% | 44.1735
4809 | 294 | 509 | 311 | 1.8 | 31.6 | 0 | 0 | 0 | 58.1029 | 27.4956 | 0 | 0 | 27.4956 | 0 | 0 | 0 | 0 | 0 | 58.1029 | 0 | 58.1029 | 4.555% | 0 | 17.6667 | 9.1797 | 14.69% | 45.1623
4810 | 511 | 719 | 311 | 4.8 | 33.3 | 0 | 0 | 0 | 101.0714 | 43.3618 | 0 | 0 | 43.3618 | 0 | 0 | 0 | 0 | 0 | 101.0714 | 0 | 159.1743 | 12.48% | 0 | 2.6472 | 6.25 | 10% | 46.009
4811 | 612 | 840 | 288 | 5.4 | 34 | 0 | 0 | 0 | 157.8364 | 53.6935 | 0 | 7.839 | 45.8544 | 0 | 0 | 0 | 0 | 0 | 157.8364 | 0 | 317.0107 | 24.85% | 7.839 | 0 | 13.333 | 21.33% | 45.8544
4812 | 656 | 915 | 280 | 4.7 | 33.9 | 0 | 0 | 0 | 176.701 | 60.3986 | 0 | 15.4438 | 44.9548 | 0 | 0 | 0 | 0 | 0 | 176.701 | 0 | 493.7117 | 38.71% | 15.4438 | 0 | 27.2874 | 43.66% | 44.9548
4813 | 673 | 933 | 271 | 5.7 | 33.7 | 0 | 0 | 0 | 183.9346 | 44.5855 | 19.0306 | 0.34655 | 44.2389 | 0 | 0 | 0 | 0 | 0 | 183.9346 | 0 | 677.6463 | 53.13% | 0.34655 | 0 | 27.6006 | 44.16% | 44.2389
4814 | 662 | 888 | 263 | 6 | 33.4 | 0 | 0 | 0 | 179.3276 | 61.9391 | 0 | 18.143 | 43.796 | 0 | 0 | 0 | 0 | 0 | 179.3276 | 0 | 856.9739 | 67.19% | 18.143 | 0 | 43.9939 | 70.39% | 43.796
4815 | 614 | 783 | 257 | 6.3 | 32.7 | 0 | 0 | 0 | 160.7679 | 55.4152 | 0 | 12.101 | 43.3142 | 0 | 0 | 0 | 0 | 0 | 160.7679 | 0 | 1017.7418 | 79.79% | 12.101 | 0 | 54.9278 | 87.88% | 43.3142
4816 | 536 | 633 | 243 | 6.8 | 31.4 | 0 | 0 | 0 | 131.7282 | 44.6981 | 0 | 1.4633 | 43.2348 | 0 | 0 | 0 | 0 | 0 | 131.7282 | 0 | 1149.47 | 90.12% | 1.4633 | 0 | 56.25 | 90% | 43.2348
4817 | 418 | 450 | 212 | 7 | 30.7 | 0 | 0 | 0 | 91.5493 | 30.6721 | 0 | 0 | 30.6721 | 0 | 0 | 0 | 0 | 0 | 91.5493 | 0 | 1241.0193 | 97.3% | 0 | 12.4331 | 42.4899 | 67.98% | 43.1053
4818 | 268 | 258 | 153 | 6.6 | 30.2 | 0 | 0 | 0 | 0 | 15.0017 | 0 | 0 | 15.0017 | 0 | 0 | 0 | 75.4109 | 28.1955 | 0 | 75.4109 | 1165.6083 | 91.38% | 0 | 0 | 42.4899 | 67.98% | 43.1972
4819 | 71 | 84 | 68 | 6.2 | 28.1 | 0 | 0 | 0 | 0 | 3.8301 | 0 | 0 | 3.8301 | 0 | 0 | 0 | 100.5163 | 39.0064 | 0 | 100.5163 | 1065.092 | 83.5% | 0 | 0 | 42.4899 | 67.98% | 42.8365
4820 | 1 | 5 | 5 | 5.5 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9381 | 40.3059 | 0 | 102.9381 | 962.1539 | 75.43% | 0 | 0 | 42.4899 | 67.98% | 40.3059
4821 | 0 | 0 | 0 | 4.9 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4147 | 38.0136 | 0 | 97.4147 | 864.7392 | 67.8% | 0 | 0 | 42.4899 | 67.98% | 38.0136
4822 | 0 | 0 | 0 | 2.1 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8078 | 34.3914 | 0 | 88.8078 | 775.9314 | 60.83% | 0 | 1.2768 | 41.0767 | 65.72% | 35.6683
4823 | 0 | 0 | 0 | 1.2 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.7494 | 0 | 38.2653 | 737.6661 | 57.83% | 0 | 21.2282 | 17.5828 | 28.13% | 33.9775
4824 | 0 | 0 | 0 | 0.9 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0942 | 32.7339 | 0 | 85.0942 | 652.5719 | 51.16% | 0 | 0 | 17.5828 | 28.13% | 32.7339
4825 | 0 | 0 | 0 | 0.9 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.221 | 31.9414 | 0 | 83.221 | 569.3509 | 44.64% | 0 | 0 | 17.5828 | 28.13% | 31.9414
4826 | 0 | 0 | 0 | 1 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1394 | 31.5933 | 0 | 82.1394 | 487.2115 | 38.2% | 0 | 0 | 17.5828 | 28.13% | 31.5933
4827 | 0 | 0 | 0 | 1 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6234 | 31.4052 | 0 | 81.6234 | 405.5881 | 31.8% | 0 | 0 | 17.5828 | 28.13% | 31.4052
4828 | 0 | 0 | 0 | 2 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5354 | 30.9763 | 0 | 80.5354 | 325.0527 | 25.48% | 0 | 0 | 17.5828 | 28.13% | 30.9763
4829 | 0 | 0 | 0 | 2.6 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7058 | 32.2854 | 0 | 83.7058 | 241.3469 | 18.92% | 0 | 0 | 17.5828 | 28.13% | 32.2854
4830 | 35 | 33 | 28 | 3.6 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.9157 | 34.8967 | 0 | 89.9157 | 151.4311 | 11.87% | 0 | 0 | 17.5828 | 28.13% | 34.8967
4831 | 274 | 177 | 99 | 3.4 | 24.6 | 0 | 0 | 0 | 0 | 4.7658 | 0 | 0 | 4.7658 | 0 | 0 | 0 | 83.9862 | 32.291 | 0 | 83.9862 | 67.4449 | 5.288% | 0 | 0 | 17.5828 | 28.13% | 37.0568
4832 | 476 | 374 | 151 | 3.6 | 27.4 | 0 | 0 | 0 | 0 | 13.7558 | 0 | 0 | 13.7558 | 0 | 0 | 0 | 67.4449 | 25.0433 | 0 | 67.4449 | 0 | 0% | 0 | 0 | 17.5828 | 28.13% | 38.7991
4833 | 593 | 567 | 184 | 6.1 | 29.2 | 0 | 0 | 0 | 132.2174 | 29.9658 | 0 | 0 | 29.9658 | 0 | 0 | 0 | 0 | 0 | 132.2174 | 0 | 132.2174 | 10.37% | 0 | 10.2399 | 6.25 | 10% | 40.2057
4834 | 679 | 735 | 199 | 7.4 | 31 | 0 | 0 | 0 | 167.7663 | 44.971 | 0 | 3.4437 | 41.5273 | 0 | 0 | 0 | 0 | 0 | 167.7663 | 0 | 299.9837 | 23.52% | 3.4437 | 0 | 9.3616 | 14.98% | 41.5273
4835 | 704 | 853 | 220 | 7.4 | 31.4 | 0 | 0 | 0 | 182.8223 | 51.4908 | 4.1986 | 9.0499 | 42.4409 | 0 | 0 | 0 | 0 | 0 | 182.8223 | 0 | 482.8061 | 37.85% | 9.0499 | 0 | 17.5387 | 28.06% | 42.4409
4836 | 695 | 926 | 254 | 8.1 | 32.3 | 0 | 0 | 0 | 185.4539 | 62.7207 | 0 | 20.9079 | 41.8128 | 0 | 0 | 0 | 0 | 0 | 185.4539 | 0 | 668.26 | 52.39% | 20.9079 | 0 | 36.4302 | 58.29% | 41.8128
4837 | 617 | 909 | 300 | 8.5 | 32.1 | 0 | 0 | 0 | 164.6148 | 63.0768 | 0 | 21.9352 | 41.1416 | 0 | 0 | 0 | 0 | 0 | 164.6148 | 0 | 832.8748 | 65.3% | 21.9352 | 0 | 56.25 | 90% | 41.1416
4838 | 534 | 892 | 385 | 9.3 | 31.5 | 0 | 0 | 0 | 137.9436 | 40.8338 | 21.8812 | 0 | 40.8338 | 0 | 0 | 0 | 0 | 0 | 137.9436 | 0 | 970.8184 | 76.11% | 0 | 0 | 56.25 | 90% | 40.8338
4839 | 619 | 788 | 258 | 9 | 31 | 0 | 0 | 0 | 159.9439 | 40.5455 | 16.1824 | 0 | 40.5455 | 0 | 0 | 0 | 0 | 0 | 159.9439 | 0 | 1130.7624 | 88.65% | 0 | 0 | 56.25 | 90% | 40.5455
4840 | 554 | 636 | 233 | 8.2 | 30.6 | 0 | 0 | 0 | 44.786 | 40.707 | 4.6356 | 0 | 40.707 | 0 | 0 | 0 | 0 | 0 | 44.786 | 0 | 1175.5483 | 92.16% | 0 | 0 | 56.25 | 90% | 40.707
4841 | 454 | 459 | 201 | 8.4 | 29.9 | 0 | 0 | 0 | 99.9619 | 31.6014 | 0 | 0 | 31.6014 | 0 | 0 | 0 | 0 | 0 | 99.9619 | 0 | 1275.5102 | 100% | 0 | 9.4622 | 45.7779 | 73.24% | 41.0636
4842 | 128 | 173 | 118 | 8.1 | 28.2 | 0 | 0 | 0 | 0 | 9.8668 | 0 | 0 | 9.8668 | 0 | 0 | 0 | 84.7834 | 32.3318 | 0 | 84.7834 | 1190.7268 | 93.35% | 0 | 0 | 45.7779 | 73.24% | 42.1986
4843 | 27 | 71 | 65 | 7.4 | 25.9 | 0 | 0 | 0 | 0 | 3.6747 | 0 | 0 | 3.6747 | 0 | 0 | 0 | 101.948 | 39.8442 | 0 | 101.948 | 1088.7788 | 85.36% | 0 | 0 | 45.7779 | 73.24% | 43.5189
4844 | 0 | 6 | 6 | 5.4 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.07 | 41.3324 | 0 | 105.07 | 983.7088 | 77.12% | 0 | 0 | 45.7779 | 73.24% | 41.3324
4845 | 0 | 0 | 0 | 5.5 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9289 | 38.7489 | 0 | 98.9289 | 884.7799 | 69.37% | 0 | 0 | 45.7779 | 73.24% | 38.7489
4846 | 0 | 0 | 0 | 4.6 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.4352 | 47.9907 | 0 | 120.4352 | 764.3447 | 59.92% | 11.5898 | 0 | 56.25 | 90% | 36.4008
4847 | 0 | 0 | 0 | 2.3 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.3447 | 59.92% | 0 | 0 | 56.25 | 90% | 0
4848 | 0 | 0 | 0 | 1.5 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.3447 | 59.92% | 0 | 17.5444 | 36.8331 | 58.93% | 17.5444
4849 | 0 | 0 | 0 | 2.4 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.1784 | 40.5688 | 0 | 103.1784 | 661.1663 | 51.84% | 7.2737 | 0 | 43.4053 | 69.45% | 33.2951
4850 | 0 | 0 | 0 | 2.7 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1312 | 33.7478 | 0 | 87.1312 | 574.0351 | 45% | 0 | 0 | 43.4053 | 69.45% | 33.7478
4851 | 0 | 0 | 0 | 2.4 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.1374 | 0 | 127.551 | 446.4841 | 35% | 14.2157 | 0 | 56.25 | 90% | 36.9217
4852 | 0 | 0 | 0 | 2.3 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5784 | 40.0023 | 0 | 101.5784 | 344.9057 | 27.04% | 0 | 0 | 56.25 | 90% | 40.0023
4853 | 0 | 0 | 0 | 1.3 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.5675 | 43.8364 | 0 | 110.5675 | 234.3382 | 18.37% | 0 | 0 | 56.25 | 90% | 43.8364
4854 | 51 | 31 | 24 | 1 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.1424 | 47.5466 | 0 | 119.1424 | 115.1959 | 9.031% | 0 | 0 | 56.25 | 90% | 47.5466
4855 | 369 | 187 | 86 | 2.1 | 25.6 | 0 | 0 | 0 | 0 | 4.2904 | 0 | 0 | 4.2904 | 0 | 0 | 0 | 115.1959 | 45.5235 | 0 | 115.1959 | 0 | 0% | 0 | 0 | 56.25 | 90% | 49.8139
4856 | 535 | 381 | 135 | 4.7 | 27.7 | 0 | 0 | 0 | 24.4942 | 13.4209 | 0 | 0 | 13.4209 | 0 | 0 | 0 | 0 | 0 | 24.4942 | 0 | 24.4942 | 1.92% | 0 | 20.8296 | 33.1972 | 53.12% | 34.2505
4857 | 631 | 573 | 172 | 7 | 30.5 | 0 | 0 | 0 | 141.2784 | 30.3087 | 3.5527e-15 | 0 | 30.3087 | 0 | 0 | 0 | 0 | 0 | 141.2784 | 0 | 165.7726 | 13% | 0 | 19.6913 | 11.4042 | 18.25% | 50
4858 | 680 | 734 | 204 | 7.7 | 31.5 | 0 | 0 | 0 | 167.7685 | 45.3429 | 0 | 0 | 45.3429 | 0 | 0 | 0 | 0 | 0 | 167.7685 | 0 | 333.5411 | 26.15% | 0 | 4.6571 | 6.25 | 10% | 50
4859 | 691 | 849 | 233 | 7.6 | 32.5 | 0 | 0 | 0 | 178.9055 | 55.6835 | 0 | 5.6835 | 50 | 0 | 0 | 0 | 0 | 0 | 178.9055 | 0 | 512.4466 | 40.18% | 5.6835 | 0 | 11.3854 | 18.22% | 50
4860 | 723 | 927 | 233 | 7.7 | 33.6 | 0 | 0 | 0 | 194.2321 | 62.8112 | 0 | 12.8112 | 50 | 0 | 0 | 0 | 0 | 0 | 194.2321 | 0 | 706.6787 | 55.4% | 12.8112 | 0 | 22.9611 | 36.74% | 50
4861 | 734 | 944 | 227 | 8.3 | 34.2 | 0 | 0 | 0 | 200.1748 | 65.6077 | 0 | 15.6077 | 50 | 0 | 0 | 0 | 0 | 0 | 200.1748 | 0 | 906.8535 | 71.1% | 15.6077 | 0 | 37.0636 | 59.3% | 50
4862 | 717 | 900 | 227 | 9.2 | 34.2 | 0 | 0 | 0 | 193.2969 | 63.9734 | 0 | 13.9734 | 50 | 0 | 0 | 0 | 0 | 0 | 193.2969 | 0 | 1100.1503 | 86.25% | 13.9734 | 0 | 49.6894 | 79.5% | 50
4863 | 668 | 793 | 225 | 8 | 33.7 | 0 | 0 | 0 | 175.3599 | 56.916 | 0 | 6.916 | 50 | 0 | 0 | 0 | 0 | 0 | 175.3599 | 0 | 1275.5102 | 100% | 6.916 | 0 | 55.9384 | 89.5% | 50
4864 | 586 | 640 | 217 | 8.2 | 32.4 | 0 | 0 | 0 | 0 | 37.5342 | 8.4241 | 0 | 37.5342 | 0 | 0 | 0 | 38.2653 | 12.4658 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 55.9384 | 89.5% | 50
4865 | 490 | 462 | 187 | 7.6 | 32.1 | 0 | 0 | 0 | 0 | 31.8632 | 0 | 0 | 31.8632 | 0 | 0 | 0 | 52.6101 | 18.4816 | 0 | 52.6101 | 1184.6348 | 92.88% | 0.34482 | 0 | 56.25 | 90% | 50
4866 | 321 | 266 | 144 | 7.8 | 30.3 | 0 | 0 | 0 | 55.9076 | 15.6214 | 0 | 0 | 15.6214 | 0 | 0 | 0 | 0 | 0 | 55.9076 | 0 | 1240.5424 | 97.26% | 0 | 25 | 28.5817 | 45.73% | 40.6215
4867 | 93 | 90 | 70 | 6.9 | 27.9 | 0 | 0 | 0 | 0 | 3.9973 | 0 | 0 | 3.9973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.5424 | 97.26% | 0 | 20.178 | 6.25 | 10% | 24.1753
4868 | 0 | 5 | 5 | 5.5 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.4345 | 44.7166 | 0 | 113.4345 | 1127.1079 | 88.37% | 0 | 0 | 6.25 | 10% | 44.7166
4869 | 0 | 0 | 0 | 4.3 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.4092 | 42.2028 | 0 | 107.4092 | 1019.6986 | 79.94% | 0 | 0 | 6.25 | 10% | 42.2028
4870 | 0 | 0 | 0 | 3.4 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 50.8048 | 0 | 127.551 | 892.1476 | 69.94% | 11.1158 | 0 | 16.2938 | 26.07% | 39.689
4871 | 0 | 0 | 0 | 1.2 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 50.8781 | 0 | 127.551 | 764.5966 | 59.94% | 13.0094 | 0 | 28.0486 | 44.88% | 37.8687
4872 | 0 | 0 | 0 | 1.2 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.5966 | 59.94% | 0 | 19.6963 | 6.25 | 10% | 19.6963
4873 | 0 | 0 | 0 | 2 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.5966 | 59.94% | 0 | 0 | 6.25 | 10% | 0
4874 | 0 | 0 | 0 | 3 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.0419 | 36.6961 | 0 | 94.0419 | 670.5547 | 52.57% | 0 | 0 | 6.25 | 10% | 36.6961
4875 | 0 | 0 | 0 | 2.4 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4473 | 39.0219 | 0 | 99.4473 | 571.1074 | 44.77% | 0 | 0 | 6.25 | 10% | 39.0219
4876 | 0 | 0 | 0 | 2.7 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.2125 | 47.4873 | 0 | 119.2125 | 451.8948 | 35.43% | 5.641 | 0 | 11.347 | 18.16% | 41.8463
4877 | 0 | 0 | 0 | 2.5 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.36 | 45.0258 | 0 | 113.36 | 338.5348 | 26.54% | 0 | 0 | 11.347 | 18.16% | 45.0258
4878 | 58 | 34 | 27 | 2.3 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.5173 | 48.5368 | 0 | 121.5173 | 217.0176 | 17.01% | 0 | 0 | 11.347 | 18.16% | 48.5368
4879 | 324 | 181 | 92 | 2.6 | 25.2 | 0 | 0 | 0 | 0 | 4.4252 | 0 | 0 | 4.4252 | 0 | 0 | 0 | 115.2124 | 45.5748 | 0 | 115.2124 | 101.8051 | 7.982% | 0 | 0 | 11.347 | 18.16% | 50
4880 | 536 | 381 | 135 | 2.7 | 29 | 0 | 0 | 0 | 0 | 13.3111 | 0 | 0 | 13.3111 | 0 | 0 | 0 | 95.2693 | 36.6889 | 0 | 95.2693 | 6.5358 | 0.5124% | 0 | 0 | 11.347 | 18.16% | 50
4881 | 661 | 579 | 162 | 4.1 | 31.7 | 0 | 0 | 0 | 151.3379 | 30.4285 | 0 | 0 | 30.4285 | 0 | 0 | 0 | 0 | 0 | 151.3379 | 0 | 157.8737 | 12.38% | 0 | 0 | 11.347 | 18.16% | 30.4285
4882 | 731 | 749 | 179 | 5.3 | 33.3 | 0 | 0 | 0 | 183.9879 | 45.3946 | 0 | 0 | 45.3946 | 0 | 0 | 0 | 0 | 0 | 183.9879 | 0 | 341.8616 | 26.8% | 0 | 4.6054 | 6.25 | 10% | 50
4883 | 772 | 875 | 188 | 5.5 | 34.6 | 0 | 0 | 0 | 204.2144 | 56.3383 | 0 | 6.3383 | 50 | 0 | 0 | 0 | 0 | 0 | 204.2144 | 0 | 546.076 | 42.81% | 6.3383 | 0 | 11.977 | 19.16% | 50
4884 | 783 | 947 | 199 | 6.9 | 35.3 | 0 | 0 | 0 | 212.7071 | 63.331 | 0 | 13.331 | 50 | 0 | 0 | 0 | 0 | 0 | 212.7071 | 0 | 758.783 | 59.49% | 13.331 | 0 | 24.0224 | 38.44% | 50
4885 | 799 | 968 | 192 | 8 | 35.6 | 0 | 0 | 0 | 220.0654 | 66.6909 | 0 | 16.6909 | 50 | 0 | 0 | 0 | 0 | 0 | 220.0654 | 0 | 978.8484 | 76.74% | 16.6909 | 0 | 39.1036 | 62.57% | 50
4886 | 790 | 936 | 198 | 7.8 | 35.9 | 0 | 0 | 0 | 216.3648 | 65.5844 | 0 | 15.5844 | 50 | 0 | 0 | 0 | 0 | 0 | 216.3648 | 0 | 1195.2132 | 93.7% | 15.5844 | 0 | 53.1851 | 85.1% | 50
4887 | 699 | 819 | 223 | 7.5 | 35.9 | 0 | 0 | 0 | 80.297 | 53.392 | 4.726 | 3.392 | 50 | 0 | 0 | 0 | 0 | 0 | 80.297 | 0 | 1275.5102 | 100% | 3.392 | 0 | 56.25 | 90% | 50
4888 | 160 | 417 | 298 | 7.1 | 35 | 0 | 0 | 0 | 0 | 27.5332 | 0 | 0 | 27.5332 | 0 | 0 | 0 | 62.6903 | 22.4668 | 0 | 62.6903 | 1212.8199 | 95.09% | 0 | 0 | 56.25 | 90% | 50
4889 | 149 | 280 | 203 | 6.3 | 34.1 | 0 | 0 | 0 | 0 | 18.5687 | 0 | 0 | 18.5687 | 0 | 0 | 0 | 84.0587 | 31.422 | 0 | 84.0587 | 1128.7611 | 88.49% | 0 | 0 | 56.25 | 90% | 49.9907
4890 | 461 | 288 | 116 | 6.6 | 34 | 0 | 0 | 0 | 91.0055 | 16.7306 | 0 | 0 | 16.7306 | 0 | 0 | 0 | 0 | 0 | 91.0055 | 0 | 1219.7666 | 95.63% | 0 | 20.178 | 33.9183 | 54.27% | 36.9086
4891 | 183 | 99 | 62 | 6.1 | 32.1 | 0 | 0 | 0 | 0 | 3.5528 | 0 | 0 | 3.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219.7666 | 95.63% | 0 | 25 | 6.25 | 10% | 28.5528
4892 | 2 | 5 | 5 | 4.6 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.7325 | 44.5425 | 0 | 113.7325 | 1106.0342 | 86.71% | 0 | 0 | 6.25 | 10% | 44.5425
4893 | 0 | 0 | 0 | 4 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.2065 | 42.4465 | 0 | 108.2065 | 997.8277 | 78.23% | 0 | 0 | 6.25 | 10% | 42.4465
4894 | 0 | 0 | 0 | 2.6 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8346 | 39.8255 | 0 | 101.8346 | 895.9931 | 70.25% | 0 | 0 | 6.25 | 10% | 39.8255
4895 | 0 | 0 | 0 | 1.4 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.7193 | 38.1347 | 0 | 97.7193 | 798.2738 | 62.58% | 0 | 0 | 6.25 | 10% | 38.1347
4896 | 0 | 0 | 0 | 1 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1204 | 37.0846 | 0 | 95.1204 | 703.1534 | 55.13% | 0 | 0 | 6.25 | 10% | 37.0846
4897 | 0 | 0 | 0 | 1.6 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.0177 | 0 | 127.551 | 575.6023 | 45.13% | 14.4107 | 0 | 19.271 | 30.83% | 36.607
4898 | 0 | 0 | 0 | 1.9 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2807 | 36.7337 | 0 | 94.2807 | 481.3216 | 37.74% | 0 | 0 | 19.271 | 30.83% | 36.7337
4899 | 0 | 0 | 0 | 2.4 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.688 | 47.2108 | 0 | 118.688 | 362.6336 | 28.43% | 8.0845 | 0 | 26.5758 | 42.52% | 39.1263
4900 | 0 | 0 | 0 | 2.4 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.04 | 0 | 127.551 | 235.0826 | 18.43% | 9.3372 | 0 | 35.0125 | 56.02% | 41.7028
4901 | 0 | 0 | 0 | 2.5 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3309 | 44.8865 | 0 | 113.3309 | 121.7517 | 9.545% | 0 | 0 | 35.0125 | 56.02% | 44.8865
4902 | 55 | 30 | 23 | 2.3 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.7517 | 48.5228 | 0 | 121.7517 | 0 | 0% | 0 | 0 | 35.0125 | 56.02% | 48.5228
4903 | 412 | 188 | 77 | 2.6 | 26.5 | 0 | 0 | 0 | 47.8648 | 3.7795 | 0 | 0 | 3.7795 | 0 | 0 | 0 | 0 | 0 | 47.8648 | 0 | 47.8648 | 3.753% | 0 | 0.98867 | 33.9183 | 54.27% | 4.7682
4904 | 618 | 391 | 110 | 3.5 | 29.6 | 0 | 0 | 0 | 116.7004 | 12.8483 | 0 | 0 | 12.8483 | 0 | 0 | 0 | 0 | 0 | 116.7004 | 0 | 164.5653 | 12.9% | 0 | 25 | 6.25 | 10% | 37.8483
4905 | 738 | 592 | 128 | 4.7 | 32.3 | 0 | 0 | 0 | 0 | 30.5862 | 0 | 0 | 30.5862 | 0 | 0 | 0 | 54.8689 | 19.4138 | 0 | 54.8689 | 109.6964 | 8.6% | 0 | 0 | 6.25 | 10% | 50
4906 | 790 | 759 | 144 | 5 | 33.3 | 0 | 0 | 0 | 0 | 37.5729 | 8.1051 | 0 | 37.5729 | 0 | 0 | 0 | 38.2653 | 12.4271 | 0 | 38.2653 | 71.4311 | 5.6% | 0 | 0 | 6.25 | 10% | 50
4907 | 814 | 882 | 159 | 6 | 34 | 0 | 0 | 0 | 215.9042 | 56.8869 | 0 | 6.8869 | 50 | 0 | 0 | 0 | 0 | 0 | 215.9042 | 0 | 287.3353 | 22.53% | 6.8869 | 0 | 12.4727 | 19.96% | 50
4908 | 830 | 955 | 163 | 6.3 | 34.6 | 0 | 0 | 0 | 227.2807 | 63.9856 | 0 | 13.9856 | 50 | 0 | 0 | 0 | 0 | 0 | 227.2807 | 0 | 514.616 | 40.35% | 13.9856 | 0 | 25.1096 | 40.18% | 50
4909 | 849 | 976 | 155 | 6.8 | 35 | 0 | 0 | 0 | 236.3488 | 66.6254 | 0 | 16.6254 | 50 | 0 | 0 | 0 | 0 | 0 | 236.3488 | 0 | 750.9648 | 58.88% | 16.6254 | 0 | 40.1317 | 64.21% | 50
4910 | 849 | 934 | 145 | 6.6 | 35.1 | 0 | 0 | 0 | 235.2869 | 65.1659 | 0 | 15.1659 | 50 | 0 | 0 | 0 | 0 | 0 | 235.2869 | 0 | 986.2517 | 77.32% | 15.1659 | 0 | 53.835 | 86.14% | 50
4911 | 822 | 833 | 139 | 5.8 | 35.2 | 0 | 0 | 0 | 0 | 52.6728 | 6.1378 | 2.6728 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 986.2517 | 77.32% | 2.6728 | 0 | 56.25 | 90% | 50
4912 | 780 | 686 | 129 | 6.4 | 34.8 | 0 | 0 | 0 | 0 | 49.3722 | 0 | 0 | 49.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 986.2517 | 77.32% | 0 | 0.6278 | 55.5552 | 88.89% | 50
4913 | 712 | 504 | 111 | 6 | 34.5 | 0 | 0 | 0 | 171.9045 | 35.4588 | 0 | 0 | 35.4588 | 0 | 0 | 0 | 0 | 0 | 171.9045 | 0 | 1158.1562 | 90.8% | 0 | 14.5412 | 39.462 | 63.14% | 50
4914 | 568 | 298 | 88 | 6.1 | 33.3 | 0 | 0 | 0 | 117.354 | 17.3839 | 0 | 0 | 17.3839 | 0 | 0 | 0 | 0 | 0 | 117.354 | 0 | 1275.5102 | 100% | 0 | 25 | 11.7936 | 18.87% | 42.3839
4915 | 262 | 100 | 50 | 4.5 | 31.5 | 0 | 0 | 0 | 0 | 2.9338 | 0 | 0 | 2.9338 | 0 | 0 | 0 | 116.637 | 45.3662 | 0 | 116.637 | 1158.8732 | 90.86% | 0 | 0 | 11.7936 | 18.87% | 48.3
4916 | 4 | 4 | 4 | 3.7 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.6561 | 44.9074 | 0 | 114.6561 | 1044.2172 | 81.87% | 0 | 0 | 11.7936 | 18.87% | 44.9074
4917 | 0 | 0 | 0 | 2.9 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.7105 | 42.6053 | 0 | 108.7105 | 935.5067 | 73.34% | 0 | 0 | 11.7936 | 18.87% | 42.6053
4918 | 0 | 0 | 0 | 1.5 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.036 | 39.8617 | 0 | 102.036 | 833.4707 | 65.34% | 0 | 0 | 11.7936 | 18.87% | 39.8617
4919 | 0 | 0 | 0 | 2.2 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1554 | 37.8019 | 0 | 97.1554 | 736.3153 | 57.73% | 0 | 0 | 11.7936 | 18.87% | 37.8019
4920 | 0 | 0 | 0 | 3.1 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736.3153 | 57.73% | 0 | 0 | 11.7936 | 18.87% | 0
4921 | 0 | 0 | 0 | 2 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736.3153 | 57.73% | 0 | 0 | 11.7936 | 18.87% | 0
4922 | 0 | 0 | 0 | 2.5 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.6818 | 15.8942 | 0 | 45.6818 | 690.6336 | 54.15% | 0 | 0 | 11.7936 | 18.87% | 15.8942
4923 | 0 | 0 | 0 | 2.3 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.7706 | 38.1835 | 0 | 97.7706 | 592.863 | 46.48% | 0 | 0 | 11.7936 | 18.87% | 38.1835
4924 | 0 | 0 | 0 | 2.1 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8973 | 40.3937 | 0 | 102.8973 | 489.9657 | 38.41% | 0 | 0 | 11.7936 | 18.87% | 40.3937
4925 | 0 | 0 | 0 | 2.7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3902 | 43.2097 | 0 | 109.3902 | 380.5755 | 29.84% | 0 | 0 | 11.7936 | 18.87% | 43.2097
4926 | 57 | 29 | 23 | 2.9 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.1866 | 46.5048 | 0 | 117.1866 | 263.389 | 20.65% | 0 | 0 | 11.7936 | 18.87% | 46.5048
4927 | 409 | 186 | 76 | 1.4 | 27.2 | 0 | 0 | 0 | 0 | 3.7056 | 0 | 0 | 3.7056 | 0 | 0 | 0 | 114.5654 | 45.0693 | 0 | 114.5654 | 148.8236 | 11.67% | 0 | 0 | 11.7936 | 18.87% | 48.7749
4928 | 634 | 391 | 105 | 2 | 30.1 | 0 | 0 | 0 | 0 | 12.6159 | 0 | 0 | 12.6159 | 0 | 0 | 0 | 97.2064 | 37.3841 | 0 | 97.2064 | 51.6171 | 4.047% | 0 | 0 | 11.7936 | 18.87% | 50
4929 | 766 | 594 | 114 | 3.8 | 31.8 | 0 | 0 | 0 | 0 | 30.4816 | 3.5527e-15 | 0 | 30.4816 | 0 | 0 | 0 | 51.6171 | 18.0841 | 0 | 51.6171 | 0 | 0% | 0 | 1.4343 | 10.2062 | 16.33% | 50
4930 | 844 | 770 | 117 | 4.8 | 32.6 | 0 | 0 | 0 | 0 | 46.4253 | 7.1054e-15 | 0 | 46.4253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.5747 | 6.25 | 10% | 50
4931 | 890 | 902 | 116 | 5.1 | 33.5 | 0 | 0 | 0 | 238.8799 | 50 | 7.7026 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 238.8799 | 0 | 238.8799 | 18.73% | 0 | 0 | 6.25 | 10% | 50
4932 | 903 | 973 | 117 | 4.9 | 34.3 | 0 | 0 | 0 | 250.5189 | 64.4381 | 0 | 14.4381 | 50 | 0 | 0 | 0 | 0 | 0 | 250.5189 | 0 | 489.3988 | 38.37% | 14.4381 | 0 | 19.2956 | 30.87% | 50
4933 | 902 | 985 | 116 | 5.1 | 34.8 | 0 | 0 | 0 | 253.956 | 67.0102 | 0 | 17.0102 | 50 | 0 | 0 | 0 | 0 | 0 | 253.956 | 0 | 743.3548 | 58.28% | 17.0102 | 0 | 34.6654 | 55.46% | 50
4934 | 898 | 943 | 112 | 5.5 | 34.9 | 0 | 0 | 0 | 251.1517 | 64.0864 | 1.7942 | 14.0864 | 50 | 0 | 0 | 0 | 0 | 0 | 251.1517 | 0 | 994.5065 | 77.97% | 14.0864 | 0 | 47.3932 | 75.83% | 50
4935 | 865 | 838 | 112 | 6 | 35 | 0 | 0 | 0 | 235.3565 | 59.8021 | 0 | 9.8021 | 50 | 0 | 0 | 0 | 0 | 0 | 235.3565 | 0 | 1229.8629 | 96.42% | 9.8021 | 0 | 56.25 | 90% | 50
4936 | 780 | 677 | 122 | 5.2 | 34.1 | 0 | 0 | 0 | 45.6473 | 48.8295 | 0 | 0 | 48.8295 | 0 | 0 | 0 | 0 | 0 | 45.6473 | 0 | 1275.5102 | 100% | 0 | 0.76432 | 55.4041 | 88.65% | 49.5938
4937 | 685 | 488 | 111 | 4.2 | 33.6 | 0 | 0 | 0 | 0 | 34.3417 | 0 | 0 | 34.3417 | 0 | 0 | 0 | 41.9484 | 13.9472 | 0 | 41.9484 | 1233.5618 | 96.71% | 0 | 0 | 55.4041 | 88.65% | 48.2889
4938 | 517 | 283 | 93 | 3.8 | 32.8 | 0 | 0 | 0 | 0 | 16.6303 | 0 | 0 | 16.6303 | 0 | 0 | 0 | 82.8163 | 31.0485 | 0 | 82.8163 | 1150.7455 | 90.22% | 0 | 0 | 55.4041 | 88.65% | 47.6789
4939 | 248 | 98 | 52 | 4 | 30.8 | 0 | 0 | 0 | 0 | 3.0322 | 0 | 0 | 3.0322 | 0 | 0 | 0 | 112.0965 | 43.5604 | 0 | 112.0965 | 1038.649 | 81.43% | 0 | 0 | 55.4041 | 88.65% | 46.5926
4940 | 5 | 5 | 5 | 3.1 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3596 | 43.5635 | 0 | 111.3596 | 927.2894 | 72.7% | 0 | 0 | 55.4041 | 88.65% | 43.5635
4941 | 0 | 0 | 0 | 2.3 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8493 | 41.3895 | 0 | 105.8493 | 821.4401 | 64.4% | 0 | 0 | 55.4041 | 88.65% | 41.3895
4942 | 0 | 0 | 0 | 1.3 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5019 | 38.8018 | 0 | 99.5019 | 721.9382 | 56.6% | 0 | 0 | 55.4041 | 88.65% | 38.8018
4943 | 0 | 0 | 0 | 1.6 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1144 | 37.0651 | 0 | 95.1144 | 626.8238 | 49.14% | 0 | 0 | 55.4041 | 88.65% | 37.0651
4944 | 0 | 0 | 0 | 1.6 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.7917 | 0 | 38.2653 | 588.5585 | 46.14% | 0 | 0 | 55.4041 | 88.65% | 12.7917
4945 | 0 | 0 | 0 | 1 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.3043 | 26.5906 | 0 | 70.3043 | 518.2542 | 40.63% | 0 | 0 | 55.4041 | 88.65% | 26.5906
4946 | 0 | 0 | 0 | 0.7 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3352 | 35.6794 | 0 | 91.3352 | 426.919 | 33.47% | 0 | 0 | 55.4041 | 88.65% | 35.6794
4947 | 0 | 0 | 0 | 0.3 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1284 | 38.2086 | 0 | 97.1284 | 329.7906 | 25.86% | 0 | 0 | 55.4041 | 88.65% | 38.2086
4948 | 0 | 0 | 0 | 1.4 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0935 | 40.7934 | 0 | 103.0935 | 226.6971 | 17.77% | 0 | 0 | 55.4041 | 88.65% | 40.7934
4949 | 0 | 0 | 0 | 0.8 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5154 | 43.6512 | 0 | 109.5154 | 117.1817 | 9.187% | 0 | 0 | 55.4041 | 88.65% | 43.6512
4950 | 144 | 35 | 18 | 0.5 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.1817 | 46.8822 | 0 | 117.1817 | 0 | 0% | 0 | 0 | 55.4041 | 88.65% | 46.8822
4951 | 561 | 200 | 55 | 0.7 | 24.3 | 0 | 0 | 0 | 72.4494 | 2.8184 | 0 | 0 | 2.8184 | 0 | 0 | 0 | 0 | 0 | 72.4494 | 0 | 72.4494 | 5.68% | 0 | 19.4137 | 33.9183 | 54.27% | 22.232
4952 | 731 | 407 | 81 | 1.3 | 27.4 | 0 | 0 | 0 | 91.7474 | 12.1443 | 0 | 0 | 12.1443 | 0 | 0 | 0 | 0 | 0 | 91.7474 | 0 | 164.1968 | 12.87% | 0 | 25 | 6.25 | 10% | 37.1443
4953 | 778 | 616 | 134 | 3.7 | 29.6 | 0 | 0 | 0 | 0 | 32.4208 | 0 | 0 | 32.4208 | 0 | 0 | 0 | 93.4257 | 35.8461 | 0 | 93.4257 | 70.7711 | 5.548% | 18.2669 | 0 | 22.7552 | 36.41% | 50
4954 | 446 | 663 | 313 | 4 | 30.8 | 0 | 0 | 0 | 0 | 40.7849 | 0 | 3.3164 | 37.4685 | 0 | 0 | 0 | 38.2653 | 12.5315 | 0 | 38.2653 | 32.5058 | 2.548% | 3.3164 | 0 | 25.7518 | 41.2% | 50
4955 | 353 | 704 | 391 | 4.1 | 31.8 | 0 | 0 | 0 | 83.632 | 45.9233 | 0 | 0 | 45.9233 | 0 | 0 | 0 | 0 | 0 | 83.632 | 0 | 116.1378 | 9.105% | 0 | 4.0767 | 21.24 | 33.98% | 50
4956 | 326 | 678 | 362 | 3.2 | 32.9 | 0 | 0 | 0 | 79.1297 | 44.9146 | 0 | 0 | 44.9146 | 0 | 0 | 0 | 0 | 0 | 79.1297 | 0 | 195.2675 | 15.31% | 0 | 4.5372 | 16.2185 | 25.95% | 49.4518
4957 | 779 | 927 | 176 | 2.9 | 34.4 | 0 | 0 | 0 | 218.1773 | 62.5248 | 0 | 13.5424 | 48.9824 | 0 | 0 | 0 | 0 | 0 | 218.1773 | 0 | 413.4447 | 32.41% | 13.5424 | 0 | 28.4549 | 45.53% | 48.9824
4958 | 875 | 937 | 128 | 4.1 | 35.5 | 0 | 0 | 0 | 245.4167 | 64.6282 | 0 | 16.0886 | 48.5396 | 0 | 0 | 0 | 0 | 0 | 245.4167 | 0 | 658.8614 | 51.65% | 16.0886 | 0 | 42.9919 | 68.79% | 48.5396
4959 | 850 | 839 | 127 | 4.4 | 36.1 | 0 | 0 | 0 | 232.2916 | 59.0632 | 0 | 11.5933 | 47.47 | 0 | 0 | 0 | 0 | 0 | 232.2916 | 0 | 891.153 | 69.87% | 11.5933 | 0 | 53.4672 | 85.55% | 47.47
4960 | 805 | 691 | 120 | 4.9 | 35.8 | 0 | 0 | 0 | 210.2556 | 49.6112 | 0 | 3.0799 | 46.5313 | 0 | 0 | 0 | 0 | 0 | 210.2556 | 0 | 1101.4086 | 86.35% | 3.0799 | 0 | 56.25 | 90% | 46.5313
4961 | 719 | 516 | 121 | 5.6 | 35.7 | 0 | 0 | 0 | 174.1016 | 36.2525 | 0 | 0 | 36.2525 | 0 | 0 | 0 | 0 | 0 | 174.1016 | 0 | 1275.5102 | 100% | 0 | 9.2134 | 46.0533 | 73.69% | 45.4659
4962 | 240 | 199 | 101 | 3.7 | 35.1 | 0 | 0 | 0 | 0 | 11.1074 | 0 | 0 | 11.1074 | 0 | 0 | 0 | 89.8784 | 33.7151 | 0 | 89.8784 | 1185.6318 | 92.95% | 0 | 0 | 46.0533 | 73.69% | 44.8225
4963 | 340 | 135 | 75 | 6 | 33.7 | 0 | 0 | 0 | 0 | 4.5018 | 0 | 0 | 4.5018 | 0 | 0 | 0 | 101.7811 | 38.843 | 0 | 101.7811 | 1083.8506 | 84.97% | 0 | 0 | 46.0533 | 73.69% | 43.3448
4964 | 8 | 6 | 5 | 4.7 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5499 | 40.6499 | 0 | 105.5499 | 978.3007 | 76.7% | 0 | 0 | 46.0533 | 73.69% | 40.6499
4965 | 0 | 0 | 0 | 2.8 | 30.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2256 | 39.4244 | 0 | 102.2256 | 876.0752 | 68.68% | 0 | 0 | 46.0533 | 73.69% | 39.4244
4966 | 0 | 0 | 0 | 4.1 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7646 | 37.2546 | 0 | 96.7646 | 779.3106 | 61.1% | 0 | 0 | 46.0533 | 73.69% | 37.2546
4967 | 0 | 0 | 0 | 3.2 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7789 | 35.3243 | 0 | 91.7789 | 687.5317 | 53.9% | 0 | 0 | 46.0533 | 73.69% | 35.3243
4968 | 0 | 0 | 0 | 2.2 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3671 | 34.3856 | 0 | 89.3671 | 598.1646 | 46.9% | 0 | 0 | 46.0533 | 73.69% | 34.3856
4969 | 0 | 0 | 0 | 1.9 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.5134 | 44.7615 | 0 | 113.5134 | 484.6511 | 38% | 11.1586 | 0 | 56.1357 | 89.82% | 33.6029
4970 | 0 | 0 | 0 | 1.3 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 484.6511 | 38% | 0 | 25 | 28.4674 | 45.55% | 25
4971 | 0 | 0 | 0 | 2.1 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 484.6511 | 38% | 0 | 18.657 | 7.819 | 12.51% | 18.657
4972 | 0 | 0 | 0 | 2.1 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0273 | 33.7032 | 0 | 87.0273 | 397.6239 | 31.17% | 0 | 0 | 7.819 | 12.51% | 33.7032
4973 | 0 | 0 | 0 | 1.3 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2691 | 35.6167 | 0 | 91.2691 | 306.3548 | 24.02% | 0 | 0 | 7.819 | 12.51% | 35.6167
4974 | 161 | 32 | 15 | 2.1 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2195 | 0 | 127.551 | 178.8038 | 14.02% | 12.6725 | 0 | 19.2694 | 30.83% | 38.547
4975 | 613 | 199 | 41 | 1.1 | 25 | 0 | 0 | 0 | 0 | 2.1251 | 0 | 0 | 2.1251 | 0 | 0 | 0 | 98.6375 | 38.5178 | 0 | 98.6375 | 80.1663 | 6.285% | 0 | 0 | 19.2694 | 30.83% | 40.643
4976 | 786 | 406 | 55 | 1 | 27.9 | 0 | 0 | 0 | 0 | 11.1451 | 0 | 0 | 11.1451 | 0 | 0 | 0 | 80.1663 | 30.4017 | 0 | 80.1663 | 0 | 0% | 0 | 0 | 19.2694 | 30.83% | 41.5468
4977 | 864 | 602 | 65 | 1.5 | 29.9 | 0 | 0 | 0 | 0 | 30.0198 | 0 | 0 | 30.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 11.7638 | 6.25 | 10% | 41.7836
4978 | 905 | 770 | 73 | 2.6 | 31.5 | 0 | 0 | 0 | 0 | 42.3504 | 3.2 | 0 | 42.3504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 42.3504
4979 | 927 | 895 | 79 | 4.6 | 32.6 | 0 | 0 | 0 | 0 | 41.8532 | 15.589 | 0 | 41.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 41.8532
4980 | 931 | 963 | 84 | 4 | 32.7 | 0 | 0 | 0 | 226.8148 | 40.7906 | 23.2748 | 0 | 40.7906 | 0 | 0 | 0 | 0 | 0 | 226.8148 | 0 | 226.8148 | 17.78% | 0 | 0 | 6.25 | 10% | 40.7906
4981 | 925 | 978 | 90 | 2.5 | 32.5 | 0 | 0 | 0 | 0 | 39.8923 | 25.6484 | 0 | 39.8923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226.8148 | 17.78% | 0 | 0 | 6.25 | 10% | 39.8923
4982 | 920 | 934 | 84 | 3.8 | 33.9 | 0 | 0 | 0 | 259.2069 | 64.3812 | 0.54285 | 25 | 39.3812 | 0 | 0 | 0 | 0 | 0 | 259.2069 | 0 | 486.0217 | 38.1% | 25 | 0 | 28.839 | 46.14% | 39.3812
4983 | 882 | 828 | 87 | 8.9 | 34.7 | 0 | 0 | 0 | 238.0202 | 60.1204 | 0 | 21.079 | 39.0414 | 0 | 0 | 0 | 0 | 0 | 238.0202 | 0 | 724.0419 | 56.76% | 21.079 | 0 | 47.8851 | 76.62% | 39.0414
4984 | 817 | 679 | 97 | 6.3 | 35.5 | 0 | 0 | 0 | 212.481 | 48.4662 | 0.448 | 9.2577 | 39.2085 | 0 | 0 | 0 | 0 | 0 | 212.481 | 0 | 936.5229 | 73.42% | 9.2577 | 0 | 56.25 | 90% | 39.2085
4985 | 770 | 504 | 83 | 4.3 | 34.2 | 0 | 0 | 0 | 188.9127 | 35.6985 | 0 | 0 | 35.6985 | 0 | 0 | 0 | 0 | 0 | 188.9127 | 0 | 1125.4356 | 88.23% | 0 | 3.5615 | 52.3083 | 83.69% | 39.26
4986 | 663 | 309 | 69 | 6.1 | 32.5 | 0 | 0 | 0 | 0 | 18.3938 | 0 | 0 | 18.3938 | 0 | 0 | 0 | 38.2653 | 12.4616 | 0 | 38.2653 | 1087.1703 | 85.23% | 0 | 9.1038 | 42.2328 | 67.57% | 39.9592
4987 | 430 | 116 | 41 | 5 | 30.4 | 0 | 0 | 0 | 0 | 2.7915 | 0 | 0 | 2.7915 | 0 | 0 | 0 | 91.6678 | 35.0188 | 0 | 91.6678 | 995.5025 | 78.05% | 0 | 1.6586 | 40.3972 | 64.64% | 39.4689
4988 | 7 | 4 | 4 | 3.7 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3607 | 37.1501 | 0 | 96.3607 | 899.1419 | 70.49% | 0 | 0 | 40.3972 | 64.64% | 37.1501
4989 | 0 | 0 | 0 | 4.1 | 28.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2831 | 35.0847 | 0 | 91.2831 | 807.8588 | 63.34% | 0 | 0 | 40.3972 | 64.64% | 35.0847
4990 | 0 | 0 | 0 | 4.2 | 27.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5323 | 33.1545 | 0 | 86.5323 | 721.3265 | 56.55% | 0 | 0 | 40.3972 | 64.64% | 33.1545
4991 | 0 | 0 | 0 | 2.8 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5483 | 31.5292 | 0 | 82.5483 | 638.7782 | 50.08% | 0 | 0 | 40.3972 | 64.64% | 31.5292
4992 | 0 | 0 | 0 | 1.9 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0933 | 30.5613 | 0 | 80.0933 | 558.6849 | 43.8% | 0 | 0 | 40.3972 | 64.64% | 30.5613
4993 | 0 | 0 | 0 | 1.3 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6178 | 30.0237 | 0 | 78.6178 | 480.0671 | 37.64% | 0 | 0 | 40.3972 | 64.64% | 30.0237
4994 | 0 | 0 | 0 | 1.5 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.642 | 29.6393 | 0 | 77.642 | 402.4251 | 31.55% | 0 | 0 | 40.3972 | 64.64% | 29.6393
4995 | 0 | 0 | 0 | 1.7 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6617 | 29.6672 | 0 | 77.6617 | 324.7634 | 25.46% | 0 | 0 | 40.3972 | 64.64% | 29.6672
4996 | 0 | 0 | 0 | 1.6 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.4283 | 29.2173 | 0 | 76.4283 | 248.3351 | 19.47% | 0 | 0 | 40.3972 | 64.64% | 29.2173
4997 | 0 | 0 | 0 | 2.1 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3481 | 30.4902 | 0 | 79.3481 | 168.9869 | 13.25% | 0 | 0 | 40.3972 | 64.64% | 30.4902
4998 | 136 | 30 | 16 | 1.9 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6871 | 32.7269 | 0 | 84.6871 | 84.2998 | 6.609% | 0 | 0 | 40.3972 | 64.64% | 32.7269
4999 | 563 | 194 | 48 | 2 | 25.1 | 0 | 0 | 0 | 0 | 2.3539 | 0 | 0 | 2.3539 | 0 | 0 | 0 | 84.2998 | 32.3869 | 0 | 84.2998 | 0 | 0% | 0 | 0 | 40.3972 | 64.64% | 34.7407
5000 | 747 | 398 | 65 | 2 | 26.5 | 0 | 0 | 0 | 144.5522 | 11.5757 | 0 | 0 | 11.5757 | 0 | 0 | 0 | 0 | 0 | 144.5522 | 0 | 144.5522 | 11.33% | 0 | 24.4783 | 13.3062 | 21.29% | 36.0541
5001 | 843 | 597 | 71 | 3.8 | 28 | 0 | 0 | 0 | 0 | 30.592 | 0 | 0 | 30.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144.5522 | 11.33% | 0 | 6.3757 | 6.25 | 10% | 36.9677
5002 | 842 | 733 | 85 | 3.9 | 28.7 | 0 | 0 | 0 | 215.748 | 37.7866 | 6.8594 | 0 | 37.7866 | 0 | 0 | 0 | 0 | 0 | 215.748 | 0 | 360.3002 | 28.25% | 0 | 0 | 6.25 | 10% | 37.7866
5003 | 850 | 874 | 121 | 4.1 | 29.5 | 0 | 0 | 0 | 227.9985 | 38.1083 | 18.4119 | 0 | 38.1083 | 0 | 0 | 0 | 0 | 0 | 227.9985 | 0 | 588.2987 | 46.12% | 0 | 0 | 6.25 | 10% | 38.1083
5004 | 902 | 959 | 106 | 4.5 | 29.8 | 0 | 0 | 0 | 250.5619 | 37.2309 | 27.5691 | 0 | 37.2309 | 0 | 0 | 0 | 0 | 0 | 250.5619 | 0 | 838.8606 | 65.77% | 0 | 0 | 6.25 | 10% | 37.2309
5005 | 922 | 980 | 93 | 5.6 | 30.3 | 0 | 0 | 0 | 182.5978 | 36.4733 | 31.9737 | 0 | 36.4733 | 0 | 0 | 0 | 0 | 0 | 182.5978 | 0 | 1021.4583 | 80.08% | 0 | 0 | 6.25 | 10% | 36.4733
5006 | 907 | 933 | 93 | 5.2 | 30.2 | 0 | 0 | 0 | 254.0519 | 53.2086 | 13.2836 | 17.0055 | 36.2031 | 0 | 0 | 0 | 0 | 0 | 254.0519 | 0 | 1275.5102 | 100% | 17.0055 | 0 | 21.6155 | 34.58% | 36.2031
5007 | 886 | 831 | 89 | 5.1 | 30.3 | 0 | 0 | 0 | 0 | 60.4612 | 0 | 24.4239 | 36.0373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 24.4239 | 0 | 43.684 | 69.89% | 36.0373
5008 | 851 | 684 | 81 | 4.9 | 30.1 | 0 | 0 | 0 | 0 | 50.2287 | 0 | 13.9072 | 36.3215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 13.9072 | 0 | 56.25 | 90% | 36.3215
5009 | 788 | 501 | 72 | 4.6 | 29.8 | 0 | 0 | 0 | 0 | 36.3106 | 0 | 0 | 36.3106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0.6724 | 55.5058 | 88.81% | 36.983
5010 | 664 | 298 | 59 | 3.6 | 29.4 | 0 | 0 | 0 | 0 | 17.8465 | 0 | 0 | 17.8465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 20.8022 | 32.4834 | 51.97% | 38.6486
5011 | 379 | 103 | 35 | 3.4 | 28.2 | 0 | 0 | 0 | 0 | 2.355 | 0 | 0 | 2.355 | 0 | 0 | 0 | 92.3516 | 35.5373 | 0 | 92.3516 | 1183.1586 | 92.76% | 0 | 2.0794 | 30.182 | 48.29% | 39.9717
5012 | 3 | 3 | 3 | 1.8 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5623 | 37.9077 | 0 | 97.5623 | 1085.5963 | 85.11% | 0 | 0 | 30.182 | 48.29% | 37.9077
5013 | 0 | 0 | 0 | 1.6 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6636 | 35.5053 | 0 | 91.6636 | 993.9327 | 77.92% | 0 | 0 | 30.182 | 48.29% | 35.5053
5014 | 0 | 0 | 0 | 2.9 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3352 | 33.3703 | 0 | 86.3352 | 907.5975 | 71.16% | 0 | 0 | 30.182 | 48.29% | 33.3703
5015 | 0 | 0 | 0 | 1.9 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7099 | 31.8913 | 0 | 82.7099 | 824.8876 | 64.67% | 0 | 0 | 30.182 | 48.29% | 31.8913
5016 | 0 | 0 | 0 | 0.8 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.012 | 31.1685 | 0 | 81.012 | 743.8757 | 58.32% | 0 | 0 | 30.182 | 48.29% | 31.1685
5017 | 0 | 0 | 0 | 0.7 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.3012 | 23.6031 | 0 | 63.3012 | 680.5745 | 53.36% | 0 | 0 | 30.182 | 48.29% | 23.6031
5018 | 0 | 0 | 0 | 0.6 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0844 | 31.7325 | 0 | 82.0844 | 598.4901 | 46.92% | 0 | 0 | 30.182 | 48.29% | 31.7325
5019 | 0 | 0 | 0 | 0.4 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7615 | 34.6224 | 0 | 88.7615 | 509.7286 | 39.96% | 0 | 0 | 30.182 | 48.29% | 34.6224
5020 | 0 | 0 | 0 | 0.7 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.34 | 37.5038 | 0 | 95.34 | 414.3886 | 32.49% | 0 | 0 | 30.182 | 48.29% | 37.5038
5021 | 0 | 0 | 0 | 0.8 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5981 | 40.6569 | 0 | 102.5981 | 311.7905 | 24.44% | 0 | 0 | 30.182 | 48.29% | 40.6569
5022 | 135 | 30 | 16 | 1.1 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.1695 | 43.9409 | 0 | 110.1695 | 201.621 | 15.81% | 0 | 0 | 30.182 | 48.29% | 43.9409
5023 | 550 | 190 | 51 | 0.7 | 23.2 | 0 | 0 | 0 | 0 | 2.5761 | 0 | 0 | 2.5761 | 0 | 0 | 0 | 109.7079 | 43.4217 | 0 | 109.7079 | 91.9131 | 7.206% | 0 | 0 | 30.182 | 48.29% | 45.9979
5024 | 729 | 393 | 72 | 0.6 | 26.5 | 0 | 0 | 0 | 0 | 11.608 | 0 | 0 | 11.608 | 0 | 0 | 0 | 91.9131 | 35.5138 | 0 | 91.9131 | 0 | 0% | 0 | 0 | 30.182 | 48.29% | 47.1218
5025 | 812 | 589 | 87 | 1.7 | 28 | 0 | 0 | 0 | 190.9844 | 30.3283 | 0 | 0 | 30.3283 | 0 | 0 | 0 | 0 | 0 | 190.9844 | 0 | 190.9844 | 14.97% | 0 | 18.1709 | 10.0717 | 16.11% | 48.4992
5026 | 869 | 759 | 95 | 2.4 | 29.3 | 0 | 0 | 0 | 0 | 45.8357 | 7.1054e-15 | 0 | 45.8357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.9844 | 14.97% | 0 | 3.4531 | 6.25 | 10% | 49.2888
5027 | 902 | 887 | 98 | 2.6 | 30.6 | 0 | 0 | 0 | 244.318 | 56.7553 | 0 | 8.2491 | 48.5061 | 0 | 0 | 0 | 0 | 0 | 244.318 | 0 | 435.3024 | 34.13% | 8.2491 | 0 | 13.7036 | 21.93% | 48.5061
5028 | 918 | 963 | 100 | 4.8 | 31.2 | 0 | 0 | 0 | 255.1008 | 65.2979 | 0 | 18.0188 | 47.2792 | 0 | 0 | 0 | 0 | 0 | 255.1008 | 0 | 690.4033 | 54.13% | 18.0188 | 0 | 29.9846 | 47.98% | 47.2792
5029 | 908 | 973 | 106 | 5.2 | 32 | 0 | 0 | 0 | 129.7821 | 47.1496 | 20.7205 | 0 | 47.1496 | 0 | 0 | 0 | 0 | 0 | 129.7821 | 0 | 820.1853 | 64.3% | 0 | 0 | 29.9846 | 47.98% | 47.1496
5030 | 899 | 929 | 104 | 5 | 32.7 | 0 | 0 | 0 | 0 | 66.0859 | 0 | 19.0449 | 47.041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820.1853 | 64.3% | 19.0449 | 0 | 47.1928 | 75.51% | 47.041
5031 | 873 | 825 | 100 | 5.1 | 32.8 | 0 | 0 | 0 | 238.5794 | 56.2794 | 3.6868 | 10.0239 | 46.2555 | 0 | 0 | 0 | 0 | 0 | 238.5794 | 0 | 1058.7647 | 83.01% | 10.0239 | 0 | 56.25 | 90% | 46.2555
5032 | 830 | 677 | 94 | 5.6 | 32.7 | 0 | 0 | 0 | 216.7455 | 45.5272 | 4.3103 | 0 | 45.5272 | 0 | 0 | 0 | 0 | 0 | 216.7455 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 45.5272
5033 | 752 | 491 | 85 | 5.7 | 32 | 0 | 0 | 0 | 0 | 32.2827 | 3.4952 | 0 | 32.2827 | 0 | 0 | 0 | 38.2653 | 12.4826 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 44.7654
5034 | 617 | 288 | 69 | 4.7 | 31.1 | 0 | 0 | 0 | 0 | 17.524 | 0 | 0 | 17.524 | 0 | 0 | 0 | 73.3517 | 27.2511 | 0 | 73.3517 | 1163.8932 | 91.25% | 0 | 0 | 56.25 | 90% | 44.7751
5035 | 328 | 96 | 39 | 3.5 | 29.5 | 0 | 0 | 0 | 0 | 2.4743 | 0 | 0 | 2.4743 | 0 | 0 | 0 | 105.5784 | 40.9847 | 0 | 105.5784 | 1058.3148 | 82.97% | 0 | 0 | 56.25 | 90% | 43.459
5036 | 2 | 3 | 3 | 2 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0924 | 40.2809 | 0 | 103.0924 | 955.2224 | 74.89% | 0 | 0 | 56.25 | 90% | 40.2809
5037 | 0 | 0 | 0 | 0.5 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4258 | 38.4091 | 0 | 98.4258 | 856.7966 | 67.17% | 0 | 0 | 56.25 | 90% | 38.4091
5038 | 0 | 0 | 0 | 0.8 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9981 | 36.1265 | 0 | 92.9981 | 763.7985 | 59.88% | 0 | 0 | 56.25 | 90% | 36.1265
5039 | 0 | 0 | 0 | 1.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3747 | 34.6419 | 0 | 89.3747 | 674.4238 | 52.87% | 0 | 0 | 56.25 | 90% | 34.6419
5040 | 0 | 0 | 0 | 1.5 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7418 | 33.9121 | 0 | 87.7418 | 586.6819 | 46% | 0 | 0 | 56.25 | 90% | 33.9121
5041 | 0 | 0 | 0 | 1.6 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6904 | 33.5152 | 0 | 86.6904 | 499.9915 | 39.2% | 0 | 0 | 56.25 | 90% | 33.5152
5042 | 0 | 0 | 0 | 1 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3436 | 33.9483 | 0 | 87.3436 | 412.6479 | 32.35% | 0 | 0 | 56.25 | 90% | 33.9483
5043 | 0 | 0 | 0 | 0.8 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0865 | 36.4997 | 0 | 93.0865 | 319.5615 | 25.05% | 0 | 0 | 56.25 | 90% | 36.4997
5044 | 0 | 0 | 0 | 1.4 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9068 | 39.0233 | 0 | 98.9068 | 220.6546 | 17.3% | 0 | 0 | 56.25 | 90% | 39.0233
5045 | 0 | 0 | 0 | 1.9 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3306 | 41.7349 | 0 | 105.3306 | 115.3241 | 9.041% | 0 | 0 | 56.25 | 90% | 41.7349
5046 | 104 | 28 | 17 | 1.3 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.2156 | 44.5982 | 0 | 112.2156 | 3.1085 | 0.2437% | 0 | 0 | 56.25 | 90% | 44.5982
5047 | 503 | 183 | 56 | 1.4 | 23.9 | 0 | 0 | 0 | 61.8183 | 2.9184 | 0 | 0 | 2.9184 | 0 | 0 | 0 | 0 | 0 | 61.8183 | 0 | 64.9268 | 5.09% | 0 | 20.178 | 33.9183 | 54.27% | 23.0964
5048 | 705 | 388 | 78 | 1.2 | 28 | 0 | 0 | 0 | 114.0214 | 11.7724 | 0 | 0 | 11.7724 | 0 | 0 | 0 | 0 | 0 | 114.0214 | 0 | 178.9482 | 14.03% | 0 | 25 | 6.25 | 10% | 36.7724
5049 | 790 | 583 | 96 | 1.5 | 30.9 | 0 | 0 | 0 | 0 | 29.9589 | 0 | 0 | 29.9589 | 0 | 0 | 0 | 52.547 | 18.5277 | 0 | 52.547 | 126.4012 | 9.91% | 0 | 0 | 6.25 | 10% | 48.4866
5050 | 824 | 749 | 117 | 3.2 | 32.7 | 0 | 0 | 0 | 1.7906e-12 | 36.5795 | 8.7893 | 0 | 36.5795 | 0 | 0 | 0 | 38.2653 | 12.4531 | 1.7906e-12 | 38.2653 | 88.1359 | 6.91% | 0 | 0 | 6.25 | 10% | 49.0326
5051 | 841 | 875 | 136 | 4.5 | 33.7 | 0 | 0 | 0 | 225.1381 | 48.0995 | 8.7786 | 0 | 48.0995 | 0 | 0 | 0 | 0 | 0 | 225.1381 | 0 | 313.274 | 24.56% | 0 | 0 | 6.25 | 10% | 48.0995
5052 | 866 | 953 | 135 | 4.9 | 34.5 | 0 | 0 | 0 | 239.4993 | 63.7398 | 0 | 16.6779 | 47.0619 | 0 | 0 | 0 | 0 | 0 | 239.4993 | 0 | 552.7733 | 43.34% | 16.6779 | 0 | 21.3195 | 34.11% | 47.0619
5053 | 859 | 964 | 140 | 5.7 | 34.7 | 0 | 0 | 0 | 240.3565 | 51.0849 | 15.4757 | 4.2236 | 46.8614 | 0 | 0 | 0 | 0 | 0 | 240.3565 | 0 | 793.1298 | 62.18% | 4.2236 | 0 | 25.1357 | 40.22% | 46.8614
5054 | 847 | 919 | 139 | 6.3 | 34.6 | 0 | 0 | 0 | 235.0084 | 46.6093 | 18.6209 | 0 | 46.6093 | 0 | 0 | 0 | 0 | 0 | 235.0084 | 0 | 1028.1382 | 80.61% | 0 | 0 | 25.1357 | 40.22% | 46.6093
5055 | 826 | 821 | 133 | 6.2 | 34.2 | 0 | 0 | 0 | 223.6675 | 59.4985 | 0 | 13.7917 | 45.7068 | 0 | 0 | 0 | 0 | 0 | 223.6675 | 0 | 1251.8057 | 98.14% | 13.7917 | 0 | 37.5973 | 60.16% | 45.7068
5056 | 761 | 669 | 133 | 6.7 | 33 | 0 | 0 | 0 | 0 | 49.4759 | 0 | 16.8541 | 32.6219 | 0 | 0 | 0 | 38.2653 | 12.4401 | 0 | 38.2653 | 1213.5404 | 95.14% | 16.8541 | 0 | 52.826 | 84.52% | 45.062
5057 | 667 | 489 | 128 | 6.7 | 31.5 | 0 | 0 | 0 | 0 | 35.585 | 0 | 0 | 35.585 | 0 | 0 | 0 | 38.2653 | 12.5033 | 0 | 38.2653 | 1175.275 | 92.14% | 3.7895 | 0 | 56.25 | 90% | 44.2988
5058 | 502 | 279 | 100 | 6.6 | 30.3 | 0 | 0 | 0 | 100.2352 | 17.1934 | 0 | 0 | 17.1934 | 0 | 0 | 0 | 0 | 0 | 100.2352 | 0 | 1275.5102 | 100% | 0 | 20.178 | 33.9183 | 54.27% | 37.3715
5059 | 217 | 90 | 51 | 6.4 | 28.3 | 0 | 0 | 0 | 0 | 2.9673 | 0 | 0 | 2.9673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 6.25 | 10% | 27.9673
5060 | 1 | 3 | 3 | 4.9 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7652 | 40.1416 | 0 | 102.7652 | 1172.745 | 91.94% | 0 | 0 | 6.25 | 10% | 40.1416
5061 | 0 | 0 | 0 | 5.4 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0503 | 38.2851 | 0 | 98.0503 | 1074.6948 | 84.26% | 0 | 0 | 6.25 | 10% | 38.2851
5062 | 0 | 0 | 0 | 5.4 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.6948 | 84.26% | 0 | 0 | 6.25 | 10% | 0
5063 | 0 | 0 | 0 | 4.8 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.6948 | 84.26% | 0 | 0 | 6.25 | 10% | 0
5064 | 0 | 0 | 0 | 3.3 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.6948 | 84.26% | 0 | 0 | 6.25 | 10% | 0
5065 | 0 | 0 | 0 | 2.3 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.6948 | 84.26% | 0 | 0 | 6.25 | 10% | 0
5066 | 0 | 0 | 0 | 1.7 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.6948 | 84.26% | 0 | 0 | 6.25 | 10% | 0
5067 | 0 | 0 | 0 | 3.2 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.6948 | 84.26% | 0 | 0 | 6.25 | 10% | 0
5068 | 0 | 0 | 0 | 6 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6765 | 38.2294 | 0 | 97.6765 | 977.0182 | 76.6% | 0 | 0 | 6.25 | 10% | 38.2294
5069 | 0 | 0 | 0 | 4.3 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.0948 | 0 | 127.551 | 849.4672 | 66.6% | 10.5187 | 0 | 15.7542 | 25.21% | 40.5761
5070 | 0 | 15 | 15 | 4.9 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.1162 | 0 | 127.551 | 721.9162 | 56.6% | 7.7756 | 0 | 22.7799 | 36.45% | 43.3406
5071 | 0 | 32 | 32 | 4.5 | 23.3 | 0 | 0 | 0 | 0 | 1.5488 | 0 | 0 | 1.5488 | 0 | 0 | 0 | 126.4198 | 50.5772 | 0 | 126.4198 | 595.4963 | 46.69% | 7.0153 | 0 | 29.1187 | 46.59% | 45.1107
5072 | 0 | 55 | 55 | 4.7 | 23.9 | 0 | 0 | 0 | 0 | 3.0701 | 0 | 0 | 3.0701 | 0 | 0 | 0 | 109.0052 | 43.0546 | 0 | 109.0052 | 486.4911 | 38.14% | 0 | 0 | 29.1187 | 46.59% | 46.1246
5073 | 56 | 221 | 180 | 6.3 | 24.4 | 0 | 0 | 0 | 0 | 13.0549 | 0 | 0 | 13.0549 | 0 | 0 | 0 | 88.5272 | 34.248 | 0 | 88.5272 | 397.9639 | 31.2% | 0 | 0 | 29.1187 | 46.59% | 47.3028
5074 | 461 | 628 | 268 | 5.8 | 26.6 | 0 | 0 | 0 | 107.9369 | 40.2882 | 0 | 0 | 40.2882 | 0 | 0 | 0 | 0 | 0 | 107.9369 | 0 | 505.9008 | 39.66% | 0 | 7.7152 | 20.58 | 32.93% | 48.0034
5075 | 320 | 684 | 394 | 7.5 | 27.5 | 0 | 0 | 0 | 70.8967 | 45.982 | 0 | 0 | 45.982 | 0 | 0 | 0 | 0 | 0 | 70.8967 | 0 | 576.7975 | 45.22% | 0 | 1.1663 | 19.2893 | 30.86% | 47.1483
5076 | 114 | 510 | 392 | 7.7 | 28 | 0 | 0 | 0 | 0 | 34.3972 | 0 | 0 | 34.3972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.7975 | 45.22% | 0 | 11.7818 | 6.25 | 10% | 46.1789
5077 | 253 | 696 | 442 | 6.9 | 29.2 | 0 | 0 | 0 | 55.2613 | 48.5278 | 0 | 2.3809 | 46.1469 | 0 | 0 | 0 | 0 | 0 | 55.2613 | 0 | 632.0588 | 49.55% | 2.3809 | 0 | 8.4013 | 13.44% | 46.1469
5078 | 291 | 682 | 401 | 7.9 | 30 | 0 | 0 | 0 | 65.5716 | 47.9804 | 0 | 1.9881 | 45.9923 | 0 | 0 | 0 | 0 | 0 | 65.5716 | 0 | 697.6304 | 54.69% | 1.9881 | 0 | 10.1976 | 16.32% | 45.9923
5079 | 462 | 723 | 337 | 8 | 30.4 | 0 | 0 | 0 | 114.5505 | 52.9173 | 0 | 7.5002 | 45.4171 | 0 | 0 | 0 | 0 | 0 | 114.5505 | 0 | 812.1809 | 63.67% | 7.5002 | 0 | 16.9745 | 27.16% | 45.4171
5080 | 662 | 649 | 180 | 6.6 | 31.2 | 0 | 0 | 0 | 168.1196 | 48.0335 | 0 | 3.3016 | 44.7319 | 0 | 0 | 0 | 0 | 0 | 168.1196 | 0 | 980.3004 | 76.86% | 3.3016 | 0 | 19.9577 | 31.93% | 44.7319
5081 | 564 | 462 | 156 | 7.2 | 30 | 0 | 0 | 0 | 130.54 | 33.6683 | 0 | 0 | 33.6683 | 0 | 0 | 0 | 0 | 0 | 130.54 | 0 | 1110.8404 | 87.09% | 0 | 0 | 19.9577 | 31.93% | 33.6683
5082 | 420 | 266 | 114 | 7.4 | 28.3 | 0 | 0 | 0 | 79.6046 | 16.3274 | 0 | 0 | 16.3274 | 0 | 0 | 0 | 0 | 0 | 79.6046 | 0 | 1190.445 | 93.33% | 0 | 6.1664 | 13.1331 | 21.01% | 22.4938
5083 | 152 | 83 | 55 | 6.9 | 26.4 | 0 | 0 | 0 | 0 | 3.1878 | 0 | 0 | 3.1878 | 0 | 0 | 0 | 101.8131 | 39.7364 | 0 | 101.8131 | 1088.6319 | 85.35% | 0 | 0 | 13.1331 | 21.01% | 42.9242
5084 | 1 | 3 | 3 | 6.9 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4809 | 39.8241 | 0 | 101.4809 | 987.151 | 77.39% | 0 | 0 | 13.1331 | 21.01% | 39.8241
5085 | 0 | 0 | 0 | 6.6 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6914 | 38.2851 | 0 | 97.6914 | 889.4596 | 69.73% | 0 | 0 | 13.1331 | 21.01% | 38.2851
5086 | 0 | 0 | 0 | 5.4 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8844 | 36.2532 | 0 | 92.8844 | 796.5752 | 62.45% | 0 | 0 | 13.1331 | 21.01% | 36.2532
5087 | 0 | 0 | 0 | 3.4 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 796.5752 | 62.45% | 0 | 0 | 13.1331 | 21.01% | 0
5088 | 0 | 0 | 0 | 2.8 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 796.5752 | 62.45% | 0 | 0 | 13.1331 | 21.01% | 0
5089 | 0 | 0 | 0 | 2.4 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 796.5752 | 62.45% | 0 | 0 | 13.1331 | 21.01% | 0
5090 | 0 | 0 | 0 | 2.1 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1861 | 33.9372 | 0 | 87.1861 | 709.389 | 55.62% | 0 | 0 | 13.1331 | 21.01% | 33.9372
5091 | 0 | 0 | 0 | 1.8 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0943 | 36.5095 | 0 | 93.0943 | 616.2948 | 48.32% | 0 | 0 | 13.1331 | 21.01% | 36.5095
5092 | 0 | 0 | 0 | 1.3 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0379 | 39.0999 | 0 | 99.0379 | 517.2569 | 40.55% | 0 | 0 | 13.1331 | 21.01% | 39.0999
5093 | 0 | 0 | 0 | 1.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4238 | 0 | 127.551 | 389.7059 | 30.55% | 9.1276 | 0 | 21.3805 | 34.21% | 42.2961
5094 | 3 | 17 | 17 | 1.2 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1773 | 45.6419 | 0 | 114.1773 | 275.5286 | 21.6% | 0.29722 | 0 | 21.6491 | 34.64% | 45.3447
5095 | 56 | 105 | 90 | 1.1 | 21.3 | 0 | 0 | 0 | 0 | 4.0673 | 0 | 0 | 4.0673 | 0 | 0 | 0 | 108.0025 | 42.8539 | 0 | 108.0025 | 167.5261 | 13.13% | 0 | 0 | 21.6491 | 34.64% | 46.9212
5096 | 55 | 198 | 170 | 1 | 23.6 | 0 | 0 | 0 | 0 | 10.5733 | 0 | 0 | 10.5733 | 0 | 0 | 0 | 96.1064 | 37.5567 | 0 | 96.1064 | 71.4196 | 5.599% | 0 | 0 | 21.6491 | 34.64% | 48.1301
5097 | 153 | 385 | 283 | 2.1 | 25.1 | 0 | 0 | 0 | 0 | 22.7106 | 0 | 0 | 22.7106 | 0 | 0 | 0 | 71.4196 | 26.8874 | 0 | 71.4196 | 0 | 0% | 0 | 0 | 21.6491 | 34.64% | 49.598
5098 | 377 | 572 | 274 | 4.4 | 27.3 | 0 | 0 | 0 | 81.2752 | 36.086 | 0 | 0 | 36.086 | 0 | 0 | 0 | 0 | 0 | 81.2752 | 0 | 81.2752 | 6.372% | 0 | 13.914 | 6.25 | 10% | 50
5099 | 695 | 847 | 234 | 2.6 | 29.2 | 0 | 0 | 0 | 184.1581 | 55.4674 | 0 | 5.9891 | 49.4782 | 0 | 0 | 0 | 0 | 0 | 184.1581 | 0 | 265.4333 | 20.81% | 5.9891 | 0 | 11.6616 | 18.66% | 49.4782
5100 | 680 | 908 | 263 | 1.8 | 30.7 | 0 | 0 | 0 | 185.9371 | 60.2188 | 0 | 11.6862 | 48.5326 | 0 | 0 | 0 | 0 | 0 | 185.9371 | 0 | 451.3703 | 35.39% | 11.6862 | 0 | 22.2207 | 35.55% | 48.5326
5101 | 709 | 930 | 248 | 2.8 | 32 | 0 | 0 | 0 | 197.1435 | 64.0599 | 0 | 15.8435 | 48.2164 | 0 | 0 | 0 | 0 | 0 | 197.1435 | 0 | 648.5139 | 50.84% | 15.8435 | 0 | 36.5362 | 58.46% | 48.2164
5102 | 671 | 882 | 262 | 3.5 | 32.6 | 0 | 0 | 0 | 184.2961 | 61.396 | 0.96691 | 13.27 | 48.1259 | 0 | 0 | 0 | 0 | 0 | 184.2961 | 0 | 832.81 | 65.29% | 13.27 | 0 | 48.5265 | 77.64% | 48.1259
5103 | 643 | 782 | 244 | 3.4 | 33.6 | 0 | 0 | 0 | 172.1115 | 55.8916 | 0 | 8.4119 | 47.4797 | 0 | 0 | 0 | 0 | 0 | 172.1115 | 0 | 1004.9215 | 78.79% | 8.4119 | 0 | 56.1272 | 89.8% | 47.4797
5104 | 583 | 634 | 224 | 5.8 | 31.6 | 0 | 0 | 0 | 146.2008 | 46.6644 | 0 | 0.1359 | 46.5285 | 0 | 0 | 0 | 0 | 0 | 146.2008 | 0 | 1151.1223 | 90.25% | 0.1359 | 0 | 56.25 | 90% | 46.5285
5105 | 535 | 456 | 167 | 5.2 | 30.3 | 0 | 0 | 0 | 124.3879 | 32.7943 | 0 | 0 | 32.7943 | 0 | 0 | 0 | 0 | 0 | 124.3879 | 0 | 1275.5102 | 100% | 0 | 7.8752 | 47.5343 | 76.05% | 40.6695
5106 | 386 | 258 | 120 | 4.4 | 29.1 | 0 | 0 | 0 | 0 | 15.8878 | 0 | 0 | 15.8878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 19.8659 | 31.79% | 40.8878
5107 | 134 | 78 | 53 | 3.6 | 26.7 | 0 | 0 | 0 | 0 | 3.0238 | 0 | 0 | 3.0238 | 0 | 0 | 0 | 105.1399 | 41.1204 | 0 | 105.1399 | 1170.3703 | 91.76% | 0 | 0 | 19.8659 | 31.79% | 44.1442
5108 | 1 | 3 | 3 | 3.9 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7551 | 41.207 | 0 | 104.7551 | 1065.6152 | 83.54% | 0 | 0 | 19.8659 | 31.79% | 41.207
5109 | 0 | 0 | 0 | 2.9 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4814 | 38.6403 | 0 | 98.4814 | 967.1338 | 75.82% | 0 | 0 | 19.8659 | 31.79% | 38.6403
5110 | 0 | 0 | 0 | 1.7 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1817 | 36.3883 | 0 | 93.1817 | 873.9522 | 68.52% | 0 | 0 | 19.8659 | 31.79% | 36.3883
5111 | 0 | 0 | 0 | 0.6 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3479 | 34.77 | 0 | 89.3479 | 784.6042 | 61.51% | 0 | 0 | 19.8659 | 31.79% | 34.77
5112 | 0 | 0 | 0 | 1.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4009 | 33.9399 | 0 | 87.4009 | 697.2033 | 54.66% | 0 | 0 | 19.8659 | 31.79% | 33.9399
5113 | 0 | 0 | 0 | 1 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3683 | 33.5026 | 0 | 86.3683 | 610.835 | 47.89% | 0 | 0 | 19.8659 | 31.79% | 33.5026
5114 | 0 | 0 | 0 | 1.3 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3231 | 33.933 | 0 | 87.3231 | 523.5119 | 41.04% | 0 | 0 | 19.8659 | 31.79% | 33.933
5115 | 0 | 0 | 0 | 1.1 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.9649 | 47.5637 | 0 | 118.9649 | 404.547 | 31.72% | 11.376 | 0 | 30.1448 | 48.23% | 36.1878
5116 | 0 | 0 | 0 | 0.6 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3069 | 0 | 127.551 | 276.996 | 21.72% | 12.8476 | 0 | 41.7534 | 66.81% | 38.4592
5117 | 0 | 0 | 0 | 1.7 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2687 | 0 | 127.551 | 149.445 | 11.72% | 9.5129 | 0 | 50.3489 | 80.56% | 41.7557
5118 | 33 | 22 | 18 | 1.8 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2879 | 0 | 127.551 | 21.894 | 1.716% | 6.5309 | 0 | 56.25 | 90% | 44.757
5119 | 331 | 162 | 78 | 0.8 | 23 | 0 | 0 | 0 | 2.8299 | 3.8705 | 0 | 0 | 3.8705 | 0 | 0 | 0 | 0 | 0 | 2.8299 | 0 | 24.7238 | 1.938% | 0 | 20.178 | 33.9183 | 54.27% | 24.0485
5120 | 559 | 363 | 117 | 1.3 | 26.2 | 0 | 0 | 0 | 102.8763 | 12.7775 | 0 | 0 | 12.7775 | 0 | 0 | 0 | 0 | 0 | 102.8763 | 0 | 127.6001 | 10% | 0 | 25 | 6.25 | 10% | 37.7775
5121 | 666 | 555 | 146 | 2.5 | 28.9 | 0 | 0 | 0 | 0 | 30.1573 | 0 | 0 | 30.1573 | 0 | 0 | 0 | 54.8708 | 19.6232 | 0 | 54.8708 | 72.7293 | 5.702% | 0 | 0 | 6.25 | 10% | 49.7804
5122 | 723 | 720 | 170 | 3 | 30.1 | 0 | 0 | 0 | 0 | 45.0012 | 0 | 7.5601 | 37.4411 | 0 | 0 | 0 | 38.2653 | 12.5589 | 0 | 38.2653 | 34.464 | 2.702% | 7.5601 | 0 | 13.081 | 20.93% | 50
5123 | 764 | 850 | 181 | 5 | 30.6 | 0 | 0 | 0 | 202.4294 | 49.5047 | 7.4331 | 0 | 49.5047 | 0 | 0 | 0 | 0 | 0 | 202.4294 | 0 | 236.8934 | 18.57% | 0 | 0 | 13.081 | 20.93% | 49.5047
5124 | 758 | 921 | 205 | 5.5 | 31.2 | 0 | 0 | 0 | 206.6304 | 61.906 | 2.074 | 13.6143 | 48.2917 | 0 | 0 | 0 | 0 | 0 | 206.6304 | 0 | 443.5238 | 34.77% | 13.6143 | 0 | 25.3824 | 40.61% | 48.2917
5125 | 713 | 928 | 243 | 5.6 | 31.3 | 0 | 0 | 0 | 196.1336 | 66.0984 | 0 | 18.2775 | 47.8209 | 0 | 0 | 0 | 0 | 0 | 196.1336 | 0 | 639.6574 | 50.15% | 18.2775 | 0 | 41.8971 | 67.04% | 47.8209
5126 | 686 | 883 | 249 | 4.5 | 32 | 0 | 0 | 0 | 187.9836 | 63.3506 | 0 | 15.8779 | 47.4727 | 0 | 0 | 0 | 0 | 0 | 187.9836 | 0 | 827.6411 | 64.89% | 15.8779 | 0 | 56.2438 | 89.99% | 47.4727
5127 | 626 | 775 | 253 | 3 | 33 | 0 | 0 | 0 | 167.3147 | 46.9491 | 8.4677 | 0 | 46.9491 | 0 | 0 | 0 | 0 | 0 | 167.3147 | 0 | 994.9558 | 78% | 0 | 0 | 56.2438 | 89.99% | 46.9491
5128 | 616 | 633 | 202 | 3.6 | 33.9 | 0 | 0 | 0 | 157.5116 | 46.0312 | 0 | 0.0069029 | 46.0243 | 0 | 0 | 0 | 0 | 0 | 157.5116 | 0 | 1152.4674 | 90.35% | 0.0069029 | 0 | 56.25 | 90% | 46.0243
5129 | 528 | 448 | 165 | 4.6 | 33.3 | 0 | 0 | 0 | 123.0428 | 32.009 | 0 | 0 | 32.009 | 0 | 0 | 0 | 0 | 0 | 123.0428 | 0 | 1275.5102 | 100% | 0 | 13.0098 | 41.8516 | 66.96% | 45.0188
5130 | 364 | 250 | 122 | 3.7 | 32.4 | 0 | 0 | 0 | 0 | 15.3514 | 0 | 0 | 15.3514 | 0 | 0 | 0 | 78.958 | 29.478 | 0 | 78.958 | 1196.5522 | 93.81% | 0 | 0 | 41.8516 | 66.96% | 44.8294
5131 | 134 | 78 | 53 | 3.3 | 29.7 | 0 | 0 | 0 | 0 | 2.9825 | 0 | 0 | 2.9825 | 0 | 0 | 0 | 104.2764 | 40.4111 | 0 | 104.2764 | 1092.2758 | 85.63% | 0 | 0 | 41.8516 | 66.96% | 43.3935
5132 | 1 | 2 | 2 | 3.3 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.5969 | 40.5469 | 0 | 103.5969 | 988.6789 | 77.51% | 0 | 0 | 41.8516 | 66.96% | 40.5469
5133 | 0 | 0 | 0 | 2.3 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1107 | 38.32 | 0 | 98.1107 | 890.5681 | 69.82% | 0 | 0 | 41.8516 | 66.96% | 38.32
5134 | 0 | 0 | 0 | 1.2 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7448 | 36.0763 | 0 | 92.7448 | 797.8234 | 62.55% | 0 | 0 | 41.8516 | 66.96% | 36.0763
5135 | 0 | 0 | 0 | 0.7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4312 | 34.238 | 0 | 88.4312 | 709.3922 | 55.62% | 0 | 0 | 41.8516 | 66.96% | 34.238
5136 | 0 | 0 | 0 | 1 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6348 | 33.0918 | 0 | 85.6348 | 623.7574 | 48.9% | 0 | 0 | 41.8516 | 66.96% | 33.0918
5137 | 0 | 0 | 0 | 0.7 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9306 | 32.3954 | 0 | 83.9306 | 539.8268 | 42.32% | 0 | 0 | 41.8516 | 66.96% | 32.3954
5138 | 0 | 0 | 0 | 1.3 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0917 | 32.0487 | 0 | 83.0917 | 456.7352 | 35.81% | 0 | 0 | 41.8516 | 66.96% | 32.0487
5139 | 0 | 0 | 0 | 0.7 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8871 | 32.3968 | 0 | 83.8871 | 372.848 | 29.23% | 0 | 0 | 41.8516 | 66.96% | 32.3968
5140 | 0 | 0 | 0 | 1.4 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2882 | 32.6336 | 0 | 84.2882 | 288.5599 | 22.62% | 0 | 0 | 41.8516 | 66.96% | 32.6336
5141 | 0 | 0 | 0 | 0.9 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8515 | 34.6168 | 0 | 88.8515 | 199.7084 | 15.66% | 0 | 0 | 41.8516 | 66.96% | 34.6168
5142 | 23 | 22 | 19 | 0.8 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.0085 | 42.4577 | 0 | 107.0085 | 92.6999 | 7.268% | 4.8229 | 0 | 46.2094 | 73.94% | 37.6348
5143 | 287 | 160 | 86 | 0.9 | 23.4 | 0 | 0 | 0 | 0 | 4.0273 | 0 | 0 | 4.0273 | 0 | 0 | 0 | 92.6999 | 36.113 | 0 | 92.6999 | 0 | 0% | 0 | 0 | 46.2094 | 73.94% | 40.1402
5144 | 509 | 361 | 136 | 3.2 | 25.3 | 0 | 0 | 0 | 0 | 13.6153 | 0 | 0 | 13.6153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 18.5411 | 29.67% | 38.6153
5145 | 591 | 557 | 192 | 4.2 | 26.4 | 0 | 0 | 0 | 0 | 31.2177 | 0 | 0 | 31.2177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.5744 | 14.5852 | 23.34% | 34.7921
5146 | 262 | 565 | 362 | 3.3 | 27.5 | 0 | 0 | 0 | 0 | 35.9026 | 0 | 0 | 35.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 7.5314 | 6.25 | 10% | 43.4339
5147 | 611 | 809 | 267 | 2 | 29.3 | 0 | 0 | 0 | 126.7133 | 52.678 | 0 | 9.1354 | 43.5426 | 0 | 0 | 0 | 0 | 0 | 126.7133 | 0 | 126.7133 | 9.934% | 9.1354 | 0 | 14.5044 | 23.21% | 43.5426
5148 | 727 | 913 | 227 | 1.5 | 31.6 | 0 | 0 | 0 | 200.2204 | 42.6359 | 17.7096 | 0 | 42.6359 | 0 | 0 | 0 | 0 | 0 | 200.2204 | 0 | 326.9337 | 25.63% | 0 | 0 | 14.5044 | 23.21% | 42.6359
5149 | 688 | 918 | 258 | 2.9 | 33.2 | 0 | 0 | 0 | 190.7208 | 63.389 | 0 | 21.5581 | 41.8309 | 0 | 0 | 0 | 0 | 0 | 190.7208 | 0 | 517.6545 | 40.58% | 21.5581 | 0 | 33.9834 | 54.37% | 41.8309
5150 | 665 | 869 | 256 | 3.7 | 33.4 | 0 | 0 | 0 | 182.3265 | 59.5018 | 2.2826 | 18.1429 | 41.3588 | 0 | 0 | 0 | 0 | 0 | 182.3265 | 0 | 699.9809 | 54.88% | 18.1429 | 0 | 50.3766 | 80.6% | 41.3588
5151 | 664 | 776 | 225 | 4.6 | 32.8 | 0 | 0 | 0 | 177.2672 | 40.9981 | 15.8585 | 0 | 40.9981 | 0 | 0 | 0 | 0 | 0 | 177.2672 | 0 | 877.2481 | 68.78% | 0 | 0 | 50.3766 | 80.6% | 40.9981
5152 | 653 | 637 | 182 | 4.7 | 32 | 0 | 0 | 0 | 167.218 | 47.3479 | 0 | 6.5002 | 40.8477 | 0 | 0 | 0 | 0 | 0 | 167.218 | 0 | 1044.4661 | 81.89% | 6.5002 | 0 | 56.25 | 90% | 40.8477
5153 | 528 | 447 | 165 | 2.3 | 31.7 | 0 | 0 | 0 | 124.5341 | 31.8016 | 0 | 0 | 31.8016 | 0 | 0 | 0 | 0 | 0 | 124.5341 | 0 | 1169.0002 | 91.65% | 0 | 8.8219 | 46.4865 | 74.38% | 40.6235
5154 | 361 | 246 | 119 | 2.7 | 30.5 | 0 | 0 | 0 | 0 | 15.1752 | 0 | 0 | 15.1752 | 0 | 0 | 0 | 62.4185 | 22.7037 | 0 | 62.4185 | 1106.5818 | 86.76% | 0 | 3.6651 | 42.4302 | 67.89% | 41.5441
5155 | 105 | 72 | 52 | 2.7 | 28.5 | 0 | 0 | 0 | 0 | 2.8788 | 0 | 0 | 2.8788 | 0 | 0 | 0 | 97.9122 | 37.8603 | 0 | 97.9122 | 1008.6696 | 79.08% | 0 | 0 | 42.4302 | 67.89% | 40.7391
5156 | 0 | 2 | 2 | 3 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2992 | 38.2893 | 0 | 98.2992 | 910.3704 | 71.37% | 0 | 0 | 42.4302 | 67.89% | 38.2893
5157 | 0 | 0 | 0 | 2.5 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8413 | 36.0763 | 0 | 92.8413 | 817.5291 | 64.09% | 0 | 0 | 42.4302 | 67.89% | 36.0763
5158 | 0 | 0 | 0 | 2.1 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.911 | 34.0305 | 0 | 87.911 | 729.6181 | 57.2% | 0 | 0 | 42.4302 | 67.89% | 34.0305
5159 | 0 | 0 | 0 | 2.3 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7962 | 32.3105 | 0 | 83.7962 | 645.8218 | 50.63% | 0 | 0 | 42.4302 | 67.89% | 32.3105
5160 | 0 | 0 | 0 | 2.3 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3734 | 31.2715 | 0 | 81.3734 | 564.4485 | 44.25% | 0 | 0 | 42.4302 | 67.89% | 31.2715
5161 | 0 | 0 | 0 | 2.5 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5527 | 30.4777 | 0 | 79.5527 | 484.8958 | 38.02% | 0 | 0 | 42.4302 | 67.89% | 30.4777
5162 | 0 | 0 | 0 | 1.5 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9972 | 30.2591 | 0 | 78.9972 | 405.8985 | 31.82% | 0 | 0 | 42.4302 | 67.89% | 30.2591
5163 | 0 | 0 | 0 | 1.1 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1817 | 30.351 | 0 | 79.1817 | 326.7169 | 25.61% | 0 | 0 | 42.4302 | 67.89% | 30.351
5164 | 0 | 0 | 0 | 1.3 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9323 | 29.8273 | 0 | 77.9323 | 248.7846 | 19.5% | 0 | 0 | 42.4302 | 67.89% | 29.8273
5165 | 0 | 0 | 0 | 1.2 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8457 | 31.0585 | 0 | 80.8457 | 167.9389 | 13.17% | 0 | 0 | 42.4302 | 67.89% | 31.0585
5166 | 12 | 19 | 17 | 1.2 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0952 | 33.3104 | 0 | 86.0952 | 81.8437 | 6.417% | 0 | 0 | 42.4302 | 67.89% | 33.3104
5167 | 218 | 147 | 90 | 1.2 | 24.1 | 0 | 0 | 0 | 0 | 4.1611 | 0 | 0 | 4.1611 | 0 | 0 | 0 | 81.8437 | 31.4111 | 0 | 81.8437 | 0 | 0% | 0 | 0 | 42.4302 | 67.89% | 35.5722
5168 | 439 | 343 | 148 | 1.3 | 25.6 | 0 | 0 | 0 | 76.6075 | 13.5304 | 0 | 0 | 13.5304 | 0 | 0 | 0 | 0 | 0 | 76.6075 | 0 | 76.6075 | 6.006% | 0 | 23.713 | 16.1862 | 25.9% | 37.2434
5169 | 559 | 537 | 191 | 1.2 | 27.3 | 0 | 0 | 0 | 125.6805 | 29.4952 | 0 | 0 | 29.4952 | 0 | 0 | 0 | 0 | 0 | 125.6805 | 0 | 202.288 | 15.86% | 0 | 8.9779 | 6.25 | 10% | 38.4732
5170 | 629 | 701 | 220 | 1.2 | 29.7 | 0 | 0 | 0 | 157.8566 | 39.6444 | 3.4972 | 0 | 39.6444 | 0 | 0 | 0 | 0 | 0 | 157.8566 | 0 | 360.1447 | 28.24% | 0 | 0 | 6.25 | 10% | 39.6444
5171 | 678 | 828 | 233 | 2.2 | 32.2 | 0 | 0 | 0 | 179.4974 | 40.4132 | 13.4654 | 0 | 40.4132 | 0 | 0 | 0 | 0 | 0 | 179.4974 | 0 | 539.6421 | 42.31% | 0 | 0 | 6.25 | 10% | 40.4132
5172 | 691 | 899 | 248 | 2.7 | 33.9 | 0 | 0 | 0 | 188.9445 | 42.2853 | 18.2346 | 2.5587 | 39.7266 | 0 | 0 | 0 | 0 | 0 | 188.9445 | 0 | 728.5866 | 57.12% | 2.5587 | 0 | 8.5619 | 13.7% | 39.7266
5173 | 672 | 908 | 265 | 3 | 34.6 | 0 | 0 | 0 | 185.8153 | 62.6947 | 0 | 23.7285 | 38.9662 | 0 | 0 | 0 | 0 | 0 | 185.8153 | 0 | 914.4019 | 71.69% | 23.7285 | 0 | 30.002 | 48% | 38.9662
5174 | 645 | 862 | 268 | 4.6 | 34.1 | 0 | 0 | 0 | 0 | 61.7328 | 0 | 23.0605 | 38.6723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.4019 | 71.69% | 23.0605 | 0 | 50.8386 | 81.34% | 38.6723
5175 | 601 | 760 | 260 | 5.1 | 33.1 | 0 | 0 | 0 | 158.169 | 38.3506 | 17.2074 | 0 | 38.3506 | 0 | 0 | 0 | 0 | 0 | 158.169 | 0 | 1072.5709 | 84.09% | 0 | 0 | 50.8386 | 81.34% | 38.3506
5176 | 543 | 613 | 233 | 4.2 | 33.3 | 0 | 0 | 0 | 103.5321 | 44.5012 | 0 | 5.989 | 38.5122 | 0 | 0 | 0 | 0 | 0 | 103.5321 | 0 | 1176.103 | 92.21% | 5.989 | 0 | 56.25 | 90% | 38.5122
5177 | 439 | 431 | 195 | 4 | 32.9 | 0 | 0 | 0 | 99.4072 | 30.5334 | 0 | 0 | 30.5334 | 0 | 0 | 0 | 0 | 0 | 99.4072 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 30.5334
5178 | 304 | 240 | 133 | 4 | 32.5 | 0 | 0 | 0 | 0 | 14.6266 | 0 | 0 | 14.6266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 39.6266
5179 | 108 | 72 | 52 | 3.7 | 31 | 0 | 0 | 0 | 0 | 2.8542 | 0 | 0 | 2.8542 | 0 | 0 | 0 | 64.581 | 23.5761 | 0 | 64.581 | 1210.9292 | 94.94% | 0 | 14.533 | 12.4975 | 20% | 40.9633
5180 | 1 | 2 | 2 | 2.4 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7717 | 38.6472 | 0 | 99.7717 | 1111.1575 | 87.11% | 0 | 0 | 12.4975 | 20% | 38.6472
5181 | 0 | 0 | 0 | 2 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3094 | 36.1265 | 0 | 93.3094 | 1017.8481 | 79.8% | 0 | 0 | 12.4975 | 20% | 36.1265
5182 | 0 | 0 | 0 | 2.4 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9062 | 33.8856 | 0 | 87.9062 | 929.9419 | 72.91% | 0 | 0 | 12.4975 | 20% | 33.8856
5183 | 0 | 0 | 0 | 1.2 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1323 | 32.3383 | 0 | 84.1323 | 845.8096 | 66.31% | 0 | 0 | 12.4975 | 20% | 32.3383
5184 | 0 | 0 | 0 | 1.2 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5558 | 14.1596 | 0 | 41.5558 | 804.2538 | 63.05% | 0 | 0 | 12.4975 | 20% | 14.1596
5185 | 0 | 0 | 0 | 0.7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5858 | 31.3078 | 0 | 81.5858 | 722.6679 | 56.66% | 0 | 0 | 12.4975 | 20% | 31.3078
5186 | 0 | 0 | 0 | 1.1 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.464 | 31.7256 | 0 | 82.464 | 640.2039 | 50.19% | 0 | 0 | 12.4975 | 20% | 31.7256
5187 | 0 | 0 | 0 | 1.1 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4698 | 34.3146 | 0 | 88.4698 | 551.7341 | 43.26% | 0 | 0 | 12.4975 | 20% | 34.3146
5188 | 0 | 0 | 0 | 1.3 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9243 | 36.7072 | 0 | 93.9243 | 457.8098 | 35.89% | 0 | 0 | 12.4975 | 20% | 36.7072
5189 | 0 | 0 | 0 | 0.9 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8304 | 40.0859 | 0 | 101.8304 | 355.9794 | 27.91% | 0 | 0 | 12.4975 | 20% | 40.0859
5190 | 14 | 18 | 16 | 1.2 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5404 | 43.491 | 0 | 109.5404 | 246.439 | 19.32% | 0 | 0 | 12.4975 | 20% | 43.491
5191 | 255 | 150 | 86 | 0.7 | 23.6 | 0 | 0 | 0 | 0 | 3.9822 | 0 | 0 | 3.9822 | 0 | 0 | 0 | 105.4605 | 41.5644 | 0 | 105.4605 | 140.9785 | 11.05% | 0 | 0 | 12.4975 | 20% | 45.5467
5192 | 472 | 345 | 139 | 1.3 | 26.5 | 0 | 0 | 0 | 0 | 13.3271 | 0 | 0 | 13.3271 | 0 | 0 | 0 | 88.0854 | 33.8852 | 0 | 88.0854 | 52.8931 | 4.147% | 0 | 0 | 12.4975 | 20% | 47.2123
5193 | 606 | 543 | 172 | 2.8 | 29.3 | 0 | 0 | 0 | 0 | 30.0098 | 0 | 0 | 30.0098 | 0 | 0 | 0 | 52.8931 | 18.7652 | 0 | 52.8931 | 0 | 0% | 0 | 0 | 12.4975 | 20% | 48.7749
5194 | 668 | 707 | 199 | 2.8 | 31.5 | 0 | 0 | 0 | 63.8609 | 44.336 | 0 | 0 | 44.336 | 0 | 0 | 0 | 0 | 0 | 63.8609 | 0 | 63.8609 | 5.007% | 0 | 5.645 | 6.25 | 10% | 49.981
5195 | 694 | 831 | 224 | 2.8 | 32.9 | 0 | 0 | 0 | 183.9048 | 54.591 | 0 | 4.7228 | 49.8682 | 0 | 0 | 0 | 0 | 0 | 183.9048 | 0 | 247.7657 | 19.42% | 4.7228 | 0 | 10.5173 | 16.83% | 49.8682
5196 | 684 | 897 | 253 | 3.5 | 33.9 | 0 | 0 | 0 | 186.4234 | 61.1408 | 0 | 12.2392 | 48.9017 | 0 | 0 | 0 | 0 | 0 | 186.4234 | 0 | 434.189 | 34.04% | 12.2392 | 0 | 21.5762 | 34.52% | 48.9017
5197 | 658 | 905 | 275 | 4.4 | 34.8 | 0 | 0 | 0 | 180.5057 | 63.4708 | 0 | 14.8546 | 48.6161 | 0 | 0 | 0 | 0 | 0 | 180.5057 | 0 | 614.6948 | 48.19% | 14.8546 | 0 | 34.9982 | 56% | 48.6161
5198 | 650 | 862 | 265 | 4.1 | 35 | 0 | 0 | 0 | 177.4927 | 61.4748 | 0 | 13.0634 | 48.4114 | 0 | 0 | 0 | 0 | 0 | 177.4927 | 0 | 792.1875 | 62.11% | 13.0634 | 0 | 46.8018 | 74.88% | 48.4114
5199 | 622 | 758 | 241 | 5.7 | 34.7 | 0 | 0 | 0 | 163.9574 | 55.5794 | 0 | 7.8198 | 47.7596 | 0 | 0 | 0 | 0 | 0 | 163.9574 | 0 | 956.1449 | 74.96% | 7.8198 | 0 | 53.8674 | 86.19% | 47.7596
5200 | 567 | 617 | 221 | 4.6 | 34.7 | 0 | 0 | 0 | 142.7793 | 45.1322 | 0 | 0 | 45.1322 | 0 | 0 | 0 | 0 | 0 | 142.7793 | 0 | 1098.9242 | 86.16% | 0 | 1.6164 | 52.0785 | 83.33% | 46.7485
5201 | 496 | 441 | 178 | 4.9 | 34.8 | 0 | 0 | 0 | 114.2073 | 31.5987 | 0 | 0 | 31.5987 | 0 | 0 | 0 | 0 | 0 | 114.2073 | 0 | 1213.1314 | 95.11% | 0 | 0 | 52.0785 | 83.33% | 31.5987
5202 | 336 | 242 | 126 | 3.8 | 34 | 0 | 0 | 0 | 62.3788 | 14.9893 | 1.7764e-15 | 0 | 14.9893 | 0 | 0 | 0 | 0 | 0 | 62.3788 | 0 | 1275.5102 | 100% | 0 | 25 | 24.4102 | 39.06% | 39.9894
5203 | 108 | 71 | 52 | 3.8 | 30.9 | 0 | 0 | 0 | 0 | 2.8548 | 0 | 0 | 2.8548 | 0 | 0 | 0 | 108.6899 | 42.1153 | 0 | 108.6899 | 1166.8203 | 91.48% | 0 | 0 | 24.4102 | 39.06% | 44.9701
5204 | 0 | 2 | 2 | 2.4 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9 | 41.6875 | 0 | 106.9 | 1059.9202 | 83.1% | 0 | 0 | 24.4102 | 39.06% | 41.6875
5205 | 0 | 0 | 0 | 2.4 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 50.6905 | 0 | 127.551 | 932.3692 | 73.1% | 11.7995 | 0 | 35.0717 | 56.11% | 38.891
5206 | 0 | 0 | 0 | 2.1 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2606 | 36.3215 | 0 | 93.2606 | 839.1087 | 65.79% | 0 | 0 | 35.0717 | 56.11% | 36.3215
5207 | 0 | 0 | 0 | 0.3 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3847 | 34.7143 | 0 | 89.3847 | 749.724 | 58.78% | 0 | 0 | 35.0717 | 56.11% | 34.7143
5208 | 0 | 0 | 0 | 0.8 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1285 | 33.7394 | 0 | 87.1285 | 662.5955 | 51.95% | 0 | 0 | 35.0717 | 56.11% | 33.7394
5209 | 0 | 0 | 0 | 1.3 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4485 | 43.7671 | 0 | 110.4485 | 552.147 | 43.29% | 10.4274 | 0 | 44.4935 | 71.19% | 33.3397
5210 | 0 | 0 | 0 | 0.9 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1366 | 33.7784 | 0 | 87.1366 | 465.0104 | 36.46% | 0 | 0 | 44.4935 | 71.19% | 33.7784
5211 | 0 | 0 | 0 | 0.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0889 | 35.9552 | 0 | 92.0889 | 372.9215 | 29.24% | 0 | 0 | 44.4935 | 71.19% | 35.9552
5212 | 0 | 0 | 0 | 0.5 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2394 | 0 | 127.551 | 245.3705 | 19.24% | 13.0113 | 0 | 56.25 | 90% | 38.228
5213 | 0 | 0 | 0 | 1.1 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9471 | 41.4577 | 0 | 104.9471 | 140.4233 | 11.01% | 0 | 0 | 56.25 | 90% | 41.4577
5214 | 16 | 19 | 17 | 1.2 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1292 | 44.5787 | 0 | 112.1292 | 28.2942 | 2.218% | 0 | 0 | 56.25 | 90% | 44.5787
5215 | 264 | 150 | 84 | 1 | 23.1 | 0 | 0 | 0 | 0 | 3.891 | 0 | 0 | 3.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.2942 | 2.218% | 0 | 20.178 | 33.9183 | 54.27% | 24.069
5216 | 514 | 351 | 128 | 0.8 | 26.5 | 0 | 0 | 0 | 65.9019 | 13.0968 | 0 | 0 | 13.0968 | 0 | 0 | 0 | 0 | 0 | 65.9019 | 0 | 94.1961 | 7.385% | 0 | 25 | 6.25 | 10% | 38.0968
5217 | 658 | 550 | 151 | 0.8 | 31 | 0 | 0 | 0 | 0 | 29.7358 | 0 | 0 | 29.7358 | 0 | 0 | 0 | 55.9308 | 19.943 | 0 | 55.9308 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 49.6788
5218 | 716 | 715 | 174 | 2.4 | 32.6 | 0 | 0 | 0 | 0 | 37.5427 | 7.0561 | 0 | 37.5427 | 0 | 0 | 0 | 38.2653 | 12.4573 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 50
5219 | 743 | 844 | 199 | 4.8 | 34.7 | 0 | 0 | 0 | 196.7568 | 56.0586 | 0.3768 | 6.0586 | 50 | 0 | 0 | 0 | 0 | 0 | 196.7568 | 0 | 196.7568 | 15.43% | 6.0586 | 0 | 11.7243 | 18.76% | 50
5220 | 758 | 920 | 210 | 4.4 | 36.1 | 0 | 0 | 0 | 207.7773 | 63.0386 | 0 | 13.3933 | 49.6454 | 0 | 0 | 0 | 0 | 0 | 207.7773 | 0 | 404.5341 | 31.72% | 13.3933 | 0 | 23.8259 | 38.12% | 49.6454
5221 | 736 | 928 | 227 | 3.3 | 37.6 | 0 | 0 | 0 | 205.0876 | 64.0231 | 0 | 14.6535 | 49.3696 | 0 | 0 | 0 | 0 | 0 | 205.0876 | 0 | 609.6217 | 47.79% | 14.6535 | 0 | 37.0662 | 59.31% | 49.3696
5222 | 721 | 887 | 229 | 3.3 | 38.5 | 0 | 0 | 0 | 199.672 | 62.3126 | 0 | 13.4096 | 48.903 | 0 | 0 | 0 | 0 | 0 | 199.672 | 0 | 809.2937 | 63.45% | 13.4096 | 0 | 49.1826 | 78.69% | 48.903
5223 | 673 | 782 | 226 | 3.5 | 39.2 | 0 | 0 | 0 | 180.9179 | 55.7819 | 0 | 7.8217 | 47.9602 | 0 | 0 | 0 | 0 | 0 | 180.9179 | 0 | 990.2117 | 77.63% | 7.8217 | 0 | 56.25 | 90% | 47.9602
5224 | 600 | 632 | 216 | 3.8 | 39.4 | 0 | 0 | 0 | 152.8699 | 45.491 | 0 | 0 | 45.491 | 0 | 0 | 0 | 0 | 0 | 152.8699 | 0 | 1143.0815 | 89.62% | 0 | 0 | 56.25 | 90% | 45.491
5225 | 491 | 443 | 185 | 4.2 | 38.7 | 0 | 0 | 0 | 113.422 | 31.3499 | 3.5527e-15 | 0 | 31.3499 | 0 | 0 | 0 | 0 | 0 | 113.422 | 0 | 1256.5036 | 98.51% | 0 | 0 | 56.25 | 90% | 31.3499
5226 | 293 | 236 | 133 | 5.2 | 34 | 0 | 0 | 0 | 19.0066 | 14.3767 | 0 | 0 | 14.3767 | 0 | 0 | 0 | 0 | 0 | 19.0066 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 14.3767
5227 | 66 | 67 | 55 | 4.5 | 30.3 | 0 | 0 | 0 | 0 | 3.0295 | 0 | 0 | 3.0295 | 0 | 0 | 0 | 108.8967 | 42.2818 | 0 | 108.8967 | 1166.6135 | 91.46% | 0 | 0 | 56.25 | 90% | 45.3113
5228 | 0 | 1 | 1 | 4.4 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.1549 | 41.7836 | 0 | 107.1549 | 1059.4586 | 83.06% | 0 | 0 | 56.25 | 90% | 41.7836
5229 | 0 | 0 | 0 | 2.9 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.6963 | 38.9885 | 0 | 99.6963 | 959.7623 | 75.25% | 0 | 0 | 56.25 | 90% | 38.9885
5230 | 0 | 0 | 0 | 2.7 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2523 | 36.2771 | 0 | 93.2523 | 866.5101 | 67.93% | 0 | 0 | 56.25 | 90% | 36.2771
5231 | 0 | 0 | 0 | 1 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866.5101 | 67.93% | 0 | 0 | 56.25 | 90% | 0
5232 | 0 | 0 | 0 | 0.9 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866.5101 | 67.93% | 0 | 0 | 56.25 | 90% | 0
5233 | 0 | 0 | 0 | 0.6 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866.5101 | 67.93% | 0 | 0 | 56.25 | 90% | 0
5234 | 0 | 0 | 0 | 1 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866.5101 | 67.93% | 0 | 0 | 56.25 | 90% | 0
5235 | 0 | 0 | 0 | 1.5 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4276 | 36.3354 | 0 | 93.4276 | 773.0825 | 60.61% | 0 | 0 | 56.25 | 90% | 36.3354
5236 | 0 | 0 | 0 | 1.7 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8208 | 38.7614 | 0 | 98.8208 | 674.2617 | 52.86% | 0 | 0 | 56.25 | 90% | 38.7614
5237 | 0 | 0 | 0 | 1 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6854 | 41.7321 | 0 | 105.6854 | 568.5763 | 44.58% | 0 | 0 | 56.25 | 90% | 41.7321
5238 | 6 | 16 | 16 | 0.9 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.8602 | 44.8113 | 0 | 112.8602 | 455.716 | 35.73% | 0 | 0 | 56.25 | 90% | 44.8113
5239 | 148 | 137 | 99 | 1.7 | 25 | 0 | 0 | 0 | 0 | 4.1202 | 0 | 0 | 4.1202 | 0 | 0 | 0 | 107.6623 | 42.3721 | 0 | 107.6623 | 348.0537 | 27.29% | 0 | 0 | 56.25 | 90% | 46.4923
5240 | 399 | 356 | 183 | 1.5 | 30.2 | 0 | 0 | 0 | 67.6595 | 14.9375 | 0 | 0 | 14.9375 | 0 | 0 | 0 | 0 | 0 | 67.6595 | 0 | 415.7132 | 32.59% | 0 | 18.2266 | 36.078 | 57.72% | 33.1641
5241 | 468 | 510 | 225 | 2.1 | 34.2 | 0 | 0 | 0 | 101.7383 | 28.6013 | 0 | 0 | 28.6013 | 0 | 0 | 0 | 0 | 0 | 101.7383 | 0 | 517.4515 | 40.57% | 0 | 20.7669 | 13.0946 | 20.95% | 49.3682
5242 | 573 | 705 | 270 | 3.1 | 36.3 | 0 | 0 | 0 | 141.5008 | 43.8154 | 0 | 0 | 43.8154 | 0 | 0 | 0 | 0 | 0 | 141.5008 | 0 | 658.9523 | 51.66% | 0 | 6.1845 | 6.25 | 10% | 50
5243 | 608 | 823 | 292 | 3.4 | 38.5 | 0 | 0 | 0 | 158.6845 | 53.4 | 0 | 4.2393 | 49.1607 | 0 | 0 | 0 | 0 | 0 | 158.6845 | 0 | 817.6368 | 64.1% | 4.2393 | 0 | 10.0805 | 16.13% | 49.1607
5244 | 721 | 970 | 293 | 4 | 40.1 | 0 | 0 | 0 | 197.2568 | 64.6152 | 0 | 16.7051 | 47.9101 | 0 | 0 | 0 | 0 | 0 | 197.2568 | 0 | 1014.8936 | 79.57% | 16.7051 | 0 | 25.1746 | 40.28% | 47.9101
5245 | 301 | 817 | 521 | 4 | 40.1 | 0 | 0 | 0 | 72.4308 | 54.3325 | 0 | 6.7553 | 47.5772 | 0 | 0 | 0 | 0 | 0 | 72.4308 | 0 | 1087.3245 | 85.25% | 6.7553 | 0 | 31.2784 | 50.05% | 47.5772
5246 | 126 | 569 | 447 | 3.6 | 39 | 0 | 0 | 0 | 0 | 37.5792 | 0 | 0 | 37.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1087.3245 | 85.25% | 0 | 9.5691 | 20.688 | 33.1% | 47.1483
5247 | 282 | 630 | 396 | 5.8 | 37.4 | 0 | 0 | 0 | 63.2739 | 44.1007 | 0 | 0 | 44.1007 | 0 | 0 | 0 | 0 | 0 | 63.2739 | 0 | 1150.5983 | 90.21% | 0 | 2.2788 | 18.166 | 29.07% | 46.3795
5248 | 266 | 547 | 355 | 5.6 | 37.4 | 0 | 0 | 0 | 55.7349 | 37.4756 | 0 | 0 | 37.4756 | 0 | 0 | 0 | 0 | 0 | 55.7349 | 0 | 1206.3333 | 94.58% | 0 | 8.1978 | 9.0933 | 14.55% | 45.6734
5249 | 36 | 257 | 235 | 5.9 | 36 | 0 | 0 | 0 | 0 | 15.9316 | 0 | 0 | 15.9316 | 0 | 0 | 0 | 79.1304 | 29.1638 | 0 | 79.1304 | 1127.2029 | 88.37% | 0 | 0 | 9.0933 | 14.55% | 45.0954
5250 | 1 | 105 | 105 | 4 | 34.8 | 0 | 0 | 0 | 0 | 6.0306 | 0 | 0 | 6.0306 | 0 | 0 | 0 | 104.7659 | 39.9241 | 0 | 104.7659 | 1022.4369 | 80.16% | 0 | 0 | 9.0933 | 14.55% | 45.9547
5251 | 0 | 28 | 28 | 2.9 | 33.5 | 0 | 0 | 0 | 0 | 1.2692 | 0 | 0 | 1.2692 | 0 | 0 | 0 | 112.1917 | 43.2065 | 0 | 112.1917 | 910.2452 | 71.36% | 0 | 0 | 9.0933 | 14.55% | 44.4757
5252 | 0 | 0 | 0 | 1.2 | 31.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.252 | 41.4173 | 0 | 107.252 | 802.9932 | 62.95% | 0 | 0 | 9.0933 | 14.55% | 41.4173
5253 | 0 | 0 | 0 | 1 | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4056 | 38.767 | 0 | 100.4056 | 702.5876 | 55.08% | 0 | 0 | 9.0933 | 14.55% | 38.767
5254 | 0 | 0 | 0 | 1 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6312 | 36.4719 | 0 | 94.6312 | 607.9563 | 47.66% | 0 | 0 | 9.0933 | 14.55% | 36.4719
5255 | 0 | 0 | 0 | 1.4 | 28.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4763 | 34.6836 | 0 | 90.4763 | 517.4801 | 40.57% | 0 | 0 | 9.0933 | 14.55% | 34.6836
5256 | 0 | 0 | 0 | 1.7 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 517.4801 | 40.57% | 0 | 0 | 9.0933 | 14.55% | 0
5257 | 0 | 0 | 0 | 2 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 517.4801 | 40.57% | 0 | 0 | 9.0933 | 14.55% | 0
5258 | 0 | 0 | 0 | 1.2 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 517.4801 | 40.57% | 0 | 0 | 9.0933 | 14.55% | 0
5259 | 0 | 0 | 0 | 1.9 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3477 | 35.8145 | 0 | 92.3477 | 425.1324 | 33.33% | 0 | 0 | 9.0933 | 14.55% | 35.8145
5260 | 0 | 0 | 0 | 2.9 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5658 | 37.9481 | 0 | 97.5658 | 327.5666 | 25.68% | 0 | 0 | 9.0933 | 14.55% | 37.9481
5261 | 0 | 0 | 0 | 0.7 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5681 | 41.2265 | 0 | 104.5681 | 222.9985 | 17.48% | 0 | 0 | 9.0933 | 14.55% | 41.2265
5262 | 5 | 16 | 15 | 1.4 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.2404 | 44.8977 | 0 | 113.2404 | 109.758 | 8.605% | 0 | 0 | 9.0933 | 14.55% | 44.8977
5263 | 164 | 141 | 100 | 1.5 | 26.5 | 0 | 0 | 0 | 0 | 4.0792 | 0 | 0 | 4.0792 | 0 | 0 | 0 | 109.758 | 43.1067 | 0 | 109.758 | 0 | 0% | 0 | 0 | 9.0933 | 14.55% | 47.1859
5264 | 371 | 337 | 177 | 0.6 | 29.7 | 0 | 0 | 0 | 62.0622 | 14.2782 | 0 | 0 | 14.2782 | 0 | 0 | 0 | 0 | 0 | 62.0622 | 0 | 62.0622 | 4.866% | 0 | 0 | 9.0933 | 14.55% | 14.2782
5265 | 499 | 535 | 231 | 0.9 | 32.1 | 0 | 0 | 0 | 110.1554 | 29.7481 | 0 | 0 | 29.7481 | 0 | 0 | 0 | 0 | 0 | 110.1554 | 0 | 172.2176 | 13.5% | 0 | 0 | 9.0933 | 14.55% | 29.7481
5266 | 593 | 712 | 261 | 1.1 | 34.2 | 0 | 0 | 0 | 14.7609 | 43.3424 | 0 | 0 | 43.3424 | 0 | 0 | 0 | 0 | 0 | 14.7609 | 0 | 186.9785 | 14.66% | 0 | 2.5691 | 6.25 | 10% | 45.9114
5267 | 670 | 850 | 267 | 1.7 | 35.4 | 0 | 0 | 0 | 177.5267 | 52.2758 | 2.3052 | 2.2758 | 50 | 0 | 0 | 0 | 0 | 0 | 177.5267 | 0 | 364.5052 | 28.58% | 2.2758 | 0 | 8.3063 | 13.29% | 50
5268 | 713 | 925 | 259 | 2.5 | 36.3 | 0 | 0 | 0 | 195.7911 | 62.0141 | 0 | 12.0141 | 50 | 0 | 0 | 0 | 0 | 0 | 195.7911 | 0 | 560.2963 | 43.93% | 12.0141 | 0 | 19.1618 | 30.66% | 50
5269 | 734 | 943 | 248 | 3.4 | 36.6 | 0 | 0 | 0 | 204.3947 | 65.6556 | 0 | 15.8752 | 49.7804 | 0 | 0 | 0 | 0 | 0 | 204.3947 | 0 | 764.691 | 59.95% | 15.8752 | 0 | 33.506 | 53.61% | 49.7804
5270 | 718 | 894 | 243 | 5.6 | 36.4 | 0 | 0 | 0 | 196.8158 | 65.0255 | 0 | 15.5362 | 49.4894 | 0 | 0 | 0 | 0 | 0 | 196.8158 | 0 | 961.5068 | 75.38% | 15.5362 | 0 | 47.5438 | 76.07% | 49.4894
5271 | 665 | 785 | 240 | 6.7 | 35.9 | 0 | 0 | 0 | 175.7854 | 58.3115 | 0 | 9.6354 | 48.676 | 0 | 0 | 0 | 0 | 0 | 175.7854 | 0 | 1137.2921 | 89.16% | 9.6354 | 0 | 56.25 | 90% | 48.676
5272 | 556 | 622 | 238 | 6.3 | 35.3 | 0 | 0 | 0 | 138.2181 | 45.8672 | 0 | 0 | 45.8672 | 0 | 0 | 0 | 0 | 0 | 138.2181 | 0 | 1275.5102 | 100% | 0 | 1.7045 | 54.3636 | 86.98% | 47.5716
5273 | 445 | 433 | 200 | 4.7 | 35 | 0 | 0 | 0 | 7.4604e-13 | 31.1005 | 0 | 0 | 31.1005 | 0 | 0 | 0 | 45.9515 | 15.5338 | 7.4604e-13 | 45.9515 | 1229.5587 | 96.4% | 0 | 0 | 54.3636 | 86.98% | 46.6343
5274 | 299 | 234 | 133 | 4 | 34 | 0 | 0 | 0 | 0 | 14.4947 | 0 | 0 | 14.4947 | 0 | 0 | 0 | 87.0439 | 32.6744 | 0 | 87.0439 | 1142.5148 | 89.57% | 0 | 0 | 54.3636 | 86.98% | 47.1691
5275 | 99 | 67 | 50 | 2.9 | 31.5 | 0 | 0 | 0 | 0 | 2.708 | 0 | 0 | 2.708 | 0 | 0 | 0 | 111.2967 | 43.1269 | 0 | 111.2967 | 1031.2181 | 80.85% | 0 | 0 | 54.3636 | 86.98% | 45.8349
5276 | 1 | 1 | 1 | 2 | 28.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.2127 | 42.6304 | 0 | 109.2127 | 922.0054 | 72.29% | 0 | 0 | 54.3636 | 86.98% | 42.6304
5277 | 0 | 0 | 0 | 0.8 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.738 | 39.6737 | 0 | 101.738 | 820.2674 | 64.31% | 0 | 0 | 54.3636 | 86.98% | 39.6737
5278 | 0 | 0 | 0 | 0.3 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.674 | 37.1891 | 0 | 95.674 | 724.5934 | 56.81% | 0 | 0 | 54.3636 | 86.98% | 37.1891
5279 | 0 | 0 | 0 | 0.5 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2054 | 35.3438 | 0 | 91.2054 | 633.388 | 49.66% | 0 | 0 | 54.3636 | 86.98% | 35.3438
5280 | 0 | 0 | 0 | 0.3 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8274 | 34.3842 | 0 | 88.8274 | 544.5606 | 42.69% | 0 | 0 | 54.3636 | 86.98% | 34.3842
5281 | 0 | 0 | 0 | 1 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.5606 | 42.69% | 0 | 0 | 54.3636 | 86.98% | 0
5282 | 0 | 0 | 0 | 0.3 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.5606 | 42.69% | 0 | 7.1494 | 46.4511 | 74.32% | 7.1494
5283 | 0 | 0 | 0 | 0.5 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9167 | 36.1822 | 0 | 92.9167 | 451.6439 | 35.41% | 0 | 0 | 46.4511 | 74.32% | 36.1822
5284 | 0 | 0 | 0 | 0.3 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9519 | 49.1828 | 0 | 122.9519 | 328.6921 | 25.77% | 10.8448 | 0 | 56.25 | 90% | 38.3381
5285 | 0 | 0 | 0 | 1.3 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7402 | 41.3003 | 0 | 104.7402 | 223.9519 | 17.56% | 0 | 0 | 56.25 | 90% | 41.3003
5286 | 13 | 16 | 15 | 1.4 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.3281 | 44.945 | 0 | 113.3281 | 110.6238 | 8.673% | 0 | 0 | 56.25 | 90% | 44.945
5287 | 282 | 155 | 87 | 0.6 | 25.9 | 0 | 0 | 0 | 0 | 3.905 | 0 | 0 | 3.905 | 0 | 0 | 0 | 110.6238 | 43.5413 | 0 | 110.6238 | 0 | 0% | 0 | 0 | 56.25 | 90% | 47.4463
5288 | 535 | 363 | 137 | 0.9 | 30.2 | 0 | 0 | 0 | 96.5591 | 13.8295 | 0 | 0 | 13.8295 | 0 | 0 | 0 | 0 | 0 | 96.5591 | 0 | 96.5591 | 7.57% | 0 | 22.928 | 30.8748 | 49.4% | 36.7576
5289 | 651 | 566 | 175 | 2.3 | 34.2 | 0 | 0 | 0 | 4.9571 | 31.1997 | 0 | 0 | 31.1997 | 0 | 0 | 0 | 0 | 0 | 4.9571 | 0 | 101.5162 | 7.959% | 0 | 18.8003 | 10.0679 | 16.11% | 50
5290 | 739 | 747 | 191 | 3 | 36.4 | 0 | 0 | 0 | 187.6554 | 46.5503 | 7.1054e-15 | 0 | 46.5503 | 0 | 0 | 0 | 0 | 0 | 187.6554 | 0 | 289.1717 | 22.67% | 0 | 3.4497 | 6.25 | 10% | 50
5291 | 772 | 875 | 207 | 4 | 37.9 | 0 | 0 | 0 | 205.9055 | 50 | 7.725 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 205.9055 | 0 | 495.0771 | 38.81% | 0 | 0 | 6.25 | 10% | 50
5292 | 764 | 941 | 230 | 5.1 | 38.9 | 0 | 0 | 0 | 209.095 | 64.6398 | 0 | 14.6398 | 50 | 0 | 0 | 0 | 0 | 0 | 209.095 | 0 | 704.1721 | 55.21% | 14.6398 | 0 | 19.4779 | 31.16% | 50
5293 | 750 | 956 | 247 | 5.9 | 39.8 | 0 | 0 | 0 | 207.1604 | 64.9429 | 2.4967 | 15.3407 | 49.6022 | 0 | 0 | 0 | 0 | 0 | 207.1604 | 0 | 911.3325 | 71.45% | 15.3407 | 0 | 33.3392 | 53.34% | 49.6022
5294 | 705 | 901 | 260 | 6.8 | 40.3 | 0 | 0 | 0 | 192.0269 | 64.8897 | 0 | 15.761 | 49.1287 | 0 | 0 | 0 | 0 | 0 | 192.0269 | 0 | 1103.3594 | 86.5% | 15.761 | 0 | 47.5802 | 76.13% | 49.1287
5295 | 654 | 792 | 254 | 7.3 | 40.4 | 0 | 0 | 0 | 172.1508 | 57.8116 | 0 | 9.5951 | 48.2164 | 0 | 0 | 0 | 0 | 0 | 172.1508 | 0 | 1275.5102 | 100% | 9.5951 | 0 | 56.25 | 90% | 48.2164
5296 | 556 | 632 | 247 | 6.3 | 40.6 | 0 | 0 | 0 | 0 | 35.0844 | 10.5333 | 0 | 35.0844 | 0 | 0 | 0 | 38.2653 | 12.0638 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 56.25 | 90% | 47.1483
5297 | 415 | 436 | 217 | 5.7 | 40.2 | 0 | 0 | 0 | 0 | 30.569 | 0 | 0 | 30.569 | 0 | 0 | 0 | 46.8288 | 15.557 | 0 | 46.8288 | 1190.4161 | 93.33% | 0 | 0 | 56.25 | 90% | 46.126
5298 | 244 | 233 | 150 | 3.9 | 38.1 | 0 | 0 | 0 | 39.3287 | 14.2045 | 0 | 0 | 14.2045 | 0 | 0 | 0 | 0 | 0 | 39.3287 | 0 | 1229.7447 | 96.41% | 0 | 25 | 28.5817 | 45.73% | 39.2045
5299 | 51 | 65 | 56 | 1.9 | 35 | 0 | 0 | 0 | 0 | 2.9738 | 0 | 0 | 2.9738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.7447 | 96.41% | 0 | 20.178 | 6.25 | 10% | 23.1518
5300 | 1 | 1 | 1 | 1.1 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.8863 | 41.8435 | 0 | 107.8863 | 1121.8584 | 87.95% | 0 | 0 | 6.25 | 10% | 41.8435
5301 | 0 | 0 | 0 | 1.2 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.0209 | 39.4954 | 0 | 102.0209 | 1019.8375 | 79.96% | 0 | 0 | 6.25 | 10% | 39.4954
5302 | 0 | 0 | 0 | 0.6 | 28.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.88 | 37.0108 | 0 | 95.88 | 923.9576 | 72.44% | 0 | 0 | 6.25 | 10% | 37.0108
5303 | 0 | 0 | 0 | 0.9 | 29.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6109 | 35.0806 | 0 | 91.6109 | 832.3467 | 65.26% | 0 | 0 | 6.25 | 10% | 35.0806
5304 | 0 | 0 | 0 | 0.7 | 29.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3491 | 33.7547 | 0 | 88.3491 | 743.9976 | 58.33% | 0 | 0 | 6.25 | 10% | 33.7547
5305 | 0 | 0 | 0 | 0.7 | 28.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1853 | 32.9163 | 0 | 86.1853 | 657.8123 | 51.57% | 0 | 0 | 6.25 | 10% | 32.9163
5306 | 0 | 0 | 0 | 0.7 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5562 | 36.4915 | 0 | 94.5562 | 563.2561 | 44.16% | 3.9331 | 4.0126e-16 | 9.8038 | 15.69% | 32.5584
5307 | 0 | 0 | 0 | 0.9 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0087 | 32.9497 | 0 | 86.0087 | 477.2475 | 37.42% | 0 | 0 | 9.8038 | 15.69% | 32.9497
5308 | 0 | 0 | 0 | 1.2 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4346 | 33.1656 | 0 | 86.4346 | 390.8128 | 30.64% | 0 | 0 | 9.8038 | 15.69% | 33.1656
5309 | 0 | 0 | 0 | 0.7 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6592 | 35.0249 | 0 | 90.6592 | 300.1536 | 23.53% | 0 | 0 | 9.8038 | 15.69% | 35.0249
5310 | 5 | 14 | 14 | 1.3 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 50.7034 | 0 | 127.551 | 172.6026 | 13.53% | 12.2693 | 0 | 20.8898 | 33.42% | 38.4342
5311 | 166 | 138 | 96 | 2.2 | 28.3 | 0 | 0 | 0 | 0 | 3.8598 | 0 | 0 | 3.8598 | 0 | 0 | 0 | 96.518 | 37.2915 | 0 | 96.518 | 76.0846 | 5.965% | 0 | 0 | 20.8898 | 33.42% | 41.1513
5312 | 383 | 334 | 170 | 2.1 | 31.5 | 0 | 0 | 0 | 0 | 14.1377 | 0 | 0 | 14.1377 | 0 | 0 | 0 | 76.0846 | 28.3617 | 0 | 76.0846 | 0 | 0% | 0 | 0 | 20.8898 | 33.42% | 42.4994
5313 | 467 | 528 | 244 | 4.1 | 33.7 | 0 | 0 | 0 | 100.0439 | 30.1349 | 0 | 0 | 30.1349 | 0 | 0 | 0 | 0 | 0 | 100.0439 | 0 | 100.0439 | 7.843% | 0 | 11.0708 | 8.6374 | 13.82% | 41.2057
5314 | 527 | 669 | 271 | 3.2 | 34.6 | 0 | 0 | 0 | 114.7211 | 42.4383 | 0 | 0 | 42.4383 | 0 | 0 | 0 | 0 | 0 | 114.7211 | 0 | 214.765 | 16.84% | 0 | 2.1571 | 6.25 | 10% | 44.5954
5315 | 653 | 832 | 261 | 2.2 | 36.1 | 0 | 0 | 0 | 172.4525 | 53.953 | 0 | 9.4857 | 44.4673 | 0 | 0 | 0 | 0 | 0 | 172.4525 | 0 | 387.2175 | 30.36% | 9.4857 | 0 | 14.8209 | 23.71% | 44.4673
5316 | 715 | 910 | 240 | 2.7 | 37.4 | 0 | 0 | 0 | 196.3549 | 61.2025 | 0 | 17.7602 | 43.4423 | 0 | 0 | 0 | 0 | 0 | 196.3549 | 0 | 583.5723 | 45.75% | 17.7602 | 0 | 30.8683 | 49.39% | 43.4423
5317 | 561 | 897 | 360 | 4.5 | 38.4 | 0 | 0 | 0 | 151.0554 | 42.7125 | 19.4744 | 0 | 42.7125 | 0 | 0 | 0 | 0 | 0 | 151.0554 | 0 | 734.6277 | 57.59% | 0 | 0 | 30.8683 | 49.39% | 42.7125
5318 | 737 | 892 | 223 | 6 | 38.9 | 0 | 0 | 0 | 202.1923 | 64.7248 | 0 | 22.6571 | 42.0677 | 0 | 0 | 0 | 0 | 0 | 202.1923 | 0 | 936.8201 | 73.45% | 22.6571 | 0 | 51.3403 | 82.14% | 42.0677
5319 | 699 | 791 | 218 | 6.4 | 39.2 | 0 | 0 | 0 | 186.1505 | 42.1598 | 16.1348 | 0.53918 | 41.6206 | 0 | 0 | 0 | 0 | 0 | 186.1505 | 0 | 1122.9706 | 88.04% | 0.53918 | 0 | 51.8275 | 82.92% | 41.6206
5320 | 605 | 625 | 209 | 5.9 | 39.1 | 0 | 0 | 0 | 152.5396 | 46.1628 | 0 | 4.8945 | 41.2683 | 0 | 0 | 0 | 0 | 0 | 152.5396 | 0 | 1275.5102 | 100% | 4.8945 | 0 | 56.25 | 90% | 41.2683
5321 | 488 | 434 | 179 | 4.6 | 38.9 | 0 | 0 | 0 | 0 | 31.0302 | 0 | 0 | 31.0302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 9.9108 | 45.2814 | 72.45% | 40.941
5322 | 318 | 232 | 125 | 5 | 36.5 | 0 | 0 | 0 | 0 | 14.5241 | 0 | 0 | 14.5241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 17.613 | 28.18% | 39.5241
5323 | 72 | 59 | 46 | 5.6 | 32.8 | 0 | 0 | 0 | 0 | 2.4807 | 0 | 0 | 2.4807 | 0 | 0 | 0 | 100.3558 | 38.3712 | 0 | 100.3558 | 1175.1544 | 92.13% | 0 | 0 | 17.613 | 28.18% | 40.8519
5324 | 0 | 1 | 1 | 4.4 | 30.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7029 | 38.4119 | 0 | 99.7029 | 1075.4515 | 84.32% | 0 | 0 | 17.613 | 28.18% | 38.4119
5325 | 0 | 0 | 0 | 3 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7326 | 36.2407 | 0 | 93.7326 | 981.7188 | 76.97% | 0 | 0 | 17.613 | 28.18% | 36.2407
5326 | 0 | 0 | 0 | 1.1 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.2914 | 46.2249 | 0 | 116.2914 | 865.4274 | 67.85% | 12.1708 | 0 | 28.6101 | 45.78% | 34.0541
5327 | 0 | 0 | 0 | 0.9 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8515 | 32.3133 | 0 | 83.8515 | 781.5759 | 61.28% | 0 | 0 | 28.6101 | 45.78% | 32.3133
5328 | 0 | 0 | 0 | 0.9 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6848 | 31.3217 | 0 | 81.6848 | 699.8911 | 54.87% | 0 | 0 | 28.6101 | 45.78% | 31.3217
5329 | 0 | 0 | 0 | 1.7 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7944 | 30.5613 | 0 | 79.7944 | 620.0967 | 48.62% | 0 | 0 | 28.6101 | 45.78% | 30.5613
5330 | 0 | 0 | 0 | 1.2 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2979 | 30.2939 | 0 | 79.2979 | 540.7988 | 42.4% | 0 | 0 | 28.6101 | 45.78% | 30.2939
5331 | 0 | 0 | 0 | 1.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6142 | 30.4638 | 0 | 79.6142 | 461.1845 | 36.16% | 0 | 0 | 28.6101 | 45.78% | 30.4638
5332 | 0 | 0 | 0 | 0.9 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2517 | 29.8872 | 0 | 78.2517 | 382.9329 | 30.02% | 0 | 0 | 28.6101 | 45.78% | 29.8872
5333 | 0 | 0 | 0 | 1.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2975 | 30.7562 | 0 | 80.2975 | 302.6354 | 23.73% | 0 | 0 | 28.6101 | 45.78% | 30.7562
5334 | 1 | 9 | 9 | 1.2 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6901 | 33.0194 | 0 | 85.6901 | 216.9453 | 17.01% | 0 | 0 | 28.6101 | 45.78% | 33.0194
5335 | 148 | 141 | 103 | 1.9 | 25.9 | 0 | 0 | 0 | 0 | 4.0171 | 0 | 0 | 4.0171 | 0 | 0 | 0 | 81.8165 | 31.2654 | 0 | 81.8165 | 135.1288 | 10.59% | 0 | 0 | 28.6101 | 45.78% | 35.2825
5336 | 320 | 292 | 150 | 5 | 27.3 | 0 | 0 | 0 | 47.4742 | 12.6304 | 0 | 0 | 12.6304 | 0 | 0 | 0 | 0 | 0 | 47.4742 | 0 | 182.603 | 14.32% | 0 | 12.2454 | 15.0577 | 24.09% | 24.8757
5337 | 549 | 522 | 189 | 5.2 | 29.2 | 0 | 0 | 0 | 119.9324 | 30.1778 | 0 | 0 | 30.1778 | 0 | 0 | 0 | 0 | 0 | 119.9324 | 0 | 302.5355 | 23.72% | 0 | 7.9583 | 6.25 | 10% | 38.1361
5338 | 658 | 703 | 206 | 3 | 31.7 | 0 | 0 | 0 | 165.0349 | 39.15 | 5.7666 | 0 | 39.15 | 0 | 0 | 0 | 0 | 0 | 165.0349 | 0 | 467.5704 | 36.66% | 0 | 0 | 6.25 | 10% | 39.15
5339 | 692 | 832 | 231 | 2.1 | 33.5 | 0 | 0 | 0 | 183.8098 | 50.4438 | 4.3481 | 10.8133 | 39.6305 | 0 | 0 | 0 | 0 | 0 | 183.8098 | 0 | 651.3802 | 51.07% | 10.8133 | 0 | 16.0205 | 25.63% | 39.6305
5340 | 654 | 859 | 247 | 2.1 | 34.9 | 0 | 0 | 0 | 178.289 | 58.2236 | 0 | 19.5234 | 38.7002 | 0 | 0 | 0 | 0 | 0 | 178.289 | 0 | 829.6692 | 65.05% | 19.5234 | 0 | 33.661 | 53.86% | 38.7002
5341 | 709 | 901 | 230 | 4.4 | 35.4 | 0 | 0 | 0 | 196.0517 | 62.9286 | 1.4437 | 25 | 37.9286 | 0 | 0 | 0 | 0 | 0 | 196.0517 | 0 | 1025.721 | 80.42% | 25 | 0 | 56.25 | 90% | 37.9286
5342 | 143 | 536 | 396 | 5.3 | 33.4 | 0 | 0 | 0 | 0 | 36.6002 | 0 | 0 | 36.6002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1025.721 | 80.42% | 0 | 0 | 56.25 | 90% | 36.6002
5343 | 164 | 473 | 335 | 4.2 | 32.8 | 0 | 0 | 0 | 0 | 32.6869 | 0 | 0 | 32.6869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1025.721 | 80.42% | 0 | 0 | 56.25 | 90% | 32.6869
5344 | 82 | 377 | 314 | 3.7 | 33 | 0 | 0 | 0 | 0 | 24.3891 | 0 | 0 | 24.3891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1025.721 | 80.42% | 0 | 0 | 56.25 | 90% | 24.3891
5345 | 43 | 260 | 233 | 3.4 | 31.2 | 0 | 0 | 0 | 0 | 16.3559 | 0 | 0 | 16.3559 | 0 | 0 | 0 | 58.4473 | 20.9864 | 0 | 58.4473 | 967.2737 | 75.83% | 0 | 0 | 56.25 | 90% | 37.3423
5346 | 207 | 237 | 172 | 3 | 30.5 | 0 | 0 | 0 | 0 | 15.0356 | 0 | 0 | 15.0356 | 0 | 0 | 0 | 66.5003 | 24.4208 | 0 | 66.5003 | 900.7734 | 70.62% | 0 | 0 | 56.25 | 90% | 39.4564
5347 | 55 | 63 | 53 | 2 | 29.6 | 0 | 0 | 0 | 0 | 2.8771 | 0 | 0 | 2.8771 | 0 | 0 | 0 | 95.2826 | 36.6294 | 0 | 95.2826 | 805.4908 | 63.15% | 0 | 0 | 56.25 | 90% | 39.5065
5348 | 0 | 0 | 0 | 1.3 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2676 | 37.2476 | 0 | 96.2676 | 709.2232 | 55.6% | 0 | 0 | 56.25 | 90% | 37.2476
5349 | 0 | 0 | 0 | 0.8 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2762 | 34.8173 | 0 | 90.2762 | 618.947 | 48.53% | 0 | 0 | 56.25 | 90% | 34.8173
5350 | 0 | 0 | 0 | 0.6 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3659 | 32.8731 | 0 | 85.3659 | 533.581 | 41.83% | 0 | 0 | 56.25 | 90% | 32.8731
5351 | 0 | 0 | 0 | 0.7 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9509 | 31.4498 | 0 | 81.9509 | 451.6302 | 35.41% | 0 | 0 | 56.25 | 90% | 31.4498
5352 | 0 | 0 | 0 | 0.4 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.6302 | 35.41% | 0 | 0 | 56.25 | 90% | 0
5353 | 0 | 0 | 0 | 0.6 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451.6302 | 35.41% | 0 | 0 | 56.25 | 90% | 0
5354 | 0 | 0 | 0 | 0.5 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7769 | 30.6128 | 0 | 79.7769 | 371.8532 | 29.15% | 0 | 0 | 56.25 | 90% | 30.6128
5355 | 0 | 0 | 0 | 0.7 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4622 | 32.5821 | 0 | 84.4622 | 287.391 | 22.53% | 0 | 0 | 56.25 | 90% | 32.5821
5356 | 0 | 0 | 0 | 0.9 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3141 | 34.7059 | 0 | 89.3141 | 198.0769 | 15.53% | 0 | 0 | 56.25 | 90% | 34.7059
5357 | 0 | 0 | 0 | 1.4 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5656 | 37.4272 | 0 | 95.5656 | 102.5113 | 8.037% | 0 | 0 | 56.25 | 90% | 37.4272
5358 | 23 | 14 | 11 | 1.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5113 | 40.4355 | 0 | 102.5113 | 0 | 0% | 0 | 0 | 56.25 | 90% | 40.4355
5359 | 374 | 151 | 65 | 1.1 | 24.6 | 0 | 0 | 0 | 38.484 | 3.0857 | 0 | 0 | 3.0857 | 0 | 0 | 0 | 0 | 0 | 38.484 | 0 | 38.484 | 3.017% | 0 | 7.8644 | 47.5462 | 76.07% | 10.9501
5360 | 605 | 356 | 104 | 0.5 | 28.2 | 0 | 0 | 0 | 110.9413 | 13.0142 | 0 | 0 | 13.0142 | 0 | 0 | 0 | 0 | 0 | 110.9413 | 0 | 149.4254 | 11.71% | 0 | 25 | 19.8779 | 31.8% | 38.0142
5361 | 708 | 571 | 150 | 1.4 | 29.8 | 0 | 0 | 0 | 162.8509 | 32.0674 | 0 | 0 | 32.0674 | 0 | 0 | 0 | 0 | 0 | 162.8509 | 0 | 312.2762 | 24.48% | 0 | 12.3136 | 6.25 | 10% | 44.381
5362 | 734 | 756 | 207 | 2.6 | 31.5 | 0 | 0 | 0 | 186.3245 | 48.2302 | 0 | 3.2031 | 45.0272 | 0 | 0 | 0 | 0 | 0 | 186.3245 | 0 | 498.6008 | 39.09% | 3.2031 | 0 | 9.1442 | 14.63% | 45.0272
5363 | 815 | 938 | 237 | 4.5 | 32.5 | 0 | 0 | 0 | 217.9313 | 63.5761 | 0 | 19.0615 | 44.5147 | 0 | 0 | 0 | 0 | 0 | 217.9313 | 0 | 716.532 | 56.18% | 19.0615 | 0 | 26.3674 | 42.19% | 44.5147
5364 | 447 | 806 | 390 | 5.2 | 32.5 | 0 | 0 | 0 | 114.2035 | 56.8819 | 0 | 13.3686 | 43.5133 | 0 | 0 | 0 | 0 | 0 | 114.2035 | 0 | 830.7356 | 65.13% | 13.3686 | 0 | 38.4467 | 61.51% | 43.5133
5365 | 234 | 642 | 415 | 5.7 | 32.4 | 0 | 0 | 0 | 50.244 | 45.5144 | 0 | 2.5164 | 42.998 | 0 | 0 | 0 | 0 | 0 | 50.244 | 0 | 880.9796 | 69.07% | 2.5164 | 0 | 40.7204 | 65.15% | 42.998
5366 | 30 | 398 | 364 | 5.9 | 31 | 0 | 0 | 0 | 0 | 26.0432 | 0 | 0 | 26.0432 | 0 | 0 | 0 | 47.5827 | 16.4368 | 0 | 47.5827 | 833.3969 | 65.34% | 0 | 0 | 40.7204 | 65.15% | 42.4799
5367 | 93 | 440 | 363 | 5.7 | 30.6 | 0 | 0 | 0 | 0 | 29.7584 | 0 | 8.8776 | 20.8808 | 0 | 0 | 0 | 58.8716 | 21.205 | 0 | 58.8716 | 774.5253 | 60.72% | 8.8776 | 0 | 48.7418 | 77.99% | 42.0858
5368 | 264 | 508 | 321 | 5.1 | 30.2 | 0 | 0 | 0 | 55.38 | 36.2768 | 0 | 0 | 36.2768 | 0 | 0 | 0 | 0 | 0 | 55.38 | 0 | 829.9053 | 65.06% | 0 | 5.2658 | 42.9139 | 68.66% | 41.5427
5369 | 512 | 434 | 175 | 5 | 29.6 | 0 | 0 | 0 | 117.8571 | 32.9049 | 0 | 0 | 32.9049 | 0 | 0 | 0 | 0 | 0 | 117.8571 | 0 | 947.7625 | 74.3% | 0 | 8.128 | 33.9183 | 54.27% | 41.0329
5370 | 566 | 258 | 77 | 4.8 | 28.8 | 0 | 0 | 0 | 114.379 | 17.2439 | 0 | 0 | 17.2439 | 0 | 0 | 0 | 0 | 0 | 114.379 | 0 | 1062.1414 | 83.27% | 0 | 25 | 6.25 | 10% | 42.2439
5371 | 201 | 61 | 31 | 4.6 | 27.1 | 0 | 0 | 0 | 0 | 1.7651 | 0 | 0 | 1.7651 | 0 | 0 | 0 | 100.7565 | 39.2149 | 0 | 100.7565 | 961.385 | 75.37% | 0 | 0 | 6.25 | 10% | 40.98
5372 | 0 | 0 | 0 | 4.8 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.248 | 37.9244 | 0 | 97.248 | 864.1369 | 67.75% | 0 | 0 | 6.25 | 10% | 37.9244
5373 | 0 | 0 | 0 | 4 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3379 | 35.5137 | 0 | 91.3379 | 772.7991 | 60.59% | 0 | 0 | 6.25 | 10% | 35.5137
5374 | 0 | 0 | 0 | 2.9 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2123 | 33.3536 | 0 | 86.2123 | 686.5868 | 53.83% | 0 | 0 | 6.25 | 10% | 33.3536
5375 | 0 | 0 | 0 | 2.6 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8496 | 41.7938 | 0 | 105.8496 | 580.7372 | 45.53% | 9.8315 | 0 | 15.1333 | 24.21% | 31.9623
5376 | 0 | 0 | 0 | 1.7 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.7372 | 45.53% | 0 | 0 | 15.1333 | 24.21% | 0
5377 | 0 | 0 | 0 | 1.2 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.7372 | 45.53% | 0 | 0 | 15.1333 | 24.21% | 0
5378 | 0 | 0 | 0 | 1.1 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580.7372 | 45.53% | 0 | 8.0266 | 6.25 | 10% | 8.0266
5379 | 0 | 0 | 0 | 1 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.3707 | 39.5461 | 0 | 100.3707 | 480.3665 | 37.66% | 6.4878 | 0 | 12.1121 | 19.38% | 33.0584
5380 | 0 | 0 | 0 | 1.5 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2783 | 0 | 127.551 | 352.8155 | 27.66% | 16.5056 | 0 | 27.0259 | 43.24% | 34.7728
5381 | 0 | 0 | 0 | 1.5 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3163 | 0 | 127.551 | 225.2645 | 17.66% | 14.233 | 0 | 39.8862 | 63.82% | 37.0833
5382 | 0 | 7 | 7 | 0.7 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3069 | 0 | 127.551 | 97.7135 | 7.661% | 11.5232 | 0 | 50.2981 | 80.48% | 39.7837
5383 | 20 | 78 | 72 | 0.7 | 22.1 | 0 | 0 | 0 | 0 | 3.0658 | 0 | 0 | 3.0658 | 0 | 0 | 0 | 97.7135 | 38.3654 | 0 | 97.7135 | 0 | 0% | 0 | 0 | 50.2981 | 80.48% | 41.4312
5384 | 362 | 337 | 181 | 3.2 | 24.9 | 0 | 0 | 0 | 0 | 15.136 | 0 | 0 | 15.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 22.6298 | 36.21% | 40.136
5385 | 523 | 492 | 181 | 3.9 | 26.4 | 0 | 0 | 0 | 96.1803 | 29.1686 | 0 | 0 | 29.1686 | 0 | 0 | 0 | 0 | 0 | 96.1803 | 0 | 96.1803 | 7.541% | 0 | 14.8001 | 6.25 | 10% | 43.9687
5386 | 800 | 734 | 140 | 5.1 | 27.6 | 0 | 0 | 0 | 202.6732 | 44.9032 | 3.6488 | 0 | 44.9032 | 0 | 0 | 0 | 0 | 0 | 202.6732 | 0 | 298.8535 | 23.43% | 0 | 0 | 6.25 | 10% | 44.9032
5387 | 828 | 863 | 156 | 5.8 | 28.8 | 0 | 0 | 0 | 220.5456 | 44.3336 | 16.0785 | 0 | 44.3336 | 0 | 0 | 0 | 0 | 0 | 220.5456 | 0 | 519.3991 | 40.72% | 0 | 0 | 6.25 | 10% | 44.3336
5388 | 762 | 900 | 196 | 6.8 | 29.1 | 0 | 0 | 0 | 206.9325 | 43.3239 | 22.4656 | 0 | 43.3239 | 0 | 0 | 0 | 0 | 0 | 206.9325 | 0 | 726.3316 | 56.94% | 0 | 0 | 6.25 | 10% | 43.3239
5389 | 689 | 970 | 323 | 7.3 | 29.5 | 0 | 0 | 0 | 187.365 | 65.7438 | 5.9005 | 22.7722 | 42.9716 | 0 | 0 | 0 | 0 | 0 | 187.365 | 0 | 913.6966 | 71.63% | 22.7722 | 0 | 26.8261 | 42.92% | 42.9716
5390 | 323 | 701 | 405 | 7.1 | 29 | 0 | 0 | 0 | 75.8356 | 51.3638 | 0 | 8.7223 | 42.6415 | 0 | 0 | 0 | 0 | 0 | 75.8356 | 0 | 989.5322 | 77.58% | 8.7223 | 0 | 34.7072 | 55.53% | 42.6415
5391 | 607 | 788 | 296 | 6.8 | 29.1 | 0 | 0 | 0 | 158.2662 | 60.0659 | 0 | 17.8631 | 42.2028 | 0 | 0 | 0 | 0 | 0 | 158.2662 | 0 | 1147.7983 | 89.99% | 17.8631 | 0 | 50.8476 | 81.36% | 42.2028
5392 | 520 | 625 | 271 | 6.2 | 28.5 | 0 | 0 | 0 | 127.7119 | 47.5412 | 0 | 5.979 | 41.5622 | 0 | 0 | 0 | 0 | 0 | 127.7119 | 0 | 1275.5102 | 100% | 5.979 | 0 | 56.25 | 90% | 41.5622
5393 | 371 | 373 | 193 | 6 | 27.4 | 0 | 0 | 0 | 0 | 28.8068 | 0 | 0 | 28.8068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 12.4156 | 42.5093 | 68.01% | 41.2223
5394 | 318 | 212 | 110 | 5.4 | 26.5 | 0 | 0 | 0 | 0 | 14.1155 | 0 | 0 | 14.1155 | 0 | 0 | 0 | 38.2653 | 12.6872 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 16.0087 | 24.7919 | 39.67% | 42.8114
5395 | 55 | 43 | 34 | 4.6 | 25 | 0 | 0 | 0 | 0 | 1.812 | 0 | 0 | 1.812 | 0 | 0 | 0 | 92.8026 | 36.0259 | 0 | 92.8026 | 1144.4423 | 89.72% | 0 | 3.2884 | 21.1526 | 33.84% | 41.1262
5396 | 0 | 0 | 0 | 4.2 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4264 | 38.1055 | 0 | 97.4264 | 1047.0159 | 82.09% | 0 | 0 | 21.1526 | 33.84% | 38.1055
5397 | 0 | 0 | 0 | 3.9 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8692 | 35.795 | 0 | 91.8692 | 955.1467 | 74.88% | 0 | 0 | 21.1526 | 33.84% | 35.795
5398 | 0 | 0 | 0 | 3.4 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.755 | 33.6489 | 0 | 86.755 | 868.3916 | 68.08% | 0 | 0 | 21.1526 | 33.84% | 33.6489
5399 | 0 | 0 | 0 | 3.4 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1501 | 32.1253 | 0 | 83.1501 | 785.2415 | 61.56% | 0 | 0 | 21.1526 | 33.84% | 32.1253
5400 | 0 | 0 | 0 | 2.9 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1908 | 31.2827 | 0 | 81.1908 | 704.0507 | 55.2% | 0 | 0 | 21.1526 | 33.84% | 31.2827
5401 | 0 | 0 | 0 | 2.8 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.361 | 27.9264 | 0 | 73.361 | 630.6897 | 49.45% | 0 | 0 | 21.1526 | 33.84% | 27.9264
5402 | 0 | 0 | 0 | 2.7 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.028 | 31.2367 | 0 | 81.028 | 549.6617 | 43.09% | 0 | 0 | 21.1526 | 33.84% | 31.2367
5403 | 0 | 0 | 0 | 2.1 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1482 | 33.0347 | 0 | 85.1482 | 464.5135 | 36.42% | 0 | 0 | 21.1526 | 33.84% | 33.0347
5404 | 0 | 0 | 0 | 1.8 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4788 | 34.919 | 0 | 89.4788 | 375.0347 | 29.4% | 0 | 0 | 21.1526 | 33.84% | 34.919
5405 | 0 | 0 | 0 | 0.7 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0136 | 37.3242 | 0 | 95.0136 | 280.0211 | 21.95% | 0 | 0 | 21.1526 | 33.84% | 37.3242
5406 | 19 | 13 | 11 | 1.4 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4477 | 40.1263 | 0 | 101.4477 | 178.5734 | 14% | 0 | 0 | 21.1526 | 33.84% | 40.1263
5407 | 344 | 142 | 64 | 1 | 22.1 | 0 | 0 | 0 | 0 | 3.0402 | 0 | 0 | 3.0402 | 0 | 0 | 0 | 99.1536 | 38.9844 | 0 | 99.1536 | 79.4198 | 6.227% | 0 | 0 | 21.1526 | 33.84% | 42.0245
5408 | 597 | 345 | 99 | 1.1 | 23.8 | 0 | 0 | 0 | 0 | 13.0162 | 0 | 0 | 13.0162 | 0 | 0 | 0 | 79.4198 | 30.3941 | 0 | 79.4198 | 0 | 0% | 0 | 0 | 21.1526 | 33.84% | 43.4103
5409 | 744 | 550 | 110 | 1.7 | 25.7 | 0 | 0 | 0 | 0 | 31.371 | 0 | 0 | 31.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 13.4654 | 6.25 | 10% | 44.8364
5410 | 820 | 726 | 116 | 1.7 | 27.8 | 0 | 0 | 0 | 0 | 45.9394 | 0.54756 | 0 | 45.9394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 45.9394
5411 | 842 | 854 | 134 | 1.8 | 29.3 | 0 | 0 | 0 | 227.5825 | 45.5843 | 11.7245 | 0 | 45.5843 | 0 | 0 | 0 | 0 | 0 | 227.5825 | 0 | 227.5825 | 17.84% | 0 | 0 | 6.25 | 10% | 45.5843
5412 | 778 | 903 | 185 | 2 | 30.6 | 0 | 0 | 0 | 215.4114 | 51.2901 | 11.053 | 6.5888 | 44.7013 | 0 | 0 | 0 | 0 | 0 | 215.4114 | 0 | 442.9938 | 34.73% | 6.5888 | 0 | 12.2034 | 19.53% | 44.7013
5413 | 362 | 593 | 251 | 2.8 | 31.1 | 0 | 0 | 0 | 0 | 43.5446 | 0 | 0 | 43.5446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 442.9938 | 34.73% | 0 | 0.64144 | 11.4935 | 18.39% | 44.186
5414 | 851 | 940 | 181 | 4.1 | 32.2 | 0 | 0 | 0 | 174.5252 | 68.8573 | 0.72881 | 25 | 43.8573 | 0 | 0 | 0 | 0 | 0 | 174.5252 | 0 | 617.519 | 48.41% | 25 | 0 | 34.0825 | 54.53% | 43.8573
5415 | 809 | 795 | 147 | 4.6 | 32.3 | 0 | 0 | 0 | 219.7917 | 60.9181 | 0 | 17.512 | 43.4061 | 0 | 0 | 0 | 0 | 0 | 219.7917 | 0 | 837.3107 | 65.65% | 17.512 | 0 | 49.9056 | 79.85% | 43.4061
5416 | 767 | 634 | 121 | 5.8 | 32.5 | 0 | 0 | 0 | 198.7322 | 49.7869 | 0 | 7.0215 | 42.7654 | 0 | 0 | 0 | 0 | 0 | 198.7322 | 0 | 1036.0429 | 81.23% | 7.0215 | 0 | 56.25 | 90% | 42.7654
5417 | 680 | 443 | 102 | 6.3 | 31.9 | 0 | 0 | 0 | 161.7341 | 34.8055 | 0 | 0 | 34.8055 | 0 | 0 | 0 | 0 | 0 | 161.7341 | 0 | 1197.7771 | 93.91% | 0 | 7.304 | 48.1664 | 77.07% | 42.1095
5418 | 522 | 237 | 74 | 5.6 | 30.6 | 0 | 0 | 0 | 0 | 16.0101 | 0 | 0 | 16.0101 | 0 | 0 | 0 | 73.2489 | 27.2511 | 0 | 73.2489 | 1124.5282 | 88.16% | 0 | 0 | 48.1664 | 77.07% | 43.2612
5419 | 191 | 57 | 30 | 2.7 | 29.1 | 0 | 0 | 0 | 0 | 1.6594 | 0 | 0 | 1.6594 | 0 | 0 | 0 | 102.922 | 39.9111 | 0 | 102.922 | 1021.6062 | 80.09% | 0 | 0 | 48.1664 | 77.07% | 41.5705
5420 | 0 | 0 | 0 | 3.6 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.187 | 21.2012 | 0 | 58.187 | 963.4191 | 75.53% | 0 | 17.5198 | 28.7766 | 46.04% | 38.7211
5421 | 0 | 0 | 0 | 2.8 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.8346 | 36.5178 | 0 | 93.8346 | 869.5845 | 68.18% | 0 | 0 | 28.7766 | 46.04% | 36.5178
5422 | 0 | 0 | 0 | 0.8 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5423 | 34.316 | 0 | 88.5423 | 781.0422 | 61.23% | 0 | 0 | 28.7766 | 46.04% | 34.316
5423 | 0 | 0 | 0 | 0.7 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4492 | 32.6044 | 0 | 84.4492 | 696.593 | 54.61% | 0 | 0 | 28.7766 | 46.04% | 32.6044
5424 | 0 | 0 | 0 | 0.3 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0786 | 31.6072 | 0 | 82.0786 | 614.5143 | 48.18% | 0 | 0 | 28.7766 | 46.04% | 31.6072
5425 | 0 | 0 | 0 | 0.8 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4921 | 30.9262 | 0 | 80.4921 | 534.0222 | 41.87% | 0 | 0 | 28.7766 | 46.04% | 30.9262
5426 | 0 | 0 | 0 | 1 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7368 | 30.681 | 0 | 79.7368 | 454.2854 | 35.62% | 0 | 0 | 28.7766 | 46.04% | 30.681
5427 | 0 | 0 | 0 | 0.9 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3323 | 30.9373 | 0 | 80.3323 | 373.9531 | 29.32% | 0 | 0 | 28.7766 | 46.04% | 30.9373
5428 | 0 | 0 | 0 | 1.4 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9094 | 30.8008 | 0 | 79.9094 | 294.0437 | 23.05% | 0 | 0 | 28.7766 | 46.04% | 30.8008
5429 | 0 | 0 | 0 | 1.2 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.088 | 31.7283 | 0 | 82.088 | 211.9557 | 16.62% | 0 | 0 | 28.7766 | 46.04% | 31.7283
5430 | 39 | 14 | 10 | 0.8 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1559 | 33.9302 | 0 | 87.1559 | 124.7998 | 9.784% | 0 | 0 | 28.7766 | 46.04% | 33.9302
5431 | 461 | 150 | 49 | 1.3 | 22.5 | 0 | 0 | 0 | 0 | 2.5273 | 0 | 0 | 2.5273 | 0 | 0 | 0 | 86.5345 | 33.5337 | 0 | 86.5345 | 38.2653 | 3% | 0 | 0 | 28.7766 | 46.04% | 36.061
5432 | 690 | 356 | 73 | 1.8 | 26.3 | 0 | 0 | 0 | 0 | 12.3203 | 0 | 0 | 12.3203 | 0 | 0 | 0 | 38.2653 | 12.6937 | 0 | 38.2653 | 0 | 0% | 0 | 12.7572 | 14.6578 | 23.45% | 37.7712
5433 | 795 | 558 | 89 | 2.1 | 29.1 | 0 | 0 | 0 | 184.2791 | 31.4207 | 0 | 0 | 31.4207 | 0 | 0 | 0 | 0 | 0 | 184.2791 | 0 | 184.2791 | 14.45% | 0 | 7.597 | 6.25 | 10% | 39.0177
5434 | 846 | 728 | 100 | 1.4 | 31.4 | 0 | 0 | 0 | 217.8522 | 40.1235 | 5.6983 | 0 | 40.1235 | 0 | 0 | 0 | 0 | 0 | 217.8522 | 0 | 402.1313 | 31.53% | 0 | 0 | 6.25 | 10% | 40.1235
5435 | 876 | 854 | 107 | 1.6 | 32.9 | 0 | 0 | 0 | 0 | 40.3352 | 15.7698 | 0 | 40.3352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402.1313 | 31.53% | 0 | 0 | 6.25 | 10% | 40.3352
5436 | 892 | 928 | 110 | 2.9 | 34 | 0 | 0 | 0 | 98.521 | 39.5581 | 24.5299 | 0 | 39.5581 | 0 | 0 | 0 | 0 | 0 | 98.521 | 0 | 500.6523 | 39.25% | 0 | 0 | 6.25 | 10% | 39.5581
5437 | 891 | 940 | 112 | 5.3 | 34.1 | 0 | 0 | 0 | 250.4967 | 38.923 | 29.4813 | 0 | 38.923 | 0 | 0 | 0 | 0 | 0 | 250.4967 | 0 | 751.149 | 58.89% | 0 | 0 | 6.25 | 10% | 38.923
5438 | 873 | 890 | 113 | 5.7 | 33.8 | 0 | 0 | 0 | 243.4828 | 63.4662 | 3.1802 | 25 | 38.4662 | 0 | 0 | 0 | 0 | 0 | 243.4828 | 0 | 994.6318 | 77.98% | 25 | 0 | 28.839 | 46.14% | 38.4662
5439 | 840 | 784 | 111 | 5.4 | 34.3 | 0 | 0 | 0 | 228.3016 | 59.8412 | 0 | 21.6452 | 38.196 | 0 | 0 | 0 | 0 | 0 | 228.3016 | 0 | 1222.9334 | 95.88% | 21.6452 | 0 | 48.3967 | 77.43% | 38.196
5440 | 788 | 629 | 103 | 5.4 | 33.6 | 0 | 0 | 0 | 0 | 46.5323 | 2.5396 | 8.6915 | 37.8409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.9334 | 95.88% | 8.6915 | 0 | 56.25 | 90% | 37.8409
5441 | 705 | 441 | 90 | 5.1 | 33.4 | 0 | 0 | 0 | 0 | 34.6694 | 0 | 0 | 34.6694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.9334 | 95.88% | 0 | 3.3595 | 52.5319 | 84.05% | 38.0289
5442 | 549 | 236 | 66 | 4 | 32 | 0 | 0 | 0 | 0 | 15.8763 | 0 | 0 | 15.8763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.9334 | 95.88% | 0 | 24.0216 | 25.9464 | 41.51% | 39.8979
5443 | 206 | 56 | 27 | 1.6 | 30.1 | 0 | 0 | 0 | 0 | 1.4927 | 0 | 0 | 1.4927 | 0 | 0 | 0 | 99.1778 | 38.2144 | 0 | 99.1778 | 1123.7556 | 88.1% | 0 | 0 | 25.9464 | 41.51% | 39.7071
5444 | 0 | 0 | 0 | 0.9 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8266 | 31.5468 | 0 | 82.8266 | 1040.929 | 81.61% | 0 | 5.9334 | 19.3797 | 31.01% | 37.4802
5445 | 0 | 0 | 0 | 2.9 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4397 | 35.3925 | 0 | 91.4397 | 949.4892 | 74.44% | 0 | 0 | 19.3797 | 31.01% | 35.3925
5446 | 0 | 0 | 0 | 1.9 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3598 | 33.3662 | 0 | 86.3598 | 863.1295 | 67.67% | 0 | 0 | 19.3797 | 31.01% | 33.3662
5447 | 0 | 0 | 0 | 0.9 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8248 | 31.8871 | 0 | 82.8248 | 780.3046 | 61.18% | 0 | 0 | 19.3797 | 31.01% | 31.8871
5448 | 0 | 0 | 0 | 1.6 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7331 | 31.0167 | 0 | 80.7331 | 699.5715 | 54.85% | 0 | 0 | 19.3797 | 31.01% | 31.0167
5449 | 0 | 0 | 0 | 1.1 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7278 | 30.5724 | 0 | 79.7278 | 619.8437 | 48.6% | 0 | 0 | 19.3797 | 31.01% | 30.5724
5450 | 0 | 0 | 0 | 1.1 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3068 | 30.8593 | 0 | 80.3068 | 539.5369 | 42.3% | 0 | 0 | 19.3797 | 31.01% | 30.8593
5451 | 0 | 0 | 0 | 2.1 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9261 | 32.3592 | 0 | 83.9261 | 455.6108 | 35.72% | 0 | 0 | 19.3797 | 31.01% | 32.3592
5452 | 0 | 0 | 0 | 1.9 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2549 | 33.9358 | 0 | 87.2549 | 368.3559 | 28.88% | 0 | 0 | 19.3797 | 31.01% | 33.9358
5453 | 0 | 0 | 0 | 2.1 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.5014 | 36.1181 | 0 | 92.5014 | 275.8545 | 21.63% | 0 | 0 | 19.3797 | 31.01% | 36.1181
5454 | 35 | 12 | 9 | 1.8 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0861 | 39.001 | 0 | 99.0861 | 176.7684 | 13.86% | 0 | 0 | 19.3797 | 31.01% | 39.001
5455 | 423 | 144 | 51 | 1.9 | 23.2 | 0 | 0 | 0 | 0 | 2.6643 | 0 | 0 | 2.6643 | 0 | 0 | 0 | 97.9726 | 38.3895 | 0 | 97.9726 | 78.7958 | 6.178% | 0 | 0 | 19.3797 | 31.01% | 41.0538
5456 | 657 | 347 | 79 | 3.5 | 26.1 | 0 | 0 | 0 | 0 | 12.5168 | 0 | 0 | 12.5168 | 0 | 0 | 0 | 78.7958 | 29.9631 | 0 | 78.7958 | 0 | 0% | 0 | 0 | 19.3797 | 31.01% | 42.4799
5457 | 782 | 550 | 93 | 4 | 28.3 | 0 | 0 | 0 | 29.5217 | 31.8852 | 0 | 0 | 31.8852 | 0 | 0 | 0 | 0 | 0 | 29.5217 | 0 | 29.5217 | 2.315% | 0 | 11.8635 | 6.25 | 10% | 43.7487
5458 | 846 | 725 | 102 | 3.8 | 30.2 | 0 | 0 | 0 | 0 | 47.599 | 0 | 2.4646 | 45.1344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5217 | 2.315% | 2.4646 | 0 | 8.4769 | 13.56% | 45.1344
5459 | 877 | 853 | 109 | 2.8 | 31.8 | 0 | 0 | 0 | 237.4856 | 45.2542 | 12.5308 | 0 | 45.2542 | 0 | 0 | 0 | 0 | 0 | 237.4856 | 0 | 267.0072 | 20.93% | 0 | 0 | 8.4769 | 13.56% | 45.2542
5460 | 889 | 927 | 115 | 2.5 | 33.1 | 0 | 0 | 0 | 248.7529 | 52.9185 | 11.2044 | 8.1936 | 44.725 | 0 | 0 | 0 | 0 | 0 | 248.7529 | 0 | 515.7602 | 40.44% | 8.1936 | 0 | 15.8803 | 25.41% | 44.725
5461 | 887 | 937 | 116 | 3.3 | 34.1 | 0 | 0 | 0 | 251.003 | 67.1248 | 0 | 22.7494 | 44.3754 | 0 | 0 | 0 | 0 | 0 | 251.003 | 0 | 766.7631 | 60.11% | 22.7494 | 0 | 36.4358 | 58.3% | 44.3754
5462 | 871 | 887 | 116 | 4.5 | 34.7 | 0 | 0 | 0 | 243.9088 | 65.9605 | 0 | 21.9291 | 44.0314 | 0 | 0 | 0 | 0 | 0 | 243.9088 | 0 | 1010.6719 | 79.24% | 21.9291 | 0 | 56.25 | 90% | 44.0314
5463 | 845 | 782 | 110 | 4.6 | 34.6 | 0 | 0 | 0 | 230.4482 | 43.4493 | 16.2787 | 0 | 43.4493 | 0 | 0 | 0 | 0 | 0 | 230.4482 | 0 | 1241.1201 | 97.3% | 0 | 0 | 56.25 | 90% | 43.4493
5464 | 798 | 629 | 101 | 4.3 | 34.5 | 0 | 0 | 0 | 0 | 42.8922 | 6.1139 | 0 | 42.8922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241.1201 | 97.3% | 0 | 0 | 56.25 | 90% | 42.8922
5465 | 701 | 435 | 90 | 3.6 | 33.8 | 0 | 0 | 0 | 0 | 34.2395 | 0 | 0 | 34.2395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241.1201 | 97.3% | 0 | 8.1889 | 47.1871 | 75.5% | 42.4284
5466 | 538 | 231 | 67 | 4.1 | 33.4 | 0 | 0 | 0 | 0 | 15.6329 | 0 | 0 | 15.6329 | 0 | 0 | 0 | 75.6422 | 27.9946 | 0 | 75.6422 | 1165.4779 | 91.37% | 0 | 0 | 47.1871 | 75.5% | 43.6275
5467 | 176 | 51 | 27 | 3.1 | 31.1 | 0 | 0 | 0 | 0 | 1.4338 | 0 | 0 | 1.4338 | 0 | 0 | 0 | 104.9339 | 40.5113 | 0 | 104.9339 | 1060.5441 | 83.15% | 0 | 0 | 47.1871 | 75.5% | 41.9451
5468 | 1 | 0 | 0 | 3.4 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0715 | 39.3171 | 0 | 101.0715 | 959.4726 | 75.22% | 0 | 0 | 47.1871 | 75.5% | 39.3171
5469 | 0 | 0 | 0 | 3.2 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1241 | 36.9997 | 0 | 95.1241 | 864.3485 | 67.76% | 0 | 0 | 47.1871 | 75.5% | 36.9997
5470 | 0 | 0 | 0 | 1.9 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.7667 | 0 | 38.2653 | 826.0832 | 64.76% | 0 | 21.9796 | 22.8616 | 36.58% | 34.7463
5471 | 0 | 0 | 0 | 1.7 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.053 | 32.8564 | 0 | 85.053 | 741.0301 | 58.1% | 0 | 0 | 22.8616 | 36.58% | 32.8564
5472 | 0 | 0 | 0 | 1.2 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1435 | 31.635 | 0 | 82.1435 | 658.8866 | 51.66% | 0 | 0 | 22.8616 | 36.58% | 31.635
5473 | 0 | 0 | 0 | 0.3 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3198 | 30.8649 | 0 | 80.3198 | 578.5669 | 45.36% | 0 | 0 | 22.8616 | 36.58% | 30.8649
5474 | 0 | 0 | 0 | 0.3 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1491 | 30.8287 | 0 | 80.1491 | 498.4177 | 39.08% | 0 | 0 | 22.8616 | 36.58% | 30.8287
5475 | 0 | 0 | 0 | 0.7 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4011 | 31.3913 | 0 | 81.4011 | 417.0166 | 32.69% | 0 | 0 | 22.8616 | 36.58% | 31.3913
5476 | 0 | 0 | 0 | 0.7 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4099 | 31.4011 | 0 | 81.4099 | 335.6068 | 26.31% | 0 | 0 | 22.8616 | 36.58% | 31.4011
5477 | 0 | 0 | 0 | 1 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8324 | 32.9107 | 0 | 84.8324 | 250.7744 | 19.66% | 0 | 0 | 22.8616 | 36.58% | 32.9107
5478 | 33 | 12 | 8 | 1.1 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.3192 | 36.1098 | 0 | 92.3192 | 158.4552 | 12.42% | 0 | 0 | 22.8616 | 36.58% | 36.1098
5479 | 438 | 143 | 49 | 1.3 | 24.8 | 0 | 0 | 0 | 0 | 2.495 | 0 | 0 | 2.495 | 0 | 0 | 0 | 83.6785 | 32.1444 | 0 | 83.6785 | 74.7768 | 5.862% | 0 | 4.0886 | 18.3365 | 29.34% | 38.728
5480 | 674 | 347 | 75 | 1.3 | 27.7 | 0 | 0 | 0 | 0 | 12.3377 | 0 | 0 | 12.3377 | 0 | 0 | 0 | 74.7768 | 28.1326 | 0 | 74.7768 | 0 | 0% | 0 | 0 | 18.3365 | 29.34% | 40.4703
5481 | 787 | 550 | 91 | 1.1 | 30.9 | 0 | 0 | 0 | 0 | 30.9671 | 0 | 0 | 30.9671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 10.9209 | 6.25 | 10% | 41.888
5482 | 857 | 727 | 97 | 1.3 | 33.1 | 0 | 0 | 0 | 0 | 44.5374 | 1.186 | 1.4475 | 43.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 1.4475 | 0 | 7.5579 | 12.09% | 43.0899
5483 | 889 | 853 | 100 | 1.7 | 34.8 | 0 | 0 | 0 | 4.3784 | 43.2264 | 13.0329 | 0 | 43.2264 | 0 | 0 | 0 | 0 | 0 | 4.3784 | 0 | 4.3784 | 0.3433% | 0 | 0 | 7.5579 | 12.09% | 43.2264
5484 | 903 | 925 | 101 | 1.8 | 36.2 | 0 | 0 | 0 | 0 | 42.5078 | 20.0365 | 0 | 42.5078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3784 | 0.3433% | 0 | 0 | 7.5579 | 12.09% | 42.5078
5485 | 907 | 939 | 101 | 2.6 | 37 | 0 | 0 | 0 | 257.375 | 41.8268 | 24.2338 | 0 | 41.8268 | 0 | 0 | 0 | 0 | 0 | 257.375 | 0 | 261.7534 | 20.52% | 0 | 0 | 7.5579 | 12.09% | 41.8268
5486 | 906 | 896 | 96 | 4.8 | 37.3 | 0 | 0 | 0 | 254.2739 | 66.3686 | 0.10288 | 25 | 41.3686 | 0 | 0 | 0 | 0 | 0 | 254.2739 | 0 | 516.0272 | 40.46% | 25 | 0 | 30.1469 | 48.24% | 41.3686
5487 | 884 | 792 | 91 | 5.4 | 37.4 | 0 | 0 | 0 | 241.4389 | 60.5359 | 0 | 19.5879 | 40.948 | 0 | 0 | 0 | 0 | 0 | 241.4389 | 0 | 757.4661 | 59.39% | 19.5879 | 0 | 47.8457 | 76.55% | 40.948
5488 | 832 | 634 | 86 | 5.6 | 36.8 | 0 | 0 | 0 | 217.3619 | 49.7103 | 0 | 9.3013 | 40.409 | 0 | 0 | 0 | 0 | 0 | 217.3619 | 0 | 974.8281 | 76.43% | 9.3013 | 0 | 56.25 | 90% | 40.409
5489 | 744 | 441 | 77 | 5.6 | 36.1 | 0 | 0 | 0 | 178.8906 | 35.0268 | 0 | 0 | 35.0268 | 0 | 0 | 0 | 0 | 0 | 178.8906 | 0 | 1153.7187 | 90.45% | 0 | 5.2833 | 50.4028 | 80.64% | 40.3101
5490 | 576 | 233 | 59 | 4.7 | 34.6 | 0 | 0 | 0 | 0 | 15.904 | 0 | 0 | 15.904 | 0 | 0 | 0 | 70.8599 | 25.8893 | 0 | 70.8599 | 1082.8588 | 84.9% | 0 | 0 | 50.4028 | 80.64% | 41.7933
5491 | 215 | 53 | 24 | 3.2 | 33 | 0 | 0 | 0 | 0 | 1.2995 | 0 | 0 | 1.2995 | 0 | 0 | 0 | 102.2629 | 39.1402 | 0 | 102.2629 | 980.5959 | 76.88% | 0 | 0 | 50.4028 | 80.64% | 40.4396
5492 | 0 | 0 | 0 | 2.1 | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1188 | 37.8144 | 0 | 98.1188 | 882.4771 | 69.19% | 0 | 0 | 50.4028 | 80.64% | 37.8144
5493 | 0 | 0 | 0 | 0.9 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4686 | 35.6265 | 0 | 92.4686 | 790.0085 | 61.94% | 0 | 0 | 50.4028 | 80.64% | 35.6265
5494 | 0 | 0 | 0 | 1.7 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9428 | 33.4246 | 0 | 86.9428 | 703.0657 | 55.12% | 0 | 0 | 50.4028 | 80.64% | 33.4246
5495 | 0 | 0 | 0 | 0.6 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.0122 | 22.4491 | 0 | 61.0122 | 642.0535 | 50.34% | 0 | 9.328 | 40.0791 | 64.13% | 31.7771
5496 | 0 | 0 | 0 | 0.2 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.317 | 30.7437 | 0 | 80.317 | 561.7366 | 44.04% | 0 | 0 | 40.0791 | 64.13% | 30.7437
5497 | 0 | 0 | 0 | 0.5 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9823 | 30.2201 | 0 | 78.9823 | 482.7543 | 37.85% | 0 | 0 | 40.0791 | 64.13% | 30.2201
5498 | 0 | 0 | 0 | 1.2 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5158 | 30.007 | 0 | 78.5158 | 404.2384 | 31.69% | 0 | 0 | 40.0791 | 64.13% | 30.007
5499 | 0 | 0 | 0 | 1.1 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2465 | 29.9178 | 0 | 78.2465 | 325.9919 | 25.56% | 0 | 0 | 40.0791 | 64.13% | 29.9178
5500 | 0 | 0 | 0 | 1.1 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1665 | 29.4485 | 0 | 77.1665 | 248.8254 | 19.51% | 0 | 0 | 40.0791 | 64.13% | 29.4485
5501 | 0 | 0 | 0 | 1.2 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0686 | 30.2702 | 0 | 79.0686 | 169.7568 | 13.31% | 0 | 0 | 40.0791 | 64.13% | 30.2702
5502 | 44 | 12 | 8 | 1.7 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.209 | 32.5013 | 0 | 84.209 | 85.5478 | 6.707% | 0 | 0 | 40.0791 | 64.13% | 32.5013
5503 | 504 | 148 | 42 | 1 | 26.5 | 0 | 0 | 0 | 0 | 1.9826 | 0 | 0 | 1.9826 | 0 | 0 | 0 | 85.5478 | 32.8055 | 0 | 85.5478 | 0 | 0% | 0 | 0 | 40.0791 | 64.13% | 34.7881
5504 | 707 | 354 | 71 | 1.3 | 30.4 | 0 | 0 | 0 | 130.494 | 12.3964 | 0 | 0 | 12.3964 | 0 | 0 | 0 | 0 | 0 | 130.494 | 0 | 130.494 | 10.23% | 0 | 24.3861 | 13.0903 | 20.94% | 36.7824
5505 | 800 | 556 | 90 | 3.1 | 29.7 | 0 | 0 | 0 | 184.6948 | 32.1561 | 0 | 0 | 32.1561 | 0 | 0 | 0 | 0 | 0 | 184.6948 | 0 | 315.1888 | 24.71% | 0 | 6.1806 | 6.25 | 10% | 38.3367
5506 | 848 | 726 | 104 | 3.4 | 30.7 | 0 | 0 | 0 | 217.3485 | 39.5191 | 8.2946 | 0 | 39.5191 | 0 | 0 | 0 | 0 | 0 | 217.3485 | 0 | 532.5373 | 41.75% | 0 | 0 | 6.25 | 10% | 39.5191
5507 | 887 | 856 | 106 | 3.1 | 33.2 | 0 | 0 | 0 | 240.4001 | 40.3073 | 17.9596 | 0 | 40.3073 | 0 | 0 | 0 | 0 | 0 | 240.4001 | 0 | 772.9374 | 60.6% | 0 | 0 | 6.25 | 10% | 40.3073
5508 | 913 | 931 | 100 | 3.8 | 34.8 | 0 | 0 | 0 | 242.0935 | 39.5414 | 26.0242 | 0 | 39.5414 | 0 | 0 | 0 | 0 | 0 | 242.0935 | 0 | 1015.031 | 79.58% | 0 | 0 | 6.25 | 10% | 39.5414
5509 | 924 | 946 | 96 | 5.3 | 35.9 | 0 | 0 | 0 | 260.4792 | 38.9328 | 30.3734 | 0 | 38.9328 | 0 | 0 | 0 | 0 | 0 | 260.4792 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 38.9328
5510 | 924 | 906 | 92 | 7 | 36.6 | 0 | 0 | 0 | 0 | 63.3687 | 5.2075 | 25 | 38.3687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 25 | 0 | 28.839 | 46.14% | 38.3687
5511 | 896 | 799 | 90 | 6.4 | 36.6 | 0 | 0 | 0 | 0 | 56.7921 | 4.9735 | 18.7312 | 38.0609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 18.7312 | 0 | 45.7638 | 73.22% | 38.0609
5512 | 799 | 626 | 101 | 6.9 | 36.2 | 0 | 0 | 0 | 0 | 49.4867 | 0 | 11.6055 | 37.8813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 11.6055 | 0 | 56.25 | 90% | 37.8813
5513 | 701 | 430 | 89 | 6.6 | 35.3 | 0 | 0 | 0 | 0 | 34.4327 | 7.1054e-15 | 0 | 34.4327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 2.4551 | 53.5329 | 85.65% | 36.8878
5514 | 525 | 222 | 64 | 5.4 | 33.9 | 0 | 0 | 0 | 0 | 15.1478 | 0 | 0 | 15.1478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 25.8645 | 41.38% | 40.1478
5515 | 177 | 48 | 25 | 4.8 | 31.4 | 0 | 0 | 0 | 0 | 1.306 | 0 | 0 | 1.306 | 0 | 0 | 0 | 100.6077 | 38.6574 | 0 | 100.6077 | 1174.9025 | 92.11% | 0 | 0 | 25.8645 | 41.38% | 39.9633
5516 | 0 | 0 | 0 | 3 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0149 | 37.827 | 0 | 98.0149 | 1076.8876 | 84.43% | 0 | 0 | 25.8645 | 41.38% | 37.827
5517 | 0 | 0 | 0 | 1.1 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2006 | 35.6084 | 0 | 92.2006 | 984.687 | 77.2% | 0 | 0 | 25.8645 | 41.38% | 35.6084
5518 | 0 | 0 | 0 | 0.8 | 25.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.565 | 33.3299 | 0 | 86.565 | 898.122 | 70.41% | 0 | 0 | 25.8645 | 41.38% | 33.3299
5519 | 0 | 0 | 0 | 0.5 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.9883 | 31.8495 | 0 | 82.9883 | 815.1338 | 63.91% | 0 | 0 | 25.8645 | 41.38% | 31.8495
5520 | 0 | 0 | 0 | 0.7 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.1959 | 27.753 | 0 | 73.1959 | 741.9378 | 58.17% | 0 | 0 | 25.8645 | 41.38% | 27.753
5521 | 0 | 0 | 0 | 0.1 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9892 | 30.7103 | 0 | 79.9892 | 661.9486 | 51.9% | 0 | 0 | 25.8645 | 41.38% | 30.7103
5522 | 0 | 0 | 0 | 1 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0736 | 31.22 | 0 | 81.0736 | 580.875 | 45.54% | 0 | 0 | 25.8645 | 41.38% | 31.22
5523 | 0 | 0 | 0 | 1.3 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8252 | 33.6517 | 0 | 86.8252 | 494.0498 | 38.73% | 0 | 0 | 25.8645 | 41.38% | 33.6517
5524 | 0 | 0 | 0 | 1.1 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6184 | 36.139 | 0 | 92.6184 | 401.4314 | 31.47% | 0 | 0 | 25.8645 | 41.38% | 36.139
5525 | 0 | 0 | 0 | 1.4 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4691 | 39.0804 | 0 | 99.4691 | 301.9622 | 23.67% | 0 | 0 | 25.8645 | 41.38% | 39.0804
5526 | 39 | 10 | 7 | 2.1 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.8746 | 42.161 | 0 | 106.8746 | 195.0876 | 15.29% | 0 | 0 | 25.8645 | 41.38% | 42.161
5527 | 474 | 142 | 43 | 2 | 26 | 0 | 0 | 0 | 0 | 2.0464 | 0 | 0 | 2.0464 | 0 | 0 | 0 | 107.5259 | 42.2106 | 0 | 107.5259 | 87.5617 | 6.865% | 0 | 0 | 25.8645 | 41.38% | 44.257
5528 | 720 | 350 | 64 | 0.9 | 29.2 | 0 | 0 | 0 | 0 | 12.3155 | 0 | 0 | 12.3155 | 0 | 0 | 0 | 87.5617 | 33.4123 | 0 | 87.5617 | 0 | 0% | 0 | 0 | 25.8645 | 41.38% | 45.7277
5529 | 834 | 556 | 74 | 0.7 | 32.8 | 0 | 0 | 0 | 0 | 31.0367 | 0 | 0 | 31.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 15.9848 | 8.1736 | 13.08% | 47.0215
5530 | 885 | 729 | 83 | 1.9 | 34.6 | 0 | 0 | 0 | 228.3872 | 46.4588 | 0 | 0 | 46.4588 | 0 | 0 | 0 | 0 | 0 | 228.3872 | 0 | 228.3872 | 17.91% | 0 | 1.7381 | 6.25 | 10% | 48.1969
5531 | 905 | 851 | 90 | 2.3 | 35.6 | 0 | 0 | 0 | 246.1313 | 48.0034 | 9.1316 | 0 | 48.0034 | 0 | 0 | 0 | 0 | 0 | 246.1313 | 0 | 474.5186 | 37.2% | 0 | 0 | 6.25 | 10% | 48.0034
5532 | 906 | 917 | 95 | 3.7 | 36.1 | 0 | 0 | 0 | 253.276 | 64.561 | 0 | 17.5228 | 47.0382 | 0 | 0 | 0 | 0 | 0 | 253.276 | 0 | 727.7946 | 57.06% | 17.5228 | 0 | 22.0829 | 35.33% | 47.0382
5533 | 944 | 952 | 87 | 5.1 | 36.5 | 0 | 0 | 0 | 266.7066 | 46.4463 | 23.3598 | 0 | 46.4463 | 0 | 0 | 0 | 0 | 0 | 266.7066 | 0 | 994.5012 | 77.97% | 0 | 0 | 22.0829 | 35.33% | 46.4463
5534 | 955 | 912 | 77 | 5.4 | 37.1 | 0 | 0 | 0 | 268.4674 | 68.7783 | 0 | 22.8431 | 45.9352 | 0 | 0 | 0 | 0 | 0 | 268.4674 | 0 | 1262.9686 | 99.02% | 22.8431 | 0 | 42.723 | 68.36% | 45.9352
5535 | 940 | 809 | 72 | 5.3 | 37.4 | 0 | 0 | 0 | 12.5416 | 59.8823 | 2.6754 | 14.9708 | 44.9116 | 0 | 0 | 0 | 0 | 0 | 12.5416 | 0 | 1275.5102 | 100% | 14.9708 | 0 | 56.25 | 90% | 44.9116
5536 | 908 | 656 | 66 | 5.4 | 35.9 | 0 | 0 | 0 | 0 | 44.0648 | 8.2533 | 0 | 44.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 44.0648
5537 | 768 | 439 | 70 | 5.4 | 33.8 | 0 | 0 | 0 | 0 | 35.6651 | 0 | 0 | 35.6651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 8.1184 | 47.2651 | 75.62% | 43.7835
5538 | 578 | 224 | 55 | 5.2 | 32.2 | 0 | 0 | 0 | 0 | 15.7888 | 0 | 0 | 15.7888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 19.5968 | 31.35% | 40.7888
5539 | 189 | 46 | 22 | 5 | 29.1 | 0 | 0 | 0 | 0 | 1.1568 | 0 | 0 | 1.1568 | 0 | 0 | 0 | 107.4677 | 41.8314 | 0 | 107.4677 | 1168.0425 | 91.57% | 0 | 0 | 19.5968 | 31.35% | 42.9883
5540 | 0 | 0 | 0 | 4.2 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.3504 | 39.9132 | 0 | 102.3504 | 1065.692 | 83.55% | 0 | 0 | 19.5968 | 31.35% | 39.9132
5541 | 0 | 0 | 0 | 5 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8662 | 37.3952 | 0 | 95.8662 | 969.8259 | 76.03% | 0 | 0 | 19.5968 | 31.35% | 37.3952
5542 | 0 | 0 | 0 | 4.3 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.3426 | 35.1251 | 0 | 90.3426 | 879.4833 | 68.95% | 0 | 0 | 19.5968 | 31.35% | 35.1251
5543 | 0 | 0 | 0 | 4.1 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6664 | 33.5904 | 0 | 86.6664 | 792.8169 | 62.16% | 0 | 0 | 19.5968 | 31.35% | 33.5904
5544 | 0 | 0 | 0 | 2.2 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9248 | 32.8885 | 0 | 84.9248 | 707.8921 | 55.5% | 0 | 0 | 19.5968 | 31.35% | 32.8885
5545 | 0 | 0 | 0 | 2.4 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9175 | 32.4679 | 0 | 83.9175 | 623.9745 | 48.92% | 0 | 0 | 19.5968 | 31.35% | 32.4679
5546 | 0 | 0 | 0 | 2.3 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4877 | 32.738 | 0 | 84.4877 | 539.4868 | 42.3% | 0 | 0 | 19.5968 | 31.35% | 32.738
5547 | 0 | 0 | 0 | 1.8 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.5188 | 44.4563 | 0 | 111.5188 | 427.968 | 33.55% | 9.5428 | 0 | 28.2193 | 45.15% | 34.9134
5548 | 0 | 0 | 0 | 1.6 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6061 | 37.1807 | 0 | 94.6061 | 333.3619 | 26.14% | 0 | 0 | 28.2193 | 45.15% | 37.1807
5549 | 0 | 0 | 0 | 1.8 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0712 | 39.5915 | 0 | 100.0712 | 233.2907 | 18.29% | 0 | 0 | 28.2193 | 45.15% | 39.5915
5550 | 40 | 10 | 7 | 2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.389 | 0 | 127.551 | 105.7397 | 8.29% | 9.0121 | 0 | 36.3622 | 58.18% | 42.3769
5551 | 450 | 140 | 48 | 1.7 | 22 | 0 | 0 | 0 | 0 | 2.4282 | 0 | 0 | 2.4282 | 0 | 0 | 0 | 105.7397 | 41.8233 | 0 | 105.7397 | 0 | 0% | 0 | 0 | 36.3622 | 58.18% | 44.2514
5552 | 658 | 345 | 85 | 3.4 | 24.1 | 0 | 0 | 0 | 0 | 13.369 | 0 | 0 | 13.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 13.6477 | 21.2578 | 34.01% | 27.0167
5553 | 785 | 551 | 99 | 4 | 25.6 | 0 | 0 | 0 | 0 | 33.1379 | 0 | 0 | 33.1379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 13.5605 | 6.25 | 10% | 46.6984
5554 | 864 | 727 | 100 | 3.7 | 27.4 | 0 | 0 | 0 | 31.4742 | 47.4017 | 1.7866 | 0 | 47.4017 | 0 | 0 | 0 | 0 | 0 | 31.4742 | 0 | 31.4742 | 2.468% | 0 | 0 | 6.25 | 10% | 47.4017
5555 | 898 | 857 | 103 | 3.6 | 29.2 | 0 | 0 | 0 | 243.2997 | 55.5752 | 4.5048 | 9.0244 | 46.5508 | 0 | 0 | 0 | 0 | 0 | 243.2997 | 0 | 274.7739 | 21.54% | 9.0244 | 0 | 14.4041 | 23.05% | 46.5508
5556 | 905 | 932 | 114 | 3.2 | 30.8 | 0 | 0 | 0 | 253.3303 | 66.6598 | 0 | 21.3123 | 45.3475 | 0 | 0 | 0 | 0 | 0 | 253.3303 | 0 | 528.1042 | 41.4% | 21.3123 | 0 | 33.661 | 53.86% | 45.3475
5557 | 862 | 946 | 156 | 4 | 31.8 | 0 | 0 | 0 | 242.7386 | 69.6874 | 0.61524 | 25 | 44.6874 | 0 | 0 | 0 | 0 | 0 | 242.7386 | 0 | 770.8428 | 60.43% | 25 | 0 | 56.25 | 90% | 44.6874
5558 | 752 | 903 | 242 | 4.9 | 32.2 | 0 | 0 | 0 | 207.4399 | 44.2696 | 24.5765 | 0 | 44.2696 | 0 | 0 | 0 | 0 | 0 | 207.4399 | 0 | 978.2827 | 76.7% | 0 | 0 | 56.25 | 90% | 44.2696
5559 | 469 | 636 | 259 | 6.7 | 31 | 0 | 0 | 0 | 117.4745 | 43.4144 | 5.8618 | 0 | 43.4144 | 0 | 0 | 0 | 0 | 0 | 117.4745 | 0 | 1095.7572 | 85.91% | 0 | 0 | 56.25 | 90% | 43.4144
5560 | 514 | 618 | 282 | 6.1 | 30.6 | 0 | 0 | 0 | 126.0609 | 42.5774 | 5.3662 | 0 | 42.5774 | 0 | 0 | 0 | 0 | 0 | 126.0609 | 0 | 1221.8182 | 95.79% | 0 | 0 | 56.25 | 90% | 42.5774
5561 | 281 | 302 | 154 | 6.3 | 29.5 | 0 | 0 | 0 | 53.692 | 21.9146 | 0 | 0 | 21.9146 | 0 | 0 | 0 | 0 | 0 | 53.692 | 0 | 1275.5102 | 100% | 0 | 20.5876 | 33.465 | 53.54% | 42.5022
5562 | 161 | 143 | 99 | 6.1 | 28 | 0 | 0 | 0 | 0 | 9.7194 | 0 | 0 | 9.7194 | 0 | 0 | 0 | 89.1406 | 34.1964 | 0 | 89.1406 | 1186.3696 | 93.01% | 0 | 0 | 33.465 | 53.54% | 43.9158
5563 | 88 | 39 | 27 | 6.3 | 26.5 | 0 | 0 | 0 | 0 | 1.357 | 0 | 0 | 1.357 | 0 | 0 | 0 | 103.312 | 40.3639 | 0 | 103.312 | 1083.0577 | 84.91% | 0 | 0 | 33.465 | 53.54% | 41.7209
5564 | 0 | 0 | 0 | 5.5 | 25.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3176 | 38.7991 | 0 | 99.3176 | 983.7401 | 77.13% | 0 | 0 | 33.465 | 53.54% | 38.7991
5565 | 0 | 0 | 0 | 5.2 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5906 | 36.3967 | 0 | 93.5906 | 890.1494 | 69.79% | 0 | 0 | 33.465 | 53.54% | 36.3967
5566 | 0 | 0 | 0 | 4.4 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.62 | 34.2798 | 0 | 88.62 | 801.5295 | 62.84% | 0 | 0 | 33.465 | 53.54% | 34.2798
5567 | 0 | 0 | 0 | 4.4 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2589 | 40.1481 | 0 | 102.2589 | 699.2706 | 54.82% | 7.3139 | 0 | 40.0736 | 64.12% | 32.8341
5568 | 0 | 0 | 0 | 3.8 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 699.2706 | 54.82% | 0 | 25 | 12.4052 | 19.85% | 25
5569 | 0 | 0 | 0 | 3.1 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 699.2706 | 54.82% | 0 | 5.5616 | 6.25 | 10% | 5.5616
5570 | 0 | 0 | 0 | 3.1 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.949 | 32.3551 | 0 | 83.949 | 615.3216 | 48.24% | 0 | 0 | 6.25 | 10% | 32.3551
5571 | 0 | 0 | 0 | 3 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9124 | 34.5263 | 0 | 88.9124 | 526.4092 | 41.27% | 0 | 0 | 6.25 | 10% | 34.5263
5572 | 0 | 0 | 0 | 3.3 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1881 | 36.7588 | 0 | 94.1881 | 432.2212 | 33.89% | 0 | 0 | 6.25 | 10% | 36.7588
5573 | 0 | 0 | 0 | 3.2 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3272 | 39.0275 | 0 | 99.3272 | 332.8939 | 26.1% | 0 | 0 | 6.25 | 10% | 39.0275
5574 | 1 | 7 | 7 | 2.7 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.469 | 41.6903 | 0 | 105.469 | 227.425 | 17.83% | 0 | 0 | 6.25 | 10% | 41.6903
5575 | 132 | 96 | 63 | 3.8 | 23.2 | 0 | 0 | 0 | 0 | 2.4341 | 0 | 0 | 2.4341 | 0 | 0 | 0 | 104.1348 | 41.0319 | 0 | 104.1348 | 123.2902 | 9.666% | 0 | 0 | 6.25 | 10% | 43.466
5576 | 418 | 306 | 144 | 5 | 25.4 | 0 | 0 | 0 | 0 | 14.0473 | 0 | 0 | 14.0473 | 0 | 0 | 0 | 79.934 | 30.5007 | 0 | 79.934 | 43.3562 | 3.399% | 0 | 0 | 6.25 | 10% | 44.5481
5577 | 479 | 499 | 222 | 6.6 | 26.2 | 0 | 0 | 0 | 0 | 31.1485 | 0 | 0 | 31.1485 | 0 | 0 | 0 | 43.3562 | 14.8647 | 0 | 43.3562 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.0132
5578 | 727 | 724 | 194 | 6.9 | 27.2 | 0 | 0 | 0 | 180.6689 | 46.8098 | 3.4231 | 0 | 46.8098 | 0 | 0 | 0 | 0 | 0 | 180.6689 | 0 | 180.6689 | 14.16% | 0 | 0 | 6.25 | 10% | 46.8098
5579 | 664 | 821 | 260 | 8.5 | 27.2 | 0 | 0 | 0 | 170.8224 | 46.5619 | 13.5057 | 0 | 46.5619 | 0 | 0 | 0 | 0 | 0 | 170.8224 | 0 | 351.4913 | 27.56% | 0 | 0 | 6.25 | 10% | 46.5619
5580 | 638 | 856 | 273 | 8.4 | 27.4 | 0 | 0 | 0 | 168.7361 | 45.6692 | 18.9493 | 0 | 45.6692 | 0 | 0 | 0 | 0 | 0 | 168.7361 | 0 | 520.2274 | 40.79% | 0 | 0 | 6.25 | 10% | 45.6692
5581 | 760 | 913 | 212 | 8.7 | 27.7 | 0 | 0 | 0 | 207.4755 | 54.5095 | 16.5711 | 9.1272 | 45.3823 | 0 | 0 | 0 | 0 | 0 | 207.4755 | 0 | 727.7029 | 57.05% | 9.1272 | 0 | 14.497 | 23.2% | 45.3823
5582 | 753 | 869 | 207 | 8.5 | 28.2 | 0 | 0 | 0 | 204.5092 | 69.0747 | 0 | 24.1854 | 44.8893 | 0 | 0 | 0 | 0 | 0 | 204.5092 | 0 | 932.2122 | 73.09% | 24.1854 | 0 | 36.3499 | 58.16% | 44.8893
5583 | 689 | 747 | 204 | 8.7 | 28 | 0 | 0 | 0 | 180.6137 | 60.4993 | 0 | 16.2047 | 44.2946 | 0 | 0 | 0 | 0 | 0 | 180.6137 | 0 | 1112.8258 | 87.25% | 16.2047 | 0 | 50.9918 | 81.59% | 44.2946
5584 | 639 | 599 | 184 | 8.7 | 27.2 | 0 | 0 | 0 | 159.4757 | 49.3202 | 0 | 5.8194 | 43.5008 | 0 | 0 | 0 | 0 | 0 | 159.4757 | 0 | 1272.3016 | 99.75% | 5.8194 | 0 | 56.25 | 90% | 43.5008
5585 | 558 | 410 | 142 | 8.6 | 26.2 | 0 | 0 | 0 | 3.2086 | 33.7549 | 0 | 0 | 33.7549 | 0 | 0 | 0 | 0 | 0 | 3.2086 | 0 | 1275.5102 | 100% | 0 | 9.349 | 45.9032 | 73.45% | 43.1039
5586 | 210 | 174 | 107 | 7.7 | 24.8 | 0 | 0 | 0 | 0 | 11.4654 | 0 | 0 | 11.4654 | 0 | 0 | 0 | 38.2653 | 12.7405 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 20.2044 | 23.5423 | 37.67% | 44.4102
5587 | 0 | 18 | 18 | 6.8 | 23.5 | 0 | 0 | 0 | 0 | 0.70605 | 0 | 0 | 0.70605 | 0 | 0 | 0 | 104.8882 | 41.3282 | 0 | 104.8882 | 1132.3567 | 88.78% | 0 | 0 | 23.5423 | 37.67% | 42.0343
5588 | 0 | 0 | 0 | 6.3 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.9637 | 39.2517 | 0 | 99.9637 | 1032.393 | 80.94% | 0 | 0 | 23.5423 | 37.67% | 39.2517
5589 | 0 | 0 | 0 | 4.4 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1754 | 36.8075 | 0 | 94.1754 | 938.2176 | 73.56% | 0 | 0 | 23.5423 | 37.67% | 36.8075
5590 | 0 | 0 | 0 | 3.5 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4095 | 34.7965 | 0 | 89.4095 | 848.8081 | 66.55% | 0 | 0 | 23.5423 | 37.67% | 34.7965
5591 | 0 | 0 | 0 | 2.8 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6158 | 33.1921 | 0 | 85.6158 | 763.1923 | 59.83% | 0 | 0 | 23.5423 | 37.67% | 33.1921
5592 | 0 | 0 | 0 | 3.3 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.9759 | 26.5049 | 0 | 69.9759 | 693.2164 | 54.35% | 0 | 0 | 23.5423 | 37.67% | 26.5049
5593 | 0 | 0 | 0 | 3.7 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.8448 | 0 | 38.2653 | 654.9511 | 51.35% | 0 | 0 | 23.5423 | 37.67% | 12.8448
5594 | 0 | 0 | 0 | 3.8 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5178 | 32.3676 | 0 | 83.5178 | 571.4334 | 44.8% | 0 | 0 | 23.5423 | 37.67% | 32.3676
5595 | 0 | 0 | 0 | 1.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1974 | 34.4093 | 0 | 88.1974 | 483.2359 | 37.89% | 0 | 0 | 23.5423 | 37.67% | 34.4093
5596 | 0 | 0 | 0 | 0.8 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1054 | 36.5331 | 0 | 93.1054 | 390.1306 | 30.59% | 0 | 0 | 23.5423 | 37.67% | 36.5331
5597 | 0 | 0 | 0 | 1 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6647 | 38.9648 | 0 | 98.6647 | 291.4659 | 22.85% | 0 | 0 | 23.5423 | 37.67% | 38.9648
5598 | 26 | 9 | 7 | 1.6 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8815 | 42.0886 | 0 | 105.8815 | 185.5843 | 14.55% | 0 | 0 | 23.5423 | 37.67% | 42.0886
5599 | 382 | 129 | 50 | 1.8 | 21 | 0 | 0 | 0 | 0 | 2.1151 | 0 | 0 | 2.1151 | 0 | 0 | 0 | 105.5337 | 41.8146 | 0 | 105.5337 | 80.0507 | 6.276% | 0 | 0 | 23.5423 | 37.67% | 43.9297
5600 | 645 | 332 | 80 | 3.1 | 23.6 | 0 | 0 | 0 | 0 | 13.0649 | 0 | 0 | 13.0649 | 0 | 0 | 0 | 80.0507 | 30.6778 | 0 | 80.0507 | 0 | 0% | 0 | 1.7705 | 21.5828 | 34.53% | 45.5132
5601 | 775 | 535 | 94 | 5.6 | 25.5 | 0 | 0 | 0 | 0 | 32.9626 | 0 | 0 | 32.9626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 13.8541 | 6.25 | 10% | 46.8168
5602 | 839 | 708 | 103 | 5.6 | 26.6 | 0 | 0 | 0 | 0 | 47.8557 | 1.3221 | 0 | 47.8557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 47.8557
5603 | 860 | 835 | 117 | 5.5 | 27.7 | 0 | 0 | 0 | 230.465 | 47.2959 | 13.0396 | 0 | 47.2959 | 0 | 0 | 0 | 0 | 0 | 230.465 | 0 | 230.465 | 18.07% | 0 | 0 | 6.25 | 10% | 47.2959
5604 | 873 | 911 | 126 | 6.5 | 28 | 0 | 0 | 0 | 240.8765 | 46.1539 | 22.1078 | 0 | 46.1539 | 0 | 0 | 0 | 0 | 0 | 240.8765 | 0 | 471.3416 | 36.95% | 0 | 0 | 6.25 | 10% | 46.1539
5605 | 892 | 925 | 112 | 7.1 | 28.7 | 0 | 0 | 0 | 0 | 51.2761 | 20.0086 | 5.5763 | 45.6998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471.3416 | 36.95% | 5.5763 | 0 | 11.2885 | 18.06% | 45.6998
5606 | 884 | 877 | 109 | 7.2 | 29.1 | 0 | 0 | 0 | 203.9928 | 69.3838 | 0 | 24.1603 | 45.2235 | 0 | 0 | 0 | 0 | 0 | 203.9928 | 0 | 675.3343 | 52.95% | 24.1603 | 0 | 33.1188 | 52.99% | 45.2235
5607 | 850 | 769 | 108 | 7.8 | 29.1 | 0 | 0 | 0 | 228.8022 | 62.5237 | 0 | 17.9074 | 44.6163 | 0 | 0 | 0 | 0 | 0 | 228.8022 | 0 | 904.1365 | 70.88% | 17.9074 | 0 | 49.2992 | 78.88% | 44.6163
5608 | 798 | 612 | 102 | 7.7 | 28.5 | 0 | 0 | 0 | 205.4733 | 51.4817 | 0 | 7.6927 | 43.7891 | 0 | 0 | 0 | 0 | 0 | 205.4733 | 0 | 1109.6098 | 86.99% | 7.6927 | 0 | 56.25 | 90% | 43.7891
5609 | 708 | 420 | 88 | 7.7 | 27.5 | 0 | 0 | 0 | 165.9004 | 35.7584 | 0 | 0 | 35.7584 | 0 | 0 | 0 | 0 | 0 | 165.9004 | 0 | 1275.5102 | 100% | 0 | 7.6407 | 47.7938 | 76.47% | 43.3991
5610 | 529 | 212 | 63 | 7.2 | 26.4 | 0 | 0 | 0 | 0 | 15.5789 | 0 | 0 | 15.5789 | 0 | 0 | 0 | 38.2653 | 12.6905 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 16.5642 | 29.4616 | 47.14% | 44.8336
5611 | 134 | 38 | 22 | 6.3 | 24.9 | 0 | 0 | 0 | 0 | 1.0874 | 0 | 0 | 1.0874 | 0 | 0 | 0 | 58.0336 | 21.182 | 0 | 58.0336 | 1179.2113 | 92.45% | 0 | 20.2747 | 7.023 | 11.24% | 42.544
5612 | 0 | 0 | 0 | 5.1 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6945 | 39.5567 | 0 | 100.6945 | 1078.5168 | 84.56% | 0 | 0 | 7.023 | 11.24% | 39.5567
5613 | 0 | 0 | 0 | 4.5 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8808 | 37.1626 | 0 | 94.8808 | 983.6361 | 77.12% | 0 | 0 | 7.023 | 11.24% | 37.1626
5614 | 0 | 0 | 0 | 3.7 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.5761 | 34.9288 | 0 | 89.5761 | 894.06 | 70.09% | 0 | 0 | 7.023 | 11.24% | 34.9288
5615 | 0 | 0 | 0 | 3.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8499 | 33.3369 | 0 | 85.8499 | 808.2101 | 63.36% | 0 | 0 | 7.023 | 11.24% | 33.3369
5616 | 0 | 0 | 0 | 2.8 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.4025 | 28.0354 | 0 | 73.4025 | 734.8076 | 57.61% | 0 | 0 | 7.023 | 11.24% | 28.0354
5617 | 0 | 0 | 0 | 1.7 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.8825 | 0 | 38.2653 | 696.5423 | 54.61% | 0 | 0 | 7.023 | 11.24% | 12.8825
5618 | 0 | 0 | 0 | 1 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3397 | 32.3565 | 0 | 83.3397 | 613.2026 | 48.08% | 0 | 0 | 7.023 | 11.24% | 32.3565
5619 | 0 | 0 | 0 | 1.3 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9629 | 34.3703 | 0 | 87.9629 | 525.2397 | 41.18% | 0 | 0 | 7.023 | 11.24% | 34.3703
5620 | 0 | 0 | 0 | 1.1 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6631 | 36.4189 | 0 | 92.6631 | 432.5766 | 33.91% | 0 | 0 | 7.023 | 11.24% | 36.4189
5621 | 0 | 0 | 0 | 1.9 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.7676 | 38.6723 | 0 | 97.7676 | 334.809 | 26.25% | 0 | 0 | 7.023 | 11.24% | 38.6723
5622 | 43 | 9 | 6 | 1.6 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3753 | 41.9354 | 0 | 105.3753 | 229.4337 | 17.99% | 0 | 0 | 7.023 | 11.24% | 41.9354
5623 | 493 | 137 | 39 | 1.9 | 20.7 | 0 | 0 | 0 | 0 | 1.7438 | 0 | 0 | 1.7438 | 0 | 0 | 0 | 106.6587 | 42.3224 | 0 | 106.6587 | 122.775 | 9.626% | 0 | 0 | 7.023 | 11.24% | 44.0662
5624 | 727 | 343 | 62 | 3.6 | 24.1 | 0 | 0 | 0 | 0 | 13.0169 | 0 | 0 | 13.0169 | 0 | 0 | 0 | 84.5097 | 32.552 | 0 | 84.5097 | 38.2653 | 3% | 0 | 0 | 7.023 | 11.24% | 45.5689
5625 | 833 | 547 | 75 | 5.8 | 26.1 | 0 | 0 | 0 | 0 | 33.5783 | 0 | 0 | 33.5783 | 0 | 0 | 0 | 38.2653 | 12.7002 | 0 | 38.2653 | 0 | 0% | 0 | 0.69846 | 6.25 | 10% | 46.9769
5626 | 892 | 722 | 81 | 6 | 27.3 | 0 | 0 | 0 | 0 | 47.9867 | 1.9788 | 0 | 47.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 47.9867
5627 | 917 | 851 | 88 | 5.7 | 28.3 | 0 | 0 | 0 | 247.1623 | 47.4115 | 14.2466 | 0 | 47.4115 | 0 | 0 | 0 | 0 | 0 | 247.1623 | 0 | 247.1623 | 19.38% | 0 | 0 | 6.25 | 10% | 47.4115
5628 | 924 | 923 | 95 | 6.4 | 28.9 | 0 | 0 | 0 | 0 | 46.1246 | 23.15 | 0 | 46.1246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247.1623 | 19.38% | 0 | 0 | 6.25 | 10% | 46.1246
5629 | 927 | 936 | 95 | 6.7 | 29.5 | 0 | 0 | 0 | 120.3733 | 50.4182 | 21.5818 | 4.8144 | 45.6038 | 0 | 0 | 0 | 0 | 0 | 120.3733 | 0 | 367.5356 | 28.81% | 4.8144 | 0 | 10.6001 | 16.96% | 45.6038
5630 | 915 | 885 | 94 | 6.7 | 29.8 | 0 | 0 | 0 | 255.1424 | 70.1149 | 0 | 24.8398 | 45.2751 | 0 | 0 | 0 | 0 | 0 | 255.1424 | 0 | 622.678 | 48.82% | 24.8398 | 0 | 33.0444 | 52.87% | 45.2751
5631 | 882 | 774 | 92 | 6.7 | 30 | 0 | 0 | 0 | 239.3032 | 62.9275 | 0 | 18.4045 | 44.523 | 0 | 0 | 0 | 0 | 0 | 239.3032 | 0 | 861.9812 | 67.58% | 18.4045 | 0 | 49.674 | 79.48% | 44.523
5632 | 811 | 609 | 92 | 7.3 | 29.1 | 0 | 0 | 0 | 209.3599 | 50.9904 | 0 | 7.2779 | 43.7125 | 0 | 0 | 0 | 0 | 0 | 209.3599 | 0 | 1071.3411 | 83.99% | 7.2779 | 0 | 56.25 | 90% | 43.7125
5633 | 697 | 412 | 87 | 7.4 | 28.2 | 0 | 0 | 0 | 162.9279 | 35.1386 | 0 | 0 | 35.1386 | 0 | 0 | 0 | 0 | 0 | 162.9279 | 0 | 1234.269 | 96.77% | 0 | 8.0837 | 47.3035 | 75.69% | 43.2222
5634 | 501 | 203 | 64 | 7.7 | 26.8 | 0 | 0 | 0 | 0 | 15.0256 | 0 | 0 | 15.0256 | 0 | 0 | 0 | 38.2653 | 12.6773 | 0 | 38.2653 | 1196.0037 | 93.77% | 0 | 16.724 | 28.7945 | 46.07% | 44.4269
5635 | 132 | 37 | 21 | 5.6 | 25.4 | 0 | 0 | 0 | 0 | 1.0167 | 0 | 0 | 1.0167 | 0 | 0 | 0 | 75.7727 | 28.7253 | 0 | 75.7727 | 1120.2309 | 87.83% | 0 | 12.1642 | 15.332 | 24.53% | 41.9062
5636 | 0 | 0 | 0 | 3.9 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5429 | 39.0205 | 0 | 99.5429 | 1020.6881 | 80.02% | 0 | 0 | 15.332 | 24.53% | 39.0205
5637 | 0 | 0 | 0 | 3.7 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.63 | 37.0178 | 0 | 94.63 | 926.0581 | 72.6% | 0 | 0 | 15.332 | 24.53% | 37.0178
5638 | 0 | 0 | 0 | 3.8 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.085 | 35.1279 | 0 | 90.085 | 835.9731 | 65.54% | 0 | 0 | 15.332 | 24.53% | 35.1279
5639 | 0 | 0 | 0 | 3 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7677 | 33.3077 | 0 | 85.7677 | 750.2054 | 58.82% | 0 | 0 | 15.332 | 24.53% | 33.3077
5640 | 0 | 0 | 0 | 1.4 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1144 | 32.1879 | 0 | 83.1144 | 667.091 | 52.3% | 0 | 0 | 15.332 | 24.53% | 32.1879
5641 | 0 | 0 | 0 | 1 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2376 | 31.3955 | 0 | 81.2376 | 585.8534 | 45.93% | 0 | 0 | 15.332 | 24.53% | 31.3955
5642 | 0 | 0 | 0 | 1.2 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.1073 | 30.9498 | 0 | 80.1073 | 505.7462 | 39.65% | 0 | 0 | 15.332 | 24.53% | 30.9498
5643 | 0 | 0 | 0 | 1.1 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1928 | 31.4289 | 0 | 81.1928 | 424.5533 | 33.28% | 0 | 0 | 15.332 | 24.53% | 31.4289
5644 | 0 | 0 | 0 | 2.4 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9842 | 31.7339 | 0 | 81.9842 | 342.5692 | 26.86% | 0 | 0 | 15.332 | 24.53% | 31.7339
5645 | 0 | 0 | 0 | 1.7 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0321 | 33.0876 | 0 | 85.0321 | 257.5371 | 20.19% | 0 | 0 | 15.332 | 24.53% | 33.0876
5646 | 36 | 9 | 6 | 1.7 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2189 | 36.2156 | 0 | 92.2189 | 165.3182 | 12.96% | 0 | 0 | 15.332 | 24.53% | 36.2156
5647 | 443 | 132 | 45 | 1.9 | 20.3 | 0 | 0 | 0 | 0 | 2.1129 | 0 | 0 | 2.1129 | 0 | 0 | 0 | 93.6674 | 36.7502 | 0 | 93.6674 | 71.6508 | 5.617% | 0 | 0 | 15.332 | 24.53% | 38.8631
5648 | 680 | 336 | 73 | 4.3 | 23 | 0 | 0 | 0 | 0 | 13.2659 | 0 | 0 | 13.2659 | 0 | 0 | 0 | 71.6508 | 27.1139 | 0 | 71.6508 | 0 | 0% | 0 | 0 | 15.332 | 24.53% | 40.3798
5649 | 794 | 538 | 88 | 5 | 25 | 0 | 0 | 0 | 0 | 33.409 | 0 | 0 | 33.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 8.2061 | 6.25 | 10% | 41.6151
5650 | 861 | 715 | 96 | 6.7 | 26.8 | 0 | 0 | 0 | 0 | 42.615 | 7.2914 | 0 | 42.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 42.615
5651 | 894 | 845 | 101 | 6.5 | 27.9 | 0 | 0 | 0 | 0 | 42.466 | 19.2472 | 0 | 42.466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 42.466
5652 | 906 | 917 | 105 | 6.1 | 28.4 | 0 | 0 | 0 | 191.3867 | 41.5566 | 27.3722 | 0 | 41.5566 | 0 | 0 | 0 | 0 | 0 | 191.3867 | 0 | 191.3867 | 15% | 0 | 0 | 6.25 | 10% | 41.5566
5653 | 910 | 929 | 103 | 6.1 | 29.4 | 0 | 0 | 0 | 255.4596 | 40.6708 | 30.8197 | 0 | 40.6708 | 0 | 0 | 0 | 0 | 0 | 255.4596 | 0 | 446.8463 | 35.03% | 0 | 0 | 6.25 | 10% | 40.6708
5654 | 891 | 874 | 103 | 5.6 | 29.7 | 0 | 0 | 0 | 248.9076 | 65.182 | 3.6367 | 25 | 40.182 | 0 | 0 | 0 | 0 | 0 | 248.9076 | 0 | 695.754 | 54.55% | 25 | 0 | 28.839 | 46.14% | 40.182
5655 | 850 | 762 | 106 | 5.7 | 29.8 | 0 | 0 | 0 | 230.5688 | 61.7356 | 0 | 21.899 | 39.8366 | 0 | 0 | 0 | 0 | 0 | 230.5688 | 0 | 926.3228 | 72.62% | 21.899 | 0 | 48.6261 | 77.8% | 39.8366
5656 | 780 | 600 | 104 | 6.2 | 29.3 | 0 | 0 | 0 | 201.4201 | 48.057 | 2.2793 | 8.4376 | 39.6193 | 0 | 0 | 0 | 0 | 0 | 201.4201 | 0 | 1127.7429 | 88.42% | 8.4376 | 0 | 56.25 | 90% | 39.6193
5657 | 672 | 404 | 92 | 5.8 | 28.3 | 0 | 0 | 0 | 0 | 34.3503 | 0 | 0 | 34.3503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.7429 | 88.42% | 0 | 5.4417 | 50.2274 | 80.36% | 39.792
5658 | 482 | 196 | 64 | 5.5 | 27.3 | 0 | 0 | 0 | 0 | 14.5384 | 0 | 0 | 14.5384 | 0 | 0 | 0 | 42.8548 | 14.6092 | 0 | 42.8548 | 1084.8881 | 85.06% | 0 | 12.2181 | 36.7052 | 58.73% | 41.3658
5659 | 112 | 33 | 19 | 4.9 | 25.7 | 0 | 0 | 0 | 0 | 0.86581 | 0 | 0 | 0.86581 | 0 | 0 | 0 | 98.7554 | 38.5029 | 0 | 98.7554 | 986.1327 | 77.31% | 0 | 0 | 36.7052 | 58.73% | 39.3687
5660 | 0 | 0 | 0 | 3.8 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2606 | 37.178 | 0 | 95.2606 | 890.8721 | 69.84% | 0 | 0 | 36.7052 | 58.73% | 37.178
5661 | 0 | 0 | 0 | 4 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.222 | 35.1028 | 0 | 90.222 | 800.6501 | 62.77% | 0 | 0 | 36.7052 | 58.73% | 35.1028
5662 | 0 | 0 | 0 | 2.6 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.254 | 33.0236 | 0 | 85.254 | 715.3961 | 56.09% | 0 | 0 | 36.7052 | 58.73% | 33.0236
5663 | 0 | 0 | 0 | 1.8 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5738 | 31.4596 | 0 | 81.5738 | 633.8223 | 49.69% | 0 | 0 | 36.7052 | 58.73% | 31.4596
5664 | 0 | 0 | 0 | 1.4 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3793 | 30.5613 | 0 | 79.3793 | 554.443 | 43.47% | 0 | 0 | 36.7052 | 58.73% | 30.5613
5665 | 0 | 0 | 0 | 1.9 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6282 | 29.8176 | 0 | 77.6282 | 476.8149 | 37.38% | 0 | 0 | 36.7052 | 58.73% | 29.8176
5666 | 0 | 0 | 0 | 2.2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9291 | 29.5474 | 0 | 76.9291 | 399.8858 | 31.35% | 0 | 0 | 36.7052 | 58.73% | 29.5474
5667 | 0 | 0 | 0 | 2.2 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3897 | 29.7563 | 0 | 77.3897 | 322.4961 | 25.28% | 0 | 0 | 36.7052 | 58.73% | 29.7563
5668 | 0 | 0 | 0 | 1.7 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.644 | 29.4443 | 0 | 76.644 | 245.852 | 19.27% | 0 | 0 | 36.7052 | 58.73% | 29.4443
5669 | 0 | 0 | 0 | 1.7 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8839 | 29.9944 | 0 | 77.8839 | 167.9682 | 13.17% | 0 | 0 | 36.7052 | 58.73% | 29.9944
5670 | 33 | 8 | 5 | 2.3 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2632 | 32.3286 | 0 | 83.2632 | 84.705 | 6.641% | 0 | 0 | 36.7052 | 58.73% | 32.3286
5671 | 456 | 129 | 41 | 1.3 | 20.9 | 0 | 0 | 0 | 0 | 1.785 | 0 | 0 | 1.785 | 0 | 0 | 0 | 84.705 | 32.8499 | 0 | 84.705 | 0 | 0% | 0 | 0 | 36.7052 | 58.73% | 34.6349
5672 | 695 | 334 | 67 | 2.4 | 23 | 0 | 0 | 0 | 0 | 13.0612 | 0 | 0 | 13.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 23.412 | 10.7944 | 17.27% | 36.4733
5673 | 809 | 538 | 81 | 4.7 | 25.2 | 0 | 0 | 0 | 0 | 33.4688 | 0 | 0 | 33.4688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 4.1061 | 6.25 | 10% | 37.5749
5674 | 865 | 711 | 91 | 5.7 | 26.8 | 0 | 0 | 0 | 219.7849 | 38.7865 | 10.877 | 0 | 38.7865 | 0 | 0 | 0 | 0 | 0 | 219.7849 | 0 | 219.7849 | 17.23% | 0 | 0 | 6.25 | 10% | 38.7865
5675 | 886 | 838 | 101 | 6.4 | 27.9 | 0 | 0 | 0 | 237.431 | 39.3283 | 22.0157 | 0 | 39.3283 | 0 | 0 | 0 | 0 | 0 | 237.431 | 0 | 457.2159 | 35.85% | 0 | 0 | 6.25 | 10% | 39.3283
5676 | 883 | 906 | 114 | 6.2 | 28.7 | 0 | 0 | 0 | 244.1844 | 38.4732 | 29.684 | 0 | 38.4732 | 0 | 0 | 0 | 0 | 0 | 244.1844 | 0 | 701.4003 | 54.99% | 0 | 0 | 6.25 | 10% | 38.4732
5677 | 876 | 915 | 120 | 5.8 | 28.9 | 0 | 0 | 0 | 245.4647 | 43.6864 | 26.7869 | 5.9472 | 37.7392 | 0 | 0 | 0 | 0 | 0 | 245.4647 | 0 | 946.865 | 74.23% | 5.9472 | 0 | 11.6237 | 18.6% | 37.7392
5678 | 849 | 860 | 126 | 6.2 | 29.3 | 0 | 0 | 0 | 122.7617 | 62.2225 | 5.8407 | 25 | 37.2225 | 0 | 0 | 0 | 0 | 0 | 122.7617 | 0 | 1069.6267 | 83.86% | 25 | 0 | 34.2127 | 54.74% | 37.2225
5679 | 771 | 745 | 149 | 7.2 | 28.8 | 0 | 0 | 0 | 205.8835 | 61.1816 | 0 | 24.3894 | 36.7922 | 0 | 0 | 0 | 0 | 0 | 205.8835 | 0 | 1275.5102 | 100% | 24.3894 | 0 | 56.25 | 90% | 36.7922
5680 | 668 | 582 | 158 | 6.5 | 28.5 | 0 | 0 | 0 | 0 | 36.6251 | 12.0499 | 0 | 36.6251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 36.6251
5681 | 548 | 383 | 128 | 6.7 | 27.8 | 0 | 0 | 0 | 0 | 32.1169 | 0 | 0 | 32.1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 32.1169
5682 | 387 | 192 | 86 | 6.8 | 26.2 | 0 | 0 | 0 | 0 | 13.9642 | 0 | 0 | 13.9642 | 0 | 0 | 0 | 69.4882 | 25.9922 | 0 | 69.4882 | 1206.022 | 94.55% | 0 | 0 | 56.25 | 90% | 39.9564
5683 | 78 | 41 | 31 | 5.9 | 24.5 | 0 | 0 | 0 | 0 | 1.5656 | 0 | 0 | 1.5656 | 0 | 0 | 0 | 96.5963 | 37.6903 | 0 | 96.5963 | 1109.4256 | 86.98% | 0 | 0 | 56.25 | 90% | 39.2559
5684 | 0 | 0 | 0 | 4.6 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.4256 | 86.98% | 0 | 8.1047 | 47.2802 | 75.65% | 8.1047
5685 | 0 | 0 | 0 | 3.4 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.4256 | 86.98% | 0 | 25 | 19.6119 | 31.38% | 25
5686 | 0 | 0 | 0 | 2.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.4256 | 86.98% | 0 | 0 | 19.6119 | 31.38% | 0
5687 | 0 | 0 | 0 | 2.8 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.4256 | 86.98% | 0 | 0 | 19.6119 | 31.38% | 0
5688 | 0 | 0 | 0 | 3.1 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.4256 | 86.98% | 0 | 0 | 19.6119 | 31.38% | 0
5689 | 0 | 0 | 0 | 3 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.4256 | 86.98% | 0 | 0 | 19.6119 | 31.38% | 0
5690 | 0 | 0 | 0 | 3.4 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.4256 | 86.98% | 0 | 0 | 19.6119 | 31.38% | 0
5691 | 0 | 0 | 0 | 2.5 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.4256 | 86.98% | 0 | 0 | 19.6119 | 31.38% | 0
5692 | 0 | 0 | 0 | 2.6 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.4256 | 86.98% | 0 | 0 | 19.6119 | 31.38% | 0
5693 | 0 | 0 | 0 | 3.2 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.012 | 48.9735 | 0 | 122.012 | 987.4137 | 77.41% | 8.1843 | 0 | 27.0069 | 43.21% | 40.7892
5694 | 1 | 5 | 5 | 3.9 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.8662 | 43.7125 | 0 | 109.8662 | 877.5475 | 68.8% | 0 | 0 | 27.0069 | 43.21% | 43.7125
5695 | 44 | 87 | 78 | 3.2 | 21.5 | 0 | 0 | 0 | 0 | 2.1813 | 0 | 0 | 2.1813 | 0 | 0 | 0 | 109.8569 | 43.6356 | 0 | 109.8569 | 767.6906 | 60.19% | 0 | 0 | 27.0069 | 43.21% | 45.8168
5696 | 123 | 232 | 188 | 4.6 | 23.5 | 0 | 0 | 0 | 0 | 13.2685 | 0 | 0 | 13.2685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.6906 | 60.19% | 0 | 0 | 27.0069 | 43.21% | 13.2685
5697 | 115 | 344 | 275 | 5.3 | 24.5 | 0 | 0 | 0 | 0 | 22.3124 | 0 | 0 | 22.3124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.6906 | 60.19% | 0 | 0 | 27.0069 | 43.21% | 22.3124
5698 | 49 | 371 | 331 | 5.8 | 25.2 | 0 | 0 | 0 | 0 | 24.8997 | 0 | 0 | 24.8997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.6906 | 60.19% | 0 | 0 | 27.0069 | 43.21% | 24.8997
5699 | 344 | 731 | 438 | 6 | 26.7 | 0 | 0 | 0 | 79.5929 | 52.5244 | 0 | 4.4876 | 48.0368 | 0 | 0 | 0 | 0 | 0 | 79.5929 | 0 | 847.2835 | 66.43% | 4.4876 | 0 | 31.0617 | 49.7% | 48.0368
5700 | 301 | 699 | 422 | 6.4 | 27.5 | 0 | 0 | 0 | 69.1443 | 51.5243 | 0 | 4.7939 | 46.7304 | 0 | 0 | 0 | 0 | 0 | 69.1443 | 0 | 916.4278 | 71.85% | 4.7939 | 0 | 35.3933 | 56.63% | 46.7304
5701 | 434 | 813 | 415 | 6.3 | 28.6 | 0 | 0 | 0 | 110.9092 | 61.0677 | 0 | 14.847 | 46.2207 | 0 | 0 | 0 | 0 | 0 | 110.9092 | 0 | 1027.337 | 80.54% | 14.847 | 0 | 48.8084 | 78.09% | 46.2207
5702 | 364 | 710 | 390 | 7.7 | 28.6 | 0 | 0 | 0 | 87.9374 | 54.2672 | 0 | 8.2358 | 46.0313 | 0 | 0 | 0 | 0 | 0 | 87.9374 | 0 | 1115.2744 | 87.44% | 8.2358 | 0 | 56.25 | 90% | 46.0313
5703 | 249 | 552 | 356 | 7.4 | 28.2 | 0 | 0 | 0 | 51.3019 | 42.1463 | 0 | 0 | 42.1463 | 0 | 0 | 0 | 0 | 0 | 51.3019 | 0 | 1166.5762 | 91.46% | 0 | 0 | 56.25 | 90% | 42.1463
5704 | 29 | 279 | 259 | 7.6 | 27.1 | 0 | 0 | 0 | 0 | 18.7454 | 0 | 0 | 18.7454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.5762 | 91.46% | 0 | 20.178 | 33.9183 | 54.27% | 38.9234
5705 | 160 | 306 | 226 | 7.2 | 26.4 | 0 | 0 | 0 | 0 | 21.9504 | 0 | 0 | 21.9504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.5762 | 91.46% | 0 | 0 | 33.9183 | 54.27% | 21.9504
5706 | 20 | 104 | 98 | 6.9 | 25.1 | 0 | 0 | 0 | 0 | 6.4044 | 0 | 0 | 6.4044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.5762 | 91.46% | 0 | 25 | 6.25 | 10% | 31.4044
5707 | 4 | 30 | 30 | 5.9 | 24.1 | 0 | 0 | 0 | 0 | 1.4329 | 0 | 0 | 1.4329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.5762 | 91.46% | 0 | 0 | 6.25 | 10% | 1.4329
5708 | 0 | 0 | 0 | 4.7 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 1166.5762 | 91.46% | 0 | 0 | 6.25 | 10% | 0
5709 | 0 | 0 | 0 | 4.6 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7705 | 37.0164 | 0 | 94.7705 | 1071.8057 | 84.03% | 0 | 0 | 6.25 | 10% | 37.0164
5710 | 0 | 0 | 0 | 4.3 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7548 | 34.9023 | 0 | 89.7548 | 982.0509 | 76.99% | 0 | 0 | 6.25 | 10% | 34.9023
5711 | 0 | 0 | 0 | 1.7 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5886 | 33.557 | 0 | 86.5886 | 895.4623 | 70.2% | 0 | 0 | 6.25 | 10% | 33.557
5712 | 0 | 0 | 0 | 1 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6265 | 32.7854 | 0 | 84.6265 | 810.8359 | 63.57% | 0 | 0 | 6.25 | 10% | 32.7854
5713 | 0 | 0 | 0 | 1.3 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5079 | 32.3342 | 0 | 83.5079 | 727.328 | 57.02% | 0 | 0 | 6.25 | 10% | 32.3342
5714 | 0 | 0 | 0 | 1.1 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2748 | 32.6823 | 0 | 84.2748 | 643.0532 | 50.42% | 0 | 0 | 6.25 | 10% | 32.6823
5715 | 0 | 0 | 0 | 1.4 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3818 | 37.4961 | 0 | 95.3818 | 547.6714 | 42.94% | 2.325 | 0 | 8.3508 | 13.36% | 35.1711
5716 | 0 | 0 | 0 | 1.4 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5582 | 37.9969 | 0 | 96.5582 | 451.1132 | 35.37% | 0 | 0 | 8.3508 | 13.36% | 37.9969
5717 | 0 | 0 | 0 | 0.7 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4152 | 0 | 127.551 | 323.5622 | 25.37% | 10.6719 | 0 | 17.9935 | 28.79% | 40.7433
5718 | 0 | 6 | 6 | 0.5 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4575 | 0 | 127.551 | 196.0112 | 15.37% | 7.7854 | 0 | 25.0281 | 40.04% | 43.6721
5719 | 48 | 85 | 78 | 0.7 | 20.8 | 0 | 0 | 0 | 0 | 2.0213 | 0 | 0 | 2.0213 | 0 | 0 | 0 | 109.097 | 43.3652 | 0 | 109.097 | 86.9142 | 6.814% | 0 | 0 | 25.0281 | 40.04% | 45.3865
5720 | 159 | 241 | 177 | 0.9 | 22.9 | 0 | 0 | 0 | 0 | 13.0518 | 0 | 0 | 13.0518 | 0 | 0 | 0 | 86.9142 | 33.6689 | 0 | 86.9142 | 0 | 0% | 0 | 0 | 25.0281 | 40.04% | 46.7207
5721 | 574 | 500 | 177 | 1.2 | 25.4 | 0 | 0 | 0 | 127.329 | 31.4327 | 0 | 0 | 31.4327 | 0 | 0 | 0 | 0 | 0 | 127.329 | 0 | 127.329 | 9.983% | 0 | 16.3645 | 6.9169 | 11.07% | 47.7972
5722 | 699 | 687 | 187 | 1.7 | 27 | 0 | 0 | 0 | 170.7424 | 47.3269 | 0 | 0 | 47.3269 | 0 | 0 | 0 | 0 | 0 | 170.7424 | 0 | 298.0715 | 23.37% | 0 | 0.6026 | 6.25 | 10% | 47.9296
5723 | 803 | 846 | 183 | 2.6 | 28.8 | 0 | 0 | 0 | 216.2403 | 60.9466 | 0 | 14.2552 | 46.6914 | 0 | 0 | 0 | 0 | 0 | 216.2403 | 0 | 514.3117 | 40.32% | 14.2552 | 0 | 19.1304 | 30.61% | 46.6914
5724 | 796 | 919 | 211 | 5.3 | 29.4 | 0 | 0 | 0 | 218.6561 | 65.1116 | 4.7377 | 19.6889 | 45.4227 | 0 | 0 | 0 | 0 | 0 | 218.6561 | 0 | 732.9678 | 57.46% | 19.6889 | 0 | 36.9205 | 59.07% | 45.4227
5725 | 638 | 859 | 283 | 4.7 | 29.5 | 0 | 0 | 0 | 174.1712 | 66.2485 | 0 | 21.3926 | 44.8559 | 0 | 0 | 0 | 0 | 0 | 174.1712 | 0 | 907.139 | 71.12% | 21.3926 | 0 | 56.25 | 90% | 44.8559
5726 | 248 | 587 | 370 | 3.8 | 29.6 | 0 | 0 | 0 | 55.9249 | 43.994 | 0 | 0 | 43.994 | 0 | 0 | 0 | 0 | 0 | 55.9249 | 0 | 963.0639 | 75.5% | 0 | 0.31731 | 55.8988 | 89.44% | 44.3113
5727 | 707 | 759 | 220 | 3.9 | 30.2 | 0 | 0 | 0 | 189.935 | 44.1248 | 16.8385 | 0.38866 | 43.7362 | 0 | 0 | 0 | 0 | 0 | 189.935 | 0 | 1152.9988 | 90.4% | 0.38866 | 0 | 56.25 | 90% | 43.7362
5728 | 501 | 501 | 185 | 5.2 | 29.7 | 0 | 0 | 0 | 122.5114 | 40.9971 | 0 | 0 | 40.9971 | 0 | 0 | 0 | 0 | 0 | 122.5114 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 40.9971
5729 | 157 | 225 | 154 | 3.1 | 28.7 | 0 | 0 | 0 | 0 | 16.4681 | 0 | 0 | 16.4681 | 0 | 0 | 0 | 72.0204 | 26.8878 | 0 | 72.0204 | 1203.4899 | 94.35% | 0 | 0 | 56.25 | 90% | 43.3559
5730 | 4 | 70 | 69 | 1.9 | 27.6 | 0 | 0 | 0 | 0 | 3.9879 | 0 | 0 | 3.9879 | 0 | 0 | 0 | 104.6854 | 40.829 | 0 | 104.6854 | 1098.8045 | 86.15% | 0 | 0 | 56.25 | 90% | 44.8169
5731 | 19 | 16 | 14 | 4.4 | 26.5 | 0 | 0 | 0 | 0 | 0.49753 | 0 | 0 | 0.49753 | 0 | 0 | 0 | 85.0192 | 32.5806 | 0 | 85.0192 | 1013.7853 | 79.48% | 0 | 0 | 56.25 | 90% | 33.0781
5732 | 0 | 0 | 0 | 5.9 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3279 | 38.9954 | 0 | 99.3279 | 914.4574 | 71.69% | 0 | 0 | 56.25 | 90% | 38.9954
5733 | 0 | 0 | 0 | 3.4 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1728 | 36.4496 | 0 | 93.1728 | 821.2845 | 64.39% | 0 | 0 | 56.25 | 90% | 36.4496
5734 | 0 | 0 | 0 | 1.4 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4083 | 34.426 | 0 | 88.4083 | 732.8762 | 57.46% | 0 | 0 | 56.25 | 90% | 34.426
5735 | 0 | 0 | 0 | 1.3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9251 | 32.9386 | 0 | 84.9251 | 647.9512 | 50.8% | 0 | 0 | 56.25 | 90% | 32.9386
5736 | 0 | 0 | 0 | 0.6 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4773 | 32.3328 | 0 | 83.4773 | 564.4739 | 44.25% | 0 | 0 | 56.25 | 90% | 32.3328
5737 | 0 | 0 | 0 | 2.4 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8656 | 32.0807 | 0 | 82.8656 | 481.6083 | 37.76% | 0 | 0 | 56.25 | 90% | 32.0807
5738 | 0 | 0 | 0 | 1.5 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8786 | 32.5514 | 0 | 83.8786 | 397.7297 | 31.18% | 0 | 0 | 56.25 | 90% | 32.5514
5739 | 0 | 0 | 0 | 0.6 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6512 | 35.1001 | 0 | 89.6512 | 308.0785 | 24.15% | 0 | 0 | 56.25 | 90% | 35.1001
5740 | 0 | 0 | 0 | 0.3 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2749 | 38.0038 | 0 | 96.2749 | 211.8036 | 16.61% | 0 | 0 | 56.25 | 90% | 38.0038
5741 | 0 | 0 | 0 | 1 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4582 | 40.6973 | 0 | 102.4582 | 109.3454 | 8.573% | 0 | 0 | 56.25 | 90% | 40.6973
5742 | 13 | 5 | 5 | 0.7 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3454 | 43.6596 | 0 | 109.3454 | 0 | 0% | 0 | 0 | 56.25 | 90% | 43.6596
5743 | 340 | 114 | 48 | 0.4 | 20.5 | 0 | 0 | 0 | 0 | 1.6232 | 0 | 0 | 1.6232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 28.5817 | 45.73% | 26.6232
5744 | 617 | 315 | 82 | 0.6 | 23.6 | 0 | 0 | 0 | 109.5174 | 13.2512 | 0 | 0 | 13.2512 | 0 | 0 | 0 | 0 | 0 | 109.5174 | 0 | 109.5174 | 8.586% | 0 | 20.178 | 6.25 | 10% | 33.4291
5745 | 752 | 520 | 100 | 0.8 | 27.1 | 0 | 0 | 0 | 0 | 32.0521 | 0 | 0 | 32.0521 | 0 | 0 | 0 | 46.5822 | 16.2005 | 0 | 46.5822 | 62.9351 | 4.934% | 0 | 0 | 6.25 | 10% | 48.2527
5746 | 822 | 697 | 114 | 1.5 | 29.4 | 0 | 0 | 0 | 0 | 36.3134 | 11.2531 | 0 | 36.3134 | 0 | 0 | 0 | 38.2653 | 12.5855 | 0 | 38.2653 | 24.6698 | 1.934% | 0 | 0 | 6.25 | 10% | 48.8989
5747 | 852 | 826 | 126 | 1.7 | 30.7 | 0 | 0 | 0 | 231.0261 | 48.371 | 10.0732 | 0 | 48.371 | 0 | 0 | 0 | 0 | 0 | 231.0261 | 0 | 255.6959 | 20.05% | 0 | 0 | 6.25 | 10% | 48.371
5748 | 768 | 842 | 163 | 2.6 | 31.6 | 0 | 0 | 0 | 212.3805 | 47.1469 | 15.1797 | 0 | 47.1469 | 0 | 0 | 0 | 0 | 0 | 212.3805 | 0 | 468.0764 | 36.7% | 0 | 0 | 6.25 | 10% | 47.1469
5749 | 857 | 940 | 175 | 5.8 | 31.5 | 0 | 0 | 0 | 239.681 | 63.335 | 8.665 | 16.5502 | 46.7848 | 0 | 0 | 0 | 0 | 0 | 239.681 | 0 | 707.7574 | 55.49% | 16.5502 | 0 | 21.2041 | 33.93% | 46.7848
5750 | 854 | 865 | 140 | 5.3 | 31.8 | 0 | 0 | 0 | 237.896 | 68.4921 | 0 | 22.3382 | 46.1539 | 0 | 0 | 0 | 0 | 0 | 237.896 | 0 | 945.6535 | 74.14% | 22.3382 | 0 | 41.388 | 66.22% | 46.1539
5751 | 819 | 748 | 129 | 6.2 | 31.5 | 0 | 0 | 0 | 220.7973 | 61.999 | 0 | 16.4482 | 45.5508 | 0 | 0 | 0 | 0 | 0 | 220.7973 | 0 | 1166.4507 | 91.45% | 16.4482 | 0 | 56.25 | 90% | 45.5508
5752 | 758 | 583 | 114 | 6.2 | 31.2 | 0 | 0 | 0 | 25.5719 | 44.5954 | 5.096 | 0 | 44.5954 | 0 | 0 | 0 | 0 | 0 | 25.5719 | 0 | 1192.0226 | 93.45% | 0 | 0 | 56.25 | 90% | 44.5954
5753 | 660 | 387 | 92 | 5.4 | 30.6 | 0 | 0 | 0 | 0 | 33.5596 | 0 | 0 | 33.5596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1192.0226 | 93.45% | 0 | 10.9801 | 44.098 | 70.56% | 44.5397
5754 | 463 | 180 | 61 | 5.2 | 29.3 | 0 | 0 | 0 | 83.4876 | 13.7317 | 0 | 0 | 13.7317 | 0 | 0 | 0 | 0 | 0 | 83.4876 | 0 | 1275.5102 | 100% | 0 | 25 | 16.4296 | 26.29% | 38.7317
5755 | 99 | 25 | 15 | 3.9 | 27.7 | 0 | 0 | 0 | 0 | 0.58787 | 0 | 0 | 0.58787 | 0 | 0 | 0 | 108.5513 | 42.4575 | 0 | 108.5513 | 1166.9589 | 91.49% | 0 | 0 | 16.4296 | 26.29% | 43.0454
5756 | 0 | 0 | 0 | 1.6 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.3103 | 39.948 | 0 | 102.3103 | 1064.6486 | 83.47% | 0 | 0 | 16.4296 | 26.29% | 39.948
5757 | 0 | 0 | 0 | 1.6 | 24.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4662 | 37.6083 | 0 | 96.4662 | 968.1824 | 75.91% | 0 | 0 | 16.4296 | 26.29% | 37.6083
5758 | 0 | 0 | 0 | 0.9 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1718 | 35.458 | 0 | 91.1718 | 877.0106 | 68.76% | 0 | 0 | 16.4296 | 26.29% | 35.458
5759 | 0 | 0 | 0 | 1.2 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4415 | 33.9232 | 0 | 87.4415 | 789.5691 | 61.9% | 0 | 0 | 16.4296 | 26.29% | 33.9232
5760 | 0 | 0 | 0 | 0.8 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.694 | 33.1795 | 0 | 85.694 | 703.8752 | 55.18% | 0 | 0 | 16.4296 | 26.29% | 33.1795
5761 | 0 | 0 | 0 | 1.6 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.795 | 32.8704 | 0 | 84.795 | 619.0802 | 48.54% | 0 | 0 | 16.4296 | 26.29% | 32.8704
5762 | 0 | 0 | 0 | 1.9 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4332 | 33.1935 | 0 | 85.4332 | 533.6469 | 41.84% | 0 | 0 | 16.4296 | 26.29% | 33.1935
5763 | 0 | 0 | 0 | 1.6 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3103 | 35.7337 | 0 | 91.3103 | 442.3367 | 34.68% | 0 | 0 | 16.4296 | 26.29% | 35.7337
5764 | 0 | 0 | 0 | 1.5 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0754 | 38.6779 | 0 | 98.0754 | 344.2613 | 26.99% | 0 | 0 | 16.4296 | 26.29% | 38.6779
5765 | 0 | 0 | 0 | 1.1 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5698 | 48.4335 | 0 | 120.5698 | 223.6915 | 17.54% | 7.1053 | 0 | 22.8497 | 36.56% | 41.3282
5766 | 19 | 8 | 7 | 1.7 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.37 | 44.4074 | 0 | 111.37 | 112.3215 | 8.806% | 0 | 0 | 22.8497 | 36.56% | 44.4074
5767 | 329 | 115 | 50 | 0.9 | 22.5 | 0 | 0 | 0 | 0 | 1.6993 | 0 | 0 | 1.6993 | 0 | 0 | 0 | 112.3215 | 44.6077 | 0 | 112.3215 | 0 | 0% | 0 | 0 | 22.8497 | 36.56% | 46.3071
5768 | 602 | 317 | 90 | 1.4 | 24.9 | 0 | 0 | 0 | 105.7687 | 13.7027 | 0 | 0 | 13.7027 | 0 | 0 | 0 | 0 | 0 | 105.7687 | 0 | 105.7687 | 8.292% | 0 | 0 | 22.8497 | 36.56% | 13.7027
5769 | 704 | 552 | 160 | 4.2 | 27.6 | 0 | 0 | 0 | 158.1043 | 35.5387 | 0 | 0 | 35.5387 | 0 | 0 | 0 | 0 | 0 | 158.1043 | 0 | 263.873 | 20.69% | 0 | 0 | 22.8497 | 36.56% | 35.5387
5770 | 719 | 687 | 177 | 5.4 | 28.6 | 0 | 0 | 0 | 179.5813 | 49.1671 | 0 | 0 | 49.1671 | 0 | 0 | 0 | 0 | 0 | 179.5813 | 0 | 443.4544 | 34.77% | 0 | 0 | 22.8497 | 36.56% | 49.1671
5771 | 643 | 782 | 244 | 5.6 | 29.7 | 0 | 0 | 0 | 167.5068 | 57.5585 | 0 | 8.0998 | 49.4587 | 0 | 0 | 0 | 0 | 0 | 167.5068 | 0 | 610.9612 | 47.9% | 8.0998 | 0 | 30.1684 | 48.27% | 49.4587
5772 | 768 | 871 | 190 | 4.7 | 31 | 0 | 0 | 0 | 210.8286 | 66.2487 | 0 | 18.1102 | 48.1385 | 0 | 0 | 0 | 0 | 0 | 210.8286 | 0 | 821.7898 | 64.43% | 18.1102 | 0 | 46.5321 | 74.45% | 48.1385
5773 | 230 | 625 | 409 | 4.9 | 31.2 | 0 | 0 | 0 | 49.6812 | 46.0865 | 0 | 0 | 46.0865 | 0 | 0 | 0 | 0 | 0 | 49.6812 | 0 | 871.4711 | 68.32% | 0 | 0 | 46.5321 | 74.45% | 46.0865
5774 | 431 | 718 | 350 | 5.1 | 30.6 | 0 | 0 | 0 | 110.3763 | 56.1329 | 0 | 8.9164 | 47.2165 | 0 | 0 | 0 | 0 | 0 | 110.3763 | 0 | 981.8474 | 76.98% | 8.9164 | 0 | 54.5886 | 87.34% | 47.2165
5775 | 415 | 601 | 283 | 5.4 | 30.8 | 0 | 0 | 0 | 102.302 | 47.8527 | 0 | 1.4119 | 46.4408 | 0 | 0 | 0 | 0 | 0 | 102.302 | 0 | 1084.1493 | 85% | 1.4119 | 0 | 55.8644 | 89.38% | 46.4408
5776 | 119 | 357 | 286 | 4.5 | 29.1 | 0 | 0 | 0 | 0 | 26.1618 | 0 | 0 | 26.1618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.1493 | 85% | 0 | 3.3582 | 52.1477 | 83.44% | 29.52
5777 | 422 | 352 | 170 | 2.8 | 29.6 | 0 | 0 | 0 | 92.6395 | 29.0836 | 0 | 0 | 29.0836 | 0 | 0 | 0 | 0 | 0 | 92.6395 | 0 | 1176.7888 | 92.26% | 0 | 16.4714 | 33.9183 | 54.27% | 45.555
5778 | 334 | 159 | 70 | 2 | 28.7 | 0 | 0 | 0 | 56.3035 | 11.4326 | 0 | 0 | 11.4326 | 0 | 0 | 0 | 0 | 0 | 56.3035 | 0 | 1233.0923 | 96.67% | 0 | 25 | 6.25 | 10% | 36.4326
5779 | 1 | 11 | 11 | 2.6 | 27 | 0 | 0 | 0 | 0 | 0.26519 | 0 | 0 | 0.26519 | 0 | 0 | 0 | 111.2131 | 43.6687 | 0 | 111.2131 | 1121.8792 | 87.96% | 0 | 0 | 6.25 | 10% | 43.9339
5780 | 0 | 0 | 0 | 2.6 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.0196 | 41.1221 | 0 | 105.0196 | 1016.8596 | 79.72% | 0 | 0 | 6.25 | 10% | 41.1221
5781 | 0 | 0 | 0 | 1.1 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4665 | 38.4899 | 0 | 98.4665 | 918.3931 | 72% | 0 | 0 | 6.25 | 10% | 38.4899
5782 | 0 | 0 | 0 | 1.2 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1012 | 36.2532 | 0 | 93.1012 | 825.2919 | 64.7% | 0 | 0 | 6.25 | 10% | 36.2532
5783 | 0 | 0 | 0 | 0.9 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0292 | 34.5764 | 0 | 89.0292 | 736.2627 | 57.72% | 0 | 0 | 6.25 | 10% | 34.5764
5784 | 0 | 0 | 0 | 1.2 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0874 | 33.8118 | 0 | 87.0874 | 649.1753 | 50.9% | 0 | 0 | 6.25 | 10% | 33.8118
5785 | 0 | 0 | 0 | 0.9 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8965 | 33.3383 | 0 | 85.8965 | 563.2789 | 44.16% | 0 | 0 | 6.25 | 10% | 33.3383
5786 | 0 | 0 | 0 | 1.2 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4725 | 33.6113 | 0 | 86.4725 | 476.8063 | 37.38% | 0 | 0 | 6.25 | 10% | 33.6113
5787 | 0 | 0 | 0 | 1.3 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1533 | 36.9853 | 0 | 94.1533 | 382.6531 | 30% | 0.91458 | 0 | 7.0764 | 11.32% | 36.0708
5788 | 0 | 0 | 0 | 0.9 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4152 | 0 | 127.551 | 255.102 | 20% | 12.4518 | 0 | 18.3273 | 29.32% | 38.9634
5789 | 0 | 0 | 0 | 0.9 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3978 | 0 | 127.551 | 127.551 | 10% | 10.1016 | 0 | 27.4547 | 43.93% | 41.2962
5790 | 19 | 5 | 5 | 1.8 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4065 | 0 | 127.551 | 0 | 0% | 6.7957 | 0 | 33.5951 | 53.75% | 44.6108
5791 | 368 | 113 | 45 | 0.8 | 22.4 | 0 | 0 | 0 | 0 | 1.4879 | 0 | 0 | 1.4879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 33.5951 | 53.75% | 1.4879
5792 | 627 | 312 | 79 | 1 | 25.3 | 0 | 0 | 0 | 110.8758 | 13.3262 | 0 | 0 | 13.3262 | 0 | 0 | 0 | 0 | 0 | 110.8758 | 0 | 110.8758 | 8.693% | 0 | 24.7079 | 6.25 | 10% | 38.0341
5793 | 750 | 513 | 99 | 1.3 | 27.7 | 0 | 0 | 0 | 0 | 32.3448 | 0 | 0 | 32.3448 | 0 | 0 | 0 | 50.0738 | 17.6552 | 0 | 50.0738 | 60.8019 | 4.767% | 0 | 0 | 6.25 | 10% | 50
5794 | 813 | 685 | 114 | 1.3 | 29.6 | 0 | 0 | 0 | 0 | 37.422 | 9.7622 | 0 | 37.422 | 0 | 0 | 0 | 38.2653 | 12.578 | 0 | 38.2653 | 22.5366 | 1.767% | 0 | 0 | 6.25 | 10% | 50
5795 | 854 | 815 | 119 | 2.7 | 30.4 | 0 | 0 | 0 | 231.2048 | 55.879 | 3.0697 | 5.879 | 50 | 0 | 0 | 0 | 0 | 0 | 231.2048 | 0 | 253.7415 | 19.89% | 5.879 | 0 | 11.562 | 18.5% | 50
5796 | 873 | 889 | 122 | 3.4 | 31.5 | 0 | 0 | 0 | 243.5809 | 66.3016 | 0 | 17.2523 | 49.0493 | 0 | 0 | 0 | 0 | 0 | 243.5809 | 0 | 497.3224 | 38.99% | 17.2523 | 0 | 27.1505 | 43.44% | 49.0493
5797 | 861 | 895 | 131 | 4.4 | 32 | 0 | 0 | 0 | 242.1439 | 69.1085 | 0 | 20.4938 | 48.6148 | 0 | 0 | 0 | 0 | 0 | 242.1439 | 0 | 739.4663 | 57.97% | 20.4938 | 0 | 45.6678 | 73.07% | 48.6148
5798 | 684 | 755 | 174 | 3 | 32 | 0 | 0 | 0 | 188.4221 | 59.8278 | 0 | 11.7116 | 48.1162 | 0 | 0 | 0 | 0 | 0 | 188.4221 | 0 | 927.8884 | 72.75% | 11.7116 | 0 | 56.25 | 90% | 48.1162
5799 | 556 | 671 | 244 | 4.8 | 31.4 | 0 | 0 | 0 | 144.535 | 47.0299 | 6.5572 | 0 | 47.0299 | 0 | 0 | 0 | 0 | 0 | 144.535 | 0 | 1072.4234 | 84.08% | 0 | 0 | 56.25 | 90% | 47.0299
5800 | 470 | 477 | 197 | 5.7 | 30.5 | 0 | 0 | 0 | 113.1203 | 40.2704 | 0 | 0 | 40.2704 | 0 | 0 | 0 | 0 | 0 | 113.1203 | 0 | 1185.5438 | 92.95% | 0 | 5.5019 | 50.1608 | 80.26% | 45.7723
5801 | 272 | 278 | 155 | 4.8 | 29.6 | 0 | 0 | 0 | 51.1575 | 21.708 | 0 | 0 | 21.708 | 0 | 0 | 0 | 0 | 0 | 51.1575 | 0 | 1236.7012 | 96.96% | 0 | 23.7481 | 23.878 | 38.2% | 45.4561
5802 | 48 | 71 | 55 | 3.5 | 28.4 | 0 | 0 | 0 | 0 | 4.1975 | 0 | 0 | 4.1975 | 0 | 0 | 0 | 107.7276 | 42.026 | 0 | 107.7276 | 1128.9736 | 88.51% | 0 | 0 | 23.878 | 38.2% | 46.2235
5803 | 11 | 12 | 11 | 4.4 | 26.8 | 0 | 0 | 0 | 0 | 0.30201 | 0 | 0 | 0.30201 | 0 | 0 | 0 | 109.4149 | 42.9272 | 0 | 109.4149 | 1019.5587 | 79.93% | 0 | 0 | 23.878 | 38.2% | 43.2292
5804 | 0 | 0 | 0 | 3.3 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0981 | 40.3742 | 0 | 103.0981 | 916.4606 | 71.85% | 0 | 0 | 23.878 | 38.2% | 40.3742
5805 | 0 | 0 | 0 | 2.8 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4271 | 38.0888 | 0 | 97.4271 | 819.0335 | 64.21% | 0 | 0 | 23.878 | 38.2% | 38.0888
5806 | 0 | 0 | 0 | 1.9 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9666 | 35.8368 | 0 | 91.9666 | 727.0669 | 57% | 0 | 0 | 23.878 | 38.2% | 35.8368
5807 | 0 | 0 | 0 | 1.8 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1582 | 34.231 | 0 | 88.1582 | 638.9087 | 50.09% | 0 | 0 | 23.878 | 38.2% | 34.231
5808 | 0 | 0 | 0 | 1.3 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9696 | 33.2979 | 0 | 85.9696 | 552.9392 | 43.35% | 0 | 0 | 23.878 | 38.2% | 33.2979
5809 | 0 | 0 | 0 | 1.3 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.239 | 32.5612 | 0 | 84.239 | 468.7002 | 36.75% | 0 | 0 | 23.878 | 38.2% | 32.5612
5810 | 0 | 0 | 0 | 1 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6874 | 31.9386 | 0 | 82.6874 | 386.0128 | 30.26% | 0 | 0 | 23.878 | 38.2% | 31.9386
5811 | 0 | 0 | 0 | 1.4 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0224 | 32.1072 | 0 | 83.0224 | 302.9904 | 23.75% | 0 | 0 | 23.878 | 38.2% | 32.1072
5812 | 0 | 0 | 0 | 1.8 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9657 | 32.8996 | 0 | 84.9657 | 218.0247 | 17.09% | 0 | 0 | 23.878 | 38.2% | 32.8996
5813 | 0 | 0 | 0 | 1.1 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4737 | 35.3349 | 0 | 90.4737 | 127.551 | 10% | 1.2389 | 0 | 24.9975 | 40% | 34.0959
5814 | 15 | 5 | 5 | 0.8 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.3622 | 0 | 127.551 | 0 | 0% | 14.0324 | 0 | 37.6766 | 60.28% | 37.3298
5815 | 246 | 104 | 57 | 0.4 | 22.2 | 0 | 0 | 0 | 0 | 1.7402 | 0 | 0 | 1.7402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.3958 | 33.9183 | 54.27% | 5.136
5816 | 522 | 292 | 98 | 0.8 | 24.3 | 0 | 0 | 0 | 89.4045 | 13.1804 | 0 | 0 | 13.1804 | 0 | 0 | 0 | 0 | 0 | 89.4045 | 0 | 89.4045 | 7.009% | 0 | 25 | 6.25 | 10% | 38.1804
5817 | 627 | 491 | 143 | 1 | 26.4 | 0 | 0 | 0 | 0 | 30.2365 | 1.1931 | 0 | 30.2365 | 0 | 0 | 0 | 38.2653 | 12.6905 | 0 | 38.2653 | 51.1392 | 4.009% | 0 | 0 | 6.25 | 10% | 42.927
5818 | 723 | 667 | 158 | 1.1 | 28.7 | 0 | 0 | 0 | 0 | 31.1917 | 15.0419 | 0 | 31.1917 | 0 | 0 | 0 | 38.2653 | 12.6113 | 0 | 38.2653 | 12.8738 | 1.009% | 0 | 0 | 6.25 | 10% | 43.803
5819 | 792 | 791 | 145 | 1.5 | 30.2 | 0 | 0 | 0 | 213.6937 | 43.6596 | 13.0268 | 0 | 43.6596 | 0 | 0 | 0 | 0 | 0 | 213.6937 | 0 | 226.5676 | 17.76% | 0 | 0 | 6.25 | 10% | 43.6596
5820 | 823 | 876 | 154 | 3 | 31.6 | 0 | 0 | 0 | 228.6601 | 42.7571 | 22.9487 | 0 | 42.7571 | 0 | 0 | 0 | 0 | 0 | 228.6601 | 0 | 455.2277 | 35.69% | 0 | 0 | 6.25 | 10% | 42.7571
5821 | 812 | 924 | 205 | 5.3 | 31.7 | 0 | 0 | 0 | 100.8219 | 48.7655 | 23.2345 | 7.0377 | 41.7279 | 0 | 0 | 0 | 0 | 0 | 100.8219 | 0 | 556.0496 | 43.59% | 7.0377 | 0 | 12.6089 | 20.17% | 41.7279
5822 | 715 | 862 | 257 | 6.2 | 31.7 | 0 | 0 | 0 | 195.1214 | 66.1541 | 2.9569 | 25 | 41.1541 | 0 | 0 | 0 | 0 | 0 | 195.1214 | 0 | 751.171 | 58.89% | 25 | 0 | 35.1979 | 56.32% | 41.1541
5823 | 590 | 649 | 212 | 5.8 | 30.8 | 0 | 0 | 0 | 153.5955 | 54.3354 | 0 | 13.6451 | 40.6903 | 0 | 0 | 0 | 0 | 0 | 153.5955 | 0 | 904.7665 | 70.93% | 13.6451 | 0 | 47.5271 | 76.04% | 40.6903
5824 | 691 | 585 | 165 | 6.1 | 31.3 | 0 | 0 | 0 | 175.2128 | 49.9919 | 0 | 9.6539 | 40.338 | 0 | 0 | 0 | 0 | 0 | 175.2128 | 0 | 1079.9793 | 84.67% | 9.6539 | 0 | 56.25 | 90% | 40.338
5825 | 575 | 395 | 147 | 4.5 | 31 | 0 | 0 | 0 | 130.8753 | 33.9517 | 0 | 0 | 33.9517 | 0 | 0 | 0 | 0 | 0 | 130.8753 | 0 | 1210.8546 | 94.93% | 0 | 6.8626 | 48.6549 | 77.85% | 40.8143
5826 | 184 | 119 | 64 | 4.5 | 29 | 0 | 0 | 0 | 0 | 7.9799 | 0 | 0 | 7.9799 | 0 | 0 | 0 | 69.9867 | 26.0051 | 0 | 69.9867 | 1140.8678 | 89.44% | 0 | 8.6997 | 39.0267 | 62.44% | 42.6847
5827 | 41 | 15 | 12 | 3.4 | 27.3 | 0 | 0 | 0 | 0 | 0.36579 | 0 | 0 | 0.36579 | 0 | 0 | 0 | 102.1793 | 39.7981 | 0 | 102.1793 | 1038.6885 | 81.43% | 0 | 0 | 39.0267 | 62.44% | 40.1639
5828 | 0 | 0 | 0 | 2.1 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8921 | 37.6612 | 0 | 96.8921 | 941.7965 | 73.84% | 0 | 0 | 39.0267 | 62.44% | 37.6612
5829 | 0 | 0 | 0 | 1.9 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8672 | 35.6349 | 0 | 91.8672 | 849.9293 | 66.63% | 0 | 0 | 39.0267 | 62.44% | 35.6349
5830 | 0 | 0 | 0 | 0.5 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3045 | 33.3425 | 0 | 86.3045 | 763.6249 | 59.87% | 0 | 0 | 39.0267 | 62.44% | 33.3425
5831 | 0 | 0 | 0 | 0.8 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4391 | 31.7353 | 0 | 82.4391 | 681.1857 | 53.4% | 0 | 0 | 39.0267 | 62.44% | 31.7353
5832 | 0 | 0 | 0 | 0.7 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0815 | 30.7562 | 0 | 80.0815 | 601.1042 | 47.13% | 0 | 0 | 39.0267 | 62.44% | 30.7562
5833 | 0 | 0 | 0 | 1.1 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.531 | 30.0905 | 0 | 78.531 | 522.5732 | 40.97% | 0 | 0 | 39.0267 | 62.44% | 30.0905
5834 | 0 | 0 | 0 | 0.8 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6932 | 29.7786 | 0 | 77.6932 | 444.88 | 34.88% | 0 | 0 | 39.0267 | 62.44% | 29.7786
5835 | 0 | 0 | 0 | 0.6 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1313 | 30.0557 | 0 | 78.1313 | 366.7486 | 28.75% | 0 | 0 | 39.0267 | 62.44% | 30.0557
5836 | 0 | 0 | 0 | 0.8 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0105 | 29.9931 | 0 | 78.0105 | 288.7382 | 22.64% | 0 | 0 | 39.0267 | 62.44% | 29.9931
5837 | 0 | 0 | 0 | 1.2 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7691 | 30.3719 | 0 | 78.7691 | 209.9691 | 16.46% | 0 | 0 | 39.0267 | 62.44% | 30.3719
5838 | 19 | 5 | 4 | 1.3 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2467 | 32.7213 | 0 | 84.2467 | 125.7224 | 9.857% | 0 | 0 | 39.0267 | 62.44% | 32.7213
5839 | 382 | 110 | 41 | 1.1 | 21.2 | 0 | 0 | 0 | 0 | 1.6325 | 0 | 0 | 1.6325 | 0 | 0 | 0 | 85.9558 | 33.3701 | 0 | 85.9558 | 39.7667 | 3.118% | 0 | 0 | 39.0267 | 62.44% | 35.0026
5840 | 638 | 308 | 73 | 0.9 | 25.2 | 0 | 0 | 0 | 0 | 13.2558 | 0 | 0 | 13.2558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.7667 | 3.118% | 0 | 23.5754 | 12.9351 | 20.7% | 36.8312
5841 | 764 | 510 | 90 | 0.8 | 28.3 | 0 | 0 | 0 | 174.8104 | 32.1236 | 0 | 0 | 32.1236 | 0 | 0 | 0 | 0 | 0 | 174.8104 | 0 | 214.577 | 16.82% | 0 | 6.0404 | 6.25 | 10% | 38.164
5842 | 834 | 683 | 100 | 1.8 | 30.1 | 0 | 0 | 0 | 213.8506 | 39.6639 | 8.0954 | 0 | 39.6639 | 0 | 0 | 0 | 0 | 0 | 213.8506 | 0 | 428.4276 | 33.59% | 0 | 0 | 6.25 | 10% | 39.6639
5843 | 869 | 816 | 112 | 2.9 | 31.4 | 0 | 0 | 0 | 235.5996 | 40.338 | 19.1393 | 0 | 40.338 | 0 | 0 | 0 | 0 | 0 | 235.5996 | 0 | 664.0272 | 52.06% | 0 | 0 | 6.25 | 10% | 40.338
5844 | 775 | 857 | 181 | 3.7 | 32.7 | 0 | 0 | 0 | 213.7881 | 55.6516 | 9.2616 | 16.2662 | 39.3854 | 0 | 0 | 0 | 0 | 0 | 213.7881 | 0 | 877.8153 | 68.82% | 16.2662 | 0 | 20.9475 | 33.52% | 39.3854
5845 | 794 | 893 | 192 | 6.1 | 33.1 | 0 | 0 | 0 | 220.2235 | 63.5275 | 6.7744 | 25 | 38.5275 | 0 | 0 | 0 | 0 | 0 | 220.2235 | 0 | 1098.0388 | 86.09% | 25 | 0 | 43.5365 | 69.66% | 38.5275
5846 | 467 | 657 | 255 | 6 | 32.7 | 0 | 0 | 0 | 120.3783 | 52.1954 | 0 | 14.0704 | 38.125 | 0 | 0 | 0 | 0 | 0 | 120.3783 | 0 | 1218.4171 | 95.52% | 14.0704 | 0 | 56.25 | 90% | 38.125
5847 | 119 | 459 | 368 | 5.9 | 31.3 | 0 | 0 | 0 | 0 | 33.4741 | 0 | 0 | 33.4741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1218.4171 | 95.52% | 0 | 4.5604 | 51.2029 | 81.92% | 38.0345
5848 | 273 | 451 | 291 | 5.5 | 30.5 | 0 | 0 | 0 | 57.0931 | 35.6298 | 0 | 0 | 35.6298 | 0 | 0 | 0 | 0 | 0 | 57.0931 | 0 | 1275.5102 | 100% | 0 | 2.2501 | 48.7126 | 77.94% | 37.8799
5849 | 577 | 386 | 138 | 4.7 | 30.6 | 0 | 0 | 0 | 0 | 33.5006 | 0 | 0 | 33.5006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 5.6981 | 42.4063 | 67.85% | 39.1988
5850 | 311 | 153 | 76 | 3.7 | 29.3 | 0 | 0 | 0 | 0 | 11.3842 | 0 | 0 | 11.3842 | 0 | 0 | 0 | 80.2083 | 30.2978 | 0 | 80.2083 | 1195.3019 | 93.71% | 0 | 0 | 42.4063 | 67.85% | 41.6819
5851 | 4 | 10 | 9 | 2.5 | 26.6 | 0 | 0 | 0 | 0 | 0.15906 | 0 | 0 | 0.15906 | 0 | 0 | 0 | 103.2486 | 40.3265 | 0 | 103.2486 | 1092.0533 | 85.62% | 0 | 0 | 42.4063 | 67.85% | 40.4856
5852 | 0 | 0 | 0 | 1.2 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4937 | 38.0651 | 0 | 97.4937 | 994.5597 | 77.97% | 0 | 0 | 42.4063 | 67.85% | 38.0651
5853 | 0 | 0 | 0 | 1 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.64 | 35.6195 | 0 | 91.64 | 902.9196 | 70.79% | 0 | 0 | 42.4063 | 67.85% | 35.6195
5854 | 0 | 0 | 0 | 1.1 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6612 | 33.5026 | 0 | 86.6612 | 816.2585 | 63.99% | 0 | 0 | 42.4063 | 67.85% | 33.5026
5855 | 0 | 0 | 0 | 1 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2295 | 34.2188 | 0 | 88.2295 | 728.0289 | 57.08% | 2.0588 | 0 | 44.2665 | 70.83% | 32.1601
5856 | 0 | 0 | 0 | 1.2 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728.0289 | 57.08% | 0 | 9.3502 | 33.9183 | 54.27% | 9.3502
5857 | 0 | 0 | 0 | 1.1 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728.0289 | 57.08% | 0 | 25 | 6.25 | 10% | 25
5858 | 0 | 0 | 0 | 1.2 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8499 | 32.0208 | 0 | 82.8499 | 645.179 | 50.58% | 0 | 0 | 6.25 | 10% | 32.0208
5859 | 0 | 0 | 0 | 0.3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0632 | 35.1516 | 0 | 90.0632 | 555.1158 | 43.52% | 0 | 0 | 6.25 | 10% | 35.1516
5860 | 0 | 0 | 0 | 1.1 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6021 | 38.8575 | 0 | 98.6021 | 456.5137 | 35.79% | 0 | 0 | 6.25 | 10% | 38.8575
5861 | 0 | 0 | 0 | 1.8 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7362 | 41.448 | 0 | 104.7362 | 351.7775 | 27.58% | 0 | 0 | 6.25 | 10% | 41.448
5862 | 2 | 2 | 2 | 2.4 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.9613 | 44.1359 | 0 | 110.9613 | 240.8162 | 18.88% | 0 | 0 | 6.25 | 10% | 44.1359
5863 | 57 | 54 | 40 | 5.3 | 21 | 0 | 0 | 0 | 0 | 1.1398 | 0 | 0 | 1.1398 | 0 | 0 | 0 | 111.9856 | 44.5934 | 0 | 111.9856 | 128.8306 | 10.1% | 0 | 0 | 6.25 | 10% | 45.7333
5864 | 527 | 292 | 96 | 6.1 | 23.6 | 0 | 0 | 0 | 0 | 13.556 | 0 | 0 | 13.556 | 0 | 0 | 0 | 85.5951 | 33.0533 | 0 | 85.5951 | 43.2355 | 3.39% | 0 | 0 | 6.25 | 10% | 46.6093
5865 | 695 | 499 | 116 | 6.5 | 25.9 | 0 | 0 | 0 | 0 | 33.2861 | 0 | 0 | 33.2861 | 0 | 0 | 0 | 43.2355 | 14.8246 | 0 | 43.2355 | 0 | 0% | 0 | 0 | 6.25 | 10% | 48.1106
5866 | 802 | 675 | 115 | 6.1 | 27.5 | 0 | 0 | 0 | 201.819 | 49.5778 | 0 | 0.52579 | 49.0521 | 0 | 0 | 0 | 0 | 0 | 201.819 | 0 | 201.819 | 15.82% | 0.52579 | 0 | 6.7251 | 10.76% | 49.0521
5867 | 839 | 804 | 125 | 7.1 | 28.4 | 0 | 0 | 0 | 223.2542 | 61.8263 | 0 | 13.0917 | 48.7345 | 0 | 0 | 0 | 0 | 0 | 223.2542 | 0 | 425.0732 | 33.33% | 13.0917 | 0 | 18.5542 | 29.69% | 48.7345
5868 | 867 | 880 | 123 | 7.7 | 28.7 | 0 | 0 | 0 | 237.9314 | 69.1014 | 0 | 20.8863 | 48.2151 | 0 | 0 | 0 | 0 | 0 | 237.9314 | 0 | 663.0046 | 51.98% | 20.8863 | 0 | 37.4263 | 59.88% | 48.2151
5869 | 873 | 888 | 119 | 7.6 | 29 | 0 | 0 | 0 | 243.0227 | 48.2025 | 23.4025 | 0 | 48.2025 | 0 | 0 | 0 | 0 | 0 | 243.0227 | 0 | 906.0273 | 71.03% | 0 | 0 | 37.4263 | 59.88% | 48.2025
5870 | 863 | 838 | 115 | 8.1 | 29.2 | 0 | 0 | 0 | 237.8416 | 47.9394 | 21.5151 | 0.25353 | 47.6858 | 0 | 0 | 0 | 0 | 0 | 237.8416 | 0 | 1143.8688 | 89.68% | 0.25353 | 0 | 37.6554 | 60.25% | 47.6858
5871 | 847 | 732 | 105 | 7.9 | 29.4 | 0 | 0 | 0 | 131.6414 | 62.6198 | 0 | 15.9784 | 46.6413 | 0 | 0 | 0 | 0 | 0 | 131.6414 | 0 | 1275.5102 | 100% | 15.9784 | 0 | 52.0929 | 83.35% | 46.6413
5872 | 780 | 570 | 100 | 6.5 | 29.6 | 0 | 0 | 0 | 0 | 50.2617 | 0 | 4.6008 | 45.6609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 4.6008 | 0 | 56.25 | 90% | 45.6609
5873 | 660 | 369 | 86 | 6 | 29.3 | 0 | 0 | 0 | 0 | 33.3203 | 0 | 0 | 33.3203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 12.4255 | 42.4983 | 68% | 45.7458
5874 | 395 | 146 | 53 | 6.1 | 27.9 | 0 | 0 | 0 | 0 | 11.7048 | 0 | 0 | 11.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 14.83 | 23.73% | 36.7048
5875 | 22 | 10 | 8 | 4.6 | 26.1 | 0 | 0 | 0 | 0 | 0.11644 | 0 | 0 | 0.11644 | 0 | 0 | 0 | 111.0194 | 43.6879 | 0 | 111.0194 | 1164.4908 | 91.3% | 0 | 0 | 14.83 | 23.73% | 43.8044
5876 | 0 | 0 | 0 | 2.6 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4061 | 40.5831 | 0 | 103.4061 | 1061.0846 | 83.19% | 0 | 0 | 14.83 | 23.73% | 40.5831
5877 | 0 | 0 | 0 | 3.3 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2388 | 38.4787 | 0 | 98.2388 | 962.8458 | 75.49% | 0 | 0 | 14.83 | 23.73% | 38.4787
5878 | 0 | 0 | 0 | 3.5 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3887 | 36.5067 | 0 | 93.3887 | 869.4571 | 68.17% | 0 | 0 | 14.83 | 23.73% | 36.5067
5879 | 0 | 0 | 0 | 2.7 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0197 | 35.0931 | 0 | 90.0197 | 779.4374 | 61.11% | 0 | 0 | 14.83 | 23.73% | 35.0931
5880 | 0 | 0 | 0 | 3.2 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.3962 | 51.2117 | 0 | 127.3962 | 652.0412 | 51.12% | 16.8302 | 0 | 30.0371 | 48.06% | 34.3814
5881 | 0 | 0 | 0 | 3.7 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 652.0412 | 51.12% | 0 | 0 | 30.0371 | 48.06% | 0
5882 | 0 | 0 | 0 | 1.8 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 652.0412 | 51.12% | 0 | 15.4301 | 12.96 | 20.74% | 15.4301
5883 | 0 | 0 | 0 | 1.4 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.344 | 0 | 127.551 | 524.4902 | 41.12% | 14.4808 | 0 | 26.0443 | 41.67% | 36.8632
5884 | 0 | 0 | 0 | 1.6 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2325 | 40.0539 | 0 | 101.2325 | 423.2577 | 33.18% | 0 | 0 | 26.0443 | 41.67% | 40.0539
5885 | 0 | 0 | 0 | 1.1 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.1748 | 42.1944 | 0 | 106.1748 | 317.0829 | 24.86% | 0 | 0 | 26.0443 | 41.67% | 42.1944
5886 | 8 | 4 | 3 | 1.2 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7455 | 45.0314 | 0 | 112.7455 | 204.3374 | 16.02% | 0 | 0 | 26.0443 | 41.67% | 45.0314
5887 | 303 | 100 | 45 | 1.2 | 21.7 | 0 | 0 | 0 | 0 | 1.5063 | 0 | 0 | 1.5063 | 0 | 0 | 0 | 113.9358 | 45.3732 | 0 | 113.9358 | 90.4016 | 7.087% | 0 | 0 | 26.0443 | 41.67% | 46.8795
5888 | 585 | 295 | 82 | 1.5 | 23.9 | 0 | 0 | 0 | 0 | 13.4851 | 0 | 0 | 13.4851 | 0 | 0 | 0 | 90.4016 | 35.0893 | 0 | 90.4016 | 0 | 0% | 0 | 0 | 26.0443 | 41.67% | 48.5744
5889 | 725 | 498 | 104 | 3.4 | 26.3 | 0 | 0 | 0 | 0 | 33.154 | 2.1316e-14 | 0 | 33.154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 16.846 | 7.4003 | 11.84% | 50
5890 | 798 | 671 | 118 | 3.8 | 28.2 | 0 | 0 | 0 | 0 | 48.9607 | 0 | 0 | 48.9607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 1.0393 | 6.25 | 10% | 50
5891 | 832 | 797 | 128 | 3.6 | 29.6 | 0 | 0 | 0 | 224.3295 | 60.0815 | 0 | 10.0815 | 50 | 0 | 0 | 0 | 0 | 0 | 224.3295 | 0 | 224.3295 | 17.59% | 10.0815 | 0 | 15.3593 | 24.57% | 50
5892 | 853 | 870 | 131 | 3 | 30.7 | 0 | 0 | 0 | 237.6883 | 50 | 15.8895 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 237.6883 | 0 | 462.0178 | 36.22% | 0 | 0 | 15.3593 | 24.57% | 50
5893 | 855 | 880 | 131 | 3.3 | 31.5 | 0 | 0 | 0 | 241.2651 | 68.32 | 0 | 18.32 | 50 | 0 | 0 | 0 | 0 | 0 | 241.2651 | 0 | 703.2828 | 55.14% | 18.32 | 0 | 31.9125 | 51.06% | 50
5894 | 839 | 826 | 130 | 4.8 | 31.5 | 0 | 0 | 0 | 233.3649 | 67.1098 | 0 | 17.438 | 49.6718 | 0 | 0 | 0 | 0 | 0 | 233.3649 | 0 | 936.6477 | 73.43% | 17.438 | 0 | 47.6687 | 76.27% | 49.6718
5895 | 797 | 712 | 127 | 4.7 | 31.2 | 0 | 0 | 0 | 215.3195 | 56.4195 | 3.8849 | 8.0109 | 48.4086 | 0 | 0 | 0 | 0 | 0 | 215.3195 | 0 | 1151.9672 | 90.31% | 8.0109 | 0 | 54.907 | 87.85% | 48.4086
5896 | 718 | 549 | 122 | 6 | 30.1 | 0 | 0 | 0 | 123.543 | 48.4466 | 0 | 1.4863 | 46.9602 | 0 | 0 | 0 | 0 | 0 | 123.543 | 0 | 1275.5102 | 100% | 1.4863 | 0 | 56.25 | 90% | 46.9602
5897 | 391 | 267 | 90 | 5.4 | 28.6 | 0 | 0 | 0 | 0 | 22.8622 | 0 | 0 | 22.8622 | 0 | 0 | 0 | 65.217 | 24.0173 | 0 | 65.217 | 1210.2932 | 94.89% | 0 | 0 | 56.25 | 90% | 46.8795
5898 | 0 | 34 | 33 | 4 | 27 | 0 | 0 | 0 | 0 | 1.6346 | 0 | 0 | 1.6346 | 0 | 0 | 0 | 117.6032 | 46.3841 | 0 | 117.6032 | 1092.69 | 85.67% | 0 | 0 | 56.25 | 90% | 48.0187
5899 | 0 | 6 | 6 | 2.6 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7095 | 44.4631 | 0 | 112.7095 | 979.9804 | 76.83% | 0 | 0 | 56.25 | 90% | 44.4631
5900 | 0 | 0 | 0 | 3.1 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5543 | 41.1304 | 0 | 104.5543 | 875.4261 | 68.63% | 0 | 0 | 56.25 | 90% | 41.1304
5901 | 0 | 0 | 0 | 3.8 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7502 | 39.1848 | 0 | 99.7502 | 775.6759 | 60.81% | 0 | 0 | 56.25 | 90% | 39.1848
5902 | 0 | 0 | 0 | 3.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.0889 | 37.2448 | 0 | 95.0889 | 680.5869 | 53.36% | 0 | 0 | 56.25 | 90% | 37.2448
5903 | 0 | 0 | 0 | 2.3 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.2986 | 21.0202 | 0 | 57.2986 | 623.2883 | 48.87% | 0 | 0 | 56.25 | 90% | 21.0202
5904 | 0 | 0 | 0 | 2.8 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6746 | 34.958 | 0 | 89.6746 | 533.6137 | 41.84% | 0 | 0 | 56.25 | 90% | 34.958
5905 | 0 | 0 | 0 | 2.8 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533.6137 | 41.84% | 0 | 0 | 56.25 | 90% | 0
5906 | 0 | 0 | 0 | 2 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 533.6137 | 41.84% | 0 | 0.0797 | 56.1618 | 89.86% | 0.0797
5907 | 0 | 0 | 0 | 2.2 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4969 | 37.5192 | 0 | 95.4969 | 438.1168 | 34.35% | 0 | 0 | 56.1618 | 89.86% | 37.5192
5908 | 0 | 0 | 0 | 1.4 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.802 | 40.675 | 0 | 102.802 | 335.3149 | 26.29% | 0 | 0 | 56.1618 | 89.86% | 40.675
5909 | 0 | 0 | 0 | 1.6 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7323 | 42.8156 | 0 | 107.7323 | 227.5825 | 17.84% | 0 | 0 | 56.1618 | 89.86% | 42.8156
5910 | 3 | 3 | 3 | 1.6 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.0092 | 45.5383 | 0 | 114.0092 | 113.5733 | 8.904% | 0 | 0 | 56.1618 | 89.86% | 45.5383
5911 | 235 | 95 | 53 | 1.1 | 21.2 | 0 | 0 | 0 | 0 | 1.8711 | 0 | 0 | 1.8711 | 0 | 0 | 0 | 113.5733 | 45.2604 | 0 | 113.5733 | 0 | 0% | 0 | 0 | 56.1618 | 89.86% | 47.1315
5912 | 497 | 287 | 107 | 2.5 | 23 | 0 | 0 | 0 | 82.0603 | 13.9939 | 0 | 0 | 13.9939 | 0 | 0 | 0 | 0 | 0 | 82.0603 | 0 | 82.0603 | 6.434% | 0 | 25 | 28.4935 | 45.59% | 38.9939
5913 | 641 | 483 | 137 | 2.6 | 24.5 | 0 | 0 | 0 | 0 | 32.733 | 0 | 0 | 32.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0603 | 6.434% | 0 | 17.267 | 9.3835 | 15.01% | 50
5914 | 716 | 659 | 163 | 1.3 | 27 | 0 | 0 | 0 | 134.2445 | 47.1687 | 0 | 0 | 47.1687 | 0 | 0 | 0 | 0 | 0 | 134.2445 | 0 | 216.3049 | 16.96% | 0 | 2.8313 | 6.25 | 10% | 50
5915 | 755 | 782 | 175 | 1.7 | 28.6 | 0 | 0 | 0 | 202.9939 | 57.8929 | 0 | 7.8929 | 50 | 0 | 0 | 0 | 0 | 0 | 202.9939 | 0 | 419.2987 | 32.87% | 7.8929 | 0 | 13.3818 | 21.41% | 50
5916 | 770 | 863 | 196 | 2.5 | 30.1 | 0 | 0 | 0 | 212.9562 | 60.9348 | 4.9045 | 10.9348 | 50 | 0 | 0 | 0 | 0 | 0 | 212.9562 | 0 | 632.2549 | 49.57% | 10.9348 | 0 | 23.262 | 37.22% | 50
5917 | 719 | 873 | 244 | 5.1 | 30.4 | 0 | 0 | 0 | 198.4511 | 69.8202 | 0 | 19.8685 | 49.9517 | 0 | 0 | 0 | 0 | 0 | 198.4511 | 0 | 830.706 | 65.13% | 19.8685 | 0 | 41.2144 | 65.94% | 49.9517
5918 | 461 | 653 | 268 | 5.6 | 29.5 | 0 | 0 | 0 | 118.7352 | 53.3788 | 0 | 3.8337 | 49.5451 | 0 | 0 | 0 | 0 | 0 | 118.7352 | 0 | 949.4413 | 74.44% | 3.8337 | 0 | 44.6783 | 71.49% | 49.5451
5919 | 643 | 732 | 258 | 6.2 | 29.1 | 0 | 0 | 0 | 168.7632 | 61.1708 | 0 | 12.8068 | 48.3641 | 0 | 0 | 0 | 0 | 0 | 168.7632 | 0 | 1118.2045 | 87.67% | 12.8068 | 0 | 56.25 | 90% | 48.3641
5920 | 629 | 564 | 192 | 5.7 | 28.6 | 0 | 0 | 0 | 157.3057 | 47.0675 | 2.0008 | 0 | 47.0675 | 0 | 0 | 0 | 0 | 0 | 157.3057 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 47.0675
5921 | 122 | 165 | 108 | 4.9 | 26.6 | 0 | 0 | 0 | 0 | 12.4442 | 0 | 0 | 12.4442 | 0 | 0 | 0 | 90.2012 | 34.7764 | 0 | 90.2012 | 1185.309 | 92.93% | 0 | 0 | 56.25 | 90% | 47.2207
5922 | 0 | 16 | 16 | 4.7 | 25.2 | 0 | 0 | 0 | 0 | 0.59281 | 0 | 0 | 0.59281 | 0 | 0 | 0 | 119.9599 | 47.6014 | 0 | 119.9599 | 1065.3491 | 83.52% | 0 | 0 | 56.25 | 90% | 48.1942
5923 | 0 | 4 | 4 | 2.1 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7732 | 44.6679 | 0 | 112.7732 | 952.5759 | 74.68% | 0 | 0 | 56.25 | 90% | 44.6679
5924 | 0 | 0 | 0 | 0.4 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9029 | 41.3073 | 0 | 104.9029 | 847.673 | 66.46% | 0 | 0 | 56.25 | 90% | 41.3073
5925 | 0 | 0 | 0 | 1.4 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4573 | 39.4035 | 0 | 100.4573 | 747.2157 | 58.58% | 0 | 0 | 56.25 | 90% | 39.4035
5926 | 0 | 0 | 0 | 1 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747.2157 | 58.58% | 0 | 0 | 56.25 | 90% | 0
5927 | 0 | 0 | 0 | 1.5 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747.2157 | 58.58% | 0 | 0 | 56.25 | 90% | 0
5928 | 0 | 0 | 0 | 1.1 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747.2157 | 58.58% | 0 | 0 | 56.25 | 90% | 0
5929 | 0 | 0 | 0 | 0.8 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747.2157 | 58.58% | 0 | 0 | 56.25 | 90% | 0
5930 | 0 | 0 | 0 | 1.4 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747.2157 | 58.58% | 0 | 0 | 56.25 | 90% | 0
5931 | 0 | 0 | 0 | 1 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 747.2157 | 58.58% | 0 | 0 | 56.25 | 90% | 0
5932 | 0 | 0 | 0 | 1.4 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.5197 | 40.455 | 0 | 102.5197 | 644.696 | 50.54% | 0 | 0 | 56.25 | 90% | 40.455
5933 | 0 | 0 | 0 | 1.7 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.0052 | 42.3504 | 0 | 107.0052 | 537.6908 | 42.15% | 0 | 0 | 56.25 | 90% | 42.3504
5934 | 0 | 2 | 1 | 1.5 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.6511 | 44.7584 | 0 | 112.6511 | 425.0396 | 33.32% | 0 | 0 | 56.25 | 90% | 44.7584
5935 | 0 | 31 | 31 | 1.4 | 22.6 | 0 | 0 | 0 | 0 | 0.85949 | 0 | 0 | 0.85949 | 0 | 0 | 0 | 113.2869 | 45.0131 | 0 | 113.2869 | 311.7528 | 24.44% | 0 | 0 | 56.25 | 90% | 45.8725
5936 | 256 | 271 | 173 | 2 | 23.8 | 0 | 0 | 0 | 0 | 14.7325 | 0 | 0 | 14.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311.7528 | 24.44% | 0 | 0 | 56.25 | 90% | 14.7325
5937 | 399 | 473 | 253 | 2.5 | 25.3 | 0 | 0 | 0 | 81.8264 | 31.7303 | 0 | 0 | 31.7303 | 0 | 0 | 0 | 0 | 0 | 81.8264 | 0 | 393.5792 | 30.86% | 0 | 0 | 56.25 | 90% | 31.7303
5938 | 450 | 555 | 241 | 2.7 | 26.5 | 0 | 0 | 0 | 106.7414 | 40.525 | 0 | 0 | 40.525 | 0 | 0 | 0 | 0 | 0 | 106.7414 | 0 | 500.3206 | 39.23% | 0 | 8.5215 | 46.819 | 74.91% | 49.0465
5939 | 591 | 762 | 284 | 2.8 | 27.9 | 0 | 0 | 0 | 154.5793 | 56.7559 | 0 | 8.6091 | 48.1468 | 0 | 0 | 0 | 0 | 0 | 154.5793 | 0 | 654.8998 | 51.34% | 8.6091 | 0 | 54.5978 | 87.36% | 48.1468
5940 | 230 | 603 | 399 | 4.6 | 28.3 | 0 | 0 | 0 | 49.0489 | 44.3758 | 0 | 0 | 44.3758 | 0 | 0 | 0 | 0 | 0 | 49.0489 | 0 | 703.9488 | 55.19% | 0 | 0 | 54.5978 | 87.36% | 44.3758
5941 | 196 | 570 | 391 | 5.2 | 28.3 | 0 | 0 | 0 | 39.2716 | 42.2858 | 0 | 0 | 42.2858 | 0 | 0 | 0 | 0 | 0 | 39.2716 | 0 | 743.2203 | 58.27% | 0 | 0.43948 | 54.1114 | 86.58% | 42.7252
5942 | 46 | 324 | 280 | 5.1 | 27.9 | 0 | 0 | 0 | 0 | 22.0822 | 0 | 0 | 22.0822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743.2203 | 58.27% | 0 | 24.7304 | 26.7414 | 42.79% | 46.8126
5943 | 1 | 122 | 120 | 5.2 | 26.6 | 0 | 0 | 0 | 0 | 7.1601 | 0 | 0 | 7.1601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743.2203 | 58.27% | 0 | 0 | 26.7414 | 42.79% | 7.1601
5944 | 7 | 192 | 187 | 5 | 26 | 0 | 0 | 0 | 0 | 12.0572 | 0 | 0 | 12.0572 | 0 | 0 | 0 | 85.8361 | 32.97 | 0 | 85.8361 | 657.3843 | 51.54% | 0 | 0 | 26.7414 | 42.79% | 45.0272
5945 | 149 | 203 | 136 | 5 | 25.8 | 0 | 0 | 0 | 0 | 15.2099 | 0 | 0 | 15.2099 | 0 | 0 | 0 | 79.6097 | 30.3326 | 0 | 79.6097 | 577.7746 | 45.3% | 0 | 0 | 26.7414 | 42.79% | 45.5425
5946 | 77 | 105 | 90 | 4.8 | 24.9 | 0 | 0 | 0 | 0 | 7.2829 | 0 | 0 | 7.2829 | 0 | 0 | 0 | 100.6687 | 39.3947 | 0 | 100.6687 | 477.1059 | 37.41% | 0 | 0 | 26.7414 | 42.79% | 46.6775
5947 | 0 | 11 | 11 | 4.8 | 23.9 | 0 | 0 | 0 | 0 | 0.24858 | 0 | 0 | 0.24858 | 0 | 0 | 0 | 56.7827 | 20.6951 | 0 | 56.7827 | 420.3232 | 32.95% | 0 | 0 | 26.7414 | 42.79% | 20.9437
5948 | 0 | 0 | 0 | 4.6 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.3232 | 32.95% | 0 | 0 | 26.7414 | 42.79% | 0
5949 | 0 | 0 | 0 | 3.5 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.3232 | 32.95% | 0 | 0 | 26.7414 | 42.79% | 0
5950 | 0 | 0 | 0 | 2.4 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.3232 | 32.95% | 0 | 0 | 26.7414 | 42.79% | 0
5951 | 0 | 0 | 0 | 1.2 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.3232 | 32.95% | 0 | 0 | 26.7414 | 42.79% | 0
5952 | 0 | 0 | 0 | 1 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 420.3232 | 32.95% | 0 | 0 | 26.7414 | 42.79% | 0
5953 | 0 | 0 | 0 | 1.7 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.3232 | 32.95% | 0 | 0 | 26.7414 | 42.79% | 0
5954 | 0 | 0 | 0 | 1.6 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.3232 | 32.95% | 0 | 0 | 26.7414 | 42.79% | 0
5955 | 0 | 0 | 0 | 1.3 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.3232 | 32.95% | 0 | 0 | 26.7414 | 42.79% | 0
5956 | 0 | 0 | 0 | 0.7 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.6245 | 39.3728 | 0 | 99.6245 | 320.6987 | 25.14% | 0 | 0 | 26.7414 | 42.79% | 39.3728
5957 | 0 | 0 | 0 | 0.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.5111 | 41.0845 | 0 | 103.5111 | 217.1876 | 17.03% | 0 | 0 | 26.7414 | 42.79% | 41.0845
5958 | 4 | 3 | 3 | 1.6 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.028 | 43.4688 | 0 | 109.028 | 108.1595 | 8.48% | 0 | 0 | 26.7414 | 42.79% | 43.4688
5959 | 261 | 92 | 46 | 1.7 | 20 | 0 | 0 | 0 | 0 | 1.5774 | 0 | 0 | 1.5774 | 0 | 0 | 0 | 108.1595 | 43.0222 | 0 | 108.1595 | 0 | 0% | 0 | 0 | 26.7414 | 42.79% | 44.5996
5960 | 563 | 290 | 89 | 2.4 | 22.2 | 0 | 0 | 0 | 94.7091 | 14.0837 | 0 | 0 | 14.0837 | 0 | 0 | 0 | 0 | 0 | 94.7091 | 0 | 94.7091 | 7.425% | 0 | 0 | 26.7414 | 42.79% | 14.0837
5961 | 546 | 423 | 133 | 4 | 24.1 | 0 | 0 | 0 | 117.6928 | 29.4126 | 0 | 0 | 29.4126 | 0 | 0 | 0 | 0 | 0 | 117.6928 | 0 | 212.4019 | 16.65% | 0 | 17.251 | 7.6492 | 12.24% | 46.6636
5962 | 658 | 612 | 155 | 4.5 | 25.1 | 0 | 0 | 0 | 163.1679 | 46.0219 | 0 | 0 | 46.0219 | 0 | 0 | 0 | 0 | 0 | 163.1679 | 0 | 375.5698 | 29.44% | 0 | 1.2643 | 6.25 | 10% | 47.2861
5963 | 800 | 818 | 179 | 4.3 | 26.6 | 0 | 0 | 0 | 214.4222 | 63.3927 | 0 | 17.1093 | 46.2834 | 0 | 0 | 0 | 0 | 0 | 214.4222 | 0 | 589.992 | 46.26% | 17.1093 | 0 | 21.7093 | 34.73% | 46.2834
5964 | 678 | 876 | 290 | 3.2 | 27.7 | 0 | 0 | 0 | 185.1002 | 55.5267 | 11.9093 | 10.1248 | 45.4018 | 0 | 0 | 0 | 0 | 0 | 185.1002 | 0 | 775.0922 | 60.77% | 10.1248 | 0 | 30.8577 | 49.37% | 45.4018
5965 | 733 | 917 | 278 | 4.7 | 28.2 | 0 | 0 | 0 | 202.8469 | 70.0745 | 1.9255 | 25 | 45.0745 | 0 | 0 | 0 | 0 | 0 | 202.8469 | 0 | 977.939 | 76.67% | 25 | 0 | 53.4467 | 85.51% | 45.0745
5966 | 336 | 606 | 323 | 5.2 | 28.3 | 0 | 0 | 0 | 81.1999 | 47.8526 | 0 | 3.1025 | 44.75 | 0 | 0 | 0 | 0 | 0 | 81.1999 | 0 | 1059.1389 | 83.04% | 3.1025 | 0 | 56.25 | 90% | 44.75
5967 | 271 | 426 | 237 | 4.7 | 27.7 | 0 | 0 | 0 | 60.4891 | 35.189 | 0 | 0 | 35.189 | 0 | 0 | 0 | 0 | 0 | 60.4891 | 0 | 1119.628 | 87.78% | 0 | 0 | 56.25 | 90% | 35.189
5968 | 299 | 345 | 170 | 4.4 | 28.1 | 0 | 0 | 0 | 65.0653 | 29.495 | 0 | 0 | 29.495 | 0 | 0 | 0 | 0 | 0 | 65.0653 | 0 | 1184.6934 | 92.88% | 0 | 0 | 56.25 | 90% | 29.495
5969 | 293 | 215 | 103 | 5.5 | 27.2 | 0 | 0 | 0 | 55.174 | 19.6271 | 0 | 0 | 19.6271 | 0 | 0 | 0 | 0 | 0 | 55.174 | 0 | 1239.8674 | 97.21% | 0 | 20.178 | 33.9183 | 54.27% | 39.8051
5970 | 267 | 122 | 62 | 5.6 | 25.9 | 0 | 0 | 0 | 35.6428 | 9.5714 | 0 | 0 | 9.5714 | 0 | 0 | 0 | 0 | 0 | 35.6428 | 0 | 1275.5102 | 100% | 0 | 25 | 6.25 | 10% | 34.5714
5971 | 0 | 6 | 6 | 4.7 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7519 | 41.2335 | 0 | 104.7519 | 1170.7583 | 91.79% | 0 | 0 | 6.25 | 10% | 41.2335
5972 | 0 | 0 | 0 | 5.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.7261 | 38.3785 | 0 | 97.7261 | 1073.0322 | 84.13% | 0 | 0 | 6.25 | 10% | 38.3785
5973 | 0 | 0 | 0 | 4.8 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.1243 | 36.866 | 0 | 94.1243 | 978.9078 | 76.75% | 0 | 0 | 6.25 | 10% | 36.866
5974 | 0 | 0 | 0 | 3.3 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 978.9078 | 76.75% | 0 | 0 | 6.25 | 10% | 0
5975 | 0 | 0 | 0 | 3.6 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 978.9078 | 76.75% | 0 | 0 | 6.25 | 10% | 0
5976 | 0 | 0 | 0 | 3.9 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 978.9078 | 76.75% | 0 | 0 | 6.25 | 10% | 0
5977 | 0 | 0 | 0 | 3.1 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 978.9078 | 76.75% | 0 | 0 | 6.25 | 10% | 0
5978 | 0 | 0 | 0 | 4 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 978.9078 | 76.75% | 0 | 0 | 6.25 | 10% | 0
5979 | 0 | 0 | 0 | 3.1 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 978.9078 | 76.75% | 0 | 0 | 6.25 | 10% | 0
5980 | 0 | 0 | 0 | 3.9 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 978.9078 | 76.75% | 0 | 0 | 6.25 | 10% | 0
5981 | 0 | 0 | 0 | 3.7 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2974 | 0 | 127.551 | 851.3568 | 66.75% | 17.4369 | 0 | 22.0052 | 35.21% | 33.8606
5982 | 2 | 3 | 3 | 4.1 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2783 | 0 | 127.551 | 723.8058 | 56.75% | 14.6185 | 0 | 35.2139 | 56.34% | 36.6599
5983 | 266 | 96 | 48 | 4.2 | 21.3 | 0 | 0 | 0 | 0 | 1.8831 | 0 | 1.8831 | 0 | 0 | 0 | 0 | 113.2123 | 45.0965 | 0 | 113.2123 | 610.5935 | 47.87% | 8.1374 | 0 | 42.5665 | 68.11% | 38.8422
5984 | 494 | 280 | 107 | 4.2 | 22.8 | 0 | 0 | 0 | 79.1649 | 14.309 | 0 | 0 | 14.309 | 0 | 0 | 0 | 0 | 0 | 79.1649 | 0 | 689.7584 | 54.08% | 0 | 25 | 14.8982 | 23.84% | 39.309
5985 | 287 | 403 | 247 | 5.2 | 23.5 | 0 | 0 | 0 | 51.2666 | 27.7264 | 0 | 0 | 27.7264 | 0 | 0 | 0 | 0 | 0 | 51.2666 | 0 | 741.025 | 58.1% | 0 | 6.0953 | 8.1524 | 13.04% | 33.8217
5986 | 468 | 599 | 267 | 5.9 | 24.6 | 0 | 0 | 0 | 109.1962 | 44.4143 | 0 | 3.3966 | 41.0176 | 0 | 0 | 0 | 0 | 0 | 109.1962 | 0 | 850.2212 | 66.66% | 3.3966 | 0 | 11.2214 | 17.95% | 41.0176
5987 | 308 | 592 | 344 | 6.6 | 25.3 | 0 | 0 | 0 | 68.616 | 45.2692 | 0 | 4.7446 | 40.5246 | 0 | 0 | 0 | 0 | 0 | 68.616 | 0 | 918.8372 | 72.04% | 4.7446 | 0 | 15.5084 | 24.81% | 40.5246
5988 | 128 | 595 | 475 | 6.6 | 25.8 | 0 | 0 | 0 | 0 | 42.8005 | 0 | 3.7688 | 39.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 918.8372 | 72.04% | 3.7688 | 0 | 18.9138 | 30.26% | 39.0316
5989 | 299 | 711 | 442 | 7.3 | 26.2 | 0 | 0 | 0 | 68.7106 | 55.3798 | 0 | 17.1183 | 38.2615 | 0 | 0 | 0 | 0 | 0 | 68.7106 | 0 | 987.5478 | 77.42% | 17.1183 | 0 | 34.3812 | 55.01% | 38.2615
5990 | 240 | 609 | 405 | 7.4 | 26.1 | 0 | 0 | 0 | 49.9401 | 46.8263 | 0 | 8.8294 | 37.9969 | 0 | 0 | 0 | 0 | 0 | 49.9401 | 0 | 1037.4879 | 81.34% | 8.8294 | 0 | 42.3591 | 67.77% | 37.9969
5991 | 251 | 522 | 339 | 8 | 25.5 | 0 | 0 | 0 | 51.1307 | 42.1684 | 0 | 4.4654 | 37.703 | 0 | 0 | 0 | 0 | 0 | 51.1307 | 0 | 1088.6186 | 85.35% | 4.4654 | 0 | 46.3938 | 74.23% | 37.703
5992 | 312 | 411 | 230 | 8 | 25.2 | 0 | 0 | 0 | 65.3415 | 34.4098 | 0 | 0 | 34.4098 | 0 | 0 | 0 | 0 | 0 | 65.3415 | 0 | 1153.9601 | 90.47% | 0 | 0 | 46.3938 | 74.23% | 34.4098
5993 | 420 | 325 | 157 | 7.5 | 25.2 | 0 | 0 | 0 | 86.2973 | 29.0964 | 0 | 0 | 29.0964 | 0 | 0 | 0 | 0 | 0 | 86.2973 | 0 | 1240.2574 | 97.24% | 0 | 9.5898 | 35.7804 | 57.25% | 38.6862
5994 | 270 | 125 | 66 | 7.7 | 23.6 | 0 | 0 | 0 | 35.2528 | 10.0192 | 0 | 0 | 10.0192 | 0 | 0 | 0 | 0 | 0 | 35.2528 | 0 | 1275.5102 | 100% | 0 | 25 | 8.1121 | 12.98% | 35.0192
5995 | 10 | 11 | 10 | 7.8 | 22 | 0 | 0 | 0 | 0 | 0.19761 | 0 | 0 | 0.19761 | 0 | 0 | 0 | 96.7902 | 37.9761 | 0 | 96.7902 | 1178.72 | 92.41% | 0 | 0 | 8.1121 | 12.98% | 38.1737
5996 | 0 | 0 | 0 | 8.6 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5881 | 35.795 | 0 | 91.5881 | 1087.1319 | 85.23% | 0 | 0 | 8.1121 | 12.98% | 35.795
5997 | 0 | 0 | 0 | 6.9 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5268 | 34.0778 | 0 | 87.5268 | 999.6052 | 78.37% | 0 | 0 | 8.1121 | 12.98% | 34.0778
5998 | 0 | 0 | 0 | 4.8 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0631 | 32.1601 | 0 | 83.0631 | 916.5421 | 71.86% | 0 | 0 | 8.1121 | 12.98% | 32.1601
5999 | 0 | 0 | 0 | 3.8 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916.5421 | 71.86% | 0 | 0 | 8.1121 | 12.98% | 0
6000 | 0 | 0 | 0 | 4 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916.5421 | 71.86% | 0 | 0 | 8.1121 | 12.98% | 0
6001 | 0 | 0 | 0 | 2.2 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916.5421 | 71.86% | 0 | 0 | 8.1121 | 12.98% | 0
6002 | 0 | 0 | 0 | 1.9 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916.5421 | 71.86% | 0 | 0 | 8.1121 | 12.98% | 0
6003 | 0 | 0 | 0 | 0.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916.5421 | 71.86% | 0 | 0 | 8.1121 | 12.98% | 0
6004 | 0 | 0 | 0 | 2.3 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916.5421 | 71.86% | 0 | 0 | 8.1121 | 12.98% | 0
6005 | 0 | 0 | 0 | 2.3 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 916.5421 | 71.86% | 0 | 0 | 8.1121 | 12.98% | 0
6006 | 0 | 2 | 2 | 3.3 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916.5421 | 71.86% | 0 | 0 | 8.1121 | 12.98% | 0
6007 | 37 | 68 | 61 | 3.6 | 19.7 | 0 | 0 | 0 | 0 | 2.5287 | 0 | 2.5287 | 0 | 0 | 0 | 0 | 96.3811 | 37.9596 | 0 | 96.3811 | 820.161 | 64.3% | 6.3324 | 0 | 13.8338 | 22.13% | 34.1558
6008 | 208 | 234 | 168 | 5.1 | 21.9 | 0 | 0 | 0 | 0 | 14.1946 | 0 | 0 | 14.1946 | 0 | 0 | 0 | 57.9183 | 21.2704 | 0 | 57.9183 | 762.2427 | 59.76% | 0 | 0 | 13.8338 | 22.13% | 35.4649
6009 | 4 | 236 | 231 | 5.5 | 22.5 | 0 | 0 | 0 | 0 | 15.4664 | 0 | 0 | 15.4664 | 0 | 0 | 0 | 56.9557 | 20.8314 | 0 | 56.9557 | 705.287 | 55.29% | 0 | 0 | 13.8338 | 22.13% | 36.2978
6010 | 89 | 434 | 363 | 5.9 | 23.5 | 0 | 0 | 0 | 0 | 30.3687 | 0 | 0 | 30.3687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.287 | 55.29% | 0 | 6.8524 | 6.25 | 10% | 37.2211
6011 | 473 | 741 | 352 | 6.2 | 25.1 | 0 | 0 | 0 | 117.4019 | 38.804 | 17.185 | 1.4241 | 37.3799 | 0 | 0 | 0 | 0 | 0 | 117.4019 | 0 | 822.6888 | 64.5% | 1.4241 | 0 | 7.5368 | 12.06% | 37.3799
6012 | 115 | 659 | 547 | 6.2 | 26 | 0 | 0 | 0 | 0 | 47.4483 | 0 | 11.3163 | 36.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822.6888 | 64.5% | 11.3163 | 0 | 17.7617 | 28.42% | 36.132
6013 | 266 | 728 | 486 | 6.4 | 26.5 | 0 | 0 | 0 | 59.8537 | 54.9284 | 0 | 19.4606 | 35.4677 | 0 | 0 | 0 | 0 | 0 | 59.8537 | 0 | 882.5425 | 69.19% | 19.4606 | 0 | 35.3455 | 56.55% | 35.4677
6014 | 158 | 500 | 363 | 6.5 | 26.2 | 0 | 0 | 0 | 0 | 34.9664 | 2.8503 | 0 | 34.9664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 882.5425 | 69.19% | 0 | 0 | 35.3455 | 56.55% | 34.9664
6015 | 340 | 524 | 287 | 6 | 26.2 | 0 | 0 | 0 | 79.3077 | 43.7651 | 0 | 8.8809 | 34.8842 | 0 | 0 | 0 | 0 | 0 | 79.3077 | 0 | 961.8502 | 75.41% | 8.8809 | 0 | 43.37 | 69.39% | 34.8842
6016 | 692 | 544 | 145 | 5.6 | 26.9 | 0 | 0 | 0 | 174.4858 | 49.4411 | 0 | 14.2547 | 35.1864 | 0 | 0 | 0 | 0 | 0 | 174.4858 | 0 | 1136.336 | 89.09% | 14.2547 | 0 | 56.25 | 90% | 35.1864
6017 | 479 | 319 | 122 | 4.1 | 26.5 | 0 | 0 | 0 | 103.9727 | 28.5044 | 0 | 0 | 28.5044 | 0 | 0 | 0 | 0 | 0 | 103.9727 | 0 | 1240.3087 | 97.24% | 0 | 0 | 56.25 | 90% | 28.5044
6018 | 254 | 131 | 72 | 4 | 25.6 | 0 | 0 | 0 | 35.2015 | 10.0183 | 0 | 0 | 10.0183 | 0 | 0 | 0 | 0 | 0 | 35.2015 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 35.0183
6019 | 1 | 6 | 6 | 4.1 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2801 | 38.0679 | 0 | 97.2801 | 1178.2301 | 92.37% | 0 | 0 | 28.5817 | 45.73% | 38.0679
6020 | 0 | 0 | 0 | 3.4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7487 | 35.8089 | 0 | 91.7487 | 1086.4814 | 85.18% | 0 | 0 | 28.5817 | 45.73% | 35.8089
6021 | 0 | 0 | 0 | 2 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4496 | 33.589 | 0 | 86.4496 | 1000.0318 | 78.4% | 0 | 0 | 28.5817 | 45.73% | 33.589
6022 | 0 | 0 | 0 | 2.4 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1919 | 32.2214 | 0 | 83.1919 | 916.8399 | 71.88% | 0 | 0 | 28.5817 | 45.73% | 32.2214
6023 | 0 | 0 | 0 | 1.7 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6044 | 31.117 | 0 | 80.6044 | 836.2355 | 65.56% | 0 | 0 | 28.5817 | 45.73% | 31.117
6024 | 0 | 0 | 0 | 1.5 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5258 | 30.6518 | 0 | 79.5258 | 756.7097 | 59.33% | 0 | 0 | 28.5817 | 45.73% | 30.6518
6025 | 0 | 0 | 0 | 1.4 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3572 | 30.6003 | 0 | 79.3572 | 677.3525 | 53.1% | 0 | 0 | 28.5817 | 45.73% | 30.6003
6026 | 0 | 0 | 0 | 1.1 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9328 | 31.3064 | 0 | 80.9328 | 596.4198 | 46.76% | 0 | 0 | 28.5817 | 45.73% | 31.3064
6027 | 0 | 0 | 0 | 0.2 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.7183 | 45.9567 | 0 | 114.7183 | 481.7014 | 37.77% | 11.6909 | 0 | 39.1451 | 62.63% | 34.2658
6028 | 0 | 0 | 0 | 0.2 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8126 | 37.7573 | 0 | 95.8126 | 385.8889 | 30.25% | 0 | 0 | 39.1451 | 62.63% | 37.7573
6029 | 0 | 0 | 0 | 0.5 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.3311 | 39.7349 | 0 | 100.3311 | 285.5578 | 22.39% | 0 | 0 | 39.1451 | 62.63% | 39.7349
6030 | 2 | 2 | 2 | 0.5 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.56 | 0 | 127.551 | 158.0068 | 12.39% | 9.6594 | 0 | 47.8729 | 76.6% | 41.9006
6031 | 232 | 93 | 53 | 0.7 | 18.7 | 0 | 0 | 0 | 0 | 2.1417 | 0 | 0 | 2.1417 | 0 | 0 | 0 | 103.4896 | 41.0945 | 0 | 103.4896 | 54.5172 | 4.274% | 0 | 0 | 47.8729 | 76.6% | 43.2362
6032 | 504 | 275 | 94 | 0.6 | 22 | 0 | 0 | 0 | 82.5912 | 13.5898 | 0 | 0 | 13.5898 | 0 | 0 | 0 | 0 | 0 | 82.5912 | 0 | 137.1084 | 10.75% | 0 | 25 | 20.2046 | 32.33% | 38.5898
6033 | 688 | 476 | 111 | 1.1 | 23.8 | 0 | 0 | 0 | 154.4362 | 32.7679 | 0 | 0 | 32.7679 | 0 | 0 | 0 | 0 | 0 | 154.4362 | 0 | 291.5445 | 22.86% | 0 | 12.6088 | 6.25 | 10% | 45.3767
6034 | 799 | 661 | 118 | 1.6 | 25.5 | 0 | 0 | 0 | 204 | 48.938 | 0 | 3.0613 | 45.8767 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 495.5445 | 38.85% | 3.0613 | 0 | 9.0161 | 14.43% | 45.8767
6035 | 836 | 802 | 142 | 1.8 | 26.9 | 0 | 0 | 0 | 226.6487 | 60.852 | 0 | 15.8582 | 44.9938 | 0 | 0 | 0 | 0 | 0 | 226.6487 | 0 | 722.1932 | 56.62% | 15.8582 | 0 | 23.3449 | 37.35% | 44.9938
6036 | 562 | 833 | 351 | 3.6 | 28.3 | 0 | 0 | 0 | 149.9784 | 64.4892 | 0 | 20.3882 | 44.101 | 0 | 0 | 0 | 0 | 0 | 149.9784 | 0 | 872.1716 | 68.38% | 20.3882 | 0 | 41.7669 | 66.83% | 44.101
6037 | 57 | 413 | 357 | 3.7 | 27.5 | 0 | 0 | 0 | 0 | 28.6448 | 0 | 0 | 28.6448 | 0 | 0 | 0 | 44.5772 | 15.3323 | 0 | 44.5772 | 827.5943 | 64.88% | 0 | 0 | 41.7669 | 66.83% | 43.9771
6038 | 1 | 122 | 120 | 3.4 | 25.5 | 0 | 0 | 0 | 0 | 7.1723 | 0 | 0 | 7.1723 | 0 | 0 | 0 | 94.0707 | 36.5234 | 0 | 94.0707 | 733.5236 | 57.51% | 0 | 0 | 41.7669 | 66.83% | 43.6958
6039 | 4 | 182 | 178 | 5 | 24.4 | 0 | 0 | 0 | 0 | 11.3251 | 0 | 0 | 11.3251 | 0 | 0 | 0 | 83.1575 | 31.9515 | 0 | 83.1575 | 650.3662 | 50.99% | 0 | 0 | 41.7669 | 66.83% | 43.2766
6040 | 270 | 430 | 268 | 3.8 | 25.6 | 0 | 0 | 0 | 56.966 | 34.4836 | 0 | 0 | 34.4836 | 0 | 0 | 0 | 0 | 0 | 56.966 | 0 | 707.3322 | 55.45% | 0 | 7.0916 | 33.9183 | 54.27% | 41.5753
6041 | 56 | 186 | 163 | 2.1 | 26.5 | 0 | 0 | 0 | 0 | 12.8029 | 0 | 0 | 12.8029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707.3322 | 55.45% | 0 | 25 | 6.25 | 10% | 37.8029
6042 | 6 | 56 | 55 | 2.3 | 26.2 | 0 | 0 | 0 | 0 | 3.1514 | 0 | 0 | 3.1514 | 0 | 0 | 0 | 106.5018 | 41.7532 | 0 | 106.5018 | 600.8304 | 47.11% | 0 | 0 | 6.25 | 10% | 44.9046
6043 | 16 | 9 | 8 | 2.1 | 25.7 | 0 | 0 | 0 | 0 | 0.067365 | 0 | 0 | 0.067365 | 0 | 0 | 0 | 104.6526 | 41.0171 | 0 | 104.6526 | 496.1779 | 38.9% | 0 | 0 | 6.25 | 10% | 41.0845
6044 | 0 | 0 | 0 | 3.4 | 24.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8684 | 30.9937 | 0 | 80.8684 | 415.3094 | 32.56% | 0 | 0 | 6.25 | 10% | 30.9937
6045 | 0 | 0 | 0 | 2.8 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.3094 | 32.56% | 0 | 0 | 6.25 | 10% | 0
6046 | 0 | 0 | 0 | 3 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.3094 | 32.56% | 0 | 0 | 6.25 | 10% | 0
6047 | 0 | 0 | 0 | 2.2 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.3094 | 32.56% | 0 | 0 | 6.25 | 10% | 0
6048 | 0 | 0 | 0 | 1 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.3094 | 32.56% | 0 | 0 | 6.25 | 10% | 0
6049 | 0 | 0 | 0 | 0.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.3094 | 32.56% | 0 | 0 | 6.25 | 10% | 0
6050 | 0 | 0 | 0 | 3.8 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.3094 | 32.56% | 0 | 0 | 6.25 | 10% | 0
6051 | 0 | 0 | 0 | 2.3 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.3094 | 32.56% | 0 | 0 | 6.25 | 10% | 0
6052 | 0 | 0 | 0 | 2.5 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.6534 | 39.1834 | 0 | 99.6534 | 315.6561 | 24.75% | 0 | 0 | 6.25 | 10% | 39.1834
6053 | 0 | 0 | 0 | 3.8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1095 | 41.0385 | 0 | 104.1095 | 211.5465 | 16.59% | 0 | 0 | 6.25 | 10% | 41.0385
6054 | 5 | 2 | 2 | 2.2 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.1199 | 42.8964 | 0 | 108.1199 | 103.4266 | 8.109% | 0 | 0 | 6.25 | 10% | 42.8964
6055 | 231 | 99 | 69 | 2.8 | 21.4 | 0 | 0 | 0 | 0 | 2.8959 | 0 | 0 | 2.8959 | 0 | 0 | 0 | 103.4266 | 40.8765 | 0 | 103.4266 | 0 | 0% | 0 | 0 | 6.25 | 10% | 43.7724
6056 | 71 | 164 | 137 | 4.6 | 23.1 | 0 | 0 | 0 | 0 | 9.9337 | 0 | 0 | 9.9337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 9.9337
6057 | 216 | 384 | 266 | 7.9 | 26.4 | 0 | 0 | 0 | 31.86 | 26.7423 | 0 | 0 | 26.7423 | 0 | 0 | 0 | 0 | 0 | 31.86 | 0 | 31.86 | 2.498% | 0 | 0 | 6.25 | 10% | 26.7423
6058 | 115 | 428 | 342 | 9.6 | 27 | 0 | 0 | 0 | 0 | 30.0861 | 0 | 0 | 30.0861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.86 | 2.498% | 0 | 0 | 6.25 | 10% | 30.0861
6059 | 436 | 680 | 326 | 9.8 | 28 | 0 | 0 | 0 | 103.5209 | 43.6401 | 8.4921 | 0 | 43.6401 | 0 | 0 | 0 | 0 | 0 | 103.5209 | 0 | 135.381 | 10.61% | 0 | 0 | 6.25 | 10% | 43.6401
6060 | 878 | 883 | 138 | 8.3 | 28.4 | 0 | 0 | 0 | 240.6311 | 42.8128 | 29.1872 | 0 | 42.8128 | 0 | 0 | 0 | 0 | 0 | 240.6311 | 0 | 376.0121 | 29.48% | 0 | 0 | 6.25 | 10% | 42.8128
6061 | 833 | 884 | 172 | 8.6 | 27.1 | 0 | 0 | 0 | 229.4225 | 54.7547 | 17.2453 | 12.2497 | 42.505 | 0 | 0 | 0 | 0 | 0 | 229.4225 | 0 | 605.4347 | 47.47% | 12.2497 | 0 | 17.3183 | 27.71% | 42.505
6062 | 849 | 838 | 154 | 9.4 | 26.7 | 0 | 0 | 0 | 231.6787 | 67.2989 | 4.7011 | 25 | 42.2989 | 0 | 0 | 0 | 0 | 0 | 231.6787 | 0 | 837.1134 | 65.63% | 25 | 0 | 39.9073 | 63.85% | 42.2989
6063 | 735 | 672 | 146 | 6.1 | 26.4 | 0 | 0 | 0 | 195.5725 | 59.6339 | 0 | 18.087 | 41.5468 | 0 | 0 | 0 | 0 | 0 | 195.5725 | 0 | 1032.6858 | 80.96% | 18.087 | 0 | 56.25 | 90% | 41.5468
6064 | 313 | 346 | 170 | 4.7 | 25.7 | 0 | 0 | 0 | 68.2637 | 30.6364 | 0 | 0 | 30.6364 | 0 | 0 | 0 | 0 | 0 | 68.2637 | 0 | 1100.9495 | 86.31% | 0 | 0 | 56.25 | 90% | 30.6364
6065 | 572 | 314 | 101 | 4.7 | 25.9 | 0 | 0 | 0 | 126.7354 | 31.1338 | 0 | 0 | 31.1338 | 0 | 0 | 0 | 0 | 0 | 126.7354 | 0 | 1227.6849 | 96.25% | 0 | 12.1748 | 42.7757 | 68.44% | 43.3086
6066 | 485 | 141 | 45 | 4.9 | 25.1 | 0 | 0 | 0 | 47.8253 | 12.7084 | 0 | 0 | 12.7084 | 0 | 0 | 0 | 0 | 0 | 47.8253 | 0 | 1275.5102 | 100% | 0 | 25 | 15.1074 | 24.17% | 37.7084
6067 | 36 | 9 | 6 | 2.7 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6068 | 0 | 0 | 0 | 2.5 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6069 | 0 | 0 | 0 | 2.5 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6070 | 0 | 0 | 0 | 2.5 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6071 | 0 | 0 | 0 | 6.4 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6072 | 0 | 0 | 0 | 7.4 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6073 | 0 | 0 | 0 | 3.9 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6074 | 0 | 0 | 0 | 4.9 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6075 | 0 | 0 | 0 | 3.8 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6076 | 0 | 0 | 0 | 4 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 15.1074 | 24.17% | 0
6077 | 0 | 0 | 0 | 2.4 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9633 | 38.4105 | 0 | 96.9633 | 1178.5469 | 92.4% | 0 | 0 | 15.1074 | 24.17% | 38.4105
6078 | 0 | 1 | 1 | 1.7 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5434 | 39.9592 | 0 | 100.5434 | 1078.0035 | 84.52% | 0 | 0 | 15.1074 | 24.17% | 39.9592
6079 | 24 | 52 | 47 | 2.5 | 16.8 | 0 | 0 | 0 | 0 | 1.8723 | 0 | 0 | 1.8723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 0 | 0 | 15.1074 | 24.17% | 1.8723
6080 | 47 | 125 | 111 | 2.5 | 17.8 | 0 | 0 | 0 | 0 | 7.8874 | 0 | 0 | 7.8874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 0 | 0 | 15.1074 | 24.17% | 7.8874
6081 | 0 | 129 | 128 | 2.7 | 18.8 | 0 | 0 | 0 | 0 | 8.0735 | 0 | 8.0735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 8.0735 | 0 | 22.4023 | 35.84% | 0
6082 | 0 | 92 | 91 | 1.7 | 18.9 | 0 | 0 | 0 | 0 | 5.4107 | 0 | 0 | 5.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 0 | 0 | 22.4023 | 35.84% | 5.4107
6083 | 0 | 123 | 121 | 3.2 | 18.9 | 0 | 0 | 0 | 0 | 7.3805 | 0 | 0 | 7.3805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 0 | 0 | 22.4023 | 35.84% | 7.3805
6084 | 0 | 133 | 132 | 3.1 | 18.8 | 0 | 0 | 0 | 0 | 8.0945 | 0 | 0 | 8.0945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 0 | 0 | 22.4023 | 35.84% | 8.0945
6085 | 0 | 177 | 175 | 1.7 | 19.6 | 0 | 0 | 0 | 0 | 10.9306 | 0 | 0 | 10.9306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 0 | 0 | 22.4023 | 35.84% | 10.9306
6086 | 0 | 195 | 193 | 2.9 | 20.8 | 0 | 0 | 0 | 0 | 12.1606 | 0 | 0 | 12.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 0 | 0 | 22.4023 | 35.84% | 12.1606
6087 | 16 | 183 | 169 | 5.2 | 21.3 | 0 | 0 | 0 | 0 | 12.2343 | 0 | 0 | 12.2343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 0 | 0 | 22.4023 | 35.84% | 12.2343
6088 | 109 | 240 | 176 | 6.4 | 20.9 | 0 | 0 | 0 | 0 | 18.6385 | 0 | 0 | 18.6385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.0035 | 84.52% | 0 | 0 | 22.4023 | 35.84% | 18.6385
6089 | 430 | 281 | 102 | 6.7 | 20.4 | 0 | 0 | 0 | 88.4175 | 25.7445 | 0 | 0 | 25.7445 | 0 | 0 | 0 | 0 | 0 | 88.4175 | 0 | 1166.4209 | 91.45% | 0 | 0 | 22.4023 | 35.84% | 25.7445
6090 | 0 | 23 | 23 | 3.4 | 16 | 0 | 0 | 0 | 0 | 1.0762 | 0 | 0 | 1.0762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4209 | 91.45% | 0 | 14.5946 | 6.25 | 10% | 15.6708
6091 | 0 | 1 | 1 | 2.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4209 | 91.45% | 0 | 0 | 6.25 | 10% | 0
6092 | 0 | 0 | 0 | 3.5 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4209 | 91.45% | 0 | 0 | 6.25 | 10% | 0
6093 | 0 | 0 | 0 | 5.3 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4209 | 91.45% | 0 | 0 | 6.25 | 10% | 0
6094 | 0 | 0 | 0 | 5 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4209 | 91.45% | 0 | 0 | 6.25 | 10% | 0
6095 | 0 | 0 | 0 | 5.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4209 | 91.45% | 0 | 0 | 6.25 | 10% | 0
6096 | 0 | 0 | 0 | 4.4 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4209 | 91.45% | 0 | 0 | 6.25 | 10% | 0
6097 | 0 | 0 | 0 | 4.2 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4209 | 91.45% | 0 | 0 | 6.25 | 10% | 0
6098 | 0 | 0 | 0 | 3.6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4209 | 91.45% | 0 | 0 | 6.25 | 10% | 0
6099 | 0 | 0 | 0 | 5 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8615 | 34.4692 | 0 | 87.8615 | 1078.5594 | 84.56% | 0 | 0 | 6.25 | 10% | 34.4692
6100 | 0 | 0 | 0 | 3.6 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5786 | 38.2573 | 0 | 96.5786 | 981.9808 | 76.99% | 0 | 0 | 6.25 | 10% | 38.2573
6101 | 0 | 0 | 0 | 1.9 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1383 | 40.2642 | 0 | 101.1383 | 880.8425 | 69.06% | 0 | 0 | 6.25 | 10% | 40.2642
6102 | 0 | 1 | 1 | 2.5 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2849 | 42.0607 | 0 | 105.2849 | 775.5576 | 60.8% | 0 | 0 | 6.25 | 10% | 42.0607
6103 | 1 | 40 | 40 | 2.3 | 15.7 | 0 | 0 | 0 | 0 | 1.5393 | 0 | 0 | 1.5393 | 0 | 0 | 0 | 104.539 | 41.7177 | 0 | 104.539 | 671.0186 | 52.61% | 0 | 0 | 6.25 | 10% | 43.2571
6104 | 1 | 49 | 48 | 2.3 | 16.1 | 0 | 0 | 0 | 0 | 2.7155 | 0 | 0 | 2.7155 | 0 | 0 | 0 | 103.0425 | 41.0485 | 0 | 103.0425 | 567.9761 | 44.53% | 0 | 0 | 6.25 | 10% | 43.764
6105 | 15 | 137 | 123 | 2.2 | 15.5 | 0 | 0 | 0 | 0 | 8.3835 | 0 | 0 | 8.3835 | 0 | 0 | 0 | 91.2894 | 35.9738 | 0 | 91.2894 | 476.6866 | 37.37% | 0 | 0 | 6.25 | 10% | 44.3573
6106 | 343 | 565 | 307 | 1.6 | 18.3 | 0 | 0 | 0 | 77.2925 | 40.5626 | 0 | 0 | 40.5626 | 0 | 0 | 0 | 0 | 0 | 77.2925 | 0 | 553.9792 | 43.43% | 0 | 0 | 6.25 | 10% | 40.5626
6107 | 85 | 374 | 302 | 4.7 | 20.4 | 0 | 0 | 0 | 0 | 26.7025 | 0 | 0 | 26.7025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.9792 | 43.43% | 0 | 0 | 6.25 | 10% | 26.7025
6108 | 529 | 798 | 348 | 5.3 | 22.4 | 0 | 0 | 0 | 138.4924 | 64.7129 | 0 | 21.9934 | 42.7195 | 0 | 0 | 0 | 0 | 0 | 138.4924 | 0 | 692.4716 | 54.29% | 21.9934 | 0 | 26.1223 | 41.8% | 42.7195
6109 | 335 | 650 | 361 | 6 | 22.9 | 0 | 0 | 0 | 80.6661 | 52.734 | 0 | 10.332 | 42.402 | 0 | 0 | 0 | 0 | 0 | 80.6661 | 0 | 773.1376 | 60.61% | 10.332 | 0 | 35.458 | 56.73% | 42.402
6110 | 186 | 492 | 335 | 6.4 | 22.7 | 0 | 0 | 0 | 34.8596 | 38.3659 | 0 | 0 | 38.3659 | 0 | 0 | 0 | 0 | 0 | 34.8596 | 0 | 807.9972 | 63.35% | 0 | 0 | 35.458 | 56.73% | 38.3659
6111 | 2 | 159 | 156 | 5.4 | 21.8 | 0 | 0 | 0 | 0 | 9.8155 | 0 | 0 | 9.8155 | 0 | 0 | 0 | 82.8819 | 32.0099 | 0 | 82.8819 | 725.1153 | 56.85% | 0 | 0 | 35.458 | 56.73% | 41.8254
6112 | 1 | 156 | 154 | 5.4 | 21 | 0 | 0 | 0 | 0 | 9.7191 | 0 | 0 | 9.7191 | 0 | 0 | 0 | 82.8147 | 32.0297 | 0 | 82.8147 | 642.3006 | 50.36% | 0 | 0 | 35.458 | 56.73% | 41.7488
6113 | 1 | 83 | 82 | 4 | 20.3 | 0 | 0 | 0 | 0 | 4.9015 | 0 | 0 | 4.9015 | 0 | 0 | 0 | 97.8647 | 38.5603 | 0 | 97.8647 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 43.4618
6114 | 0 | 22 | 22 | 2.8 | 19.8 | 0 | 0 | 0 | 0 | 0.99049 | 0 | 0 | 0.99049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0.99049
6115 | 0 | 0 | 0 | 2.1 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0
6116 | 0 | 0 | 0 | 2.9 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0
6117 | 0 | 0 | 0 | 1.4 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0
6118 | 0 | 0 | 0 | 2.8 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0
6119 | 0 | 0 | 0 | 2.5 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0
6120 | 0 | 0 | 0 | 3.7 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0
6121 | 0 | 0 | 0 | 3.3 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0
6122 | 0 | 0 | 0 | 2.1 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0
6123 | 0 | 0 | 0 | 3.2 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.4359 | 42.68% | 0 | 0 | 35.458 | 56.73% | 0
6124 | 0 | 0 | 0 | 3.4 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8934 | 37.9774 | 0 | 95.8934 | 448.5424 | 35.17% | 0 | 0 | 35.458 | 56.73% | 37.9774
6125 | 0 | 0 | 0 | 3.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.2749 | 39.9021 | 0 | 100.2749 | 348.2675 | 27.3% | 0 | 0 | 35.458 | 56.73% | 39.9021
6126 | 0 | 0 | 0 | 1.9 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6776 | 41.824 | 0 | 104.6776 | 243.5899 | 19.1% | 0 | 0 | 35.458 | 56.73% | 41.824
6127 | 16 | 37 | 33 | 1.9 | 15 | 0 | 0 | 0 | 0 | 1.203 | 0 | 0 | 1.203 | 0 | 0 | 0 | 104.5166 | 41.7407 | 0 | 104.5166 | 139.0733 | 10.9% | 0 | 0 | 35.458 | 56.73% | 42.9437
6128 | 118 | 166 | 112 | 1.3 | 16.4 | 0 | 0 | 0 | 0 | 9.3277 | 0 | 0 | 9.3277 | 0 | 0 | 0 | 86.9513 | 34.0533 | 0 | 86.9513 | 52.122 | 4.086% | 0 | 0 | 35.458 | 56.73% | 43.381
6129 | 341 | 379 | 188 | 1.4 | 19 | 0 | 0 | 0 | 67.3318 | 26.2964 | 0 | 0 | 26.2964 | 0 | 0 | 0 | 0 | 0 | 67.3318 | 0 | 119.4538 | 9.365% | 0 | 5.134 | 29.7759 | 47.64% | 31.4305
6130 | 693 | 664 | 201 | 3 | 21.5 | 0 | 0 | 0 | 173.7921 | 51.6181 | 0 | 7.5477 | 44.0704 | 0 | 0 | 0 | 0 | 0 | 173.7921 | 0 | 293.2459 | 22.99% | 7.5477 | 0 | 36.5957 | 58.55% | 44.0704
6131 | 638 | 717 | 223 | 6.6 | 23.2 | 0 | 0 | 0 | 165.4031 | 59.1215 | 0 | 16.5176 | 42.6039 | 0 | 0 | 0 | 0 | 0 | 165.4031 | 0 | 458.649 | 35.96% | 16.5176 | 0 | 51.5204 | 82.43% | 42.6039
6132 | 62 | 441 | 383 | 6.4 | 23 | 0 | 0 | 0 | 0 | 31.7582 | 0 | 0 | 31.7582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458.649 | 35.96% | 0 | 0 | 51.5204 | 82.43% | 31.7582
6133 | 14 | 114 | 102 | 7.1 | 21 | 0 | 0 | 0 | 0 | 7.4969 | 0 | 0 | 7.4969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458.649 | 35.96% | 0 | 0 | 51.5204 | 82.43% | 7.4969
6134 | 85 | 360 | 287 | 5.9 | 21.1 | 0 | 0 | 0 | 0 | 27.4904 | 0 | 0 | 27.4904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458.649 | 35.96% | 0 | 13.2305 | 36.8777 | 59% | 40.721
6135 | 122 | 385 | 296 | 5.6 | 22 | 0 | 0 | 0 | 0 | 29.8762 | 0 | 0 | 29.8762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458.649 | 35.96% | 0 | 10.5384 | 25.2145 | 40.34% | 40.4146
6136 | 72 | 319 | 276 | 6.1 | 22.8 | 0 | 0 | 0 | 0 | 23.2623 | 0 | 0 | 23.2623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458.649 | 35.96% | 0 | 17.1356 | 6.25 | 10% | 40.3979
6137 | 6 | 122 | 118 | 5.3 | 22.6 | 0 | 0 | 0 | 0 | 7.5198 | 0 | 0 | 7.5198 | 0 | 0 | 0 | 88.7569 | 34.4811 | 0 | 88.7569 | 369.8921 | 29% | 0 | 0 | 6.25 | 10% | 42.0009
6138 | 10 | 51 | 50 | 5.2 | 22.1 | 0 | 0 | 0 | 0 | 2.9598 | 0 | 0 | 2.9598 | 0 | 0 | 0 | 100.6076 | 39.6093 | 0 | 100.6076 | 269.2844 | 21.11% | 0 | 0 | 6.25 | 10% | 42.5691
6139 | 0 | 4 | 4 | 5.5 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.783 | 38.8631 | 0 | 98.783 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 38.8631
6140 | 0 | 0 | 0 | 3.3 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6141 | 0 | 0 | 0 | 4.4 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6142 | 0 | 0 | 0 | 4.2 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6143 | 0 | 0 | 0 | 2.9 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6144 | 0 | 0 | 0 | 4.1 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6145 | 0 | 0 | 0 | 3.2 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6146 | 0 | 0 | 0 | 3.4 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6147 | 0 | 0 | 0 | 3.1 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6148 | 0 | 0 | 0 | 3.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6149 | 0 | 0 | 0 | 3.4 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170.5015 | 13.37% | 0 | 0 | 6.25 | 10% | 0
6150 | 0 | 1 | 1 | 3.5 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.237 | 34.9427 | 0 | 89.237 | 81.2644 | 6.371% | 0 | 0 | 6.25 | 10% | 34.9427
6151 | 0 | 31 | 31 | 4 | 19 | 0 | 0 | 0 | 0 | 1.0838 | 0 | 0 | 1.0838 | 0 | 0 | 0 | 81.2644 | 31.4699 | 0 | 81.2644 | 0 | 0% | 0 | 0 | 6.25 | 10% | 32.5537
6152 | 0 | 57 | 57 | 5.2 | 20 | 0 | 0 | 0 | 0 | 3.2581 | 0 | 0 | 3.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 3.2581
6153 | 0 | 116 | 116 | 3.7 | 19.5 | 0 | 0 | 0 | 0 | 7.2459 | 0 | 0 | 7.2459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 7.2459
6154 | 0 | 187 | 186 | 4.2 | 21.5 | 0 | 0 | 0 | 0 | 11.9182 | 0 | 0 | 11.9182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 11.9182
6155 | 8 | 322 | 312 | 5.8 | 22.6 | 0 | 0 | 0 | 0 | 21.284 | 0 | 0 | 21.284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 21.284
6156 | 26 | 382 | 355 | 4.9 | 23 | 0 | 0 | 0 | 0 | 25.5314 | 0 | 0 | 25.5314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 25.5314
6157 | 310 | 693 | 423 | 5.8 | 24.3 | 0 | 0 | 0 | 73.1215 | 55.3514 | 0 | 19.8377 | 35.5137 | 0 | 0 | 0 | 0 | 0 | 73.1215 | 0 | 73.1215 | 5.733% | 19.8377 | 0 | 24.1746 | 38.68% | 35.5137
6158 | 342 | 673 | 395 | 6.6 | 24.9 | 0 | 0 | 0 | 81.5078 | 50.1412 | 4.7674 | 15.0523 | 35.0889 | 0 | 0 | 0 | 0 | 0 | 81.5078 | 0 | 154.6293 | 12.12% | 15.0523 | 0 | 37.7752 | 60.44% | 35.0889
6159 | 351 | 580 | 336 | 6.3 | 24.6 | 0 | 0 | 0 | 82.213 | 48.6541 | 0 | 13.7253 | 34.9288 | 0 | 0 | 0 | 0 | 0 | 82.213 | 0 | 236.8423 | 18.57% | 13.7253 | 0 | 50.1769 | 80.28% | 34.9288
6160 | 456 | 468 | 215 | 6 | 24.7 | 0 | 0 | 0 | 106.8963 | 42.0484 | 0 | 6.7213 | 35.3271 | 0 | 0 | 0 | 0 | 0 | 106.8963 | 0 | 343.7386 | 26.95% | 6.7213 | 0 | 56.25 | 90% | 35.3271
6161 | 343 | 276 | 150 | 5.1 | 24.7 | 0 | 0 | 0 | 66.9427 | 25.411 | 0 | 0 | 25.411 | 0 | 0 | 0 | 0 | 0 | 66.9427 | 0 | 410.6813 | 32.2% | 0 | 12.0831 | 42.8772 | 68.6% | 37.4941
6162 | 125 | 97 | 71 | 5.9 | 23.5 | 0 | 0 | 0 | 0 | 7.1443 | 0 | 0 | 7.1443 | 0 | 0 | 0 | 63.3279 | 23.5182 | 0 | 63.3279 | 347.3534 | 27.23% | 0 | 8.3427 | 33.6441 | 53.83% | 39.0052
6163 | 1 | 4 | 4 | 4.8 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3895 | 36.4997 | 0 | 93.3895 | 253.9639 | 19.91% | 0 | 0 | 33.6441 | 53.83% | 36.4997
6164 | 0 | 0 | 0 | 4.7 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.84 | 0 | 38.2653 | 215.6986 | 16.91% | 0 | 0 | 33.6441 | 53.83% | 12.84
6165 | 0 | 0 | 0 | 4.2 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.3915 | 32.2228 | 0 | 83.3915 | 132.3071 | 10.37% | 0 | 0 | 33.6441 | 53.83% | 32.2228
6166 | 0 | 0 | 0 | 3.2 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.3071 | 10.37% | 0 | 0 | 33.6441 | 53.83% | 0
6167 | 0 | 0 | 0 | 2.9 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.3071 | 10.37% | 0 | 0 | 33.6441 | 53.83% | 0
6168 | 0 | 0 | 0 | 2.2 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.3071 | 10.37% | 0 | 0 | 33.6441 | 53.83% | 0
6169 | 0 | 0 | 0 | 0.8 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.3071 | 10.37% | 0 | 0 | 33.6441 | 53.83% | 0
6170 | 0 | 0 | 0 | 0.6 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.3071 | 10.37% | 0 | 0 | 33.6441 | 53.83% | 0
6171 | 0 | 0 | 0 | 0.9 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.3071 | 10.37% | 0 | 0 | 33.6441 | 53.83% | 0
6172 | 0 | 0 | 0 | 0.5 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.3071 | 10.37% | 0 | 0 | 33.6441 | 53.83% | 0
6173 | 0 | 0 | 0 | 0.5 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.3071 | 10.37% | 0 | 0 | 33.6441 | 53.83% | 0
6174 | 0 | 1 | 1 | 1.7 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.7878 | 18.2868 | 0 | 50.7878 | 81.5193 | 6.391% | 0 | 0 | 33.6441 | 53.83% | 18.2868
6175 | 76 | 65 | 52 | 1.7 | 20.4 | 0 | 0 | 0 | 0 | 2.0803 | 0 | 0 | 2.0803 | 0 | 0 | 0 | 81.5193 | 31.5059 | 0 | 81.5193 | 0 | 0% | 0 | 0 | 33.6441 | 53.83% | 33.5862
6176 | 348 | 244 | 126 | 1.1 | 22.3 | 0 | 0 | 0 | 49.542 | 13.8953 | 0 | 0 | 13.8953 | 0 | 0 | 0 | 0 | 0 | 49.542 | 0 | 49.542 | 3.884% | 0 | 21.0029 | 10.3995 | 16.64% | 34.8981
6177 | 520 | 444 | 172 | 2.9 | 24.5 | 0 | 0 | 0 | 0 | 32.0095 | 0 | 0 | 32.0095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.542 | 3.884% | 0 | 3.7493 | 6.25 | 10% | 35.7588
6178 | 634 | 618 | 192 | 4.3 | 26 | 0 | 0 | 0 | 66.9844 | 36.5861 | 11.2526 | 0 | 36.5861 | 0 | 0 | 0 | 0 | 0 | 66.9844 | 0 | 116.5264 | 9.136% | 0 | 0 | 6.25 | 10% | 36.5861
6179 | 702 | 744 | 199 | 4.2 | 26.8 | 0 | 0 | 0 | 186.2715 | 36.3855 | 23.5618 | 0 | 36.3855 | 0 | 0 | 0 | 0 | 0 | 186.2715 | 0 | 302.7979 | 23.74% | 0 | 0 | 6.25 | 10% | 36.3855
6180 | 734 | 816 | 200 | 4.5 | 27.6 | 0 | 0 | 0 | 200.5666 | 34.8619 | 32.2626 | 0 | 34.8619 | 0 | 0 | 0 | 0 | 0 | 200.5666 | 0 | 503.3645 | 39.46% | 0 | 0 | 6.25 | 10% | 34.8619
6181 | 718 | 821 | 215 | 4.5 | 27.9 | 0 | 0 | 0 | 198.0461 | 33.9372 | 35.0201 | 0 | 33.9372 | 0 | 0 | 0 | 0 | 0 | 198.0461 | 0 | 701.4106 | 54.99% | 0 | 0 | 6.25 | 10% | 33.9372
6182 | 661 | 748 | 222 | 5.7 | 27.7 | 0 | 0 | 0 | 178.1653 | 58.5221 | 6.4257 | 25 | 33.5221 | 0 | 0 | 0 | 0 | 0 | 178.1653 | 0 | 879.5759 | 68.96% | 25 | 0 | 28.839 | 46.14% | 33.5221
6183 | 653 | 644 | 193 | 5.7 | 27.5 | 0 | 0 | 0 | 171.5808 | 58.0648 | 0 | 24.5998 | 33.465 | 0 | 0 | 0 | 0 | 0 | 171.5808 | 0 | 1051.1566 | 82.41% | 24.5998 | 0 | 51.0664 | 81.71% | 33.465
6184 | 560 | 477 | 170 | 6 | 27.1 | 0 | 0 | 0 | 135.971 | 39.7325 | 4.6388 | 5.7369 | 33.9957 | 0 | 0 | 0 | 0 | 0 | 135.971 | 0 | 1187.1277 | 93.07% | 5.7369 | 0 | 56.25 | 90% | 33.9957
6185 | 394 | 274 | 131 | 5.6 | 26.2 | 0 | 0 | 0 | 79.1969 | 25.9306 | 0 | 0 | 25.9306 | 0 | 0 | 0 | 0 | 0 | 79.1969 | 0 | 1266.3246 | 99.28% | 0 | 10.8253 | 44.2693 | 70.83% | 36.756
6186 | 104 | 83 | 59 | 4.9 | 24.9 | 0 | 0 | 0 | 0 | 5.8136 | 0 | 0 | 5.8136 | 0 | 0 | 0 | 85.3748 | 32.8615 | 0 | 85.3748 | 1180.9497 | 92.59% | 0 | 0 | 44.2693 | 70.83% | 38.6751
6187 | 0 | 3 | 3 | 3.8 | 23.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6802 | 36.9537 | 0 | 94.6802 | 1086.2696 | 85.16% | 0 | 0 | 44.2693 | 70.83% | 36.9537
6188 | 0 | 0 | 0 | 3.1 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9048 | 34.5374 | 0 | 88.9048 | 997.3648 | 78.19% | 0 | 0 | 44.2693 | 70.83% | 34.5374
6189 | 0 | 0 | 0 | 2.1 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5929 | 32.2966 | 0 | 83.5929 | 913.7719 | 71.64% | 0 | 0 | 44.2693 | 70.83% | 32.2966
6190 | 0 | 0 | 0 | 1.9 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.6711 | 30.6643 | 0 | 79.6711 | 834.1008 | 65.39% | 0 | 0 | 44.2693 | 70.83% | 30.6643
6191 | 0 | 0 | 0 | 1 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.4944 | 23.6997 | 0 | 63.4944 | 770.6064 | 60.42% | 0 | 5.9299 | 37.7064 | 60.33% | 29.6296
6192 | 0 | 0 | 0 | 1.3 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1593 | 29.1686 | 0 | 76.1593 | 694.4471 | 54.44% | 0 | 0 | 37.7064 | 60.33% | 29.1686
6193 | 0 | 0 | 0 | 1.6 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5699 | 29.3454 | 0 | 76.5699 | 617.8773 | 48.44% | 0 | 0 | 37.7064 | 60.33% | 29.3454
6194 | 0 | 0 | 0 | 0.7 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.8424 | 0 | 38.2653 | 579.612 | 45.44% | 0 | 17.3275 | 18.5295 | 29.65% | 30.1699
6195 | 0 | 0 | 0 | 0.8 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2029 | 33.5194 | 0 | 86.2029 | 493.4091 | 38.68% | 0 | 0 | 18.5295 | 29.65% | 33.5194
6196 | 0 | 0 | 0 | 1.1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2257 | 38.3046 | 0 | 97.2257 | 396.1834 | 31.06% | 0 | 0 | 18.5295 | 29.65% | 38.3046
6197 | 0 | 0 | 0 | 0.9 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8083 | 40.7544 | 0 | 102.8083 | 293.3751 | 23% | 0 | 0 | 18.5295 | 29.65% | 40.7544
6198 | 0 | 1 | 1 | 1.1 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.1576 | 42.6805 | 0 | 107.1576 | 186.2175 | 14.6% | 0 | 0 | 18.5295 | 29.65% | 42.6805
6199 | 155 | 71 | 43 | 1.3 | 19.1 | 0 | 0 | 0 | 0 | 1.6567 | 0 | 0 | 1.6567 | 0 | 0 | 0 | 106.8217 | 42.5084 | 0 | 106.8217 | 79.3958 | 6.225% | 0 | 0 | 18.5295 | 29.65% | 44.1651
6200 | 532 | 266 | 88 | 2 | 21.8 | 0 | 0 | 0 | 0 | 14.3883 | 0 | 0 | 14.3883 | 0 | 0 | 0 | 79.3958 | 30.5108 | 0 | 79.3958 | 0 | 0% | 0 | 0 | 18.5295 | 29.65% | 44.8991
6201 | 728 | 475 | 103 | 1.7 | 23.6 | 0 | 0 | 0 | 15.1764 | 34.7341 | 0 | 0 | 34.7341 | 0 | 0 | 0 | 0 | 0 | 15.1764 | 0 | 15.1764 | 1.19% | 0 | 11.0953 | 6.25 | 10% | 45.8294
6202 | 815 | 651 | 113 | 1.9 | 25.6 | 0 | 0 | 0 | 0 | 45.9617 | 4.3716 | 0 | 45.9617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1764 | 1.19% | 0 | 0 | 6.25 | 10% | 45.9617
6203 | 540 | 607 | 195 | 1.8 | 26.4 | 0 | 0 | 0 | 140.4355 | 44.8461 | 4.1417 | 0 | 44.8461 | 0 | 0 | 0 | 0 | 0 | 140.4355 | 0 | 155.6119 | 12.2% | 0 | 0 | 6.25 | 10% | 44.8461
6204 | 825 | 873 | 189 | 4.3 | 26.8 | 0 | 0 | 0 | 227.8375 | 44.1512 | 27.8488 | 0 | 44.1512 | 0 | 0 | 0 | 0 | 0 | 227.8375 | 0 | 383.4494 | 30.06% | 0 | 0 | 6.25 | 10% | 44.1512
6205 | 833 | 850 | 156 | 5.2 | 26.5 | 0 | 0 | 0 | 232.0303 | 44.4207 | 27.5793 | 0.41021 | 44.0105 | 0 | 0 | 0 | 0 | 0 | 232.0303 | 0 | 615.4797 | 48.25% | 0.41021 | 0 | 6.6206 | 10.59% | 44.0105
6206 | 806 | 788 | 157 | 4.6 | 26.9 | 0 | 0 | 0 | 222.4224 | 69.0634 | 0.092716 | 25 | 44.0634 | 0 | 0 | 0 | 0 | 0 | 222.4224 | 0 | 837.902 | 65.69% | 25 | 0 | 29.2096 | 46.74% | 44.0634
6207 | 753 | 709 | 194 | 4.1 | 27 | 0 | 0 | 0 | 202.218 | 63.5726 | 0 | 20.2362 | 43.3364 | 0 | 0 | 0 | 0 | 0 | 202.218 | 0 | 1040.12 | 81.55% | 20.2362 | 0 | 47.4942 | 75.99% | 43.3364
6208 | 612 | 602 | 270 | 3 | 27.2 | 0 | 0 | 0 | 152.7905 | 52.5518 | 0 | 9.6903 | 42.8615 | 0 | 0 | 0 | 0 | 0 | 152.7905 | 0 | 1192.9105 | 93.52% | 9.6903 | 0 | 56.25 | 90% | 42.8615
6209 | 401 | 359 | 211 | 3.5 | 26.2 | 0 | 0 | 0 | 82.5997 | 31.2839 | 0 | 0 | 31.2839 | 0 | 0 | 0 | 0 | 0 | 82.5997 | 0 | 1275.5102 | 100% | 0 | 13.5775 | 41.2233 | 65.96% | 44.8614
6210 | 134 | 111 | 85 | 3.3 | 24.5 | 0 | 0 | 0 | 0 | 8.0204 | 0 | 0 | 8.0204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 13.555 | 21.69% | 33.0204
6211 | 0 | 2 | 2 | 2.5 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 13.555 | 21.69% | 0
6212 | 0 | 0 | 0 | 1.4 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.8153 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 0 | 13.555 | 21.69% | 12.8153
6213 | 0 | 0 | 0 | 0.5 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7161 | 35.3995 | 0 | 90.7161 | 1146.5288 | 89.89% | 0 | 0 | 13.555 | 21.69% | 35.3995
6214 | 0 | 0 | 0 | 0.3 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8313 | 33.7533 | 0 | 86.8313 | 1059.6975 | 83.08% | 0 | 0 | 13.555 | 21.69% | 33.7533
6215 | 0 | 0 | 0 | 0.8 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.063 | 32.5793 | 0 | 84.063 | 975.6345 | 76.49% | 0 | 0 | 13.555 | 21.69% | 32.5793
6216 | 0 | 0 | 0 | 1.4 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6583 | 32.0138 | 0 | 82.6583 | 892.9761 | 70.01% | 0 | 0 | 13.555 | 21.69% | 32.0138
6217 | 0 | 0 | 0 | 1.1 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5195 | 31.954 | 0 | 82.5195 | 810.4566 | 63.54% | 0 | 0 | 13.555 | 21.69% | 31.954
6218 | 0 | 0 | 0 | 1.1 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8979 | 32.5598 | 0 | 83.8979 | 726.5586 | 56.96% | 0 | 0 | 13.555 | 21.69% | 32.5598
6219 | 0 | 0 | 0 | 0.5 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5982 | 35.4691 | 0 | 90.5982 | 635.9605 | 49.86% | 0 | 0 | 13.555 | 21.69% | 35.4691
6220 | 0 | 0 | 0 | 1.2 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.8061 | 39.8631 | 0 | 100.8061 | 535.1544 | 41.96% | 0 | 0 | 13.555 | 21.69% | 39.8631
6221 | 0 | 0 | 0 | 1.4 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2468 | 41.7655 | 0 | 105.2468 | 429.9075 | 33.7% | 0 | 0 | 13.555 | 21.69% | 41.7655
6222 | 0 | 0 | 0 | 1.8 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.2134 | 43.0746 | 0 | 108.2134 | 321.6941 | 25.22% | 0 | 0 | 13.555 | 21.69% | 43.0746
6223 | 123 | 79 | 55 | 1.2 | 19.9 | 0 | 0 | 0 | 0 | 2.2286 | 0 | 0 | 2.2286 | 0 | 0 | 0 | 105.3232 | 41.8056 | 0 | 105.3232 | 216.371 | 16.96% | 0 | 0 | 13.555 | 21.69% | 44.0342
6224 | 152 | 171 | 126 | 1.4 | 21.8 | 0 | 0 | 0 | 0 | 10.8955 | 0 | 0 | 10.8955 | 0 | 0 | 0 | 38.2653 | 12.8229 | 0 | 38.2653 | 178.1056 | 13.96% | 0 | 0 | 13.555 | 21.69% | 23.7184
6225 | 57 | 185 | 152 | 2.3 | 22.2 | 0 | 0 | 0 | 0 | 12.2739 | 0 | 0 | 12.2739 | 0 | 0 | 0 | 88.3138 | 34.3187 | 0 | 88.3138 | 89.7919 | 7.04% | 0 | 0 | 13.555 | 21.69% | 46.5926
6226 | 0 | 109 | 108 | 2 | 23.3 | 0 | 0 | 0 | 0 | 6.4566 | 0 | 0 | 6.4566 | 0 | 0 | 0 | 89.7919 | 34.874 | 0 | 89.7919 | 0 | 0% | 0 | 0 | 13.555 | 21.69% | 41.3306
6227 | 54 | 280 | 236 | 3.8 | 24 | 0 | 0 | 0 | 0 | 19.5415 | 0 | 0 | 19.5415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0.017319 | 13.5358 | 21.66% | 19.5588
6228 | 231 | 407 | 212 | 4 | 24 | 0 | 0 | 0 | 49.7135 | 32.9374 | 0 | 0 | 32.9374 | 0 | 0 | 0 | 0 | 0 | 49.7135 | 0 | 49.7135 | 3.898% | 0 | 0 | 13.5358 | 21.66% | 32.9374
6229 | 819 | 908 | 231 | 4.1 | 25.8 | 0 | 0 | 0 | 228.6636 | 69.9882 | 2.0118 | 25 | 44.9882 | 0 | 0 | 0 | 0 | 0 | 228.6636 | 0 | 278.3771 | 21.82% | 25 | 0 | 36.1248 | 57.8% | 44.9882
6230 | 438 | 597 | 256 | 3.5 | 26.7 | 0 | 0 | 0 | 113.0324 | 51.4315 | 0 | 6.7358 | 44.6957 | 0 | 0 | 0 | 0 | 0 | 113.0324 | 0 | 391.4096 | 30.69% | 6.7358 | 0 | 42.211 | 67.54% | 44.6957
6231 | 721 | 658 | 170 | 3.1 | 27.5 | 0 | 0 | 0 | 193.6386 | 59.3544 | 0 | 15.5375 | 43.8169 | 0 | 0 | 0 | 0 | 0 | 193.6386 | 0 | 585.0482 | 45.87% | 15.5375 | 0 | 56.25 | 90% | 43.8169
6232 | 598 | 460 | 139 | 2.4 | 27.9 | 0 | 0 | 0 | 149.0341 | 43.0192 | 0 | 0 | 43.0192 | 0 | 0 | 0 | 0 | 0 | 149.0341 | 0 | 734.0823 | 57.55% | 0 | 0 | 56.25 | 90% | 43.0192
6233 | 272 | 213 | 112 | 2.4 | 27.4 | 0 | 0 | 0 | 50.0988 | 19.3391 | 0 | 0 | 19.3391 | 0 | 0 | 0 | 0 | 0 | 50.0988 | 0 | 784.1811 | 61.48% | 0 | 25 | 28.5817 | 45.73% | 44.3391
6234 | 92 | 68 | 53 | 4 | 25.1 | 0 | 0 | 0 | 0 | 5.1325 | 0 | 0 | 5.1325 | 0 | 0 | 0 | 102.6533 | 40.2233 | 0 | 102.6533 | 681.5278 | 53.43% | 0 | 0 | 28.5817 | 45.73% | 45.3559
6235 | 1 | 2 | 2 | 3.9 | 23.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0505 | 40.987 | 0 | 104.0505 | 577.4773 | 45.27% | 0 | 0 | 28.5817 | 45.73% | 40.987
6236 | 0 | 0 | 0 | 3.3 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8806 | 37.5777 | 0 | 95.8806 | 481.5967 | 37.76% | 0 | 0 | 28.5817 | 45.73% | 37.5777
6237 | 0 | 0 | 0 | 1.6 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3449 | 35.6836 | 0 | 91.3449 | 390.2518 | 30.6% | 0 | 0 | 28.5817 | 45.73% | 35.6836
6238 | 0 | 0 | 0 | 1.7 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1752 | 29.2017 | 0 | 76.1752 | 314.0767 | 24.62% | 0 | 0 | 28.5817 | 45.73% | 29.2017
6239 | 0 | 0 | 0 | 1.6 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.0767 | 24.62% | 0 | 0 | 28.5817 | 45.73% | 0
6240 | 0 | 0 | 0 | 1.5 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.0767 | 24.62% | 0 | 0 | 28.5817 | 45.73% | 0
6241 | 0 | 0 | 0 | 1.1 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.0767 | 24.62% | 0 | 0 | 28.5817 | 45.73% | 0
6242 | 0 | 0 | 0 | 1 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.0767 | 24.62% | 0 | 0 | 28.5817 | 45.73% | 0
6243 | 0 | 0 | 0 | 0.7 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.0767 | 24.62% | 0 | 0 | 28.5817 | 45.73% | 0
6244 | 0 | 0 | 0 | 0.7 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.0704 | 39.6402 | 0 | 100.0704 | 214.0063 | 16.78% | 0 | 0 | 28.5817 | 45.73% | 39.6402
6245 | 0 | 0 | 0 | 1 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.957 | 41.7418 | 0 | 104.957 | 109.0493 | 8.549% | 0 | 0 | 28.5817 | 45.73% | 41.7418
6246 | 0 | 0 | 0 | 1.8 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.0493 | 43.5314 | 0 | 109.0493 | 0 | 0% | 0 | 0 | 28.5817 | 45.73% | 43.5314
6247 | 165 | 64 | 37 | 2.6 | 19.6 | 0 | 0 | 0 | 0 | 1.3664 | 0 | 0 | 1.3664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 20.178 | 6.25 | 10% | 21.5444
6248 | 573 | 264 | 77 | 0.8 | 22.6 | 0 | 0 | 0 | 92.4325 | 14.4083 | 0 | 0 | 14.4083 | 0 | 0 | 0 | 0 | 0 | 92.4325 | 0 | 92.4325 | 7.247% | 0 | 0 | 6.25 | 10% | 14.4083
6249 | 741 | 469 | 97 | 0.5 | 25.1 | 0 | 0 | 0 | 0 | 33.7943 | 0.38296 | 0 | 33.7943 | 0 | 0 | 0 | 38.2653 | 12.7314 | 0 | 38.2653 | 54.1672 | 4.247% | 0 | 0 | 6.25 | 10% | 46.5257
6250 | 721 | 612 | 143 | 1.2 | 26 | 0 | 0 | 0 | 0 | 34.236 | 13.4413 | 0 | 34.236 | 0 | 0 | 0 | 38.2653 | 12.7034 | 0 | 38.2653 | 15.9019 | 1.247% | 0 | 0 | 6.25 | 10% | 46.9393
6251 | 713 | 746 | 201 | 1.3 | 26.8 | 0 | 0 | 0 | 191.2308 | 45.8767 | 12.5894 | 0 | 45.8767 | 0 | 0 | 0 | 0 | 0 | 191.2308 | 0 | 207.1327 | 16.24% | 0 | 0 | 6.25 | 10% | 45.8767
6252 | 840 | 837 | 150 | 1.9 | 27.7 | 0 | 0 | 0 | 233.8553 | 46.7532 | 20.8717 | 1.5394 | 45.2138 | 0 | 0 | 0 | 0 | 0 | 233.8553 | 0 | 440.988 | 34.57% | 1.5394 | 0 | 7.641 | 12.23% | 45.2138
6253 | 802 | 818 | 158 | 1.9 | 28.5 | 0 | 0 | 0 | 224.8584 | 67.5254 | 0 | 22.5748 | 44.9506 | 0 | 0 | 0 | 0 | 0 | 224.8584 | 0 | 665.8465 | 52.2% | 22.5748 | 0 | 28.0387 | 44.86% | 44.9506
6254 | 756 | 769 | 184 | 2.1 | 29.3 | 0 | 0 | 0 | 209.0593 | 65.5329 | 0 | 20.4876 | 45.0453 | 0 | 0 | 0 | 0 | 0 | 209.0593 | 0 | 874.9058 | 68.59% | 20.4876 | 0 | 46.5505 | 74.48% | 45.0453
6255 | 625 | 618 | 200 | 2.3 | 29.3 | 0 | 0 | 0 | 165.7634 | 54.84 | 0 | 10.7348 | 44.1052 | 0 | 0 | 0 | 0 | 0 | 165.7634 | 0 | 1040.6692 | 81.59% | 10.7348 | 0 | 56.25 | 90% | 44.1052
6256 | 532 | 449 | 167 | 4.2 | 28.6 | 0 | 0 | 0 | 129.2137 | 41.6989 | 0 | 0 | 41.6989 | 0 | 0 | 0 | 0 | 0 | 129.2137 | 0 | 1169.8829 | 91.72% | 0 | 1.9231 | 54.1217 | 86.59% | 43.622
6257 | 360 | 249 | 126 | 4.1 | 27.1 | 0 | 0 | 0 | 71.2383 | 24.0151 | 0 | 0 | 24.0151 | 0 | 0 | 0 | 0 | 0 | 71.2383 | 0 | 1241.1212 | 97.3% | 0 | 21.6318 | 30.1811 | 48.29% | 45.6469
6258 | 242 | 93 | 52 | 2.6 | 26 | 0 | 0 | 0 | 0 | 8.0817 | 0 | 0 | 8.0817 | 0 | 0 | 0 | 95.965 | 37.2853 | 0 | 95.965 | 1145.1561 | 89.78% | 0 | 0 | 30.1811 | 48.29% | 45.367
6259 | 1 | 2 | 2 | 1.8 | 24.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1575 | 40.9327 | 0 | 104.1575 | 1040.9986 | 81.61% | 0 | 0 | 30.1811 | 48.29% | 40.9327
6260 | 0 | 0 | 0 | 0.3 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1396 | 37.6194 | 0 | 96.1396 | 944.859 | 74.08% | 0 | 0 | 30.1811 | 48.29% | 37.6194
6261 | 0 | 0 | 0 | 0.9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5155 | 35.7087 | 0 | 91.5155 | 853.3436 | 66.9% | 0 | 0 | 30.1811 | 48.29% | 35.7087
6262 | 0 | 0 | 0 | 0.4 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.0438 | 33.8257 | 0 | 87.0438 | 766.2998 | 60.08% | 0 | 0 | 30.1811 | 48.29% | 33.8257
6263 | 0 | 0 | 0 | 0.5 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.0898 | 32.5849 | 0 | 84.0898 | 682.21 | 53.49% | 0 | 0 | 30.1811 | 48.29% | 32.5849
6264 | 0 | 0 | 0 | 0.2 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 682.21 | 53.49% | 0 | 12.6591 | 16.1708 | 25.87% | 12.6591
6265 | 0 | 0 | 0 | 0.6 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 682.21 | 53.49% | 0 | 0 | 16.1708 | 25.87% | 0
6266 | 0 | 0 | 0 | 0.3 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5744 | 43.2448 | 0 | 108.5744 | 573.6356 | 44.97% | 10.7003 | 0 | 25.8392 | 41.34% | 32.5445
6267 | 0 | 0 | 0 | 0.7 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4821 | 0 | 127.551 | 446.0846 | 34.97% | 15.9643 | 0 | 40.2639 | 64.42% | 35.5179
6268 | 0 | 0 | 0 | 0.3 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.8431 | 39.9564 | 0 | 100.8431 | 345.2414 | 27.07% | 0 | 0 | 40.2639 | 64.42% | 39.9564
6269 | 0 | 0 | 0 | 1.7 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.5296 | 0 | 127.551 | 217.6904 | 17.07% | 9.4271 | 0 | 48.7818 | 78.05% | 42.1025
6270 | 0 | 1 | 1 | 1.6 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3286 | 43.6192 | 0 | 109.3286 | 108.3618 | 8.496% | 0 | 0 | 48.7818 | 78.05% | 43.6192
6271 | 184 | 66 | 38 | 1.4 | 19.8 | 0 | 0 | 0 | 0 | 1.4113 | 0 | 0 | 1.4113 | 0 | 0 | 0 | 108.3618 | 43.1242 | 0 | 108.3618 | 0 | 0% | 0 | 0 | 48.7818 | 78.05% | 44.5356
6272 | 493 | 248 | 89 | 0.8 | 22.2 | 0 | 0 | 0 | 76.5025 | 14.0108 | 3.5527e-15 | 0 | 14.0108 | 0 | 0 | 0 | 0 | 0 | 76.5025 | 0 | 76.5025 | 5.998% | 0 | 25 | 21.1135 | 33.78% | 39.0108
6273 | 653 | 449 | 121 | 0.9 | 24.5 | 0 | 0 | 0 | 143.2165 | 33.2224 | 0 | 0 | 33.2224 | 0 | 0 | 0 | 0 | 0 | 143.2165 | 0 | 219.7191 | 17.23% | 0 | 13.4301 | 6.25 | 10% | 46.6525
6274 | 760 | 622 | 129 | 1.6 | 25.6 | 0 | 0 | 0 | 192.724 | 49.0841 | 0 | 1.8495 | 47.2346 | 0 | 0 | 0 | 0 | 0 | 192.724 | 0 | 412.4431 | 32.34% | 1.8495 | 0 | 7.9212 | 12.67% | 47.2346
6275 | 798 | 746 | 143 | 1.8 | 26.6 | 0 | 0 | 0 | 215.6029 | 46.1413 | 13.7123 | 0 | 46.1413 | 0 | 0 | 0 | 0 | 0 | 215.6029 | 0 | 628.046 | 49.24% | 0 | 0 | 7.9212 | 12.67% | 46.1413
6276 | 752 | 810 | 197 | 2.3 | 27 | 0 | 0 | 0 | 207.2916 | 66.6179 | 0 | 21.1618 | 45.4561 | 0 | 0 | 0 | 0 | 0 | 207.2916 | 0 | 835.3376 | 65.49% | 21.1618 | 0 | 27.0421 | 43.27% | 45.4561
6277 | 716 | 785 | 199 | 3.8 | 27.4 | 0 | 0 | 0 | 0 | 67.0938 | 0.53735 | 21.9664 | 45.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 835.3376 | 65.49% | 21.9664 | 0 | 46.8901 | 75.02% | 45.1275
6278 | 697 | 738 | 202 | 4.4 | 27.6 | 0 | 0 | 0 | 153.3055 | 45.0592 | 20.4447 | 0 | 45.0592 | 0 | 0 | 0 | 0 | 0 | 153.3055 | 0 | 988.6431 | 77.51% | 0 | 0 | 46.8901 | 75.02% | 45.0592
6279 | 598 | 600 | 196 | 4.4 | 27.6 | 0 | 0 | 0 | 156.2839 | 54.5227 | 0 | 10.359 | 44.1637 | 0 | 0 | 0 | 0 | 0 | 156.2839 | 0 | 1144.927 | 89.76% | 10.359 | 0 | 56.25 | 90% | 44.1637
6280 | 337 | 328 | 153 | 4.6 | 26.8 | 0 | 0 | 0 | 74.2145 | 30.6641 | 0 | 0 | 30.6641 | 0 | 0 | 0 | 0 | 0 | 74.2145 | 0 | 1219.1415 | 95.58% | 0 | 13.0971 | 41.755 | 66.81% | 43.7612
6281 | 304 | 220 | 114 | 4.8 | 26 | 0 | 0 | 0 | 56.3687 | 21.0212 | 0 | 0 | 21.0212 | 0 | 0 | 0 | 0 | 0 | 56.3687 | 0 | 1275.5102 | 100% | 0 | 24.712 | 14.4054 | 23.05% | 45.7333
6282 | 129 | 72 | 50 | 4.7 | 24.5 | 0 | 0 | 0 | 0 | 5.5903 | 0 | 0 | 5.5903 | 0 | 0 | 0 | 101.6487 | 39.8505 | 0 | 101.6487 | 1173.8615 | 92.03% | 0 | 0 | 14.4054 | 23.05% | 45.4408
6283 | 0 | 1 | 1 | 3.9 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4919 | 41.2112 | 0 | 104.4919 | 1069.3696 | 83.84% | 0 | 0 | 14.4054 | 23.05% | 41.2112
6284 | 0 | 0 | 0 | 3 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.546 | 37.9008 | 0 | 96.546 | 972.8236 | 76.27% | 0 | 0 | 14.4054 | 23.05% | 37.9008
6285 | 0 | 0 | 0 | 2.5 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6 | 35.8201 | 0 | 91.6 | 881.2235 | 69.09% | 0 | 0 | 14.4054 | 23.05% | 35.8201
6286 | 0 | 0 | 0 | 3.1 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4607 | 34.0736 | 0 | 87.4607 | 793.7628 | 62.23% | 0 | 0 | 14.4054 | 23.05% | 34.0736
6287 | 0 | 0 | 0 | 3.5 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.2852 | 48.7103 | 0 | 121.2852 | 672.4776 | 52.72% | 15.8539 | 0 | 28.7303 | 45.97% | 32.8564
6288 | 0 | 0 | 0 | 2 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 672.4776 | 52.72% | 0 | 0 | 28.7303 | 45.97% | 0
6289 | 0 | 0 | 0 | 2.4 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 672.4776 | 52.72% | 0 | 0 | 28.7303 | 45.97% | 0
6290 | 0 | 0 | 0 | 3.1 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 672.4776 | 52.72% | 0 | 0 | 28.7303 | 45.97% | 0
6291 | 0 | 0 | 0 | 3 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.871 | 35.575 | 0 | 90.871 | 581.6066 | 45.6% | 0 | 0 | 28.7303 | 45.97% | 35.575
6292 | 0 | 0 | 0 | 2.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.509 | 40.1528 | 0 | 101.509 | 480.0976 | 37.64% | 0 | 0 | 28.7303 | 45.97% | 40.1528
6293 | 0 | 0 | 0 | 2.2 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4238 | 0 | 127.551 | 352.5466 | 27.64% | 9.3491 | 0 | 37.1777 | 59.48% | 42.0747
6294 | 0 | 0 | 0 | 2.4 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.4902 | 0 | 127.551 | 224.9956 | 17.64% | 7.7763 | 0 | 44.2041 | 70.73% | 43.7139
6295 | 13 | 46 | 44 | 2.5 | 18.9 | 0 | 0 | 0 | 0 | 1.7087 | 0 | 1.7087 | 0 | 0 | 0 | 0 | 127.551 | 51.4821 | 0 | 127.551 | 97.4446 | 7.64% | 8.1804 | 0 | 51.5956 | 82.55% | 45.0105
6296 | 89 | 168 | 135 | 3.5 | 20 | 0 | 0 | 0 | 0 | 10.7764 | 0 | 0 | 10.7764 | 0 | 0 | 0 | 89.5441 | 34.9903 | 0 | 89.5441 | 7.9005 | 0.6194% | 0 | 0 | 51.5956 | 82.55% | 45.7667
6297 | 163 | 339 | 261 | 5.3 | 22.4 | 0 | 0 | 0 | 0 | 25.6124 | 0 | 0 | 25.6124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9005 | 0.6194% | 0 | 20.9342 | 28.427 | 45.48% | 46.5466
6298 | 102 | 352 | 279 | 5.5 | 22.6 | 0 | 0 | 0 | 0 | 25.3523 | 0 | 0 | 25.3523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9005 | 0.6194% | 0 | 20.0383 | 6.25 | 10% | 45.3906
6299 | 51 | 349 | 307 | 4.3 | 23.2 | 0 | 0 | 0 | 0 | 24.9661 | 0 | 0 | 24.9661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9005 | 0.6194% | 0 | 0 | 6.25 | 10% | 24.9661
6300 | 19 | 406 | 384 | 4.8 | 23.5 | 0 | 0 | 0 | 0 | 27.3251 | 0 | 0 | 27.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9005 | 0.6194% | 0 | 0 | 6.25 | 10% | 27.3251
6301 | 165 | 655 | 511 | 5.5 | 24.5 | 0 | 0 | 0 | 0 | 50.8314 | 0 | 7.2457 | 43.5857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9005 | 0.6194% | 7.2457 | 0 | 12.7969 | 20.48% | 43.5857
6302 | 257 | 661 | 455 | 6 | 25 | 0 | 0 | 0 | 56.2729 | 52.5847 | 0 | 9.4614 | 43.1234 | 0 | 0 | 0 | 0 | 0 | 56.2729 | 0 | 64.1734 | 5.031% | 9.4614 | 0 | 21.3458 | 34.15% | 43.1234
6303 | 336 | 546 | 326 | 6 | 25 | 0 | 0 | 0 | 77.7512 | 47.109 | 0 | 4.565 | 42.544 | 0 | 0 | 0 | 0 | 0 | 77.7512 | 0 | 141.9246 | 11.13% | 4.565 | 0 | 25.4706 | 40.75% | 42.544
6304 | 239 | 376 | 245 | 6.2 | 24.7 | 0 | 0 | 0 | 45.0619 | 31.8629 | 0 | 0 | 31.8629 | 0 | 0 | 0 | 0 | 0 | 45.0619 | 0 | 186.9864 | 14.66% | 0 | 10.436 | 13.9207 | 22.27% | 42.2989
6305 | 51 | 166 | 146 | 6.1 | 23.7 | 0 | 0 | 0 | 0 | 11.7839 | 0 | 0 | 11.7839 | 0 | 0 | 0 | 84.3812 | 32.526 | 0 | 84.3812 | 102.6053 | 8.044% | 0 | 0 | 13.9207 | 22.27% | 44.3099
6306 | 2 | 61 | 60 | 7.1 | 22.5 | 0 | 0 | 0 | 0 | 3.4751 | 0 | 0 | 3.4751 | 0 | 0 | 0 | 102.6053 | 40.4352 | 0 | 102.6053 | 1.7764e-15 | 1.393e-16% | 0 | 0 | 13.9207 | 22.27% | 43.9102
6307 | 0 | 1 | 1 | 5.1 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7764e-15 | 1.393e-16% | 0 | 0 | 13.9207 | 22.27% | 0
6308 | 0 | 0 | 0 | 4.7 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7764e-15 | 1.393e-16% | 0 | 0 | 13.9207 | 22.27% | 0
6309 | 0 | 0 | 0 | 4.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7764e-15 | 1.393e-16% | 0 | 6.931 | 6.25 | 10% | 6.931
6310 | 0 | 0 | 0 | 2.4 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7764e-15 | 1.393e-16% | 0 | 0 | 6.25 | 10% | 0
6311 | 0 | 0 | 0 | 1.8 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7764e-15 | 1.393e-16% | 0 | 0 | 6.25 | 10% | 0
6312 | 0 | 0 | 0 | 1.8 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7764e-15 | 1.393e-16% | 0 | 0 | 6.25 | 10% | 0
6313 | 0 | 0 | 0 | 1.3 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7764e-15 | 1.393e-16% | 0 | 0 | 6.25 | 10% | 0
6314 | 0 | 0 | 0 | 1.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7764e-15 | 1.393e-16% | 0 | 0 | 6.25 | 10% | 0
6315 | 0 | 0 | 0 | 1.4 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7764e-15 | 0 | 0 | 1.7764e-15 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6316 | 0 | 0 | 0 | 1 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6317 | 0 | 0 | 0 | 0.7 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6318 | 0 | 0 | 0 | 1 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6319 | 1 | 32 | 32 | 0.8 | 19.1 | 0 | 0 | 0 | 0 | 1.1283 | 0 | 0 | 1.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 1.1283
6320 | 2 | 112 | 110 | 1.1 | 20.1 | 0 | 0 | 0 | 0 | 7.103 | 0 | 0 | 7.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 7.103
6321 | 29 | 283 | 266 | 0.5 | 22.3 | 0 | 0 | 0 | 0 | 19.3306 | 0 | 0 | 19.3306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 19.3306
6322 | 235 | 469 | 306 | 1 | 23.9 | 0 | 0 | 0 | 47.1509 | 34.1641 | 0 | 0 | 34.1641 | 0 | 0 | 0 | 0 | 0 | 47.1509 | 0 | 47.1509 | 3.697% | 0 | 0 | 6.25 | 10% | 34.1641
6323 | 278 | 636 | 416 | 2.1 | 24.9 | 0 | 0 | 0 | 63.5724 | 47.6524 | 0 | 7.9578 | 39.6946 | 0 | 0 | 0 | 0 | 0 | 63.5724 | 0 | 110.7234 | 8.681% | 7.9578 | 0 | 13.4404 | 21.5% | 39.6946
6324 | 401 | 786 | 454 | 3.4 | 25.8 | 0 | 0 | 0 | 101.5313 | 61.9016 | 0 | 24.1346 | 37.7671 | 0 | 0 | 0 | 0 | 0 | 101.5313 | 0 | 212.2547 | 16.64% | 24.1346 | 0 | 35.2474 | 56.4% | 37.7671
6325 | 210 | 602 | 424 | 3.8 | 26 | 0 | 0 | 0 | 44.249 | 46.742 | 0 | 10.2158 | 36.5262 | 0 | 0 | 0 | 0 | 0 | 44.249 | 0 | 256.5037 | 20.11% | 10.2158 | 0 | 44.478 | 71.16% | 36.5262
6326 | 35 | 398 | 366 | 3.9 | 25.6 | 0 | 0 | 0 | 0 | 28.4261 | 0 | 0 | 28.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.5037 | 20.11% | 0 | 0 | 44.478 | 71.16% | 28.4261
6327 | 71 | 348 | 295 | 4.9 | 25.1 | 0 | 0 | 0 | 0 | 25.3094 | 0 | 0 | 25.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.5037 | 20.11% | 0 | 5.3696 | 38.5353 | 61.66% | 30.679
6328 | 14 | 224 | 216 | 4.7 | 24.3 | 0 | 0 | 0 | 0 | 14.817 | 0 | 0 | 14.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.5037 | 20.11% | 0 | 21.3526 | 14.9036 | 23.85% | 36.1696
6329 | 2 | 92 | 91 | 4 | 23.8 | 0 | 0 | 0 | 0 | 5.5112 | 0 | 0 | 5.5112 | 0 | 0 | 0 | 67.9546 | 25.4841 | 0 | 67.9546 | 188.5491 | 14.78% | 0 | 7.8191 | 6.25 | 10% | 38.8144
6330 | 10 | 52 | 50 | 3.2 | 23.5 | 0 | 0 | 0 | 0 | 2.9213 | 0 | 0 | 2.9213 | 0 | 0 | 0 | 93.8626 | 36.6034 | 0 | 93.8626 | 94.6865 | 7.423% | 0 | 0 | 6.25 | 10% | 39.5246
6331 | 0 | 1 | 1 | 3.3 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.6865 | 37.0039 | 0 | 94.6865 | 4.7962e-14 | 3.76e-15% | 0 | 0 | 6.25 | 10% | 37.0039
6332 | 0 | 0 | 0 | 1.7 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0396e-14 | 4.735e-15% | 0 | 0 | 6.25 | 10% | 0
6333 | 0 | 0 | 0 | 1.8 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0396e-14 | 4.735e-15% | 0 | 0 | 6.25 | 10% | 0
6334 | 0 | 0 | 0 | 1.7 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0396e-14 | 4.735e-15% | 0 | 0 | 6.25 | 10% | 0
6335 | 0 | 0 | 0 | 1.4 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0396e-14 | 4.735e-15% | 0 | 0 | 6.25 | 10% | 0
6336 | 0 | 0 | 0 | 0.6 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0396e-14 | 0 | 0 | 6.0396e-14 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6337 | 0 | 0 | 0 | 1 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6338 | 0 | 0 | 0 | 1.2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6339 | 0 | 0 | 0 | 1 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6340 | 0 | 0 | 0 | 0.9 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6341 | 0 | 0 | 0 | 1.6 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6342 | 0 | 0 | 0 | 0.7 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
6343 | 0 | 27 | 27 | 0.5 | 18.6 | 0 | 0 | 0 | 0 | 0.89271 | 0 | 0 | 0.89271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0.89271
6344 | 415 | 240 | 91 | 1 | 19.6 | 0 | 0 | 0 | 55.0895 | 13.318 | 0 | 0 | 13.318 | 0 | 0 | 0 | 0 | 0 | 55.0895 | 0 | 55.0895 | 4.319% | 0 | 0 | 6.25 | 10% | 13.318
6345 | 749 | 456 | 87 | 1.3 | 22.8 | 0 | 0 | 0 | 0 | 34.9594 | 0 | 0 | 34.9594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.0895 | 4.319% | 0 | 0 | 6.25 | 10% | 34.9594
6346 | 859 | 635 | 84 | 2 | 25.2 | 0 | 0 | 0 | 0 | 36.5401 | 14.2519 | 0 | 36.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.0895 | 4.319% | 0 | 0 | 6.25 | 10% | 36.5401
6347 | 869 | 754 | 105 | 1.6 | 26.9 | 0 | 0 | 0 | 236.1471 | 36.2045 | 24.4246 | 0 | 36.2045 | 0 | 0 | 0 | 0 | 0 | 236.1471 | 0 | 291.2366 | 22.83% | 0 | 0 | 6.25 | 10% | 36.2045
6348 | 852 | 812 | 126 | 1.6 | 28.1 | 0 | 0 | 0 | 237.4727 | 34.5318 | 31.936 | 0 | 34.5318 | 0 | 0 | 0 | 0 | 0 | 237.4727 | 0 | 528.7093 | 41.45% | 0 | 0 | 6.25 | 10% | 34.5318
6349 | 792 | 790 | 150 | 1.2 | 29.3 | 0 | 0 | 0 | 221.9292 | 36.9311 | 28.24 | 3.4814 | 33.4497 | 0 | 0 | 0 | 0 | 0 | 221.9292 | 0 | 750.6384 | 58.85% | 3.4814 | 0 | 9.3957 | 15.03% | 33.4497
6350 | 755 | 740 | 167 | 2 | 30.1 | 0 | 0 | 0 | 208.5137 | 58.2506 | 5.9037 | 25 | 33.2506 | 0 | 0 | 0 | 0 | 0 | 208.5137 | 0 | 959.1521 | 75.2% | 25 | 0 | 31.9847 | 51.18% | 33.2506
6351 | 614 | 584 | 181 | 3 | 30.3 | 0 | 0 | 0 | 161.6922 | 53.3018 | 0 | 20.0471 | 33.2547 | 0 | 0 | 0 | 0 | 0 | 161.6922 | 0 | 1120.8443 | 87.87% | 20.0471 | 0 | 50.0984 | 80.16% | 33.2547
6352 | 597 | 425 | 112 | 2.8 | 30.3 | 0 | 0 | 0 | 147.732 | 40.7746 | 0 | 6.8082 | 33.9664 | 0 | 0 | 0 | 0 | 0 | 147.732 | 0 | 1268.5763 | 99.46% | 6.8082 | 0 | 56.25 | 90% | 33.9664
6353 | 119 | 188 | 149 | 2.8 | 29.3 | 0 | 0 | 0 | 0 | 14.913 | 0 | 0 | 14.913 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 1268.5763 | 99.46% | 0 | 22.304 | 31.5655 | 50.5% | 37.217
6354 | 255 | 94 | 54 | 2.4 | 28.2 | 0 | 0 | 0 | 0 | 8.311 | 0 | 0 | 8.311 | 0 | 0 | 0 | 79.8647 | 30.2485 | 0 | 79.8647 | 1188.7116 | 93.19% | 0 | 0 | 31.5655 | 50.5% | 38.5595
6355 | 0 | 1 | 1 | 1.5 | 25.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.258 | 36.5763 | 0 | 94.258 | 1094.4536 | 85.81% | 0 | 0 | 31.5655 | 50.5% | 36.5763
6356 | 0 | 0 | 0 | 1.9 | 23.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4833 | 34.2756 | 0 | 88.4833 | 1005.9703 | 78.87% | 0 | 0 | 31.5655 | 50.5% | 34.2756
6357 | 0 | 0 | 0 | 1.5 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1987 | 32.0946 | 0 | 83.1987 | 922.7716 | 72.35% | 0 | 0 | 31.5655 | 50.5% | 32.0946
6358 | 0 | 0 | 0 | 0.7 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5987 | 30.5738 | 0 | 79.5987 | 843.1728 | 66.1% | 0 | 0 | 31.5655 | 50.5% | 30.5738
6359 | 0 | 0 | 0 | 1.1 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9092 | 29.4471 | 0 | 76.9092 | 766.2637 | 60.08% | 0 | 0 | 31.5655 | 50.5% | 29.4471
6360 | 0 | 0 | 0 | 1.5 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.5418 | 28.9026 | 0 | 75.5418 | 690.7219 | 54.15% | 0 | 0 | 31.5655 | 50.5% | 28.9026
6361 | 0 | 0 | 0 | 1.2 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7763 | 29.0349 | 0 | 75.7763 | 614.9456 | 48.21% | 0 | 0 | 31.5655 | 50.5% | 29.0349
6362 | 0 | 0 | 0 | 1.1 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4059 | 29.7633 | 0 | 77.4059 | 537.5397 | 42.14% | 0 | 0 | 31.5655 | 50.5% | 29.7633
6363 | 0 | 0 | 0 | 1.3 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1954 | 33.1419 | 0 | 85.1954 | 452.3443 | 35.46% | 0 | 0 | 31.5655 | 50.5% | 33.1419
6364 | 0 | 0 | 0 | 1.7 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.1922 | 37.9509 | 0 | 96.1922 | 356.1521 | 27.92% | 0 | 0 | 31.5655 | 50.5% | 37.9509
6365 | 0 | 0 | 0 | 2 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9217 | 39.9717 | 0 | 100.9217 | 255.2304 | 20.01% | 0 | 0 | 31.5655 | 50.5% | 39.9717
6366 | 0 | 0 | 0 | 1.3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5215 | 41.5844 | 0 | 104.5215 | 150.709 | 11.82% | 0 | 0 | 31.5655 | 50.5% | 41.5844
6367 | 239 | 61 | 27 | 1.1 | 19.3 | 0 | 0 | 0 | 0 | 0.88981 | 0 | 0 | 0.88981 | 0 | 0 | 0 | 77.4361 | 29.801 | 0 | 77.4361 | 73.2729 | 5.745% | 0 | 12.2 | 18.0634 | 28.9% | 42.8908
6368 | 611 | 267 | 79 | 1.7 | 22 | 0 | 0 | 0 | 0 | 15.6717 | 0 | 0 | 15.6717 | 0 | 0 | 0 | 73.2729 | 27.8667 | 0 | 73.2729 | 0 | 0% | 0 | 0 | 18.0634 | 28.9% | 43.5384
6369 | 617 | 433 | 130 | 2.9 | 23 | 0 | 0 | 0 | 131.8432 | 33.6011 | 0 | 0 | 33.6011 | 0 | 0 | 0 | 0 | 0 | 131.8432 | 0 | 131.8432 | 10.34% | 0 | 10.6741 | 6.25 | 10% | 44.2751
6370 | 734 | 611 | 141 | 3.4 | 24.2 | 0 | 0 | 0 | 183.6503 | 44.4478 | 5.9567 | 0 | 44.4478 | 0 | 0 | 0 | 0 | 0 | 183.6503 | 0 | 315.4935 | 24.73% | 0 | 0 | 6.25 | 10% | 44.4478
6371 | 706 | 734 | 210 | 2.3 | 25.4 | 0 | 0 | 0 | 188.1757 | 43.1972 | 17.3466 | 0 | 43.1972 | 0 | 0 | 0 | 0 | 0 | 188.1757 | 0 | 503.6692 | 39.49% | 0 | 0 | 6.25 | 10% | 43.1972
6372 | 792 | 877 | 241 | 2.2 | 26.2 | 0 | 0 | 0 | 219.104 | 42.4368 | 29.551 | 0 | 42.4368 | 0 | 0 | 0 | 0 | 0 | 219.104 | 0 | 722.7732 | 56.67% | 0 | 0 | 6.25 | 10% | 42.4368
6373 | 681 | 777 | 229 | 3.5 | 26.5 | 0 | 0 | 0 | 187.2717 | 56.8104 | 10.7009 | 14.6967 | 42.1137 | 0 | 0 | 0 | 0 | 0 | 187.2717 | 0 | 910.0449 | 71.35% | 14.6967 | 0 | 19.5294 | 31.25% | 42.1137
6374 | 662 | 694 | 197 | 3.9 | 26.8 | 0 | 0 | 0 | 149.4311 | 62.9033 | 0 | 20.947 | 41.9563 | 0 | 0 | 0 | 0 | 0 | 149.4311 | 0 | 1059.476 | 83.06% | 20.947 | 0 | 38.4563 | 61.53% | 41.9563
6375 | 803 | 635 | 116 | 3.8 | 27 | 0 | 0 | 0 | 216.0342 | 60.6443 | 0 | 19.0668 | 41.5775 | 0 | 0 | 0 | 0 | 0 | 216.0342 | 0 | 1275.5102 | 100% | 19.0668 | 0 | 55.6843 | 89.09% | 41.5775
6376 | 570 | 425 | 134 | 4.6 | 26.1 | 0 | 0 | 0 | 0 | 42.1604 | 0 | 0.62605 | 41.5343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0.62605 | 0 | 56.25 | 90% | 41.5343
6377 | 125 | 191 | 143 | 4.3 | 24.6 | 0 | 0 | 0 | 0 | 15.0257 | 0 | 0 | 15.0257 | 0 | 0 | 0 | 64.5495 | 23.9823 | 0 | 64.5495 | 1210.9607 | 94.94% | 0 | 5.4371 | 50.2326 | 80.37% | 44.445
6378 | 16 | 50 | 48 | 3.3 | 23.4 | 0 | 0 | 0 | 0 | 2.9967 | 0 | 0 | 2.9967 | 0 | 0 | 0 | 104.0201 | 40.9651 | 0 | 104.0201 | 1106.9407 | 86.78% | 0 | 0 | 50.2326 | 80.37% | 43.9618
6379 | 0 | 1 | 1 | 2.7 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.7639 | 39.6764 | 0 | 100.7639 | 1006.1767 | 78.88% | 0 | 0 | 50.2326 | 80.37% | 39.6764
6380 | 0 | 0 | 0 | 1.9 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9794 | 36.4008 | 0 | 92.9794 | 913.1973 | 71.59% | 0 | 0 | 50.2326 | 80.37% | 36.4008
6381 | 0 | 0 | 0 | 0.7 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8229 | 34.6488 | 0 | 88.8229 | 824.3744 | 64.63% | 0 | 0 | 50.2326 | 80.37% | 34.6488
6382 | 0 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7243 | 32.9107 | 0 | 84.7243 | 739.6501 | 57.99% | 0 | 0 | 50.2326 | 80.37% | 32.9107
6383 | 0 | 0 | 0 | 0.8 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1148 | 31.8272 | 0 | 82.1148 | 657.5353 | 51.55% | 0 | 0 | 50.2326 | 80.37% | 31.8272
6384 | 0 | 0 | 0 | 0.6 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 657.5353 | 51.55% | 0 | 25 | 22.5642 | 36.1% | 25
6385 | 0 | 0 | 0 | 0.7 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 657.5353 | 51.55% | 0 | 5.1845 | 16.8264 | 26.92% | 5.1845
6386 | 0 | 0 | 0 | 1.1 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3462 | 31.9623 | 0 | 82.3462 | 575.1891 | 45.09% | 0 | 0 | 16.8264 | 26.92% | 31.9623
6387 | 0 | 0 | 0 | 0.3 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0767 | 34.5054 | 0 | 88.0767 | 487.1124 | 38.19% | 0 | 0 | 16.8264 | 26.92% | 34.5054
6388 | 0 | 0 | 0 | 0.5 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.1256 | 38.8492 | 0 | 98.1256 | 388.9868 | 30.5% | 0 | 0 | 16.8264 | 26.92% | 38.8492
6389 | 0 | 0 | 0 | 0.6 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6992 | 40.4299 | 0 | 101.6992 | 287.2875 | 22.52% | 0 | 0 | 16.8264 | 26.92% | 40.4299
6390 | 0 | 0 | 0 | 0.3 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.0804 | 41.9173 | 0 | 105.0804 | 182.2071 | 14.29% | 0 | 0 | 16.8264 | 26.92% | 41.9173
6391 | 323 | 67 | 23 | 1 | 17.3 | 0 | 0 | 0 | 0 | 0.70953 | 0 | 0 | 0.70953 | 0 | 0 | 0 | 106.016 | 42.2732 | 0 | 106.016 | 76.1911 | 5.973% | 0 | 0 | 16.8264 | 26.92% | 42.9827
6392 | 691 | 259 | 48 | 0.6 | 21.5 | 0 | 0 | 0 | 0 | 14.829 | 0 | 0 | 14.829 | 0 | 0 | 0 | 76.1911 | 29.1495 | 0 | 76.1911 | 0 | 0% | 0 | 0 | 16.8264 | 26.92% | 43.9785
6393 | 829 | 460 | 60 | 0.8 | 24.3 | 0 | 0 | 0 | 184.0157 | 35.4638 | 0 | 0 | 35.4638 | 0 | 0 | 0 | 0 | 0 | 184.0157 | 0 | 184.0157 | 14.43% | 0 | 9.5564 | 6.25 | 10% | 45.0202
6394 | 905 | 635 | 65 | 1.5 | 25.9 | 0 | 0 | 0 | 231.3221 | 45.5912 | 5.5984 | 0 | 45.5912 | 0 | 0 | 0 | 0 | 0 | 231.3221 | 0 | 415.3378 | 32.56% | 0 | 0 | 6.25 | 10% | 45.5912
6395 | 939 | 760 | 69 | 2 | 27.8 | 0 | 0 | 0 | 256.1989 | 44.3253 | 18.0918 | 0 | 44.3253 | 0 | 0 | 0 | 0 | 0 | 256.1989 | 0 | 671.5367 | 52.65% | 0 | 0 | 6.25 | 10% | 44.3253
6396 | 934 | 816 | 76 | 2.8 | 28.6 | 0 | 0 | 0 | 261.4236 | 43.725 | 25.2714 | 0 | 43.725 | 0 | 0 | 0 | 0 | 0 | 261.4236 | 0 | 932.9603 | 73.14% | 0 | 0 | 6.25 | 10% | 43.725
6397 | 937 | 819 | 76 | 2.7 | 29.5 | 0 | 0 | 0 | 265.0112 | 68.7375 | 2.0549 | 25 | 43.7375 | 0 | 0 | 0 | 0 | 0 | 265.0112 | 0 | 1197.9715 | 93.92% | 25 | 0 | 28.839 | 46.14% | 43.7375
6398 | 918 | 755 | 74 | 3.5 | 30.1 | 0 | 0 | 0 | 0 | 68.3733 | 0 | 24.7249 | 43.6484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1197.9715 | 93.92% | 24.7249 | 0 | 51.1794 | 81.89% | 43.6484
6399 | 883 | 634 | 71 | 4.6 | 29.5 | 0 | 0 | 0 | 77.5388 | 48.6906 | 12.6829 | 5.6118 | 43.0788 | 0 | 0 | 0 | 0 | 0 | 77.5388 | 0 | 1275.5102 | 100% | 5.6118 | 0 | 56.25 | 90% | 43.0788
6400 | 815 | 465 | 64 | 4.4 | 29.6 | 0 | 0 | 0 | 0 | 42.7738 | 5.433 | 0 | 42.7738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 42.7738
6401 | 687 | 267 | 51 | 4.2 | 28.2 | 0 | 0 | 0 | 0 | 30.8327 | 0 | 0 | 30.8327 | 0 | 0 | 0 | 38.2653 | 12.6293 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 1.802 | 54.2556 | 86.81% | 45.2639
6402 | 314 | 68 | 25 | 3.4 | 24.6 | 0 | 0 | 0 | 0 | 7.288 | 0 | 0 | 7.288 | 0 | 0 | 0 | 61.2514 | 22.5724 | 0 | 61.2514 | 1175.9935 | 92.2% | 0 | 14.9258 | 37.7367 | 60.38% | 44.7862
6403 | 0 | 0 | 0 | 1.8 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9221 | 40.604 | 0 | 102.9221 | 1073.0714 | 84.13% | 0 | 0 | 37.7367 | 60.38% | 40.604
6404 | 0 | 0 | 0 | 0.4 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.5689 | 37.1125 | 0 | 94.5689 | 978.5026 | 76.71% | 0 | 0 | 37.7367 | 60.38% | 37.1125
6405 | 0 | 0 | 0 | 0.3 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7742 | 35.5025 | 0 | 90.7742 | 887.7284 | 69.6% | 0 | 0 | 37.7367 | 60.38% | 35.5025
6406 | 0 | 0 | 0 | 0.7 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.663 | 33.7296 | 0 | 86.663 | 801.0654 | 62.8% | 0 | 0 | 37.7367 | 60.38% | 33.7296
6407 | 0 | 0 | 0 | 0.9 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8188 | 32.5528 | 0 | 83.8188 | 717.2467 | 56.23% | 0 | 0 | 37.7367 | 60.38% | 32.5528
6408 | 0 | 0 | 0 | 0.6 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 717.2467 | 56.23% | 0 | 3.4501 | 33.9183 | 54.27% | 3.4501
6409 | 0 | 0 | 0 | 1.6 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 717.2467 | 56.23% | 0 | 25 | 6.25 | 10% | 25
6410 | 0 | 0 | 0 | 2.2 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1075 | 32.6044 | 0 | 84.1075 | 633.1392 | 49.64% | 0 | 0 | 6.25 | 10% | 32.6044
6411 | 0 | 0 | 0 | 2.4 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5901 | 35.4106 | 0 | 90.5901 | 542.5491 | 42.54% | 0 | 0 | 6.25 | 10% | 35.4106
6412 | 0 | 0 | 0 | 2.4 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5748 | 40.1388 | 0 | 101.5748 | 440.9742 | 34.57% | 0 | 0 | 6.25 | 10% | 40.1388
6413 | 0 | 0 | 0 | 1.5 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2426 | 41.792 | 0 | 105.2426 | 335.7316 | 26.32% | 0 | 0 | 6.25 | 10% | 41.792
6414 | 0 | 0 | 0 | 2.7 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8411 | 43.3741 | 0 | 108.8411 | 226.8906 | 17.79% | 0 | 0 | 6.25 | 10% | 43.3741
6415 | 346 | 66 | 22 | 2.5 | 20.4 | 0 | 0 | 0 | 0 | 0.64974 | 0 | 0 | 0.64974 | 0 | 0 | 0 | 109.8057 | 43.702 | 0 | 109.8057 | 117.0849 | 9.179% | 0 | 0 | 6.25 | 10% | 44.3517
6416 | 706 | 260 | 47 | 1.2 | 22.6 | 0 | 0 | 0 | 0 | 15.1038 | 0 | 0 | 15.1038 | 0 | 0 | 0 | 78.8196 | 30.2145 | 0 | 78.8196 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 45.3183
6417 | 836 | 461 | 60 | 1 | 26.7 | 0 | 0 | 0 | 0 | 33.515 | 2.1148 | 0 | 33.515 | 0 | 0 | 0 | 38.2653 | 12.6806 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.1956
6418 | 896 | 631 | 69 | 2.2 | 28.3 | 0 | 0 | 0 | 228.2218 | 46.1079 | 5.1856 | 0 | 46.1079 | 0 | 0 | 0 | 0 | 0 | 228.2218 | 0 | 228.2218 | 17.89% | 0 | 0 | 6.25 | 10% | 46.1079
6419 | 925 | 753 | 75 | 2.8 | 29.4 | 0 | 0 | 0 | 251.6285 | 44.9701 | 17.6387 | 0 | 44.9701 | 0 | 0 | 0 | 0 | 0 | 251.6285 | 0 | 479.8502 | 37.62% | 0 | 0 | 6.25 | 10% | 44.9701
6420 | 937 | 817 | 78 | 2.9 | 30 | 0 | 0 | 0 | 262.2421 | 44.1818 | 24.935 | 0 | 44.1818 | 0 | 0 | 0 | 0 | 0 | 262.2421 | 0 | 742.0924 | 58.18% | 0 | 0 | 6.25 | 10% | 44.1818
6421 | 930 | 815 | 81 | 3.9 | 30.1 | 0 | 0 | 0 | 262.0393 | 54.9296 | 16.8483 | 11.0096 | 43.92 | 0 | 0 | 0 | 0 | 0 | 262.0393 | 0 | 1004.1317 | 78.72% | 11.0096 | 0 | 16.1978 | 25.92% | 43.92
6422 | 901 | 748 | 84 | 4 | 30 | 0 | 0 | 0 | 0 | 68.451 | 0 | 24.6396 | 43.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.1317 | 78.72% | 24.6396 | 0 | 38.4612 | 61.54% | 43.8114
6423 | 850 | 622 | 83 | 3.5 | 30.1 | 0 | 0 | 0 | 0 | 59.596 | 0 | 16.5088 | 43.0872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.1317 | 78.72% | 16.5088 | 0 | 53.3779 | 85.4% | 43.0872
6424 | 761 | 447 | 77 | 3 | 30.1 | 0 | 0 | 0 | 138.4624 | 46.2296 | 0 | 3.1786 | 43.0509 | 0 | 0 | 0 | 0 | 0 | 138.4624 | 0 | 1142.5941 | 89.58% | 3.1786 | 0 | 56.25 | 90% | 43.0509
6425 | 618 | 252 | 61 | 2 | 29.9 | 0 | 0 | 0 | 132.9161 | 28.4522 | 0 | 0 | 28.4522 | 0 | 0 | 0 | 0 | 0 | 132.9161 | 0 | 1275.5102 | 100% | 0 | 17.1292 | 37.2925 | 59.67% | 45.5815
6426 | 270 | 64 | 28 | 2.5 | 27 | 0 | 0 | 0 | 0 | 6.6844 | 0 | 0 | 6.6844 | 0 | 0 | 0 | 98.3746 | 38.2132 | 0 | 98.3746 | 1177.1356 | 92.29% | 0 | 0 | 37.2925 | 59.67% | 44.8977
6427 | 0 | 0 | 0 | 2.1 | 24.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.1276 | 40.5107 | 0 | 103.1276 | 1074.0079 | 84.2% | 0 | 0 | 37.2925 | 59.67% | 40.5107
6428 | 0 | 0 | 0 | 3.7 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.2095 | 0 | 127.551 | 946.4569 | 74.2% | 14.0273 | 0 | 49.967 | 79.95% | 37.1821
6429 | 0 | 0 | 0 | 3.2 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5602 | 35.3786 | 0 | 90.5602 | 855.8968 | 67.1% | 0 | 0 | 49.967 | 79.95% | 35.3786
6430 | 0 | 0 | 0 | 2.2 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7298 | 33.7283 | 0 | 86.7298 | 769.167 | 60.3% | 0 | 0 | 49.967 | 79.95% | 33.7283
6431 | 0 | 0 | 0 | 2.3 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1269 | 32.6127 | 0 | 84.1269 | 685.0401 | 53.71% | 0 | 0 | 49.967 | 79.95% | 32.6127
6432 | 0 | 0 | 0 | 2.5 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1557 | 32.2172 | 0 | 83.1557 | 601.8844 | 47.19% | 0 | 0 | 49.967 | 79.95% | 32.2172
6433 | 0 | 0 | 0 | 2.6 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5751 | 31.9944 | 0 | 82.5751 | 519.3093 | 40.71% | 0 | 0 | 49.967 | 79.95% | 31.9944
6434 | 0 | 0 | 0 | 2.4 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6073 | 32.472 | 0 | 83.6073 | 435.702 | 34.16% | 0 | 0 | 49.967 | 79.95% | 32.472
6435 | 0 | 0 | 0 | 2.8 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.2506 | 42.2751 | 0 | 106.2506 | 329.4514 | 25.83% | 6.9536 | 0 | 56.25 | 90% | 35.3215
6436 | 0 | 0 | 0 | 2.2 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5362 | 39.8478 | 0 | 100.5362 | 228.9152 | 17.95% | 0 | 0 | 56.25 | 90% | 39.8478
6437 | 0 | 0 | 0 | 1.8 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7589 | 41.6624 | 0 | 104.7589 | 124.1563 | 9.734% | 0 | 0 | 56.25 | 90% | 41.6624
6438 | 0 | 0 | 0 | 2.3 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.7026 | 42.9423 | 0 | 107.7026 | 16.4537 | 1.29% | 0 | 0 | 56.25 | 90% | 42.9423
6439 | 304 | 63 | 24 | 1.8 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4537 | 1.29% | 0 | 25 | 28.5817 | 45.73% | 25
6440 | 679 | 255 | 52 | 1.1 | 22.2 | 0 | 0 | 0 | 61.5616 | 15.1084 | 0 | 0 | 15.1084 | 0 | 0 | 0 | 0 | 0 | 61.5616 | 0 | 78.0153 | 6.116% | 0 | 20.178 | 6.25 | 10% | 35.2864
6441 | 824 | 458 | 65 | 2 | 24.5 | 0 | 0 | 0 | 0 | 32.8892 | 3.5661 | 0 | 32.8892 | 0 | 0 | 0 | 38.2653 | 12.7494 | 0 | 38.2653 | 39.75 | 3.116% | 0 | 0 | 6.25 | 10% | 45.6386
6442 | 894 | 630 | 72 | 4.2 | 25.7 | 0 | 0 | 0 | 0 | 33.4076 | 19.6352 | 0 | 33.4076 | 0 | 0 | 0 | 38.2653 | 12.7129 | 0 | 38.2653 | 1.4847 | 0.1164% | 0 | 0 | 6.25 | 10% | 46.1204
6443 | 929 | 754 | 77 | 5.3 | 26.1 | 0 | 0 | 0 | 250.588 | 45.0898 | 20.274 | 0 | 45.0898 | 0 | 0 | 0 | 0 | 0 | 250.588 | 0 | 252.0727 | 19.76% | 0 | 0 | 6.25 | 10% | 45.0898
6444 | 941 | 818 | 79 | 4.5 | 26.8 | 0 | 0 | 0 | 262.0975 | 44.5606 | 27.0843 | 0 | 44.5606 | 0 | 0 | 0 | 0 | 0 | 262.0975 | 0 | 514.1702 | 40.31% | 0 | 0 | 6.25 | 10% | 44.5606
6445 | 933 | 816 | 82 | 3.4 | 27.2 | 0 | 0 | 0 | 263.2645 | 54.9372 | 17.0628 | 10.4267 | 44.5105 | 0 | 0 | 0 | 0 | 0 | 263.2645 | 0 | 777.4347 | 60.95% | 10.4267 | 0 | 15.6712 | 25.07% | 44.5105
6446 | 903 | 747 | 85 | 3 | 27.9 | 0 | 0 | 0 | 252.146 | 68.3209 | 0 | 23.9483 | 44.3726 | 0 | 0 | 0 | 0 | 0 | 252.146 | 0 | 1029.5808 | 80.72% | 23.9483 | 0 | 37.3099 | 59.7% | 44.3726
6447 | 859 | 623 | 83 | 3.7 | 28.1 | 0 | 0 | 0 | 0 | 60.6544 | 0 | 17.0631 | 43.5913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1029.5808 | 80.72% | 17.0631 | 0 | 52.7274 | 84.36% | 43.5913
6448 | 770 | 447 | 76 | 3.8 | 27.9 | 0 | 0 | 0 | 193.1089 | 47.2475 | 0 | 3.8985 | 43.349 | 0 | 0 | 0 | 0 | 0 | 193.1089 | 0 | 1222.6896 | 95.86% | 3.8985 | 0 | 56.25 | 90% | 43.349
6449 | 600 | 244 | 61 | 3.8 | 26.9 | 0 | 0 | 0 | 52.8206 | 28.3464 | 0 | 0 | 28.3464 | 0 | 0 | 0 | 0 | 0 | 52.8206 | 0 | 1275.5102 | 100% | 0 | 17.6626 | 36.7022 | 58.72% | 46.009
6450 | 225 | 58 | 27 | 3.7 | 24.6 | 0 | 0 | 0 | 0 | 5.8789 | 0 | 0 | 5.8789 | 0 | 0 | 0 | 100.8713 | 39.509 | 0 | 100.8713 | 1174.6389 | 92.09% | 0 | 0 | 36.7022 | 58.72% | 45.3879
6451 | 0 | 0 | 0 | 3.1 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.075 | 41.0747 | 0 | 104.075 | 1070.5639 | 83.93% | 0 | 0 | 36.7022 | 58.72% | 41.0747
6452 | 0 | 0 | 0 | 2.3 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7673 | 37.6013 | 0 | 95.7673 | 974.7966 | 76.42% | 0 | 0 | 36.7022 | 58.72% | 37.6013
6453 | 0 | 0 | 0 | 2 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6461 | 35.8786 | 0 | 91.6461 | 883.1505 | 69.24% | 0 | 0 | 36.7022 | 58.72% | 35.8786
6454 | 0 | 0 | 0 | 1.4 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.389 | 0 | 127.551 | 755.5994 | 59.24% | 17.0995 | 0 | 52.1526 | 83.44% | 34.2895
6455 | 0 | 0 | 0 | 1.3 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3628 | 37.5263 | 0 | 95.3628 | 660.2366 | 51.76% | 4.5348 | 0 | 56.25 | 90% | 32.9915
6456 | 0 | 0 | 0 | 0.9 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6602 | 32.479 | 0 | 83.6602 | 576.5764 | 45.2% | 0 | 0 | 56.25 | 90% | 32.479
6457 | 0 | 0 | 0 | 0.1 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6543 | 32.0807 | 0 | 82.6543 | 493.9221 | 38.72% | 0 | 0 | 56.25 | 90% | 32.0807
6458 | 0 | 0 | 0 | 0.2 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.8299 | 32.6378 | 0 | 83.8299 | 410.0922 | 32.15% | 0 | 0 | 56.25 | 90% | 32.6378
6459 | 0 | 0 | 0 | 0.8 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2439 | 35.4148 | 0 | 90.2439 | 319.8484 | 25.08% | 0 | 0 | 56.25 | 90% | 35.4148
6460 | 0 | 0 | 0 | 0.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.228 | 39.7544 | 0 | 100.228 | 219.6203 | 17.22% | 0 | 0 | 56.25 | 90% | 39.7544
6461 | 0 | 0 | 0 | 0.4 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1047 | 41.4619 | 0 | 104.1047 | 115.5156 | 9.056% | 0 | 0 | 56.25 | 90% | 41.4619
6462 | 0 | 0 | 0 | 0.5 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.9824 | 43.1651 | 0 | 107.9824 | 7.5332 | 0.5906% | 0 | 0 | 56.25 | 90% | 43.1651
6463 | 254 | 59 | 26 | 1.5 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5332 | 0.5906% | 0 | 25 | 28.5817 | 45.73% | 25
6464 | 633 | 247 | 59 | 0.6 | 22 | 0 | 0 | 0 | 68.9974 | 14.9519 | 0 | 0 | 14.9519 | 0 | 0 | 0 | 0 | 0 | 68.9974 | 0 | 76.5306 | 6% | 0 | 20.178 | 6.25 | 10% | 35.1299
6465 | 799 | 450 | 71 | 0.9 | 24.7 | 0 | 0 | 0 | 0 | 33.3937 | 2.1701 | 0 | 33.3937 | 0 | 0 | 0 | 38.2653 | 12.7434 | 0 | 38.2653 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 46.1372
6466 | 881 | 623 | 75 | 1.4 | 26.1 | 0 | 0 | 0 | 0 | 33.9481 | 16.9625 | 0 | 33.9481 | 0 | 0 | 0 | 38.2653 | 12.7002 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.6483
6467 | 922 | 747 | 78 | 1.5 | 27.1 | 0 | 0 | 0 | 251.0496 | 45.3071 | 16.4936 | 0 | 45.3071 | 0 | 0 | 0 | 0 | 0 | 251.0496 | 0 | 251.0496 | 19.68% | 0 | 0 | 6.25 | 10% | 45.3071
6468 | 939 | 812 | 79 | 1.9 | 28.2 | 0 | 0 | 0 | 263.2065 | 44.342 | 24.1973 | 0 | 44.342 | 0 | 0 | 0 | 0 | 0 | 263.2065 | 0 | 514.2562 | 40.32% | 0 | 0 | 6.25 | 10% | 44.342
6469 | 928 | 809 | 84 | 2.7 | 28.9 | 0 | 0 | 0 | 262.0882 | 51.8841 | 19.1251 | 7.985 | 43.8991 | 0 | 0 | 0 | 0 | 0 | 262.0882 | 0 | 776.3444 | 60.87% | 7.985 | 0 | 13.4649 | 21.54% | 43.8991
6470 | 906 | 743 | 84 | 3.5 | 29.5 | 0 | 0 | 0 | 252.6536 | 68.4957 | 0 | 24.8696 | 43.6261 | 0 | 0 | 0 | 0 | 0 | 252.6536 | 0 | 1028.998 | 80.67% | 24.8696 | 0 | 35.936 | 57.5% | 43.6261
6471 | 865 | 619 | 80 | 3.9 | 29.7 | 0 | 0 | 0 | 197.1415 | 60.532 | 0 | 17.7917 | 42.7404 | 0 | 0 | 0 | 0 | 0 | 197.1415 | 0 | 1226.1395 | 96.13% | 17.7917 | 0 | 52.0119 | 83.22% | 42.7404
6472 | 774 | 443 | 74 | 3.9 | 29 | 0 | 0 | 0 | 0 | 47.1077 | 0 | 4.6905 | 42.4173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.1395 | 96.13% | 4.6905 | 0 | 56.25 | 90% | 42.4173
6473 | 605 | 241 | 59 | 3.2 | 28 | 0 | 0 | 0 | 0 | 28.1325 | 0 | 0 | 28.1325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.1395 | 96.13% | 0 | 16.1552 | 38.3705 | 61.39% | 44.2877
6474 | 235 | 56 | 26 | 3.5 | 24.7 | 0 | 0 | 0 | 0 | 5.9368 | 0 | 0 | 5.9368 | 0 | 0 | 0 | 96.231 | 37.5166 | 0 | 96.231 | 1129.9085 | 88.58% | 0 | 0 | 38.3705 | 61.39% | 43.4534
6475 | 0 | 0 | 0 | 1.8 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.3686 | 39.5065 | 0 | 100.3686 | 1029.5399 | 80.72% | 0 | 0 | 38.3705 | 61.39% | 39.5065
6476 | 0 | 0 | 0 | 0.7 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3864 | 36.5624 | 0 | 93.3864 | 936.1535 | 73.39% | 0 | 0 | 38.3705 | 61.39% | 36.5624
6477 | 0 | 0 | 0 | 0.8 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0602 | 34.7196 | 0 | 89.0602 | 847.0933 | 66.41% | 0 | 0.35264 | 37.9803 | 60.77% | 35.0722
6478 | 0 | 0 | 0 | 1.2 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9486 | 33.4038 | 0 | 85.9486 | 761.1447 | 59.67% | 0 | 0 | 37.9803 | 60.77% | 33.4038
6479 | 0 | 0 | 0 | 0.9 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4626 | 31.9512 | 0 | 82.4626 | 678.6821 | 53.21% | 0 | 0 | 37.9803 | 60.77% | 31.9512
6480 | 0 | 0 | 0 | 0.2 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6191 | 31.181 | 0 | 80.6191 | 598.0631 | 46.89% | 0 | 0 | 37.9803 | 60.77% | 31.181
6481 | 0 | 0 | 0 | 1.4 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2994 | 30.6351 | 0 | 79.2994 | 518.7637 | 40.67% | 0 | 0 | 37.9803 | 60.77% | 30.6351
6482 | 0 | 0 | 0 | 1.1 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.6159 | 30.3301 | 0 | 78.6159 | 440.1478 | 34.51% | 0 | 0 | 37.9803 | 60.77% | 30.3301
6483 | 0 | 0 | 0 | 1.3 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.9887 | 30.9331 | 0 | 79.9887 | 360.1592 | 28.24% | 0 | 0 | 37.9803 | 60.77% | 30.9331
6484 | 0 | 0 | 0 | 2 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2793 | 32.3509 | 0 | 83.2793 | 276.8799 | 21.71% | 0 | 0 | 37.9803 | 60.77% | 32.3509
6485 | 0 | 0 | 0 | 1 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1747 | 33.5973 | 0 | 86.1747 | 190.7053 | 14.95% | 0 | 0 | 37.9803 | 60.77% | 33.5973
6486 | 0 | 0 | 0 | 1.2 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7952 | 36.4872 | 0 | 92.7952 | 97.9101 | 7.676% | 0 | 0 | 37.9803 | 60.77% | 36.4872
6487 | 281 | 58 | 23 | 1.1 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9101 | 38.6514 | 0 | 97.9101 | 0 | 0% | 0 | 0 | 37.9803 | 60.77% | 38.6514
6488 | 655 | 245 | 53 | 1.1 | 22.8 | 0 | 0 | 0 | 0 | 14.9983 | 0 | 0 | 14.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 24.5459 | 10.8145 | 17.3% | 39.5441
6489 | 803 | 446 | 68 | 1.5 | 24.8 | 0 | 0 | 0 | 0 | 35.8892 | 0 | 0 | 35.8892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 4.1243 | 6.25 | 10% | 40.0135
6490 | 875 | 617 | 76 | 1.1 | 27 | 0 | 0 | 0 | 0 | 40.4396 | 9.8469 | 0 | 40.4396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 40.4396
6491 | 909 | 738 | 81 | 1.6 | 28.3 | 0 | 0 | 0 | 27.549 | 39.5901 | 21.6506 | 0 | 39.5901 | 0 | 0 | 0 | 0 | 0 | 27.549 | 0 | 27.549 | 2.16% | 0 | 0 | 6.25 | 10% | 39.5901
6492 | 918 | 800 | 86 | 3.7 | 28.9 | 0 | 0 | 0 | 255.9162 | 37.9648 | 31.7066 | 0 | 37.9648 | 0 | 0 | 0 | 0 | 0 | 255.9162 | 0 | 283.4651 | 22.22% | 0 | 0 | 6.25 | 10% | 37.9648
6493 | 906 | 796 | 91 | 3.8 | 28.9 | 0 | 0 | 0 | 254.7048 | 36.912 | 34.3315 | 0 | 36.912 | 0 | 0 | 0 | 0 | 0 | 254.7048 | 0 | 538.1699 | 42.19% | 0 | 0 | 6.25 | 10% | 36.912
6494 | 875 | 730 | 96 | 3.6 | 29.2 | 0 | 0 | 0 | 243.1571 | 61.4788 | 6.0967 | 25 | 36.4788 | 0 | 0 | 0 | 0 | 0 | 243.1571 | 0 | 781.327 | 61.26% | 25 | 0 | 28.839 | 46.14% | 36.4788
6495 | 818 | 604 | 97 | 4.6 | 29 | 0 | 0 | 0 | 0 | 59.5175 | 0 | 23.2991 | 36.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 781.327 | 61.26% | 23.2991 | 0 | 49.8912 | 79.83% | 36.2184
6496 | 733 | 432 | 85 | 4.3 | 28.4 | 0 | 0 | 0 | 181.5091 | 43.4217 | 2.6815 | 7.0375 | 36.3841 | 0 | 0 | 0 | 0 | 0 | 181.5091 | 0 | 962.8362 | 75.49% | 7.0375 | 0 | 56.25 | 90% | 36.3841
6497 | 561 | 232 | 65 | 4.7 | 27.2 | 0 | 0 | 0 | 115.3367 | 27.1936 | 0 | 0 | 27.1936 | 0 | 0 | 0 | 0 | 0 | 115.3367 | 0 | 1078.1728 | 84.53% | 0 | 11.7197 | 43.2794 | 69.25% | 38.9133
6498 | 185 | 51 | 27 | 4.1 | 25 | 0 | 0 | 0 | 0 | 5.1643 | 0 | 0 | 5.1643 | 0 | 0 | 0 | 88.1071 | 34.0206 | 0 | 88.1071 | 990.0658 | 77.62% | 0 | 0 | 43.2794 | 69.25% | 39.1848
6499 | 0 | 0 | 0 | 3.8 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3283 | 36.4287 | 0 | 93.3283 | 896.7375 | 70.3% | 0 | 0 | 43.2794 | 69.25% | 36.4287
6500 | 0 | 0 | 0 | 3.4 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7989 | 34.1572 | 0 | 87.7989 | 808.9386 | 63.42% | 0 | 0 | 43.2794 | 69.25% | 34.1572
6501 | 0 | 0 | 0 | 2.8 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6007 | 31.9665 | 0 | 82.6007 | 726.3379 | 56.94% | 0 | 0 | 43.2794 | 69.25% | 31.9665
6502 | 0 | 0 | 0 | 1.1 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3987 | 30.1866 | 0 | 78.3987 | 647.9393 | 50.8% | 0 | 0 | 43.2794 | 69.25% | 30.1866
6503 | 0 | 0 | 0 | 1.5 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.166 | 28.8204 | 0 | 75.166 | 572.7733 | 44.91% | 0 | 0 | 43.2794 | 69.25% | 28.8204
6504 | 0 | 0 | 0 | 0.9 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.9786 | 27.8845 | 0 | 72.9786 | 499.7947 | 39.18% | 0 | 0 | 43.2794 | 69.25% | 27.8845
6505 | 0 | 0 | 0 | 1.3 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.7561 | 27.3943 | 0 | 71.7561 | 428.0386 | 33.56% | 0 | 0 | 43.2794 | 69.25% | 27.3943
6506 | 0 | 0 | 0 | 0.8 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.6885 | 27.365 | 0 | 71.6885 | 356.3501 | 27.94% | 0 | 0 | 43.2794 | 69.25% | 27.365
6507 | 0 | 0 | 0 | 1.4 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.8312 | 27.8636 | 0 | 72.8312 | 283.5189 | 22.23% | 0 | 0 | 43.2794 | 69.25% | 27.8636
6508 | 0 | 0 | 0 | 0.5 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.0586 | 14.9999 | 0 | 43.0586 | 240.4603 | 18.85% | 0 | 13.3818 | 28.4694 | 45.55% | 28.3817
6509 | 0 | 0 | 0 | 0.9 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8127 | 28.7577 | 0 | 74.8127 | 165.6477 | 12.99% | 0 | 0 | 28.4694 | 45.55% | 28.7577
6510 | 0 | 0 | 0 | 1.3 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2056 | 31.0988 | 0 | 80.2056 | 85.442 | 6.699% | 0 | 0 | 28.4694 | 45.55% | 31.0988
6511 | 189 | 54 | 29 | 1.8 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.442 | 33.3453 | 0 | 85.442 | 0 | 0% | 0 | 0 | 28.4694 | 45.55% | 33.3453
6512 | 530 | 237 | 81 | 1.2 | 20.4 | 0 | 0 | 0 | 0 | 15.0194 | 0 | 0 | 15.0194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 19.5612 | 6.8204 | 10.91% | 34.5806
6513 | 688 | 435 | 111 | 1.2 | 24 | 0 | 0 | 0 | 147.5424 | 35.0025 | 0 | 0 | 35.0025 | 0 | 0 | 0 | 0 | 0 | 147.5424 | 0 | 147.5424 | 11.57% | 0 | 0.51537 | 6.25 | 10% | 35.5179
6514 | 775 | 608 | 129 | 2.7 | 24.6 | 0 | 0 | 0 | 193.8607 | 36.4175 | 15.268 | 0 | 36.4175 | 0 | 0 | 0 | 0 | 0 | 193.8607 | 0 | 341.4031 | 26.77% | 0 | 0 | 6.25 | 10% | 36.4175
6515 | 831 | 732 | 132 | 2.6 | 25.5 | 0 | 0 | 0 | 0 | 36.4524 | 26.3358 | 0 | 36.4524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341.4031 | 26.77% | 0 | 0 | 6.25 | 10% | 36.4524
6516 | 873 | 800 | 122 | 2 | 27.3 | 0 | 0 | 0 | 206.9642 | 35.0945 | 33.5136 | 0 | 35.0945 | 0 | 0 | 0 | 0 | 0 | 206.9642 | 0 | 548.3672 | 42.99% | 0 | 0 | 6.25 | 10% | 35.0945
6517 | 885 | 799 | 113 | 2.2 | 28.2 | 0 | 0 | 0 | 249.2924 | 34.277 | 35.5939 | 0 | 34.277 | 0 | 0 | 0 | 0 | 0 | 249.2924 | 0 | 797.6596 | 62.54% | 0 | 0 | 6.25 | 10% | 34.277
6518 | 860 | 730 | 110 | 2.2 | 29.6 | 0 | 0 | 0 | 239.3137 | 55.0799 | 11.0225 | 21.0773 | 34.0026 | 0 | 0 | 0 | 0 | 0 | 239.3137 | 0 | 1036.9734 | 81.3% | 21.0773 | 0 | 25.2946 | 40.47% | 34.0026
6519 | 794 | 600 | 110 | 2.5 | 30 | 0 | 0 | 0 | 212.7956 | 58.083 | 0 | 23.9815 | 34.1015 | 0 | 0 | 0 | 0 | 0 | 212.7956 | 0 | 1249.769 | 97.98% | 23.9815 | 0 | 46.9633 | 75.14% | 34.1015
6520 | 705 | 428 | 97 | 3.2 | 29.6 | 0 | 0 | 0 | 0 | 45.0284 | 0 | 10.2779 | 34.7505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.769 | 97.98% | 10.2779 | 0 | 56.25 | 90% | 34.7505
6521 | 554 | 233 | 70 | 3.8 | 27.5 | 0 | 0 | 0 | 0 | 27.1883 | 0 | 0 | 27.1883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.769 | 97.98% | 0 | 11.1373 | 43.924 | 70.28% | 38.3255
6522 | 175 | 48 | 27 | 3.6 | 25.8 | 0 | 0 | 0 | 0 | 4.7423 | 0 | 0 | 4.7423 | 0 | 0 | 0 | 88.7064 | 34.21 | 0 | 88.7064 | 1161.0626 | 91.03% | 0 | 0 | 43.924 | 70.28% | 38.9522
6523 | 0 | 0 | 0 | 2.9 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.927 | 36.678 | 0 | 93.927 | 1067.1356 | 83.66% | 0 | 0 | 43.924 | 70.28% | 36.678
6524 | 0 | 0 | 0 | 1 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.8279 | 0 | 38.2653 | 1028.8703 | 80.66% | 0 | 21.3669 | 20.2765 | 32.44% | 34.1948
6525 | 0 | 0 | 0 | 0.8 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.8128 | 32.0347 | 0 | 82.8128 | 946.0575 | 74.17% | 0 | 0 | 20.2765 | 32.44% | 32.0347
6526 | 0 | 0 | 0 | 0.4 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.0446 | 26.1319 | 0 | 69.0446 | 877.013 | 68.76% | 0 | 4.2623 | 15.5593 | 24.89% | 30.3941
6527 | 0 | 0 | 0 | 0.7 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3189 | 29.3232 | 0 | 76.3189 | 800.6941 | 62.77% | 0 | 0 | 15.5593 | 24.89% | 29.3232
6528 | 0 | 0 | 0 | 0.7 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1463 | 28.8483 | 0 | 75.1463 | 725.5478 | 56.88% | 0 | 0 | 15.5593 | 24.89% | 28.8483
6529 | 0 | 0 | 0 | 0.6 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3202 | 28.9235 | 0 | 75.3202 | 650.2275 | 50.98% | 0 | 0 | 15.5593 | 24.89% | 28.9235
6530 | 0 | 0 | 0 | 0.8 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3264 | 29.8134 | 0 | 77.3264 | 572.9011 | 44.92% | 0 | 0 | 15.5593 | 24.89% | 29.8134
6531 | 0 | 0 | 0 | 0.5 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4316 | 33.3592 | 0 | 85.4316 | 487.4695 | 38.22% | 0 | 0 | 15.5593 | 24.89% | 33.3592
6532 | 0 | 0 | 0 | 1.7 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0892 | 38.3562 | 0 | 97.0892 | 390.3803 | 30.61% | 0 | 0 | 15.5593 | 24.89% | 38.3562
6533 | 0 | 0 | 0 | 1.4 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.7616 | 40.4243 | 0 | 101.7616 | 288.6187 | 22.63% | 0 | 0 | 15.5593 | 24.89% | 40.4243
6534 | 0 | 0 | 0 | 0.8 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3179 | 42.051 | 0 | 105.3179 | 183.3008 | 14.37% | 0 | 0 | 15.5593 | 24.89% | 42.051
6535 | 286 | 57 | 22 | 0.9 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.2888 | 43.2459 | 0 | 108.2888 | 75.012 | 5.881% | 0 | 0 | 15.5593 | 24.89% | 43.2459
6536 | 692 | 250 | 52 | 0.6 | 22.4 | 0 | 0 | 0 | 0 | 15.5515 | 0 | 0 | 15.5515 | 0 | 0 | 0 | 75.012 | 28.5913 | 0 | 75.012 | 0 | 0% | 0 | 0 | 15.5593 | 24.89% | 44.1428
6537 | 839 | 455 | 67 | 0.9 | 25.1 | 0 | 0 | 0 | 183.3206 | 36.9151 | 0 | 0 | 36.9151 | 0 | 0 | 0 | 0 | 0 | 183.3206 | 0 | 183.3206 | 14.37% | 0 | 8.4115 | 6.25 | 10% | 45.3266
6538 | 906 | 627 | 76 | 2.3 | 25 | 0 | 0 | 0 | 229.3921 | 45.7764 | 7.6106 | 0 | 45.7764 | 0 | 0 | 0 | 0 | 0 | 229.3921 | 0 | 412.7127 | 32.36% | 0 | 0 | 6.25 | 10% | 45.7764
6539 | 928 | 746 | 85 | 2 | 26 | 0 | 0 | 0 | 126.6281 | 44.7124 | 19.0073 | 0 | 44.7124 | 0 | 0 | 0 | 0 | 0 | 126.6281 | 0 | 539.3408 | 42.28% | 0 | 0 | 6.25 | 10% | 44.7124
6540 | 937 | 808 | 89 | 1.8 | 28.5 | 0 | 0 | 0 | 0 | 44.0439 | 24.9114 | 0 | 44.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.3408 | 42.28% | 0 | 0 | 6.25 | 10% | 44.0439
6541 | 927 | 804 | 92 | 2.3 | 29.4 | 0 | 0 | 0 | 0 | 54.5566 | 16.3159 | 10.5349 | 44.0217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.3408 | 42.28% | 10.5349 | 0 | 15.7689 | 25.23% | 44.0217
6542 | 910 | 746 | 96 | 2.9 | 30.3 | 0 | 0 | 0 | 253.9435 | 68.7956 | 0 | 24.8881 | 43.9075 | 0 | 0 | 0 | 0 | 0 | 253.9435 | 0 | 793.2843 | 62.19% | 24.8881 | 0 | 38.2568 | 61.21% | 43.9075
6543 | 784 | 591 | 112 | 3.3 | 30.2 | 0 | 0 | 0 | 209.2934 | 58.1926 | 0 | 15.1361 | 43.0565 | 0 | 0 | 0 | 0 | 0 | 209.2934 | 0 | 1002.5778 | 78.6% | 15.1361 | 0 | 51.9332 | 83.09% | 43.0565
6544 | 766 | 442 | 88 | 4.1 | 29.3 | 0 | 0 | 0 | 189.7838 | 47.7241 | 0 | 4.7776 | 42.9465 | 0 | 0 | 0 | 0 | 0 | 189.7838 | 0 | 1192.3616 | 93.48% | 4.7776 | 0 | 56.25 | 90% | 42.9465
6545 | 429 | 206 | 76 | 3.9 | 26.5 | 0 | 0 | 0 | 83.1486 | 23.0173 | 0 | 0 | 23.0173 | 0 | 0 | 0 | 0 | 0 | 83.1486 | 0 | 1275.5102 | 100% | 0 | 22.5419 | 31.3021 | 50.08% | 45.5592
6546 | 48 | 39 | 33 | 2.5 | 23.1 | 0 | 0 | 0 | 0 | 2.6609 | 0 | 0 | 2.6609 | 0 | 0 | 0 | 105.7092 | 41.7159 | 0 | 105.7092 | 1169.801 | 91.71% | 0 | 0 | 31.3021 | 50.08% | 44.3768
6547 | 0 | 0 | 0 | 1.5 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.2905 | 39.9647 | 0 | 101.2905 | 1068.5105 | 83.77% | 0 | 0 | 31.3021 | 50.08% | 39.9647
6548 | 0 | 0 | 0 | 0.7 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1995 | 36.5485 | 0 | 93.1995 | 975.311 | 76.46% | 0 | 0 | 31.3021 | 50.08% | 36.5485
6549 | 0 | 0 | 0 | 1.4 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2014 | 34.8243 | 0 | 89.2014 | 886.1096 | 69.47% | 0 | 0 | 31.3021 | 50.08% | 34.8243
6550 | 0 | 0 | 0 | 2 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.119 | 33.0403 | 0 | 85.119 | 800.9905 | 62.8% | 0 | 0 | 31.3021 | 50.08% | 33.0403
6551 | 0 | 0 | 0 | 1.6 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.552 | 31.9512 | 0 | 82.552 | 718.4385 | 56.33% | 0 | 0 | 31.3021 | 50.08% | 31.9512
6552 | 0 | 0 | 0 | 1.2 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2907 | 31.4609 | 0 | 81.2907 | 637.1479 | 49.95% | 0 | 0 | 31.3021 | 50.08% | 31.4609
6553 | 0 | 0 | 0 | 0.6 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.1479 | 49.95% | 0 | 0 | 31.3021 | 50.08% | 0
6554 | 0 | 0 | 0 | 0.2 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.1479 | 49.95% | 0 | 14.1696 | 15.6202 | 24.99% | 14.1696
6555 | 0 | 0 | 0 | 0.9 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7594 | 35.2101 | 0 | 89.7594 | 547.3884 | 42.92% | 0 | 0 | 15.6202 | 24.99% | 35.2101
6556 | 0 | 0 | 0 | 1.1 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6943 | 39.962 | 0 | 100.6943 | 446.6941 | 35.02% | 0 | 0 | 15.6202 | 24.99% | 39.962
6557 | 0 | 0 | 0 | 0.4 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.4316 | 46.4132 | 0 | 115.4316 | 331.2626 | 25.97% | 4.2758 | 0 | 19.4837 | 31.17% | 42.1373
6558 | 0 | 0 | 0 | 0.3 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.671 | 0 | 127.551 | 203.7115 | 15.97% | 8.1493 | 0 | 26.8471 | 42.96% | 43.5217
6559 | 36 | 37 | 34 | 1.6 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.8442 | 44.7069 | 0 | 111.8442 | 91.8674 | 7.202% | 0 | 0 | 26.8471 | 42.96% | 44.7069
6560 | 58 | 134 | 116 | 0.7 | 19.7 | 0 | 0 | 0 | 0 | 9.4381 | 0 | 0 | 9.4381 | 0 | 0 | 0 | 91.8674 | 36.0111 | 0 | 91.8674 | 0 | 0% | 0 | 0 | 26.8471 | 42.96% | 45.4492
6561 | 229 | 365 | 256 | 0.9 | 23 | 0 | 0 | 0 | 0 | 28.123 | 0 | 0 | 28.123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 18.2078 | 6.6959 | 10.71% | 46.3307
6562 | 375 | 604 | 361 | 1 | 26.1 | 0 | 0 | 0 | 0 | 46.0866 | 0 | 0 | 46.0866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0.40291 | 6.25 | 10% | 46.4895
6563 | 859 | 860 | 246 | 2.2 | 27.5 | 0 | 0 | 0 | 202.7045 | 45.4575 | 25.3967 | 0 | 45.4575 | 0 | 0 | 0 | 0 | 0 | 202.7045 | 0 | 202.7045 | 15.89% | 0 | 0 | 6.25 | 10% | 45.4575
6564 | 914 | 804 | 106 | 2.1 | 26.8 | 0 | 0 | 0 | 255.4968 | 69.6052 | 0.078133 | 25 | 44.6052 | 0 | 0 | 0 | 0 | 0 | 255.4968 | 0 | 458.2013 | 35.92% | 25 | 0 | 28.839 | 46.14% | 44.6052
6565 | 919 | 797 | 96 | 2.3 | 28.1 | 0 | 0 | 0 | 259.2582 | 69.6386 | 1.3715 | 25 | 44.6386 | 0 | 0 | 0 | 0 | 0 | 259.2582 | 0 | 717.4595 | 56.25% | 25 | 0 | 51.428 | 82.28% | 44.6386
6566 | 896 | 730 | 95 | 2.2 | 29.5 | 0 | 0 | 0 | 250.0237 | 44.718 | 22.5325 | 0 | 44.718 | 0 | 0 | 0 | 0 | 0 | 250.0237 | 0 | 967.4832 | 75.85% | 0 | 0 | 51.428 | 82.28% | 44.718
6567 | 838 | 600 | 93 | 2.8 | 30.1 | 0 | 0 | 0 | 224.9071 | 49.1968 | 9.8267 | 5.3367 | 43.8601 | 0 | 0 | 0 | 0 | 0 | 224.9071 | 0 | 1192.3903 | 93.48% | 5.3367 | 0 | 56.25 | 90% | 43.8601
6568 | 372 | 309 | 126 | 2.5 | 29 | 0 | 0 | 0 | 83.1199 | 29.9125 | 0 | 0 | 29.9125 | 0 | 0 | 0 | 0 | 0 | 83.1199 | 0 | 1275.5102 | 100% | 0 | 13.6872 | 41.1019 | 65.76% | 43.5997
6569 | 73 | 146 | 125 | 1.6 | 28.6 | 0 | 0 | 0 | 0 | 10.9324 | 0 | 0 | 10.9324 | 0 | 0 | 0 | 91.9076 | 35.3092 | 0 | 91.9076 | 1183.6026 | 92.79% | 0 | 0 | 41.1019 | 65.76% | 46.2416
6570 | 10 | 22 | 22 | 3.6 | 28.7 | 0 | 0 | 0 | 0 | 1.1031 | 0 | 0 | 1.1031 | 0 | 0 | 0 | 112.5772 | 44.0411 | 0 | 112.5772 | 1071.0255 | 83.97% | 0 | 0 | 41.1019 | 65.76% | 45.1442
6571 | 0 | 0 | 0 | 3.1 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8384 | 40.8602 | 0 | 104.8384 | 966.187 | 75.75% | 0 | 0 | 41.1019 | 65.76% | 40.8602
6572 | 0 | 0 | 0 | 2.3 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.51 | 37.508 | 0 | 96.51 | 869.677 | 68.18% | 0 | 0 | 41.1019 | 65.76% | 37.508
6573 | 0 | 0 | 0 | 1.9 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6684 | 35.575 | 0 | 91.6684 | 778.0086 | 61% | 0 | 0 | 41.1019 | 65.76% | 35.575
6574 | 0 | 0 | 0 | 3.5 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6331 | 33.8578 | 0 | 87.6331 | 690.3755 | 54.13% | 0 | 0 | 41.1019 | 65.76% | 33.8578
6575 | 0 | 0 | 0 | 3.1 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690.3755 | 54.13% | 0 | 24.4562 | 14.0354 | 22.46% | 24.4562
6576 | 0 | 0 | 0 | 2.9 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690.3755 | 54.13% | 0 | 0 | 14.0354 | 22.46% | 0
6577 | 0 | 0 | 0 | 1.5 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690.3755 | 54.13% | 0 | 0 | 14.0354 | 22.46% | 0
6578 | 0 | 0 | 0 | 2.1 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1742 | 32.3105 | 0 | 83.1742 | 607.2013 | 47.6% | 0 | 0 | 14.0354 | 22.46% | 32.3105
6579 | 0 | 0 | 0 | 2.7 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.064 | 35.2616 | 0 | 90.064 | 517.1373 | 40.54% | 0 | 0 | 14.0354 | 22.46% | 35.2616
6580 | 0 | 0 | 0 | 2.6 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.3504 | 39.7433 | 0 | 100.3504 | 416.7869 | 32.68% | 0 | 0 | 14.0354 | 22.46% | 39.7433
6581 | 0 | 0 | 0 | 1.9 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.9215 | 41.7697 | 0 | 104.9215 | 311.8654 | 24.45% | 0 | 0 | 14.0354 | 22.46% | 41.7697
6582 | 0 | 0 | 0 | 2.2 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.7228 | 48.2314 | 0 | 119.7228 | 192.1427 | 15.06% | 5.0983 | 0 | 18.642 | 29.83% | 43.1331
6583 | 217 | 64 | 41 | 2.6 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.6479 | 43.764 | 0 | 109.6479 | 82.4947 | 6.468% | 0 | 0 | 18.642 | 29.83% | 43.764
6584 | 305 | 191 | 98 | 1.5 | 19.6 | 0 | 0 | 0 | 0 | 12.6181 | 0 | 0 | 12.6181 | 0 | 0 | 0 | 82.4947 | 31.9704 | 0 | 82.4947 | 0 | 0% | 0 | 0 | 18.642 | 29.83% | 44.5885
6585 | 614 | 426 | 143 | 0.8 | 23.7 | 0 | 0 | 0 | 0 | 34.4194 | 0 | 0 | 34.4194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 11.1969 | 6.25 | 10% | 45.6163
6586 | 794 | 598 | 117 | 1.2 | 25.1 | 0 | 0 | 0 | 93.6913 | 45.8015 | 4.8707 | 0 | 45.8015 | 0 | 0 | 0 | 0 | 0 | 93.6913 | 0 | 93.6913 | 7.345% | 0 | 0 | 6.25 | 10% | 45.8015
6587 | 949 | 744 | 76 | 1.1 | 27.7 | 0 | 0 | 0 | 0 | 44.5634 | 17.9579 | 0 | 44.5634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6913 | 7.345% | 0 | 0 | 6.25 | 10% | 44.5634
6588 | 955 | 805 | 81 | 1.5 | 29.1 | 0 | 0 | 0 | 267.9393 | 43.8392 | 24.9668 | 0 | 43.8392 | 0 | 0 | 0 | 0 | 0 | 267.9393 | 0 | 361.6306 | 28.35% | 0 | 0 | 6.25 | 10% | 43.8392
6589 | 943 | 798 | 83 | 1.6 | 29.8 | 0 | 0 | 0 | 266.7161 | 54.4413 | 15.5176 | 10.9433 | 43.498 | 0 | 0 | 0 | 0 | 0 | 266.7161 | 0 | 628.3467 | 49.26% | 10.9433 | 0 | 16.1379 | 25.82% | 43.498
6590 | 888 | 717 | 93 | 3 | 29.9 | 0 | 0 | 0 | 247.1592 | 67.4414 | 0 | 24.1899 | 43.2515 | 0 | 0 | 0 | 0 | 0 | 247.1592 | 0 | 875.5059 | 68.64% | 24.1899 | 0 | 37.9949 | 60.79% | 43.2515
6591 | 854 | 596 | 86 | 4 | 29.4 | 0 | 0 | 0 | 228.4453 | 60.3406 | 0 | 17.8872 | 42.4535 | 0 | 0 | 0 | 0 | 0 | 228.4453 | 0 | 1103.9512 | 86.55% | 17.8872 | 0 | 54.1571 | 86.65% | 42.4535
6592 | 703 | 409 | 86 | 4.3 | 28.4 | 0 | 0 | 0 | 171.559 | 44.5386 | 0 | 2.3163 | 42.2223 | 0 | 0 | 0 | 0 | 0 | 171.559 | 0 | 1275.5102 | 100% | 2.3163 | 0 | 56.25 | 90% | 42.2223
6593 | 146 | 129 | 82 | 3.5 | 26.1 | 0 | 0 | 0 | 0 | 11.5831 | 0 | 0 | 11.5831 | 0 | 0 | 0 | 87.2431 | 33.561 | 0 | 87.2431 | 1188.2671 | 93.16% | 0 | 0 | 56.25 | 90% | 45.1442
6594 | 11 | 19 | 17 | 1.8 | 23.9 | 0 | 0 | 0 | 0 | 0.83109 | 0 | 0 | 0.83109 | 0 | 0 | 0 | 109.4042 | 43.2254 | 0 | 109.4042 | 1078.863 | 84.58% | 0 | 0 | 56.25 | 90% | 44.0565
6595 | 0 | 0 | 0 | 4.1 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.1058 | 39.8547 | 0 | 101.1058 | 977.7571 | 76.66% | 0 | 0 | 56.25 | 90% | 39.8547
6596 | 0 | 0 | 0 | 4.1 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.526 | 36.6362 | 0 | 93.526 | 884.2311 | 69.32% | 0 | 0 | 56.25 | 90% | 36.6362
6597 | 0 | 0 | 0 | 1.8 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4024 | 34.9232 | 0 | 89.4024 | 794.8287 | 62.31% | 0 | 0 | 56.25 | 90% | 34.9232
6598 | 0 | 0 | 0 | 1.3 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6342 | 33.3369 | 0 | 85.6342 | 709.1945 | 55.6% | 0 | 0 | 56.25 | 90% | 33.3369
6599 | 0 | 0 | 0 | 2 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1675 | 32.2924 | 0 | 83.1675 | 626.027 | 49.08% | 0 | 0 | 56.25 | 90% | 32.2924
6600 | 0 | 0 | 0 | 1.9 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626.027 | 49.08% | 0 | 1.6799 | 54.3908 | 87.03% | 1.6799
6601 | 0 | 0 | 0 | 2.2 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 626.027 | 49.08% | 0 | 25 | 26.7225 | 42.76% | 25
6602 | 0 | 0 | 0 | 1.7 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4597 | 32.0306 | 0 | 82.4597 | 543.5673 | 42.62% | 0 | 0 | 26.7225 | 42.76% | 32.0306
6603 | 0 | 0 | 0 | 1.7 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7452 | 34.7951 | 0 | 88.7452 | 454.8221 | 35.66% | 0 | 0 | 26.7225 | 42.76% | 34.7951
6604 | 0 | 0 | 0 | 1.3 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8235 | 39.2224 | 0 | 98.8235 | 355.9987 | 27.91% | 0 | 0 | 26.7225 | 42.76% | 39.2224
6605 | 0 | 0 | 0 | 0.7 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.9793 | 48.8829 | 0 | 120.9793 | 235.0194 | 18.43% | 7.7107 | 0 | 33.6896 | 53.9% | 41.1722
6606 | 0 | 0 | 0 | 1.1 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.7599 | 0 | 127.551 | 107.4683 | 8.426% | 9.3858 | 0 | 42.1702 | 67.47% | 42.3741
6607 | 153 | 39 | 18 | 1.2 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.4683 | 42.9994 | 0 | 107.4683 | 0 | 0% | 0 | 0 | 42.1702 | 67.47% | 42.9994
6608 | 662 | 237 | 54 | 0.8 | 19.5 | 0 | 0 | 0 | 0 | 15.7195 | 0 | 0 | 15.7195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 14.5019 | 23.2% | 40.7195
6609 | 818 | 438 | 68 | 1.3 | 23.2 | 0 | 0 | 0 | 0 | 37.0015 | 7.1054e-15 | 0 | 37.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 7.4561 | 6.25 | 10% | 44.4576
6610 | 884 | 608 | 80 | 3.6 | 25 | 0 | 0 | 0 | 221.6948 | 44.5578 | 9.0275 | 0 | 44.5578 | 0 | 0 | 0 | 0 | 0 | 221.6948 | 0 | 221.6948 | 17.38% | 0 | 0 | 6.25 | 10% | 44.5578
6611 | 914 | 735 | 94 | 3.4 | 26.3 | 0 | 0 | 0 | 246.7845 | 43.5259 | 21.4962 | 0 | 43.5259 | 0 | 0 | 0 | 0 | 0 | 246.7845 | 0 | 468.4793 | 36.73% | 0 | 0 | 6.25 | 10% | 43.5259
6612 | 826 | 772 | 147 | 3.4 | 27.2 | 0 | 0 | 0 | 228.286 | 42.8588 | 26.3498 | 0 | 42.8588 | 0 | 0 | 0 | 0 | 0 | 228.286 | 0 | 696.7653 | 54.63% | 0 | 0 | 6.25 | 10% | 42.8588
6613 | 909 | 790 | 105 | 5.1 | 27.3 | 0 | 0 | 0 | 254.0316 | 53.406 | 18.594 | 10.7436 | 42.6624 | 0 | 0 | 0 | 0 | 0 | 254.0316 | 0 | 950.7969 | 74.54% | 10.7436 | 0 | 15.9575 | 25.53% | 42.6624
6614 | 760 | 692 | 158 | 6.4 | 26.9 | 0 | 0 | 0 | 205.7993 | 67.349 | 0.4503 | 25 | 42.349 | 0 | 0 | 0 | 0 | 0 | 205.7993 | 0 | 1156.5962 | 90.68% | 25 | 0 | 38.5465 | 61.67% | 42.349
6615 | 616 | 570 | 200 | 5.7 | 26.7 | 0 | 0 | 0 | 118.914 | 56.535 | 0 | 14.6692 | 41.8658 | 0 | 0 | 0 | 0 | 0 | 118.914 | 0 | 1275.5102 | 100% | 14.6692 | 0 | 51.801 | 82.88% | 41.8658
6616 | 666 | 430 | 131 | 5.1 | 26.4 | 0 | 0 | 0 | 0 | 46.7896 | 0 | 4.9238 | 41.8658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 4.9238 | 0 | 56.25 | 90% | 41.8658
6617 | 358 | 189 | 87 | 4.6 | 25.5 | 0 | 0 | 0 | 0 | 20.8494 | 0 | 0 | 20.8494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 11.8304 | 43.1569 | 69.05% | 32.6798
6618 | 52 | 26 | 21 | 4.4 | 23.3 | 0 | 0 | 0 | 0 | 2.0073 | 0 | 0 | 2.0073 | 0 | 0 | 0 | 105.625 | 41.662 | 0 | 105.625 | 1169.8852 | 91.72% | 0 | 0 | 43.1569 | 69.05% | 43.6693
6619 | 0 | 0 | 0 | 2.3 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1218 | 39.4467 | 0 | 100.1218 | 1069.7634 | 83.87% | 0 | 0 | 43.1569 | 69.05% | 39.4467
6620 | 0 | 0 | 0 | 0.9 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.9559 | 23.9458 | 0 | 63.9559 | 1005.8075 | 78.86% | 0 | 0 | 43.1569 | 69.05% | 23.9458
6621 | 0 | 0 | 0 | 1 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7364 | 34.7101 | 0 | 88.7364 | 917.0711 | 71.9% | 0 | 0 | 43.1569 | 69.05% | 34.7101
6622 | 0 | 0 | 0 | 1.6 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8945 | 33.0695 | 0 | 84.8945 | 832.1765 | 65.24% | 0 | 0 | 43.1569 | 69.05% | 33.0695
6623 | 0 | 0 | 0 | 1.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2063 | 31.9484 | 0 | 82.2063 | 749.9702 | 58.8% | 0 | 0 | 43.1569 | 69.05% | 31.9484
6624 | 0 | 0 | 0 | 2.6 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.187 | 31.4609 | 0 | 81.187 | 668.7832 | 52.43% | 0 | 0 | 43.1569 | 69.05% | 31.4609
6625 | 0 | 0 | 0 | 1.1 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.965 | 31.4526 | 0 | 80.965 | 587.8182 | 46.08% | 0 | 0 | 43.1569 | 69.05% | 31.4526
6626 | 0 | 0 | 0 | 1.6 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8617 | 31.8036 | 0 | 81.8617 | 505.9564 | 39.67% | 0 | 0 | 43.1569 | 69.05% | 31.8036
6627 | 0 | 0 | 0 | 1 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5229 | 34.7394 | 0 | 88.5229 | 417.4335 | 32.73% | 0 | 0 | 43.1569 | 69.05% | 34.7394
6628 | 0 | 0 | 0 | 0.8 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0772 | 39.3645 | 0 | 99.0772 | 318.3563 | 24.96% | 0 | 0 | 43.1569 | 69.05% | 39.3645
6629 | 0 | 0 | 0 | 1 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0628 | 41.0956 | 0 | 103.0628 | 215.2934 | 16.88% | 0 | 0 | 43.1569 | 69.05% | 41.0956
6630 | 0 | 0 | 0 | 1.1 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3571 | 42.512 | 0 | 106.3571 | 108.9364 | 8.541% | 0 | 0 | 43.1569 | 69.05% | 42.512
6631 | 256 | 55 | 26 | 0.5 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.9364 | 43.5899 | 0 | 108.9364 | 0 | 0% | 0 | 0 | 43.1569 | 69.05% | 43.5899
6632 | 654 | 230 | 50 | 0.3 | 20.6 | 0 | 0 | 0 | 99.2167 | 15.2381 | 0 | 0 | 15.2381 | 0 | 0 | 0 | 0 | 0 | 99.2167 | 0 | 99.2167 | 7.779% | 0 | 25 | 15.4886 | 24.78% | 40.2381
6633 | 835 | 436 | 61 | 0.7 | 24 | 0 | 0 | 0 | 0 | 36.6851 | 0 | 0 | 36.6851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2167 | 7.779% | 0 | 8.3476 | 6.25 | 10% | 45.0327
6634 | 907 | 607 | 68 | 0.5 | 27.2 | 0 | 0 | 0 | 229.3025 | 45.2834 | 5.3865 | 0 | 45.2834 | 0 | 0 | 0 | 0 | 0 | 229.3025 | 0 | 328.5192 | 25.76% | 0 | 0 | 6.25 | 10% | 45.2834
6635 | 946 | 731 | 72 | 2.1 | 28.1 | 0 | 0 | 0 | 256.5507 | 44.0133 | 19.5892 | 0 | 44.0133 | 0 | 0 | 0 | 0 | 0 | 256.5507 | 0 | 585.07 | 45.87% | 0 | 0 | 6.25 | 10% | 44.0133
6636 | 955 | 790 | 75 | 3.3 | 28.7 | 0 | 0 | 0 | 266.9829 | 48.2651 | 22.7606 | 5.3367 | 42.9284 | 0 | 0 | 0 | 0 | 0 | 266.9829 | 0 | 852.0529 | 66.8% | 5.3367 | 0 | 11.072 | 17.72% | 42.9284
6637 | 947 | 784 | 76 | 5.3 | 29 | 0 | 0 | 0 | 265.1797 | 67.5384 | 4.4616 | 25 | 42.5384 | 0 | 0 | 0 | 0 | 0 | 265.1797 | 0 | 1117.2326 | 87.59% | 25 | 0 | 33.661 | 53.86% | 42.5384
6638 | 925 | 717 | 75 | 6 | 28.9 | 0 | 0 | 0 | 97.6788 | 67.2209 | 3.4094 | 25 | 42.2209 | 0 | 0 | 0 | 0 | 0 | 97.6788 | 0 | 1214.9115 | 95.25% | 25 | 0 | 56.25 | 90% | 42.2209
6639 | 877 | 590 | 73 | 5.9 | 28.7 | 0 | 0 | 0 | 0 | 41.4661 | 20.1314 | 0 | 41.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214.9115 | 95.25% | 0 | 0 | 56.25 | 90% | 41.4661
6640 | 800 | 418 | 64 | 6.1 | 28.3 | 0 | 0 | 0 | 0 | 41.3602 | 6.2993 | 0 | 41.3602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214.9115 | 95.25% | 0 | 0 | 56.25 | 90% | 41.3602
6641 | 629 | 216 | 48 | 5.3 | 27.6 | 0 | 0 | 0 | 0 | 27.9965 | 0 | 0 | 27.9965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214.9115 | 95.25% | 0 | 15.7257 | 38.8458 | 62.15% | 43.7222
6642 | 152 | 35 | 16 | 3.9 | 25.4 | 0 | 0 | 0 | 0 | 3.5488 | 0 | 0 | 3.5488 | 0 | 0 | 0 | 95.8623 | 37.2968 | 0 | 95.8623 | 1119.0492 | 87.73% | 0 | 1.6901 | 36.9754 | 59.16% | 42.5356
6643 | 0 | 0 | 0 | 3.2 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.886 | 38.7977 | 0 | 98.886 | 1020.1631 | 79.98% | 0 | 0 | 36.9754 | 59.16% | 38.7977
6644 | 0 | 0 | 0 | 1.9 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.283 | 36.1209 | 0 | 92.283 | 927.8801 | 72.75% | 0 | 0 | 36.9754 | 59.16% | 36.1209
6645 | 0 | 0 | 0 | 0.5 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9978 | 34.7839 | 0 | 88.9978 | 838.8823 | 65.77% | 0 | 0 | 36.9754 | 59.16% | 34.7839
6646 | 0 | 0 | 0 | 0.3 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3974 | 32.8495 | 0 | 84.3974 | 754.4849 | 59.15% | 0 | 0 | 36.9754 | 59.16% | 32.8495
6647 | 0 | 0 | 0 | 1.1 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0327 | 31.4401 | 0 | 81.0327 | 673.4522 | 52.8% | 0 | 0 | 36.9754 | 59.16% | 31.4401
6648 | 0 | 0 | 0 | 0.8 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1039 | 30.6295 | 0 | 79.1039 | 594.3483 | 46.6% | 0 | 0 | 36.9754 | 59.16% | 30.6295
6649 | 0 | 0 | 0 | 0.3 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2632 | 30.273 | 0 | 78.2632 | 516.0852 | 40.46% | 0 | 0 | 36.9754 | 59.16% | 30.273
6650 | 0 | 0 | 0 | 0.8 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.829 | 30.0808 | 0 | 77.829 | 438.2562 | 34.36% | 0 | 0 | 36.9754 | 59.16% | 30.0808
6651 | 0 | 0 | 0 | 1.7 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4249 | 30.7479 | 0 | 79.4249 | 358.8313 | 28.13% | 0 | 0 | 36.9754 | 59.16% | 30.7479
6652 | 0 | 0 | 0 | 1.6 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.101 | 32.3537 | 0 | 83.101 | 275.7303 | 21.62% | 0 | 0 | 36.9754 | 59.16% | 32.3537
6653 | 0 | 0 | 0 | 1.7 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0775 | 33.6252 | 0 | 86.0775 | 189.6528 | 14.87% | 0 | 0 | 36.9754 | 59.16% | 33.6252
6654 | 0 | 0 | 0 | 1.4 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.4736 | 36.4301 | 0 | 92.4736 | 97.1791 | 7.619% | 0 | 0 | 36.9754 | 59.16% | 36.4301
6655 | 226 | 45 | 20 | 1.7 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1791 | 38.4801 | 0 | 97.1791 | 0 | 0% | 0 | 0 | 36.9754 | 59.16% | 38.4801
6656 | 646 | 227 | 51 | 0.8 | 21.7 | 0 | 0 | 0 | 0 | 15.2485 | 0 | 0 | 15.2485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 24.0436 | 10.3656 | 16.58% | 39.2921
6657 | 804 | 426 | 66 | 0.9 | 25 | 0 | 0 | 0 | 0 | 36.0427 | 0 | 0 | 36.0427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 3.7187 | 6.25 | 10% | 39.7614
6658 | 881 | 597 | 73 | 0.8 | 27.6 | 0 | 0 | 0 | 0 | 40.1124 | 10.1927 | 0 | 40.1124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 40.1124
6659 | 916 | 717 | 79 | 1.6 | 28.8 | 0 | 0 | 0 | 32.6601 | 39.04 | 22.6508 | 0 | 39.04 | 0 | 0 | 0 | 0 | 0 | 32.6601 | 0 | 32.6601 | 2.561% | 0 | 0 | 6.25 | 10% | 39.04
6660 | 930 | 779 | 82 | 2.4 | 29.5 | 0 | 0 | 0 | 259.9426 | 37.3381 | 31.4857 | 0 | 37.3381 | 0 | 0 | 0 | 0 | 0 | 259.9426 | 0 | 292.6027 | 22.94% | 0 | 0 | 6.25 | 10% | 37.3381
6661 | 927 | 780 | 86 | 3.6 | 29.7 | 0 | 0 | 0 | 260.6027 | 48.4003 | 23.4957 | 12.0691 | 36.3312 | 0 | 0 | 0 | 0 | 0 | 260.6027 | 0 | 553.2053 | 43.37% | 12.0691 | 0 | 17.1552 | 27.45% | 36.3312
6662 | 855 | 698 | 104 | 2.3 | 30.3 | 0 | 0 | 0 | 237.2589 | 60.7811 | 4.5378 | 25 | 35.7811 | 0 | 0 | 0 | 0 | 0 | 237.2589 | 0 | 790.4643 | 61.97% | 25 | 0 | 39.7442 | 63.59% | 35.7811
6663 | 684 | 536 | 129 | 2.9 | 30 | 0 | 0 | 0 | 179.4977 | 53.6489 | 0 | 18.2675 | 35.3814 | 0 | 0 | 0 | 0 | 0 | 179.4977 | 0 | 969.9619 | 76.05% | 18.2675 | 0 | 56.25 | 90% | 35.3814
6664 | 432 | 320 | 128 | 2.5 | 29.2 | 0 | 0 | 0 | 98.3771 | 33.0946 | 0 | 0 | 33.0946 | 0 | 0 | 0 | 0 | 0 | 98.3771 | 0 | 1068.3391 | 83.76% | 0 | 2.8495 | 53.0964 | 84.95% | 35.944
6665 | 271 | 169 | 88 | 2.9 | 27.7 | 0 | 0 | 0 | 44.3524 | 17.3786 | 0 | 0 | 17.3786 | 0 | 0 | 0 | 0 | 0 | 44.3524 | 0 | 1112.6915 | 87.24% | 0 | 21.408 | 29.4035 | 47.05% | 38.7865
6666 | 3 | 21 | 21 | 2.4 | 24.8 | 0 | 0 | 0 | 0 | 0.91671 | 0 | 0 | 0.91671 | 0 | 0 | 0 | 94.1757 | 36.6296 | 0 | 94.1757 | 1018.5158 | 79.85% | 0 | 1.0396 | 28.2529 | 45.2% | 38.586
6667 | 0 | 0 | 0 | 1.6 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9472 | 35.9496 | 0 | 91.9472 | 926.5687 | 72.64% | 0 | 0 | 28.2529 | 45.2% | 35.9496
6668 | 0 | 0 | 0 | 0.2 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.7996 | 33.3689 | 0 | 85.7996 | 840.7691 | 65.92% | 0 | 0 | 28.2529 | 45.2% | 33.3689
6669 | 0 | 0 | 0 | 1.5 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9449 | 31.6838 | 0 | 81.9449 | 758.8242 | 59.49% | 0 | 0 | 28.2529 | 45.2% | 31.6838
6670 | 0 | 0 | 0 | 1.7 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0286 | 30.032 | 0 | 78.0286 | 680.7956 | 53.37% | 0 | 0 | 28.2529 | 45.2% | 30.032
6671 | 0 | 0 | 0 | 1.6 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6341 | 28.5572 | 0 | 74.6341 | 606.1615 | 47.52% | 0 | 0 | 28.2529 | 45.2% | 28.5572
6672 | 0 | 0 | 0 | 1.2 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.1022 | 27.9555 | 0 | 73.1022 | 533.0593 | 41.79% | 0 | 0 | 28.2529 | 45.2% | 27.9555
6673 | 0 | 0 | 0 | 0.5 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.957 | 27.5349 | 0 | 71.957 | 461.1024 | 36.15% | 0 | 0 | 28.2529 | 45.2% | 27.5349
6674 | 0 | 0 | 0 | 0.6 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.9551 | 27.5377 | 0 | 71.9551 | 389.1472 | 30.51% | 0 | 0 | 28.2529 | 45.2% | 27.5377
6675 | 0 | 0 | 0 | 0.9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5511 | 27.8204 | 0 | 72.5511 | 316.5961 | 24.82% | 0 | 0 | 28.2529 | 45.2% | 27.8204
6676 | 0 | 0 | 0 | 2.3 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.265 | 28.5126 | 0 | 74.265 | 242.3311 | 19% | 0 | 0 | 28.2529 | 45.2% | 28.5126
6677 | 0 | 0 | 0 | 1 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3138 | 28.9903 | 0 | 75.3138 | 167.0173 | 13.09% | 0 | 0 | 28.2529 | 45.2% | 28.9903
6678 | 0 | 0 | 0 | 0.9 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7813 | 31.4178 | 0 | 80.7813 | 86.236 | 6.761% | 0 | 0 | 28.2529 | 45.2% | 31.4178
6679 | 169 | 46 | 25 | 1.2 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.236 | 33.7213 | 0 | 86.236 | 0 | 0% | 0 | 0 | 28.2529 | 45.2% | 33.7213
6680 | 628 | 222 | 52 | 0.7 | 19.6 | 0 | 0 | 0 | 0 | 15.169 | 0 | 0 | 15.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 19.8809 | 6.25 | 10% | 35.0499
6681 | 799 | 422 | 66 | 0.6 | 24.5 | 0 | 0 | 0 | 0 | 35.6808 | 0.11856 | 0 | 35.6808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 35.6808
6682 | 882 | 594 | 73 | 0.7 | 27.6 | 0 | 0 | 0 | 0 | 36.5122 | 13.7477 | 0 | 36.5122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 36.5122
6683 | 910 | 713 | 82 | 1.2 | 29.1 | 0 | 0 | 0 | 178.7532 | 36.1585 | 24.7549 | 0 | 36.1585 | 0 | 0 | 0 | 0 | 0 | 178.7532 | 0 | 178.7532 | 14.01% | 0 | 0 | 6.25 | 10% | 36.1585
6684 | 909 | 769 | 91 | 2 | 29.4 | 0 | 0 | 0 | 253.8559 | 34.5332 | 33.1629 | 0 | 34.5332 | 0 | 0 | 0 | 0 | 0 | 253.8559 | 0 | 432.6091 | 33.92% | 0 | 0 | 6.25 | 10% | 34.5332
6685 | 890 | 758 | 96 | 2.3 | 29.8 | 0 | 0 | 0 | 250.1922 | 33.5528 | 35.2815 | 0 | 33.5528 | 0 | 0 | 0 | 0 | 0 | 250.1922 | 0 | 682.8013 | 53.53% | 0 | 0 | 6.25 | 10% | 33.5528
6686 | 871 | 692 | 93 | 2.3 | 29.9 | 0 | 0 | 0 | 241.998 | 58.1545 | 7.4452 | 25 | 33.1545 | 0 | 0 | 0 | 0 | 0 | 241.998 | 0 | 924.7993 | 72.5% | 25 | 0 | 28.839 | 46.14% | 33.1545
6687 | 831 | 569 | 84 | 3.8 | 29.4 | 0 | 0 | 0 | 220.9362 | 58.043 | 0.58528 | 25 | 33.043 | 0 | 0 | 0 | 0 | 0 | 220.9362 | 0 | 1145.7356 | 89.83% | 25 | 0 | 51.428 | 82.28% | 33.043
6688 | 692 | 396 | 92 | 4.4 | 28.3 | 0 | 0 | 0 | 0 | 39.6373 | 4.8711 | 5.3367 | 34.3007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1145.7356 | 89.83% | 5.3367 | 0 | 56.25 | 90% | 34.3007
6689 | 561 | 209 | 66 | 3.6 | 27.7 | 0 | 0 | 0 | 111.024 | 26.7782 | 0 | 0 | 26.7782 | 0 | 0 | 0 | 0 | 0 | 111.024 | 0 | 1256.7596 | 98.53% | 0 | 11.3413 | 43.6982 | 69.92% | 38.1194
6690 | 123 | 33 | 17 | 2.9 | 25.4 | 0 | 0 | 0 | 0 | 3.1829 | 0 | 0 | 3.1829 | 0 | 0 | 0 | 38.2653 | 12.7222 | 0 | 38.2653 | 1218.4943 | 95.53% | 0 | 22.3564 | 18.9557 | 30.33% | 38.2615
6691 | 0 | 0 | 0 | 1.7 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2734 | 35.1394 | 0 | 90.2734 | 1128.2209 | 88.45% | 0 | 1.0122 | 17.8355 | 28.54% | 36.1515
6692 | 0 | 0 | 0 | 0.3 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8443 | 33.7714 | 0 | 86.8443 | 1041.3765 | 81.64% | 0 | 0 | 17.8355 | 28.54% | 33.7714
6693 | 0 | 0 | 0 | 0.5 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3373 | 31.9024 | 0 | 82.3373 | 959.0392 | 75.19% | 0 | 0 | 17.8355 | 28.54% | 31.9024
6694 | 0 | 0 | 0 | 1.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.402 | 30.2033 | 0 | 78.402 | 880.6372 | 69.04% | 0 | 0 | 17.8355 | 28.54% | 30.2033
6695 | 0 | 0 | 0 | 2.3 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.1318 | 29.2034 | 0 | 76.1318 | 804.5054 | 63.07% | 0 | 0 | 17.8355 | 28.54% | 29.2034
6696 | 0 | 0 | 0 | 2.3 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.4304 | 28.9346 | 0 | 75.4304 | 729.0751 | 57.16% | 0 | 0 | 17.8355 | 28.54% | 28.9346
6697 | 0 | 0 | 0 | 1.4 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7943 | 29.0627 | 0 | 75.7943 | 653.2808 | 51.22% | 0 | 0 | 17.8355 | 28.54% | 29.0627
6698 | 0 | 0 | 0 | 1.3 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5922 | 29.8733 | 0 | 77.5922 | 575.6887 | 45.13% | 0 | 0 | 17.8355 | 28.54% | 29.8733
6699 | 0 | 0 | 0 | 2 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.718 | 33.3731 | 0 | 85.718 | 489.9706 | 38.41% | 0 | 0 | 17.8355 | 28.54% | 33.3731
6700 | 0 | 0 | 0 | 1.3 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5064 | 38.4954 | 0 | 97.5064 | 392.4642 | 30.77% | 0 | 0 | 17.8355 | 28.54% | 38.4954
6701 | 0 | 0 | 0 | 1.7 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.3367 | 40.6388 | 0 | 102.3367 | 290.1275 | 22.75% | 0 | 0 | 17.8355 | 28.54% | 40.6388
6702 | 0 | 0 | 0 | 2.5 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.4446 | 41.9201 | 0 | 105.4446 | 184.6829 | 14.48% | 0 | 0 | 17.8355 | 28.54% | 41.9201
6703 | 166 | 45 | 25 | 0.8 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.4001 | 42.8114 | 0 | 107.4001 | 77.2828 | 6.059% | 0 | 0 | 17.8355 | 28.54% | 42.8114
6704 | 546 | 205 | 58 | 1.7 | 22.4 | 0 | 0 | 0 | 0 | 14.1235 | 0 | 0 | 14.1235 | 0 | 0 | 0 | 77.2828 | 29.5667 | 0 | 77.2828 | 0 | 0% | 0 | 0 | 17.8355 | 28.54% | 43.6902
6705 | 700 | 397 | 93 | 0.5 | 26.6 | 0 | 0 | 0 | 147.1352 | 34.084 | 0 | 0 | 34.084 | 0 | 0 | 0 | 0 | 0 | 147.1352 | 0 | 147.1352 | 11.54% | 0 | 10.4682 | 6.25 | 10% | 44.5523
6706 | 847 | 582 | 88 | 0.9 | 28.3 | 0 | 0 | 0 | 211.9331 | 44.8935 | 5.381 | 0 | 44.8935 | 0 | 0 | 0 | 0 | 0 | 211.9331 | 0 | 359.0683 | 28.15% | 0 | 0 | 6.25 | 10% | 44.8935
6707 | 887 | 703 | 94 | 1 | 30.2 | 0 | 0 | 0 | 239.4171 | 43.8002 | 16.138 | 0 | 43.8002 | 0 | 0 | 0 | 0 | 0 | 239.4171 | 0 | 598.4854 | 46.92% | 0 | 0 | 6.25 | 10% | 43.8002
6708 | 872 | 751 | 107 | 1.5 | 31.4 | 0 | 0 | 0 | 242.9524 | 43.0287 | 22.2964 | 0 | 43.0287 | 0 | 0 | 0 | 0 | 0 | 242.9524 | 0 | 841.4378 | 65.97% | 0 | 0 | 6.25 | 10% | 43.0287
6709 | 900 | 753 | 91 | 3.4 | 31.3 | 0 | 0 | 0 | 252.5653 | 56.7963 | 13.1555 | 14.0141 | 42.7822 | 0 | 0 | 0 | 0 | 0 | 252.5653 | 0 | 1094.0031 | 85.77% | 14.0141 | 0 | 18.9126 | 30.26% | 42.7822
6710 | 902 | 689 | 77 | 5.7 | 30.5 | 0 | 0 | 0 | 181.5071 | 67.6499 | 1.0568 | 25 | 42.6499 | 0 | 0 | 0 | 0 | 0 | 181.5071 | 0 | 1275.5102 | 100% | 25 | 0 | 41.5016 | 66.4% | 42.6499
6711 | 785 | 549 | 94 | 5.8 | 30.3 | 0 | 0 | 0 | 0 | 57.8233 | 0 | 15.9255 | 41.8978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 15.9255 | 0 | 55.8912 | 89.43% | 41.8978
6712 | 600 | 389 | 132 | 4.4 | 29.6 | 0 | 0 | 0 | 0 | 42.7489 | 0 | 0.39706 | 42.3518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0.39706 | 0 | 56.25 | 90% | 42.3518
6713 | 181 | 154 | 111 | 3.7 | 28.2 | 0 | 0 | 0 | 0 | 15.1873 | 0 | 0 | 15.1873 | 0 | 0 | 0 | 38.2653 | 12.6293 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 17.1285 | 37.2933 | 59.67% | 44.945
6714 | 38 | 26 | 22 | 2.9 | 26.3 | 0 | 0 | 0 | 0 | 1.6507 | 0 | 0 | 1.6507 | 0 | 0 | 0 | 86.6749 | 33.3021 | 0 | 86.6749 | 1150.57 | 90.2% | 0 | 9.0605 | 27.2658 | 43.63% | 44.0133
6715 | 0 | 0 | 0 | 4 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150.57 | 90.2% | 0 | 0 | 27.2658 | 43.63% | 0
6716 | 0 | 0 | 0 | 4.2 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150.57 | 90.2% | 0 | 0 | 27.2658 | 43.63% | 0
6717 | 0 | 0 | 0 | 4.2 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.2342 | 34.4427 | 0 | 88.2342 | 1062.3358 | 83.29% | 0 | 0 | 27.2658 | 43.63% | 34.4427
6718 | 0 | 0 | 0 | 3.3 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.2375 | 32.7283 | 0 | 84.2375 | 978.0983 | 76.68% | 0 | 0 | 27.2658 | 43.63% | 32.7283
6719 | 0 | 0 | 0 | 2.5 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6461 | 31.6643 | 0 | 81.6461 | 896.4522 | 70.28% | 0 | 0 | 27.2658 | 43.63% | 31.6643
6720 | 0 | 0 | 0 | 1.9 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8005 | 31.3217 | 0 | 80.8005 | 815.6517 | 63.95% | 0 | 0 | 27.2658 | 43.63% | 31.3217
6721 | 0 | 0 | 0 | 1.8 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2637 | 31.071 | 0 | 80.2637 | 735.3879 | 57.65% | 0 | 0 | 27.2658 | 43.63% | 31.071
6722 | 0 | 0 | 0 | 2.2 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7291 | 31.7548 | 0 | 81.7291 | 653.6588 | 51.25% | 0 | 0 | 27.2658 | 43.63% | 31.7548
6723 | 0 | 0 | 0 | 3 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.9525 | 21.4339 | 0 | 57.9525 | 595.7063 | 46.7% | 0 | 0 | 27.2658 | 43.63% | 21.4339
6724 | 0 | 0 | 0 | 1.6 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7491 | 39.5302 | 0 | 99.7491 | 495.9572 | 38.88% | 0 | 0 | 27.2658 | 43.63% | 39.5302
6725 | 0 | 0 | 0 | 1.7 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9188 | 41.3588 | 0 | 103.9188 | 392.0384 | 30.74% | 0 | 0 | 27.2658 | 43.63% | 41.3588
6726 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.8391 | 42.6471 | 0 | 106.8391 | 285.1993 | 22.36% | 0 | 0 | 27.2658 | 43.63% | 42.6471
6727 | 0 | 18 | 18 | 0.8 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.6686 | 43.4284 | 0 | 108.6686 | 176.5307 | 13.84% | 0 | 0 | 27.2658 | 43.63% | 43.4284
6728 | 0 | 96 | 96 | 1.2 | 18.6 | 0 | 0 | 0 | 0 | 6.7333 | 0 | 0 | 6.7333 | 0 | 0 | 0 | 95.8392 | 37.7925 | 0 | 95.8392 | 80.6915 | 6.326% | 0 | 0 | 27.2658 | 43.63% | 44.5258
6729 | 4 | 202 | 199 | 2.7 | 20.5 | 0 | 0 | 0 | 0 | 14.3753 | 0 | 0 | 14.3753 | 0 | 0 | 0 | 80.6915 | 31.1435 | 0 | 80.6915 | 0 | 0% | 0 | 0 | 27.2658 | 43.63% | 45.5188
6730 | 124 | 352 | 273 | 3.4 | 21.9 | 0 | 0 | 0 | 0 | 27.1774 | 0 | 0 | 27.1774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 18.989 | 6.25 | 10% | 46.1664
6731 | 440 | 534 | 225 | 3.7 | 23 | 0 | 0 | 0 | 108.4679 | 47.221 | 0.48504 | 2.2189 | 45.0021 | 0 | 0 | 0 | 0 | 0 | 108.4679 | 0 | 108.4679 | 8.504% | 2.2189 | 0 | 8.2549 | 13.21% | 45.0021
6732 | 748 | 715 | 164 | 3.8 | 24.2 | 0 | 0 | 0 | 204.4673 | 67.1029 | 0 | 23.0394 | 44.0634 | 0 | 0 | 0 | 0 | 0 | 204.4673 | 0 | 312.9352 | 24.53% | 23.0394 | 0 | 29.0724 | 46.52% | 44.0634
6733 | 761 | 692 | 135 | 3.1 | 24.6 | 0 | 0 | 0 | 210.5998 | 43.9632 | 22.3219 | 0 | 43.9632 | 0 | 0 | 0 | 0 | 0 | 210.5998 | 0 | 523.535 | 41.05% | 0 | 0 | 29.0724 | 46.52% | 43.9632
6734 | 742 | 661 | 159 | 3.3 | 25.1 | 0 | 0 | 0 | 202.6397 | 65.4511 | 0 | 21.5116 | 43.9395 | 0 | 0 | 0 | 0 | 0 | 202.6397 | 0 | 726.1748 | 56.93% | 21.5116 | 0 | 48.5094 | 77.62% | 43.9395
6735 | 606 | 500 | 152 | 3.1 | 25.2 | 0 | 0 | 0 | 156.248 | 51.7709 | 0 | 8.5668 | 43.2041 | 0 | 0 | 0 | 0 | 0 | 156.248 | 0 | 882.4228 | 69.18% | 8.5668 | 0 | 56.25 | 90% | 43.2041
6736 | 574 | 346 | 108 | 2.6 | 25.1 | 0 | 0 | 0 | 135.5378 | 39.7418 | 0 | 0 | 39.7418 | 0 | 0 | 0 | 0 | 0 | 135.5378 | 0 | 1017.9605 | 79.81% | 0 | 3.6685 | 52.1899 | 83.5% | 43.4103
6737 | 508 | 182 | 56 | 1.7 | 24.6 | 0 | 0 | 0 | 98.5621 | 23.9045 | 0 | 0 | 23.9045 | 0 | 0 | 0 | 0 | 0 | 98.5621 | 0 | 1116.5227 | 87.54% | 0 | 22.1491 | 27.6767 | 44.28% | 46.0536
6738 | 72 | 24 | 15 | 2 | 22.1 | 0 | 0 | 0 | 0 | 2.0641 | 0 | 0 | 2.0641 | 0 | 0 | 0 | 107.2575 | 42.4673 | 0 | 107.2575 | 1009.2651 | 79.13% | 0 | 0 | 27.6767 | 44.28% | 44.5314
6739 | 0 | 0 | 0 | 1.6 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4024 | 40.0929 | 0 | 101.4024 | 907.8628 | 71.18% | 0 | 0 | 27.6767 | 44.28% | 40.0929
6740 | 0 | 0 | 0 | 1.7 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4274 | 36.7323 | 0 | 93.4274 | 814.4354 | 63.85% | 0 | 0 | 27.6767 | 44.28% | 36.7323
6741 | 0 | 0 | 0 | 0.7 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2337 | 34.9622 | 0 | 89.2337 | 725.2017 | 56.86% | 0 | 0 | 27.6767 | 44.28% | 34.9622
6742 | 0 | 0 | 0 | 1.5 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0168 | 33.1517 | 0 | 85.0168 | 640.1849 | 50.19% | 0 | 0 | 27.6767 | 44.28% | 33.1517
6743 | 0 | 0 | 0 | 1.1 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.8944 | 31.7952 | 0 | 81.8944 | 558.2906 | 43.77% | 0 | 0 | 27.6767 | 44.28% | 31.7952
6744 | 0 | 0 | 0 | 1.6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558.2906 | 43.77% | 0 | 7.2607 | 19.6411 | 31.43% | 7.2607
6745 | 0 | 0 | 0 | 1.1 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558.2906 | 43.77% | 0 | 0 | 19.6411 | 31.43% | 0
6746 | 0 | 0 | 0 | 0.6 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558.2906 | 43.77% | 0 | 0 | 19.6411 | 31.43% | 0
6747 | 0 | 0 | 0 | 0.2 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5744 | 34.3605 | 0 | 87.5744 | 470.7162 | 36.9% | 0 | 0 | 19.6411 | 31.43% | 34.3605
6748 | 0 | 0 | 0 | 0.5 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2047 | 38.5512 | 0 | 97.2047 | 373.5115 | 29.28% | 0 | 0 | 19.6411 | 31.43% | 38.5512
6749 | 0 | 0 | 0 | 1.1 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.7433 | 0 | 127.551 | 245.9605 | 19.28% | 11.2995 | 0 | 29.8509 | 47.76% | 40.4438
6750 | 0 | 0 | 0 | 1 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.7433 | 0 | 127.551 | 118.4095 | 9.283% | 10.1853 | 0 | 39.0539 | 62.49% | 41.558
6751 | 165 | 36 | 18 | 0.8 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.4095 | 47.7719 | 0 | 118.4095 | 0 | 0% | 5.3142 | 0 | 43.8556 | 70.17% | 42.4577
6752 | 572 | 204 | 56 | 0.7 | 18.3 | 0 | 0 | 0 | 0 | 14.6468 | 0 | 0 | 14.6468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 25 | 16.1873 | 25.9% | 39.6467
6753 | 756 | 398 | 71 | 0.7 | 20.9 | 0 | 0 | 0 | 0 | 35.3505 | 0 | 0 | 35.3505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 8.9789 | 6.25 | 10% | 44.3294
6754 | 841 | 564 | 79 | 0.8 | 22.6 | 0 | 0 | 0 | 136.9426 | 44.4506 | 5.9279 | 0 | 44.4506 | 0 | 0 | 0 | 0 | 0 | 136.9426 | 0 | 136.9426 | 10.74% | 0 | 0 | 6.25 | 10% | 44.4506
6755 | 884 | 682 | 83 | 1 | 24.1 | 0 | 0 | 0 | 0 | 43.3713 | 17.112 | 0 | 43.3713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136.9426 | 10.74% | 0 | 0 | 6.25 | 10% | 43.3713
6756 | 902 | 741 | 84 | 1 | 25.5 | 0 | 0 | 0 | 251.9329 | 42.4618 | 23.5452 | 0 | 42.4618 | 0 | 0 | 0 | 0 | 0 | 251.9329 | 0 | 388.8755 | 30.49% | 0 | 0 | 6.25 | 10% | 42.4618
6757 | 900 | 738 | 84 | 1.5 | 26.8 | 0 | 0 | 0 | 253.2971 | 67.1763 | 0.91902 | 25 | 42.1763 | 0 | 0 | 0 | 0 | 0 | 253.2971 | 0 | 642.1726 | 50.35% | 25 | 0 | 28.839 | 46.14% | 42.1763
6758 | 872 | 669 | 84 | 1.9 | 28.1 | 0 | 0 | 0 | 241.795 | 53.5718 | 11.3128 | 11.5654 | 42.0064 | 0 | 0 | 0 | 0 | 0 | 241.795 | 0 | 883.9676 | 69.3% | 11.5654 | 0 | 39.289 | 62.86% | 42.0064
6759 | 824 | 545 | 79 | 3.7 | 28 | 0 | 0 | 0 | 218.2574 | 57.9732 | 0 | 16.6186 | 41.3546 | 0 | 0 | 0 | 0 | 0 | 218.2574 | 0 | 1102.225 | 86.41% | 16.6186 | 0 | 54.3048 | 86.89% | 41.3546
6760 | 718 | 372 | 72 | 3.4 | 27.3 | 0 | 0 | 0 | 173.2852 | 43.8235 | 0 | 2.1528 | 41.6708 | 0 | 0 | 0 | 0 | 0 | 173.2852 | 0 | 1275.5102 | 100% | 2.1528 | 0 | 56.25 | 90% | 41.6708
6761 | 523 | 178 | 51 | 3.9 | 25.7 | 0 | 0 | 0 | 0 | 24.1539 | 0 | 0 | 24.1539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 20.2424 | 33.8471 | 54.16% | 44.3963
6762 | 81 | 23 | 13 | 2.9 | 23.7 | 0 | 0 | 0 | 0 | 1.9982 | 0 | 0 | 1.9982 | 0 | 0 | 0 | 104.6515 | 41.2088 | 0 | 104.6515 | 1170.8587 | 91.8% | 0 | 0 | 33.8471 | 54.16% | 43.2069
6763 | 0 | 0 | 0 | 1.1 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7777 | 39.3283 | 0 | 99.7777 | 1071.081 | 83.97% | 0 | 0 | 33.8471 | 54.16% | 39.3283
6764 | 0 | 0 | 0 | 0.5 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1133 | 36.1112 | 0 | 92.1133 | 978.9677 | 76.75% | 0 | 0 | 33.8471 | 54.16% | 36.1112
6765 | 0 | 0 | 0 | 1.4 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.172 | 34.4552 | 0 | 88.172 | 890.7956 | 69.84% | 0 | 0 | 33.8471 | 54.16% | 34.4552
6766 | 0 | 0 | 0 | 1.6 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.4348 | 32.8606 | 0 | 84.4348 | 806.3609 | 63.22% | 0 | 0 | 33.8471 | 54.16% | 32.8606
6767 | 0 | 0 | 0 | 2.1 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0812 | 31.862 | 0 | 82.0812 | 724.2797 | 56.78% | 0 | 0 | 33.8471 | 54.16% | 31.862
6768 | 0 | 0 | 0 | 1.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.888 | 31.3774 | 0 | 80.888 | 643.3917 | 50.44% | 0 | 0 | 33.8471 | 54.16% | 31.3774
6769 | 0 | 0 | 0 | 4 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.1303 | 19.7901 | 0 | 54.1303 | 589.2613 | 46.2% | 0 | 0 | 33.8471 | 54.16% | 19.7901
6770 | 0 | 0 | 0 | 3.7 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6902 | 31.759 | 0 | 81.6902 | 507.5711 | 39.79% | 0 | 0 | 33.8471 | 54.16% | 31.759
6771 | 0 | 0 | 0 | 3.4 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8494 | 34.8633 | 0 | 88.8494 | 418.7217 | 32.83% | 0 | 0 | 33.8471 | 54.16% | 34.8633
6772 | 0 | 0 | 0 | 2.6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.073 | 39.2809 | 0 | 99.073 | 319.6487 | 25.06% | 0 | 0 | 33.8471 | 54.16% | 39.2809
6773 | 0 | 0 | 0 | 2.4 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9665 | 41.3964 | 0 | 103.9665 | 215.6822 | 16.91% | 0 | 0 | 33.8471 | 54.16% | 41.3964
6774 | 0 | 0 | 0 | 2.4 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.8038 | 42.654 | 0 | 106.8038 | 108.8784 | 8.536% | 0 | 0 | 33.8471 | 54.16% | 42.654
6775 | 91 | 27 | 16 | 1.9 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8784 | 43.5593 | 0 | 108.8784 | 0 | 0% | 0 | 0 | 33.8471 | 54.16% | 43.5593
6776 | 558 | 200 | 56 | 2.3 | 19.1 | 0 | 0 | 0 | 0 | 14.5211 | 0 | 0 | 14.5211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 15.0443 | 17.1971 | 27.52% | 29.5653
6777 | 693 | 379 | 78 | 5.3 | 21.3 | 0 | 0 | 0 | 0 | 34.9325 | 0 | 0 | 34.9325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 9.8913 | 6.25 | 10% | 44.8238
6778 | 839 | 562 | 81 | 5.9 | 22.6 | 0 | 0 | 0 | 205.332 | 45.1038 | 8.2597 | 0 | 45.1038 | 0 | 0 | 0 | 0 | 0 | 205.332 | 0 | 205.332 | 16.1% | 0 | 0 | 6.25 | 10% | 45.1038
6779 | 882 | 677 | 83 | 6.3 | 23.6 | 0 | 0 | 0 | 233.6135 | 44.0105 | 20.5826 | 0 | 44.0105 | 0 | 0 | 0 | 0 | 0 | 233.6135 | 0 | 438.9455 | 34.41% | 0 | 0 | 6.25 | 10% | 44.0105
6780 | 904 | 738 | 83 | 5.9 | 24.5 | 0 | 0 | 0 | 248.846 | 43.2487 | 27.9816 | 0 | 43.2487 | 0 | 0 | 0 | 0 | 0 | 248.846 | 0 | 687.7915 | 53.92% | 0 | 0 | 6.25 | 10% | 43.2487
6781 | 907 | 735 | 81 | 6.3 | 24.9 | 0 | 0 | 0 | 251.7546 | 52.7552 | 19.2448 | 9.6848 | 43.0704 | 0 | 0 | 0 | 0 | 0 | 251.7546 | 0 | 939.5461 | 73.66% | 9.6848 | 0 | 15.0008 | 24% | 43.0704
6782 | 885 | 667 | 78 | 5.8 | 25.3 | 0 | 0 | 0 | 117.5374 | 67.934 | 0.96307 | 25 | 42.934 | 0 | 0 | 0 | 0 | 0 | 117.5374 | 0 | 1057.0835 | 82.88% | 25 | 0 | 37.5898 | 60.14% | 42.934
6783 | 833 | 540 | 75 | 6.1 | 25.2 | 0 | 0 | 0 | 218.4267 | 59.6839 | 0 | 17.5605 | 42.1234 | 0 | 0 | 0 | 0 | 0 | 218.4267 | 0 | 1275.5102 | 100% | 17.5605 | 0 | 53.4567 | 85.53% | 42.1234
6784 | 747 | 372 | 65 | 6.1 | 24.5 | 0 | 0 | 0 | 0 | 45.7301 | 0 | 3.0914 | 42.6387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 3.0914 | 0 | 56.25 | 90% | 42.6387
6785 | 556 | 178 | 46 | 5.9 | 23.2 | 0 | 0 | 0 | 0 | 25.2107 | 0 | 0 | 25.2107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 19.9919 | 34.1243 | 54.6% | 45.2027
6786 | 89 | 22 | 12 | 6.1 | 21 | 0 | 0 | 0 | 0 | 2.0472 | 0 | 0 | 2.0472 | 0 | 0 | 0 | 105.5426 | 41.8185 | 0 | 105.5426 | 1169.9676 | 91.73% | 0 | 0 | 34.1243 | 54.6% | 43.8657
6787 | 0 | 0 | 0 | 4.4 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.605 | 39.7962 | 0 | 100.605 | 1069.3626 | 83.84% | 0 | 0 | 34.1243 | 54.6% | 39.7962
6788 | 0 | 0 | 0 | 4 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4306 | 36.7337 | 0 | 93.4306 | 975.932 | 76.51% | 0 | 0 | 34.1243 | 54.6% | 36.7337
6789 | 0 | 0 | 0 | 3.9 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4798 | 35.0583 | 0 | 89.4798 | 886.4522 | 69.5% | 0 | 0 | 34.1243 | 54.6% | 35.0583
6790 | 0 | 0 | 0 | 3.3 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8017 | 33.4915 | 0 | 85.8017 | 800.6506 | 62.77% | 0 | 0 | 34.1243 | 54.6% | 33.4915
6791 | 0 | 0 | 0 | 2.7 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4203 | 32.4651 | 0 | 83.4203 | 717.2303 | 56.23% | 0 | 0 | 34.1243 | 54.6% | 32.4651
6792 | 0 | 0 | 0 | 1.8 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5163 | 31.6406 | 0 | 81.5163 | 635.714 | 49.84% | 0 | 0 | 34.1243 | 54.6% | 31.6406
6793 | 0 | 0 | 0 | 1.8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4852 | 31.2242 | 0 | 80.4852 | 555.2288 | 43.53% | 0 | 0 | 34.1243 | 54.6% | 31.2242
6794 | 0 | 0 | 0 | 1.8 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.193 | 19.4145 | 0 | 53.193 | 502.0358 | 39.36% | 0 | 0 | 34.1243 | 54.6% | 19.4145
6795 | 0 | 0 | 0 | 2 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6532 | 34.3828 | 0 | 87.6532 | 414.3826 | 32.49% | 0 | 0 | 34.1243 | 54.6% | 34.3828
6796 | 0 | 0 | 0 | 1.5 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3864 | 39.0511 | 0 | 98.3864 | 315.9962 | 24.77% | 0 | 0 | 34.1243 | 54.6% | 39.0511
6797 | 0 | 0 | 0 | 1.1 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0309 | 41.104 | 0 | 103.0309 | 212.9654 | 16.7% | 0 | 0 | 34.1243 | 54.6% | 41.104
6798 | 0 | 0 | 0 | 2 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.4248 | 42.1443 | 0 | 105.4248 | 107.5406 | 8.431% | 0 | 0 | 34.1243 | 54.6% | 42.1443
6799 | 116 | 25 | 15 | 2.3 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.5406 | 43.0259 | 0 | 107.5406 | 0 | 0% | 0 | 0 | 34.1243 | 54.6% | 43.0259
6800 | 500 | 183 | 64 | 1.8 | 17.9 | 0 | 0 | 0 | 67.8423 | 13.9443 | 0 | 0 | 13.9443 | 0 | 0 | 0 | 0 | 0 | 67.8423 | 0 | 67.8423 | 5.319% | 0 | 20.9106 | 10.9818 | 17.57% | 34.8549
6801 | 782 | 439 | 106 | 3.2 | 20.8 | 0 | 0 | 0 | 162.808 | 40.2225 | 0 | 0 | 40.2225 | 0 | 0 | 0 | 0 | 0 | 162.808 | 0 | 230.6502 | 18.08% | 0 | 4.2755 | 6.25 | 10% | 44.498
6802 | 851 | 561 | 77 | 4.6 | 23.2 | 0 | 0 | 0 | 209.3989 | 53.2304 | 0 | 8.6782 | 44.5523 | 0 | 0 | 0 | 0 | 0 | 209.3989 | 0 | 440.0491 | 34.5% | 8.6782 | 0 | 14.0912 | 22.55% | 44.5523
6803 | 863 | 688 | 110 | 5.3 | 24.2 | 0 | 0 | 0 | 228.8254 | 48.2034 | 17.438 | 4.8238 | 43.3796 | 0 | 0 | 0 | 0 | 0 | 228.8254 | 0 | 668.8745 | 52.44% | 4.8238 | 0 | 18.4498 | 29.52% | 43.3796
6804 | 598 | 725 | 287 | 5.9 | 25.1 | 0 | 0 | 0 | 157.4444 | 66.5551 | 0 | 24.3272 | 42.2279 | 0 | 0 | 0 | 0 | 0 | 157.4444 | 0 | 826.3189 | 64.78% | 24.3272 | 0 | 40.4309 | 64.69% | 42.2279
6805 | 359 | 673 | 408 | 6 | 25.5 | 0 | 0 | 0 | 87.3503 | 59.312 | 0 | 17.5075 | 41.8045 | 0 | 0 | 0 | 0 | 0 | 87.3503 | 0 | 913.6693 | 71.63% | 17.5075 | 0 | 56.25 | 90% | 41.8045
6806 | 279 | 481 | 296 | 5.2 | 25.3 | 0 | 0 | 0 | 62.9094 | 41.5858 | 2.3149 | 0 | 41.5858 | 0 | 0 | 0 | 0 | 0 | 62.9094 | 0 | 976.5786 | 76.56% | 0 | 0 | 56.25 | 90% | 41.5858
6807 | 493 | 498 | 221 | 4.7 | 25.6 | 0 | 0 | 0 | 121.9679 | 40.9535 | 9.1719 | 0 | 40.9535 | 0 | 0 | 0 | 0 | 0 | 121.9679 | 0 | 1098.5466 | 86.13% | 0 | 0 | 56.25 | 90% | 40.9535
6808 | 429 | 313 | 129 | 5 | 24.9 | 0 | 0 | 0 | 94.1335 | 33.9486 | 0 | 0 | 33.9486 | 0 | 0 | 0 | 0 | 0 | 94.1335 | 0 | 1192.68 | 93.51% | 0 | 7.7849 | 47.6342 | 76.21% | 41.7335
6809 | 2 | 70 | 70 | 4.9 | 22.8 | 0 | 0 | 0 | 0 | 4.1771 | 0 | 0 | 4.1771 | 0 | 0 | 0 | 73.254 | 27.8133 | 0 | 73.254 | 1119.426 | 87.76% | 0 | 11.8557 | 34.5131 | 55.22% | 43.8462
6810 | 1 | 10 | 10 | 4.9 | 21 | 0 | 0 | 0 | 0 | 0.22905 | 0 | 0 | 0.22905 | 0 | 0 | 0 | 106.3655 | 42.1729 | 0 | 106.3655 | 1013.0606 | 79.42% | 0 | 0 | 34.5131 | 55.22% | 42.402
6811 | 0 | 0 | 0 | 4.2 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.3946 | 38.8353 | 0 | 98.3946 | 914.666 | 71.71% | 0 | 0 | 34.5131 | 55.22% | 38.8353
6812 | 0 | 0 | 0 | 3.3 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8525 | 36.0401 | 0 | 91.8525 | 822.8135 | 64.51% | 0 | 0 | 34.5131 | 55.22% | 36.0401
6813 | 0 | 0 | 0 | 3.4 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0733 | 34.4288 | 0 | 88.0733 | 734.7402 | 57.6% | 0 | 0 | 34.5131 | 55.22% | 34.4288
6814 | 0 | 0 | 0 | 2.7 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.552 | 32.4888 | 0 | 83.552 | 651.1882 | 51.05% | 0 | 0 | 34.5131 | 55.22% | 32.4888
6815 | 0 | 0 | 0 | 2.8 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.135 | 31.0153 | 0 | 80.135 | 571.0532 | 44.77% | 0 | 0 | 34.5131 | 55.22% | 31.0153
6816 | 0 | 0 | 0 | 2.4 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9325 | 30.0669 | 0 | 77.9325 | 493.1207 | 38.66% | 0 | 0 | 34.5131 | 55.22% | 30.0669
6817 | 0 | 0 | 0 | 1.7 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1555 | 29.7438 | 0 | 77.1555 | 415.9652 | 32.61% | 0 | 0 | 34.5131 | 55.22% | 29.7438
6818 | 0 | 0 | 0 | 1.3 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.9652 | 32.61% | 0 | 16.7365 | 15.9903 | 25.58% | 16.7365
6819 | 0 | 0 | 0 | 2.5 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.9652 | 32.61% | 0 | 0 | 15.9903 | 25.58% | 0
6820 | 0 | 0 | 0 | 1.8 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9652 | 30.5613 | 0 | 78.9652 | 337 | 26.42% | 0 | 0 | 15.9903 | 25.58% | 30.5613
6821 | 0 | 0 | 0 | 1.2 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.2697 | 31.5807 | 0 | 81.2697 | 255.7302 | 20.05% | 0 | 0 | 15.9903 | 25.58% | 31.5807
6822 | 0 | 0 | 0 | 1.5 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3508 | 34.2046 | 0 | 87.3508 | 168.3794 | 13.2% | 0 | 0 | 15.9903 | 25.58% | 34.2046
6823 | 27 | 23 | 20 | 1.8 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1512 | 36.256 | 0 | 92.1512 | 76.2282 | 5.976% | 0 | 0 | 15.9903 | 25.58% | 36.256
6824 | 23 | 105 | 99 | 2.5 | 18.7 | 0 | 0 | 0 | 0 | 7.7956 | 0 | 0 | 7.7956 | 0 | 0 | 0 | 76.2282 | 29.3072 | 0 | 76.2282 | 0 | 0% | 0 | 0 | 15.9903 | 25.58% | 37.1028
6825 | 270 | 340 | 221 | 3.2 | 20.4 | 0 | 0 | 0 | 43.5726 | 28.7154 | 0 | 0 | 28.7154 | 0 | 0 | 0 | 0 | 0 | 43.5726 | 0 | 43.5726 | 3.416% | 0 | 8.801 | 6.25 | 10% | 37.5164
6826 | 42 | 315 | 287 | 4.2 | 21.2 | 0 | 0 | 0 | 0 | 24.4093 | 0 | 0 | 24.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.5726 | 3.416% | 0 | 0 | 6.25 | 10% | 24.4093
6827 | 20 | 396 | 376 | 4.6 | 22 | 0 | 0 | 0 | 0 | 28.4499 | 0 | 0 | 28.4499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.5726 | 3.416% | 0 | 0 | 6.25 | 10% | 28.4499
6828 | 114 | 498 | 407 | 3.7 | 23.6 | 0 | 0 | 0 | 0 | 35.5039 | 3.5249 | 0 | 35.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.5726 | 3.416% | 0 | 0 | 6.25 | 10% | 35.5039
6829 | 485 | 651 | 299 | 2.9 | 25.1 | 0 | 0 | 0 | 127.5493 | 34.2644 | 25.178 | 0 | 34.2644 | 0 | 0 | 0 | 0 | 0 | 127.5493 | 0 | 171.1219 | 13.42% | 0 | 0 | 6.25 | 10% | 34.2644
6830 | 763 | 642 | 141 | 2 | 26.5 | 0 | 0 | 0 | 208.5009 | 58.1962 | 5.585 | 24.2562 | 33.9399 | 0 | 0 | 0 | 0 | 0 | 208.5009 | 0 | 379.6229 | 29.76% | 24.2562 | 0 | 28.167 | 45.07% | 33.9399
6831 | 742 | 542 | 135 | 2 | 27.3 | 0 | 0 | 0 | 195.1969 | 57.0707 | 0 | 23.3689 | 33.7018 | 0 | 0 | 0 | 0 | 0 | 195.1969 | 0 | 574.8198 | 45.07% | 23.3689 | 0 | 49.2821 | 78.85% | 33.7018
6832 | 662 | 355 | 89 | 3.6 | 27 | 0 | 0 | 0 | 156.9304 | 42.5581 | 0 | 7.7116 | 34.8466 | 0 | 0 | 0 | 0 | 0 | 156.9304 | 0 | 731.7502 | 57.37% | 7.7116 | 0 | 56.25 | 90% | 34.8466
6833 | 397 | 153 | 61 | 4.9 | 25.1 | 0 | 0 | 0 | 69.1608 | 20.3931 | 0 | 0 | 20.3931 | 0 | 0 | 0 | 0 | 0 | 69.1608 | 0 | 800.911 | 62.79% | 0 | 17.4575 | 36.9292 | 59.09% | 37.8506
6834 | 36 | 16 | 12 | 4.1 | 22.8 | 0 | 0 | 0 | 0 | 1.0474 | 0 | 0 | 1.0474 | 0 | 0 | 0 | 77.1212 | 29.473 | 0 | 77.1212 | 723.7898 | 56.75% | 0 | 7.216 | 28.943 | 46.31% | 37.7364
6835 | 0 | 0 | 0 | 3.4 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7132 | 35.4315 | 0 | 90.7132 | 633.0766 | 49.63% | 0 | 0 | 28.943 | 46.31% | 35.4315
6836 | 0 | 0 | 0 | 2.7 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1984 | 33.5695 | 0 | 86.1984 | 546.8782 | 42.88% | 0 | 0 | 28.943 | 46.31% | 33.5695
6837 | 0 | 0 | 0 | 2.2 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5015 | 31.5724 | 0 | 81.5015 | 465.3768 | 36.49% | 0 | 0 | 28.943 | 46.31% | 31.5724
6838 | 0 | 0 | 0 | 1.2 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8237 | 30.0153 | 0 | 77.8237 | 387.5531 | 30.38% | 0 | 0 | 28.943 | 46.31% | 30.0153
6839 | 0 | 0 | 0 | 1 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6228 | 28.2062 | 0 | 73.6228 | 313.9303 | 24.61% | 0 | 0 | 28.943 | 46.31% | 28.2062
6840 | 0 | 0 | 0 | 1.5 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313.9303 | 24.61% | 0 | 0 | 28.943 | 46.31% | 0
6841 | 0 | 0 | 0 | 0.9 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313.9303 | 24.61% | 0 | 0 | 28.943 | 46.31% | 0
6842 | 0 | 0 | 0 | 1.1 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313.9303 | 24.61% | 0 | 0 | 28.943 | 46.31% | 0
6843 | 0 | 0 | 0 | 1.4 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313.9303 | 24.61% | 0 | 0 | 28.943 | 46.31% | 0
6844 | 0 | 0 | 0 | 1.6 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.3118 | 28.5669 | 0 | 74.3118 | 239.6184 | 18.79% | 0 | 0 | 28.943 | 46.31% | 28.5669
6845 | 0 | 0 | 0 | 1.1 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.9118 | 28.8552 | 0 | 74.9118 | 164.7066 | 12.91% | 0 | 0 | 28.943 | 46.31% | 28.8552
6846 | 0 | 0 | 0 | 2 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7276 | 30.9387 | 0 | 79.7276 | 84.9791 | 6.662% | 0 | 0 | 28.943 | 46.31% | 30.9387
6847 | 102 | 28 | 18 | 1.4 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9791 | 33.206 | 0 | 84.9791 | 1.4211e-13 | 1.114e-14% | 0 | 0 | 28.943 | 46.31% | 33.206
6848 | 509 | 191 | 63 | 0.7 | 18.4 | 0 | 0 | 0 | 68.9441 | 13.9187 | 0 | 0 | 13.9187 | 0 | 0 | 0 | 0 | 0 | 68.9441 | 0 | 68.9441 | 5.405% | 0 | 20.5045 | 6.25 | 10% | 34.4232
6849 | 705 | 385 | 88 | 1.1 | 21.4 | 0 | 0 | 0 | 145.0961 | 35.0666 | 0.21292 | 0 | 35.0666 | 0 | 0 | 0 | 0 | 0 | 145.0961 | 0 | 214.0403 | 16.78% | 0 | 0 | 6.25 | 10% | 35.0666
6850 | 796 | 550 | 101 | 0.7 | 24.3 | 0 | 0 | 0 | 196.6406 | 35.8521 | 13.6957 | 0 | 35.8521 | 0 | 0 | 0 | 0 | 0 | 196.6406 | 0 | 410.6808 | 32.2% | 0 | 0 | 6.25 | 10% | 35.8521
6851 | 840 | 666 | 109 | 1.5 | 25.5 | 0 | 0 | 0 | 224.5365 | 35.7727 | 25.2384 | 0 | 35.7727 | 0 | 0 | 0 | 0 | 0 | 224.5365 | 0 | 635.2173 | 49.8% | 0 | 0 | 6.25 | 10% | 35.7727
6852 | 858 | 726 | 113 | 1.2 | 27 | 0 | 0 | 0 | 237.667 | 34.0541 | 32.0558 | 0 | 34.0541 | 0 | 0 | 0 | 0 | 0 | 237.667 | 0 | 872.8843 | 68.43% | 0 | 0 | 6.25 | 10% | 34.0541
6853 | 850 | 719 | 115 | 1.5 | 28.1 | 0 | 0 | 0 | 237.8512 | 34.49 | 33.0041 | 1.3996 | 33.0904 | 0 | 0 | 0 | 0 | 0 | 237.8512 | 0 | 1110.7355 | 87.08% | 1.3996 | 0 | 7.5147 | 12.02% | 33.0904
6854 | 808 | 646 | 118 | 2.7 | 28.5 | 0 | 0 | 0 | 0 | 57.6113 | 7.2178 | 25 | 32.6113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110.7355 | 87.08% | 25 | 0 | 30.1037 | 48.17% | 32.6113
6855 | 736 | 517 | 114 | 2.6 | 27.5 | 0 | 0 | 0 | 164.7747 | 55.6215 | 0 | 22.9433 | 32.6782 | 0 | 0 | 0 | 0 | 0 | 164.7747 | 0 | 1275.5102 | 100% | 22.9433 | 0 | 50.8343 | 81.33% | 32.6782
6856 | 606 | 342 | 100 | 3.8 | 27.3 | 0 | 0 | 0 | 0 | 40.6397 | 0 | 5.9937 | 34.646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 5.9937 | 0 | 56.25 | 90% | 34.646
6857 | 379 | 152 | 65 | 4.3 | 25.8 | 0 | 0 | 0 | 0 | 19.9671 | 0 | 0 | 19.9671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 18.1133 | 36.2034 | 57.93% | 38.0804
6858 | 24 | 16 | 12 | 3.5 | 23.6 | 0 | 0 | 0 | 0 | 0.73093 | 0 | 0 | 0.73093 | 0 | 0 | 0 | 95.4212 | 37.2631 | 0 | 95.4212 | 1180.089 | 92.52% | 0 | 0 | 36.2034 | 57.93% | 37.9941
6859 | 0 | 0 | 0 | 3.5 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.034 | 35.9802 | 0 | 92.034 | 1088.055 | 85.3% | 0 | 0 | 36.2034 | 57.93% | 35.9802
6860 | 0 | 0 | 0 | 3.3 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5504 | 33.7101 | 0 | 86.5504 | 1001.5046 | 78.52% | 0 | 0 | 36.2034 | 57.93% | 33.7101
6861 | 0 | 0 | 0 | 2.5 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5461 | 31.6016 | 0 | 81.5461 | 919.9585 | 72.12% | 0 | 0 | 36.2034 | 57.93% | 31.6016
6862 | 0 | 0 | 0 | 1.3 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.9679 | 30.0822 | 0 | 77.9679 | 841.9906 | 66.01% | 0 | 0 | 36.2034 | 57.93% | 30.0822
6863 | 0 | 0 | 0 | 1.7 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.6253 | 29.1059 | 0 | 75.6253 | 766.3653 | 60.08% | 0 | 0 | 36.2034 | 57.93% | 29.1059
6864 | 0 | 0 | 0 | 1.9 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6757 | 28.6825 | 0 | 74.6757 | 691.6896 | 54.23% | 0 | 0 | 36.2034 | 57.93% | 28.6825
6865 | 0 | 0 | 0 | 2.4 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.6896 | 54.23% | 0 | 3.0597 | 32.8171 | 52.51% | 3.0597
6866 | 0 | 0 | 0 | 2.7 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691.6896 | 54.23% | 0 | 0 | 32.8171 | 52.51% | 0
6867 | 0 | 0 | 0 | 2.3 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4775 | 33.3745 | 0 | 85.4775 | 606.2121 | 47.53% | 0 | 0 | 32.8171 | 52.51% | 33.3745
6868 | 0 | 0 | 0 | 2.2 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.2368 | 38.9133 | 0 | 98.2368 | 507.9754 | 39.83% | 0 | 0 | 32.8171 | 52.51% | 38.9133
6869 | 0 | 0 | 0 | 2.7 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4386 | 41.5301 | 0 | 104.4386 | 403.5368 | 31.64% | 0 | 0 | 32.8171 | 52.51% | 41.5301
6870 | 0 | 0 | 0 | 1.6 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.4044 | 42.8323 | 0 | 107.4044 | 296.1324 | 23.22% | 0 | 0 | 32.8171 | 52.51% | 42.8323
6871 | 22 | 27 | 25 | 1.1 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.2356 | 45.8591 | 0 | 114.2356 | 181.8968 | 14.26% | 2.2274 | 0 | 34.8297 | 55.73% | 43.6317
6872 | 43 | 76 | 69 | 1.8 | 18.2 | 0 | 0 | 0 | 0 | 5.7045 | 0 | 0 | 5.7045 | 0 | 0 | 0 | 97.6267 | 38.5887 | 0 | 97.6267 | 84.2701 | 6.607% | 0 | 0 | 34.8297 | 55.73% | 44.2932
6873 | 32 | 163 | 148 | 1.3 | 19.9 | 0 | 0 | 0 | 0 | 12.0881 | 0 | 0 | 12.0881 | 0 | 0 | 0 | 84.2701 | 32.7204 | 0 | 84.2701 | 0 | 0% | 0 | 0 | 34.8297 | 55.73% | 44.8085
6874 | 114 | 279 | 211 | 1.5 | 22 | 0 | 0 | 0 | 0 | 22.3542 | 0 | 0 | 22.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 22.5267 | 9.8986 | 15.84% | 44.8809
6875 | 316 | 469 | 255 | 1.1 | 24.3 | 0 | 0 | 0 | 73.5685 | 40.0718 | 0 | 0 | 40.0718 | 0 | 0 | 0 | 0 | 0 | 73.5685 | 0 | 73.5685 | 5.768% | 0 | 3.2967 | 6.25 | 10% | 43.3685
6876 | 655 | 722 | 254 | 2.9 | 26.7 | 0 | 0 | 0 | 176.4062 | 47.6105 | 18.2168 | 5.3367 | 42.2738 | 0 | 0 | 0 | 0 | 0 | 176.4062 | 0 | 249.9747 | 19.6% | 5.3367 | 0 | 11.072 | 17.72% | 42.2738
6877 | 860 | 723 | 118 | 6.1 | 28 | 0 | 0 | 0 | 237.3568 | 67.207 | 4.793 | 25 | 42.207 | 0 | 0 | 0 | 0 | 0 | 237.3568 | 0 | 487.3315 | 38.21% | 25 | 0 | 33.661 | 53.86% | 42.207
6878 | 825 | 646 | 112 | 6.4 | 27.6 | 0 | 0 | 0 | 222.9585 | 66.9897 | 0.88469 | 25 | 41.9897 | 0 | 0 | 0 | 0 | 0 | 222.9585 | 0 | 710.2901 | 55.69% | 25 | 0 | 56.25 | 90% | 41.9897
6879 | 262 | 298 | 147 | 9.1 | 26.3 | 0 | 0 | 0 | 51.3571 | 30.0968 | 0 | 0 | 30.0968 | 0 | 0 | 0 | 0 | 0 | 51.3571 | 0 | 761.6472 | 59.71% | 0 | 11.4417 | 43.5871 | 69.74% | 41.5385
6880 | 590 | 336 | 99 | 10.7 | 26.6 | 0 | 0 | 0 | 131.0649 | 40.6433 | 0 | 0 | 40.6433 | 0 | 0 | 0 | 0 | 0 | 131.0649 | 0 | 892.7121 | 69.99% | 0 | 1.8381 | 41.5528 | 66.48% | 42.4813
6881 | 455 | 144 | 47 | 8.8 | 25.3 | 0 | 0 | 0 | 77.8544 | 21.3211 | 0 | 0 | 21.3211 | 0 | 0 | 0 | 0 | 0 | 77.8544 | 0 | 970.5665 | 76.09% | 0 | 23.4498 | 15.6001 | 24.96% | 44.7709
6882 | 37 | 16 | 9 | 7.1 | 23.6 | 0 | 0 | 0 | 0 | 0.99834 | 0 | 0 | 0.99834 | 0 | 0 | 0 | 107.0648 | 42.2518 | 0 | 107.0648 | 863.5017 | 67.7% | 0 | 0 | 15.6001 | 24.96% | 43.2501
6883 | 0 | 0 | 0 | 6.4 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0882 | 38.9328 | 0 | 99.0882 | 764.4135 | 59.93% | 0 | 0 | 15.6001 | 24.96% | 38.9328
6884 | 0 | 0 | 0 | 6.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0851 | 35.5917 | 0 | 91.0851 | 673.3284 | 52.79% | 0 | 0 | 15.6001 | 24.96% | 35.5917
6885 | 0 | 0 | 0 | 7.9 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3378 | 34.8708 | 0 | 89.3378 | 583.9906 | 45.78% | 0.98099 | 0 | 16.4864 | 26.38% | 33.8898
6886 | 0 | 0 | 0 | 6.6 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9906 | 45.78% | 0 | 0 | 16.4864 | 26.38% | 0
6887 | 0 | 0 | 0 | 4.3 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9906 | 45.78% | 0 | 0 | 16.4864 | 26.38% | 0
6888 | 0 | 0 | 0 | 3.9 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9906 | 45.78% | 0 | 0 | 16.4864 | 26.38% | 0
6889 | 0 | 0 | 0 | 4.6 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9906 | 45.78% | 0 | 0 | 16.4864 | 26.38% | 0
6890 | 0 | 0 | 0 | 4.6 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 583.9906 | 45.78% | 0 | 9.2492 | 6.25 | 10% | 9.2492
6891 | 0 | 0 | 0 | 4.1 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4633 | 34.2533 | 0 | 87.4633 | 496.5273 | 38.93% | 0 | 0 | 6.25 | 10% | 34.2533
6892 | 0 | 0 | 0 | 2.4 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4168 | 39.0316 | 0 | 98.4168 | 398.1105 | 31.21% | 0 | 0 | 6.25 | 10% | 39.0316
6893 | 0 | 0 | 0 | 2.1 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2616 | 41.182 | 0 | 103.2616 | 294.8489 | 23.12% | 0 | 0 | 6.25 | 10% | 41.182
6894 | 0 | 0 | 0 | 2.3 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.45 | 42.2084 | 0 | 105.45 | 189.3989 | 14.85% | 0 | 0 | 6.25 | 10% | 42.2084
6895 | 170 | 27 | 12 | 2.2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.9184 | 48.1084 | 0 | 118.9184 | 70.4805 | 5.526% | 5.336 | 0 | 11.0714 | 17.71% | 42.7724
6896 | 688 | 206 | 43 | 1.6 | 14.7 | 0 | 0 | 0 | 0 | 16.0912 | 0 | 0 | 16.0912 | 0 | 0 | 0 | 70.4805 | 26.9611 | 0 | 70.4805 | 0 | 0% | 0 | 0 | 11.0714 | 17.71% | 43.0523
6897 | 852 | 406 | 58 | 1.5 | 17.3 | 0 | 0 | 0 | 0 | 39.1611 | 0 | 0 | 39.1611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 4.3564 | 6.25 | 10% | 43.5175
6898 | 918 | 572 | 68 | 1.7 | 19 | 0 | 0 | 0 | 227.972 | 43.4506 | 11.3231 | 0 | 43.4506 | 0 | 0 | 0 | 0 | 0 | 227.972 | 0 | 227.972 | 17.87% | 0 | 0 | 6.25 | 10% | 43.4506
6899 | 940 | 686 | 76 | 1.9 | 20.5 | 0 | 0 | 0 | 252.963 | 41.9312 | 23.4273 | 0 | 41.9312 | 0 | 0 | 0 | 0 | 0 | 252.963 | 0 | 480.935 | 37.71% | 0 | 0 | 6.25 | 10% | 41.9312
6900 | 953 | 744 | 77 | 1.6 | 21 | 0 | 0 | 0 | 265.2076 | 41.0329 | 29.7805 | 0 | 41.0329 | 0 | 0 | 0 | 0 | 0 | 265.2076 | 0 | 746.1425 | 58.5% | 0 | 0 | 6.25 | 10% | 41.0329
6901 | 942 | 735 | 79 | 2.1 | 21.6 | 0 | 0 | 0 | 264.6404 | 47.9353 | 24.0647 | 7.1684 | 40.7669 | 0 | 0 | 0 | 0 | 0 | 264.6404 | 0 | 1010.783 | 79.25% | 7.1684 | 0 | 12.7271 | 20.36% | 40.7669
6902 | 909 | 662 | 81 | 1.8 | 22.2 | 0 | 0 | 0 | 0 | 65.6304 | 2.3434 | 25 | 40.6304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010.783 | 79.25% | 25 | 0 | 35.3161 | 56.51% | 40.6304
6903 | 853 | 534 | 80 | 2.3 | 22.3 | 0 | 0 | 0 | 225.9351 | 59.6797 | 0 | 19.4852 | 40.1945 | 0 | 0 | 0 | 0 | 0 | 225.9351 | 0 | 1236.7181 | 96.96% | 19.4852 | 0 | 52.9222 | 84.68% | 40.1945
6904 | 743 | 357 | 71 | 2.8 | 22 | 0 | 0 | 0 | 38.7921 | 45.3427 | 0 | 3.683 | 41.6596 | 0 | 0 | 0 | 0 | 0 | 38.7921 | 0 | 1275.5102 | 100% | 3.683 | 0 | 56.25 | 90% | 41.6596
6905 | 503 | 156 | 47 | 3.2 | 20.7 | 0 | 0 | 0 | 0 | 23.1602 | 0 | 0 | 23.1602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 21.2751 | 32.7041 | 52.33% | 44.4353
6906 | 25 | 12 | 8 | 2.1 | 17.8 | 0 | 0 | 0 | 0 | 0.5883 | 0 | 0 | 0.5883 | 0 | 0 | 0 | 106.3644 | 42.3944 | 0 | 106.3644 | 1169.1458 | 91.66% | 0 | 0 | 32.7041 | 52.33% | 42.9827
6907 | 0 | 0 | 0 | 2.1 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7477 | 39.1848 | 0 | 98.7477 | 1070.398 | 83.92% | 0 | 0 | 32.7041 | 52.33% | 39.1848
6908 | 0 | 0 | 0 | 0.9 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6283 | 35.6947 | 0 | 90.6283 | 979.7698 | 76.81% | 0 | 0 | 32.7041 | 52.33% | 35.6947
6909 | 0 | 0 | 0 | 0.8 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.3135 | 33.8494 | 0 | 86.3135 | 893.4563 | 70.05% | 0 | 0 | 32.7041 | 52.33% | 33.8494
6910 | 0 | 0 | 0 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4776 | 32.1977 | 0 | 82.4776 | 810.9787 | 63.58% | 0 | 0 | 32.7041 | 52.33% | 32.1977
6911 | 0 | 0 | 0 | 1.2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8538 | 31.0891 | 0 | 79.8538 | 731.1249 | 57.32% | 0 | 0 | 32.7041 | 52.33% | 31.0891
6912 | 0 | 0 | 0 | 1.1 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.3289 | 26.9484 | 0 | 70.3289 | 660.796 | 51.81% | 0 | 0 | 32.7041 | 52.33% | 26.9484
6913 | 0 | 0 | 0 | 1.8 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.4696 | 30.4888 | 0 | 78.4696 | 582.3264 | 45.65% | 0 | 0 | 32.7041 | 52.33% | 30.4888
6914 | 0 | 0 | 0 | 1.5 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7211 | 31.0362 | 0 | 79.7211 | 502.6053 | 39.4% | 0 | 0 | 32.7041 | 52.33% | 31.0362
6915 | 0 | 0 | 0 | 0.7 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7465 | 34.1377 | 0 | 86.7465 | 415.8588 | 32.6% | 0 | 0 | 32.7041 | 52.33% | 34.1377
6916 | 0 | 0 | 0 | 0.7 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.615 | 39.3143 | 0 | 98.615 | 317.2438 | 24.87% | 0 | 0 | 32.7041 | 52.33% | 39.3143
6917 | 0 | 0 | 0 | 1.5 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.0957 | 41.6972 | 0 | 104.0957 | 213.1481 | 16.71% | 0 | 0 | 32.7041 | 52.33% | 41.6972
6918 | 0 | 0 | 0 | 1.1 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8192 | 42.4577 | 0 | 105.8192 | 107.3289 | 8.415% | 0 | 0 | 32.7041 | 52.33% | 42.4577
6919 | 177 | 27 | 13 | 1.4 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3289 | 43.0913 | 0 | 107.3289 | 0 | 0% | 0 | 0 | 32.7041 | 52.33% | 43.0913
6920 | 659 | 197 | 42 | 1.1 | 15.1 | 0 | 0 | 0 | 92.2748 | 15.4334 | 0 | 0 | 15.4334 | 0 | 0 | 0 | 0 | 0 | 92.2748 | 0 | 92.2748 | 7.234% | 0 | 23.9029 | 6.25 | 10% | 39.3362
6921 | 823 | 392 | 59 | 0.9 | 17.9 | 0 | 0 | 0 | 0 | 37.7687 | 0 | 0 | 37.7687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2748 | 7.234% | 0 | 0 | 6.25 | 10% | 37.7687
6922 | 918 | 563 | 63 | 1.3 | 19.1 | 0 | 0 | 0 | 227.8328 | 43.8712 | 10.0933 | 0 | 43.8712 | 0 | 0 | 0 | 0 | 0 | 227.8328 | 0 | 320.1076 | 25.1% | 0 | 0 | 6.25 | 10% | 43.8712
6923 | 957 | 684 | 66 | 1.9 | 20.6 | 0 | 0 | 0 | 257.6401 | 42.5872 | 22.9453 | 0 | 42.5872 | 0 | 0 | 0 | 0 | 0 | 257.6401 | 0 | 577.7478 | 45.3% | 0 | 0 | 6.25 | 10% | 42.5872
6924 | 966 | 741 | 69 | 1.8 | 21.6 | 0 | 0 | 0 | 268.6931 | 41.8546 | 29.331 | 0 | 41.8546 | 0 | 0 | 0 | 0 | 0 | 268.6931 | 0 | 846.4409 | 66.36% | 0 | 0 | 6.25 | 10% | 41.8546
6925 | 957 | 732 | 70 | 2.1 | 22.6 | 0 | 0 | 0 | 268.8058 | 49.3672 | 22.6328 | 7.9012 | 41.4661 | 0 | 0 | 0 | 0 | 0 | 268.8058 | 0 | 1115.2468 | 87.44% | 7.9012 | 0 | 13.3892 | 21.42% | 41.4661
6926 | 935 | 660 | 68 | 2.8 | 23.1 | 0 | 0 | 0 | 0 | 66.2293 | 3.356 | 25 | 41.2293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115.2468 | 87.44% | 25 | 0 | 35.9782 | 57.57% | 41.2293
6927 | 890 | 532 | 64 | 2 | 23.7 | 0 | 0 | 0 | 160.2634 | 59.8699 | 0 | 19.0041 | 40.8658 | 0 | 0 | 0 | 0 | 0 | 160.2634 | 0 | 1275.5102 | 100% | 19.0041 | 0 | 53.1495 | 85.04% | 40.8658
6928 | 789 | 355 | 56 | 3.4 | 23.4 | 0 | 0 | 0 | 0 | 45.942 | 0 | 3.4314 | 42.5106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 3.4314 | 0 | 56.25 | 90% | 42.5106
6929 | 567 | 158 | 40 | 3.9 | 21.2 | 0 | 0 | 0 | 0 | 24.7935 | 0 | 0 | 24.7935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 20.3771 | 33.698 | 53.92% | 45.1706
6930 | 45 | 14 | 8 | 2.7 | 18.9 | 0 | 0 | 0 | 0 | 1.0247 | 0 | 0 | 1.0247 | 0 | 0 | 0 | 107.2279 | 42.6975 | 0 | 107.2279 | 1168.2823 | 91.59% | 0 | 0 | 33.698 | 53.92% | 43.7222
6931 | 0 | 0 | 0 | 1.7 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7646 | 39.5859 | 0 | 99.7646 | 1068.5177 | 83.77% | 0 | 0 | 33.698 | 53.92% | 39.5859
6932 | 0 | 0 | 0 | 1.1 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5549 | 36.0972 | 0 | 91.5549 | 976.9627 | 76.59% | 0 | 0 | 33.698 | 53.92% | 36.0972
6933 | 0 | 0 | 0 | 0.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.5309 | 34.3786 | 0 | 87.5309 | 889.4318 | 69.73% | 0 | 0 | 33.698 | 53.92% | 34.3786
6934 | 0 | 0 | 0 | 0.8 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2486 | 32.5236 | 0 | 83.2486 | 806.1832 | 63.2% | 0 | 0 | 33.698 | 53.92% | 32.5236
6935 | 0 | 0 | 0 | 1.9 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.3654 | 15.6246 | 0 | 44.3654 | 761.8179 | 59.73% | 0 | 0 | 33.698 | 53.92% | 15.6246
6936 | 0 | 0 | 0 | 0.7 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7753 | 31.0668 | 0 | 79.7753 | 682.0426 | 53.47% | 0 | 0 | 33.698 | 53.92% | 31.0668
6937 | 0 | 0 | 0 | 1.2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3222 | 30.8649 | 0 | 79.3222 | 602.7203 | 47.25% | 0 | 0 | 33.698 | 53.92% | 30.8649
6938 | 0 | 0 | 0 | 0.6 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.2312 | 31.2883 | 0 | 80.2312 | 522.4891 | 40.96% | 0 | 0 | 33.698 | 53.92% | 31.2883
6939 | 0 | 0 | 0 | 1.2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7547 | 34.114 | 0 | 86.7547 | 435.7344 | 34.16% | 0 | 0 | 33.698 | 53.92% | 34.114
6940 | 0 | 0 | 0 | 0.7 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.16 | 39.118 | 0 | 98.16 | 337.5744 | 26.47% | 0 | 0 | 33.698 | 53.92% | 39.118
6941 | 0 | 0 | 0 | 1.4 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8036 | 41.5524 | 0 | 103.8036 | 233.7707 | 18.33% | 0 | 0 | 33.698 | 53.92% | 41.5524
6942 | 0 | 0 | 0 | 2.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3068 | 42.6317 | 0 | 106.3068 | 127.4639 | 9.993% | 0 | 0 | 33.698 | 53.92% | 42.6317
6943 | 173 | 25 | 12 | 0.6 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.4639 | 51.8929 | 0 | 127.4639 | 0 | 0% | 8.6609 | 0 | 41.5236 | 66.44% | 43.232
6944 | 578 | 178 | 45 | 0.5 | 15.4 | 0 | 0 | 0 | 78.3017 | 14.3396 | 0 | 0 | 14.3396 | 0 | 0 | 0 | 0 | 0 | 78.3017 | 0 | 78.3017 | 6.139% | 0 | 25 | 13.8553 | 22.17% | 39.3396
6945 | 822 | 388 | 58 | 0.7 | 19.3 | 0 | 0 | 0 | 0 | 37.3643 | 0 | 0 | 37.3643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.3017 | 6.139% | 0 | 6.8718 | 6.25 | 10% | 44.2361
6946 | 898 | 552 | 65 | 1.2 | 21.2 | 0 | 0 | 0 | 222.1968 | 44.2375 | 8.4351 | 0 | 44.2375 | 0 | 0 | 0 | 0 | 0 | 222.1968 | 0 | 300.4985 | 23.56% | 0 | 0 | 6.25 | 10% | 44.2375
6947 | 937 | 671 | 70 | 2.5 | 22.4 | 0 | 0 | 0 | 251.4623 | 42.881 | 22.1141 | 0 | 42.881 | 0 | 0 | 0 | 0 | 0 | 251.4623 | 0 | 551.9608 | 43.27% | 0 | 0 | 6.25 | 10% | 42.881
6948 | 947 | 728 | 73 | 2.2 | 23.8 | 0 | 0 | 0 | 262.6448 | 41.8449 | 28.542 | 0 | 41.8449 | 0 | 0 | 0 | 0 | 0 | 262.6448 | 0 | 814.6056 | 63.87% | 0 | 0 | 6.25 | 10% | 41.8449
6949 | 925 | 715 | 78 | 1.6 | 25.1 | 0 | 0 | 0 | 259.2245 | 66.7752 | 2.8591 | 25 | 41.7752 | 0 | 0 | 0 | 0 | 0 | 259.2245 | 0 | 1073.8301 | 84.19% | 25 | 0 | 28.839 | 46.14% | 41.7752
6950 | 829 | 621 | 97 | 1.2 | 26.4 | 0 | 0 | 0 | 0 | 62.3749 | 0 | 20.6846 | 41.6903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1073.8301 | 84.19% | 20.6846 | 0 | 47.5288 | 76.05% | 41.6903
6951 | 652 | 479 | 143 | 3 | 26 | 0 | 0 | 0 | 167.9925 | 50.8285 | 2.6132 | 9.6521 | 41.1764 | 0 | 0 | 0 | 0 | 0 | 167.9925 | 0 | 1241.8226 | 97.36% | 9.6521 | 0 | 56.25 | 90% | 41.1764
6952 | 398 | 294 | 142 | 3 | 25.8 | 0 | 0 | 0 | 33.6876 | 32.9506 | 0 | 0 | 32.9506 | 0 | 0 | 0 | 0 | 0 | 33.6876 | 0 | 1275.5102 | 100% | 0 | 9.7383 | 45.4723 | 72.76% | 42.6888
6953 | 391 | 172 | 97 | 3.7 | 24.4 | 0 | 0 | 0 | 0 | 22.6547 | 0 | 0 | 22.6547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 22.3822 | 20.7012 | 33.12% | 45.0369
6954 | 29 | 15 | 10 | 2.7 | 21.2 | 0 | 0 | 0 | 0 | 0.76652 | 0 | 0 | 0.76652 | 0 | 0 | 0 | 107.6152 | 42.6953 | 0 | 107.6152 | 1167.895 | 91.56% | 0 | 0 | 20.7012 | 33.12% | 43.4618
6955 | 0 | 0 | 0 | 1.3 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.5559 | 39.4578 | 0 | 99.5559 | 1068.339 | 83.76% | 0 | 0 | 20.7012 | 33.12% | 39.4578
6956 | 0 | 0 | 0 | 0.5 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1369 | 36.3117 | 0 | 92.1369 | 976.2021 | 76.53% | 0 | 0 | 20.7012 | 33.12% | 36.3117
6957 | 0 | 0 | 0 | 1.2 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7658 | 34.4552 | 0 | 87.7658 | 888.4363 | 69.65% | 0 | 0 | 20.7012 | 33.12% | 34.4552
6958 | 0 | 0 | 0 | 1.2 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6959 | 32.6726 | 0 | 83.6959 | 804.7404 | 63.09% | 0 | 0 | 20.7012 | 33.12% | 32.6726
6959 | 0 | 0 | 0 | 2.1 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804.7404 | 63.09% | 0 | 0 | 20.7012 | 33.12% | 0
6960 | 0 | 0 | 0 | 1.8 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804.7404 | 63.09% | 0 | 0 | 20.7012 | 33.12% | 0
6961 | 0 | 0 | 0 | 0.8 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.1897 | 19.4719 | 0 | 53.1897 | 751.5507 | 58.92% | 0 | 0 | 20.7012 | 33.12% | 19.4719
6962 | 0 | 0 | 0 | 0.7 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.5171 | 31.3328 | 0 | 80.5171 | 671.0336 | 52.61% | 0 | 0 | 20.7012 | 33.12% | 31.3328
6963 | 0 | 0 | 0 | 0.6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.389 | 34.3698 | 0 | 87.389 | 583.6445 | 45.76% | 0.097017 | 0 | 20.7889 | 33.26% | 34.2728
6964 | 0 | 0 | 0 | 1 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4323 | 38.7127 | 0 | 97.4323 | 486.2122 | 38.12% | 0 | 0 | 20.7889 | 33.26% | 38.7127
6965 | 0 | 0 | 0 | 0.9 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.751 | 41.019 | 0 | 102.751 | 383.4612 | 30.06% | 0 | 0 | 20.7889 | 33.26% | 41.019
6966 | 0 | 0 | 0 | 1.9 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8918 | 41.9382 | 0 | 104.8918 | 278.5694 | 21.84% | 0 | 0 | 20.7889 | 33.26% | 41.9382
6967 | 83 | 26 | 20 | 2.2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7637 | 42.7306 | 0 | 106.7637 | 171.8057 | 13.47% | 0 | 0 | 20.7889 | 33.26% | 42.7306
6968 | 212 | 140 | 88 | 1.7 | 16.4 | 0 | 0 | 0 | 0 | 11.4144 | 0 | 0 | 11.4144 | 0 | 0 | 0 | 81.502 | 31.6895 | 0 | 81.502 | 90.3037 | 7.08% | 0 | 0 | 20.7889 | 33.26% | 43.1039
6969 | 515 | 328 | 115 | 1 | 20.2 | 0 | 0 | 0 | 99.3963 | 30.2025 | 0 | 0 | 30.2025 | 0 | 0 | 0 | 0 | 0 | 99.3963 | 0 | 189.7001 | 14.87% | 0 | 13.1367 | 6.25 | 10% | 43.3392
6970 | 634 | 504 | 157 | 1.3 | 23.6 | 0 | 0 | 0 | 151.5798 | 43.3323 | 3.2537 | 0 | 43.3323 | 0 | 0 | 0 | 0 | 0 | 151.5798 | 0 | 341.2798 | 26.76% | 0 | 0 | 6.25 | 10% | 43.3323
6971 | 685 | 632 | 190 | 1 | 26 | 0 | 0 | 0 | 179.5886 | 41.8616 | 15.576 | 0 | 41.8616 | 0 | 0 | 0 | 0 | 0 | 179.5886 | 0 | 520.8684 | 40.84% | 0 | 0 | 6.25 | 10% | 41.8616
6972 | 505 | 578 | 225 | 1.2 | 26.7 | 0 | 0 | 0 | 132.0723 | 40.7238 | 12.1027 | 0 | 40.7238 | 0 | 0 | 0 | 0 | 0 | 132.0723 | 0 | 652.9408 | 51.19% | 0 | 0 | 6.25 | 10% | 40.7238
6973 | 714 | 673 | 182 | 3.3 | 26.7 | 0 | 0 | 0 | 195.1079 | 55.9816 | 10.6871 | 15.8595 | 40.1221 | 0 | 0 | 0 | 0 | 0 | 195.1079 | 0 | 848.0487 | 66.49% | 15.8595 | 0 | 20.58 | 32.93% | 40.1221
6974 | 819 | 637 | 124 | 4.4 | 26.5 | 0 | 0 | 0 | 221.9001 | 64.9703 | 2.6219 | 25 | 39.9703 | 0 | 0 | 0 | 0 | 0 | 221.9001 | 0 | 1069.9488 | 83.88% | 25 | 0 | 43.169 | 69.07% | 39.9703
6975 | 629 | 489 | 161 | 5 | 25.8 | 0 | 0 | 0 | 159.4381 | 54.2636 | 0 | 14.4772 | 39.7865 | 0 | 0 | 0 | 0 | 0 | 159.4381 | 0 | 1229.3869 | 96.38% | 14.4772 | 0 | 56.25 | 90% | 39.7865
6976 | 252 | 236 | 130 | 4.4 | 24.5 | 0 | 0 | 0 | 46.1233 | 23.7306 | 0 | 0 | 23.7306 | 0 | 0 | 0 | 0 | 0 | 46.1233 | 0 | 1275.5102 | 100% | 0 | 17.475 | 36.9098 | 59.06% | 41.2056
6977 | 12 | 68 | 66 | 3.2 | 23 | 0 | 0 | 0 | 0 | 4.2848 | 0 | 0 | 4.2848 | 0 | 0 | 0 | 98.5355 | 38.6473 | 0 | 98.5355 | 1176.9747 | 92.27% | 0 | 0.42949 | 36.4345 | 58.3% | 43.3615
6978 | 3 | 8 | 8 | 2.2 | 20.8 | 0 | 0 | 0 | 0 | 0.10964 | 0 | 0 | 0.10964 | 0 | 0 | 0 | 105.2556 | 41.7102 | 0 | 105.2556 | 1071.7192 | 84.02% | 0 | 0 | 36.4345 | 58.3% | 41.8198
6979 | 0 | 0 | 0 | 1.3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2948 | 38.4564 | 0 | 97.2948 | 974.4244 | 76.39% | 0 | 0 | 36.4345 | 58.3% | 38.4564
6980 | 0 | 0 | 0 | 0.8 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0679 | 35.8159 | 0 | 91.0679 | 883.3565 | 69.26% | 0 | 0 | 36.4345 | 58.3% | 35.8159
6981 | 0 | 0 | 0 | 1.1 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.8091 | 33.9873 | 0 | 86.8091 | 796.5474 | 62.45% | 0 | 0 | 36.4345 | 58.3% | 33.9873
6982 | 0 | 0 | 0 | 0.4 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5991 | 32.2214 | 0 | 82.5991 | 713.9483 | 55.97% | 0 | 0 | 36.4345 | 58.3% | 32.2214
6983 | 0 | 0 | 0 | 0.9 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1036 | 30.7089 | 0 | 79.1036 | 634.8447 | 49.77% | 0 | 0 | 36.4345 | 58.3% | 30.7089
6984 | 0 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6035 | 30.0474 | 0 | 77.6035 | 557.2412 | 43.69% | 0 | 0 | 36.4345 | 58.3% | 30.0474
6985 | 0 | 0 | 0 | 1.1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5617 | 29.5947 | 0 | 76.5617 | 480.6795 | 37.69% | 0 | 0 | 36.4345 | 58.3% | 29.5947
6986 | 0 | 0 | 0 | 1.9 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.0801 | 29.3886 | 0 | 76.0801 | 404.5994 | 31.72% | 0 | 0 | 36.4345 | 58.3% | 29.3886
6987 | 0 | 0 | 0 | 0.8 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.0865 | 18.9743 | 0 | 52.0865 | 352.5129 | 27.64% | 0 | 0 | 36.4345 | 58.3% | 18.9743
6988 | 0 | 0 | 0 | 1.2 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6502 | 31.8467 | 0 | 81.6502 | 270.8627 | 21.24% | 0 | 0 | 36.4345 | 58.3% | 31.8467
6989 | 0 | 0 | 0 | 1.5 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0188 | 33.2965 | 0 | 85.0188 | 185.8439 | 14.57% | 0 | 0 | 36.4345 | 58.3% | 33.2965
6990 | 0 | 0 | 0 | 0.9 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4997 | 35.7031 | 0 | 90.4997 | 95.3443 | 7.475% | 0 | 0 | 36.4345 | 58.3% | 35.7031
6991 | 154 | 22 | 10 | 0.7 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3443 | 37.8144 | 0 | 95.3443 | 0 | 0% | 0 | 0 | 36.4345 | 58.3% | 37.8144
6992 | 639 | 181 | 38 | 0.8 | 16.6 | 0 | 0 | 0 | 87.1177 | 14.6881 | 0 | 0 | 14.6881 | 0 | 0 | 0 | 0 | 0 | 87.1177 | 0 | 87.1177 | 6.83% | 0 | 23.8492 | 10.0398 | 16.06% | 38.5372
6993 | 784 | 363 | 55 | 0.6 | 20.4 | 0 | 0 | 0 | 52.3377 | 35.578 | 0 | 0 | 35.578 | 0 | 0 | 0 | 0 | 0 | 52.3377 | 0 | 139.4554 | 10.93% | 0 | 3.4243 | 6.25 | 10% | 39.0024
6994 | 881 | 532 | 59 | 1.1 | 22.6 | 0 | 0 | 0 | 217.0471 | 39.118 | 11.9273 | 0 | 39.118 | 0 | 0 | 0 | 0 | 0 | 217.0471 | 0 | 356.5025 | 27.95% | 0 | 0 | 6.25 | 10% | 39.118
6995 | 926 | 651 | 63 | 2.7 | 23.9 | 0 | 0 | 0 | 247.8645 | 38.2726 | 25.3893 | 0 | 38.2726 | 0 | 0 | 0 | 0 | 0 | 247.8645 | 0 | 604.367 | 47.38% | 0 | 0 | 6.25 | 10% | 38.2726
6996 | 926 | 709 | 75 | 4.4 | 24.9 | 0 | 0 | 0 | 254.4653 | 59.9628 | 11.0771 | 23.5801 | 36.3827 | 0 | 0 | 0 | 0 | 0 | 254.4653 | 0 | 858.8323 | 67.33% | 23.5801 | 0 | 27.556 | 44.09% | 36.3827
6997 | 804 | 665 | 117 | 5.2 | 25 | 0 | 0 | 0 | 219.8098 | 60.4301 | 8.5353 | 25 | 35.4301 | 0 | 0 | 0 | 0 | 0 | 219.8098 | 0 | 1078.6421 | 84.57% | 25 | 0 | 50.145 | 80.23% | 35.4301
6998 | 330 | 436 | 225 | 5.7 | 25.6 | 0 | 0 | 0 | 76.5265 | 41.9402 | 0 | 6.7566 | 35.1836 | 0 | 0 | 0 | 0 | 0 | 76.5265 | 0 | 1155.1686 | 90.57% | 6.7566 | 0 | 56.25 | 90% | 35.1836
6999 | 355 | 372 | 189 | 6.7 | 25.1 | 0 | 0 | 0 | 79.5436 | 35.3062 | 4.2481 | 0 | 35.3062 | 0 | 0 | 0 | 0 | 0 | 79.5436 | 0 | 1234.7122 | 96.8% | 0 | 0 | 56.25 | 90% | 35.3062
7000 | 231 | 234 | 142 | 4.3 | 25.1 | 0 | 0 | 0 | 40.798 | 23.6049 | 0 | 0 | 23.6049 | 0 | 0 | 0 | 0 | 0 | 40.798 | 0 | 1275.5102 | 100% | 0 | 7.2498 | 48.2264 | 77.16% | 30.8547
7001 | 150 | 122 | 90 | 4.1 | 24.2 | 0 | 0 | 0 | 0 | 12.6332 | 0 | 0 | 12.6332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 20.5581 | 32.89% | 37.6332
7002 | 5 | 8 | 7 | 1.8 | 21.9 | 0 | 0 | 0 | 0 | 0.064018 | 0 | 0 | 0.064018 | 0 | 0 | 0 | 98.2334 | 38.6041 | 0 | 98.2334 | 1177.2768 | 92.3% | 0 | 0 | 20.5581 | 32.89% | 38.6681
7003 | 0 | 0 | 0 | 3.9 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7369 | 35.8591 | 0 | 91.7369 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 35.8591
7004 | 0 | 0 | 0 | 3 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7005 | 0 | 0 | 0 | 2.8 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7006 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7007 | 0 | 0 | 0 | 7 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7008 | 0 | 0 | 0 | 8.7 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7009 | 0 | 0 | 0 | 7.9 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7010 | 0 | 0 | 0 | 5.6 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7011 | 0 | 0 | 0 | 4.5 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7012 | 0 | 0 | 0 | 6.1 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7013 | 0 | 0 | 0 | 6.8 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7014 | 0 | 0 | 0 | 3.6 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7015 | 2 | 6 | 6 | 3.6 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 0
7016 | 0 | 30 | 30 | 3.7 | 13.2 | 0 | 0 | 0 | 0 | 1.4839 | 0 | 0 | 1.4839 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 1.4839
7017 | 0 | 137 | 137 | 1.6 | 13.2 | 0 | 0 | 0 | 0 | 9.715 | 0 | 0 | 9.715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.5399 | 85.11% | 0 | 0 | 20.5581 | 32.89% | 9.715
7018 | 0 | 96 | 95 | 2.5 | 14.6 | 0 | 0 | 0 | 0 | 5.8936 | 0 | 0 | 5.8936 | 0 | 0 | 0 | 83.7899 | 32.749 | 0 | 83.7899 | 1001.75 | 78.54% | 2.7919 | 0 | 23.0807 | 36.93% | 35.8507
7019 | 0 | 136 | 134 | 1.9 | 14.9 | 0 | 0 | 0 | 0 | 8.5627 | 0 | 0 | 8.5627 | 0 | 0 | 0 | 70.3388 | 26.8938 | 0 | 70.3388 | 931.4112 | 73.02% | 0 | 0 | 23.0807 | 36.93% | 35.4566
7020 | 1 | 213 | 210 | 3 | 15.6 | 0 | 0 | 0 | 0 | 14.1832 | 0 | 0 | 14.1832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 931.4112 | 73.02% | 0 | 0 | 23.0807 | 36.93% | 14.1832
7021 | 10 | 269 | 258 | 3.7 | 16 | 0 | 0 | 0 | 0 | 18.5419 | 0 | 0 | 18.5419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 931.4112 | 73.02% | 0 | 0 | 23.0807 | 36.93% | 18.5419
7022 | 424 | 515 | 249 | 3.8 | 17.4 | 0 | 0 | 0 | 105.7038 | 52.4974 | 0 | 20.7286 | 31.7687 | 0 | 0 | 0 | 0 | 0 | 105.7038 | 0 | 1037.115 | 81.31% | 20.7286 | 0 | 41.8103 | 66.9% | 31.7687
7023 | 282 | 404 | 252 | 5 | 18.4 | 0 | 0 | 0 | 60.2698 | 39.6468 | 0 | 7.3516 | 32.2952 | 0 | 0 | 0 | 0 | 0 | 60.2698 | 0 | 1097.3848 | 86.03% | 7.3516 | 0 | 48.4529 | 77.52% | 32.2952
7024 | 582 | 347 | 142 | 4 | 19.3 | 0 | 0 | 0 | 132.6473 | 43.3366 | 0 | 8.6293 | 34.7073 | 0 | 0 | 0 | 0 | 0 | 132.6473 | 0 | 1230.0321 | 96.43% | 8.6293 | 0 | 56.25 | 90% | 34.7073
7025 | 298 | 121 | 66 | 3.2 | 18.2 | 0 | 0 | 0 | 45.4781 | 16.9679 | 0 | 0 | 16.9679 | 0 | 0 | 0 | 0 | 0 | 45.4781 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 16.9679
7026 | 38 | 13 | 9 | 1.5 | 16.7 | 0 | 0 | 0 | 0 | 0.71338 | 0 | 0 | 0.71338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 5.5859 | 50.0679 | 80.11% | 6.2993
7027 | 0 | 0 | 0 | 2.8 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.0679 | 80.11% | 0
7028 | 0 | 0 | 0 | 0.9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.0679 | 80.11% | 0
7029 | 0 | 0 | 0 | 1.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.0679 | 80.11% | 0
7030 | 0 | 0 | 0 | 0.9 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.0679 | 80.11% | 0
7031 | 0 | 0 | 0 | 2.2 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.0679 | 80.11% | 0
7032 | 0 | 0 | 0 | 2.6 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.0679 | 80.11% | 0
7033 | 0 | 0 | 0 | 1.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.0679 | 80.11% | 0
7034 | 0 | 0 | 0 | 2.2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.0679 | 80.11% | 0
7035 | 0 | 0 | 0 | 2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 50.0679 | 80.11% | 0
7036 | 0 | 0 | 0 | 2.1 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4117 | 38.3576 | 0 | 96.4117 | 1179.0985 | 92.44% | 0 | 0 | 50.0679 | 80.11% | 38.3576
7037 | 0 | 0 | 0 | 1.2 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8878 | 41.629 | 0 | 103.8878 | 1075.2107 | 84.3% | 0 | 0 | 50.0679 | 80.11% | 41.629
7038 | 0 | 0 | 0 | 0.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6441 | 42.4089 | 0 | 105.6441 | 969.5665 | 76.01% | 0 | 0 | 50.0679 | 80.11% | 42.4089
7039 | 19 | 11 | 9 | 0.9 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.8882 | 43.3894 | 0 | 107.8882 | 861.6783 | 67.56% | 0 | 0 | 50.0679 | 80.11% | 43.3894
7040 | 492 | 161 | 55 | 1.3 | 11.8 | 0 | 0 | 0 | 61.9021 | 13.2855 | 0 | 0 | 13.2855 | 0 | 0 | 0 | 0 | 0 | 61.9021 | 0 | 923.5804 | 72.41% | 0 | 0 | 50.0679 | 80.11% | 13.2855
7041 | 330 | 231 | 101 | 0.8 | 13.4 | 0 | 0 | 0 | 56.5905 | 22.5604 | 0 | 0 | 22.5604 | 0 | 0 | 0 | 0 | 0 | 56.5905 | 0 | 980.1709 | 76.85% | 0 | 0 | 50.0679 | 80.11% | 22.5604
7042 | 169 | 285 | 192 | 1.2 | 14.1 | 0 | 0 | 0 | 0 | 24.6608 | 0 | 0 | 24.6608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980.1709 | 76.85% | 0 | 0 | 50.0679 | 80.11% | 24.6608
7043 | 93 | 338 | 275 | 0.8 | 15.6 | 0 | 0 | 0 | 0 | 26.8343 | 0 | 0 | 26.8343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980.1709 | 76.85% | 0 | 0 | 50.0679 | 80.11% | 26.8343
7044 | 108 | 351 | 273 | 0.8 | 16.5 | 0 | 0 | 0 | 0 | 29.1815 | 0 | 0 | 29.1815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980.1709 | 76.85% | 0 | 0 | 50.0679 | 80.11% | 29.1815
7045 | 263 | 549 | 363 | 1.2 | 17.6 | 0 | 0 | 0 | 60.9766 | 47.4779 | 0 | 6.8419 | 40.636 | 0 | 0 | 0 | 0 | 0 | 60.9766 | 0 | 1041.1475 | 81.63% | 6.8419 | 0 | 56.25 | 90% | 40.636
7046 | 14 | 383 | 369 | 0.7 | 18.4 | 0 | 0 | 0 | 0 | 27.292 | 0 | 0 | 27.292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1041.1475 | 81.63% | 0 | 0 | 56.25 | 90% | 27.292
7047 | 4 | 254 | 250 | 1.4 | 18.3 | 0 | 0 | 0 | 0 | 17.6398 | 0 | 0 | 17.6398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1041.1475 | 81.63% | 0 | 20.178 | 33.9183 | 54.27% | 37.8178
7048 | 28 | 200 | 188 | 4.5 | 17.4 | 0 | 0 | 0 | 0 | 14.7304 | 0 | 0 | 14.7304 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 1041.1475 | 81.63% | 0 | 25 | 6.25 | 10% | 39.7304
7049 | 44 | 87 | 80 | 4.3 | 16.2 | 0 | 0 | 0 | 0 | 7.0444 | 0 | 0 | 7.0444 | 0 | 0 | 0 | 96.4601 | 38.1875 | 0 | 96.4601 | 944.6874 | 74.06% | 0 | 0 | 6.25 | 10% | 45.2319
7050 | 16 | 9 | 8 | 3 | 15.2 | 0 | 0 | 0 | 0 | 0.24608 | 0 | 0 | 0.24608 | 0 | 0 | 0 | 108.6575 | 43.5305 | 0 | 108.6575 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 43.7765
7051 | 0 | 0 | 0 | 2.9 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 0
7052 | 0 | 0 | 0 | 2.9 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 0
7053 | 0 | 0 | 0 | 1.7 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 0
7054 | 0 | 0 | 0 | 2 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 0
7055 | 0 | 0 | 0 | 1.5 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 0
7056 | 0 | 0 | 0 | 1.2 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 0
7057 | 0 | 0 | 0 | 2.2 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 0
7058 | 0 | 0 | 0 | 1.4 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 0
7059 | 0 | 0 | 0 | 1.6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 836.0299 | 65.54% | 0 | 0 | 6.25 | 10% | 0
7060 | 0 | 0 | 0 | 1.4 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1204 | 39.5038 | 0 | 99.1204 | 736.9095 | 57.77% | 0 | 0 | 6.25 | 10% | 39.5038
7061 | 0 | 0 | 0 | 1.7 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.8366 | 42.8741 | 0 | 106.8366 | 630.0729 | 49.4% | 0 | 0 | 6.25 | 10% | 42.8741
7062 | 0 | 0 | 0 | 1.8 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.4829 | 44.03 | 0 | 109.4829 | 520.59 | 40.81% | 0 | 0 | 6.25 | 10% | 44.03
7063 | 0 | 1 | 2 | 1.8 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.7299 | 44.5843 | 0 | 110.7299 | 409.8601 | 32.13% | 0 | 0 | 6.25 | 10% | 44.5843
7064 | 0 | 6 | 6 | 1.8 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.8601 | 32.13% | 0 | 0 | 6.25 | 10% | 0
7065 | 0 | 24 | 24 | 2.7 | 10.8 | 0 | 0 | 0 | 0 | 1.1719 | 0 | 0 | 1.1719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.8601 | 32.13% | 0 | 0 | 6.25 | 10% | 1.1719
7066 | 0 | 45 | 45 | 3.6 | 10.4 | 0 | 0 | 0 | 0 | 2.5526 | 0 | 0 | 2.5526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.8601 | 32.13% | 0 | 0 | 6.25 | 10% | 2.5526
7067 | 0 | 93 | 92 | 2.7 | 10.8 | 0 | 0 | 0 | 0 | 5.6729 | 0 | 0 | 5.6729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.8601 | 32.13% | 0 | 0 | 6.25 | 10% | 5.6729
7068 | 0 | 89 | 88 | 2 | 11.2 | 0 | 0 | 0 | 0 | 5.3581 | 0 | 0 | 5.3581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.8601 | 32.13% | 0 | 0 | 6.25 | 10% | 5.3581
7069 | 0 | 126 | 125 | 1.8 | 11.5 | 0 | 0 | 0 | 0 | 7.9303 | 0 | 0 | 7.9303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.8601 | 32.13% | 0 | 0 | 6.25 | 10% | 7.9303
7070 | 0 | 71 | 71 | 1.1 | 11.4 | 0 | 0 | 0 | 0 | 4.2168 | 0 | 0 | 4.2168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.8601 | 32.13% | 0 | 0 | 6.25 | 10% | 4.2168
7071 | 0 | 59 | 59 | 1.4 | 11.3 | 0 | 0 | 0 | 0 | 3.4458 | 0 | 0 | 3.4458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.8601 | 32.13% | 0 | 0 | 6.25 | 10% | 3.4458
7072 | 0 | 40 | 40 | 0.9 | 11 | 0 | 0 | 0 | 0 | 2.2134 | 0 | 0 | 2.2134 | 0 | 0 | 0 | 105.0426 | 42.1077 | 0 | 105.0426 | 304.8175 | 23.9% | 0 | 0 | 6.25 | 10% | 44.3211
7073 | 0 | 8 | 9 | 2.9 | 10.9 | 0 | 0 | 0 | 0 | 0.20329 | 0 | 0 | 0.20329 | 0 | 0 | 0 | 114.2995 | 46.1456 | 0 | 114.2995 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 46.3488
7074 | 0 | 0 | 0 | 1.8 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7075 | 0 | 0 | 0 | 1.3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7076 | 0 | 0 | 0 | 2.2 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7077 | 0 | 0 | 0 | 1.7 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7078 | 0 | 0 | 0 | 1.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7079 | 0 | 0 | 0 | 0.7 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7080 | 0 | 0 | 0 | 0.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7081 | 0 | 0 | 0 | 1.4 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7082 | 0 | 0 | 0 | 0.9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7083 | 0 | 0 | 0 | 0.8 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7084 | 0 | 0 | 0 | 1.2 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7085 | 0 | 0 | 0 | 1.3 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.518 | 14.94% | 0 | 0 | 6.25 | 10% | 0
7086 | 0 | 0 | 0 | 0.9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.0644 | 44.3475 | 0 | 110.0644 | 80.4536 | 6.308% | 0 | 0 | 6.25 | 10% | 44.3475
7087 | 53 | 14 | 10 | 1.8 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4536 | 31.4228 | 0 | 80.4536 | 0 | 0% | 0 | 0 | 6.25 | 10% | 31.4228
7088 | 513 | 159 | 50 | 1.2 | 10.8 | 0 | 0 | 0 | 64.2965 | 13.3555 | 0 | 0 | 13.3555 | 0 | 0 | 0 | 0 | 0 | 64.2965 | 0 | 64.2965 | 5.041% | 0 | 0 | 6.25 | 10% | 13.3555
7089 | 734 | 357 | 78 | 1.9 | 13.3 | 0 | 0 | 0 | 145.8912 | 37.2934 | 0 | 0 | 37.2934 | 0 | 0 | 0 | 0 | 0 | 145.8912 | 0 | 210.1876 | 16.48% | 0 | 0 | 6.25 | 10% | 37.2934
7090 | 712 | 539 | 170 | 4 | 14.1 | 0 | 0 | 0 | 169.2918 | 50.9543 | 3.919 | 5.3367 | 45.6177 | 0 | 0 | 0 | 0 | 0 | 169.2918 | 0 | 379.4794 | 29.75% | 5.3367 | 0 | 11.072 | 17.72% | 45.6177
7091 | 613 | 562 | 178 | 4.6 | 14.8 | 0 | 0 | 0 | 155.6209 | 44.2556 | 12.8956 | 0 | 44.2556 | 0 | 0 | 0 | 0 | 0 | 155.6209 | 0 | 535.1003 | 41.95% | 0 | 0 | 11.072 | 17.72% | 44.2556
7092 | 886 | 707 | 118 | 5.3 | 16.3 | 0 | 0 | 0 | 240.6799 | 68.2919 | 3.7081 | 25 | 43.2919 | 0 | 0 | 0 | 0 | 0 | 240.6799 | 0 | 775.7802 | 60.82% | 25 | 0 | 33.661 | 53.86% | 43.2919
7093 | 771 | 669 | 158 | 5.1 | 17.1 | 0 | 0 | 0 | 208.9289 | 67.6443 | 4.3557 | 25 | 42.6443 | 0 | 0 | 0 | 0 | 0 | 208.9289 | 0 | 984.709 | 77.2% | 25 | 0 | 56.25 | 90% | 42.6443
7094 | 199 | 360 | 233 | 3.9 | 17 | 0 | 0 | 0 | 39.1495 | 32.9519 | 0 | 0 | 32.9519 | 0 | 0 | 0 | 0 | 0 | 39.1495 | 0 | 1023.8585 | 80.27% | 0 | 9.5378 | 45.6942 | 73.11% | 42.4897
7095 | 9 | 181 | 175 | 4.8 | 16.5 | 0 | 0 | 0 | 0 | 12.3271 | 0 | 0 | 12.3271 | 0 | 0 | 0 | 70.8324 | 27.0578 | 0 | 70.8324 | 953.026 | 74.72% | 0 | 3.0309 | 42.3399 | 67.74% | 42.4159
7096 | 1 | 53 | 53 | 6.6 | 15.1 | 0 | 0 | 0 | 0 | 3.0937 | 0 | 0 | 3.0937 | 0 | 0 | 0 | 104.0569 | 41.5365 | 0 | 104.0569 | 848.9691 | 66.56% | 0 | 0 | 42.3399 | 67.74% | 44.6303
7097 | 0 | 16 | 16 | 2.4 | 14.1 | 0 | 0 | 0 | 0 | 0.63614 | 0 | 0 | 0.63614 | 0 | 0 | 0 | 114.7179 | 46.2155 | 0 | 114.7179 | 734.2512 | 57.57% | 0 | 0 | 42.3399 | 67.74% | 46.8516
7098 | 0 | 1 | 1 | 2.6 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.5846 | 45.3322 | 0 | 112.5846 | 621.6666 | 48.74% | 0 | 0 | 42.3399 | 67.74% | 45.3322
7099 | 0 | 0 | 0 | 2.5 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.8702 | 41.1067 | 0 | 102.8702 | 518.7964 | 40.67% | 0 | 0 | 42.3399 | 67.74% | 41.1067
7100 | 0 | 0 | 0 | 2.1 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3562 | 35.2291 | 0 | 89.3562 | 429.4402 | 33.67% | 0 | 0 | 42.3399 | 67.74% | 35.2291
7101 | 0 | 0 | 0 | 2.7 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.4402 | 33.67% | 0 | 0 | 42.3399 | 67.74% | 0
7102 | 0 | 0 | 0 | 4.1 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.4402 | 33.67% | 0 | 0 | 42.3399 | 67.74% | 0
7103 | 0 | 0 | 0 | 5.1 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.4402 | 33.67% | 0 | 0 | 42.3399 | 67.74% | 0
7104 | 0 | 0 | 0 | 5.4 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.4402 | 33.67% | 0 | 0 | 42.3399 | 67.74% | 0
7105 | 0 | 0 | 0 | 3.3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.4402 | 33.67% | 0 | 0 | 42.3399 | 67.74% | 0
7106 | 0 | 0 | 0 | 2.2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.4402 | 33.67% | 0 | 0 | 42.3399 | 67.74% | 0
7107 | 0 | 0 | 0 | 3.4 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 429.4402 | 33.67% | 0 | 0 | 42.3399 | 67.74% | 0
7108 | 0 | 0 | 0 | 4.2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5662 | 40.1193 | 0 | 100.5662 | 328.874 | 25.78% | 0 | 0 | 42.3399 | 67.74% | 40.1193
7109 | 0 | 0 | 0 | 4.6 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.2239 | 43.4576 | 0 | 108.2239 | 220.65 | 17.3% | 0 | 0 | 42.3399 | 67.74% | 43.4576
7110 | 0 | 0 | 0 | 2.3 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.7354 | 44.1372 | 0 | 109.7354 | 110.9146 | 8.696% | 0 | 0 | 42.3399 | 67.74% | 44.1372
7111 | 75 | 17 | 10 | 1.4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.9146 | 44.6595 | 0 | 110.9146 | 0 | 0% | 0 | 0 | 42.3399 | 67.74% | 44.6595
7112 | 595 | 169 | 46 | 1.5 | 12.4 | 0 | 0 | 0 | 76.2456 | 14.5417 | 0 | 0 | 14.5417 | 0 | 0 | 0 | 0 | 0 | 76.2456 | 0 | 76.2456 | 5.978% | 0 | 25 | 14.6715 | 23.47% | 39.5417
7113 | 788 | 361 | 65 | 1 | 16 | 0 | 0 | 0 | 0 | 37.3607 | 0 | 0 | 37.3607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.2456 | 5.978% | 0 | 7.6094 | 6.25 | 10% | 44.9701
7114 | 888 | 517 | 60 | 1 | 17.5 | 0 | 0 | 0 | 217.2082 | 44.3559 | 7.9454 | 0 | 44.3559 | 0 | 0 | 0 | 0 | 0 | 217.2082 | 0 | 293.4538 | 23.01% | 0 | 0 | 6.25 | 10% | 44.3559
7115 | 933 | 633 | 62 | 2.1 | 18.5 | 0 | 0 | 0 | 248.6225 | 42.9813 | 21.5424 | 0 | 42.9813 | 0 | 0 | 0 | 0 | 0 | 248.6225 | 0 | 542.0762 | 42.5% | 0 | 0 | 6.25 | 10% | 42.9813
7116 | 949 | 691 | 65 | 1.2 | 19.3 | 0 | 0 | 0 | 255.4223 | 42.0844 | 27.0823 | 0 | 42.0844 | 0 | 0 | 0 | 0 | 0 | 255.4223 | 0 | 797.4985 | 62.52% | 0 | 0 | 6.25 | 10% | 42.0844
7117 | 943 | 682 | 67 | 2.7 | 20.1 | 0 | 0 | 0 | 0 | 51.0602 | 20.9398 | 9.3824 | 41.6778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 797.4985 | 62.52% | 9.3824 | 0 | 14.7276 | 23.56% | 41.6778
7118 | 921 | 611 | 63 | 3.9 | 20.6 | 0 | 0 | 0 | 250.8719 | 66.3351 | 3.1631 | 25 | 41.3351 | 0 | 0 | 0 | 0 | 0 | 250.8719 | 0 | 1048.3704 | 82.19% | 25 | 0 | 37.3166 | 59.71% | 41.3351
7119 | 874 | 486 | 59 | 3.6 | 20.6 | 0 | 0 | 0 | 227.1398 | 60.0536 | 0 | 18.9093 | 41.1443 | 0 | 0 | 0 | 0 | 0 | 227.1398 | 0 | 1275.5102 | 100% | 18.9093 | 0 | 54.4022 | 87.04% | 41.1443
7120 | 784 | 316 | 48 | 4.7 | 19.7 | 0 | 0 | 0 | 0 | 45.5263 | 0 | 2.045 | 43.4813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 2.045 | 0 | 56.25 | 90% | 43.4813
7121 | 525 | 124 | 30 | 2.3 | 19 | 0 | 0 | 0 | 0 | 21.9456 | 0 | 0 | 21.9456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 24.1818 | 29.4872 | 47.18% | 46.1274
7122 | 14 | 6 | 4 | 2 | 15.9 | 0 | 0 | 0 | 0 | 0.021868 | 0 | 0 | 0.021868 | 0 | 0 | 0 | 112.5659 | 45.1919 | 0 | 112.5659 | 1162.9443 | 91.17% | 0 | 0 | 29.4872 | 47.18% | 45.2138
7123 | 0 | 0 | 0 | 1.4 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.4598 | 41.3073 | 0 | 103.4598 | 1059.4846 | 83.06% | 0 | 0 | 29.4872 | 47.18% | 41.3073
7124 | 0 | 0 | 0 | 1.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.3711 | 37.8228 | 0 | 95.3711 | 964.1135 | 75.59% | 0 | 0 | 29.4872 | 47.18% | 37.8228
7125 | 0 | 0 | 0 | 1.3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7608 | 35.3967 | 0 | 89.7608 | 874.3527 | 68.55% | 0 | 0 | 29.4872 | 47.18% | 35.3967
7126 | 0 | 0 | 0 | 0.7 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6357 | 33.1976 | 0 | 84.6357 | 789.717 | 61.91% | 0 | 0 | 29.4872 | 47.18% | 33.1976
7127 | 0 | 0 | 0 | 1.2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6078 | 31.8718 | 0 | 81.6078 | 708.1092 | 55.52% | 0 | 0 | 29.4872 | 47.18% | 31.8718
7128 | 0 | 0 | 0 | 2.7 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.1898 | 27.3147 | 0 | 71.1898 | 636.9194 | 49.93% | 0 | 0 | 29.4872 | 47.18% | 27.3147
7129 | 0 | 0 | 0 | 2.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.989 | 0 | 38.2653 | 598.6541 | 46.93% | 0 | 0 | 29.4872 | 47.18% | 12.989
7130 | 0 | 0 | 0 | 1.9 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.855 | 31.5348 | 0 | 80.855 | 517.799 | 40.6% | 0 | 0 | 29.4872 | 47.18% | 31.5348
7131 | 0 | 0 | 0 | 0.9 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1339 | 34.7407 | 0 | 88.1339 | 429.6651 | 33.69% | 0 | 0 | 29.4872 | 47.18% | 34.7407
7132 | 0 | 0 | 0 | 1.1 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.7489 | 40.2488 | 0 | 100.7489 | 328.9161 | 25.79% | 0 | 0 | 29.4872 | 47.18% | 40.2488
7133 | 0 | 0 | 0 | 1.6 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0659 | 43.4256 | 0 | 108.0659 | 220.8503 | 17.31% | 0 | 0 | 29.4872 | 47.18% | 43.4256
7134 | 0 | 0 | 0 | 1 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.0604 | 44.3113 | 0 | 110.0604 | 110.7899 | 8.686% | 0 | 0 | 29.4872 | 47.18% | 44.3113
7135 | 81 | 15 | 8 | 1.4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.7899 | 44.6024 | 0 | 110.7899 | 0 | 0% | 0 | 0 | 29.4872 | 47.18% | 44.6024
7136 | 614 | 161 | 37 | 0.5 | 13.7 | 0 | 0 | 0 | 0 | 13.8037 | 0 | 0 | 13.8037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 20.9962 | 6.25 | 10% | 34.7999
7137 | 821 | 353 | 49 | 0.7 | 17.2 | 0 | 0 | 0 | 0 | 36.76 | 7.1054e-15 | 0 | 36.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 36.76
7138 | 905 | 517 | 55 | 0.6 | 20.2 | 0 | 0 | 0 | 221.5477 | 44.1776 | 7.4564 | 0 | 44.1776 | 0 | 0 | 0 | 0 | 0 | 221.5477 | 0 | 221.5477 | 17.37% | 0 | 0 | 6.25 | 10% | 44.1776
7139 | 945 | 633 | 59 | 1.4 | 20.9 | 0 | 0 | 0 | 251.9311 | 42.7097 | 20.7345 | 0 | 42.7097 | 0 | 0 | 0 | 0 | 0 | 251.9311 | 0 | 473.4788 | 37.12% | 0 | 0 | 6.25 | 10% | 42.7097
7140 | 960 | 690 | 62 | 1.2 | 21.6 | 0 | 0 | 0 | 0 | 41.7641 | 27.1935 | 0 | 41.7641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 473.4788 | 37.12% | 0 | 0 | 6.25 | 10% | 41.7641
7141 | 956 | 682 | 62 | 1.8 | 22.3 | 0 | 0 | 0 | 265.853 | 49.8961 | 21.208 | 8.7698 | 41.1262 | 0 | 0 | 0 | 0 | 0 | 265.853 | 0 | 739.3318 | 57.96% | 8.7698 | 0 | 14.1741 | 22.68% | 41.1262
7142 | 932 | 610 | 61 | 3.1 | 22.5 | 0 | 0 | 0 | 254.4709 | 65.675 | 3.1936 | 25 | 40.675 | 0 | 0 | 0 | 0 | 0 | 254.4709 | 0 | 993.8027 | 77.91% | 25 | 0 | 36.7631 | 58.82% | 40.675
7143 | 880 | 482 | 56 | 3.2 | 22.3 | 0 | 0 | 0 | 228.676 | 59.4995 | 0 | 19.0961 | 40.4034 | 0 | 0 | 0 | 0 | 0 | 228.676 | 0 | 1222.4788 | 95.84% | 19.0961 | 0 | 54.0175 | 86.43% | 40.4034
7144 | 780 | 311 | 48 | 3.7 | 21.5 | 0 | 0 | 0 | 10.6277 | 44.7418 | 0 | 2.4707 | 42.271 | 0 | 0 | 0 | 0 | 0 | 10.6277 | 0 | 1233.1064 | 96.68% | 2.4707 | 0 | 56.25 | 90% | 42.271
7145 | 529 | 123 | 31 | 3.3 | 20.1 | 0 | 0 | 0 | 0 | 22.1654 | 0 | 0 | 22.1654 | 0 | 0 | 0 | 59.7676 | 22.139 | 0 | 59.7676 | 1173.3388 | 91.99% | 0 | 0 | 56.25 | 90% | 44.3044
7146 | 10 | 6 | 4 | 2.3 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.4147 | 43.3183 | 0 | 108.4147 | 1064.9241 | 83.49% | 0 | 0 | 56.25 | 90% | 43.3183
7147 | 0 | 0 | 0 | 0.6 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.825 | 39.6848 | 0 | 99.825 | 965.0992 | 75.66% | 0 | 0 | 56.25 | 90% | 39.6848
7148 | 0 | 0 | 0 | 0.5 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3185 | 17.7672 | 0 | 49.3185 | 915.7807 | 71.8% | 0 | 19.0459 | 35.1713 | 56.27% | 36.8131
7149 | 0 | 0 | 0 | 0.5 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4097 | 34.7937 | 0 | 88.4097 | 827.371 | 64.87% | 0 | 0 | 35.1713 | 56.27% | 34.7937
7150 | 0 | 0 | 0 | 0.6 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2212 | 32.5473 | 0 | 83.2212 | 744.1498 | 58.34% | 0 | 0 | 35.1713 | 56.27% | 32.5473
7151 | 0 | 0 | 0 | 0.9 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1669 | 30.7925 | 0 | 79.1669 | 664.9829 | 52.13% | 0 | 0 | 35.1713 | 56.27% | 30.7925
7152 | 0 | 0 | 0 | 1 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9948 | 29.858 | 0 | 76.9948 | 587.9881 | 46.1% | 0 | 0 | 35.1713 | 56.27% | 29.858
7153 | 0 | 0 | 0 | 0.8 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3716 | 29.5947 | 0 | 76.3716 | 511.6165 | 40.11% | 0 | 0 | 35.1713 | 56.27% | 29.5947
7154 | 0 | 0 | 0 | 1.2 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.9318 | 29.3928 | 0 | 75.9318 | 435.6846 | 34.16% | 0 | 0 | 35.1713 | 56.27% | 29.3928
7155 | 0 | 0 | 0 | 0.7 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.6996 | 30.1713 | 0 | 77.6996 | 357.985 | 28.07% | 0 | 0 | 35.1713 | 56.27% | 30.1713
7156 | 0 | 0 | 0 | 1.1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7304 | 31.9317 | 0 | 81.7304 | 276.2546 | 21.66% | 0 | 0 | 35.1713 | 56.27% | 31.9317
7157 | 0 | 0 | 0 | 1.2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6398 | 34.0541 | 0 | 86.6398 | 189.6148 | 14.87% | 0 | 0 | 35.1713 | 56.27% | 34.0541
7158 | 0 | 0 | 0 | 2.1 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8444 | 36.742 | 0 | 92.8444 | 96.7704 | 7.587% | 0 | 0 | 35.1713 | 56.27% | 36.742
7159 | 76 | 14 | 7 | 2.1 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7704 | 38.4383 | 0 | 96.7704 | 0 | 0% | 0 | 0 | 35.1713 | 56.27% | 38.4383
7160 | 628 | 161 | 35 | 1.3 | 16 | 0 | 0 | 0 | 80.2787 | 13.7987 | 0 | 0 | 13.7987 | 0 | 0 | 0 | 0 | 0 | 80.2787 | 0 | 80.2787 | 6.294% | 0 | 24.8457 | 7.6737 | 12.28% | 38.6445
7161 | 822 | 351 | 49 | 2.1 | 18.4 | 0 | 0 | 0 | 163.516 | 37.3344 | 0 | 0 | 37.3344 | 0 | 0 | 0 | 0 | 0 | 163.516 | 0 | 243.7947 | 19.11% | 0 | 1.2864 | 6.25 | 10% | 38.6208
7162 | 909 | 517 | 56 | 1.4 | 21.5 | 0 | 0 | 0 | 221.8314 | 38.6166 | 14.0528 | 0 | 38.6166 | 0 | 0 | 0 | 0 | 0 | 221.8314 | 0 | 465.6262 | 36.51% | 0 | 0 | 6.25 | 10% | 38.6166
7163 | 948 | 632 | 60 | 1.7 | 22 | 0 | 0 | 0 | 252.1553 | 37.82 | 26.0318 | 0 | 37.82 | 0 | 0 | 0 | 0 | 0 | 252.1553 | 0 | 717.7815 | 56.27% | 0 | 0 | 6.25 | 10% | 37.82
7164 | 960 | 686 | 62 | 1.5 | 22.7 | 0 | 0 | 0 | 140.5406 | 36.0805 | 33.1594 | 0 | 36.0805 | 0 | 0 | 0 | 0 | 0 | 140.5406 | 0 | 858.322 | 67.29% | 0 | 0 | 6.25 | 10% | 36.0805
7165 | 952 | 676 | 62 | 1.3 | 23.9 | 0 | 0 | 0 | 0 | 35.0332 | 34.4298 | 0 | 35.0332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 858.322 | 67.29% | 0 | 0 | 6.25 | 10% | 35.0332
7166 | 927 | 604 | 61 | 2.5 | 24.1 | 0 | 0 | 0 | 0 | 59.7129 | 7.8014 | 25 | 34.7129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 858.322 | 67.29% | 25 | 0 | 28.839 | 46.14% | 34.7129
7167 | 878 | 477 | 56 | 3.3 | 24 | 0 | 0 | 0 | 227.5886 | 59.0451 | 0 | 24.3865 | 34.6586 | 0 | 0 | 0 | 0 | 0 | 227.5886 | 0 | 1085.9107 | 85.14% | 24.3865 | 0 | 50.8737 | 81.4% | 34.6586
7168 | 777 | 306 | 47 | 3.2 | 23.2 | 0 | 0 | 0 | 0 | 42.7576 | 1.2781 | 5.9501 | 36.8075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.9107 | 85.14% | 5.9501 | 0 | 56.25 | 90% | 36.8075
7169 | 525 | 117 | 29 | 2.8 | 21.9 | 0 | 0 | 0 | 0 | 21.347 | 0 | 0 | 21.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.9107 | 85.14% | 0 | 17.5439 | 36.8335 | 58.93% | 38.891
7170 | 9 | 5 | 3 | 1.2 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.6021 | 32.4854 | 0 | 83.6021 | 1002.3086 | 78.58% | 0 | 6.1494 | 30.0278 | 48.04% | 38.6347
7171 | 0 | 0 | 0 | 1.4 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0625 | 36.2518 | 0 | 92.0625 | 910.2461 | 71.36% | 0 | 0 | 30.0278 | 48.04% | 36.2518
7172 | 0 | 0 | 0 | 1.8 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1452 | 34.2004 | 0 | 87.1452 | 823.1009 | 64.53% | 0 | 0 | 30.0278 | 48.04% | 34.2004
7173 | 0 | 0 | 0 | 1.9 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3197 | 32.1197 | 0 | 82.3197 | 740.7812 | 58.08% | 0 | 0 | 30.0278 | 48.04% | 32.1197
7174 | 0 | 0 | 0 | 1.7 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.5247 | 30.0348 | 0 | 77.5247 | 663.2565 | 52% | 0 | 0 | 30.0278 | 48.04% | 30.0348
7175 | 0 | 0 | 0 | 1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.188 | 28.6129 | 0 | 74.188 | 589.0685 | 46.18% | 0 | 0 | 30.0278 | 48.04% | 28.6129
7176 | 0 | 0 | 0 | 0.7 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2898 | 27.8023 | 0 | 72.2898 | 516.7787 | 40.52% | 0 | 0 | 30.0278 | 48.04% | 27.8023
7177 | 0 | 0 | 0 | 1.2 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.6149 | 27.0809 | 0 | 70.6149 | 446.1638 | 34.98% | 0 | 0 | 30.0278 | 48.04% | 27.0809
7178 | 0 | 0 | 0 | 2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.0495 | 26.8205 | 0 | 70.0495 | 376.1143 | 29.49% | 0 | 0 | 30.0278 | 48.04% | 26.8205
7179 | 0 | 0 | 0 | 2.1 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.5491 | 27.0196 | 0 | 70.5491 | 305.5652 | 23.96% | 0 | 0 | 30.0278 | 48.04% | 27.0196
7180 | 0 | 0 | 0 | 1.6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.8925 | 27.6394 | 0 | 71.8925 | 233.6727 | 18.32% | 0 | 0 | 30.0278 | 48.04% | 27.6394
7181 | 0 | 0 | 0 | 1.9 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3234 | 28.2647 | 0 | 73.3234 | 160.3493 | 12.57% | 0 | 0 | 30.0278 | 48.04% | 28.2647
7182 | 0 | 0 | 0 | 2.4 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.9503 | 29.8273 | 0 | 76.9503 | 83.399 | 6.538% | 0 | 0 | 30.0278 | 48.04% | 29.8273
7183 | 70 | 14 | 8 | 1.6 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.399 | 32.667 | 0 | 83.399 | 0 | 0% | 0 | 0 | 30.0278 | 48.04% | 32.667
7184 | 569 | 148 | 37 | 1.8 | 14.7 | 0 | 0 | 0 | 0 | 12.6976 | 0 | 0 | 12.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 21.4847 | 6.25 | 10% | 34.1823
7185 | 795 | 343 | 53 | 2.2 | 16.6 | 0 | 0 | 0 | 156.8661 | 34.6767 | 2.4515 | 0 | 34.6767 | 0 | 0 | 0 | 0 | 0 | 156.8661 | 0 | 156.8661 | 12.3% | 0 | 0 | 6.25 | 10% | 34.6767
7186 | 867 | 505 | 68 | 2.3 | 18.7 | 0 | 0 | 0 | 209.9818 | 34.5931 | 18.6851 | 0 | 34.5931 | 0 | 0 | 0 | 0 | 0 | 209.9818 | 0 | 366.8478 | 28.76% | 0 | 0 | 6.25 | 10% | 34.5931
7187 | 906 | 617 | 73 | 2.2 | 19.9 | 0 | 0 | 0 | 127.2205 | 35.2338 | 28.3568 | 0 | 35.2338 | 0 | 0 | 0 | 0 | 0 | 127.2205 | 0 | 494.0683 | 38.73% | 0 | 0 | 6.25 | 10% | 35.2338
7188 | 930 | 672 | 71 | 1.6 | 21.2 | 0 | 0 | 0 | 255.4519 | 34.8536 | 33.8335 | 0 | 34.8536 | 0 | 0 | 0 | 0 | 0 | 255.4519 | 0 | 749.5202 | 58.76% | 0 | 0 | 6.25 | 10% | 34.8536
7189 | 925 | 663 | 70 | 1.4 | 22.1 | 0 | 0 | 0 | 256.3425 | 47.9998 | 21.0948 | 14.7924 | 33.2074 | 0 | 0 | 0 | 0 | 0 | 256.3425 | 0 | 1005.8626 | 78.86% | 14.7924 | 0 | 19.6158 | 31.39% | 33.2074
7190 | 808 | 567 | 96 | 2.4 | 22.7 | 0 | 0 | 0 | 217.9151 | 57.3927 | 6.4056 | 25 | 32.3927 | 0 | 0 | 0 | 0 | 0 | 217.9151 | 0 | 1223.7777 | 95.94% | 25 | 0 | 42.2048 | 67.53% | 32.3927
7191 | 540 | 405 | 155 | 3.5 | 21.5 | 0 | 0 | 0 | 0 | 48.0442 | 0 | 15.5443 | 32.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1223.7777 | 95.94% | 15.5443 | 0 | 56.25 | 90% | 32.4999
7192 | 292 | 187 | 83 | 3.1 | 20.6 | 0 | 0 | 0 | 0 | 23.0091 | 3.5527e-15 | 0 | 23.0091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1223.7777 | 95.94% | 0 | 0 | 56.25 | 90% | 23.0091
7193 | 340 | 99 | 45 | 2.6 | 19 | 0 | 0 | 0 | 51.7325 | 16.8175 | 2.8422e-14 | 0 | 16.8175 | 0 | 0 | 0 | 0 | 0 | 51.7325 | 0 | 1275.5102 | 100% | 0 | 20.6404 | 33.4066 | 53.45% | 37.4579
7194 | 3 | 4 | 4 | 1.7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8753 | 38.3283 | 0 | 96.8753 | 1178.6349 | 92.4% | 0 | 0 | 33.4066 | 53.45% | 38.3283
7195 | 0 | 0 | 0 | 1.3 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7862 | 37.9133 | 0 | 95.7862 | 1082.8488 | 84.9% | 0 | 0 | 33.4066 | 53.45% | 37.9133
7196 | 0 | 0 | 0 | 0.7 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.1302 | 35.9245 | 0 | 91.1302 | 991.7186 | 77.75% | 0 | 0 | 33.4066 | 53.45% | 35.9245
7197 | 0 | 0 | 0 | 0.6 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.3248 | 32.9915 | 0 | 84.3248 | 907.3938 | 71.14% | 0 | 0 | 33.4066 | 53.45% | 32.9915
7198 | 0 | 0 | 0 | 0.5 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.3422 | 30.8482 | 0 | 79.3422 | 828.0516 | 64.92% | 0 | 0 | 33.4066 | 53.45% | 30.8482
7199 | 0 | 0 | 0 | 1.2 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828.0516 | 64.92% | 0 | 0 | 33.4066 | 53.45% | 0
7200 | 0 | 0 | 0 | 1.3 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828.0516 | 64.92% | 0 | 0 | 33.4066 | 53.45% | 0
7201 | 0 | 0 | 0 | 0.6 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828.0516 | 64.92% | 0 | 0 | 33.4066 | 53.45% | 0
7202 | 0 | 0 | 0 | 0.5 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828.0516 | 64.92% | 0 | 0 | 33.4066 | 53.45% | 0
7203 | 0 | 0 | 0 | 1.3 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828.0516 | 64.92% | 0 | 0 | 33.4066 | 53.45% | 0
7204 | 0 | 0 | 0 | 1.4 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.5016 | 33.5681 | 0 | 85.5016 | 742.55 | 58.22% | 0 | 0 | 33.4066 | 53.45% | 33.5681
7205 | 0 | 0 | 0 | 0.7 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4282 | 38.32 | 0 | 96.4282 | 646.1219 | 50.66% | 0 | 0 | 33.4066 | 53.45% | 38.32
7206 | 0 | 0 | 0 | 0.3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.046 | 41.2112 | 0 | 103.046 | 543.0759 | 42.58% | 0 | 0 | 33.4066 | 53.45% | 41.2112
7207 | 14 | 17 | 14 | 0.8 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8571 | 42.4298 | 0 | 105.8571 | 437.2188 | 34.28% | 0 | 0 | 33.4066 | 53.45% | 42.4298
7208 | 177 | 151 | 103 | 0.4 | 14.4 | 0 | 0 | 0 | 0 | 14.7654 | 0 | 0 | 14.7654 | 0 | 0 | 0 | 73.1588 | 28.1337 | 0 | 73.1588 | 364.06 | 28.54% | 0 | 0 | 33.4066 | 53.45% | 42.8991
7209 | 5 | 139 | 136 | 0.4 | 15.6 | 0 | 0 | 0 | 0 | 10.0819 | 0 | 0 | 10.0819 | 0 | 0 | 0 | 84.6706 | 33.0958 | 0 | 84.6706 | 279.3894 | 21.9% | 0 | 0 | 33.4066 | 53.45% | 43.1777
7210 | 2 | 195 | 193 | 1.1 | 15.8 | 0 | 0 | 0 | 0 | 13.7958 | 0 | 0 | 13.7958 | 0 | 0 | 0 | 76.9285 | 29.7273 | 0 | 76.9285 | 202.4609 | 15.87% | 0 | 0 | 33.4066 | 53.45% | 43.5231
7211 | 4 | 252 | 246 | 1.8 | 16.8 | 0 | 0 | 0 | 0 | 17.6313 | 0 | 0 | 17.6313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.4609 | 15.87% | 0 | 0 | 33.4066 | 53.45% | 17.6313
7212 | 17 | 319 | 304 | 2.2 | 17.7 | 0 | 0 | 0 | 0 | 22.9249 | 0 | 0 | 22.9249 | 0 | 0 | 0 | 2.8422e-14 | 0 | 0 | 2.8422e-14 | 202.4609 | 15.87% | 0 | 0 | 33.4066 | 53.45% | 22.9249
7213 | 39 | 332 | 302 | 2.9 | 18.1 | 0 | 0 | 0 | 0 | 26.0682 | 0 | 0 | 26.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.4609 | 15.87% | 0 | 11.3563 | 20.8382 | 33.34% | 37.4245
7214 | 787 | 607 | 145 | 2.4 | 19.8 | 0 | 0 | 0 | 211.5661 | 66.3546 | 0.82353 | 25 | 41.3546 | 0 | 0 | 0 | 0 | 0 | 211.5661 | 0 | 414.027 | 32.46% | 25 | 0 | 43.4272 | 69.48% | 41.3546
7215 | 786 | 453 | 76 | 2.2 | 21 | 0 | 0 | 0 | 201.5856 | 55.7174 | 0 | 14.1914 | 41.5259 | 0 | 0 | 0 | 0 | 0 | 201.5856 | 0 | 615.6126 | 48.26% | 14.1914 | 0 | 56.25 | 90% | 41.5259
7216 | 659 | 282 | 63 | 2.5 | 21 | 0 | 0 | 0 | 149.1755 | 40.0633 | 0 | 0 | 40.0633 | 0 | 0 | 0 | 0 | 0 | 149.1755 | 0 | 764.7881 | 59.96% | 0 | 3.5266 | 52.347 | 83.76% | 43.5899
7217 | 332 | 94 | 36 | 2.6 | 19.2 | 0 | 0 | 0 | 49.5875 | 15.6117 | 0 | 0 | 15.6117 | 0 | 0 | 0 | 0 | 0 | 49.5875 | 0 | 814.3755 | 63.85% | 0 | 25 | 24.6787 | 39.49% | 40.6117
7218 | 1 | 2 | 2 | 2.3 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.2947 | 45.4631 | 0 | 113.2947 | 701.0808 | 54.96% | 0 | 0 | 24.6787 | 39.49% | 45.4631
7219 | 0 | 0 | 0 | 0.9 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8601 | 43.6136 | 0 | 108.8601 | 592.2208 | 46.43% | 0 | 0 | 24.6787 | 39.49% | 43.6136
7220 | 0 | 0 | 0 | 0.3 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9675 | 39.3422 | 0 | 98.9675 | 493.2533 | 38.67% | 0 | 0 | 24.6787 | 39.49% | 39.3422
7221 | 0 | 0 | 0 | 0.4 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2788 | 36.029 | 0 | 91.2788 | 401.9745 | 31.51% | 0 | 0 | 24.6787 | 39.49% | 36.029
7222 | 0 | 0 | 0 | 0.8 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2036 | 33.8397 | 0 | 86.2036 | 315.7709 | 24.76% | 0 | 0 | 24.6787 | 39.49% | 33.8397
7223 | 0 | 0 | 0 | 0.8 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.7709 | 24.76% | 0 | 0 | 24.6787 | 39.49% | 0
7224 | 0 | 0 | 0 | 0.7 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.7709 | 24.76% | 0 | 0 | 24.6787 | 39.49% | 0
7225 | 0 | 0 | 0 | 0.3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.7709 | 24.76% | 0 | 0 | 24.6787 | 39.49% | 0
7226 | 0 | 0 | 0 | 0.3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.7709 | 24.76% | 0 | 0 | 24.6787 | 39.49% | 0
7227 | 0 | 0 | 0 | 0.6 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315.7709 | 24.76% | 0 | 0 | 24.6787 | 39.49% | 0
7228 | 0 | 0 | 0 | 1.4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.3377 | 34.7714 | 0 | 88.3377 | 227.4332 | 17.83% | 0 | 0 | 24.6787 | 39.49% | 34.7714
7229 | 0 | 0 | 0 | 0.8 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1542 | 43.8782 | 0 | 109.1542 | 118.2791 | 9.273% | 4.5694 | 0 | 28.8074 | 46.09% | 39.3088
7230 | 0 | 0 | 0 | 0.7 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7433 | 41.9535 | 0 | 104.7433 | 13.5358 | 1.061% | 0 | 0 | 28.8074 | 46.09% | 41.9535
7231 | 30 | 10 | 7 | 1.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5358 | 1.061% | 0 | 20.382 | 6.25 | 10% | 20.382
7232 | 531 | 142 | 38 | 1.5 | 16 | 0 | 0 | 0 | 62.9948 | 12.0003 | 0 | 0 | 12.0003 | 0 | 0 | 0 | 0 | 0 | 62.9948 | 0 | 76.5306 | 6% | 0 | 0 | 6.25 | 10% | 12.0003
7233 | 760 | 328 | 56 | 0.8 | 18.2 | 0 | 0 | 0 | 0 | 30.881 | 4.2925 | 0 | 30.881 | 0 | 0 | 0 | 38.2653 | 12.9025 | 0 | 38.2653 | 38.2653 | 3% | 0 | 0 | 6.25 | 10% | 43.7835
7234 | 851 | 489 | 65 | 1.1 | 20.2 | 0 | 0 | 0 | 0 | 31.1803 | 19.3191 | 0 | 31.1803 | 0 | 0 | 0 | 38.2653 | 12.8609 | 0 | 38.2653 | 0 | 0% | 0 | 0 | 6.25 | 10% | 44.0412
7235 | 898 | 605 | 71 | 2.2 | 21.1 | 0 | 0 | 0 | 236.1683 | 44.1177 | 18.5327 | 0 | 44.1177 | 0 | 0 | 0 | 0 | 0 | 236.1683 | 0 | 236.1683 | 18.52% | 0 | 0 | 6.25 | 10% | 44.1177
7236 | 918 | 662 | 74 | 1.9 | 22.8 | 0 | 0 | 0 | 251.3338 | 42.7696 | 25.4371 | 0 | 42.7696 | 0 | 0 | 0 | 0 | 0 | 251.3338 | 0 | 487.502 | 38.22% | 0 | 0 | 6.25 | 10% | 42.7696
7237 | 908 | 653 | 77 | 2.5 | 23.4 | 0 | 0 | 0 | 250.2568 | 66.9089 | 2.9507 | 25 | 41.9089 | 0 | 0 | 0 | 0 | 0 | 250.2568 | 0 | 737.7589 | 57.84% | 25 | 0 | 28.839 | 46.14% | 41.9089
7238 | 881 | 584 | 77 | 3.1 | 23.4 | 0 | 0 | 0 | 238.4953 | 59.0308 | 7.563 | 17.2416 | 41.7892 | 0 | 0 | 0 | 0 | 0 | 238.4953 | 0 | 976.2542 | 76.54% | 17.2416 | 0 | 44.4178 | 71.07% | 41.7892
7239 | 779 | 447 | 80 | 2.3 | 23.6 | 0 | 0 | 0 | 199.2171 | 55.1837 | 0 | 13.0951 | 42.0886 | 0 | 0 | 0 | 0 | 0 | 199.2171 | 0 | 1175.4713 | 92.16% | 13.0951 | 0 | 56.25 | 90% | 42.0886
7240 | 589 | 269 | 76 | 2.3 | 23.2 | 0 | 0 | 0 | 100.0389 | 37.52 | 0 | 0 | 37.52 | 0 | 0 | 0 | 0 | 0 | 100.0389 | 0 | 1275.5102 | 100% | 0 | 6.4821 | 49.076 | 78.52% | 44.0022
7241 | 314 | 95 | 43 | 2.7 | 20.7 | 0 | 0 | 0 | 0 | 15.5824 | 0 | 0 | 15.5824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 21.4077 | 34.25% | 40.5824
7242 | 2 | 3 | 3 | 1.6 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.2628 | 45.4004 | 0 | 113.2628 | 1162.2474 | 91.12% | 0 | 0 | 21.4077 | 34.25% | 45.4004
7243 | 0 | 0 | 0 | 0.5 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1393 | 43.6888 | 0 | 109.1393 | 1053.1081 | 82.56% | 0 | 0 | 21.4077 | 34.25% | 43.6888
7244 | 0 | 0 | 0 | 0.2 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.8578 | 39.6946 | 0 | 99.8578 | 953.2503 | 74.73% | 0 | 0 | 21.4077 | 34.25% | 39.6946
7245 | 0 | 0 | 0 | 0.9 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9155 | 36.2657 | 0 | 91.9155 | 861.3348 | 67.53% | 0 | 0 | 21.4077 | 34.25% | 36.2657
7246 | 0 | 0 | 0 | 1.4 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6482 | 36.1648 | 0 | 91.6482 | 769.6866 | 60.34% | 2.0619 | 0 | 23.2707 | 37.23% | 34.1029
7247 | 0 | 0 | 0 | 1.9 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1731 | 32.4456 | 0 | 83.1731 | 686.5135 | 53.82% | 0 | 0 | 23.2707 | 37.23% | 32.4456
7248 | 0 | 0 | 0 | 1.9 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4005 | 31.266 | 0 | 80.4005 | 606.1131 | 47.52% | 0 | 0 | 23.2707 | 37.23% | 31.266
7249 | 0 | 0 | 0 | 0.4 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606.1131 | 47.52% | 0 | 0 | 23.2707 | 37.23% | 0
7250 | 0 | 0 | 0 | 2 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606.1131 | 47.52% | 0 | 0 | 23.2707 | 37.23% | 0
7251 | 0 | 0 | 0 | 2.1 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606.1131 | 47.52% | 0 | 0.0029677 | 23.2674 | 37.23% | 0.0029677
7252 | 0 | 0 | 0 | 2.2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4604 | 34.7756 | 0 | 88.4604 | 517.6527 | 40.58% | 0 | 0 | 23.2674 | 37.23% | 34.7756
7253 | 0 | 0 | 0 | 2.7 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.1757 | 39.4327 | 0 | 99.1757 | 418.477 | 32.81% | 0 | 0 | 23.2674 | 37.23% | 39.4327
7254 | 0 | 0 | 0 | 2.7 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.5528 | 41.7474 | 0 | 104.5528 | 313.9242 | 24.61% | 0 | 0 | 23.2674 | 37.23% | 41.7474
7255 | 5 | 7 | 6 | 1.9 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.9426 | 42.8128 | 0 | 106.9426 | 206.9816 | 16.23% | 0 | 0 | 23.2674 | 37.23% | 42.8128
7256 | 236 | 120 | 68 | 1.5 | 15.8 | 0 | 0 | 0 | 0 | 9.943 | 0 | 0 | 9.943 | 0 | 0 | 0 | 85.3098 | 33.3655 | 0 | 85.3098 | 121.6718 | 9.539% | 0 | 0 | 23.2674 | 37.23% | 43.3086
7257 | 393 | 293 | 151 | 0.5 | 19.8 | 0 | 0 | 0 | 68.4589 | 28.2786 | 0 | 0 | 28.2786 | 0 | 0 | 0 | 0 | 0 | 68.4589 | 0 | 190.1307 | 14.91% | 0 | 15.2932 | 6.3419 | 10.15% | 43.5718
7258 | 487 | 474 | 229 | 0.6 | 22.2 | 0 | 0 | 0 | 110.3351 | 43.9734 | 0 | 0 | 43.9734 | 0 | 0 | 0 | 0 | 0 | 110.3351 | 0 | 300.4658 | 23.56% | 0 | 0.083071 | 6.25 | 10% | 44.0565
7259 | 349 | 511 | 295 | 1.2 | 23.1 | 0 | 0 | 0 | 81.0829 | 44.1038 | 1.9081 | 0 | 44.1038 | 0 | 0 | 0 | 0 | 0 | 81.0829 | 0 | 381.5487 | 29.91% | 0 | 0 | 6.25 | 10% | 44.1038
7260 | 864 | 652 | 105 | 1.8 | 23.9 | 0 | 0 | 0 | 235.1943 | 59.8926 | 7.5595 | 16.9085 | 42.9841 | 0 | 0 | 0 | 0 | 0 | 235.1943 | 0 | 616.743 | 48.35% | 16.9085 | 0 | 21.5278 | 34.44% | 42.9841
7261 | 707 | 609 | 162 | 1.5 | 24.6 | 0 | 0 | 0 | 191.1437 | 63.0682 | 0 | 20.6857 | 42.3825 | 0 | 0 | 0 | 0 | 0 | 191.1437 | 0 | 807.8868 | 63.34% | 20.6857 | 0 | 40.2186 | 64.35% | 42.3825
7262 | 634 | 542 | 182 | 2.9 | 24.6 | 0 | 0 | 0 | 166.5369 | 59.6264 | 0 | 17.7425 | 41.8839 | 0 | 0 | 0 | 0 | 0 | 166.5369 | 0 | 974.4237 | 76.39% | 17.7425 | 0 | 56.25 | 90% | 41.8839
7263 | 286 | 295 | 161 | 3.7 | 23.7 | 0 | 0 | 0 | 60.9589 | 31.4992 | 0 | 0 | 31.4992 | 0 | 0 | 0 | 0 | 0 | 60.9589 | 0 | 1035.3826 | 81.17% | 0 | 0 | 56.25 | 90% | 31.4992
7264 | 57 | 88 | 70 | 4 | 21.8 | 0 | 0 | 0 | 0 | 7.8979 | 0 | 0 | 7.8979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035.3826 | 81.17% | 0 | 20.178 | 33.9183 | 54.27% | 28.0759
7265 | 306 | 107 | 58 | 3.6 | 21.5 | 0 | 0 | 0 | 42.9331 | 16.2689 | 0 | 0 | 16.2689 | 0 | 0 | 0 | 0 | 0 | 42.9331 | 0 | 1078.3157 | 84.54% | 0 | 25 | 6.25 | 10% | 41.2689
7266 | 1 | 2 | 2 | 3.2 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.2379 | 44.8197 | 0 | 112.2379 | 966.0777 | 75.74% | 0 | 0 | 6.25 | 10% | 44.8197
7267 | 0 | 0 | 0 | 2.2 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.2683 | 43.154 | 0 | 108.2683 | 857.8094 | 67.25% | 0 | 0 | 6.25 | 10% | 43.154
7268 | 0 | 0 | 0 | 0.9 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2715 | 39.3617 | 0 | 99.2715 | 758.5379 | 59.47% | 0 | 0 | 6.25 | 10% | 39.3617
7269 | 0 | 0 | 0 | 1 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.045 | 42.7586 | 0 | 107.045 | 651.4929 | 51.08% | 6.5389 | 0 | 12.1582 | 19.45% | 36.2198
7270 | 0 | 0 | 0 | 1.7 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.6645 | 0 | 127.551 | 523.9419 | 41.08% | 17.3904 | 0 | 27.8715 | 44.59% | 34.2742
7271 | 0 | 0 | 0 | 1.2 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.762 | 32.6531 | 0 | 83.762 | 440.1799 | 34.51% | 0 | 0 | 27.8715 | 44.59% | 32.6531
7272 | 0 | 0 | 0 | 1 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 440.1799 | 34.51% | 0 | 0 | 27.8715 | 44.59% | 0
7273 | 0 | 0 | 0 | 1.3 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440.1799 | 34.51% | 0 | 0 | 27.8715 | 44.59% | 0
7274 | 0 | 0 | 0 | 1.5 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440.1799 | 34.51% | 0 | 0 | 27.8715 | 44.59% | 0
7275 | 0 | 0 | 0 | 1.6 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440.1799 | 34.51% | 0 | 0 | 27.8715 | 44.59% | 0
7276 | 0 | 0 | 0 | 1.4 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.8625 | 34.4079 | 0 | 87.8625 | 352.3173 | 27.62% | 0 | 0 | 27.8715 | 44.59% | 34.4079
7277 | 0 | 0 | 0 | 1.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2153 | 38.4495 | 0 | 97.2153 | 255.102 | 20% | 0 | 0 | 27.8715 | 44.59% | 38.4495
7278 | 0 | 0 | 0 | 1.1 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.6515 | 0 | 127.551 | 127.551 | 10% | 10.6882 | 0 | 37.5289 | 60.05% | 40.9633
7279 | 17 | 8 | 6 | 1.3 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.7023 | 0 | 127.551 | 7.1054e-15 | 5.571e-16% | 9.2516 | 0 | 45.8882 | 73.42% | 42.4507
7280 | 483 | 133 | 43 | 1.1 | 18.7 | 0 | 0 | 0 | 49.5678 | 10.3238 | 0 | 0 | 10.3238 | 0 | 0 | 0 | 0 | 0 | 49.5678 | 0 | 49.5678 | 3.886% | 0 | 25 | 18.2199 | 29.15% | 35.3237
7281 | 696 | 304 | 59 | 0.7 | 22.4 | 0 | 0 | 0 | 133.7776 | 32.4165 | 0 | 0 | 32.4165 | 0 | 0 | 0 | 0 | 0 | 133.7776 | 0 | 183.3454 | 14.37% | 0 | 10.8155 | 6.25 | 10% | 43.232
7282 | 827 | 476 | 73 | 2.5 | 24.5 | 0 | 0 | 0 | 197.7109 | 43.8991 | 6.7987 | 0 | 43.8991 | 0 | 0 | 0 | 0 | 0 | 197.7109 | 0 | 381.0563 | 29.87% | 0 | 0 | 6.25 | 10% | 43.8991
7283 | 820 | 580 | 100 | 3 | 25.8 | 0 | 0 | 0 | 212.8816 | 44.0801 | 16.5332 | 0 | 44.0801 | 0 | 0 | 0 | 0 | 0 | 212.8816 | 0 | 593.9378 | 46.56% | 0 | 0 | 6.25 | 10% | 44.0801
7284 | 753 | 617 | 141 | 4.9 | 26.4 | 0 | 0 | 0 | 200.4647 | 65.7237 | 0 | 23.0502 | 42.6735 | 0 | 0 | 0 | 0 | 0 | 200.4647 | 0 | 794.4025 | 62.28% | 23.0502 | 0 | 27.0772 | 43.32% | 42.6735
7285 | 730 | 610 | 152 | 5.7 | 26.7 | 0 | 0 | 0 | 194.7845 | 66.5454 | 0.085681 | 25 | 41.5454 | 0 | 0 | 0 | 0 | 0 | 194.7845 | 0 | 989.187 | 77.55% | 25 | 0 | 49.6662 | 79.47% | 41.5454
7286 | 638 | 598 | 228 | 5.1 | 27.6 | 0 | 0 | 0 | 165.8394 | 48.3584 | 15.1036 | 7.2865 | 41.0719 | 0 | 0 | 0 | 0 | 0 | 165.8394 | 0 | 1155.0264 | 90.55% | 7.2865 | 0 | 56.25 | 90% | 41.0719
7287 | 17 | 205 | 195 | 4.7 | 26.2 | 0 | 0 | 0 | 0 | 14.1492 | 0 | 0 | 14.1492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1155.0264 | 90.55% | 0 | 25 | 28.5817 | 45.73% | 39.1492
7288 | 282 | 231 | 136 | 2.8 | 26.4 | 0 | 0 | 0 | 52.1938 | 25.6102 | 0 | 0 | 25.6102 | 0 | 0 | 0 | 0 | 0 | 52.1938 | 0 | 1207.2202 | 94.65% | 0 | 17.1692 | 9.5799 | 15.33% | 42.7794
7289 | 84 | 67 | 51 | 1.8 | 24.6 | 0 | 0 | 0 | 0 | 6.3792 | 0 | 0 | 6.3792 | 0 | 0 | 0 | 95.394 | 37.1676 | 0 | 95.394 | 1111.8261 | 87.17% | 0 | 0 | 9.5799 | 15.33% | 43.5467
7290 | 0 | 2 | 2 | 5 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.482 | 42.7919 | 0 | 108.482 | 1003.3441 | 78.66% | 0 | 0 | 9.5799 | 15.33% | 42.7919
7291 | 0 | 0 | 0 | 3.2 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8542 | 41.3226 | 0 | 104.8542 | 898.49 | 70.44% | 0 | 0 | 9.5799 | 15.33% | 41.3226
7292 | 0 | 0 | 0 | 2.3 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8352 | 37.9955 | 0 | 96.8352 | 801.6548 | 62.85% | 0 | 0 | 9.5799 | 15.33% | 37.9955
7293 | 0 | 0 | 0 | 3 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7528 | 35.4287 | 0 | 90.7528 | 710.902 | 55.73% | 0 | 0 | 9.5799 | 15.33% | 35.4287
7294 | 0 | 0 | 0 | 3 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9617 | 33.784 | 0 | 86.9617 | 623.9403 | 48.92% | 0 | 0 | 9.5799 | 15.33% | 33.784
7295 | 0 | 0 | 0 | 2.3 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.6593 | 49.6574 | 0 | 123.6593 | 500.281 | 39.22% | 17.5043 | 0 | 25.3961 | 40.63% | 32.1531
7296 | 0 | 0 | 0 | 2.6 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5907 | 30.6239 | 0 | 79.5907 | 420.6904 | 32.98% | 0 | 0 | 25.3961 | 40.63% | 30.6239
7297 | 0 | 0 | 0 | 1.1 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.6904 | 32.98% | 0 | 0 | 25.3961 | 40.63% | 0
7298 | 0 | 0 | 0 | 2.4 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.6904 | 32.98% | 0 | 0 | 25.3961 | 40.63% | 0
7299 | 0 | 0 | 0 | 3.7 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.6904 | 32.98% | 0 | 0 | 25.3961 | 40.63% | 0
7300 | 0 | 0 | 0 | 4.8 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.6904 | 32.98% | 0 | 0 | 25.3961 | 40.63% | 0
7301 | 0 | 0 | 0 | 4.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.5725 | 30.1449 | 0 | 78.5725 | 342.1178 | 26.82% | 0 | 0 | 25.3961 | 40.63% | 30.1449
7302 | 0 | 0 | 0 | 4.7 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.088 | 30.8496 | 0 | 80.088 | 262.0299 | 20.54% | 0 | 0 | 25.3961 | 40.63% | 30.8496
7303 | 30 | 10 | 6 | 2.7 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.389 | 0 | 127.551 | 134.4788 | 10.54% | 17.9838 | 0 | 41.6456 | 66.63% | 33.4051
7304 | 536 | 146 | 47 | 2.9 | 21.1 | 0 | 0 | 0 | 52.9186 | 10.5226 | 0 | 0 | 10.5226 | 0 | 0 | 0 | 0 | 0 | 52.9186 | 0 | 187.3974 | 14.69% | 0 | 11.7684 | 28.6211 | 45.79% | 22.291
7305 | 773 | 351 | 84 | 2.7 | 23.2 | 0 | 0 | 0 | 148.8438 | 38.0241 | 0 | 2.3294 | 35.6947 | 0 | 0 | 0 | 0 | 0 | 148.8438 | 0 | 336.2412 | 26.36% | 2.3294 | 0 | 30.7258 | 49.16% | 35.6947
7306 | 307 | 367 | 225 | 3.5 | 24.3 | 0 | 0 | 0 | 61.3943 | 35.8077 | 0 | 0 | 35.8077 | 0 | 0 | 0 | 0 | 0 | 61.3943 | 0 | 397.6355 | 31.17% | 0 | 0.24357 | 30.4562 | 48.73% | 36.0513
7307 | 12 | 286 | 275 | 3.2 | 24.6 | 0 | 0 | 0 | 0 | 20.3988 | 0 | 0 | 20.3988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.6355 | 31.17% | 0 | 16.3196 | 12.3948 | 19.83% | 36.7184
7308 | 13 | 316 | 304 | 4.1 | 24.8 | 0 | 0 | 0 | 0 | 22.4714 | 0 | 0 | 22.4714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.6355 | 31.17% | 0 | 0 | 12.3948 | 19.83% | 22.4714
7309 | 62 | 378 | 334 | 4.9 | 25.4 | 0 | 0 | 0 | 0 | 30.4326 | 0 | 0 | 30.4326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.6355 | 31.17% | 0 | 0 | 12.3948 | 19.83% | 30.4326
7310 | 110 | 371 | 302 | 4.1 | 26.3 | 0 | 0 | 0 | 0 | 30.7564 | 0 | 0 | 30.7564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.6355 | 31.17% | 0 | 0 | 12.3948 | 19.83% | 30.7564
7311 | 111 | 273 | 218 | 2.2 | 26.8 | 0 | 0 | 0 | 0 | 23.9654 | 0 | 0 | 23.9654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397.6355 | 31.17% | 0 | 0 | 12.3948 | 19.83% | 23.9654
7312 | 158 | 186 | 143 | 2.3 | 26.7 | 0 | 0 | 0 | 0 | 19.0411 | 0 | 0 | 19.0411 | 0 | 0 | 0 | 47.6763 | 16.6828 | 0 | 47.6763 | 349.9593 | 27.44% | 0 | 0 | 12.3948 | 19.83% | 35.724
7313 | 25 | 58 | 53 | 3.5 | 25.4 | 0 | 0 | 0 | 0 | 4.0493 | 0 | 0 | 4.0493 | 0 | 0 | 0 | 85.4762 | 32.8654 | 0 | 85.4762 | 264.4831 | 20.74% | 0 | 0 | 12.3948 | 19.83% | 36.9147
7314 | 0 | 2 | 2 | 4.4 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7597 | 37.4245 | 0 | 95.7597 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 37.4245
7315 | 0 | 0 | 0 | 4 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7316 | 0 | 0 | 0 | 5.7 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7317 | 0 | 0 | 0 | 6.6 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7318 | 0 | 0 | 0 | 5.5 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7319 | 0 | 0 | 0 | 6.9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7320 | 0 | 0 | 0 | 6.5 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7321 | 0 | 0 | 0 | 6.2 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7322 | 0 | 0 | 0 | 7 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7323 | 0 | 0 | 0 | 7.3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7324 | 0 | 0 | 0 | 7.3 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7325 | 0 | 0 | 0 | 5.7 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7326 | 0 | 0 | 0 | 7.2 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.7234 | 13.23% | 0 | 0 | 12.3948 | 19.83% | 0
7327 | 4 | 7 | 6 | 6.6 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5625 | 34.5179 | 0 | 88.5625 | 80.1609 | 6.285% | 0 | 0 | 12.3948 | 19.83% | 34.5179
7328 | 357 | 118 | 51 | 7.7 | 21.7 | 0 | 0 | 0 | 0 | 8.491 | 0 | 0 | 8.491 | 0 | 0 | 0 | 73.0438 | 27.7845 | 0 | 73.0438 | 7.1171 | 0.558% | 0 | 0 | 12.3948 | 19.83% | 36.2755
7329 | 364 | 251 | 137 | 6.4 | 22.7 | 0 | 0 | 0 | 57.0579 | 26.6429 | 0 | 0 | 26.6429 | 0 | 0 | 0 | 0 | 0 | 57.0579 | 0 | 64.175 | 5.031% | 0 | 0 | 12.3948 | 19.83% | 26.6429
7330 | 137 | 286 | 217 | 9.3 | 22.4 | 0 | 0 | 0 | 0 | 25.7811 | 0 | 0 | 25.7811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.175 | 5.031% | 0 | 0 | 12.3948 | 19.83% | 25.7811
7331 | 306 | 365 | 184 | 10 | 22.9 | 0 | 0 | 0 | 61.6609 | 36.068 | 0 | 0 | 36.068 | 0 | 0 | 0 | 0 | 0 | 61.6609 | 0 | 125.8359 | 9.866% | 0 | 0 | 12.3948 | 19.83% | 36.068
7332 | 85 | 270 | 216 | 8.4 | 23.1 | 0 | 0 | 0 | 0 | 22.0237 | 0 | 0 | 22.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.8359 | 9.866% | 0 | 0 | 12.3948 | 19.83% | 22.0237
7333 | 169 | 334 | 226 | 8.9 | 23.5 | 0 | 0 | 0 | 0 | 30.5798 | 0 | 0 | 30.5798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.8359 | 9.866% | 0 | 0 | 12.3948 | 19.83% | 30.5798
7334 | 89 | 266 | 213 | 8.7 | 22.8 | 0 | 0 | 0 | 0 | 22.0382 | 0 | 0 | 22.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.8359 | 9.866% | 0 | 0 | 12.3948 | 19.83% | 22.0382
7335 | 559 | 387 | 135 | 9.4 | 23.7 | 0 | 0 | 0 | 130.8957 | 48.7972 | 0 | 14.7347 | 34.0625 | 0 | 0 | 0 | 0 | 0 | 130.8957 | 0 | 256.7316 | 20.13% | 14.7347 | 0 | 25.7085 | 41.13% | 34.0625
7336 | 182 | 161 | 113 | 7.8 | 23.1 | 0 | 0 | 0 | 0 | 19.0139 | 0 | 0 | 19.0139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.7316 | 20.13% | 0 | 17.582 | 6.25 | 10% | 36.5958
7337 | 237 | 95 | 54 | 6.9 | 22.7 | 0 | 0 | 0 | 0 | 13.4633 | 0 | 0 | 13.4633 | 0 | 0 | 0 | 64.5067 | 24.0642 | 0 | 64.5067 | 192.2249 | 15.07% | 0 | 0 | 6.25 | 10% | 37.5275
7338 | 1 | 2 | 2 | 7.9 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.781 | 37.9871 | 0 | 96.781 | 95.4439 | 7.483% | 0 | 0 | 6.25 | 10% | 37.9871
7339 | 0 | 0 | 0 | 8 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.4439 | 37.469 | 0 | 95.4439 | 0 | 0% | 0 | 0 | 6.25 | 10% | 37.469
7340 | 0 | 0 | 0 | 5.1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7341 | 0 | 0 | 0 | 5.1 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7342 | 0 | 0 | 0 | 5.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7343 | 0 | 0 | 0 | 5 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7344 | 0 | 0 | 0 | 4.7 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7345 | 0 | 0 | 0 | 4.5 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7346 | 0 | 0 | 0 | 4.1 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7347 | 0 | 0 | 0 | 6.9 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7348 | 0 | 0 | 0 | 10.2 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7349 | 0 | 0 | 0 | 12.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7350 | 0 | 0 | 0 | 13.3 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7351 | 11 | 9 | 8 | 11.7 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7352 | 270 | 142 | 92 | 9.4 | 19.3 | 0 | 0 | 0 | 0 | 11.1481 | 0 | 0 | 11.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 11.1481
7353 | 51 | 200 | 181 | 8.6 | 19.9 | 0 | 0 | 0 | 0 | 18.5995 | 0 | 0 | 18.5995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 18.5995
7354 | 158 | 325 | 242 | 10 | 20.6 | 0 | 0 | 0 | 0 | 29.6837 | 0 | 0 | 29.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 29.6837
7355 | 224 | 382 | 244 | 11.6 | 20.5 | 0 | 0 | 0 | 36.5968 | 34.8633 | 0.33592 | 0 | 34.8633 | 0 | 0 | 0 | 0 | 0 | 36.5968 | 0 | 36.5968 | 2.869% | 0 | 0 | 6.25 | 10% | 34.8633
7356 | 618 | 551 | 161 | 13.7 | 21.2 | 0 | 0 | 0 | 152.8318 | 34.7644 | 26.2272 | 0 | 34.7644 | 0 | 0 | 0 | 0 | 0 | 152.8318 | 0 | 189.4286 | 14.85% | 0 | 0 | 6.25 | 10% | 34.7644
7357 | 893 | 715 | 166 | 14.2 | 21.8 | 0 | 0 | 0 | 234.5194 | 32.8578 | 39.1422 | 0 | 32.8578 | 0 | 0 | 0 | 0 | 0 | 234.5194 | 0 | 423.948 | 33.24% | 0 | 0 | 6.25 | 10% | 32.8578
7358 | 865 | 557 | 76 | 13 | 22.1 | 0 | 0 | 0 | 223.9958 | 56.8258 | 11.8323 | 25 | 31.8258 | 0 | 0 | 0 | 0 | 0 | 223.9958 | 0 | 647.9437 | 50.8% | 25 | 0 | 28.839 | 46.14% | 31.8258
7359 | 855 | 443 | 59 | 11.1 | 22.2 | 0 | 0 | 0 | 210.6126 | 56.9247 | 3.0781 | 25 | 31.9247 | 0 | 0 | 0 | 0 | 0 | 210.6126 | 0 | 858.5563 | 67.31% | 25 | 0 | 51.428 | 82.28% | 31.9247
7360 | 711 | 268 | 49 | 10.5 | 21.8 | 0 | 0 | 0 | 151.7107 | 40.2738 | 1.5947 | 5.3367 | 34.9371 | 0 | 0 | 0 | 0 | 0 | 151.7107 | 0 | 1010.267 | 79.2% | 5.3367 | 0 | 56.25 | 90% | 34.9371
7361 | 431 | 85 | 26 | 9.9 | 20.9 | 0 | 0 | 0 | 60.9017 | 18.0333 | 0 | 0 | 18.0333 | 0 | 0 | 0 | 0 | 0 | 60.9017 | 0 | 1071.1686 | 83.98% | 0 | 18.8299 | 35.4103 | 56.66% | 36.8632
7362 | 2 | 1 | 1 | 10.1 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7632 | 34.216 | 0 | 87.7632 | 983.4054 | 77.1% | 0 | 3.5831 | 31.4448 | 50.31% | 37.7991
7363 | 0 | 0 | 0 | 11.2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5214 | 37.5693 | 0 | 95.5214 | 887.884 | 69.61% | 0 | 0 | 31.4448 | 50.31% | 37.5693
7364 | 0 | 0 | 0 | 5.6 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3572 | 35.8145 | 0 | 91.3572 | 796.5269 | 62.45% | 0 | 0 | 31.4448 | 50.31% | 35.8145
7365 | 0 | 0 | 0 | 1.7 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.2196 | 33.2979 | 0 | 85.2196 | 711.3072 | 55.77% | 0 | 0 | 31.4448 | 50.31% | 33.2979
7366 | 0 | 0 | 0 | 1.3 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6398 | 31.2785 | 0 | 80.6398 | 630.6675 | 49.44% | 0 | 0 | 31.4448 | 50.31% | 31.2785
7367 | 0 | 0 | 0 | 4.7 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.2071 | 29.7396 | 0 | 77.2071 | 553.4603 | 43.39% | 0 | 0 | 31.4448 | 50.31% | 29.7396
7368 | 0 | 0 | 0 | 5.4 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.4603 | 43.39% | 0 | 0 | 31.4448 | 50.31% | 0
7369 | 0 | 0 | 0 | 3.1 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.4603 | 43.39% | 0 | 0 | 31.4448 | 50.31% | 0
7370 | 0 | 0 | 0 | 5.9 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.4603 | 43.39% | 0 | 15.111 | 14.7209 | 23.55% | 15.111
7371 | 0 | 0 | 0 | 3.2 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.4842 | 29.4179 | 0 | 76.4842 | 476.9761 | 37.39% | 0 | 0 | 14.7209 | 23.55% | 29.4179
7372 | 0 | 0 | 0 | 2 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.0752 | 33.2436 | 0 | 85.0752 | 391.9009 | 30.73% | 0 | 0 | 14.7209 | 23.55% | 33.2436
7373 | 0 | 0 | 0 | 2.6 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7197 | 37.852 | 0 | 95.7197 | 296.1812 | 23.22% | 0 | 0 | 14.7209 | 23.55% | 37.852
7374 | 0 | 0 | 0 | 2.5 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4257 | 40.8143 | 0 | 102.4257 | 193.7556 | 15.19% | 0 | 0 | 14.7209 | 23.55% | 40.8143
7375 | 31 | 7 | 4 | 2.6 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.638 | 42.6485 | 0 | 106.638 | 87.1176 | 6.83% | 0 | 0 | 14.7209 | 23.55% | 42.6485
7376 | 580 | 128 | 28 | 5.1 | 17.7 | 0 | 0 | 0 | 0 | 9.4403 | 0 | 0 | 9.4403 | 0 | 0 | 0 | 87.1176 | 34.0661 | 0 | 87.1176 | 0 | 0% | 0 | 0 | 14.7209 | 23.55% | 43.5064
7377 | 800 | 309 | 43 | 5.9 | 19.7 | 0 | 0 | 0 | 0 | 36.2353 | 0 | 0 | 36.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 7.654 | 6.25 | 10% | 43.8893
7378 | 891 | 468 | 50 | 6.7 | 21.2 | 0 | 0 | 0 | 207.5847 | 44.2514 | 9.1661 | 0 | 44.2514 | 0 | 0 | 0 | 0 | 0 | 207.5847 | 0 | 207.5847 | 16.27% | 0 | 0 | 6.25 | 10% | 44.2514
7379 | 935 | 580 | 54 | 8.3 | 22.4 | 0 | 0 | 0 | 238.9036 | 44.154 | 21.6074 | 0 | 44.154 | 0 | 0 | 0 | 0 | 0 | 238.9036 | 0 | 446.4884 | 35% | 0 | 0 | 6.25 | 10% | 44.154
7380 | 954 | 636 | 54 | 7.9 | 23.4 | 0 | 0 | 0 | 0 | 43.0078 | 28.9922 | 0 | 43.0078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 446.4884 | 35% | 0 | 0 | 6.25 | 10% | 43.0078
7381 | 950 | 628 | 55 | 7.9 | 24.6 | 0 | 0 | 0 | 213.3826 | 67.0329 | 4.9671 | 25 | 42.0329 | 0 | 0 | 0 | 0 | 0 | 213.3826 | 0 | 659.871 | 51.73% | 25 | 0 | 28.839 | 46.14% | 42.0329
7382 | 915 | 554 | 54 | 7 | 24.8 | 0 | 0 | 0 | 243.765 | 66.5023 | 1.6848 | 25 | 41.5023 | 0 | 0 | 0 | 0 | 0 | 243.765 | 0 | 903.636 | 70.85% | 25 | 0 | 51.428 | 82.28% | 41.5023
7383 | 858 | 429 | 51 | 8 | 24.6 | 0 | 0 | 0 | 213.8197 | 47.0994 | 11.3579 | 5.3367 | 41.7627 | 0 | 0 | 0 | 0 | 0 | 213.8197 | 0 | 1117.4558 | 87.61% | 5.3367 | 0 | 56.25 | 90% | 41.7627
7384 | 737 | 262 | 42 | 10 | 23.2 | 0 | 0 | 0 | 158.0544 | 42.24 | 0 | 0 | 42.24 | 0 | 0 | 0 | 0 | 0 | 158.0544 | 0 | 1275.5102 | 100% | 0 | 1.5379 | 54.5479 | 87.28% | 43.7779
7385 | 432 | 83 | 24 | 9.7 | 21.6 | 0 | 0 | 0 | 0 | 17.7792 | 0 | 0 | 17.7792 | 0 | 0 | 0 | 38.2653 | 12.8279 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 14.4215 | 38.5872 | 61.74% | 45.0286
7386 | 0 | 1 | 1 | 9.3 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1565 | 43.4745 | 0 | 109.1565 | 1128.0884 | 88.44% | 0 | 1.756 | 36.6438 | 58.63% | 45.2305
7387 | 0 | 0 | 0 | 8.2 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1262 | 43.5384 | 0 | 109.1262 | 1018.9622 | 79.89% | 0 | 0 | 36.6438 | 58.63% | 43.5384
7388 | 0 | 0 | 0 | 8.9 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.3624 | 39.7725 | 0 | 100.3624 | 918.5997 | 72.02% | 0 | 0 | 36.6438 | 58.63% | 39.7725
7389 | 0 | 0 | 0 | 7.4 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.535 | 36.4273 | 0 | 92.535 | 826.0647 | 64.76% | 0 | 0 | 36.6438 | 58.63% | 36.4273
7390 | 0 | 0 | 0 | 4.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.862 | 34.3981 | 0 | 87.862 | 738.2027 | 57.88% | 0 | 0 | 36.6438 | 58.63% | 34.3981
7391 | 0 | 0 | 0 | 4 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.7507 | 32.6308 | 0 | 83.7507 | 654.452 | 51.31% | 0 | 0 | 36.6438 | 58.63% | 32.6308
7392 | 0 | 0 | 0 | 7.1 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0745 | 31.4582 | 0 | 81.0745 | 573.3775 | 44.95% | 0 | 0 | 36.6438 | 58.63% | 31.4582
7393 | 0 | 0 | 0 | 8.3 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573.3775 | 44.95% | 0 | 21.0501 | 13.3469 | 21.36% | 21.0501
7394 | 0 | 0 | 0 | 8.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573.3775 | 44.95% | 0 | 0 | 13.3469 | 21.36% | 0
7395 | 0 | 0 | 0 | 5.1 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.9925 | 31.4763 | 0 | 80.9925 | 492.3851 | 38.6% | 0 | 0 | 13.3469 | 21.36% | 31.4763
7396 | 0 | 0 | 0 | 2.6 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.7658 | 34.9747 | 0 | 88.7658 | 403.6193 | 31.64% | 0 | 0 | 13.3469 | 21.36% | 34.9747
7397 | 0 | 0 | 0 | 2.1 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7966 | 39.7781 | 0 | 99.7966 | 303.8226 | 23.82% | 0 | 0 | 13.3469 | 21.36% | 39.7781
7398 | 0 | 0 | 0 | 6.8 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5344 | 42.1596 | 0 | 105.5344 | 198.2882 | 15.55% | 0 | 0 | 13.3469 | 21.36% | 42.1596
7399 | 17 | 6 | 5 | 11.3 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.6827 | 43.4799 | 0 | 108.6827 | 89.6055 | 7.025% | 0 | 0 | 13.3469 | 21.36% | 43.4799
7400 | 532 | 123 | 32 | 12.8 | 16.1 | 0 | 0 | 0 | 0 | 8.7358 | 0 | 0 | 8.7358 | 0 | 0 | 0 | 89.6055 | 35.2176 | 0 | 89.6055 | 0 | 0% | 0 | 0 | 13.3469 | 21.36% | 43.9534
7401 | 805 | 312 | 48 | 9.8 | 16.4 | 0 | 0 | 0 | 145.5443 | 37.7916 | 0 | 0 | 37.7916 | 0 | 0 | 0 | 0 | 0 | 145.5443 | 0 | 145.5443 | 11.41% | 0 | 6.4125 | 6.25 | 10% | 44.2041
7402 | 905 | 477 | 57 | 8.7 | 17.2 | 0 | 0 | 0 | 208.4374 | 44.6289 | 11.207 | 0 | 44.6289 | 0 | 0 | 0 | 0 | 0 | 208.4374 | 0 | 353.9816 | 27.75% | 0 | 0 | 6.25 | 10% | 44.6289
7403 | 956 | 596 | 62 | 9.9 | 17.6 | 0 | 0 | 0 | 242.8049 | 44.6804 | 24.4625 | 0 | 44.6804 | 0 | 0 | 0 | 0 | 0 | 242.8049 | 0 | 596.7865 | 46.79% | 0 | 0 | 6.25 | 10% | 44.6804
7404 | 963 | 649 | 66 | 7.3 | 18.8 | 0 | 0 | 0 | 258.3115 | 43.4576 | 28.5424 | 0 | 43.4576 | 0 | 0 | 0 | 0 | 0 | 258.3115 | 0 | 855.098 | 67.04% | 0 | 0 | 6.25 | 10% | 43.4576
7405 | 952 | 639 | 68 | 5.8 | 19.8 | 0 | 0 | 0 | 0 | 54.8007 | 17.1993 | 12.2762 | 42.5245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855.098 | 67.04% | 12.2762 | 0 | 17.3423 | 27.75% | 42.5245
7406 | 920 | 566 | 67 | 7 | 20.1 | 0 | 0 | 0 | 244.8319 | 66.9744 | 3.7475 | 25 | 41.9744 | 0 | 0 | 0 | 0 | 0 | 244.8319 | 0 | 1099.9299 | 86.23% | 25 | 0 | 39.9313 | 63.89% | 41.9744
7407 | 861 | 440 | 63 | 6.5 | 20.5 | 0 | 0 | 0 | 175.5803 | 60.1909 | 0 | 18.0605 | 42.1304 | 0 | 0 | 0 | 0 | 0 | 175.5803 | 0 | 1275.5102 | 100% | 18.0605 | 0 | 56.25 | 90% | 42.1304
7408 | 735 | 270 | 54 | 6.6 | 19 | 0 | 0 | 0 | 0 | 43.9795 | 0 | 0 | 43.9795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0.60483 | 55.5806 | 88.93% | 44.5843
7409 | 330 | 82 | 32 | 6.6 | 17.1 | 0 | 0 | 0 | 0 | 15.2803 | 0 | 0 | 15.2803 | 0 | 0 | 0 | 78.6736 | 30.4349 | 0 | 78.6736 | 1196.8366 | 93.83% | 0 | 0 | 55.5806 | 88.93% | 45.7152
7410 | 0 | 1 | 1 | 5.9 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.1919 | 33.3298 | 0 | 85.1919 | 1111.6447 | 87.15% | 0 | 12.728 | 41.4941 | 66.39% | 46.0578
7411 | 0 | 0 | 0 | 5.7 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.5523 | 44.3726 | 0 | 110.5523 | 1001.0924 | 78.49% | 0 | 0 | 41.4941 | 66.39% | 44.3726
7412 | 0 | 0 | 0 | 6.2 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.733 | 40.5399 | 0 | 101.733 | 899.3594 | 70.51% | 0 | 0 | 41.4941 | 66.39% | 40.5399
7413 | 0 | 0 | 0 | 6.8 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.2181 | 36.8395 | 0 | 93.2181 | 806.1414 | 63.2% | 0 | 0 | 41.4941 | 66.39% | 36.8395
7414 | 0 | 0 | 0 | 7.6 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.4323 | 34.7561 | 0 | 88.4323 | 717.7091 | 56.27% | 0 | 0 | 41.4941 | 66.39% | 34.7561
7415 | 0 | 0 | 0 | 5.8 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1793 | 32.9149 | 0 | 84.1793 | 633.5297 | 49.67% | 0 | 0 | 41.4941 | 66.39% | 32.9149
7416 | 0 | 0 | 0 | 3 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.8289 | 21.0463 | 0 | 56.8289 | 576.7009 | 45.21% | 0 | 0 | 41.4941 | 66.39% | 21.0463
7417 | 0 | 0 | 0 | 5.4 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.7009 | 45.21% | 0 | 0 | 41.4941 | 66.39% | 0
7418 | 0 | 0 | 0 | 4 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.7009 | 45.21% | 0 | 25 | 13.8258 | 22.12% | 25
7419 | 0 | 0 | 0 | 4.8 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.0979 | 32.0528 | 0 | 82.0979 | 494.603 | 38.78% | 0 | 0 | 13.8258 | 22.12% | 32.0528
7420 | 0 | 0 | 0 | 4.7 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.8821 | 35.4524 | 0 | 89.8821 | 404.7209 | 31.73% | 0 | 0 | 13.8258 | 22.12% | 35.4524
7421 | 0 | 0 | 0 | 4 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.8292 | 40.2182 | 0 | 100.8292 | 303.8916 | 23.83% | 0 | 0 | 13.8258 | 22.12% | 40.2182
7422 | 0 | 0 | 0 | 4.6 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.4215 | 42.6596 | 0 | 106.4215 | 197.4701 | 15.48% | 0 | 0 | 13.8258 | 22.12% | 42.6596
7423 | 26 | 5 | 4 | 3.2 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.1441 | 43.8824 | 0 | 109.1441 | 88.326 | 6.925% | 0 | 0 | 13.8258 | 22.12% | 43.8824
7424 | 576 | 125 | 30 | 4.2 | 13.3 | 0 | 0 | 0 | 0 | 9.3071 | 0 | 0 | 9.3071 | 0 | 0 | 0 | 88.326 | 34.7633 | 0 | 88.326 | 0 | 0% | 0 | 0 | 13.8258 | 22.12% | 44.0704
7425 | 812 | 312 | 48 | 3.4 | 15.5 | 0 | 0 | 0 | 0 | 37.4244 | 0 | 0 | 37.4244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 6.8452 | 6.25 | 10% | 44.2696
7426 | 848 | 464 | 75 | 2.6 | 17.1 | 0 | 0 | 0 | 0 | 44.406 | 8.6748 | 0 | 44.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 44.406
7427 | 950 | 589 | 61 | 1.6 | 18.8 | 0 | 0 | 0 | 201.0141 | 44.3531 | 19.8305 | 0 | 44.3531 | 0 | 0 | 0 | 0 | 0 | 201.0141 | 0 | 201.0141 | 15.76% | 0 | 0 | 6.25 | 10% | 44.3531
7428 | 941 | 640 | 74 | 3.6 | 18.9 | 0 | 0 | 0 | 255.085 | 42.9298 | 29.0702 | 0 | 42.9298 | 0 | 0 | 0 | 0 | 0 | 255.085 | 0 | 456.0991 | 35.76% | 0 | 0 | 6.25 | 10% | 42.9298
7429 | 876 | 611 | 89 | 3.1 | 18.7 | 0 | 0 | 0 | 238.3183 | 67.1137 | 3.071 | 25 | 42.1137 | 0 | 0 | 0 | 0 | 0 | 238.3183 | 0 | 694.4174 | 54.44% | 25 | 0 | 28.839 | 46.14% | 42.1137
7430 | 777 | 537 | 115 | 3 | 18.8 | 0 | 0 | 0 | 206.2916 | 55.2057 | 9.5172 | 13.3664 | 41.8393 | 0 | 0 | 0 | 0 | 0 | 206.2916 | 0 | 900.7089 | 70.62% | 13.3664 | 0 | 40.9164 | 65.47% | 41.8393
7431 | 852 | 432 | 62 | 4.5 | 19 | 0 | 0 | 0 | 214.4034 | 59.1716 | 0 | 16.9702 | 42.2014 | 0 | 0 | 0 | 0 | 0 | 214.4034 | 0 | 1115.1123 | 87.42% | 16.9702 | 0 | 56.25 | 90% | 42.2014
7432 | 734 | 261 | 48 | 5 | 18.2 | 0 | 0 | 0 | 160.3979 | 42.7826 | 0 | 0 | 42.7826 | 0 | 0 | 0 | 0 | 0 | 160.3979 | 0 | 1275.5102 | 100% | 0 | 1.7139 | 54.3531 | 86.97% | 44.4966
7433 | 401 | 80 | 25 | 3.7 | 16.9 | 0 | 0 | 0 | 0 | 16.9036 | 0 | 0 | 16.9036 | 0 | 0 | 0 | 75.2603 | 28.9633 | 0 | 75.2603 | 1200.2499 | 94.1% | 0 | 0 | 54.3531 | 86.97% | 45.867
7434 | 0 | 1 | 1 | 3.8 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.3834 | 46.477 | 0 | 115.3834 | 1084.8665 | 85.05% | 0 | 0 | 54.3531 | 86.97% | 46.477
7435 | 0 | 0 | 0 | 2.5 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.406 | 44.796 | 0 | 111.406 | 973.4605 | 76.32% | 0 | 0 | 54.3531 | 86.97% | 44.796
7436 | 0 | 0 | 0 | 1.9 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4817 | 40.9535 | 0 | 102.4817 | 870.9788 | 68.28% | 0 | 0 | 54.3531 | 86.97% | 40.9535
7437 | 0 | 0 | 0 | 2.4 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9726 | 37.242 | 0 | 93.9726 | 777.0062 | 60.92% | 0 | 0 | 54.3531 | 86.97% | 37.242
7438 | 0 | 0 | 0 | 1.9 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4728 | 35.2853 | 0 | 89.4728 | 687.5334 | 53.9% | 0 | 0 | 54.3531 | 86.97% | 35.2853
7439 | 0 | 0 | 0 | 2.3 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8451 | 33.3104 | 0 | 84.8451 | 602.6883 | 47.25% | 0 | 0 | 54.3531 | 86.97% | 33.3104
7440 | 0 | 0 | 0 | 2.2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602.6883 | 47.25% | 0 | 16.9485 | 35.5956 | 56.95% | 16.9485
7441 | 0 | 0 | 0 | 2.3 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602.6883 | 47.25% | 0 | 0 | 35.5956 | 56.95% | 0
7442 | 0 | 0 | 0 | 1.7 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602.6883 | 47.25% | 0 | 0 | 35.5956 | 56.95% | 0
7443 | 0 | 0 | 0 | 1.8 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.3101 | 32.2297 | 0 | 82.3101 | 520.3782 | 40.8% | 0 | 0 | 35.5956 | 56.95% | 32.2297
7444 | 0 | 0 | 0 | 1.8 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7744 | 35.9162 | 0 | 90.7744 | 429.6038 | 33.68% | 0 | 0 | 35.5956 | 56.95% | 35.9162
7445 | 0 | 0 | 0 | 1.6 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.7058 | 40.6806 | 0 | 101.7058 | 327.898 | 25.71% | 0 | 0 | 35.5956 | 56.95% | 40.6806
7446 | 0 | 0 | 0 | 1.3 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.3557 | 43.1484 | 0 | 107.3557 | 220.5423 | 17.29% | 0 | 0 | 35.5956 | 56.95% | 43.1484
7447 | 24 | 5 | 4 | 1.1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.333 | 44.4534 | 0 | 110.333 | 110.2093 | 8.64% | 0 | 0 | 35.5956 | 56.95% | 44.4534
7448 | 532 | 119 | 33 | 0.6 | 12.1 | 0 | 0 | 0 | 0 | 8.944 | 0 | 0 | 8.944 | 0 | 0 | 0 | 90.9035 | 35.9189 | 0 | 90.9035 | 19.3058 | 1.514% | 0 | 0 | 35.5956 | 56.95% | 44.8628
7449 | 780 | 304 | 53 | 1.4 | 15 | 0 | 0 | 0 | 145.2962 | 35.9697 | 0 | 0 | 35.9697 | 0 | 0 | 0 | 0 | 0 | 145.2962 | 0 | 164.602 | 12.9% | 0 | 8.9976 | 25.6377 | 41.02% | 44.9673
7450 | 878 | 455 | 54 | 1.9 | 16.9 | 0 | 0 | 0 | 205.7041 | 51.894 | 0 | 6.7011 | 45.1929 | 0 | 0 | 0 | 0 | 0 | 205.7041 | 0 | 370.3061 | 29.03% | 6.7011 | 0 | 31.6925 | 50.71% | 45.1929
7451 | 669 | 537 | 170 | 3 | 18.4 | 0 | 0 | 0 | 168.0886 | 58.5403 | 0 | 13.3084 | 45.2319 | 0 | 0 | 0 | 0 | 0 | 168.0886 | 0 | 538.3947 | 42.21% | 13.3084 | 0 | 43.7175 | 69.95% | 45.2319
7452 | 335 | 517 | 310 | 4.8 | 19.4 | 0 | 0 | 0 | 77.4289 | 50.9804 | 0 | 7.2526 | 43.7278 | 0 | 0 | 0 | 0 | 0 | 77.4289 | 0 | 615.8236 | 48.28% | 7.2526 | 0 | 50.2706 | 80.43% | 43.7278
7453 | 254 | 427 | 271 | 5.1 | 20.2 | 0 | 0 | 0 | 54.0408 | 42.3529 | 0 | 0 | 42.3529 | 0 | 0 | 0 | 0 | 0 | 54.0408 | 0 | 669.8644 | 52.52% | 0 | 0.73838 | 49.4534 | 79.13% | 43.0913
7454 | 419 | 457 | 238 | 7.2 | 20.9 | 0 | 0 | 0 | 98.9474 | 50.3779 | 0 | 7.522 | 42.856 | 0 | 0 | 0 | 0 | 0 | 98.9474 | 0 | 768.8118 | 60.27% | 7.522 | 0 | 56.25 | 90% | 42.856
7455 | 51 | 201 | 175 | 7.2 | 21 | 0 | 0 | 0 | 0 | 16.1837 | 0 | 0 | 16.1837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768.8118 | 60.27% | 0 | 14.9362 | 39.7197 | 63.55% | 31.1198
7456 | 634 | 248 | 74 | 7.4 | 20.8 | 0 | 0 | 0 | 133.2532 | 40.678 | 0 | 0 | 40.678 | 0 | 0 | 0 | 0 | 0 | 133.2532 | 0 | 902.0649 | 70.72% | 0 | 5.2418 | 33.9183 | 54.27% | 45.9199
7457 | 412 | 78 | 22 | 8.7 | 19.5 | 0 | 0 | 0 | 56.4961 | 16.9066 | 0 | 0 | 16.9066 | 0 | 0 | 0 | 0 | 0 | 56.4961 | 0 | 958.561 | 75.15% | 0 | 25 | 6.25 | 10% | 41.9066
7458 | 0 | 1 | 1 | 5.5 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.1108 | 47.4936 | 0 | 118.1108 | 840.4502 | 65.89% | 0 | 0 | 6.25 | 10% | 47.4936
7459 | 0 | 0 | 0 | 5.6 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.4665 | 45.5829 | 0 | 113.4665 | 726.9837 | 57% | 0 | 0 | 6.25 | 10% | 45.5829
7460 | 0 | 0 | 0 | 5.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4678 | 41.7195 | 0 | 104.4678 | 622.5159 | 48.81% | 0 | 0 | 6.25 | 10% | 41.7195
7461 | 0 | 0 | 0 | 6.3 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8544 | 38.4356 | 0 | 96.8544 | 525.6615 | 41.21% | 0 | 0 | 6.25 | 10% | 38.4356
7462 | 0 | 0 | 0 | 4.9 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.5569 | 36.1599 | 0 | 91.5569 | 434.1046 | 34.03% | 0 | 0 | 6.25 | 10% | 36.1599
7463 | 0 | 0 | 0 | 4.9 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434.1046 | 34.03% | 0 | 0 | 6.25 | 10% | 0
7464 | 0 | 0 | 0 | 3.6 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434.1046 | 34.03% | 0 | 0 | 6.25 | 10% | 0
7465 | 0 | 0 | 0 | 6.1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434.1046 | 34.03% | 0 | 0 | 6.25 | 10% | 0
7466 | 0 | 0 | 0 | 7.1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434.1046 | 34.03% | 0 | 0 | 6.25 | 10% | 0
7467 | 0 | 0 | 0 | 6.8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434.1046 | 34.03% | 0 | 0 | 6.25 | 10% | 0
7468 | 0 | 0 | 0 | 4.4 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434.1046 | 34.03% | 0 | 0 | 6.25 | 10% | 0
7469 | 0 | 0 | 0 | 4.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6489 | 41.4953 | 0 | 103.6489 | 330.4557 | 25.91% | 0 | 0 | 6.25 | 10% | 41.4953
7470 | 0 | 0 | 0 | 3.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.0729 | 44.303 | 0 | 110.0729 | 220.3828 | 17.28% | 0 | 0 | 6.25 | 10% | 44.303
7471 | 3 | 3 | 3 | 2.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.7608 | 46.7852 | 0 | 115.7608 | 104.6219 | 8.202% | 0.9767 | 0 | 7.1325 | 11.41% | 45.8085
7472 | 129 | 65 | 37 | 4.6 | 10.8 | 0 | 0 | 0 | 0 | 4.2124 | 0 | 0 | 4.2124 | 0 | 0 | 0 | 104.6219 | 41.929 | 0 | 104.6219 | 0 | 0% | 0 | 0 | 7.1325 | 11.41% | 46.1413
7473 | 748 | 298 | 61 | 7.1 | 12.5 | 0 | 0 | 0 | 133.1353 | 36.6038 | 0 | 0 | 36.6038 | 0 | 0 | 0 | 0 | 0 | 133.1353 | 0 | 133.1353 | 10.44% | 0 | 0.7974 | 6.25 | 10% | 37.4012
7474 | 836 | 457 | 80 | 7.7 | 13.7 | 0 | 0 | 0 | 189.5898 | 46.353 | 8.5918 | 0 | 46.353 | 0 | 0 | 0 | 0 | 0 | 189.5898 | 0 | 322.7251 | 25.3% | 0 | 0 | 6.25 | 10% | 46.353
7475 | 898 | 591 | 100 | 5.9 | 14.6 | 0 | 0 | 0 | 228.6325 | 45.9477 | 22.9449 | 0 | 45.9477 | 0 | 0 | 0 | 0 | 0 | 228.6325 | 0 | 551.3576 | 43.23% | 0 | 0 | 6.25 | 10% | 45.9477
7476 | 920 | 632 | 87 | 2.6 | 15.8 | 0 | 0 | 0 | 249.1112 | 44.4701 | 27.0141 | 0 | 44.4701 | 0 | 0 | 0 | 0 | 0 | 249.1112 | 0 | 800.4688 | 62.76% | 0 | 0 | 6.25 | 10% | 44.4701
7477 | 920 | 625 | 86 | 5.7 | 16.1 | 0 | 0 | 0 | 248.5104 | 58.5476 | 13.4524 | 15.136 | 43.4117 | 0 | 0 | 0 | 0 | 0 | 248.5104 | 0 | 1048.9792 | 82.24% | 15.136 | 0 | 19.9263 | 31.88% | 43.4117
7478 | 891 | 553 | 81 | 4.8 | 16.4 | 0 | 0 | 0 | 226.531 | 68.0036 | 1.8468 | 25 | 43.0036 | 0 | 0 | 0 | 0 | 0 | 226.531 | 0 | 1275.5102 | 100% | 25 | 0 | 42.5153 | 68.02% | 43.0036
7479 | 830 | 426 | 72 | 2.4 | 16.9 | 0 | 0 | 0 | 0 | 58.441 | 0 | 15.2007 | 43.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 15.2007 | 0 | 56.25 | 90% | 43.2404
7480 | 721 | 259 | 55 | 5.3 | 16.4 | 0 | 0 | 0 | 0 | 43.4699 | 7.1054e-15 | 0 | 43.4699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 2.3108 | 53.6926 | 85.91% | 45.7806
7481 | 426 | 81 | 27 | 5.2 | 14.9 | 0 | 0 | 0 | 0 | 18.1609 | 0 | 0 | 18.1609 | 0 | 0 | 0 | 74.3264 | 28.6266 | 0 | 74.3264 | 1201.1838 | 94.17% | 0 | 0 | 53.6926 | 85.91% | 46.7875
7482 | 0 | 1 | 1 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.6953 | 46.6664 | 0 | 115.6953 | 1085.4885 | 85.1% | 0 | 0 | 53.6926 | 85.91% | 46.6664
7483 | 0 | 0 | 0 | 1.3 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.778 | 45.0244 | 0 | 111.778 | 973.7104 | 76.34% | 0 | 0 | 53.6926 | 85.91% | 45.0244
7484 | 0 | 0 | 0 | 4.6 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.2095 | 41.7293 | 0 | 104.2095 | 869.5009 | 68.17% | 0 | 0 | 53.6926 | 85.91% | 41.7293
7485 | 0 | 0 | 0 | 2.8 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2542 | 38.7169 | 0 | 97.2542 | 772.2467 | 60.54% | 0 | 0 | 53.6926 | 85.91% | 38.7169
7486 | 0 | 0 | 0 | 3.9 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.255 | 36.1014 | 0 | 91.255 | 680.9918 | 53.39% | 0 | 0 | 53.6926 | 85.91% | 36.1014
7487 | 0 | 0 | 0 | 6.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2088 | 33.9149 | 0 | 86.2088 | 594.783 | 46.63% | 0 | 0 | 53.6926 | 85.91% | 33.9149
7488 | 0 | 0 | 0 | 8.3 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.1449 | 32.1364 | 0 | 82.1449 | 512.6381 | 40.19% | 0 | 0 | 53.6926 | 85.91% | 32.1364
7489 | 0 | 0 | 0 | 8.8 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0698 | 31.2284 | 0 | 80.0698 | 432.5682 | 33.91% | 0 | 0 | 53.6926 | 85.91% | 31.2284
7490 | 0 | 0 | 0 | 4.1 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432.5682 | 33.91% | 0 | 25 | 26.0243 | 41.64% | 25
7491 | 0 | 0 | 0 | 4.8 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432.5682 | 33.91% | 0 | 13.6311 | 10.9383 | 17.5% | 13.6311
7492 | 0 | 0 | 0 | 1.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0242 | 31.6768 | 0 | 81.0242 | 351.5441 | 27.56% | 0 | 0 | 10.9383 | 17.5% | 31.6768
7493 | 0 | 0 | 0 | 3.3 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8267 | 33.3381 | 0 | 84.8267 | 266.7174 | 20.91% | 0.107 | 0 | 11.035 | 17.66% | 33.2311
7494 | 0 | 0 | 0 | 2.5 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0623 | 35.1864 | 0 | 89.0623 | 177.6552 | 13.93% | 0 | 0 | 11.035 | 17.66% | 35.1864
7495 | 29 | 5 | 4 | 1.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.0437 | 38.6681 | 0 | 97.0437 | 80.6115 | 6.32% | 0 | 0 | 11.035 | 17.66% | 38.6681
7496 | 565 | 117 | 30 | 1.6 | 7.6 | 0 | 0 | 0 | 0 | 9.0608 | 0 | 0 | 9.0608 | 0 | 0 | 0 | 80.6115 | 31.4959 | 0 | 80.6115 | 0 | 0% | 0 | 0 | 11.035 | 17.66% | 40.5566
7497 | 804 | 300 | 48 | 1.2 | 11.7 | 0 | 0 | 0 | 125.0594 | 36.6454 | 0 | 0 | 36.6454 | 0 | 0 | 0 | 0 | 0 | 125.0594 | 0 | 125.0594 | 9.805% | 0 | 4.3235 | 6.25 | 10% | 40.9689
7498 | 898 | 458 | 55 | 1 | 14.3 | 0 | 0 | 0 | 0 | 40.6346 | 11.8205 | 0 | 40.6346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.0594 | 9.805% | 0 | 0 | 6.25 | 10% | 40.6346
7499 | 939 | 570 | 59 | 1.1 | 15.8 | 0 | 0 | 0 | 243.2848 | 40.7725 | 22.3716 | 0 | 40.7725 | 0 | 0 | 0 | 0 | 0 | 243.2848 | 0 | 368.3442 | 28.88% | 0 | 0 | 6.25 | 10% | 40.7725
7500 | 957 | 624 | 60 | 3.4 | 16.5 | 0 | 0 | 0 | 258.781 | 39.9411 | 32.0589 | 0 | 39.9411 | 0 | 0 | 0 | 0 | 0 | 258.781 | 0 | 627.1252 | 49.17% | 0 | 0 | 6.25 | 10% | 39.9411
7501 | 945 | 617 | 65 | 3.4 | 16.7 | 0 | 0 | 0 | 257.6375 | 53.7426 | 18.2574 | 15.119 | 38.6236 | 0 | 0 | 0 | 0 | 0 | 257.6375 | 0 | 884.7627 | 69.37% | 15.119 | 0 | 19.911 | 31.86% | 38.6236
7502 | 830 | 531 | 93 | 3.6 | 17.4 | 0 | 0 | 0 | 219.7583 | 62.7211 | 3.8718 | 25 | 37.7211 | 0 | 0 | 0 | 0 | 0 | 219.7583 | 0 | 1104.521 | 86.59% | 25 | 0 | 42.5 | 68% | 37.7211
7503 | 695 | 391 | 91 | 4 | 17.4 | 0 | 0 | 0 | 170.9892 | 53.2159 | 0 | 15.2176 | 37.9983 | 0 | 0 | 0 | 0 | 0 | 170.9892 | 0 | 1275.5102 | 100% | 15.2176 | 0 | 56.25 | 90% | 37.9983
7504 | 53 | 135 | 116 | 3.5 | 16.3 | 0 | 0 | 0 | 0 | 11.2058 | 0 | 0 | 11.2058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 20.178 | 33.9183 | 54.27% | 31.3837
7505 | 10 | 37 | 36 | 2.6 | 14.7 | 0 | 0 | 0 | 0 | 2.3585 | 0 | 0 | 2.3585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 6.25 | 10% | 27.3585
7506 | 0 | 0 | 0 | 1.4 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 6.25 | 10% | 0
7507 | 0 | 0 | 0 | 1.5 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.135 | 36.0172 | 0 | 91.135 | 1184.3752 | 92.86% | 0 | 0 | 6.25 | 10% | 36.0172
7508 | 0 | 0 | 0 | 2 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.9768 | 0 | 38.2653 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 12.9768
7509 | 0 | 0 | 0 | 3.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7510 | 0 | 0 | 0 | 5.4 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7511 | 0 | 0 | 0 | 5.7 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7512 | 0 | 0 | 0 | 5.2 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7513 | 0 | 0 | 0 | 7.6 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7514 | 0 | 0 | 0 | 9.8 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7515 | 0 | 0 | 0 | 10.7 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7516 | 0 | 0 | 0 | 9.2 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7517 | 0 | 0 | 0 | 6 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7518 | 0 | 0 | 0 | 3.7 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7519 | 0 | 2 | 2 | 3.2 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 0
7520 | 0 | 35 | 35 | 3 | 14.2 | 0 | 0 | 0 | 0 | 1.9086 | 0 | 0 | 1.9086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 0 | 0 | 6.25 | 10% | 1.9086
7521 | 0 | 87 | 87 | 4.6 | 14.4 | 0 | 0 | 0 | 0 | 6.0089 | 0 | 6.0089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 6.0089 | 0 | 11.6794 | 18.69% | 0
7522 | 2 | 186 | 184 | 5.9 | 13.9 | 0 | 0 | 0 | 0 | 13.9173 | 0 | 13.9173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 13.9173 | 0 | 24.2545 | 38.81% | 0
7523 | 121 | 319 | 247 | 6.6 | 12.9 | 0 | 0 | 0 | 0 | 28.3333 | 0 | 25 | 3.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.1099 | 89.86% | 25 | 0 | 46.8435 | 74.95% | 3.3333
7524 | 263 | 439 | 279 | 5.9 | 14.3 | 0 | 0 | 0 | 55.0246 | 43.0081 | 0 | 5.8037 | 37.2044 | 0 | 0 | 0 | 0 | 0 | 55.0246 | 0 | 1201.1344 | 94.17% | 5.8037 | 0 | 52.0875 | 83.34% | 37.2044
7525 | 2 | 218 | 215 | 7.3 | 14 | 0 | 0 | 0 | 0 | 15.2755 | 0 | 4.6068 | 10.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.1344 | 94.17% | 4.6068 | 0 | 56.25 | 90% | 10.6687
7526 | 1 | 152 | 151 | 6.3 | 13.7 | 0 | 0 | 0 | 0 | 10.1389 | 0 | 0 | 10.1389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.1344 | 94.17% | 0 | 0 | 56.25 | 90% | 10.1389
7527 | 0 | 116 | 115 | 7.3 | 13.3 | 0 | 0 | 0 | 0 | 7.4662 | 0 | 0 | 7.4662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.1344 | 94.17% | 0 | 0 | 56.25 | 90% | 7.4662
7528 | 0 | 69 | 69 | 6 | 13.3 | 0 | 0 | 0 | 0 | 4.165 | 0 | 0 | 4.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.1344 | 94.17% | 0 | 0 | 56.25 | 90% | 4.165
7529 | 1 | 22 | 22 | 7.9 | 12.9 | 0 | 0 | 0 | 0 | 1.0487 | 0 | 0 | 1.0487 | 0 | 0 | 0 | 98.0557 | 39.0107 | 0 | 98.0557 | 1103.0788 | 86.48% | 0 | 0 | 56.25 | 90% | 40.0594
7530 | 0 | 0 | 0 | 4.2 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2636 | 41.3031 | 0 | 103.2636 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 41.3031
7531 | 0 | 0 | 0 | 4.9 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7532 | 0 | 0 | 0 | 4 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7533 | 0 | 0 | 0 | 4.3 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7534 | 0 | 0 | 0 | 2.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7535 | 0 | 0 | 0 | 4.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7536 | 0 | 0 | 0 | 7.4 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7537 | 0 | 0 | 0 | 4.6 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7538 | 0 | 0 | 0 | 6.6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7539 | 0 | 0 | 0 | 7.6 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7540 | 0 | 0 | 0 | 8.8 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7541 | 0 | 0 | 0 | 9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999.8151 | 78.39% | 0 | 0 | 56.25 | 90% | 0
7542 | 0 | 0 | 0 | 5.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.1032 | 44.7723 | 0 | 111.1032 | 888.7119 | 69.68% | 0 | 0 | 56.25 | 90% | 44.7723
7543 | 5 | 3 | 3 | 3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.6314 | 46.7569 | 0 | 115.6314 | 773.0806 | 60.61% | 0 | 0 | 56.25 | 90% | 46.7569
7544 | 14 | 43 | 42 | 3.3 | 10.5 | 0 | 0 | 0 | 0 | 1.8673 | 0 | 0 | 1.8673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.0806 | 60.61% | 0 | 25 | 28.5817 | 45.73% | 26.8673
7545 | 0 | 116 | 116 | 5.9 | 11.3 | 0 | 0 | 0 | 0 | 9.0785 | 0 | 0 | 9.0785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.0806 | 60.61% | 0 | 0 | 28.5817 | 45.73% | 9.0785
7546 | 12 | 217 | 209 | 4.6 | 12.7 | 0 | 0 | 0 | 0 | 17.0194 | 0 | 0 | 17.0194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.0806 | 60.61% | 0 | 0 | 28.5817 | 45.73% | 17.0194
7547 | 16 | 267 | 255 | 4.4 | 14 | 0 | 0 | 0 | 0 | 20.3174 | 0 | 0 | 20.3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.0806 | 60.61% | 0 | 0 | 28.5817 | 45.73% | 20.3174
7548 | 1 | 223 | 221 | 7 | 14.6 | 0 | 0 | 0 | 0 | 15.7938 | 0 | 0 | 15.7938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.0806 | 60.61% | 0 | 0 | 28.5817 | 45.73% | 15.7938
7549 | 8 | 235 | 228 | 5.6 | 15.3 | 0 | 0 | 0 | 0 | 16.7416 | 0 | 0 | 16.7416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.0806 | 60.61% | 0 | 0 | 28.5817 | 45.73% | 16.7416
7550 | 0 | 154 | 153 | 4.5 | 15.8 | 0 | 0 | 0 | 0 | 10.1392 | 0 | 0 | 10.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.0806 | 60.61% | 0 | 0 | 28.5817 | 45.73% | 10.1392
7551 | 0 | 132 | 131 | 6.2 | 16.4 | 0 | 0 | 0 | 0 | 8.6275 | 0 | 0 | 8.6275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773.0806 | 60.61% | 0 | 11.4046 | 15.9598 | 25.54% | 20.0322
7552 | 0 | 108 | 107 | 6.7 | 16.5 | 0 | 0 | 0 | 0 | 7.1004 | 0 | 0 | 7.1004 | 0 | 0 | 0 | 101.7456 | 40.4656 | 0 | 101.7456 | 671.3349 | 52.63% | 0 | 0 | 15.9598 | 25.54% | 47.5661
7553 | 0 | 35 | 35 | 5.4 | 16.2 | 0 | 0 | 0 | 0 | 1.83 | 0 | 0 | 1.83 | 0 | 0 | 0 | 116.6054 | 46.9282 | 0 | 116.6054 | 554.7295 | 43.49% | 0 | 0 | 15.9598 | 25.54% | 48.7582
7554 | 0 | 0 | 0 | 2.4 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.6127 | 49.1635 | 0 | 121.6127 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 49.1635
7555 | 0 | 0 | 0 | 2.5 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7556 | 0 | 0 | 0 | 1.3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7557 | 0 | 0 | 0 | 2.3 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7558 | 0 | 0 | 0 | 1.2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7559 | 0 | 0 | 0 | 2.1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7560 | 0 | 0 | 0 | 2 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7561 | 0 | 0 | 0 | 1.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7562 | 0 | 0 | 0 | 1.2 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7563 | 0 | 0 | 0 | 1.6 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7564 | 0 | 0 | 0 | 2.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433.1168 | 33.96% | 0 | 0 | 15.9598 | 25.54% | 0
7565 | 0 | 0 | 0 | 1.6 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.9898 | 42.551 | 0 | 105.9898 | 327.127 | 25.65% | 0 | 0 | 15.9598 | 25.54% | 42.551
7566 | 0 | 0 | 0 | 1.5 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.5401 | 45.8391 | 0 | 113.5401 | 213.5869 | 16.75% | 0 | 0 | 15.9598 | 25.54% | 45.8391
7567 | 4 | 4 | 3 | 1.2 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.7952 | 47.2527 | 0 | 116.7952 | 96.7917 | 7.588% | 0 | 0 | 15.9598 | 25.54% | 47.2527
7568 | 523 | 124 | 48 | 1.8 | 12 | 0 | 0 | 0 | 0 | 9.0572 | 0 | 0 | 9.0572 | 0 | 0 | 0 | 96.7917 | 38.4866 | 0 | 96.7917 | 0 | 0% | 0 | 0 | 15.9598 | 25.54% | 47.5438
7569 | 788 | 321 | 83 | 2.6 | 15.1 | 0 | 0 | 0 | 0 | 38.6102 | 0 | 0 | 38.6102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 8.7734 | 6.25 | 10% | 47.3836
7570 | 863 | 446 | 70 | 1.2 | 17.2 | 0 | 0 | 0 | 198.5638 | 47.0758 | 4.8581 | 0 | 47.0758 | 0 | 0 | 0 | 0 | 0 | 198.5638 | 0 | 198.5638 | 15.57% | 0 | 0 | 6.25 | 10% | 47.0758
7571 | 802 | 507 | 75 | 1.5 | 18.4 | 0 | 0 | 0 | 203.9014 | 46.8056 | 10.4521 | 0 | 46.8056 | 0 | 0 | 0 | 0 | 0 | 203.9014 | 0 | 402.4651 | 31.55% | 0 | 0 | 6.25 | 10% | 46.8056
7572 | 941 | 603 | 60 | 3.8 | 19.4 | 0 | 0 | 0 | 252.3125 | 45.3572 | 25.1644 | 0 | 45.3572 | 0 | 0 | 0 | 0 | 0 | 252.3125 | 0 | 654.7776 | 51.33% | 0 | 0 | 6.25 | 10% | 45.3572
7573 | 949 | 601 | 59 | 6.1 | 19.7 | 0 | 0 | 0 | 16.9482 | 62.1803 | 9.8197 | 17.4511 | 44.7291 | 0 | 0 | 0 | 0 | 0 | 16.9482 | 0 | 671.7258 | 52.66% | 17.4511 | 0 | 22.0181 | 35.23% | 44.7291
7574 | 913 | 529 | 59 | 6.4 | 19.9 | 0 | 0 | 0 | 239.8978 | 69.0031 | 0 | 24.6416 | 44.3615 | 0 | 0 | 0 | 0 | 0 | 239.8978 | 0 | 911.6236 | 71.47% | 24.6416 | 0 | 44.2833 | 70.85% | 44.3615
7575 | 850 | 403 | 53 | 5.4 | 20 | 0 | 0 | 0 | 210.9482 | 58.1165 | 0 | 13.2439 | 44.8726 | 0 | 0 | 0 | 0 | 0 | 210.9482 | 0 | 1122.5718 | 88.01% | 13.2439 | 0 | 56.25 | 90% | 44.8726
7576 | 722 | 238 | 43 | 6.5 | 19.4 | 0 | 0 | 0 | 152.9384 | 41.5911 | 0 | 0 | 41.5911 | 0 | 0 | 0 | 0 | 0 | 152.9384 | 0 | 1275.5102 | 100% | 0 | 6.2117 | 49.3753 | 79% | 47.8028
7577 | 370 | 66 | 21 | 3 | 18.3 | 0 | 0 | 0 | 0 | 15.1994 | 0 | 0 | 15.1994 | 0 | 0 | 0 | 86.6159 | 33.8192 | 0 | 86.6159 | 1188.8943 | 93.21% | 0 | 0 | 49.3753 | 79% | 49.0186
7578 | 0 | 0 | 0 | 2.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.3441 | 49.4866 | 0 | 122.3441 | 1066.5502 | 83.62% | 0 | 0 | 49.3753 | 79% | 49.4866
7579 | 0 | 0 | 0 | 4.7 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.6134 | 47.8808 | 0 | 118.6134 | 947.9368 | 74.32% | 0 | 0 | 49.3753 | 79% | 47.8808
7580 | 0 | 0 | 0 | 2.6 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.6336 | 44.0439 | 0 | 109.6336 | 838.3032 | 65.72% | 0 | 0 | 49.3753 | 79% | 44.0439
7581 | 0 | 0 | 0 | 1.6 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.6773 | 39.7642 | 0 | 99.6773 | 738.6259 | 57.91% | 0 | 0 | 49.3753 | 79% | 39.7642
7582 | 0 | 0 | 0 | 1.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.7288 | 44.5984 | 0 | 110.7288 | 627.8971 | 49.23% | 7.6085 | 0 | 56.25 | 90% | 36.9899
7583 | 0 | 0 | 0 | 1.3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1013 | 34.7226 | 0 | 88.1013 | 539.7958 | 42.32% | 0 | 0 | 56.25 | 90% | 34.7226
7584 | 0 | 0 | 0 | 1.5 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.7958 | 42.32% | 0 | 8.3744 | 46.9818 | 75.17% | 8.3744
7585 | 0 | 0 | 0 | 3.4 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.7958 | 42.32% | 0 | 0 | 46.9818 | 75.17% | 0
7586 | 0 | 0 | 0 | 3.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.7958 | 42.32% | 0 | 0 | 46.9818 | 75.17% | 0
7587 | 0 | 0 | 0 | 6 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 539.7958 | 42.32% | 0 | 25 | 19.3134 | 30.9% | 25
7588 | 0 | 0 | 0 | 7.1 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2855 | 37.7497 | 0 | 95.2855 | 444.5103 | 34.85% | 0.67754 | 0 | 19.9256 | 31.88% | 37.0721
7589 | 0 | 0 | 0 | 9.8 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.5257 | 43.0482 | 0 | 107.5257 | 336.9846 | 26.42% | 0 | 0 | 19.9256 | 31.88% | 43.0482
7590 | 0 | 0 | 0 | 9.9 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1901 | 45.9631 | 0 | 114.1901 | 222.7946 | 17.47% | 0 | 0 | 19.9256 | 31.88% | 45.9631
7591 | 1 | 2 | 2 | 10.7 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.2563 | 47.2959 | 0 | 117.2563 | 105.5382 | 8.274% | 0 | 0 | 19.9256 | 31.88% | 47.2959
7592 | 329 | 84 | 37 | 8.9 | 15.4 | 0 | 0 | 0 | 0 | 5.8081 | 0 | 0 | 5.8081 | 0 | 0 | 0 | 105.5382 | 42.1661 | 0 | 105.5382 | 0 | 0% | 0 | 0 | 19.9256 | 31.88% | 47.9741
7593 | 739 | 284 | 62 | 10.2 | 17.6 | 0 | 0 | 0 | 124.0995 | 35.8444 | 0 | 0 | 35.8444 | 0 | 0 | 0 | 0 | 0 | 124.0995 | 0 | 124.0995 | 9.729% | 0 | 12.3568 | 6.25 | 10% | 48.2011
7594 | 874 | 441 | 62 | 10.1 | 18.7 | 0 | 0 | 0 | 193.3224 | 47.7485 | 6.7404 | 0 | 47.7485 | 0 | 0 | 0 | 0 | 0 | 193.3224 | 0 | 317.4219 | 24.89% | 0 | 0 | 6.25 | 10% | 47.7485
7595 | 925 | 555 | 66 | 8 | 21.1 | 0 | 0 | 0 | 232.2511 | 47.3293 | 18.5475 | 0 | 47.3293 | 0 | 0 | 0 | 0 | 0 | 232.2511 | 0 | 549.673 | 43.09% | 0 | 0 | 6.25 | 10% | 47.3293
7596 | 924 | 597 | 66 | 7.1 | 21.7 | 0 | 0 | 0 | 244.0223 | 60.4609 | 10.4903 | 14.6622 | 45.7987 | 0 | 0 | 0 | 0 | 0 | 244.0223 | 0 | 793.6953 | 62.23% | 14.6622 | 0 | 19.4982 | 31.2% | 45.7987
7597 | 750 | 516 | 87 | 3.8 | 22.1 | 0 | 0 | 0 | 199.5812 | 61.9001 | 0 | 16.9788 | 44.9213 | 0 | 0 | 0 | 0 | 0 | 199.5812 | 0 | 993.2765 | 77.87% | 16.9788 | 0 | 34.8395 | 55.74% | 44.9213
7598 | 864 | 511 | 68 | 0.1 | 22 | 0 | 0 | 0 | 202.1372 | 59.6778 | 0 | 15.3525 | 44.3253 | 0 | 0 | 0 | 0 | 0 | 202.1372 | 0 | 1195.4137 | 93.72% | 15.3525 | 0 | 48.7115 | 77.94% | 44.3253
7599 | 852 | 404 | 56 | 0 | 22.1 | 0 | 0 | 0 | 0 | 53.167 | 0 | 8.3431 | 44.8238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.4137 | 93.72% | 8.3431 | 0 | 56.25 | 90% | 44.8238
7600 | 403 | 147 | 24 | 0 | 11.2 | 0 | 0 | 0 | 80.0965 | 23.0339 | 0 | 0 | 23.0339 | 0 | 0 | 0 | 0 | 0 | 80.0965 | 0 | 1275.5102 | 100% | 0 | 24.8998 | 28.6926 | 45.91% | 47.9337
7601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.0546 | 49.0228 | 0 | 121.0546 | 1154.4556 | 90.51% | 0 | 0 | 28.6926 | 45.91% | 49.0228
7602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.4814 | 49.644 | 0 | 122.4814 | 1031.9742 | 80.91% | 0 | 0 | 28.6926 | 45.91% | 49.644
7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.2989 | 47.3878 | 0 | 117.2989 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 47.3878
7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 914.6753 | 71.71% | 0 | 0 | 28.6926 | 45.91% | 0
7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.7511 | 45.8433 | 0 | 113.7511 | 800.9242 | 62.79% | 0 | 0 | 28.6926 | 45.91% | 45.8433
7615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.7404 | 47.58 | 0 | 117.7404 | 683.1838 | 53.56% | 0 | 0 | 28.6926 | 45.91% | 47.58
7616 | 137 | 48 | 22 | 1.9 | 4.7 | 0 | 0 | 0 | 0 | 2.568 | 0 | 0 | 2.568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 683.1838 | 53.56% | 0 | 0 | 28.6926 | 45.91% | 2.568
7617 | 511 | 248 | 94 | 6.5 | 15.8 | 0 | 0 | 0 | 80.8481 | 29.4017 | 0 | 0 | 29.4017 | 0 | 0 | 0 | 0 | 0 | 80.8481 | 0 | 764.0318 | 59.9% | 0 | 0 | 28.6926 | 45.91% | 29.4017
7618 | 128 | 228 | 172 | 6 | 16.4 | 0 | 0 | 0 | 0 | 21.8788 | 0 | 0 | 21.8788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.0318 | 59.9% | 0 | 0 | 28.6926 | 45.91% | 21.8788
7619 | 72 | 296 | 256 | 8.9 | 16.4 | 0 | 0 | 0 | 0 | 26.0139 | 0 | 0 | 26.0139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.0318 | 59.9% | 0 | 0 | 28.6926 | 45.91% | 26.0139
7620 | 16 | 248 | 237 | 13 | 16.7 | 0 | 0 | 0 | 0 | 18.3382 | 0 | 0 | 18.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.0318 | 59.9% | 0 | 0 | 28.6926 | 45.91% | 18.3382
7621 | 64 | 292 | 254 | 11.1 | 17.1 | 0 | 0 | 0 | 0 | 24.9204 | 0 | 0 | 24.9204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.0318 | 59.9% | 0 | 0 | 28.6926 | 45.91% | 24.9204
7622 | 170 | 301 | 210 | 12.4 | 17.1 | 0 | 0 | 0 | 0 | 29.8513 | 0 | 0 | 29.8513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.0318 | 59.9% | 0 | 0 | 28.6926 | 45.91% | 29.8513
7623 | 10 | 169 | 164 | 12.2 | 14.2 | 0 | 0 | 0 | 0 | 12.1568 | 0 | 0 | 12.1568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764.0318 | 59.9% | 0 | 0 | 28.6926 | 45.91% | 12.1568
7624 | 45 | 137 | 123 | 9.2 | 13.2 | 0 | 0 | 0 | 0 | 11.774 | 0 | 0 | 11.774 | 0 | 0 | 0 | 61.9756 | 23.2976 | 0 | 61.9756 | 702.0562 | 55.04% | 0 | 14.7033 | 12.42 | 19.87% | 49.7749
7625 | 3 | 34 | 33 | 10.3 | 12.2 | 0 | 0 | 0 | 0 | 1.8324 | 0 | 0 | 1.8324 | 0 | 0 | 0 | 119.0298 | 48.1676 | 0 | 119.0298 | 583.0264 | 45.71% | 0 | 0 | 12.42 | 19.87% | 50
7626 | 0 | 0 | 0 | 5.6 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.161 | 50 | 0 | 123.161 | 459.8654 | 36.05% | 0 | 0 | 12.42 | 19.87% | 50
7627 | 0 | 0 | 0 | 4.1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.8524 | 48.9908 | 0 | 120.8524 | 339.0131 | 26.58% | 0 | 0 | 12.42 | 19.87% | 48.9908
7628 | 0 | 0 | 0 | 6.1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.9442 | 45.0968 | 0 | 111.9442 | 227.0689 | 17.8% | 0 | 2.0819e-12 | 12.42 | 19.87% | 45.0968
7629 | 0 | 0 | 0 | 6.7 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 1.605e-15 | 12.42 | 19.87% | 1.605e-15
7630 | 0 | 0 | 0 | 5.5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 0 | 12.42 | 19.87% | 0
7631 | 0 | 0 | 0 | 4.3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 0 | 12.42 | 19.87% | 0
7632 | 0 | 0 | 0 | 7.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 0 | 12.42 | 19.87% | 0
7633 | 0 | 0 | 0 | 7.8 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 0 | 12.42 | 19.87% | 0
7634 | 0 | 0 | 0 | 5.2 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 0 | 12.42 | 19.87% | 0
7635 | 0 | 0 | 0 | 5.4 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 0 | 12.42 | 19.87% | 0
7636 | 0 | 0 | 0 | 7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 0 | 12.42 | 19.87% | 0
7637 | 0 | 0 | 0 | 6.4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 0 | 12.42 | 19.87% | 0
7638 | 0 | 0 | 0 | 9.4 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.0689 | 17.8% | 0 | 0 | 12.42 | 19.87% | 0
7639 | 1 | 2 | 2 | 6.4 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.7714 | 48.5772 | 0 | 119.7714 | 107.2974 | 8.412% | 0 | 0 | 12.42 | 19.87% | 48.5772
7640 | 387 | 88 | 32 | 7.5 | 9 | 0 | 0 | 0 | 0 | 6.451 | 0 | 0 | 6.451 | 0 | 0 | 0 | 107.2974 | 43.1289 | 0 | 107.2974 | 0 | 0% | 0 | 0 | 12.42 | 19.87% | 49.5799
7641 | 733 | 272 | 58 | 4.7 | 10.6 | 0 | 0 | 0 | 125.9372 | 35.4884 | 0 | 0 | 35.4884 | 0 | 0 | 0 | 0 | 0 | 125.9372 | 0 | 125.9372 | 9.873% | 0 | 5.5749 | 6.25 | 10% | 41.0634
7642 | 848 | 433 | 72 | 6 | 12.6 | 0 | 0 | 0 | 188.9256 | 54.2975 | 0 | 5.0978 | 49.1997 | 0 | 0 | 0 | 0 | 0 | 188.9256 | 0 | 314.8628 | 24.69% | 5.0978 | 0 | 10.8562 | 17.37% | 49.1997
7643 | 909 | 556 | 84 | 6.9 | 13 | 0 | 0 | 0 | 227.7443 | 68.4394 | 0 | 19.801 | 48.6384 | 0 | 0 | 0 | 0 | 0 | 227.7443 | 0 | 542.6071 | 42.54% | 19.801 | 0 | 28.7476 | 46% | 48.6384
7644 | 301 | 394 | 220 | 4 | 13.2 | 0 | 0 | 0 | 67.0244 | 41.5765 | 0 | 0 | 41.5765 | 0 | 0 | 0 | 0 | 0 | 67.0244 | 0 | 609.6315 | 47.8% | 0 | 0 | 28.7476 | 46% | 41.5765
7645 | 139 | 300 | 219 | 6.7 | 12.9 | 0 | 0 | 0 | 0 | 28.9663 | 0 | 0 | 28.9663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609.6315 | 47.8% | 0 | 0 | 28.7476 | 46% | 28.9663
7646 | 643 | 568 | 236 | 6.9 | 13.9 | 0 | 0 | 0 | 161.2399 | 67.7376 | 0 | 21.7536 | 45.984 | 0 | 0 | 0 | 0 | 0 | 161.2399 | 0 | 770.8714 | 60.44% | 21.7536 | 0 | 48.4033 | 77.45% | 45.984
7647 | 209 | 222 | 128 | 5.9 | 12.6 | 0 | 0 | 0 | 35.7258 | 25.0867 | 0 | 0 | 25.0867 | 0 | 0 | 0 | 0 | 0 | 35.7258 | 0 | 806.5972 | 63.24% | 0 | 21.5518 | 24.5513 | 39.28% | 46.6385
7648 | 192 | 150 | 92 | 5.6 | 12.3 | 0 | 0 | 0 | 0 | 18.4206 | 0 | 0 | 18.4206 | 0 | 0 | 0 | 62.6426 | 23.6047 | 0 | 62.6426 | 743.9546 | 58.33% | 0 | 7.2441 | 16.534 | 26.45% | 49.2693
7649 | 150 | 62 | 40 | 3.9 | 11.3 | 0 | 0 | 0 | 0 | 9.5328 | 0 | 0 | 9.5328 | 0 | 0 | 0 | 100.661 | 40.1905 | 0 | 100.661 | 643.2936 | 50.43% | 0 | 0 | 16.534 | 26.45% | 49.7233
7650 | 0 | 0 | 0 | 2 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.2579 | 49.215 | 0 | 121.2579 | 522.0357 | 40.93% | 0 | 0 | 16.534 | 26.45% | 49.215
7651 | 0 | 0 | 0 | 1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.5171 | 47.6051 | 0 | 117.5171 | 404.5186 | 31.71% | 0 | 0 | 16.534 | 26.45% | 47.6051
7652 | 0 | 0 | 0 | 1.6 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.7595 | 44.218 | 0 | 109.7595 | 294.7591 | 23.11% | 0 | 0 | 16.534 | 26.45% | 44.218
7653 | 0 | 0 | 0 | 0.7 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6303 | 40.6667 | 0 | 101.6303 | 193.1288 | 15.14% | 0 | 0 | 16.534 | 26.45% | 40.6667
7654 | 0 | 0 | 0 | 1.4 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8422e-14 | 0 | 0 | 2.8422e-14 | 193.1288 | 15.14% | 0 | 0.20767 | 16.3042 | 26.09% | 0.20767
7655 | 0 | 0 | 0 | 1.9 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.1288 | 15.14% | 0 | 0 | 16.3042 | 26.09% | 0
7656 | 0 | 0 | 0 | 0.8 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.1288 | 15.14% | 0 | 0 | 16.3042 | 26.09% | 0
7657 | 0 | 0 | 0 | 1 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.1288 | 15.14% | 0 | 0 | 16.3042 | 26.09% | 0
7658 | 0 | 0 | 0 | 2.5 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.1288 | 15.14% | 0 | 0 | 16.3042 | 26.09% | 0
7659 | 0 | 0 | 0 | 1.9 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.1288 | 15.14% | 0 | 0 | 16.3042 | 26.09% | 0
7660 | 0 | 0 | 0 | 1.7 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.1288 | 15.14% | 0 | 0 | 16.3042 | 26.09% | 0
7661 | 0 | 0 | 0 | 0.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.1288 | 15.14% | 0 | 0 | 16.3042 | 26.09% | 0
7662 | 0 | 0 | 0 | 1.5 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.1288 | 15.14% | 0 | 0 | 16.3042 | 26.09% | 0
7663 | 0 | 2 | 2 | 1.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4263 | 41.0148 | 0 | 102.4263 | 90.7025 | 7.111% | 0 | 0 | 16.3042 | 26.09% | 41.0148
7664 | 387 | 105 | 51 | 0.9 | 6.3 | 0 | 0 | 0 | 0 | 7.4042 | 0 | 0 | 7.4042 | 0 | 0 | 0 | 90.7025 | 35.903 | 0 | 90.7025 | 0 | 0% | 0 | 0 | 16.3042 | 26.09% | 43.3072
7665 | 699 | 267 | 64 | 3.4 | 9.9 | 0 | 0 | 0 | 0 | 34.3967 | 0 | 0 | 34.3967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 9.0846 | 6.25 | 10% | 43.4813
7666 | 807 | 416 | 75 | 4.8 | 11.4 | 0 | 0 | 0 | 179.1215 | 42.8685 | 9.3521 | 0 | 42.8685 | 0 | 0 | 0 | 0 | 0 | 179.1215 | 0 | 179.1215 | 14.04% | 0 | 0 | 6.25 | 10% | 42.8685
7667 | 879 | 537 | 83 | 5.6 | 12.8 | 0 | 0 | 0 | 220.2797 | 42.7362 | 23.3103 | 0 | 42.7362 | 0 | 0 | 0 | 0 | 0 | 220.2797 | 0 | 399.4011 | 31.31% | 0 | 0 | 6.25 | 10% | 42.7362
7668 | 899 | 592 | 86 | 4.6 | 13.7 | 0 | 0 | 0 | 237.3954 | 66.8477 | 5.1523 | 25 | 41.8477 | 0 | 0 | 0 | 0 | 0 | 237.3954 | 0 | 636.7966 | 49.92% | 25 | 0 | 28.839 | 46.14% | 41.8477
7669 | 914 | 591 | 81 | 5.1 | 14.5 | 0 | 0 | 0 | 244.6416 | 65.3853 | 6.6147 | 25 | 40.3853 | 0 | 0 | 0 | 0 | 0 | 244.6416 | 0 | 881.4382 | 69.1% | 25 | 0 | 51.428 | 82.28% | 40.3853
7670 | 903 | 526 | 73 | 5.8 | 15.1 | 0 | 0 | 0 | 180.2142 | 39.3561 | 30.9522 | 0 | 39.3561 | 0 | 0 | 0 | 0 | 0 | 180.2142 | 0 | 1061.6524 | 83.23% | 0 | 0 | 51.428 | 82.28% | 39.3561
7671 | 865 | 403 | 58 | 5.2 | 15 | 0 | 0 | 0 | 213.8578 | 45.2429 | 15.034 | 5.3367 | 39.9062 | 0 | 0 | 0 | 0 | 0 | 213.8578 | 0 | 1275.5102 | 100% | 5.3367 | 0 | 56.25 | 90% | 39.9062
7672 | 741 | 236 | 44 | 5.4 | 14.4 | 0 | 0 | 0 | 0 | 42.7459 | 0.40335 | 0 | 42.7459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 42.7459
7673 | 359 | 61 | 20 | 4.8 | 12.8 | 0 | 0 | 0 | 0 | 15.047 | 0 | 0 | 15.047 | 0 | 0 | 0 | 53.6599 | 19.6847 | 0 | 53.6599 | 1221.8503 | 95.79% | 0 | 9.1215 | 46.155 | 73.85% | 43.8531
7674 | 0 | 0 | 0 | 4.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4803 | 44.4729 | 0 | 110.4803 | 1111.37 | 87.13% | 0 | 0 | 46.155 | 73.85% | 44.4729
7675 | 0 | 0 | 0 | 2.4 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.3485 | 43.9896 | 0 | 109.3485 | 1002.0215 | 78.56% | 0 | 0 | 46.155 | 73.85% | 43.9896
7676 | 0 | 0 | 0 | 2.5 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.6623 | 41.5454 | 0 | 103.6623 | 898.3592 | 70.43% | 0 | 0 | 46.155 | 73.85% | 41.5454
7677 | 0 | 0 | 0 | 2.4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.1775 | 38.7266 | 0 | 97.1775 | 801.1817 | 62.81% | 0 | 0 | 46.155 | 73.85% | 38.7266
7678 | 0 | 0 | 0 | 1.5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.6012 | 35.8563 | 0 | 90.6012 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 35.8563
7679 | 0 | 0 | 0 | 1.9 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 0
7680 | 0 | 0 | 0 | 2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 0
7681 | 0 | 0 | 0 | 0.8 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 0
7682 | 0 | 0 | 0 | 1.1 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 0
7683 | 0 | 0 | 0 | 1.9 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 0
7684 | 0 | 0 | 0 | 2.2 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 0
7685 | 0 | 0 | 0 | 1.9 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 0
7686 | 0 | 0 | 0 | 2.3 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 0
7687 | 0 | 1 | 1 | 1.7 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 0 | 46.155 | 73.85% | 0
7688 | 470 | 101 | 37 | 2 | 7.2 | 0 | 0 | 0 | 0 | 7.7917 | 0 | 0 | 7.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710.5805 | 55.71% | 0 | 4.3099 | 41.3851 | 66.22% | 12.1015
7689 | 761 | 321 | 103 | 2.6 | 11.2 | 0 | 0 | 0 | 131.3927 | 37.9521 | 0 | 0 | 37.9521 | 0 | 0 | 0 | 0 | 0 | 131.3927 | 0 | 841.9732 | 66.01% | 0 | 2.0363 | 39.1314 | 62.61% | 39.9884
7690 | 707 | 490 | 191 | 5.3 | 14.2 | 0 | 0 | 0 | 153.4301 | 55.905 | 0 | 15.4904 | 40.4146 | 0 | 0 | 0 | 0 | 0 | 153.4301 | 0 | 995.4033 | 78.04% | 15.4904 | 0 | 53.128 | 85% | 40.4146
7691 | 290 | 436 | 288 | 5.6 | 15 | 0 | 0 | 0 | 58.9824 | 44.6943 | 0 | 3.4552 | 41.2391 | 0 | 0 | 0 | 0 | 0 | 58.9824 | 0 | 1054.3857 | 82.66% | 3.4552 | 0 | 56.25 | 90% | 41.2391
7692 | 1 | 195 | 192 | 4 | 13.7 | 0 | 0 | 0 | 0 | 13.505 | 0 | 0 | 13.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.3857 | 82.66% | 0 | 0 | 56.25 | 90% | 13.505
7693 | 0 | 176 | 174 | 3.3 | 13 | 0 | 0 | 0 | 0 | 11.8877 | 0 | 0 | 11.8877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.3857 | 82.66% | 0 | 0 | 56.25 | 90% | 11.8877
7694 | 0 | 144 | 143 | 4.6 | 13.6 | 0 | 0 | 0 | 0 | 9.5101 | 0 | 0 | 9.5101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.3857 | 82.66% | 0 | 0 | 56.25 | 90% | 9.5101
7695 | 1 | 141 | 139 | 9.6 | 14.9 | 0 | 0 | 0 | 0 | 9.4896 | 0 | 0 | 9.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.3857 | 82.66% | 0 | 4.276 | 51.5176 | 82.43% | 13.7656
7696 | 161 | 113 | 80 | 8.7 | 15.4 | 0 | 0 | 0 | 0 | 15.5151 | 0 | 0 | 15.5151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.3857 | 82.66% | 0 | 25 | 23.8492 | 38.16% | 40.5151
7697 | 146 | 51 | 30 | 7.3 | 15.2 | 0 | 0 | 0 | 0 | 8.2241 | 0 | 0 | 8.2241 | 0 | 0 | 0 | 88.2429 | 34.6625 | 0 | 88.2429 | 966.1428 | 75.75% | 0 | 0 | 23.8492 | 38.16% | 42.8866
7698 | 0 | 0 | 0 | 4 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.734 | 44.0913 | 0 | 109.734 | 856.4088 | 67.14% | 0 | 0 | 23.8492 | 38.16% | 44.0913
7699 | 0 | 0 | 0 | 3.2 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.4578 | 43.5718 | 0 | 108.4578 | 747.951 | 58.64% | 0 | 0 | 23.8492 | 38.16% | 43.5718
7700 | 0 | 0 | 0 | 3.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9635 | 41.6109 | 0 | 103.9635 | 643.9875 | 50.49% | 0 | 0 | 23.8492 | 38.16% | 41.6109
7701 | 0 | 0 | 0 | 4.2 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.6232 | 38.4077 | 0 | 96.6232 | 547.3643 | 42.91% | 0 | 0 | 23.8492 | 38.16% | 38.4077
7702 | 0 | 0 | 0 | 2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.3643 | 42.91% | 0 | 0 | 23.8492 | 38.16% | 0
7703 | 0 | 0 | 0 | 1.1 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.3643 | 42.91% | 0 | 0 | 23.8492 | 38.16% | 0
7704 | 0 | 0 | 0 | 1.1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.3643 | 42.91% | 0 | 0 | 23.8492 | 38.16% | 0
7705 | 0 | 0 | 0 | 0.8 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.3643 | 42.91% | 0 | 0 | 23.8492 | 38.16% | 0
7706 | 0 | 0 | 0 | 1.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.3643 | 42.91% | 0 | 0 | 23.8492 | 38.16% | 0
7707 | 0 | 0 | 0 | 4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.3643 | 42.91% | 0 | 0 | 23.8492 | 38.16% | 0
7708 | 0 | 0 | 0 | 3.9 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.1946 | 36.476 | 0 | 92.1946 | 455.1697 | 35.69% | 0 | 0 | 23.8492 | 38.16% | 36.476
7709 | 0 | 0 | 0 | 4.3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.2001 | 43.0482 | 0 | 107.2001 | 347.9696 | 27.28% | 0 | 0 | 23.8492 | 38.16% | 43.0482
7710 | 0 | 0 | 0 | 3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.8378 | 46.8433 | 0 | 115.8378 | 232.1319 | 18.2% | 0 | 0 | 23.8492 | 38.16% | 46.8433
7711 | 0 | 1 | 1 | 3.5 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.0997 | 48.7262 | 0 | 120.0997 | 112.0322 | 8.783% | 0 | 0 | 23.8492 | 38.16% | 48.7262
7712 | 222 | 63 | 28 | 3.4 | 8 | 0 | 0 | 0 | 0 | 3.9474 | 0 | 0 | 3.9474 | 0 | 0 | 0 | 112.0322 | 45.2063 | 0 | 112.0322 | 0 | 0% | 0 | 0 | 23.8492 | 38.16% | 49.1537
7713 | 716 | 256 | 54 | 1.4 | 11.1 | 0 | 0 | 0 | 0 | 33.0052 | 0 | 0 | 33.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 15.902 | 6.25 | 10% | 48.9072
7714 | 849 | 415 | 63 | 2.1 | 13.5 | 0 | 0 | 0 | 0 | 48.4741 | 3.2039 | 0 | 48.4741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 48.4741
7715 | 908 | 530 | 69 | 2 | 14.9 | 0 | 0 | 0 | 189.4582 | 48.6941 | 14.4172 | 0 | 48.6941 | 0 | 0 | 0 | 0 | 0 | 189.4582 | 0 | 189.4582 | 14.85% | 0 | 0 | 6.25 | 10% | 48.6941
7716 | 929 | 586 | 71 | 3.6 | 15.7 | 0 | 0 | 0 | 246.109 | 54.4057 | 16.6376 | 7.0025 | 47.4031 | 0 | 0 | 0 | 0 | 0 | 246.109 | 0 | 435.5671 | 34.15% | 7.0025 | 0 | 12.5772 | 20.12% | 47.4031
7717 | 927 | 580 | 71 | 5.4 | 15.7 | 0 | 0 | 0 | 247.2635 | 71.7708 | 0.22917 | 25 | 46.7708 | 0 | 0 | 0 | 0 | 0 | 247.2635 | 0 | 682.8306 | 53.53% | 25 | 0 | 35.1662 | 56.27% | 46.7708
7718 | 901 | 512 | 67 | 6.6 | 15.6 | 0 | 0 | 0 | 233.6638 | 69.7192 | 0 | 23.3341 | 46.3851 | 0 | 0 | 0 | 0 | 0 | 233.6638 | 0 | 916.4944 | 71.85% | 23.3341 | 0 | 56.25 | 90% | 46.3851
7719 | 843 | 391 | 60 | 6.2 | 15.4 | 0 | 0 | 0 | 206.4942 | 47.1301 | 12.1841 | 0 | 47.1301 | 0 | 0 | 0 | 0 | 0 | 206.4942 | 0 | 1122.9887 | 88.04% | 0 | 0 | 56.25 | 90% | 47.1301
7720 | 717 | 227 | 45 | 2.3 | 15.9 | 0 | 0 | 0 | 152.5215 | 41.0489 | 0 | 0 | 41.0489 | 0 | 0 | 0 | 0 | 0 | 152.5215 | 0 | 1275.5102 | 100% | 0 | 3.0555 | 52.8684 | 84.59% | 44.1044
7721 | 351 | 59 | 20 | 5.2 | 13.3 | 0 | 0 | 0 | 0 | 14.7577 | 0 | 0 | 14.7577 | 0 | 0 | 0 | 89.4264 | 35.2422 | 0 | 89.4264 | 1186.0838 | 92.99% | 0 | 0 | 52.8684 | 84.59% | 50
7722 | 0 | 0 | 0 | 2.3 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1822 | 50 | 0 | 123.1822 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 50
7723 | 0 | 0 | 0 | 1 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7724 | 0 | 0 | 0 | 0.9 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7725 | 0 | 0 | 0 | 1.3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7726 | 0 | 0 | 0 | 2.9 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7727 | 0 | 0 | 0 | 2 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7728 | 0 | 0 | 0 | 1.9 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7729 | 0 | 0 | 0 | 2 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7730 | 0 | 0 | 0 | 1.3 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7731 | 0 | 0 | 0 | 1 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7732 | 0 | 0 | 0 | 1.4 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7733 | 0 | 0 | 0 | 1.7 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.9016 | 83.33% | 0 | 0 | 52.8684 | 84.59% | 0
7734 | 0 | 0 | 0 | 2.3 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.1017 | 24.2875 | 0 | 64.1017 | 998.7999 | 78.31% | 0 | 0 | 52.8684 | 84.59% | 24.2875
7735 | 0 | 2 | 1 | 2.4 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0087 | 50 | 0 | 123.0087 | 875.7912 | 68.66% | 0 | 0 | 52.8684 | 84.59% | 50
7736 | 31 | 46 | 43 | 1.9 | 5.3 | 0 | 0 | 0 | 0 | 2.1797 | 0 | 0 | 2.1797 | 0 | 0 | 0 | 118.0146 | 47.8203 | 0 | 118.0146 | 757.7766 | 59.41% | 0 | 0 | 52.8684 | 84.59% | 50
7737 | 147 | 203 | 158 | 1 | 8.4 | 0 | 0 | 0 | 0 | 22.5741 | 0 | 0 | 22.5741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.7766 | 59.41% | 0 | 0 | 52.8684 | 84.59% | 22.5741
7738 | 195 | 312 | 228 | 0.6 | 11.5 | 0 | 0 | 0 | 0 | 31.2709 | 0 | 0 | 31.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.7766 | 59.41% | 0 | 18.1029 | 32.8333 | 52.53% | 49.3738
7739 | 343 | 424 | 243 | 1.7 | 12.7 | 0 | 0 | 0 | 75.7681 | 43.831 | 0 | 0 | 43.831 | 0 | 0 | 0 | 0 | 0 | 75.7681 | 0 | 833.5448 | 65.35% | 0 | 5.3826 | 26.8761 | 43% | 49.2136
7740 | 732 | 544 | 137 | 1.8 | 13.8 | 0 | 0 | 0 | 190.6302 | 63.7036 | 0 | 15.671 | 48.0326 | 0 | 0 | 0 | 0 | 0 | 190.6302 | 0 | 1024.1749 | 80.3% | 15.671 | 0 | 41.0358 | 65.66% | 48.0326
7741 | 698 | 546 | 160 | 1.7 | 14.5 | 0 | 0 | 0 | 183.5147 | 64.2287 | 0 | 16.8381 | 47.3906 | 0 | 0 | 0 | 0 | 0 | 183.5147 | 0 | 1207.6897 | 94.68% | 16.8381 | 0 | 56.25 | 90% | 47.3906
7742 | 251 | 336 | 207 | 0.8 | 14.9 | 0 | 0 | 0 | 53.4175 | 35.465 | 0 | 0 | 35.465 | 0 | 0 | 0 | 0 | 0 | 53.4175 | 0 | 1261.1072 | 98.87% | 0 | 11.7389 | 43.2581 | 69.21% | 47.204
7743 | 157 | 276 | 208 | 2.2 | 15 | 0 | 0 | 0 | 0 | 27.695 | 0 | 0 | 27.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1261.1072 | 98.87% | 0 | 9.2344 | 33.0381 | 52.86% | 36.9295
7744 | 95 | 161 | 139 | 3.7 | 13.5 | 0 | 0 | 0 | 0 | 16.1134 | 0 | 0 | 16.1134 | 0 | 0 | 0 | 86.3251 | 33.8866 | 0 | 86.3251 | 1174.7821 | 92.1% | 0 | 0 | 33.0381 | 52.86% | 50
7745 | 52 | 48 | 41 | 3.2 | 12.3 | 0 | 0 | 0 | 0 | 4.8293 | 0 | 0 | 4.8293 | 0 | 0 | 0 | 112.1572 | 45.1707 | 0 | 112.1572 | 1062.6249 | 83.31% | 0 | 0 | 33.0381 | 52.86% | 50
7746 | 0 | 0 | 0 | 2.3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.1167 | 50 | 0 | 123.1167 | 939.5082 | 73.66% | 0 | 0 | 33.0381 | 52.86% | 50
7747 | 0 | 0 | 0 | 2.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0946 | 50 | 0 | 123.0946 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 50
7748 | 0 | 0 | 0 | 1.4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 0
7749 | 0 | 0 | 0 | 1.5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 0
7750 | 0 | 0 | 0 | 1.4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 0
7751 | 0 | 0 | 0 | 1.1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 0
7752 | 0 | 0 | 0 | 1.3 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 0
7753 | 0 | 0 | 0 | 1.7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 0
7754 | 0 | 0 | 0 | 0.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 0
7755 | 0 | 0 | 0 | 1.2 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 0
7756 | 0 | 0 | 0 | 0.7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816.4136 | 64.01% | 0 | 0 | 33.0381 | 52.86% | 0
7757 | 0 | 0 | 0 | 0.7 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.7261 | 45.0717 | 0 | 111.7261 | 704.6875 | 55.25% | 0 | 0 | 33.0381 | 52.86% | 45.0717
7758 | 0 | 0 | 0 | 0.8 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.104 | 48.7234 | 0 | 120.104 | 584.5835 | 45.83% | 0 | 0 | 33.0381 | 52.86% | 48.7234
7759 | 0 | 1 | 1 | 1.3 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0357 | 50 | 0 | 123.0357 | 461.5478 | 36.19% | 0 | 0 | 33.0381 | 52.86% | 50
7760 | 330 | 70 | 29 | 0.7 | 5.3 | 0 | 0 | 0 | 0 | 5.4337 | 0 | 0 | 5.4337 | 0 | 0 | 0 | 110.559 | 44.5663 | 0 | 110.559 | 350.9888 | 27.52% | 0 | 0 | 33.0381 | 52.86% | 50
7761 | 668 | 248 | 66 | 0.8 | 9.2 | 0 | 0 | 0 | 111.7915 | 32.1932 | 0 | 0 | 32.1932 | 0 | 0 | 0 | 0 | 0 | 111.7915 | 0 | 462.7804 | 36.28% | 0 | 17.8068 | 13.3307 | 21.33% | 50
7762 | 635 | 360 | 103 | 0.7 | 12.1 | 0 | 0 | 0 | 137.3622 | 43.6022 | 0 | 0 | 43.6022 | 0 | 0 | 0 | 0 | 0 | 137.3622 | 0 | 600.1425 | 47.05% | 0 | 6.3979 | 6.25 | 10% | 50
7763 | 629 | 472 | 154 | 2.2 | 12.8 | 0 | 0 | 0 | 153.4751 | 54.7229 | 0 | 4.7229 | 50 | 0 | 0 | 0 | 0 | 0 | 153.4751 | 0 | 753.6176 | 59.08% | 4.7229 | 0 | 10.5174 | 16.83% | 50
7764 | 883 | 577 | 92 | 3.2 | 13.8 | 0 | 0 | 0 | 232.2859 | 70.5416 | 0 | 21.5173 | 49.0242 | 0 | 0 | 0 | 0 | 0 | 232.2859 | 0 | 985.9034 | 77.29% | 21.5173 | 0 | 29.9596 | 47.94% | 49.0242
7765 | 707 | 546 | 157 | 3.5 | 14.4 | 0 | 0 | 0 | 184.7334 | 66.2869 | 0 | 17.8128 | 48.4741 | 0 | 0 | 0 | 0 | 0 | 184.7334 | 0 | 1170.6368 | 91.78% | 17.8128 | 0 | 46.0545 | 73.69% | 48.4741
7766 | 124 | 289 | 222 | 3.4 | 14 | 0 | 0 | 0 | 0 | 27.6819 | 0 | 0 | 27.6819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170.6368 | 91.78% | 0 | 0 | 46.0545 | 73.69% | 27.6819
7767 | 1 | 164 | 163 | 2.7 | 13.7 | 0 | 0 | 0 | 0 | 11.5387 | 0 | 0 | 11.5387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170.6368 | 91.78% | 0 | 0 | 46.0545 | 73.69% | 11.5387
7768 | 0 | 49 | 49 | 2.2 | 13.5 | 0 | 0 | 0 | 0 | 2.804 | 0 | 0 | 2.804 | 0 | 0 | 0 | 116.9125 | 47.196 | 0 | 116.9125 | 1053.7243 | 82.61% | 0 | 0 | 46.0545 | 73.69% | 50
7769 | 45 | 23 | 20 | 2.2 | 12.8 | 0 | 0 | 0 | 0 | 3.0381 | 0 | 0 | 3.0381 | 0 | 0 | 0 | 116.311 | 46.9619 | 0 | 116.311 | 937.4133 | 73.49% | 0 | 0 | 46.0545 | 73.69% | 50
7770 | 0 | 0 | 0 | 1.3 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.175 | 50 | 0 | 123.175 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 50
7771 | 0 | 0 | 0 | 1.2 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7772 | 0 | 0 | 0 | 1.7 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7773 | 0 | 0 | 0 | 1.5 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7774 | 0 | 0 | 0 | 0.5 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7775 | 0 | 0 | 0 | 1 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7776 | 0 | 0 | 0 | 1.1 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7777 | 0 | 0 | 0 | 1.1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7778 | 0 | 0 | 0 | 0.7 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7779 | 0 | 0 | 0 | 0.5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7780 | 0 | 0 | 0 | 1 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7781 | 0 | 0 | 0 | 1 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814.2383 | 63.84% | 0 | 0 | 46.0545 | 73.69% | 0
7782 | 0 | 0 | 0 | 1.3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.3898 | 48.424 | 0 | 119.3898 | 694.8485 | 54.48% | 0 | 0 | 46.0545 | 73.69% | 48.424
7783 | 0 | 0 | 0 | 1.1 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9992 | 50 | 0 | 122.9992 | 571.8493 | 44.83% | 0 | 0 | 46.0545 | 73.69% | 50
7784 | 0 | 25 | 25 | 1 | 6.3 | 0 | 0 | 0 | 0 | 0.85688 | 0 | 0 | 0.85688 | 0 | 0 | 0 | 121.0362 | 49.1431 | 0 | 121.0362 | 450.8132 | 35.34% | 0 | 0 | 46.0545 | 73.69% | 50
7785 | 11 | 113 | 109 | 0.9 | 9.6 | 0 | 0 | 0 | 0 | 9.5718 | 0 | 0 | 9.5718 | 0 | 0 | 0 | 101.1273 | 40.4282 | 0 | 101.1273 | 349.6859 | 27.42% | 0 | 0 | 46.0545 | 73.69% | 50
7786 | 0 | 127 | 126 | 0.5 | 10.4 | 0 | 0 | 0 | 0 | 8.9056 | 0 | 0 | 8.9056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349.6859 | 27.42% | 0 | 0 | 46.0545 | 73.69% | 8.9056
7787 | 0 | 114 | 113 | 1.1 | 11.4 | 0 | 0 | 0 | 0 | 7.3616 | 0 | 0 | 7.3616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349.6859 | 27.42% | 0 | 0 | 46.0545 | 73.69% | 7.3616
7788 | 0 | 222 | 220 | 1.1 | 12.2 | 0 | 0 | 0 | 0 | 15.8505 | 0 | 0 | 15.8505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349.6859 | 27.42% | 0 | 0 | 46.0545 | 73.69% | 15.8505
7789 | 9 | 328 | 320 | 1.9 | 13.7 | 0 | 0 | 0 | 0 | 25.3384 | 0 | 0 | 25.3384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349.6859 | 27.42% | 0 | 0 | 46.0545 | 73.69% | 25.3384
7790 | 136 | 311 | 243 | 2 | 14.8 | 0 | 0 | 0 | 0 | 30.2155 | 0 | 0 | 30.2155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349.6859 | 27.42% | 0 | 10.9658 | 33.9183 | 54.27% | 41.1812
7791 | 68 | 213 | 183 | 2.7 | 15.1 | 0 | 0 | 0 | 0 | 18.6798 | 0 | 0 | 18.6798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349.6859 | 27.42% | 0 | 25 | 6.25 | 10% | 43.6798
7792 | 11 | 96 | 93 | 2.6 | 14.9 | 0 | 0 | 0 | 0 | 6.6625 | 0 | 0 | 6.6625 | 0 | 0 | 0 | 108.1809 | 43.3375 | 0 | 108.1809 | 241.505 | 18.93% | 0 | 0 | 6.25 | 10% | 50
7793 | 14 | 35 | 33 | 2.3 | 14.4 | 0 | 0 | 0 | 0 | 2.298 | 0 | 0 | 2.298 | 0 | 0 | 0 | 118.1685 | 47.702 | 0 | 118.1685 | 123.3365 | 9.67% | 0 | 0 | 6.25 | 10% | 50
7794 | 0 | 0 | 0 | 2.5 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.3365 | 50 | 0 | 123.3365 | 1.5632e-13 | 1.226e-14% | 0 | 0 | 6.25 | 10% | 50
7795 | 0 | 0 | 0 | 2.9 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5632e-13 | 1.226e-14% | 0 | 0 | 6.25 | 10% | 0
7796 | 0 | 0 | 0 | 2.1 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6645e-15 | 0 | 0 | 2.6645e-15 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7797 | 0 | 0 | 0 | 2.8 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7798 | 0 | 0 | 0 | 1.7 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7799 | 0 | 0 | 0 | 1.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7800 | 0 | 0 | 0 | 2.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7801 | 0 | 0 | 0 | 2.3 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7802 | 0 | 0 | 0 | 2.4 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7803 | 0 | 0 | 0 | 2.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7804 | 0 | 0 | 0 | 1.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7805 | 0 | 0 | 0 | 1.9 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7806 | 0 | 0 | 0 | 1 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7807 | 0 | 0 | 0 | 0.8 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 1.205e-14% | 0 | 0 | 6.25 | 10% | 0
7808 | 0 | 6 | 6 | 1.3 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5365e-13 | 0 | 0 | 1.5365e-13 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7809 | 0 | 23 | 23 | 2.5 | 12.3 | 0 | 0 | 0 | 0 | 1.0799 | 0 | 0 | 1.0799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 1.0799
7810 | 2 | 155 | 152 | 3.2 | 12.9 | 0 | 0 | 0 | 0 | 11.4692 | 0 | 0 | 11.4692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 11.4692
7811 | 0 | 111 | 110 | 3.4 | 13.3 | 0 | 0 | 0 | 0 | 7.1209 | 0 | 0 | 7.1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 7.1209
7812 | 2 | 201 | 197 | 5.8 | 13.9 | 0 | 0 | 0 | 0 | 14.1544 | 0 | 0 | 14.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 14.1544
7813 | 2 | 156 | 154 | 6.7 | 14.1 | 0 | 0 | 0 | 0 | 10.5104 | 0 | 0 | 10.5104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 10.5104
7814 | 20 | 231 | 219 | 8 | 14.1 | 0 | 0 | 0 | 0 | 17.4638 | 0 | 0 | 17.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 17.4638
7815 | 1 | 126 | 124 | 6 | 14 | 0 | 0 | 0 | 0 | 8.339 | 0 | 0 | 8.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 8.339
7816 | 2 | 88 | 88 | 6 | 14.1 | 0 | 0 | 0 | 0 | 5.8275 | 0 | 0 | 5.8275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 5.8275
7817 | 0 | 19 | 19 | 5 | 13.8 | 0 | 0 | 0 | 0 | 0.80663 | 0 | 0 | 0.80663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0.80663
7818 | 0 | 0 | 0 | 4.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7819 | 0 | 0 | 0 | 3.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7820 | 0 | 0 | 0 | 3.4 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7821 | 0 | 0 | 0 | 2.6 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7822 | 0 | 0 | 0 | 2.5 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7823 | 0 | 0 | 0 | 4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7824 | 0 | 0 | 0 | 4.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7825 | 0 | 0 | 0 | 5.7 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7826 | 0 | 0 | 0 | 9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7827 | 0 | 0 | 0 | 12.4 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7828 | 0 | 0 | 0 | 14.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7829 | 0 | 0 | 0 | 13.5 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7830 | 0 | 0 | 0 | 10.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7831 | 0 | 0 | 0 | 7.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
7832 | 360 | 66 | 23 | 7.2 | 11.7 | 0 | 0 | 0 | 0 | 5.3656 | 0 | 0 | 5.3656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 5.3656
7833 | 713 | 236 | 48 | 9.7 | 13.3 | 0 | 0 | 0 | 110.9862 | 32.5868 | 0 | 0 | 32.5868 | 0 | 0 | 0 | 0 | 0 | 110.9862 | 0 | 110.9862 | 8.701% | 0 | 0 | 6.25 | 10% | 32.5868
7834 | 843 | 396 | 61 | 10.9 | 14.6 | 0 | 0 | 0 | 177.649 | 52.6591 | 0 | 10.111 | 42.5482 | 0 | 0 | 0 | 0 | 0 | 177.649 | 0 | 288.6352 | 22.63% | 10.111 | 0 | 15.3859 | 24.62% | 42.5482
7835 | 909 | 514 | 67 | 2.9 | 15.2 | 0 | 0 | 0 | 228.1699 | 45.0394 | 18.3309 | 2.3728 | 42.6666 | 0 | 0 | 0 | 0 | 0 | 228.1699 | 0 | 516.8051 | 40.52% | 2.3728 | 0 | 17.5299 | 28.05% | 42.6666
7836 | 930 | 574 | 73 | 0 | 15.7 | 0 | 0 | 0 | 246.2303 | 64.6736 | 0 | 23.0293 | 41.6443 | 0 | 0 | 0 | 0 | 0 | 246.2303 | 0 | 763.0353 | 59.82% | 23.0293 | 0 | 38.3382 | 61.34% | 41.6443
7837 | 755 | 506 | 100 | 0.3 | 16.5 | 0 | 0 | 0 | 199.3808 | 59.7437 | 0 | 19.8236 | 39.9202 | 0 | 0 | 0 | 0 | 0 | 199.3808 | 0 | 962.4161 | 75.45% | 19.8236 | 0 | 56.25 | 90% | 39.9202
7838 | 0 | 173 | 171 | 2.3 | 19.5 | 0 | 0 | 0 | 0 | 11.5556 | 0 | 0 | 11.5556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 962.4161 | 75.45% | 0 | 0 | 56.25 | 90% | 11.5556
7839 | 0 | 110 | 109 | 6.1 | 20.9 | 0 | 0 | 0 | 0 | 6.901 | 0 | 0 | 6.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 962.4161 | 75.45% | 0 | 0 | 56.25 | 90% | 6.901
7840 | 278 | 170 | 110 | 7.3 | 21.4 | 0 | 0 | 0 | 42.9514 | 24.2138 | 0 | 0 | 24.2138 | 0 | 0 | 0 | 0 | 0 | 42.9514 | 0 | 1005.3676 | 78.82% | 0 | 17.6199 | 36.7495 | 58.8% | 41.8337
7841 | 306 | 64 | 33 | 5.5 | 20.9 | 0 | 0 | 0 | 34.9527 | 14.416 | 0 | 0 | 14.416 | 0 | 0 | 0 | 0 | 0 | 34.9527 | 0 | 1040.3202 | 81.56% | 0 | 25 | 9.0811 | 14.53% | 39.416
7842 | 0 | 0 | 0 | 2.6 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.5964 | 43.2543 | 0 | 108.5964 | 931.7238 | 73.05% | 0 | 0 | 9.0811 | 14.53% | 43.2543
7843 | 0 | 0 | 0 | 5.8 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.4722 | 42.849 | 0 | 107.4722 | 824.2516 | 64.62% | 0 | 0 | 9.0811 | 14.53% | 42.849
7844 | 0 | 0 | 0 | 6.3 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.243 | 41.019 | 0 | 103.243 | 721.0086 | 56.53% | 0 | 0 | 9.0811 | 14.53% | 41.019
7845 | 0 | 0 | 0 | 2.3 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5119 | 38.2099 | 0 | 96.5119 | 624.4967 | 48.96% | 0 | 0 | 9.0811 | 14.53% | 38.2099
7846 | 0 | 0 | 0 | 2.4 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4065 | 35.1975 | 0 | 89.4065 | 535.0901 | 41.95% | 0 | 0 | 9.0811 | 14.53% | 35.1975
7847 | 0 | 0 | 0 | 2.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.0485 | 32.472 | 0 | 83.0485 | 452.0417 | 35.44% | 0 | 0 | 9.0811 | 14.53% | 32.472
7848 | 0 | 0 | 0 | 4.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 452.0417 | 35.44% | 0 | 0 | 9.0811 | 14.53% | 0
7849 | 0 | 0 | 0 | 5.7 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.0417 | 35.44% | 0 | 0 | 9.0811 | 14.53% | 0
7850 | 0 | 0 | 0 | 9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.0417 | 35.44% | 0 | 0 | 9.0811 | 14.53% | 0
7851 | 0 | 0 | 0 | 12.4 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.0417 | 35.44% | 0 | 0 | 9.0811 | 14.53% | 0
7852 | 0 | 0 | 0 | 14.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.0417 | 35.44% | 0 | 0 | 9.0811 | 14.53% | 0
7853 | 0 | 0 | 0 | 13.5 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.0417 | 35.44% | 0 | 0 | 9.0811 | 14.53% | 0
7854 | 0 | 0 | 0 | 10.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.0417 | 35.44% | 0 | 0 | 9.0811 | 14.53% | 0
7855 | 0 | 0 | 0 | 7.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7162 | 34.5304 | 0 | 87.7162 | 364.3255 | 28.56% | 0 | 0 | 9.0811 | 14.53% | 34.5304
7856 | 360 | 66 | 23 | 7.2 | 11.7 | 0 | 0 | 0 | 0 | 5.3392 | 0 | 0 | 5.3392 | 0 | 0 | 0 | 82.0637 | 32.0769 | 0 | 82.0637 | 282.2618 | 22.13% | 0 | 0 | 9.0811 | 14.53% | 37.4161
7857 | 713 | 236 | 48 | 9.7 | 13.3 | 0 | 0 | 0 | 110.2106 | 32.4337 | 0 | 0 | 32.4337 | 0 | 0 | 0 | 0 | 0 | 110.2106 | 0 | 392.4724 | 30.77% | 0 | 2.5581 | 6.25 | 10% | 34.9918
7858 | 843 | 396 | 61 | 10.9 | 14.6 | 0 | 0 | 0 | 176.9792 | 38.1904 | 14.3672 | 0 | 38.1904 | 0 | 0 | 0 | 0 | 0 | 176.9792 | 0 | 569.4516 | 44.65% | 0 | 0 | 6.25 | 10% | 38.1904
7859 | 909 | 514 | 67 | 2.9 | 15.2 | 0 | 0 | 0 | 227.7988 | 46.2814 | 17.0073 | 7.6328 | 38.6486 | 0 | 0 | 0 | 0 | 0 | 227.7988 | 0 | 797.2504 | 62.5% | 7.6328 | 0 | 13.1467 | 21.03% | 38.6486
7860 | 930 | 574 | 73 | 0 | 15.7 | 0 | 0 | 0 | 245.8177 | 63.5136 | 1.104 | 25 | 38.5136 | 0 | 0 | 0 | 0 | 0 | 245.8177 | 0 | 1043.0681 | 81.78% | 25 | 0 | 35.7357 | 57.18% | 38.5136
7861 | 755 | 506 | 100 | 0.3 | 16.5 | 0 | 0 | 0 | 199.071 | 59.7064 | 0 | 22.7039 | 37.0025 | 0 | 0 | 0 | 0 | 0 | 199.071 | 0 | 1242.1391 | 97.38% | 22.7039 | 0 | 56.25 | 90% | 37.0025
7862 | 0 | 173 | 171 | 2.3 | 19.5 | 0 | 0 | 0 | 0 | 11.5719 | 0 | 0 | 11.5719 | 0 | 0 | 0 | 65.548 | 24.6576 | 0 | 65.548 | 1176.5911 | 92.24% | 0 | 0 | 56.25 | 90% | 36.2295
7863 | 0 | 110 | 109 | 6.1 | 20.9 | 0 | 0 | 0 | 0 | 6.9081 | 0 | 0 | 6.9081 | 0 | 0 | 0 | 77.9754 | 29.9509 | 0 | 77.9754 | 1098.6157 | 86.13% | 0 | 0 | 56.25 | 90% | 36.859
7864 | 278 | 170 | 110 | 7.3 | 21.4 | 0 | 0 | 0 | 42.8451 | 24.2371 | 0 | 0 | 24.2371 | 0 | 0 | 0 | 0 | 0 | 42.8451 | 0 | 1141.4608 | 89.49% | 0 | 12.2791 | 42.6603 | 68.26% | 36.5162
7865 | 306 | 64 | 33 | 5.5 | 20.9 | 0 | 0 | 0 | 34.8195 | 14.4326 | 0 | 0 | 14.4326 | 0 | 0 | 0 | 0 | 0 | 34.8195 | 0 | 1176.2802 | 92.22% | 0 | 25 | 14.992 | 23.99% | 39.4326
7866 | 0 | 0 | 0 | 2.6 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.0801 | 43.4632 | 0 | 109.0801 | 1067.2001 | 83.67% | 0 | 0 | 14.992 | 23.99% | 43.4632
7867 | 0 | 0 | 0 | 5.8 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0644 | 43.1053 | 0 | 108.0644 | 959.1357 | 75.2% | 0 | 0 | 14.992 | 23.99% | 43.1053
7868 | 0 | 0 | 0 | 6.3 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.6191 | 44.2107 | 0 | 110.6191 | 848.5166 | 66.52% | 2.877 | 0 | 17.5915 | 28.15% | 41.3338
7869 | 0 | 0 | 0 | 2.3 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.5166 | 66.52% | 0 | 0 | 17.5915 | 28.15% | 0
7870 | 0 | 0 | 0 | 2.4 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.5166 | 66.52% | 0 | 0 | 17.5915 | 28.15% | 0
7871 | 0 | 0 | 0 | 2.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.5166 | 66.52% | 0 | 0 | 17.5915 | 28.15% | 0
7872 | 0 | 0 | 0 | 2.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.5166 | 66.52% | 0 | 0 | 17.5915 | 28.15% | 0
7873 | 0 | 0 | 0 | 4.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.5166 | 66.52% | 0 | 0 | 17.5915 | 28.15% | 0
7874 | 0 | 0 | 0 | 5.7 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.5166 | 66.52% | 0 | 0 | 17.5915 | 28.15% | 0
7875 | 0 | 0 | 0 | 9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.5166 | 66.52% | 0 | 0 | 17.5915 | 28.15% | 0
7876 | 0 | 0 | 0 | 12.4 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 848.5166 | 66.52% | 0 | 0 | 17.5915 | 28.15% | 0
7877 | 0 | 0 | 0 | 14.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.7544 | 0 | 127.551 | 720.9656 | 56.52% | 8.9138 | 0 | 25.6456 | 41.03% | 42.8406
7878 | 0 | 0 | 0 | 13.5 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.7964 | 0 | 127.551 | 593.4146 | 46.52% | 5.3501 | 0 | 30.4797 | 48.77% | 46.4463
7879 | 0 | 0 | 0 | 10.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.8386 | 0 | 127.551 | 465.8636 | 36.52% | 4.0943 | 0 | 34.1791 | 54.69% | 47.7443
7880 | 0 | 0 | 0 | 7.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.883 | 0 | 127.551 | 338.3125 | 26.52% | 3.7821 | 0 | 37.5965 | 60.15% | 48.1009
7881 | 360 | 66 | 23 | 7.2 | 11.7 | 0 | 0 | 0 | 44.7716 | 16.6022 | 0 | 0 | 16.6022 | 0 | 0 | 0 | 0 | 0 | 44.7716 | 0 | 383.0841 | 30.03% | 0 | 25 | 9.9282 | 15.89% | 41.6022
7882 | 713 | 236 | 48 | 9.7 | 13.3 | 0 | 0 | 0 | 146.2097 | 44.3888 | 0 | 0 | 44.3888 | 0 | 0 | 0 | 0 | 0 | 146.2097 | 0 | 529.2938 | 41.5% | 0 | 3.3235 | 6.25 | 10% | 47.7123
7883 | 843 | 396 | 61 | 10.9 | 14.6 | 0 | 0 | 0 | 202.465 | 60.6338 | 0.54808 | 13.0399 | 47.5939 | 0 | 0 | 0 | 0 | 0 | 202.465 | 0 | 731.7588 | 57.37% | 13.0399 | 0 | 18.0324 | 28.85% | 47.5939
7884 | 909 | 514 | 67 | 2.9 | 15.2 | 0 | 0 | 0 | 237.8641 | 68.4854 | 0 | 22.1463 | 46.3391 | 0 | 0 | 0 | 0 | 0 | 237.8641 | 0 | 969.6229 | 76.02% | 22.1463 | 0 | 38.0429 | 60.87% | 46.3391
7885 | 930 | 574 | 73 | 0 | 15.7 | 0 | 0 | 0 | 248.9322 | 65.8934 | 0 | 20.1504 | 45.743 | 0 | 0 | 0 | 0 | 0 | 248.9322 | 0 | 1218.5551 | 95.53% | 20.1504 | 0 | 56.25 | 90% | 45.743
7886 | 0 | 173 | 171 | 2.3 | 19.5 | 0 | 0 | 0 | 0 | 11.5879 | 0 | 0 | 11.5879 | 0 | 0 | 0 | 87.0771 | 33.9545 | 0 | 87.0771 | 1131.478 | 88.71% | 0 | 0 | 56.25 | 90% | 45.5425
7887 | 0 | 110 | 109 | 6.1 | 20.9 | 0 | 0 | 0 | 0 | 6.9151 | 0 | 0 | 6.9151 | 0 | 0 | 0 | 100.3412 | 39.5856 | 0 | 100.3412 | 1031.1367 | 80.84% | 0 | 0 | 56.25 | 90% | 46.5006
7888 | 278 | 170 | 110 | 7.3 | 21.4 | 0 | 0 | 0 | 42.7378 | 24.2608 | 0 | 0 | 24.2608 | 0 | 0 | 0 | 0 | 0 | 42.7378 | 0 | 1073.8745 | 84.19% | 0 | 20.178 | 33.9183 | 54.27% | 44.4388
7889 | 306 | 64 | 33 | 5.5 | 20.9 | 0 | 0 | 0 | 34.6963 | 14.4505 | 0 | 0 | 14.4505 | 0 | 0 | 0 | 0 | 0 | 34.6963 | 0 | 1108.5708 | 86.91% | 0 | 25 | 6.25 | 10% | 39.4505
7890 | 0 | 0 | 0 | 2.6 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.6552 | 49.7582 | 0 | 123.6552 | 984.9156 | 77.22% | 0 | 0 | 6.25 | 10% | 49.7582
7891 | 0 | 0 | 0 | 5.8 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.6383 | 48.1134 | 0 | 119.6383 | 865.2773 | 67.84% | 0 | 0 | 6.25 | 10% | 48.1134
7892 | 0 | 0 | 0 | 6.3 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.9482 | 44.3531 | 0 | 110.9482 | 754.3291 | 59.14% | 0 | 0 | 6.25 | 10% | 44.3531
7893 | 0 | 0 | 0 | 2.3 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.8997 | 40.1138 | 0 | 100.8997 | 653.4294 | 51.23% | 0 | 0 | 6.25 | 10% | 40.1138
7894 | 0 | 0 | 0 | 2.4 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653.4294 | 51.23% | 0 | 0 | 6.25 | 10% | 0
7895 | 0 | 0 | 0 | 2.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653.4294 | 51.23% | 0 | 0 | 6.25 | 10% | 0
7896 | 0 | 0 | 0 | 1.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653.4294 | 51.23% | 0 | 0 | 6.25 | 10% | 0
7897 | 0 | 0 | 0 | 1.6 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653.4294 | 51.23% | 0 | 0 | 6.25 | 10% | 0
7898 | 0 | 0 | 0 | 1.5 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653.4294 | 51.23% | 0 | 0 | 6.25 | 10% | 0
7899 | 0 | 0 | 0 | 1.1 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653.4294 | 51.23% | 0 | 0 | 6.25 | 10% | 0
7900 | 0 | 0 | 0 | 1.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7124 | 37.6236 | 0 | 94.7124 | 558.717 | 43.8% | 0 | 0 | 6.25 | 10% | 37.6236
7901 | 0 | 0 | 0 | 2 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.2111 | 43.9562 | 0 | 109.2111 | 449.5059 | 35.24% | 0 | 0 | 6.25 | 10% | 43.9562
7902 | 0 | 0 | 0 | 1 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.807 | 46.8335 | 0 | 115.807 | 333.6989 | 26.16% | 0 | 0 | 6.25 | 10% | 46.8335
7903 | 0 | 1 | 1 | 1.5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.4312 | 47.9783 | 0 | 118.4312 | 215.2677 | 16.88% | 0 | 0 | 6.25 | 10% | 47.9783
7904 | 183 | 53 | 33 | 0.8 | 10.7 | 0 | 0 | 0 | 0 | 1.2282 | 0 | 0 | 1.2282 | 0 | 0 | 0 | 116.01 | 46.8963 | 0 | 116.01 | 99.2577 | 7.782% | 0 | 0 | 6.25 | 10% | 48.1245
7905 | 522 | 226 | 94 | 0.9 | 14.4 | 0 | 0 | 0 | 79.87 | 28.1029 | 0 | 0 | 28.1029 | 0 | 0 | 0 | 0 | 0 | 79.87 | 0 | 179.1277 | 14.04% | 0 | 0 | 6.25 | 10% | 28.1029
7906 | 584 | 334 | 105 | 1 | 16.9 | 0 | 0 | 0 | 122.0219 | 40.3688 | 0 | 0 | 40.3688 | 0 | 0 | 0 | 0 | 0 | 122.0219 | 0 | 301.1496 | 23.61% | 0 | 0 | 6.25 | 10% | 40.3688
7907 | 884 | 517 | 88 | 3.4 | 19.6 | 0 | 0 | 0 | 220.0689 | 63.3713 | 0 | 15.5991 | 47.7722 | 0 | 0 | 0 | 0 | 0 | 220.0689 | 0 | 521.2185 | 40.86% | 15.5991 | 0 | 20.3448 | 32.55% | 47.7722
7908 | 847 | 568 | 118 | 3.8 | 20.6 | 0 | 0 | 0 | 219.3611 | 69.2357 | 0 | 22.8019 | 46.4338 | 0 | 0 | 0 | 0 | 0 | 219.3611 | 0 | 740.5796 | 58.06% | 22.8019 | 0 | 40.9477 | 65.52% | 46.4338
7909 | 206 | 361 | 248 | 3.2 | 20.6 | 0 | 0 | 0 | 40.1645 | 35.5598 | 0 | 0 | 35.5598 | 0 | 0 | 0 | 0 | 0 | 40.1645 | 0 | 780.7441 | 61.21% | 0 | 1.8479 | 38.9026 | 62.24% | 37.4076
7910 | 276 | 330 | 198 | 2.5 | 20.5 | 0 | 0 | 0 | 59.3026 | 36.4524 | 0 | 0 | 36.4524 | 0 | 0 | 0 | 0 | 0 | 59.3026 | 0 | 840.0467 | 65.86% | 0 | 8.6681 | 29.3093 | 46.89% | 45.1205
7911 | 350 | 338 | 202 | 2.7 | 20.6 | 0 | 0 | 0 | 75.5224 | 39.6238 | 0 | 0 | 39.6238 | 0 | 0 | 0 | 0 | 0 | 75.5224 | 0 | 915.569 | 71.78% | 0 | 6.6861 | 21.9096 | 35.06% | 46.3098
7912 | 41 | 94 | 82 | 2.7 | 18.9 | 0 | 0 | 0 | 0 | 7.7053 | 0 | 0 | 7.7053 | 0 | 0 | 0 | 102.6466 | 40.7173 | 0 | 102.6466 | 812.9224 | 63.73% | 0 | 0 | 21.9096 | 35.06% | 48.4226
7913 | 15 | 19 | 18 | 2.4 | 17.2 | 0 | 0 | 0 | 0 | 1.2434 | 0 | 0 | 1.2434 | 0 | 0 | 0 | 119.0567 | 47.9298 | 0 | 119.0567 | 693.8657 | 54.4% | 0 | 0 | 21.9096 | 35.06% | 49.1732
7914 | 0 | 0 | 0 | 2.2 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.0033 | 49.3055 | 0 | 122.0033 | 571.8624 | 44.83% | 0 | 0 | 21.9096 | 35.06% | 49.3055
7915 | 0 | 0 | 0 | 1.3 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.2006 | 47.7346 | 0 | 118.2006 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 47.7346
7916 | 0 | 0 | 0 | 1 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 0
7917 | 0 | 0 | 0 | 2.4 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 0
7918 | 0 | 0 | 0 | 2.7 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 0
7919 | 0 | 0 | 0 | 3.2 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 0
7920 | 0 | 0 | 0 | 1.4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 0
7921 | 0 | 0 | 0 | 1.6 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 0
7922 | 0 | 0 | 0 | 1.2 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 0
7923 | 0 | 0 | 0 | 1.8 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 0
7924 | 0 | 0 | 0 | 3.2 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.6618 | 35.57% | 0 | 0 | 21.9096 | 35.06% | 0
7925 | 0 | 0 | 0 | 2.7 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.6198 | 43.0844 | 0 | 107.6198 | 346.0421 | 27.13% | 0 | 0 | 21.9096 | 35.06% | 43.0844
7926 | 0 | 0 | 0 | 3.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.1883 | 45.8906 | 0 | 114.1883 | 231.8537 | 18.18% | 0 | 0 | 21.9096 | 35.06% | 45.8906
7927 | 0 | 0 | 0 | 4.2 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.5055 | 46.8906 | 0 | 116.5055 | 115.3483 | 9.043% | 0 | 0 | 21.9096 | 35.06% | 46.8906
7928 | 306 | 57 | 22 | 3.7 | 17.3 | 0 | 0 | 0 | 0 | 0.66321 | 0 | 0 | 0.66321 | 0 | 0 | 0 | 115.3483 | 46.3165 | 0 | 115.3483 | 0 | 0% | 0 | 0 | 21.9096 | 35.06% | 46.9797
7929 | 721 | 243 | 61 | 4.3 | 18.5 | 0 | 0 | 0 | 0 | 32.6173 | 0 | 0 | 32.6173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 14.1494 | 6.25 | 10% | 46.7667
7930 | 845 | 390 | 65 | 6.3 | 19.8 | 0 | 0 | 0 | 0 | 46.6719 | 4.5474 | 0 | 46.6719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 46.6719
7931 | 900 | 484 | 61 | 5.7 | 20.9 | 0 | 0 | 0 | 221.9845 | 46.6009 | 15.5721 | 0 | 46.6009 | 0 | 0 | 0 | 0 | 0 | 221.9845 | 0 | 221.9845 | 17.4% | 0 | 0 | 6.25 | 10% | 46.6009
7932 | 925 | 548 | 64 | 6.3 | 21.6 | 0 | 0 | 0 | 236.5597 | 45.3976 | 24.1614 | 0 | 45.3976 | 0 | 0 | 0 | 0 | 0 | 236.5597 | 0 | 458.5442 | 35.95% | 0 | 0 | 6.25 | 10% | 45.3976
7933 | 928 | 544 | 58 | 5.8 | 22.1 | 0 | 0 | 0 | 243.7216 | 66.9607 | 3.6577 | 22.1953 | 44.7654 | 0 | 0 | 0 | 0 | 0 | 243.7216 | 0 | 702.2658 | 55.06% | 22.1953 | 0 | 26.3048 | 42.09% | 44.7654
7934 | 897 | 478 | 55 | 5.2 | 22.1 | 0 | 0 | 0 | 231.0312 | 66.0018 | 0 | 21.6417 | 44.3601 | 0 | 0 | 0 | 0 | 0 | 231.0312 | 0 | 933.297 | 73.17% | 21.6417 | 0 | 45.8594 | 73.38% | 44.3601
7935 | 836 | 362 | 50 | 7 | 22 | 0 | 0 | 0 | 202.1891 | 56.7092 | 0 | 11.4996 | 45.2096 | 0 | 0 | 0 | 0 | 0 | 202.1891 | 0 | 1135.4861 | 89.02% | 11.4996 | 0 | 56.25 | 90% | 45.2096
7936 | 692 | 203 | 39 | 7.3 | 21.2 | 0 | 0 | 0 | 140.0241 | 39.4881 | 0 | 0 | 39.4881 | 0 | 0 | 0 | 0 | 0 | 140.0241 | 0 | 1275.5102 | 100% | 0 | 8.1852 | 47.1912 | 75.51% | 47.6733
7937 | 269 | 44 | 16 | 5.4 | 19.3 | 0 | 0 | 0 | 0 | 11.2276 | 0 | 0 | 11.2276 | 0 | 0 | 0 | 93.4729 | 36.7284 | 0 | 93.4729 | 1182.0373 | 92.67% | 0 | 0 | 47.1912 | 75.51% | 47.956
7938 | 0 | 0 | 0 | 2.9 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.0691 | 48.761 | 0 | 121.0691 | 1060.9682 | 83.18% | 0 | 0 | 47.1912 | 75.51% | 48.761
7939 | 0 | 0 | 0 | 1.8 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.8065 | 47.4435 | 0 | 117.8065 | 943.1617 | 73.94% | 0 | 0 | 47.1912 | 75.51% | 47.4435
7940 | 0 | 0 | 0 | 3.2 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.2854 | 43.8127 | 0 | 109.2854 | 833.8763 | 65.38% | 0 | 0 | 47.1912 | 75.51% | 43.8127
7941 | 0 | 0 | 0 | 2.6 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.695 | 39.7308 | 0 | 99.695 | 734.1813 | 57.56% | 0 | 0 | 47.1912 | 75.51% | 39.7308
7942 | 0 | 0 | 0 | 1.1 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0788 | 36.8813 | 0 | 93.0788 | 641.1025 | 50.26% | 0 | 0 | 47.1912 | 75.51% | 36.8813
7943 | 0 | 0 | 0 | 1.5 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.9308 | 34.6628 | 0 | 87.9308 | 553.1716 | 43.37% | 0 | 0 | 47.1912 | 75.51% | 34.6628
7944 | 0 | 0 | 0 | 1.9 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.1716 | 43.37% | 0 | 0 | 47.1912 | 75.51% | 0
7945 | 0 | 0 | 0 | 1.5 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.1716 | 43.37% | 0 | 0 | 47.1912 | 75.51% | 0
7946 | 0 | 0 | 0 | 2.6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.1716 | 43.37% | 0 | 0 | 47.1912 | 75.51% | 0
7947 | 0 | 0 | 0 | 1.6 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553.1716 | 43.37% | 0 | 23.4635 | 21.2233 | 33.96% | 23.4635
7948 | 0 | 0 | 0 | 3 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1618 | 36.944 | 0 | 93.1618 | 460.0098 | 36.06% | 0 | 0 | 21.2233 | 33.96% | 36.944
7949 | 0 | 0 | 0 | 1.7 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7911 | 42.9131 | 0 | 106.7911 | 353.2187 | 27.69% | 0 | 0 | 21.2233 | 33.96% | 42.9131
7950 | 0 | 0 | 0 | 2.1 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.0238 | 45.6288 | 0 | 113.0238 | 240.1949 | 18.83% | 0 | 0 | 21.2233 | 33.96% | 45.6288
7951 | 0 | 0 | 0 | 1.4 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.7962 | 50.3413 | 0 | 123.7962 | 116.3987 | 9.126% | 3.5203 | 0 | 24.4042 | 39.05% | 46.821
7952 | 315 | 57 | 21 | 1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.3987 | 47.1079 | 0 | 116.3987 | 0 | 0% | 0 | 0 | 24.4042 | 39.05% | 47.1079
7953 | 703 | 221 | 48 | 1.3 | 11.9 | 0 | 0 | 0 | 112.0326 | 30.5972 | 0 | 0 | 30.5972 | 0 | 0 | 0 | 0 | 0 | 112.0326 | 0 | 112.0326 | 8.783% | 0 | 16.4034 | 6.25 | 10% | 47.0006
7954 | 845 | 379 | 58 | 1.2 | 16.1 | 0 | 0 | 0 | 182.8853 | 46.9226 | 2.0706 | 0 | 46.9226 | 0 | 0 | 0 | 0 | 0 | 182.8853 | 0 | 294.918 | 23.12% | 0 | 0 | 6.25 | 10% | 46.9226
7955 | 905 | 492 | 62 | 2.2 | 17.6 | 0 | 0 | 0 | 225.6972 | 46.924 | 14.2543 | 0 | 46.924 | 0 | 0 | 0 | 0 | 0 | 225.6972 | 0 | 520.6152 | 40.82% | 0 | 0 | 6.25 | 10% | 46.924
7956 | 932 | 552 | 64 | 3.7 | 18.5 | 0 | 0 | 0 | 242.7455 | 47.136 | 22.1766 | 1.6019 | 45.5341 | 0 | 0 | 0 | 0 | 0 | 242.7455 | 0 | 763.3606 | 59.85% | 1.6019 | 0 | 7.6974 | 12.32% | 45.5341
7957 | 932 | 549 | 63 | 2.5 | 19.5 | 0 | 0 | 0 | 247.1478 | 69.5679 | 0 | 24.5505 | 45.0174 | 0 | 0 | 0 | 0 | 0 | 247.1478 | 0 | 1010.5085 | 79.22% | 24.5505 | 0 | 29.8803 | 47.81% | 45.0174
7958 | 879 | 485 | 72 | 2.9 | 20.1 | 0 | 0 | 0 | 227.592 | 65.4201 | 0 | 20.6715 | 44.7486 | 0 | 0 | 0 | 0 | 0 | 227.592 | 0 | 1238.1005 | 97.07% | 20.6715 | 0 | 48.5582 | 77.69% | 44.7486
7959 | 725 | 364 | 93 | 3.2 | 19.9 | 0 | 0 | 0 | 37.4097 | 54.1208 | 0 | 8.5128 | 45.6079 | 0 | 0 | 0 | 0 | 0 | 37.4097 | 0 | 1275.5102 | 100% | 8.5128 | 0 | 56.25 | 90% | 45.6079
7960 | 553 | 197 | 62 | 3.1 | 19.3 | 0 | 0 | 0 | 0 | 35.1071 | 0 | 0 | 35.1071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 12.6651 | 42.2332 | 67.57% | 47.7722
7961 | 210 | 50 | 28 | 2.6 | 17.1 | 0 | 0 | 0 | 0 | 10.7632 | 0 | 0 | 10.7632 | 0 | 0 | 0 | 95.6583 | 37.7958 | 0 | 95.6583 | 1179.8519 | 92.5% | 0 | 0 | 42.2332 | 67.57% | 48.559
7962 | 0 | 0 | 0 | 1.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.8996 | 48.9309 | 0 | 120.8996 | 1058.9523 | 83.02% | 0 | 0 | 42.2332 | 67.57% | 48.9309
7963 | 0 | 0 | 0 | 0.7 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.5291 | 47.5173 | 0 | 117.5291 | 941.4232 | 73.81% | 0 | 0 | 42.2332 | 67.57% | 47.5173
7964 | 0 | 0 | 0 | 0.3 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5653 | 44.0955 | 0 | 109.5653 | 831.8579 | 65.22% | 0 | 0 | 42.2332 | 67.57% | 44.0955
7965 | 0 | 0 | 0 | 0.8 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.2518 | 40.0413 | 0 | 100.2518 | 731.6061 | 57.36% | 0 | 0 | 42.2332 | 67.57% | 40.0413
7966 | 0 | 0 | 0 | 1.4 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7103 | 37.1849 | 0 | 93.7103 | 637.8957 | 50.01% | 0 | 0 | 42.2332 | 67.57% | 37.1849
7967 | 0 | 0 | 0 | 1.7 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.8957 | 50.01% | 0 | 19.9257 | 20.1807 | 32.29% | 19.9257
7968 | 0 | 0 | 0 | 2 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.8957 | 50.01% | 0 | 0 | 20.1807 | 32.29% | 0
7969 | 0 | 0 | 0 | 1.6 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.8957 | 50.01% | 0 | 0 | 20.1807 | 32.29% | 0
7970 | 0 | 0 | 0 | 1.7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637.8957 | 50.01% | 0 | 0 | 20.1807 | 32.29% | 0
7971 | 0 | 0 | 0 | 1.3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.3103 | 33.5444 | 0 | 85.3103 | 552.5854 | 43.32% | 0 | 0 | 20.1807 | 32.29% | 33.5444
7972 | 0 | 0 | 0 | 1.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1501 | 36.9635 | 0 | 93.1501 | 459.4353 | 36.02% | 0 | 0 | 20.1807 | 32.29% | 36.9635
7973 | 0 | 0 | 0 | 1.8 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3146 | 42.7083 | 0 | 106.3146 | 353.1207 | 27.68% | 0 | 0 | 20.1807 | 32.29% | 42.7083
7974 | 0 | 0 | 0 | 1.9 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.5994 | 45.4547 | 0 | 112.5994 | 240.5213 | 18.86% | 0 | 0 | 20.1807 | 32.29% | 45.4547
7975 | 0 | 0 | 0 | 1.5 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.5067 | 50.6531 | 0 | 124.5067 | 116.0146 | 9.096% | 4.1218 | 0 | 23.905 | 38.25% | 46.5313
7976 | 336 | 55 | 19 | 1.9 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.0146 | 46.9352 | 0 | 116.0146 | 0 | 0% | 0 | 0 | 23.905 | 38.25% | 46.9352
7977 | 726 | 218 | 40 | 1.5 | 13.1 | 0 | 0 | 0 | 5.0118 | 30.7237 | 0 | 0 | 30.7237 | 0 | 0 | 0 | 0 | 0 | 5.0118 | 0 | 5.0118 | 0.3929% | 0 | 15.9524 | 6.25 | 10% | 46.6761
7978 | 857 | 373 | 49 | 0.3 | 17 | 0 | 0 | 0 | 0 | 46.438 | 0.6456 | 0 | 46.438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0118 | 0.3929% | 0 | 0 | 6.25 | 10% | 46.438
7979 | 914 | 487 | 55 | 1.3 | 18.4 | 0 | 0 | 0 | 228.2691 | 47.8478 | 11.9114 | 1.9391 | 45.9088 | 0 | 0 | 0 | 0 | 0 | 228.2691 | 0 | 233.2809 | 18.29% | 1.9391 | 0 | 8.0021 | 12.8% | 45.9088
7980 | 929 | 542 | 58 | 1.3 | 19.2 | 0 | 0 | 0 | 242.9422 | 65.6728 | 0 | 21.1777 | 44.4952 | 0 | 0 | 0 | 0 | 0 | 242.9422 | 0 | 476.2231 | 37.34% | 21.1777 | 0 | 27.1374 | 43.42% | 44.4952
7981 | 916 | 535 | 60 | 1.2 | 20 | 0 | 0 | 0 | 242.8835 | 66.2771 | 0 | 22.658 | 43.6192 | 0 | 0 | 0 | 0 | 0 | 242.8835 | 0 | 719.1066 | 56.38% | 22.658 | 0 | 47.6102 | 76.18% | 43.6192
7982 | 876 | 469 | 60 | 1.5 | 20.7 | 0 | 0 | 0 | 227.2374 | 43.1122 | 19.3966 | 0 | 43.1122 | 0 | 0 | 0 | 0 | 0 | 227.2374 | 0 | 946.344 | 74.19% | 0 | 0 | 47.6102 | 76.18% | 43.1122
7983 | 801 | 351 | 55 | 2.2 | 20.7 | 0 | 0 | 0 | 196.0997 | 53.5293 | 0 | 9.562 | 43.9673 | 0 | 0 | 0 | 0 | 0 | 196.0997 | 0 | 1142.4437 | 89.57% | 9.562 | 0 | 56.25 | 90% | 43.9673
7984 | 647 | 196 | 44 | 2.2 | 20.2 | 0 | 0 | 0 | 133.0665 | 37.4488 | 0 | 0 | 37.4488 | 0 | 0 | 0 | 0 | 0 | 133.0665 | 0 | 1275.5102 | 100% | 0 | 8.8374 | 46.4694 | 74.35% | 46.2862
7985 | 237 | 43 | 18 | 1.9 | 17.6 | 0 | 0 | 0 | 0 | 10.4504 | 0 | 0 | 10.4504 | 0 | 0 | 0 | 91.9226 | 36.1519 | 0 | 91.9226 | 1183.5876 | 92.79% | 0 | 0 | 46.4694 | 74.35% | 46.6023
7986 | 0 | 0 | 0 | 0.7 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.3371 | 46.4617 | 0 | 115.3371 | 1068.2505 | 83.75% | 0 | 0 | 46.4694 | 74.35% | 46.4617
7987 | 0 | 0 | 0 | 1.4 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.5107 | 45.2806 | 0 | 112.5107 | 955.7399 | 74.93% | 0 | 0 | 46.4694 | 74.35% | 45.2806
7988 | 0 | 0 | 0 | 1.8 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.0741 | 42.4799 | 0 | 106.0741 | 849.6657 | 66.61% | 0 | 0 | 46.4694 | 74.35% | 42.4799
7989 | 0 | 0 | 0 | 2.1 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8586 | 39.3603 | 0 | 98.8586 | 750.8071 | 58.86% | 0 | 0 | 46.4694 | 74.35% | 39.3603
7990 | 0 | 0 | 0 | 1.9 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.3169 | 36.9649 | 0 | 93.3169 | 657.4902 | 51.55% | 0 | 0 | 46.4694 | 74.35% | 36.9649
7991 | 0 | 0 | 0 | 2.6 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.4317 | 34.3828 | 0 | 87.4317 | 570.0585 | 44.69% | 0 | 0 | 46.4694 | 74.35% | 34.3828
7992 | 0 | 0 | 0 | 2.3 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.4038 | 32.6155 | 0 | 83.4038 | 486.6546 | 38.15% | 0 | 0 | 46.4694 | 74.35% | 32.6155
7993 | 0 | 0 | 0 | 1.1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486.6546 | 38.15% | 0 | 0 | 46.4694 | 74.35% | 0
7994 | 0 | 0 | 0 | 0.8 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486.6546 | 38.15% | 0 | 9.3516 | 36.1197 | 57.79% | 9.3516
7995 | 0 | 0 | 0 | 1.6 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-13 | 0 | 0 | 5.6843e-13 | 486.6546 | 38.15% | 0 | 25 | 8.4513 | 13.52% | 25
7996 | 0 | 0 | 0 | 2.7 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.637 | 31.8467 | 0 | 81.637 | 405.0176 | 31.75% | 0 | 0 | 8.4513 | 13.52% | 31.8467
7997 | 0 | 0 | 0 | 1.6 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.1527 | 33.8564 | 0 | 86.1527 | 318.8649 | 25% | 0 | 0 | 8.4513 | 13.52% | 33.8564
7998 | 0 | 0 | 0 | 1.6 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7083 | 35.8591 | 0 | 90.7083 | 228.1566 | 17.89% | 0 | 0 | 8.4513 | 13.52% | 35.8591
7999 | 0 | 0 | 0 | 1.4 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.2674 | 51.3684 | 0 | 126.2674 | 101.8892 | 7.988% | 12.4009 | 0 | 19.6563 | 31.45% | 38.9676
8000 | 219 | 43 | 20 | 1.4 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8892 | 40.7307 | 0 | 101.8892 | 0 | 0% | 0 | 0 | 19.6563 | 31.45% | 40.7307
8001 | 683 | 212 | 45 | 0.9 | 15.2 | 0 | 0 | 0 | 0 | 28.9432 | 0 | 0 | 28.9432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 12.1134 | 6.25 | 10% | 41.0566
8002 | 826 | 364 | 53 | 2.1 | 16.9 | 0 | 0 | 0 | 11.6535 | 40.4007 | 7.6077 | 0 | 40.4007 | 0 | 0 | 0 | 0 | 0 | 11.6535 | 0 | 11.6535 | 0.9136% | 0 | 0 | 6.25 | 10% | 40.4007
8003 | 887 | 475 | 57 | 1.8 | 18.4 | 0 | 0 | 0 | 220.4124 | 40.5232 | 18.4863 | 0 | 40.5232 | 0 | 0 | 0 | 0 | 0 | 220.4124 | 0 | 232.0659 | 18.19% | 0 | 0 | 6.25 | 10% | 40.5232
8004 | 916 | 534 | 58 | 1.8 | 19.4 | 0 | 0 | 0 | 238.6545 | 39.6528 | 25.9359 | 0 | 39.6528 | 0 | 0 | 0 | 0 | 0 | 238.6545 | 0 | 470.7204 | 36.9% | 0 | 0 | 6.25 | 10% | 39.6528
8005 | 916 | 532 | 58 | 2.5 | 19.7 | 0 | 0 | 0 | 241.8985 | 62.9551 | 5.0624 | 25 | 37.9551 | 0 | 0 | 0 | 0 | 0 | 241.8985 | 0 | 712.6189 | 55.87% | 25 | 0 | 28.839 | 46.14% | 37.9551
8006 | 887 | 469 | 57 | 3.1 | 20.3 | 0 | 0 | 0 | 229.259 | 61.9746 | 2.6911 | 25 | 36.9746 | 0 | 0 | 0 | 0 | 0 | 229.259 | 0 | 941.8779 | 73.84% | 25 | 0 | 51.428 | 82.28% | 36.9746
8007 | 819 | 353 | 51 | 3.7 | 19.9 | 0 | 0 | 0 | 199.5969 | 42.6901 | 12.5065 | 5.3367 | 37.3534 | 0 | 0 | 0 | 0 | 0 | 199.5969 | 0 | 1141.4748 | 89.49% | 5.3367 | 0 | 56.25 | 90% | 37.3534
8008 | 657 | 195 | 42 | 4 | 19.1 | 0 | 0 | 0 | 134.0354 | 38.3746 | 0 | 0 | 38.3746 | 0 | 0 | 0 | 0 | 0 | 134.0354 | 0 | 1275.5102 | 100% | 0 | 1.8576 | 54.1942 | 86.71% | 40.2321
8009 | 229 | 41 | 17 | 3.7 | 16.2 | 0 | 0 | 0 | 0 | 10.1535 | 0 | 0 | 10.1535 | 0 | 0 | 0 | 38.2653 | 12.9376 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 17.7246 | 34.5777 | 55.32% | 40.8157
8010 | 0 | 0 | 0 | 2.3 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.2617 | 39.9436 | 0 | 100.2617 | 1136.9832 | 89.14% | 0 | 1.1771 | 33.2751 | 53.24% | 41.1207
8011 | 0 | 0 | 0 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4066 | 40.9327 | 0 | 102.4066 | 1034.5766 | 81.11% | 0 | 0 | 33.2751 | 53.24% | 40.9327
8012 | 0 | 0 | 0 | 0.9 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0384 | 39.0609 | 0 | 98.0384 | 936.5382 | 73.42% | 0 | 0 | 33.2751 | 53.24% | 39.0609
8013 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0727 | 36.4496 | 0 | 92.0727 | 844.4655 | 66.21% | 0 | 0 | 33.2751 | 53.24% | 36.4496
8014 | 0 | 0 | 0 | 0.6 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.9403 | 33.8007 | 0 | 85.9403 | 758.5253 | 59.47% | 0 | 0 | 33.2751 | 53.24% | 33.8007
8015 | 0 | 0 | 0 | 1.3 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.4007 | 31.3927 | 0 | 80.4007 | 678.1245 | 53.16% | 0 | 0 | 33.2751 | 53.24% | 31.3927
8016 | 0 | 0 | 0 | 1 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.0383 | 29.9178 | 0 | 77.0383 | 601.0862 | 47.13% | 0 | 0 | 33.2751 | 53.24% | 29.9178
8017 | 0 | 0 | 0 | 0.8 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.1166 | 29.0808 | 0 | 75.1166 | 525.9696 | 41.24% | 0 | 0 | 33.2751 | 53.24% | 29.0808
8018 | 0 | 0 | 0 | 2.3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.0394 | 13.3424 | 0 | 39.0394 | 486.9302 | 38.18% | 0 | 0 | 33.2751 | 53.24% | 13.3424
8019 | 0 | 0 | 0 | 1.4 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.0905 | 28.6366 | 0 | 74.0905 | 412.8397 | 32.37% | 0 | 0 | 33.2751 | 53.24% | 28.6366
8020 | 0 | 0 | 0 | 1.6 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7328 | 29.358 | 0 | 75.7328 | 337.1069 | 26.43% | 0 | 0 | 33.2751 | 53.24% | 29.358
8021 | 0 | 0 | 0 | 1.4 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7449 | 30.234 | 0 | 77.7449 | 259.362 | 20.33% | 0 | 0 | 33.2751 | 53.24% | 30.234
8022 | 0 | 0 | 0 | 1.9 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8258 | 31.1448 | 0 | 79.8258 | 179.5362 | 14.08% | 0 | 0 | 33.2751 | 53.24% | 31.1448
8023 | 0 | 0 | 0 | 2 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5338 | 34.0736 | 0 | 86.5338 | 93.0023 | 7.291% | 0 | 0 | 33.2751 | 53.24% | 34.0736
8024 | 252 | 58 | 33 | 1.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0023 | 36.8632 | 0 | 93.0023 | 0 | 0% | 0 | 0 | 33.2751 | 53.24% | 36.8632
8025 | 248 | 112 | 41 | 0.6 | 10.3 | 0 | 0 | 0 | 0 | 13.6018 | 0 | 0 | 13.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 24.4188 | 6.25 | 10% | 38.0205
8026 | 818 | 380 | 73 | 0.9 | 16.1 | 0 | 0 | 0 | 174.9143 | 38.086 | 10.1812 | 0 | 38.086 | 0 | 0 | 0 | 0 | 0 | 174.9143 | 0 | 174.9143 | 13.71% | 0 | 0 | 6.25 | 10% | 38.086
8027 | 887 | 477 | 60 | 2.2 | 18 | 0 | 0 | 0 | 209.9405 | 38.6932 | 20.9804 | 0 | 38.6932 | 0 | 0 | 0 | 0 | 0 | 209.9405 | 0 | 384.8548 | 30.17% | 0 | 0 | 6.25 | 10% | 38.6932
8028 | 915 | 536 | 62 | 3.6 | 18.7 | 0 | 0 | 0 | 236.9765 | 38.5985 | 29.1581 | 0 | 38.5985 | 0 | 0 | 0 | 0 | 0 | 236.9765 | 0 | 621.8313 | 48.75% | 0 | 0 | 6.25 | 10% | 38.5985
8029 | 804 | 522 | 104 | 3.1 | 19.3 | 0 | 0 | 0 | 209.4614 | 59.3771 | 6.7196 | 22.5028 | 36.8743 | 0 | 0 | 0 | 0 | 0 | 209.4614 | 0 | 831.2926 | 65.17% | 22.5028 | 0 | 26.5826 | 42.53% | 36.8743
8030 | 784 | 459 | 93 | 3 | 19.4 | 0 | 0 | 0 | 200.4655 | 60.9426 | 1.1901 | 25 | 35.9426 | 0 | 0 | 0 | 0 | 0 | 200.4655 | 0 | 1031.7581 | 80.89% | 25 | 0 | 49.1716 | 78.67% | 35.9426
8031 | 521 | 316 | 126 | 3.4 | 19 | 0 | 0 | 0 | 120.2167 | 44.7278 | 0 | 7.8339 | 36.8938 | 0 | 0 | 0 | 0 | 0 | 120.2167 | 0 | 1151.9748 | 90.31% | 7.8339 | 0 | 56.25 | 90% | 36.8938
8032 | 610 | 195 | 54 | 3.3 | 18.1 | 0 | 0 | 0 | 123.5354 | 37.2129 | 0 | 0 | 37.2129 | 0 | 0 | 0 | 0 | 0 | 123.5354 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 37.2129
8033 | 215 | 40 | 18 | 2.8 | 15.9 | 0 | 0 | 0 | 0 | 9.8168 | 0 | 0 | 9.8168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 9.8168
8034 | 0 | 0 | 0 | 1.5 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8035 | 0 | 0 | 0 | 1.2 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8036 | 0 | 0 | 0 | 0.5 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8037 | 0 | 0 | 0 | 0.7 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8038 | 0 | 0 | 0 | 1.1 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8039 | 0 | 0 | 0 | 0.9 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8040 | 0 | 0 | 0 | 1.5 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8041 | 0 | 0 | 0 | 1.2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8042 | 0 | 0 | 0 | 0.7 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8043 | 0 | 0 | 0 | 0.7 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8044 | 0 | 0 | 0 | 1.3 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8045 | 0 | 0 | 0 | 1.7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8046 | 0 | 0 | 0 | 1.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8047 | 0 | 0 | 0 | 1.9 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8048 | 0 | 21 | 21 | 1.8 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8049 | 0 | 67 | 66 | 2.1 | 9.1 | 0 | 0 | 0 | 0 | 4.8905 | 0 | 0 | 4.8905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 4.8905
8050 | 5 | 118 | 115 | 3.3 | 10.7 | 0 | 0 | 0 | 0 | 8.5325 | 0 | 0 | 8.5325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 8.5325
8051 | 50 | 291 | 262 | 4 | 12.5 | 0 | 0 | 0 | 0 | 26.7538 | 0 | 0 | 26.7538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 26.7538
8052 | 5 | 226 | 222 | 4.6 | 13.3 | 0 | 0 | 0 | 0 | 16.8822 | 0 | 0 | 16.8822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 16.8822
8053 | 1 | 160 | 158 | 5.3 | 13.1 | 0 | 0 | 0 | 0 | 10.899 | 0 | 0 | 10.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 10.899
8054 | 1 | 157 | 155 | 4.6 | 12.9 | 0 | 0 | 0 | 0 | 10.7495 | 0 | 0 | 10.7495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 10.7495
8055 | 0 | 156 | 155 | 4.7 | 13 | 0 | 0 | 0 | 0 | 11.0644 | 0 | 0 | 11.0644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 11.0644
8056 | 13 | 109 | 104 | 5.3 | 13.1 | 0 | 0 | 0 | 0 | 7.9248 | 0 | 0 | 7.9248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 7.9248
8057 | 0 | 9 | 9 | 3.7 | 12.1 | 0 | 0 | 0 | 0 | 0.18593 | 0 | 0 | 0.18593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0.18593
8058 | 0 | 0 | 0 | 3.4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8059 | 0 | 0 | 0 | 2.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8060 | 0 | 0 | 0 | 2.9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8061 | 0 | 0 | 0 | 3.2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8062 | 0 | 0 | 0 | 3 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8063 | 0 | 0 | 0 | 2.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8064 | 0 | 0 | 0 | 2.6 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8065 | 0 | 0 | 0 | 2.3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8066 | 0 | 0 | 0 | 4.7 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8067 | 0 | 0 | 0 | 4.7 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8068 | 0 | 0 | 0 | 5.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8069 | 0 | 0 | 0 | 3.4 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8070 | 0 | 0 | 0 | 4.8 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8071 | 0 | 0 | 0 | 3.3 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8072 | 0 | 4 | 4 | 5.5 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8073 | 0 | 30 | 30 | 8 | 11 | 0 | 0 | 0 | 0 | 1.5234 | 0 | 0 | 1.5234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 1.5234
8074 | 0 | 20 | 20 | 7.1 | 10.7 | 0 | 0 | 0 | 0 | 0.91191 | 0 | 0 | 0.91191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0.91191
8075 | 0 | 8 | 7 | 7.5 | 10.6 | 0 | 0 | 0 | 0 | 0.077812 | 0 | 0 | 0.077812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0.077812
8076 | 0 | 65 | 64 | 8.7 | 10.9 | 0 | 0 | 0 | 0 | 3.8204 | 0 | 0 | 3.8204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 3.8204
8077 | 0 | 100 | 99 | 7.7 | 10.5 | 0 | 0 | 0 | 0 | 6.2744 | 0 | 0 | 6.2744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 6.2744
8078 | 1 | 145 | 143 | 8.7 | 10.7 | 0 | 0 | 0 | 0 | 9.8764 | 0 | 0 | 9.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 9.8764
8079 | 0 | 50 | 50 | 7.9 | 10.5 | 0 | 0 | 0 | 0 | 2.8995 | 0 | 0 | 2.8995 | 0 | 0 | 0 | 110.3613 | 44.4382 | 0 | 110.3613 | 1165.1489 | 91.35% | 0 | 0 | 56.25 | 90% | 47.3377
8080 | 0 | 31 | 31 | 5.5 | 10.3 | 0 | 0 | 0 | 0 | 1.6391 | 0 | 0 | 1.6391 | 0 | 0 | 0 | 117.6615 | 47.626 | 0 | 117.6615 | 1047.4875 | 82.12% | 0 | 0 | 56.25 | 90% | 49.2651
8081 | 0 | 4 | 4 | 3.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9297 | 49.9281 | 0 | 122.9297 | 924.5578 | 72.49% | 0 | 0 | 56.25 | 90% | 49.9281
8082 | 0 | 0 | 0 | 3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.0657 | 50 | 0 | 123.0657 | 801.4921 | 62.84% | 0 | 0 | 56.25 | 90% | 50
8083 | 0 | 0 | 0 | 2.6 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.1091 | 49.1426 | 0 | 121.1091 | 680.3829 | 53.34% | 0 | 0 | 56.25 | 90% | 49.1426
8084 | 0 | 0 | 0 | 2.9 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1285 | 45.2041 | 0 | 112.1285 | 568.2544 | 44.55% | 0 | 0 | 56.25 | 90% | 45.2041
8085 | 0 | 0 | 0 | 2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.2544 | 44.55% | 0 | 0 | 56.25 | 90% | 0
8086 | 0 | 0 | 0 | 2.3 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.2544 | 44.55% | 0 | 21.3724 | 32.5965 | 52.15% | 21.3724
8087 | 0 | 0 | 0 | 1.6 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.2544 | 44.55% | 0 | 0 | 32.5965 | 52.15% | 0
8088 | 0 | 0 | 0 | 1.7 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.2544 | 44.55% | 0 | 0 | 32.5965 | 52.15% | 0
8089 | 0 | 0 | 0 | 0.9 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.2544 | 44.55% | 0 | 0 | 32.5965 | 52.15% | 0
8090 | 0 | 0 | 0 | 1.4 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.2544 | 44.55% | 0 | 0 | 32.5965 | 52.15% | 0
8091 | 0 | 0 | 0 | 0.7 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 568.2544 | 44.55% | 0 | 0 | 32.5965 | 52.15% | 0
8092 | 0 | 0 | 0 | 1.2 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.759 | 37.2323 | 0 | 93.759 | 474.4954 | 37.2% | 0 | 0 | 32.5965 | 52.15% | 37.2323
8093 | 0 | 0 | 0 | 1.2 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.0426 | 43.4688 | 0 | 108.0426 | 366.4528 | 28.73% | 0 | 0 | 32.5965 | 52.15% | 43.4688
8094 | 0 | 0 | 0 | 1.5 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.2587 | 47.4917 | 0 | 117.2587 | 249.1941 | 19.54% | 0.51895 | 0 | 33.0654 | 52.9% | 46.9728
8095 | 0 | 0 | 0 | 1 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9855 | 0 | 127.551 | 121.6431 | 9.537% | 3.2509 | 0 | 36.0028 | 57.6% | 48.7345
8096 | 0 | 21 | 21 | 1 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.6431 | 49.4016 | 0 | 121.6431 | 0 | 0% | 0 | 0 | 36.0028 | 57.6% | 49.4016
8097 | 484 | 191 | 70 | 0.6 | 10.6 | 0 | 0 | 0 | 69.0645 | 24.4099 | 0 | 0 | 24.4099 | 0 | 0 | 0 | 0 | 0 | 69.0645 | 0 | 69.0645 | 5.415% | 0 | 24.9514 | 8.3883 | 13.42% | 49.3612
8098 | 770 | 364 | 83 | 1 | 14.1 | 0 | 0 | 0 | 161.9896 | 47.347 | 0 | 0 | 47.347 | 0 | 0 | 0 | 0 | 0 | 161.9896 | 0 | 231.0541 | 18.11% | 0 | 1.9321 | 6.25 | 10% | 49.2791
8099 | 641 | 428 | 134 | 4.3 | 15.4 | 0 | 0 | 0 | 151.0271 | 53.8483 | 0 | 4.455 | 49.3933 | 0 | 0 | 0 | 0 | 0 | 151.0271 | 0 | 382.0812 | 29.96% | 4.455 | 0 | 10.2754 | 16.44% | 49.3933
8100 | 309 | 334 | 175 | 6.1 | 15.5 | 0 | 0 | 0 | 64.9823 | 37.9684 | 0 | 0 | 37.9684 | 0 | 0 | 0 | 0 | 0 | 64.9823 | 0 | 447.0635 | 35.05% | 0 | 3.6372 | 6.25 | 10% | 41.6056
8101 | 839 | 573 | 145 | 7 | 16.9 | 0 | 0 | 0 | 215.0762 | 72 | 0 | 24.6136 | 47.3864 | 0 | 0 | 0 | 0 | 0 | 215.0762 | 0 | 662.1397 | 51.91% | 24.6136 | 0 | 28.4899 | 45.58% | 47.3864
8102 | 813 | 487 | 114 | 7.5 | 16.9 | 0 | 0 | 0 | 203.9206 | 68.6708 | 0 | 21.4153 | 47.2555 | 0 | 0 | 0 | 0 | 0 | 203.9206 | 0 | 866.0603 | 67.9% | 21.4153 | 0 | 47.8399 | 76.54% | 47.2555
8103 | 557 | 288 | 79 | 6.5 | 16.3 | 0 | 0 | 0 | 126.3908 | 44.351 | 0 | 0 | 44.351 | 0 | 0 | 0 | 0 | 0 | 126.3908 | 0 | 992.451 | 77.81% | 0 | 3.6551 | 43.7947 | 70.07% | 48.0062
8104 | 145 | 112 | 71 | 3.8 | 14.5 | 0 | 0 | 0 | 0 | 13.9941 | 0 | 0 | 13.9941 | 0 | 0 | 0 | 90.5513 | 35.6916 | 0 | 90.5513 | 901.8998 | 70.71% | 0 | 0 | 43.7947 | 70.07% | 49.6857
8105 | 6 | 15 | 14 | 3 | 12.8 | 0 | 0 | 0 | 0 | 0.71063 | 0 | 0 | 0.71063 | 0 | 0 | 0 | 121.5555 | 49.2453 | 0 | 121.5555 | 780.3443 | 61.18% | 0 | 0 | 43.7947 | 70.07% | 49.9559
8106 | 0 | 0 | 0 | 3.9 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2203 | 50 | 0 | 123.2203 | 657.124 | 51.52% | 0 | 0 | 43.7947 | 70.07% | 50
8107 | 0 | 0 | 0 | 4.1 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.078 | 49.0799 | 0 | 121.078 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 49.0799
8108 | 0 | 0 | 0 | 1.7 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8109 | 0 | 0 | 0 | 1.3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8110 | 0 | 0 | 0 | 2.2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8111 | 0 | 0 | 0 | 1.8 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8112 | 0 | 0 | 0 | 2.1 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8113 | 0 | 0 | 0 | 1.8 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8114 | 0 | 0 | 0 | 1.2 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8115 | 0 | 0 | 0 | 2.2 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8116 | 0 | 0 | 0 | 2.3 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8117 | 0 | 0 | 0 | 1.5 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8118 | 0 | 0 | 0 | 1.4 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8119 | 0 | 0 | 0 | 2 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8120 | 0 | 13 | 13 | 2.1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 536.0459 | 42.03% | 0 | 0 | 43.7947 | 70.07% | 0
8121 | 538 | 185 | 56 | 1.7 | 9.6 | 0 | 0 | 0 | 77.4405 | 24.9944 | 0 | 0 | 24.9944 | 0 | 0 | 0 | 0 | 0 | 77.4405 | 0 | 613.4864 | 48.1% | 0 | 0 | 43.7947 | 70.07% | 24.9944
8122 | 616 | 319 | 96 | 2.6 | 11.1 | 0 | 0 | 0 | 124.8165 | 42.1646 | 0 | 0 | 42.1646 | 0 | 0 | 0 | 0 | 0 | 124.8165 | 0 | 738.3029 | 57.88% | 0 | 0 | 43.7947 | 70.07% | 42.1646
8123 | 459 | 398 | 187 | 3.7 | 12.6 | 0 | 0 | 0 | 102.7524 | 47.2659 | 0 | 0 | 47.2659 | 0 | 0 | 0 | 0 | 0 | 102.7524 | 0 | 841.0554 | 65.94% | 0 | 0 | 43.7947 | 70.07% | 47.2659
8124 | 25 | 250 | 235 | 3.9 | 12.3 | 0 | 0 | 0 | 0 | 19.6503 | 0 | 0 | 19.6503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.0554 | 65.94% | 0 | 0 | 43.7947 | 70.07% | 19.6503
8125 | 6 | 254 | 249 | 4.2 | 13 | 0 | 0 | 0 | 0 | 19.3288 | 0 | 0 | 19.3288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.0554 | 65.94% | 0 | 0 | 43.7947 | 70.07% | 19.3288
8126 | 103 | 295 | 243 | 5.1 | 13.3 | 0 | 0 | 0 | 0 | 27.6868 | 0 | 0 | 27.6868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 841.0554 | 65.94% | 0 | 0 | 43.7947 | 70.07% | 27.6868
8127 | 211 | 266 | 188 | 4.7 | 13.6 | 0 | 0 | 0 | 36.1751 | 30.0896 | 0 | 0 | 30.0896 | 0 | 0 | 0 | 0 | 0 | 36.1751 | 0 | 877.2304 | 68.77% | 0 | 16.7745 | 25.2297 | 40.37% | 46.8641
8128 | 215 | 147 | 100 | 5 | 13.1 | 0 | 0 | 0 | 0 | 20.7639 | 0 | 0 | 20.7639 | 0 | 0 | 0 | 72.5438 | 27.8996 | 0 | 72.5438 | 804.6867 | 63.09% | 0 | 0 | 25.2297 | 40.37% | 48.6635
8129 | 58 | 33 | 25 | 3.9 | 11.9 | 0 | 0 | 0 | 0 | 4.145 | 0 | 0 | 4.145 | 0 | 0 | 0 | 110.6212 | 44.5144 | 0 | 110.6212 | 694.0655 | 54.41% | 0 | 0 | 25.2297 | 40.37% | 48.6593
8130 | 0 | 0 | 0 | 3.3 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.8424 | 48.5646 | 0 | 119.8424 | 574.223 | 45.02% | 0 | 0 | 25.2297 | 40.37% | 48.5646
8131 | 0 | 0 | 0 | 3.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9435 | 0 | 127.551 | 446.672 | 35.02% | 4.3663 | 0 | 29.175 | 46.68% | 47.5772
8132 | 0 | 0 | 0 | 2.6 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.551 | 51.9504 | 0 | 127.551 | 319.121 | 25.02% | 7.5221 | 0 | 35.9716 | 57.55% | 44.4283
8133 | 0 | 0 | 0 | 2.5 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.121 | 25.02% | 0 | 0 | 35.9716 | 57.55% | 0
8134 | 0 | 0 | 0 | 2.7 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.121 | 25.02% | 0 | 0 | 35.9716 | 57.55% | 0
8135 | 0 | 0 | 0 | 2.3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.121 | 25.02% | 0 | 0 | 35.9716 | 57.55% | 0
8136 | 0 | 0 | 0 | 3.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.121 | 25.02% | 0 | 0 | 35.9716 | 57.55% | 0
8137 | 0 | 0 | 0 | 3.2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.121 | 25.02% | 0 | 0 | 35.9716 | 57.55% | 0
8138 | 0 | 0 | 0 | 2.6 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 319.121 | 25.02% | 0 | 0 | 35.9716 | 57.55% | 0
8139 | 0 | 0 | 0 | 1.8 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.121 | 25.02% | 0 | 0 | 35.9716 | 57.55% | 0
8140 | 0 | 0 | 0 | 2.4 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.121 | 25.02% | 0 | 0 | 35.9716 | 57.55% | 0
8141 | 0 | 0 | 0 | 2.3 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.121 | 25.02% | 0 | 0 | 35.9716 | 57.55% | 0
8142 | 0 | 0 | 0 | 2.8 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319.121 | 25.02% | 0 | 1.8553 | 33.9183 | 54.27% | 1.8553
8143 | 0 | 0 | 0 | 4.3 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.368 | 37.8715 | 0 | 95.368 | 223.753 | 17.54% | 0 | 0 | 33.9183 | 54.27% | 37.8715
8144 | 0 | 13 | 13 | 4.8 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.0768 | 40.3589 | 0 | 101.0768 | 122.6762 | 9.618% | 0 | 0 | 33.9183 | 54.27% | 40.3589
8145 | 3 | 89 | 88 | 5 | 12.2 | 0 | 0 | 0 | 0 | 8.1105 | 0 | 0 | 8.1105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.6762 | 9.618% | 0 | 25 | 6.25 | 10% | 33.1105
8146 | 199 | 265 | 189 | 4.9 | 13.1 | 0 | 0 | 0 | 0 | 28.9259 | 0 | 0 | 28.9259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.6762 | 9.618% | 0 | 0 | 6.25 | 10% | 28.9259
8147 | 160 | 321 | 245 | 4.5 | 13.8 | 0 | 0 | 0 | 0 | 32.8566 | 0 | 0 | 32.8566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.6762 | 9.618% | 0 | 0 | 6.25 | 10% | 32.8566
8148 | 281 | 345 | 202 | 4.8 | 14.4 | 0 | 0 | 0 | 58.2248 | 38.5491 | 0 | 0 | 38.5491 | 0 | 0 | 0 | 0 | 0 | 58.2248 | 0 | 180.901 | 14.18% | 0 | 0 | 6.25 | 10% | 38.5491
8149 | 600 | 514 | 207 | 4.9 | 15.2 | 0 | 0 | 0 | 149.2808 | 62.8016 | 0 | 24.2045 | 38.5971 | 0 | 0 | 0 | 0 | 0 | 149.2808 | 0 | 330.1817 | 25.89% | 24.2045 | 0 | 28.1202 | 44.99% | 38.5971
8150 | 628 | 432 | 143 | 5.3 | 15.4 | 0 | 0 | 0 | 154.2516 | 58.5101 | 0 | 20.6901 | 37.82 | 0 | 0 | 0 | 0 | 0 | 154.2516 | 0 | 484.4333 | 37.98% | 20.6901 | 0 | 46.815 | 74.9% | 37.82
8151 | 656 | 337 | 99 | 5 | 15.5 | 0 | 0 | 0 | 153.7179 | 48.7689 | 3.3588 | 10.442 | 38.3269 | 0 | 0 | 0 | 0 | 0 | 153.7179 | 0 | 638.1512 | 50.03% | 10.442 | 0 | 56.25 | 90% | 38.3269
8152 | 487 | 180 | 67 | 6 | 14.6 | 0 | 0 | 0 | 92.0109 | 33.3925 | 0 | 0 | 33.3925 | 0 | 0 | 0 | 0 | 0 | 92.0109 | 0 | 730.1621 | 57.24% | 0 | 7.561 | 47.882 | 76.61% | 40.9535
8153 | 90 | 33 | 23 | 5.3 | 12.9 | 0 | 0 | 0 | 0 | 5.7755 | 0 | 0 | 5.7755 | 0 | 0 | 0 | 91.3633 | 36.0972 | 0 | 91.3633 | 638.7988 | 50.08% | 0 | 0 | 47.882 | 76.61% | 41.8727
8154 | 0 | 0 | 0 | 3.6 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.8511 | 42.4577 | 0 | 105.8511 | 532.9477 | 41.78% | 0 | 0 | 47.882 | 76.61% | 42.4577
8155 | 0 | 0 | 0 | 3.4 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.7632 | 42.4354 | 0 | 105.7632 | 427.1845 | 33.49% | 0 | 0 | 47.882 | 76.61% | 42.4354
8156 | 0 | 0 | 0 | 3.4 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9308 | 41.2098 | 0 | 102.9308 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 41.2098
8157 | 0 | 0 | 0 | 3.2 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 0
8158 | 0 | 0 | 0 | 3.2 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 0
8159 | 0 | 0 | 0 | 3.2 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 0
8160 | 0 | 0 | 0 | 1.1 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 0
8161 | 0 | 0 | 0 | 1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 0
8162 | 0 | 0 | 0 | 1.5 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 0
8163 | 0 | 0 | 0 | 1.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 0
8164 | 0 | 0 | 0 | 1.3 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 0
8165 | 0 | 0 | 0 | 1.2 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 0 | 47.882 | 76.61% | 0
8166 | 0 | 0 | 0 | 1.5 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324.2537 | 25.42% | 0 | 19.402 | 26.4091 | 42.25% | 19.402
8167 | 0 | 0 | 0 | 2.3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.3935 | 38.3715 | 0 | 96.3935 | 227.8602 | 17.86% | 0 | 0 | 26.4091 | 42.25% | 38.3715
8168 | 2 | 16 | 16 | 2.1 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8594 | 40.7641 | 0 | 101.8594 | 126.0008 | 9.878% | 0 | 0 | 26.4091 | 42.25% | 40.7641
8169 | 0 | 69 | 69 | 2 | 9.2 | 0 | 0 | 0 | 0 | 5.5317 | 0 | 5.5317 | 0 | 0 | 0 | 0 | 108.5119 | 43.6559 | 0 | 108.5119 | 17.4889 | 1.371% | 8.3107 | 0 | 33.9183 | 54.27% | 40.877
8170 | 1 | 145 | 143 | 1.4 | 10.6 | 0 | 0 | 0 | 0 | 11.2404 | 0 | 0 | 11.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4889 | 1.371% | 0 | 25 | 6.25 | 10% | 36.2404
8171 | 12 | 246 | 237 | 1.9 | 12.4 | 0 | 0 | 0 | 0 | 19.7893 | 0 | 0 | 19.7893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4889 | 1.371% | 0 | 0 | 6.25 | 10% | 19.7893
8172 | 523 | 444 | 174 | 2.2 | 14 | 0 | 0 | 0 | 127.2316 | 52.6099 | 0 | 12.7663 | 39.8436 | 0 | 0 | 0 | 0 | 0 | 127.2316 | 0 | 144.7206 | 11.35% | 12.7663 | 0 | 17.7851 | 28.46% | 39.8436
8173 | 786 | 507 | 109 | 2.6 | 15.4 | 0 | 0 | 0 | 203.349 | 63.5317 | 2.5073 | 25 | 38.5317 | 0 | 0 | 0 | 0 | 0 | 203.349 | 0 | 348.0695 | 27.29% | 25 | 0 | 40.3741 | 64.6% | 38.5317
8174 | 628 | 480 | 188 | 2.3 | 16.4 | 0 | 0 | 0 | 156.5073 | 55.1118 | 4.855 | 17.5704 | 37.5415 | 0 | 0 | 0 | 0 | 0 | 156.5073 | 0 | 504.5769 | 39.56% | 17.5704 | 0 | 56.25 | 90% | 37.5415
8175 | 113 | 199 | 160 | 2 | 16.1 | 0 | 0 | 0 | 0 | 20.6693 | 0 | 0 | 20.6693 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 504.5769 | 39.56% | 0 | 17.4836 | 36.9003 | 59.04% | 38.1528
8176 | 6 | 83 | 81 | 2.1 | 15.1 | 0 | 0 | 0 | 0 | 5.5042 | 0 | 0 | 5.5042 | 0 | 0 | 0 | 90.3916 | 35.5998 | 0 | 90.3916 | 414.1853 | 32.47% | 0 | 0 | 36.9003 | 59.04% | 41.104
8177 | 15 | 23 | 22 | 2.4 | 13.7 | 0 | 0 | 0 | 0 | 1.5301 | 0 | 0 | 1.5301 | 0 | 0 | 0 | 100.9613 | 40.248 | 0 | 100.9613 | 313.224 | 24.56% | 0 | 0 | 36.9003 | 59.04% | 41.778
8178 | 0 | 0 | 0 | 1.6 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.2976 | 42.6122 | 0 | 106.2976 | 206.9264 | 16.22% | 0 | 0 | 36.9003 | 59.04% | 42.6122
8179 | 0 | 0 | 0 | 0.7 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3917 | 42.2669 | 0 | 105.3917 | 101.5346 | 7.96% | 0 | 0 | 36.9003 | 59.04% | 42.2669
8180 | 0 | 0 | 0 | 1.1 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5346 | 40.6026 | 0 | 101.5346 | 5.1514e-14 | 4.039e-15% | 0 | 0 | 36.9003 | 59.04% | 40.6026
8181 | 0 | 0 | 0 | 0.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0658e-14 | 0 | 0 | 1.0658e-14 | 4.0856e-14 | 3.203e-15% | 0 | 0 | 36.9003 | 59.04% | 0
8182 | 0 | 0 | 0 | 0.5 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0856e-14 | 3.203e-15% | 0 | 25 | 9.232 | 14.77% | 25
8183 | 0 | 0 | 0 | 0.6 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0856e-14 | 3.203e-15% | 0 | 2.6944 | 6.25 | 10% | 2.6944
8184 | 0 | 0 | 0 | 0.7 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0856e-14 | 3.203e-15% | 0 | 0 | 6.25 | 10% | 0
8185 | 0 | 0 | 0 | 0.9 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0856e-14 | 0 | 0 | 4.0856e-14 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8186 | 0 | 0 | 0 | 1.2 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8187 | 0 | 0 | 0 | 1 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8188 | 0 | 0 | 0 | 1.3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8189 | 0 | 0 | 0 | 1.8 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8190 | 0 | 0 | 0 | 1.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8191 | 0 | 0 | 0 | 2.1 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8192 | 149 | 34 | 19 | 1.6 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8193 | 569 | 182 | 54 | 1.1 | 10.4 | 0 | 0 | 0 | 81.7801 | 25.2837 | 0 | 0 | 25.2837 | 0 | 0 | 0 | 0 | 0 | 81.7801 | 0 | 81.7801 | 6.412% | 0 | 0 | 6.25 | 10% | 25.2837
8194 | 756 | 339 | 69 | 0.5 | 13.9 | 0 | 0 | 0 | 157.1233 | 38.2726 | 6.4832 | 0 | 38.2726 | 0 | 0 | 0 | 0 | 0 | 157.1233 | 0 | 238.9035 | 18.73% | 0 | 0 | 6.25 | 10% | 38.2726
8195 | 836 | 454 | 76 | 0.7 | 15.7 | 0 | 0 | 0 | 203.0901 | 38.4676 | 18.3384 | 0 | 38.4676 | 0 | 0 | 0 | 0 | 0 | 203.0901 | 0 | 441.9935 | 34.65% | 0 | 0 | 6.25 | 10% | 38.4676
8196 | 871 | 515 | 77 | 1.7 | 16 | 0 | 0 | 0 | 223.7991 | 38.3228 | 26.9875 | 0 | 38.3228 | 0 | 0 | 0 | 0 | 0 | 223.7991 | 0 | 665.7927 | 52.2% | 0 | 0 | 6.25 | 10% | 38.3228
8197 | 872 | 516 | 76 | 2.6 | 16.7 | 0 | 0 | 0 | 227.2993 | 49.7755 | 17.5839 | 12.9373 | 36.8381 | 0 | 0 | 0 | 0 | 0 | 227.2993 | 0 | 893.092 | 70.02% | 12.9373 | 0 | 17.9397 | 28.7% | 36.8381
8198 | 842 | 456 | 73 | 2.6 | 17.3 | 0 | 0 | 0 | 195.7591 | 61.1139 | 2.9696 | 25 | 36.1139 | 0 | 0 | 0 | 0 | 0 | 195.7591 | 0 | 1088.8511 | 85.37% | 25 | 0 | 40.5287 | 64.85% | 36.1139
8199 | 774 | 342 | 63 | 2.6 | 17.6 | 0 | 0 | 0 | 186.6591 | 54.2194 | 0 | 17.3993 | 36.82 | 0 | 0 | 0 | 0 | 0 | 186.6591 | 0 | 1275.5102 | 100% | 17.3993 | 0 | 56.25 | 90% | 36.82
8200 | 627 | 190 | 47 | 3.1 | 17.1 | 0 | 0 | 0 | 0 | 37.7063 | 0 | 0 | 37.7063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 1.7013 | 54.3671 | 86.99% | 39.4077
8201 | 218 | 39 | 17 | 2 | 15.1 | 0 | 0 | 0 | 0 | 9.9684 | 0 | 0 | 9.9684 | 0 | 0 | 0 | 73.7259 | 28.3595 | 0 | 73.7259 | 1201.7843 | 94.22% | 0 | 2.5003 | 51.6 | 82.56% | 40.8282
8202 | 0 | 0 | 0 | 2.7 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.2835 | 42.1889 | 0 | 105.2835 | 1096.5008 | 85.97% | 0 | 0 | 51.6 | 82.56% | 42.1889
8203 | 0 | 0 | 0 | 0.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8912 | 42.044 | 0 | 104.8912 | 991.6096 | 77.74% | 0 | 0 | 51.6 | 82.56% | 42.044
8204 | 0 | 0 | 0 | 0.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5314 | 40.5901 | 0 | 101.5314 | 890.0782 | 69.78% | 0 | 0 | 51.6 | 82.56% | 40.5901
8205 | 0 | 0 | 0 | 1.4 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.7439 | 37.1961 | 0 | 93.7439 | 796.3343 | 62.43% | 0 | 0 | 51.6 | 82.56% | 37.1961
8206 | 0 | 0 | 0 | 1.8 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.7807 | 34.1628 | 0 | 86.7807 | 709.5536 | 55.63% | 0 | 0 | 51.6 | 82.56% | 34.1628
8207 | 0 | 0 | 0 | 2.5 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 709.5536 | 55.63% | 0 | 0 | 51.6 | 82.56% | 0
8208 | 0 | 0 | 0 | 1.5 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 709.5536 | 55.63% | 0 | 0 | 51.6 | 82.56% | 0
8209 | 0 | 0 | 0 | 1.7 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 709.5536 | 55.63% | 0 | 0 | 51.6 | 82.56% | 0
8210 | 0 | 0 | 0 | 0.8 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 709.5536 | 55.63% | 0 | 0 | 51.6 | 82.56% | 0
8211 | 0 | 0 | 0 | 1.1 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 709.5536 | 55.63% | 0 | 0 | 51.6 | 82.56% | 0
8212 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 709.5536 | 55.63% | 0 | 2.4219 | 48.9195 | 78.27% | 2.4219
8213 | 0 | 0 | 0 | 1.2 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5487 | 37.9774 | 0 | 95.5487 | 614.0049 | 48.14% | 0 | 0 | 48.9195 | 78.27% | 37.9774
8214 | 0 | 0 | 0 | 2.4 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9691 | 40.3408 | 0 | 100.9691 | 513.0358 | 40.22% | 0 | 0 | 48.9195 | 78.27% | 40.3408
8215 | 0 | 0 | 0 | 3.7 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.7209 | 42.8393 | 0 | 106.7209 | 406.3149 | 31.86% | 0 | 0 | 48.9195 | 78.27% | 42.8393
8216 | 232 | 50 | 28 | 2.4 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.8121 | 44.1707 | 0 | 109.8121 | 296.5028 | 23.25% | 0 | 0 | 48.9195 | 78.27% | 44.1707
8217 | 375 | 187 | 102 | 1.8 | 13.7 | 0 | 0 | 0 | 46.9052 | 24.1548 | 0 | 0 | 24.1548 | 0 | 0 | 0 | 0 | 0 | 46.9052 | 0 | 343.408 | 26.92% | 0 | 20.5117 | 26.2186 | 41.95% | 44.6665
8218 | 331 | 269 | 150 | 0.8 | 16.8 | 0 | 0 | 0 | 58.7201 | 30.6715 | 0 | 0 | 30.6715 | 0 | 0 | 0 | 0 | 0 | 58.7201 | 0 | 402.1282 | 31.53% | 0 | 13.8208 | 10.9226 | 17.48% | 44.4924
8219 | 483 | 393 | 170 | 0.5 | 18.7 | 0 | 0 | 0 | 109.9023 | 44.2745 | 0 | 0 | 44.2745 | 0 | 0 | 0 | 0 | 0 | 109.9023 | 0 | 512.0304 | 40.14% | 0 | 0.38088 | 10.5011 | 16.8% | 44.6553
8220 | 352 | 372 | 192 | 0.7 | 19.6 | 0 | 0 | 0 | 80.2643 | 40.0789 | 0 | 0 | 40.0789 | 0 | 0 | 0 | 0 | 0 | 80.2643 | 0 | 592.2947 | 46.44% | 0 | 3.8411 | 6.25 | 10% | 43.92
8221 | 849 | 523 | 96 | 1 | 20.8 | 0 | 0 | 0 | 221.5014 | 63.1655 | 1.702 | 20.2719 | 42.8936 | 0 | 0 | 0 | 0 | 0 | 221.5014 | 0 | 813.7961 | 63.8% | 20.2719 | 0 | 24.5669 | 39.31% | 42.8936
8222 | 870 | 494 | 99 | 2.2 | 21.5 | 0 | 0 | 0 | 223.4773 | 66.4381 | 0 | 24.2576 | 42.1805 | 0 | 0 | 0 | 0 | 0 | 223.4773 | 0 | 1037.2734 | 81.32% | 24.2576 | 0 | 46.4851 | 74.38% | 42.1805
8223 | 728 | 362 | 99 | 1.9 | 21.7 | 0 | 0 | 0 | 174.7859 | 53.7272 | 0 | 10.8071 | 42.92 | 0 | 0 | 0 | 0 | 0 | 174.7859 | 0 | 1212.0593 | 95.03% | 10.8071 | 0 | 56.25 | 90% | 42.92
8224 | 350 | 195 | 106 | 2.1 | 20.7 | 0 | 0 | 0 | 63.4509 | 28.4669 | 0 | 0 | 28.4669 | 0 | 0 | 0 | 0 | 0 | 63.4509 | 0 | 1275.5102 | 100% | 0 | 17.0436 | 37.3873 | 59.82% | 45.5104
8225 | 8 | 27 | 26 | 1.5 | 16.9 | 0 | 0 | 0 | 0 | 1.5342 | 0 | 0 | 1.5342 | 0 | 0 | 0 | 101.2691 | 40.2381 | 0 | 101.2691 | 1174.2411 | 92.06% | 0 | 4.8133 | 32.0603 | 51.3% | 46.5856
8226 | 0 | 0 | 0 | 0.8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.4257 | 47.3975 | 0 | 117.4257 | 1056.8154 | 82.85% | 0 | 0 | 32.0603 | 51.3% | 47.3975
8227 | 0 | 0 | 0 | 1.4 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.7228 | 46.7096 | 0 | 115.7228 | 941.0926 | 73.78% | 0 | 0 | 32.0603 | 51.3% | 46.7096
8228 | 0 | 0 | 0 | 1.6 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.144 | 43.4228 | 0 | 108.144 | 832.9486 | 65.3% | 0 | 0 | 32.0603 | 51.3% | 43.4228
8229 | 0 | 0 | 0 | 1.7 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6447 | 39.3018 | 0 | 98.6447 | 734.3039 | 57.57% | 0 | 0 | 32.0603 | 51.3% | 39.3018
8230 | 0 | 0 | 0 | 2.4 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7342 | 36.2755 | 0 | 91.7342 | 642.5697 | 50.38% | 0 | 0 | 32.0603 | 51.3% | 36.2755
8231 | 0 | 0 | 0 | 2 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8331 | 33.7101 | 0 | 85.8331 | 556.7366 | 43.65% | 0 | 0 | 32.0603 | 51.3% | 33.7101
8232 | 0 | 0 | 0 | 1.5 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.7366 | 43.65% | 0 | 3.4973 | 28.1898 | 45.1% | 3.4973
8233 | 0 | 0 | 0 | 2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.7366 | 43.65% | 0 | 0 | 28.1898 | 45.1% | 0
8234 | 0 | 0 | 0 | 2.7 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.7366 | 43.65% | 0 | 0 | 28.1898 | 45.1% | 0
8235 | 0 | 0 | 0 | 1.8 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.7366 | 43.65% | 0 | 0 | 28.1898 | 45.1% | 0
8236 | 0 | 0 | 0 | 2 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.0976 | 36.5095 | 0 | 92.0976 | 464.639 | 36.43% | 0 | 0 | 28.1898 | 45.1% | 36.5095
8237 | 0 | 0 | 0 | 1.4 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.5527 | 43.2571 | 0 | 107.5527 | 357.0863 | 28% | 0 | 0 | 28.1898 | 45.1% | 43.2571
8238 | 0 | 0 | 0 | 2.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.3868 | 47.1093 | 0 | 116.3868 | 240.6995 | 18.87% | 0 | 0 | 28.1898 | 45.1% | 47.1093
8239 | 0 | 0 | 0 | 2.7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.0063 | 48.6927 | 0 | 120.0063 | 120.6933 | 9.462% | 0 | 0 | 28.1898 | 45.1% | 48.6927
8240 | 261 | 38 | 14 | 2.5 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.6933 | 48.9852 | 0 | 120.6933 | 0 | 0% | 0 | 0 | 28.1898 | 45.1% | 48.9852
8241 | 736 | 196 | 37 | 0.5 | 10.5 | 0 | 0 | 0 | 110.092 | 28.8919 | 0 | 0 | 28.8919 | 0 | 0 | 0 | 0 | 0 | 110.092 | 0 | 110.092 | 8.631% | 0 | 19.6031 | 6.4943 | 10.39% | 48.495
8242 | 893 | 359 | 48 | 0.4 | 15.3 | 0 | 0 | 0 | 187.759 | 47.9511 | 0 | 0 | 47.9511 | 0 | 0 | 0 | 0 | 0 | 187.759 | 0 | 297.851 | 23.35% | 0 | 0.22078 | 6.25 | 10% | 48.1719
8243 | 962 | 480 | 52 | 0.9 | 17.6 | 0 | 0 | 0 | 235.0269 | 59.1161 | 1.5343 | 11.206 | 47.9101 | 0 | 0 | 0 | 0 | 0 | 235.0269 | 0 | 532.8779 | 41.78% | 11.206 | 0 | 16.3753 | 26.2% | 47.9101
8244 | 987 | 543 | 53 | 1.1 | 18.7 | 0 | 0 | 0 | 255.9719 | 67.5711 | 0 | 20.7947 | 46.7764 | 0 | 0 | 0 | 0 | 0 | 255.9719 | 0 | 788.8498 | 61.85% | 20.7947 | 0 | 35.1646 | 56.26% | 46.7764
8245 | 980 | 541 | 53 | 1.5 | 19.8 | 0 | 0 | 0 | 240.5692 | 69.5789 | 0 | 23.3359 | 46.243 | 0 | 0 | 0 | 0 | 0 | 240.5692 | 0 | 1029.419 | 80.71% | 23.3359 | 0 | 56.25 | 90% | 46.243
8246 | 950 | 479 | 51 | 1.5 | 20.4 | 0 | 0 | 0 | 246.0912 | 46.0842 | 19.8257 | 0 | 46.0842 | 0 | 0 | 0 | 0 | 0 | 246.0912 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 46.0842
8247 | 879 | 360 | 46 | 1.8 | 20.5 | 0 | 0 | 0 | 0 | 46.931 | 9.9025 | 0 | 46.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 46.931
8248 | 729 | 201 | 37 | 2.8 | 18.4 | 0 | 0 | 0 | 0 | 41.1286 | 0 | 0 | 41.1286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 8.131 | 47.2512 | 75.6% | 49.2596
8249 | 290 | 43 | 15 | 1.5 | 15.8 | 0 | 0 | 0 | 0 | 12.2311 | 0 | 0 | 12.2311 | 0 | 0 | 0 | 78.3817 | 30.3581 | 0 | 78.3817 | 1197.1285 | 93.85% | 0 | 7.4108 | 39.0494 | 62.48% | 50
8250 | 0 | 0 | 0 | 0.8 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2709 | 50 | 0 | 123.2709 | 1073.8576 | 84.19% | 0 | 0 | 39.0494 | 62.48% | 50
8251 | 0 | 0 | 0 | 0.6 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.1595 | 49.5966 | 0 | 122.1595 | 951.6981 | 74.61% | 0 | 0 | 39.0494 | 62.48% | 49.5966
8252 | 0 | 0 | 0 | 1.1 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.2508 | 45.711 | 0 | 113.2508 | 838.4473 | 65.73% | 0 | 0 | 39.0494 | 62.48% | 45.711
8253 | 0 | 0 | 0 | 0.8 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.6775 | 41.1221 | 0 | 102.6775 | 735.7698 | 57.68% | 0 | 0 | 39.0494 | 62.48% | 41.1221
8254 | 0 | 0 | 0 | 1.6 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735.7698 | 57.68% | 0 | 0 | 39.0494 | 62.48% | 0
8255 | 0 | 0 | 0 | 0.7 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735.7698 | 57.68% | 0 | 0 | 39.0494 | 62.48% | 0
8256 | 0 | 0 | 0 | 1.6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735.7698 | 57.68% | 0 | 0 | 39.0494 | 62.48% | 0
8257 | 0 | 0 | 0 | 1.5 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735.7698 | 57.68% | 0 | 0 | 39.0494 | 62.48% | 0
8258 | 0 | 0 | 0 | 1.3 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735.7698 | 57.68% | 0 | 0 | 39.0494 | 62.48% | 0
8259 | 0 | 0 | 0 | 1.9 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 735.7698 | 57.68% | 0 | 0 | 39.0494 | 62.48% | 0
8260 | 0 | 0 | 0 | 2 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.6745 | 26.7169 | 0 | 69.6745 | 666.0953 | 52.22% | 0 | 0 | 39.0494 | 62.48% | 26.7169
8261 | 0 | 0 | 0 | 2 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.3302 | 44.4492 | 0 | 110.3302 | 555.7651 | 43.57% | 0 | 0 | 39.0494 | 62.48% | 44.4492
8262 | 0 | 0 | 0 | 2.6 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.549 | 48.0396 | 0 | 118.549 | 437.2162 | 34.28% | 0 | 0 | 39.0494 | 62.48% | 48.0396
8263 | 0 | 0 | 0 | 2.3 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.5779 | 49.3654 | 0 | 121.5779 | 315.6383 | 24.75% | 0 | 0 | 39.0494 | 62.48% | 49.3654
8264 | 81 | 29 | 22 | 2.5 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.1547 | 49.5966 | 0 | 122.1547 | 193.4836 | 15.17% | 0 | 0 | 39.0494 | 62.48% | 49.5966
8265 | 334 | 155 | 81 | 1.5 | 11.8 | 0 | 0 | 0 | 39.751 | 19.4211 | 0 | 0 | 19.4211 | 0 | 0 | 0 | 0 | 0 | 39.751 | 0 | 233.2346 | 18.29% | 0 | 25 | 11.3811 | 18.21% | 44.4211
8266 | 711 | 386 | 139 | 1.2 | 17 | 0 | 0 | 0 | 145.2813 | 47.7758 | 0 | 0 | 47.7758 | 0 | 0 | 0 | 0 | 0 | 145.2813 | 0 | 378.5159 | 29.68% | 0 | 0.87793 | 10.4095 | 16.66% | 48.6538
8267 | 527 | 382 | 144 | 3.5 | 19.2 | 0 | 0 | 0 | 119.3564 | 46.4357 | 0 | 0 | 46.4357 | 0 | 0 | 0 | 0 | 0 | 119.3564 | 0 | 497.8723 | 39.03% | 0 | 1.8727 | 8.3369 | 13.34% | 48.3084
8268 | 619 | 467 | 157 | 6.1 | 20.7 | 0 | 0 | 0 | 150.2958 | 57.6338 | 0 | 10.6471 | 46.9867 | 0 | 0 | 0 | 0 | 0 | 150.2958 | 0 | 648.1681 | 50.82% | 10.6471 | 0 | 17.9572 | 28.73% | 46.9867
8269 | 800 | 499 | 100 | 8.1 | 21.7 | 0 | 0 | 0 | 202.015 | 66.8313 | 0 | 19.9128 | 46.9185 | 0 | 0 | 0 | 0 | 0 | 202.015 | 0 | 850.1831 | 66.65% | 19.9128 | 0 | 35.9496 | 57.52% | 46.9185
8270 | 898 | 465 | 61 | 8.7 | 21.2 | 0 | 0 | 0 | 225.6367 | 67.703 | 0 | 21.265 | 46.438 | 0 | 0 | 0 | 0 | 0 | 225.6367 | 0 | 1075.8198 | 84.34% | 21.265 | 0 | 55.1639 | 88.26% | 46.438
8271 | 579 | 334 | 116 | 6.6 | 20.8 | 0 | 0 | 0 | 131.5474 | 48.4367 | 0 | 1.2021 | 47.2346 | 0 | 0 | 0 | 0 | 0 | 131.5474 | 0 | 1207.3672 | 94.66% | 1.2021 | 0 | 56.25 | 90% | 47.2346
8272 | 385 | 178 | 94 | 6.1 | 19.3 | 0 | 0 | 0 | 68.143 | 29.8474 | 0 | 0 | 29.8474 | 0 | 0 | 0 | 0 | 0 | 68.143 | 0 | 1275.5102 | 100% | 0 | 19.848 | 34.2835 | 54.85% | 49.6955
8273 | 65 | 36 | 28 | 5.8 | 17.4 | 0 | 0 | 0 | 0 | 4.6786 | 0 | 0 | 4.6786 | 0 | 0 | 0 | 112.3042 | 44.9914 | 0 | 112.3042 | 1163.206 | 91.2% | 0 | 0.32996 | 33.9183 | 54.27% | 50
8274 | 0 | 0 | 0 | 6.1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.6571 | 50 | 0 | 123.6571 | 1039.5489 | 81.5% | 0 | 0 | 33.9183 | 54.27% | 50
8275 | 0 | 0 | 0 | 2.8 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.4657 | 50 | 0 | 123.4657 | 916.0832 | 71.82% | 0 | 0 | 33.9183 | 54.27% | 50
8276 | 0 | 0 | 0 | 3.1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.197 | 46.0341 | 0 | 114.197 | 801.8862 | 62.87% | 0 | 0 | 33.9183 | 54.27% | 46.0341
8277 | 0 | 0 | 0 | 3.2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801.8862 | 62.87% | 0 | 0 | 33.9183 | 54.27% | 0
8278 | 0 | 0 | 0 | 3.3 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801.8862 | 62.87% | 0 | 0 | 33.9183 | 54.27% | 0
8279 | 0 | 0 | 0 | 1.2 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801.8862 | 62.87% | 0 | 0 | 33.9183 | 54.27% | 0
8280 | 0 | 0 | 0 | 2.8 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801.8862 | 62.87% | 0 | 0 | 33.9183 | 54.27% | 0
8281 | 0 | 0 | 0 | 1.8 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801.8862 | 62.87% | 0 | 0 | 33.9183 | 54.27% | 0
8282 | 0 | 0 | 0 | 1.5 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801.8862 | 62.87% | 0 | 0 | 33.9183 | 54.27% | 0
8283 | 0 | 0 | 0 | 1.8 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801.8862 | 62.87% | 0 | 0 | 33.9183 | 54.27% | 0
8284 | 0 | 0 | 0 | 2.1 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801.8862 | 62.87% | 0 | 0 | 33.9183 | 54.27% | 0
8285 | 0 | 0 | 0 | 1.4 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.2879 | 44.4422 | 0 | 110.2879 | 691.5983 | 54.22% | 0 | 0 | 33.9183 | 54.27% | 44.4422
8286 | 0 | 0 | 0 | 0.5 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.8779 | 48.2011 | 0 | 118.8779 | 572.7204 | 44.9% | 0 | 0 | 33.9183 | 54.27% | 48.2011
8287 | 0 | 0 | 0 | 0.4 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.0528 | 49.5869 | 0 | 122.0528 | 450.6676 | 35.33% | 0 | 0 | 33.9183 | 54.27% | 49.5869
8288 | 7 | 19 | 19 | 1 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9993 | 50 | 0 | 122.9993 | 327.6683 | 25.69% | 0 | 0 | 33.9183 | 54.27% | 50
8289 | 100 | 113 | 91 | 0.6 | 8.3 | 0 | 0 | 0 | 0 | 13.9081 | 0 | 0 | 13.9081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.6683 | 25.69% | 0 | 25 | 6.25 | 10% | 38.9081
8290 | 45 | 150 | 132 | 4.8 | 10.6 | 0 | 0 | 0 | 0 | 13.6717 | 0 | 0 | 13.6717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.6683 | 25.69% | 0 | 0 | 6.25 | 10% | 13.6717
8291 | 0 | 118 | 117 | 1.2 | 11.1 | 0 | 0 | 0 | 0 | 7.8976 | 0 | 0 | 7.8976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.6683 | 25.69% | 0 | 0 | 6.25 | 10% | 7.8976
8292 | 150 | 272 | 194 | 3.6 | 13.2 | 0 | 0 | 0 | 0 | 27.3349 | 0 | 0 | 27.3349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.6683 | 25.69% | 0 | 0 | 6.25 | 10% | 27.3349
8293 | 3 | 158 | 155 | 7.2 | 13.3 | 0 | 0 | 0 | 0 | 10.8936 | 0 | 0 | 10.8936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.6683 | 25.69% | 0 | 0 | 6.25 | 10% | 10.8936
8294 | 0 | 155 | 154 | 8.8 | 14 | 0 | 0 | 0 | 0 | 10.6671 | 0 | 0 | 10.6671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.6683 | 25.69% | 0 | 0 | 6.25 | 10% | 10.6671
8295 | 71 | 181 | 155 | 8.2 | 14.5 | 0 | 0 | 0 | 0 | 16.7878 | 0 | 0 | 16.7878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.6683 | 25.69% | 0 | 0 | 6.25 | 10% | 16.7878
8296 | 90 | 136 | 114 | 8.7 | 14.5 | 0 | 0 | 0 | 0 | 14.7295 | 0 | 0 | 14.7295 | 0 | 0 | 0 | 89.5824 | 35.2704 | 0 | 89.5824 | 238.086 | 18.67% | 0 | 0 | 6.25 | 10% | 50
8297 | 30 | 30 | 26 | 9.6 | 13.1 | 0 | 0 | 0 | 0 | 2.7759 | 0 | 0 | 2.7759 | 0 | 0 | 0 | 116.9398 | 47.2241 | 0 | 116.9398 | 121.1462 | 9.498% | 0 | 0 | 6.25 | 10% | 50
8298 | 0 | 0 | 0 | 10.9 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.1462 | 49.0859 | 0 | 121.1462 | 0 | 0% | 0 | 0 | 6.25 | 10% | 49.0859
8299 | 0 | 0 | 0 | 11.5 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8300 | 0 | 0 | 0 | 5.9 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8301 | 0 | 0 | 0 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8302 | 0 | 0 | 0 | 0 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8303 | 0 | 0 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8312 | 0 | 9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8313 | 0 | 44 | 45 | 8.7 | 11.6 | 0 | 0 | 0 | 0 | 2.9291 | 0 | 0 | 2.9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 2.9291
8314 | 0 | 67 | 67 | 11.9 | 18.5 | 0 | 0 | 0 | 0 | 4.0614 | 0 | 0 | 4.0614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 4.0614
8315 | 0 | 88 | 88 | 9.8 | 18.3 | 0 | 0 | 0 | 0 | 5.4521 | 0 | 0 | 5.4521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 5.4521
8316 | 0 | 122 | 121 | 8.5 | 17 | 0 | 0 | 0 | 0 | 7.885 | 0 | 0 | 7.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 7.885
8317 | 0 | 142 | 141 | 9.1 | 16.5 | 0 | 0 | 0 | 0 | 9.4219 | 0 | 0 | 9.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 9.4219
8318 | 0 | 116 | 116 | 8.6 | 16.2 | 0 | 0 | 0 | 0 | 7.5015 | 0 | 0 | 7.5015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 7.5015
8319 | 0 | 80 | 80 | 0 | 16.3 | 0 | 0 | 0 | 0 | 4.8182 | 0 | 0 | 4.8182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 4.8182
8320 | 0 | 31 | 31 | 0 | 15.9 | 0 | 0 | 0 | 0 | 1.5896 | 0 | 0 | 1.5896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 1.5896
8321 | 7 | 6 | 6 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0.32454 | 0 | 0 | 0.32454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0.32454
8322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8336 | 77 | 28 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8337 | 435 | 164 | 76 | 0 | 0 | 0 | 0 | 0 | 56.7688 | 22.6471 | 0 | 0 | 22.6471 | 0 | 0 | 0 | 0 | 0 | 56.7688 | 0 | 56.7688 | 4.451% | 0 | 0 | 6.25 | 10% | 22.6471
8338 | 431 | 267 | 121 | 0 | 0 | 0 | 0 | 0 | 81.042 | 34.4798 | 0 | 0 | 34.4798 | 0 | 0 | 0 | 0 | 0 | 81.042 | 0 | 137.8108 | 10.8% | 0 | 0 | 6.25 | 10% | 34.4798
8339 | 666 | 412 | 124 | 0 | 0 | 0 | 0 | 0 | 149.6228 | 41.8685 | 11.1308 | 0 | 41.8685 | 0 | 0 | 0 | 0 | 0 | 149.6228 | 0 | 287.4336 | 22.53% | 0 | 0 | 6.25 | 10% | 41.8685
8340 | 846 | 505 | 97 | 0 | 0 | 0 | 0 | 0 | 216.6756 | 41.0775 | 24.0224 | 0 | 41.0775 | 0 | 0 | 0 | 0 | 0 | 216.6756 | 0 | 504.1092 | 39.52% | 0 | 0 | 6.25 | 10% | 41.0775
8341 | 873 | 503 | 80 | 0 | 0 | 0 | 0 | 0 | 228.0748 | 52.796 | 14.3497 | 13.2421 | 39.5539 | 0 | 0 | 0 | 0 | 0 | 228.0748 | 0 | 732.184 | 57.4% | 13.2421 | 0 | 18.2151 | 29.14% | 39.5539
8342 | 885 | 452 | 65 | 0 | 0 | 0 | 0 | 0 | 228.3954 | 63.572 | 1.1421 | 25 | 38.572 | 0 | 0 | 0 | 0 | 0 | 228.3954 | 0 | 960.5794 | 75.31% | 25 | 0 | 40.8041 | 65.29% | 38.572
8343 | 823 | 346 | 60 | 0 | 0 | 0 | 0 | 0 | 200.551 | 56.4368 | 0 | 17.0945 | 39.3422 | 0 | 0 | 0 | 0 | 0 | 200.551 | 0 | 1161.1304 | 91.03% | 17.0945 | 0 | 56.25 | 90% | 39.3422
8344 | 565 | 177 | 48 | 0 | 0 | 0 | 0 | 0 | 114.3798 | 35.6296 | 0 | 0 | 35.6296 | 0 | 0 | 0 | 0 | 0 | 114.3798 | 0 | 1275.5102 | 100% | 0 | 6.381 | 49.188 | 78.7% | 42.0106
8345 | 156 | 39 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9746 | 0 | 0 | 8.9746 | 0 | 0 | 0 | 85.6408 | 33.6056 | 0 | 85.6408 | 1189.8694 | 93.29% | 0 | 0 | 49.188 | 78.7% | 42.5802
8346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.385 | 43.0718 | 0 | 107.385 | 1082.4844 | 84.87% | 0 | 0 | 49.188 | 78.7% | 43.0718
8347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.2717 | 42.5872 | 0 | 106.2717 | 976.2127 | 76.54% | 0 | 0 | 49.188 | 78.7% | 42.5872
8348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.3209 | 40.8672 | 0 | 102.3209 | 873.8918 | 68.51% | 0 | 0 | 49.188 | 78.7% | 40.8672
8349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.8971 | 38.0707 | 0 | 95.8971 | 777.9947 | 60.99% | 0 | 0 | 49.188 | 78.7% | 38.0707
8350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9712 | 35.0555 | 0 | 88.9712 | 689.0235 | 54.02% | 0 | 0 | 49.188 | 78.7% | 35.0555
8351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7042 | 32.3272 | 0 | 82.7042 | 606.3193 | 47.54% | 0 | 0 | 49.188 | 78.7% | 32.3272
8352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.1839 | 30.3593 | 0 | 78.1839 | 528.1354 | 41.41% | 0 | 0 | 49.188 | 78.7% | 30.3593
8353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.8134 | 29.3273 | 0 | 75.8134 | 452.322 | 35.46% | 0 | 0 | 49.188 | 78.7% | 29.3273
8354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.322 | 35.46% | 0 | 3.7422 | 45.0464 | 72.07% | 3.7422
8355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.322 | 35.46% | 0 | 25 | 17.378 | 27.8% | 25
8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.6867 | 29.7075 | 0 | 76.6867 | 375.6352 | 29.45% | 0 | 0 | 17.378 | 27.8% | 29.7075
8357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.953 | 31.1295 | 0 | 79.953 | 295.6823 | 23.18% | 0 | 0 | 17.378 | 27.8% | 31.1295
8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.637 | 32.298 | 0 | 82.637 | 213.0452 | 16.7% | 0 | 0 | 17.378 | 27.8% | 32.298
8359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6705 | 34.9246 | 0 | 88.6705 | 124.3748 | 9.751% | 0 | 0 | 17.378 | 27.8% | 34.9246
8360 | 71 | 27 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.2345 | 27.7693 | 0 | 72.2345 | 52.1402 | 4.088% | 0 | 10.0549 | 6.25 | 10% | 37.8242
8361 | 381 | 145 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9239 | 0 | 0 | 19.9239 | 0 | 0 | 0 | 52.1402 | 19.0214 | 0 | 52.1402 | 0 | 0% | 0 | 0 | 6.25 | 10% | 38.9453
8362 | 813 | 334 | 63 | 0 | 0 | 0 | 0 | 0 | 134.3587 | 38.8116 | 8.5289 | 0 | 38.8116 | 0 | 0 | 0 | 0 | 0 | 134.3587 | 0 | 134.3587 | 10.53% | 0 | 0 | 6.25 | 10% | 38.8116
8363 | 892 | 439 | 57 | 0 | 0 | 0 | 0 | 0 | 215.0264 | 39.3102 | 19.5718 | 0 | 39.3102 | 0 | 0 | 0 | 0 | 0 | 215.0264 | 0 | 349.385 | 27.39% | 0 | 0 | 6.25 | 10% | 39.3102
8364 | 922 | 500 | 58 | 0 | 0 | 0 | 0 | 0 | 237.5316 | 39.2029 | 26.5073 | 0 | 39.2029 | 0 | 0 | 0 | 0 | 0 | 237.5316 | 0 | 586.9167 | 46.01% | 0 | 0 | 6.25 | 10% | 39.2029
8365 | 923 | 505 | 58 | 0 | 0 | 0 | 0 | 0 | 242.0814 | 62.6807 | 4.9519 | 25 | 37.6807 | 0 | 0 | 0 | 0 | 0 | 242.0814 | 0 | 828.9981 | 64.99% | 25 | 0 | 28.839 | 46.14% | 37.6807
8366 | 886 | 447 | 59 | 0 | 0 | 0 | 0 | 0 | 228.6234 | 61.8047 | 2.4861 | 25 | 36.8047 | 0 | 0 | 0 | 0 | 0 | 228.6234 | 0 | 1057.6215 | 82.92% | 25 | 0 | 51.428 | 82.28% | 36.8047
8367 | 627 | 294 | 69 | 0 | 0 | 0 | 0 | 0 | 148.8019 | 42.7054 | 4.5051 | 5.3367 | 37.3688 | 0 | 0 | 0 | 0 | 0 | 148.8019 | 0 | 1206.4234 | 94.58% | 5.3367 | 0 | 56.25 | 90% | 37.3688
8368 | 370 | 188 | 116 | 0 | 0 | 0 | 0 | 0 | 69.0868 | 31.8332 | 0 | 0 | 31.8332 | 0 | 0 | 0 | 0 | 0 | 69.0868 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 31.8332
8369 | 136 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3344 | 0 | 0 | 9.3344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 9.3344
8370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 0
8381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 25 | 28.5817 | 45.73% | 25
8382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 28.5817 | 45.73% | 0
8383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.6009 | 47.9546 | 0 | 118.6009 | 1156.9093 | 90.7% | 0 | 0 | 28.5817 | 45.73% | 47.9546
8384 | 0 | 17 | 17 | 1.4 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.8107 | 48.5967 | 0 | 119.8107 | 1037.0985 | 81.31% | 0 | 0 | 28.5817 | 45.73% | 48.5967
8385 | 148 | 127 | 91 | 1 | 10.1 | 0 | 0 | 0 | 0 | 15.8477 | 0 | 0 | 15.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037.0985 | 81.31% | 0 | 0 | 28.5817 | 45.73% | 15.8477
8386 | 167 | 213 | 158 | 1.4 | 11.8 | 0 | 0 | 0 | 0 | 23.5779 | 0 | 0 | 23.5779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037.0985 | 81.31% | 0 | 0 | 28.5817 | 45.73% | 23.5779
8387 | 129 | 273 | 215 | 2.8 | 12.9 | 0 | 0 | 0 | 0 | 26.8147 | 0 | 0 | 26.8147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037.0985 | 81.31% | 0 | 0 | 28.5817 | 45.73% | 26.8147
8388 | 35 | 252 | 232 | 2.4 | 14 | 0 | 0 | 0 | 0 | 20.0921 | 0 | 0 | 20.0921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037.0985 | 81.31% | 0 | 0 | 28.5817 | 45.73% | 20.0921
8389 | 45 | 266 | 241 | 2.8 | 14.3 | 0 | 0 | 0 | 0 | 23.1532 | 0 | 0 | 23.1532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037.0985 | 81.31% | 0 | 0 | 28.5817 | 45.73% | 23.1532
8390 | 14 | 202 | 194 | 3.1 | 14 | 0 | 0 | 0 | 0 | 15.0894 | 0 | 0 | 15.0894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037.0985 | 81.31% | 0 | 0 | 28.5817 | 45.73% | 15.0894
8391 | 9 | 131 | 127 | 2.8 | 13.6 | 0 | 0 | 0 | 0 | 9.2419 | 0 | 0 | 9.2419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037.0985 | 81.31% | 0 | 0 | 28.5817 | 45.73% | 9.2419
8392 | 10 | 103 | 99 | 3.4 | 12.9 | 0 | 0 | 0 | 0 | 7.3642 | 0 | 0 | 7.3642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037.0985 | 81.31% | 0 | 0 | 28.5817 | 45.73% | 7.3642
8393 | 58 | 35 | 30 | 4.5 | 11.4 | 0 | 0 | 0 | 0 | 4.219 | 0 | 0 | 4.219 | 0 | 0 | 0 | 112.1212 | 45.1826 | 0 | 112.1212 | 924.9774 | 72.52% | 0 | 0 | 28.5817 | 45.73% | 49.4016
8394 | 0 | 0 | 0 | 5 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.8551 | 49.8933 | 0 | 122.8551 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 49.8933
8395 | 0 | 0 | 0 | 3.7 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8396 | 0 | 0 | 0 | 2.9 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8397 | 0 | 0 | 0 | 2.7 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8398 | 0 | 0 | 0 | 2.3 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8399 | 0 | 0 | 0 | 1.4 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8400 | 0 | 0 | 0 | 1.9 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8401 | 0 | 0 | 0 | 1.1 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8402 | 0 | 0 | 0 | 2 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8403 | 0 | 0 | 0 | 1.3 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8404 | 0 | 0 | 0 | 2 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 0 | 28.5817 | 45.73% | 0
8405 | 0 | 0 | 0 | 2 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802.1223 | 62.89% | 0 | 16.8383 | 9.9462 | 15.91% | 16.8383
8406 | 0 | 0 | 0 | 1.9 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.8193 | 47.2694 | 0 | 116.8193 | 685.303 | 53.73% | 0 | 0 | 9.9462 | 15.91% | 47.2694
8407 | 0 | 0 | 0 | 3.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.2166 | 48.3042 | 0 | 119.2166 | 566.0864 | 44.38% | 0 | 0 | 9.9462 | 15.91% | 48.3042
8408 | 0 | 10 | 11 | 1.5 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.4033 | 48.8501 | 0 | 120.4033 | 445.6831 | 34.94% | 0 | 0 | 9.9462 | 15.91% | 48.8501
8409 | 0 | 49 | 49 | 0.8 | 9.1 | 0 | 0 | 0 | 0 | 3.4996 | 0 | 0 | 3.4996 | 0 | 0 | 0 | 112.2969 | 45.3088 | 0 | 112.2969 | 333.3862 | 26.14% | 0 | 0 | 9.9462 | 15.91% | 48.8083
8410 | 8 | 114 | 110 | 0.3 | 10 | 0 | 0 | 0 | 0 | 8.4861 | 0 | 0 | 8.4861 | 0 | 0 | 0 | 100.159 | 39.9991 | 0 | 100.159 | 233.2271 | 18.29% | 0 | 0 | 9.9462 | 15.91% | 48.4852
8411 | 510 | 377 | 148 | 0.9 | 12.6 | 0 | 0 | 0 | 114.9824 | 45.1204 | 0 | 0 | 45.1204 | 0 | 0 | 0 | 0 | 0 | 114.9824 | 0 | 348.2095 | 27.3% | 0 | 3.3397 | 6.25 | 10% | 48.4602
8412 | 706 | 471 | 122 | 2.4 | 13.6 | 0 | 0 | 0 | 176.4843 | 60.2478 | 0 | 13.3057 | 46.9421 | 0 | 0 | 0 | 0 | 0 | 176.4843 | 0 | 524.6938 | 41.14% | 13.3057 | 0 | 18.2725 | 29.24% | 46.9421
8413 | 839 | 506 | 91 | 2.6 | 14.2 | 0 | 0 | 0 | 216.8138 | 67.5651 | 0 | 21.3096 | 46.2555 | 0 | 0 | 0 | 0 | 0 | 216.8138 | 0 | 741.5077 | 58.13% | 21.3096 | 0 | 37.5269 | 60.04% | 46.2555
8414 | 529 | 393 | 147 | 2.8 | 14.9 | 0 | 0 | 0 | 128.2267 | 51.0597 | 0 | 5.1106 | 45.9491 | 0 | 0 | 0 | 0 | 0 | 128.2267 | 0 | 869.7344 | 68.19% | 5.1106 | 0 | 42.1446 | 67.43% | 45.9491
8415 | 1 | 105 | 104 | 1.9 | 13.9 | 0 | 0 | 0 | 0 | 6.8112 | 0 | 0 | 6.8112 | 0 | 0 | 0 | 42.8507 | 14.9643 | 0 | 42.8507 | 826.8837 | 64.83% | 0 | 24.5956 | 14.9238 | 23.88% | 46.3711
8416 | 3 | 83 | 82 | 1.6 | 13.5 | 0 | 0 | 0 | 0 | 5.4678 | 0 | 0 | 5.4678 | 0 | 0 | 0 | 107.2774 | 43.0035 | 0 | 107.2774 | 719.6062 | 56.42% | 0 | 0 | 14.9238 | 23.88% | 48.4713
8417 | 1 | 21 | 21 | 1.1 | 12.3 | 0 | 0 | 0 | 0 | 0.96786 | 0 | 0 | 0.96786 | 0 | 0 | 0 | 119.2365 | 48.2541 | 0 | 119.2365 | 600.3697 | 47.07% | 0 | 0 | 14.9238 | 23.88% | 49.222
8418 | 0 | 0 | 0 | 0.9 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9967 | 49.9573 | 0 | 122.9967 | 477.373 | 37.43% | 0 | 0 | 14.9238 | 23.88% | 49.9573
8419 | 0 | 0 | 0 | 1.4 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.729 | 48.9908 | 0 | 120.729 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 48.9908
8420 | 0 | 0 | 0 | 0.8 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 0
8421 | 0 | 0 | 0 | 0.9 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 0
8422 | 0 | 0 | 0 | 1.4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 0
8423 | 0 | 0 | 0 | 0.9 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 0
8424 | 0 | 0 | 0 | 0.8 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 0
8425 | 0 | 0 | 0 | 1 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 0
8426 | 0 | 0 | 0 | 1.4 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 0
8427 | 0 | 0 | 0 | 1.3 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 0
8428 | 0 | 0 | 0 | 2.8 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.644 | 27.96% | 0 | 0 | 14.9238 | 23.88% | 0
8429 | 0 | 0 | 0 | 2.6 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356.644 | 27.96% | 0 | 7.8373 | 6.25 | 10% | 7.8373
8430 | 0 | 0 | 0 | 1.8 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.299 | 47.5048 | 0 | 117.299 | 239.345 | 18.76% | 0 | 0 | 6.25 | 10% | 47.5048
8431 | 0 | 0 | 0 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.4382 | 48.4393 | 0 | 119.4382 | 119.9067 | 9.401% | 0 | 0 | 6.25 | 10% | 48.4393
8432 | 81 | 31 | 24 | 3.2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.9067 | 48.6496 | 0 | 119.9067 | 0 | 0% | 0 | 0 | 6.25 | 10% | 48.6496
8433 | 425 | 138 | 55 | 1.4 | 7.9 | 0 | 0 | 0 | 52.9752 | 18.9866 | 0 | 0 | 18.9866 | 0 | 0 | 0 | 0 | 0 | 52.9752 | 0 | 52.9752 | 4.153% | 0 | 0 | 6.25 | 10% | 18.9866
8434 | 856 | 335 | 48 | 1.8 | 10.4 | 0 | 0 | 0 | 0 | 47.6272 | 0 | 0 | 47.6272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.9752 | 4.153% | 0 | 0 | 6.25 | 10% | 47.6272
8435 | 929 | 456 | 52 | 1.2 | 13.4 | 0 | 0 | 0 | 222.8674 | 59.7307 | 0 | 11.5602 | 48.1705 | 0 | 0 | 0 | 0 | 0 | 222.8674 | 0 | 275.8426 | 21.63% | 11.5602 | 0 | 16.6953 | 26.71% | 48.1705
8436 | 957 | 522 | 56 | 0.9 | 14.5 | 0 | 0 | 0 | 246.3403 | 46.9672 | 19.4244 | 0 | 46.9672 | 0 | 0 | 0 | 0 | 0 | 246.3403 | 0 | 522.183 | 40.94% | 0 | 0 | 16.6953 | 26.71% | 46.9672
8437 | 952 | 534 | 65 | 1.3 | 15.3 | 0 | 0 | 0 | 249.3279 | 60.7499 | 8.8015 | 14.3592 | 46.3906 | 0 | 0 | 0 | 0 | 0 | 249.3279 | 0 | 771.5108 | 60.49% | 14.3592 | 0 | 29.6698 | 47.47% | 46.3906
8438 | 923 | 467 | 54 | 2.1 | 16.2 | 0 | 0 | 0 | 232.3267 | 66.4873 | 0 | 20.3209 | 46.1664 | 0 | 0 | 0 | 0 | 0 | 232.3267 | 0 | 1003.8376 | 78.7% | 20.3209 | 0 | 48.0309 | 76.85% | 46.1664
8439 | 819 | 348 | 54 | 2.8 | 16.5 | 0 | 0 | 0 | 198.1257 | 56.0872 | 0 | 9.0964 | 46.9909 | 0 | 0 | 0 | 0 | 0 | 198.1257 | 0 | 1201.9632 | 94.23% | 9.0964 | 0 | 56.25 | 90% | 46.9909
8440 | 395 | 156 | 67 | 2.6 | 14.8 | 0 | 0 | 0 | 73.547 | 28.6494 | 0 | 0 | 28.6494 | 0 | 0 | 0 | 0 | 0 | 73.547 | 0 | 1275.5102 | 100% | 0 | 20.4333 | 33.6358 | 53.82% | 49.0827
8441 | 170 | 45 | 29 | 3 | 12.9 | 0 | 0 | 0 | 0 | 9.6386 | 0 | 0 | 9.6386 | 0 | 0 | 0 | 100.4074 | 40.0346 | 0 | 100.4074 | 1175.1028 | 92.13% | 0 | 0 | 33.6358 | 53.82% | 49.6732
8442 | 0 | 0 | 0 | 1.9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.7404 | 49.8334 | 0 | 122.7404 | 1052.3623 | 82.51% | 0 | 0 | 33.6358 | 53.82% | 49.8334
8443 | 0 | 0 | 0 | 1.2 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.635 | 48.0786 | 0 | 118.635 | 933.7273 | 73.2% | 0 | 0 | 33.6358 | 53.82% | 48.0786
8444 | 0 | 0 | 0 | 1.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.7748 | 45.094 | 0 | 111.7748 | 821.9525 | 64.44% | 0 | 0 | 33.6358 | 53.82% | 45.094
8445 | 0 | 0 | 0 | 1.3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.5962 | 40.6569 | 0 | 101.5962 | 720.3562 | 56.48% | 0 | 0 | 33.6358 | 53.82% | 40.6569
8446 | 0 | 0 | 0 | 1.6 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.3562 | 56.48% | 0 | 0 | 33.6358 | 53.82% | 0
8447 | 0 | 0 | 0 | 1.6 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.3562 | 56.48% | 0 | 0 | 33.6358 | 53.82% | 0
8448 | 0 | 0 | 0 | 1.2 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.3562 | 56.48% | 0 | 0 | 33.6358 | 53.82% | 0
8449 | 0 | 0 | 0 | 1.4 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.3562 | 56.48% | 0 | 0 | 33.6358 | 53.82% | 0
8450 | 0 | 0 | 0 | 1 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.3562 | 56.48% | 0 | 0 | 33.6358 | 53.82% | 0
8451 | 0 | 0 | 0 | 1.3 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.3562 | 56.48% | 0 | 0 | 33.6358 | 53.82% | 0
8452 | 0 | 0 | 0 | 0.7 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.3562 | 56.48% | 0 | 0 | 33.6358 | 53.82% | 0
8453 | 0 | 0 | 0 | 0.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720.3562 | 56.48% | 0 | 0 | 33.6358 | 53.82% | 0
8454 | 0 | 0 | 0 | 0.8 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.4898 | 46.7221 | 0 | 115.4898 | 604.8665 | 47.42% | 0 | 0 | 33.6358 | 53.82% | 46.7221
8455 | 0 | 0 | 0 | 0.6 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.5627 | 48.0619 | 0 | 118.5627 | 486.3037 | 38.13% | 0 | 0 | 33.6358 | 53.82% | 48.0619
8456 | 2 | 15 | 15 | 1.4 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.3515 | 48.4072 | 0 | 119.3515 | 366.9523 | 28.77% | 0 | 0 | 33.6358 | 53.82% | 48.4072
8457 | 81 | 111 | 91 | 1.3 | 8.7 | 0 | 0 | 0 | 0 | 14.2352 | 0 | 0 | 14.2352 | 0 | 0 | 0 | 87.3551 | 34.4311 | 0 | 87.3551 | 279.5972 | 21.92% | 0 | 0 | 33.6358 | 53.82% | 48.6663
8458 | 686 | 344 | 110 | 2 | 12.4 | 0 | 0 | 0 | 136.5936 | 44.4495 | 0 | 0 | 44.4495 | 0 | 0 | 0 | 0 | 0 | 136.5936 | 0 | 416.1908 | 32.63% | 0 | 4.3017 | 28.8749 | 46.2% | 48.7512
8459 | 567 | 419 | 174 | 3 | 14.5 | 0 | 0 | 0 | 128.1292 | 51.3757 | 0 | 2.2847 | 49.0911 | 0 | 0 | 0 | 0 | 0 | 128.1292 | 0 | 544.32 | 42.67% | 2.2847 | 0 | 30.9393 | 49.5% | 49.0911
8460 | 64 | 208 | 175 | 3.9 | 14.4 | 0 | 0 | 0 | 0 | 18.1451 | 0 | 0 | 18.1451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.32 | 42.67% | 0 | 0 | 30.9393 | 49.5% | 18.1451
8461 | 1 | 156 | 155 | 3.9 | 14.6 | 0 | 0 | 0 | 0 | 10.6851 | 0 | 0 | 10.6851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.32 | 42.67% | 0 | 0 | 30.9393 | 49.5% | 10.6851
8462 | 6 | 168 | 163 | 4.3 | 15 | 0 | 0 | 0 | 0 | 11.7953 | 0 | 0 | 11.7953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.32 | 42.67% | 0 | 0 | 30.9393 | 49.5% | 11.7953
8463 | 533 | 293 | 100 | 5.3 | 16.4 | 0 | 0 | 0 | 120.5437 | 45.002 | 0 | 0 | 45.002 | 0 | 0 | 0 | 0 | 0 | 120.5437 | 0 | 664.8637 | 52.13% | 0 | 2.3148 | 28.3774 | 45.4% | 47.3168
8464 | 113 | 126 | 98 | 7.6 | 16 | 0 | 0 | 0 | 0 | 14.2698 | 0 | 0 | 14.2698 | 0 | 0 | 0 | 87.9571 | 34.5065 | 0 | 87.9571 | 576.9066 | 45.23% | 0 | 0 | 28.3774 | 45.4% | 48.7763
8465 | 9 | 29 | 28 | 6.1 | 15.6 | 0 | 0 | 0 | 0 | 1.7505 | 0 | 0 | 1.7505 | 0 | 0 | 0 | 117.3463 | 47.2835 | 0 | 117.3463 | 459.5603 | 36.03% | 0 | 0 | 28.3774 | 45.4% | 49.034
8466 | 0 | 0 | 0 | 3.4 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.7783 | 49.2512 | 0 | 121.7783 | 337.782 | 26.48% | 0 | 0 | 28.3774 | 45.4% | 49.2512
8467 | 0 | 0 | 0 | 2.4 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.6143 | 47.9449 | 0 | 118.6143 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 47.9449
8468 | 0 | 0 | 0 | 3.6 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8469 | 0 | 0 | 0 | 5.3 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8470 | 0 | 0 | 0 | 5.4 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8471 | 0 | 0 | 0 | 5.9 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8472 | 0 | 0 | 0 | 6.3 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8473 | 0 | 0 | 0 | 8.2 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8474 | 0 | 0 | 0 | 9.7 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8475 | 0 | 0 | 0 | 8.7 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8476 | 0 | 0 | 0 | 5.7 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8477 | 0 | 0 | 0 | 5.9 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8478 | 0 | 0 | 0 | 7.4 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8479 | 0 | 0 | 0 | 9.1 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8480 | 0 | 7 | 8 | 9.1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 0
8481 | 2 | 65 | 64 | 6.3 | 16.4 | 0 | 0 | 0 | 0 | 5.5884 | 0 | 0 | 5.5884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 5.5884
8482 | 57 | 165 | 142 | 5.9 | 17.1 | 0 | 0 | 0 | 0 | 15.4429 | 0 | 0 | 15.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 15.4429
8483 | 15 | 176 | 168 | 7.6 | 17.5 | 0 | 0 | 0 | 0 | 13.3438 | 0 | 0 | 13.3438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 13.3438
8484 | 90 | 263 | 216 | 7.9 | 18 | 0 | 0 | 0 | 0 | 23.957 | 0 | 0 | 23.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 23.957
8485 | 50 | 221 | 194 | 8.3 | 18.6 | 0 | 0 | 0 | 0 | 18.786 | 0 | 0 | 18.786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 18.786
8486 | 141 | 281 | 214 | 7.5 | 18.9 | 0 | 0 | 0 | 0 | 28.5341 | 0 | 0 | 28.5341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 28.5341
8487 | 3 | 163 | 161 | 7.3 | 18.2 | 0 | 0 | 0 | 0 | 11.7217 | 0 | 0 | 11.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 11.7217
8488 | 7 | 109 | 107 | 6.7 | 18.3 | 0 | 0 | 0 | 0 | 7.7935 | 0 | 0 | 7.7935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219.1677 | 17.18% | 0 | 0 | 28.3774 | 45.4% | 7.7935
8489 | 1 | 35 | 34 | 6.9 | 18 | 0 | 0 | 0 | 0 | 1.7617 | 0 | 0 | 1.7617 | 0 | 0 | 0 | 106.3768 | 42.3875 | 0 | 106.3768 | 112.7909 | 8.843% | 0 | 1.2707 | 26.9711 | 43.15% | 45.4199
8490 | 0 | 0 | 0 | 7.9 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7909 | 45.2208 | 0 | 112.7909 | 0 | 0% | 0 | 0 | 26.9711 | 43.15% | 45.2208
8491 | 0 | 0 | 0 | 6.6 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 18.7227 | 6.25 | 10% | 18.7227
8492 | 0 | 0 | 0 | 6.8 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8493 | 0 | 0 | 0 | 6.9 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8494 | 0 | 0 | 0 | 6.7 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8495 | 0 | 0 | 0 | 7.9 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8496 | 0 | 0 | 0 | 8.2 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8497 | 0 | 0 | 0 | 7.8 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8498 | 0 | 0 | 0 | 7.3 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8499 | 0 | 0 | 0 | 7.7 | 17.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8500 | 0 | 0 | 0 | 7.9 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8501 | 0 | 0 | 0 | 5.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8502 | 0 | 0 | 0 | 4.8 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8503 | 0 | 0 | 0 | 5.9 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8504 | 0 | 9 | 9 | 4.1 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8505 | 13 | 67 | 64 | 4.6 | 17.5 | 0 | 0 | 0 | 0 | 5.9558 | 0 | 0 | 5.9558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 5.9558
8506 | 52 | 146 | 125 | 5.1 | 17.5 | 0 | 0 | 0 | 0 | 13.1162 | 0 | 0 | 13.1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 13.1162
8507 | 148 | 281 | 214 | 5.1 | 18.3 | 0 | 0 | 0 | 0 | 28.6205 | 0 | 0 | 28.6205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 28.6205
8508 | 49 | 272 | 244 | 9 | 19.8 | 0 | 0 | 0 | 0 | 23.955 | 0 | 0 | 23.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 23.955
8509 | 603 | 534 | 233 | 6.9 | 21.1 | 0 | 0 | 0 | 0 | 59.6355 | 4.6017 | 21.7653 | 37.8701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 21.7653 | 0 | 25.9163 | 41.47% | 37.8701
8510 | 730 | 496 | 166 | 7.7 | 21.8 | 0 | 0 | 0 | 173.3854 | 62.0902 | 4.1559 | 25 | 37.0902 | 0 | 0 | 0 | 0 | 0 | 173.3854 | 0 | 173.3854 | 13.59% | 25 | 0 | 48.5053 | 77.61% | 37.0902
8511 | 504 | 329 | 139 | 9.2 | 21.3 | 0 | 0 | 0 | 0 | 45.9777 | 0 | 8.5713 | 37.4064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.3854 | 13.59% | 8.5713 | 0 | 56.25 | 90% | 37.4064
8512 | 155 | 138 | 105 | 7.1 | 19.9 | 0 | 0 | 0 | 0 | 17.0321 | 0 | 0 | 17.0321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.3854 | 13.59% | 0 | 0 | 56.25 | 90% | 17.0321
8513 | 215 | 55 | 32 | 5.5 | 19.1 | 0 | 0 | 0 | 0 | 11.5597 | 0 | 0 | 11.5597 | 0 | 0 | 0 | 74.3637 | 28.4831 | 0 | 74.3637 | 99.0217 | 7.763% | 0 | 0 | 56.25 | 90% | 40.0427
8514 | 0 | 0 | 0 | 6 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.477 | 20.3591 | 0 | 55.477 | 43.5446 | 3.414% | 0 | 20.178 | 33.9183 | 54.27% | 40.5371
8515 | 0 | 0 | 0 | 12.9 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.5446 | 15.1458 | 0 | 43.5446 | 0 | 0% | 0 | 25 | 6.25 | 10% | 40.1458
8516 | 0 | 0 | 0 | 14.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8517 | 0 | 0 | 0 | 13.9 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8518 | 0 | 0 | 0 | 15 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8519 | 0 | 0 | 0 | 15.3 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8520 | 0 | 0 | 0 | 15.9 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8521 | 0 | 0 | 0 | 14.7 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8522 | 0 | 0 | 0 | 11 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8523 | 0 | 0 | 0 | 7.8 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8524 | 0 | 0 | 0 | 5.4 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8525 | 0 | 0 | 0 | 7.5 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8526 | 0 | 0 | 0 | 12.8 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8527 | 0 | 0 | 0 | 10.3 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8528 | 166 | 23 | 10 | 9.4 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 0
8529 | 673 | 166 | 33 | 9.2 | 17.5 | 0 | 0 | 0 | 0 | 24.8143 | 0 | 0 | 24.8143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 24.8143
8530 | 840 | 323 | 45 | 9.2 | 18.2 | 0 | 0 | 0 | 0 | 36.8089 | 9.9037 | 0 | 36.8089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 36.8089
8531 | 910 | 443 | 50 | 8.7 | 19.4 | 0 | 0 | 0 | 0 | 37.1668 | 23.4757 | 0 | 37.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 37.1668
8532 | 936 | 510 | 53 | 9 | 20.2 | 0 | 0 | 0 | 180.4455 | 36.6125 | 32.2115 | 0 | 36.6125 | 0 | 0 | 0 | 0 | 0 | 180.4455 | 0 | 180.4455 | 14.15% | 0 | 0 | 6.25 | 10% | 36.6125
8533 | 945 | 520 | 52 | 9.8 | 20.8 | 0 | 0 | 0 | 240.3517 | 34.8201 | 37.0485 | 0 | 34.8201 | 0 | 0 | 0 | 0 | 0 | 240.3517 | 0 | 420.7972 | 32.99% | 0 | 0 | 6.25 | 10% | 34.8201
8534 | 928 | 469 | 49 | 12.4 | 21.1 | 0 | 0 | 0 | 230.5786 | 58.7101 | 10.5868 | 25 | 33.7101 | 0 | 0 | 0 | 0 | 0 | 230.5786 | 0 | 651.3758 | 51.07% | 25 | 0 | 28.839 | 46.14% | 33.7101
8535 | 867 | 359 | 45 | 11.2 | 21.6 | 0 | 0 | 0 | 203.9969 | 59.0569 | 0.39534 | 25 | 34.0569 | 0 | 0 | 0 | 0 | 0 | 203.9969 | 0 | 855.3727 | 67.06% | 25 | 0 | 51.428 | 82.28% | 34.0569
8536 | 727 | 207 | 36 | 10.4 | 21.1 | 0 | 0 | 0 | 145.1114 | 42.1024 | 0.28769 | 5.3367 | 36.7657 | 0 | 0 | 0 | 0 | 0 | 145.1114 | 0 | 1000.4841 | 78.44% | 5.3367 | 0 | 56.25 | 90% | 36.7657
8537 | 313 | 49 | 16 | 10 | 19.5 | 0 | 0 | 0 | 0 | 13.7435 | 0 | 0 | 13.7435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000.4841 | 78.44% | 0 | 24.096 | 29.5822 | 47.33% | 37.8395
8538 | 0 | 0 | 0 | 10.4 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5869 | 34.672 | 0 | 88.5869 | 911.8972 | 71.49% | 0 | 4.3067 | 24.8158 | 39.71% | 38.9787
8539 | 0 | 0 | 0 | 11.1 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.0352 | 39.2155 | 0 | 99.0352 | 812.862 | 63.73% | 0 | 0 | 24.8158 | 39.71% | 39.2155
8540 | 0 | 0 | 0 | 11.3 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1254 | 37.5442 | 0 | 95.1254 | 717.7367 | 56.27% | 0 | 0 | 24.8158 | 39.71% | 37.5442
8541 | 0 | 0 | 0 | 11.2 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1999 | 34.568 | 0 | 88.1999 | 629.5368 | 49.36% | 0 | 0 | 24.8158 | 39.71% | 34.568
8542 | 0 | 0 | 0 | 11.9 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.3797 | 31.6364 | 0 | 81.3797 | 548.1571 | 42.98% | 0 | 0 | 24.8158 | 39.71% | 31.6364
8543 | 0 | 0 | 0 | 10.1 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.065 | 29.3273 | 0 | 76.065 | 472.0921 | 37.01% | 0 | 0 | 24.8158 | 39.71% | 29.3273
8544 | 0 | 0 | 0 | 9.8 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6843e-14 | 0 | 0 | 5.6843e-14 | 472.0921 | 37.01% | 0 | 0 | 24.8158 | 39.71% | 0
8545 | 0 | 0 | 0 | 8.4 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472.0921 | 37.01% | 0 | 0 | 24.8158 | 39.71% | 0
8546 | 0 | 0 | 0 | 8.3 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472.0921 | 37.01% | 0 | 0 | 24.8158 | 39.71% | 0
8547 | 0 | 0 | 0 | 3.5 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472.0921 | 37.01% | 0 | 0 | 24.8158 | 39.71% | 0
8548 | 0 | 0 | 0 | 2.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.4805 | 30.9429 | 0 | 79.4805 | 392.6116 | 30.78% | 0 | 0 | 24.8158 | 39.71% | 30.9429
8549 | 0 | 0 | 0 | 2.4 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9423 | 35.0569 | 0 | 88.9423 | 303.6694 | 23.81% | 0 | 0 | 24.8158 | 39.71% | 35.0569
8550 | 0 | 0 | 0 | 2.5 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.5816 | 38.3896 | 0 | 96.5816 | 207.0877 | 16.24% | 0 | 0 | 24.8158 | 39.71% | 38.3896
8551 | 0 | 0 | 0 | 1.7 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4763 | 40.9842 | 0 | 102.4763 | 104.6114 | 8.202% | 0 | 0 | 24.8158 | 39.71% | 40.9842
8552 | 183 | 25 | 11 | 1.8 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6114 | 41.8811 | 0 | 104.6114 | 0 | 0% | 0 | 0 | 24.8158 | 39.71% | 41.8811
8553 | 695 | 180 | 44 | 1.4 | 16.4 | 0 | 0 | 0 | 0 | 24.8105 | 0 | 0 | 24.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 16.7753 | 6.25 | 10% | 41.5858
8554 | 839 | 331 | 52 | 1.1 | 20.4 | 0 | 0 | 0 | 0 | 41.0079 | 3.9462 | 0 | 41.0079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 6.25 | 10% | 41.0079
8555 | 901 | 467 | 76 | 3.1 | 21.1 | 0 | 0 | 0 | 213.4256 | 41.0872 | 19.6068 | 0 | 41.0872 | 0 | 0 | 0 | 0 | 0 | 213.4256 | 0 | 213.4256 | 16.73% | 0 | 0 | 6.25 | 10% | 41.0872
8556 | 930 | 513 | 57 | 2.2 | 21.7 | 0 | 0 | 0 | 237.7312 | 40.2085 | 24.9222 | 0 | 40.2085 | 0 | 0 | 0 | 0 | 0 | 237.7312 | 0 | 451.1568 | 35.37% | 0 | 0 | 6.25 | 10% | 40.2085
8557 | 866 | 500 | 68 | 3.2 | 20.9 | 0 | 0 | 0 | 223.9347 | 64.0344 | 1.5808 | 25 | 39.0344 | 0 | 0 | 0 | 0 | 0 | 223.9347 | 0 | 675.0915 | 52.93% | 25 | 0 | 28.839 | 46.14% | 39.0344
8558 | 847 | 450 | 64 | 3.5 | 21.1 | 0 | 0 | 0 | 144.6783 | 63.0142 | 0 | 24.4059 | 38.6083 | 0 | 0 | 0 | 0 | 0 | 144.6783 | 0 | 819.7697 | 64.27% | 24.4059 | 0 | 50.8912 | 81.43% | 38.6083
8559 | 772 | 339 | 57 | 3.9 | 20.9 | 0 | 0 | 0 | 185.6124 | 44.8955 | 8.7157 | 5.9307 | 38.9648 | 0 | 0 | 0 | 0 | 0 | 185.6124 | 0 | 1005.3821 | 78.82% | 5.9307 | 0 | 56.25 | 90% | 38.9648
8560 | 666 | 202 | 44 | 3.6 | 20.3 | 0 | 0 | 0 | 0 | 39.909 | 0 | 0 | 39.909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005.3821 | 78.82% | 0 | 1.2228 | 54.8967 | 87.83% | 41.1318
8561 | 286 | 49 | 19 | 2.3 | 18 | 0 | 0 | 0 | 0 | 13.1066 | 0 | 0 | 13.1066 | 0 | 0 | 0 | 38.2653 | 12.9063 | 0 | 38.2653 | 967.1168 | 75.82% | 0 | 15.396 | 37.8574 | 60.57% | 41.409
8562 | 0 | 0 | 0 | 2.1 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.8017 | 30.9957 | 0 | 79.8017 | 887.3152 | 69.57% | 0 | 10.6347 | 26.0876 | 41.74% | 41.6304
8563 | 0 | 0 | 0 | 0.5 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.414 | 41.3435 | 0 | 103.414 | 783.9011 | 61.46% | 0 | 0 | 26.0876 | 41.74% | 41.3435
8564 | 0 | 0 | 0 | 1 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.9627 | 39.0121 | 0 | 97.9627 | 685.9384 | 53.78% | 0 | 0 | 26.0876 | 41.74% | 39.0121
8565 | 0 | 0 | 0 | 1 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.0487 | 35.5736 | 0 | 90.0487 | 595.8896 | 46.72% | 0 | 0 | 26.0876 | 41.74% | 35.5736
8566 | 0 | 0 | 0 | 0.7 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.6671 | 32.3815 | 0 | 82.6671 | 513.2225 | 40.24% | 0 | 0 | 26.0876 | 41.74% | 32.3815
8567 | 0 | 0 | 0 | 1.2 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.133 | 29.5265 | 0 | 76.133 | 437.0895 | 34.27% | 0 | 0 | 26.0876 | 41.74% | 29.5265
8568 | 0 | 0 | 0 | 1.3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437.0895 | 34.27% | 0 | 0 | 26.0876 | 41.74% | 0
8569 | 0 | 0 | 0 | 1.5 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437.0895 | 34.27% | 0 | 0 | 26.0876 | 41.74% | 0
8570 | 0 | 0 | 0 | 0.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437.0895 | 34.27% | 0 | 0 | 26.0876 | 41.74% | 0
8571 | 0 | 0 | 0 | 1.2 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 437.0895 | 34.27% | 0 | 0 | 26.0876 | 41.74% | 0
8572 | 0 | 0 | 0 | 2.7 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6326 | 28.8427 | 0 | 74.6326 | 362.4569 | 28.42% | 0 | 0 | 26.0876 | 41.74% | 28.8427
8573 | 0 | 0 | 0 | 1.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7241 | 31.9679 | 0 | 81.7241 | 280.7328 | 22.01% | 0 | 0 | 26.0876 | 41.74% | 31.9679
8574 | 0 | 0 | 0 | 1.8 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1149 | 34.7477 | 0 | 88.1149 | 192.6179 | 15.1% | 0 | 0 | 26.0876 | 41.74% | 34.7477
8575 | 0 | 0 | 0 | 1.8 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8074 | 37.6598 | 0 | 94.8074 | 97.8105 | 7.668% | 0 | 0 | 26.0876 | 41.74% | 37.6598
8576 | 128 | 22 | 12 | 2.5 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8105 | 38.9383 | 0 | 97.8105 | 0 | 0% | 0 | 0 | 26.0876 | 41.74% | 38.9383
8577 | 538 | 148 | 37 | 1.7 | 12.9 | 0 | 0 | 0 | 12.6169 | 20.9401 | 0 | 0 | 20.9401 | 0 | 0 | 0 | 0 | 0 | 12.6169 | 0 | 12.6169 | 0.9892% | 0 | 17.9244 | 6.25 | 10% | 38.8645
8578 | 747 | 304 | 53 | 1.4 | 16.2 | 0 | 0 | 0 | 0 | 37.8311 | 3.8915 | 0 | 37.8311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6169 | 0.9892% | 0 | 0 | 6.25 | 10% | 37.8311
8579 | 763 | 398 | 70 | 1.9 | 18.4 | 0 | 0 | 0 | 178.481 | 37.4495 | 14.8678 | 0 | 37.4495 | 0 | 0 | 0 | 0 | 0 | 178.481 | 0 | 191.0978 | 14.98% | 0 | 0 | 6.25 | 10% | 37.4495
8580 | 917 | 523 | 72 | 2.3 | 20.1 | 0 | 0 | 0 | 234.0143 | 36.1432 | 29.9796 | 0 | 36.1432 | 0 | 0 | 0 | 0 | 0 | 234.0143 | 0 | 425.1121 | 33.33% | 0 | 0 | 6.25 | 10% | 36.1432
8581 | 947 | 534 | 63 | 1.9 | 21 | 0 | 0 | 0 | 247.4906 | 44.4913 | 24.171 | 9.7701 | 34.7212 | 0 | 0 | 0 | 0 | 0 | 247.4906 | 0 | 672.6028 | 52.73% | 9.7701 | 0 | 15.0778 | 24.12% | 34.7212
8582 | 860 | 454 | 61 | 2.3 | 21.4 | 0 | 0 | 0 | 220.3465 | 58.9706 | 3.5636 | 25 | 33.9706 | 0 | 0 | 0 | 0 | 0 | 220.3465 | 0 | 892.9492 | 70.01% | 25 | 0 | 37.6668 | 60.27% | 33.9706
8583 | 785 | 357 | 70 | 2.4 | 21.5 | 0 | 0 | 0 | 190.2759 | 55.1987 | 0 | 20.5666 | 34.6321 | 0 | 0 | 0 | 0 | 0 | 190.2759 | 0 | 1083.2251 | 84.92% | 20.5666 | 0 | 56.25 | 90% | 34.6321
8584 | 256 | 120 | 55 | 2.2 | 19.8 | 0 | 0 | 0 | 41.8034 | 19.2797 | 0 | 0 | 19.2797 | 0 | 0 | 0 | 0 | 0 | 41.8034 | 0 | 1125.0286 | 88.2% | 0 | 18.493 | 35.7832 | 57.25% | 37.7726
8585 | 192 | 39 | 20 | 1.6 | 17.5 | 0 | 0 | 0 | 0 | 9.8059 | 0 | 0 | 9.8059 | 0 | 0 | 0 | 73.7921 | 28.3038 | 0 | 73.7921 | 1051.2365 | 82.42% | 0 | 0 | 35.7832 | 57.25% | 38.1097
8586 | 0 | 0 | 0 | 2.1 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.9176 | 36.7128 | 0 | 92.9176 | 958.3189 | 75.13% | 0 | 0 | 35.7832 | 57.25% | 36.7128
8587 | 0 | 0 | 0 | 0.9 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.3439 | 34.3731 | 0 | 87.3439 | 870.975 | 68.28% | 0 | 0 | 35.7832 | 57.25% | 34.3731
8588 | 0 | 0 | 0 | 1.2 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3362 | 31.3412 | 0 | 80.3362 | 790.6388 | 61.99% | 0 | 0 | 35.7832 | 57.25% | 31.3412
8589 | 0 | 0 | 0 | 2.5 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3415 | 30 | 0 | 77.3415 | 713.2972 | 55.92% | 0 | 0 | 35.7832 | 57.25% | 30
8590 | 0 | 0 | 0 | 1.7 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3592 | 29.1714 | 0 | 75.3592 | 637.938 | 50.01% | 0 | 0 | 35.7832 | 57.25% | 29.1714
8591 | 0 | 0 | 0 | 2.9 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1239 | 27.7578 | 0 | 72.1239 | 565.8141 | 44.36% | 0 | 0 | 35.7832 | 57.25% | 27.7578
8592 | 0 | 0 | 0 | 2.2 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.3121 | 26.0991 | 0 | 68.3121 | 497.502 | 39% | 0 | 0 | 35.7832 | 57.25% | 26.0991
8593 | 0 | 0 | 0 | 2.9 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.521 | 18.3303 | 0 | 50.521 | 446.981 | 35.04% | 0 | 6.3566 | 28.7482 | 46% | 24.6869
8594 | 0 | 0 | 0 | 2.3 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.4182 | 23.9655 | 0 | 63.4182 | 383.5628 | 30.07% | 0 | 0 | 28.7482 | 46% | 23.9655
8595 | 0 | 0 | 0 | 2.8 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.2653 | 12.9862 | 0 | 38.2653 | 345.2975 | 27.07% | 0 | 10.9472 | 16.6325 | 26.61% | 23.9334
8596 | 0 | 0 | 0 | 2.2 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.293 | 24.3596 | 0 | 64.293 | 281.0045 | 22.03% | 0 | 0 | 16.6325 | 26.61% | 24.3596
8597 | 0 | 0 | 0 | 2.3 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.064 | 25.1242 | 0 | 66.064 | 214.9405 | 16.85% | 0 | 0 | 16.6325 | 26.61% | 25.1242
8598 | 0 | 0 | 0 | 1.8 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.8044 | 25.4431 | 0 | 66.8044 | 148.1361 | 11.61% | 0 | 0 | 16.6325 | 26.61% | 25.4431
8599 | 0 | 0 | 0 | 2.1 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.9698 | 27.2592 | 0 | 70.9698 | 77.1663 | 6.05% | 0 | 0 | 16.6325 | 26.61% | 27.2592
8600 | 118 | 19 | 9 | 2.1 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.1663 | 29.9624 | 0 | 77.1663 | 0 | 0% | 0 | 0 | 16.6325 | 26.61% | 29.9624
8601 | 613 | 154 | 33 | 1 | 12.6 | 0 | 0 | 0 | 54.946 | 22.2148 | 0 | 0 | 22.2148 | 0 | 0 | 0 | 0 | 0 | 54.946 | 0 | 54.946 | 4.308% | 0 | 9.3812 | 6.25 | 10% | 31.596
8602 | 851 | 330 | 48 | 1.5 | 15.8 | 0 | 0 | 0 | 172.4524 | 32.0083 | 13.6922 | 0 | 32.0083 | 0 | 0 | 0 | 0 | 0 | 172.4524 | 0 | 227.3984 | 17.83% | 0 | 0 | 6.25 | 10% | 32.0083
8603 | 921 | 453 | 54 | 1.8 | 18.5 | 0 | 0 | 0 | 218.8551 | 31.8328 | 26.8948 | 0 | 31.8328 | 0 | 0 | 0 | 0 | 0 | 218.8551 | 0 | 446.2535 | 34.99% | 0 | 0 | 6.25 | 10% | 31.8328
8604 | 943 | 536 | 73 | 2 | 20.6 | 0 | 0 | 0 | 241.3535 | 30.7507 | 36.4375 | 0 | 30.7507 | 0 | 0 | 0 | 0 | 0 | 241.3535 | 0 | 687.607 | 53.91% | 0 | 0 | 6.25 | 10% | 30.7507
8605 | 918 | 561 | 103 | 2.4 | 21.3 | 0 | 0 | 0 | 239.0411 | 53.6199 | 17.6685 | 25 | 28.6199 | 0 | 0 | 0 | 0 | 0 | 239.0411 | 0 | 926.6481 | 72.65% | 25 | 0 | 28.839 | 46.14% | 28.6199
8606 | 781 | 437 | 78 | 2.4 | 21.7 | 0 | 0 | 0 | 198.6408 | 52.9764 | 6.9291 | 25 | 27.9764 | 0 | 0 | 0 | 0 | 0 | 198.6408 | 0 | 1125.2889 | 88.22% | 25 | 0 | 51.428 | 82.28% | 27.9764
8607 | 633 | 337 | 105 | 2.2 | 21.6 | 0 | 0 | 0 | 150.2213 | 34.0303 | 15.6728 | 5.3367 | 28.6937 | 0 | 0 | 0 | 0 | 0 | 150.2213 | 0 | 1275.5102 | 100% | 5.3367 | 0 | 56.25 | 90% | 28.6937
8608 | 480 | 203 | 81 | 1.9 | 21 | 0 | 0 | 0 | 0 | 31.798 | 1.9123 | 0 | 31.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.5102 | 100% | 0 | 0 | 56.25 | 90% | 31.798
8609 | 253 | 61 | 35 | 2.2 | 17.4 | 0 | 0 | 0 | 0 | 13.9207 | 0 | 0 | 13.9207 | 0 | 0 | 0 | 38.2653 | 12.9173 | 0 | 38.2653 | 1237.2449 | 97% | 0 | 6.3693 | 49.2008 | 78.72% | 33.2074
8610 | 0 | 0 | 0 | 0.6 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.9728 | 29.3629 | 0 | 75.9728 | 1161.2721 | 91.04% | 0 | 5.0088 | 43.6575 | 69.85% | 34.3717
8611 | 0 | 0 | 0 | 2.2 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.388 | 34.7811 | 0 | 88.388 | 1072.8841 | 84.11% | 0 | 0 | 43.6575 | 69.85% | 34.7811
8612 | 0 | 0 | 0 | 2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.2785 | 33.8968 | 0 | 86.2785 | 986.6056 | 77.35% | 0 | 0 | 43.6575 | 69.85% | 33.8968
8613 | 0 | 0 | 0 | 2.5 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.0925 | 31.188 | 0 | 80.0925 | 906.5131 | 71.07% | 0 | 0 | 43.6575 | 69.85% | 31.188
8614 | 0 | 0 | 0 | 1.1 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.7059 | 28.4458 | 0 | 73.7059 | 832.8072 | 65.29% | 0 | 0 | 43.6575 | 69.85% | 28.4458
8615 | 0 | 0 | 0 | 0.8 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.4495 | 26.1785 | 0 | 68.4495 | 764.3577 | 59.93% | 0 | 0 | 43.6575 | 69.85% | 26.1785
8616 | 0 | 0 | 0 | 0.8 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.506 | 24.8916 | 0 | 65.506 | 698.8517 | 54.79% | 0 | 0 | 43.6575 | 69.85% | 24.8916
8617 | 0 | 0 | 0 | 0.8 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698.8517 | 54.79% | 0 | 7.166 | 35.7266 | 57.16% | 7.166
8618 | 0 | 0 | 0 | 1.2 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 698.8517 | 54.79% | 0 | 0 | 35.7266 | 57.16% | 0
8619 | 0 | 0 | 0 | 2.1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.0473 | 24.673 | 0 | 65.0473 | 633.8044 | 49.69% | 0 | 0 | 35.7266 | 57.16% | 24.673
8620 | 0 | 0 | 0 | 1.7 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.8739 | 27.2188 | 0 | 70.8739 | 562.9306 | 44.13% | 0 | 0 | 35.7266 | 57.16% | 27.2188
8621 | 0 | 0 | 0 | 2.4 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1559 | 30.7925 | 0 | 79.1559 | 483.7746 | 37.93% | 0 | 0 | 35.7266 | 57.16% | 30.7925
8622 | 0 | 0 | 0 | 3 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6525 | 34.0291 | 0 | 86.6525 | 397.1221 | 31.13% | 0 | 0 | 35.7266 | 57.16% | 34.0291
8623 | 0 | 0 | 0 | 2.3 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.1026 | 36.866 | 0 | 93.1026 | 304.0196 | 23.84% | 0 | 0 | 35.7266 | 57.16% | 36.866
8624 | 132 | 28 | 18 | 2.5 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6083 | 38.8311 | 0 | 97.6083 | 206.4113 | 16.18% | 0 | 0 | 35.7266 | 57.16% | 38.8311
8625 | 379 | 149 | 80 | 2 | 15.4 | 0 | 0 | 0 | 43.5156 | 18.7736 | 0 | 0 | 18.7736 | 0 | 0 | 0 | 0 | 0 | 43.5156 | 0 | 249.9269 | 19.59% | 0 | 20.4391 | 13.1059 | 20.97% | 39.2127
8626 | 476 | 266 | 103 | 0.7 | 18.6 | 0 | 0 | 0 | 89.0725 | 32.8076 | 0 | 0 | 32.8076 | 0 | 0 | 0 | 0 | 0 | 89.0725 | 0 | 338.9994 | 26.58% | 0 | 6.1948 | 6.25 | 10% | 39.0024
8627 | 800 | 430 | 81 | 0.6 | 21.8 | 0 | 0 | 0 | 188.4152 | 52.8559 | 0 | 13.6656 | 39.1904 | 0 | 0 | 0 | 0 | 0 | 188.4152 | 0 | 527.4146 | 41.35% | 13.6656 | 0 | 18.5976 | 29.76% | 39.1904
8628 | 848 | 509 | 91 | 0.4 | 23.7 | 0 | 0 | 0 | 215.9587 | 56.3906 | 3.7942 | 18.2252 | 38.1654 | 0 | 0 | 0 | 0 | 0 | 215.9587 | 0 | 743.3733 | 58.28% | 18.2252 | 0 | 35.0652 | 56.1% | 38.1654
8629 | 754 | 505 | 126 | 0.5 | 24.4 | 0 | 0 | 0 | 194.2205 | 59.9762 | 0 | 23.4459 | 36.5304 | 0 | 0 | 0 | 0 | 0 | 194.2205 | 0 | 937.5939 | 73.51% | 23.4459 | 0 | 56.25 | 90% | 36.5304
8630 | 577 | 423 | 154 | 2.6 | 23.7 | 0 | 0 | 0 | 142.1161 | 35.8131 | 17.3372 | 0 | 35.8131 | 0 | 0 | 0 | 0 | 0 | 142.1161 | 0 | 1079.71 | 84.65% | 0 | 0 | 56.25 | 90% | 35.8131
8631 | 544 | 344 | 139 | 2.3 | 23.4 | 0 | 0 | 0 | 126.6833 | 36.5109 | 10.1789 | 0 | 36.5109 | 0 | 0 | 0 | 0 | 0 | 126.6833 | 0 | 1206.3932 | 94.58% | 0 | 0 | 56.25 | 90% | 36.5109
8632 | 369 | 201 | 109 | 1.5 | 21.9 | 0 | 0 | 0 | 69.117 | 30.0065 | 0 | 0 | 30.0065 | 0 | 0 | 0 | 0 | 0 | 69.117 | 0 | 1275.5102 | 100% | 0 | 8.9737 | 46.3186 | 74.11% | 38.9801
8633 | 133 | 55 | 39 | 0.8 | 19.1 | 0 | 0 | 0 | 0 | 8.4345 | 0 | 0 | 8.4345 | 0 | 0 | 0 | 65.7635 | 24.7668 | 0 | 65.7635 | 1209.7467 | 94.84% | 0 | 6.5211 | 39.1014 | 62.56% | 39.7224
8634 | 0 | 0 | 0 | 1 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4513 | 40.338 | 0 | 101.4513 | 1108.2954 | 86.89% | 0 | 0 | 39.1014 | 62.56% | 40.338
8635 | 0 | 0 | 0 | 1 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.4856 | 40.026 | 0 | 100.4856 | 1007.8098 | 79.01% | 0 | 0 | 39.1014 | 62.56% | 40.026
8636 | 0 | 0 | 0 | 1.8 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2855 | 37.7921 | 0 | 95.2855 | 912.5243 | 71.54% | 0 | 0 | 39.1014 | 62.56% | 37.7921
8637 | 0 | 0 | 0 | 2.6 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6883 | 34.5082 | 0 | 87.6883 | 824.836 | 64.67% | 0 | 0 | 39.1014 | 62.56% | 34.5082
8638 | 0 | 0 | 0 | 3.4 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5106 | 31.8203 | 0 | 81.5106 | 743.3254 | 58.28% | 0 | 0 | 39.1014 | 62.56% | 31.8203
8639 | 0 | 0 | 0 | 4.4 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.7223 | 29.3037 | 0 | 75.7223 | 667.6031 | 52.34% | 0 | 0 | 39.1014 | 62.56% | 29.3037
8640 | 0 | 0 | 0 | 4.2 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667.6031 | 52.34% | 0 | 25 | 11.4331 | 18.29% | 25
8641 | 0 | 0 | 0 | 3.3 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667.6031 | 52.34% | 0 | 2.4251 | 8.7492 | 14% | 2.4251
8642 | 0 | 0 | 0 | 3.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667.6031 | 52.34% | 0 | 0 | 8.7492 | 14% | 0
8643 | 0 | 0 | 0 | 2.1 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.4071 | 27.8873 | 0 | 72.4071 | 595.1961 | 46.66% | 0 | 0 | 8.7492 | 14% | 27.8873
8644 | 0 | 0 | 0 | 1.9 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.8086 | 30.6769 | 0 | 78.8086 | 516.3874 | 40.48% | 0 | 0 | 8.7492 | 14% | 30.6769
8645 | 0 | 0 | 0 | 2.4 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.462 | 34.4566 | 0 | 87.462 | 428.9255 | 33.63% | 0 | 0 | 8.7492 | 14% | 34.4566
8646 | 0 | 0 | 0 | 2.2 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.8416 | 37.6765 | 0 | 94.8416 | 334.0839 | 26.19% | 0 | 0 | 8.7492 | 14% | 37.6765
8647 | 0 | 0 | 0 | 3.2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.672 | 40.6513 | 0 | 101.672 | 232.4119 | 18.22% | 0 | 0 | 8.7492 | 14% | 40.6513
8648 | 24 | 12 | 10 | 2.4 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7276 | 41.9953 | 0 | 104.7276 | 127.6844 | 10.01% | 0 | 0 | 8.7492 | 14% | 41.9953
8649 | 231 | 100 | 53 | 2.6 | 11 | 0 | 0 | 0 | 0 | 12.8973 | 0 | 0 | 12.8973 | 0 | 0 | 0 | 75.3804 | 29.1774 | 0 | 75.3804 | 52.3039 | 4.101% | 0 | 0 | 8.7492 | 14% | 42.0747
8650 | 629 | 286 | 76 | 3.2 | 13.7 | 0 | 0 | 0 | 121.5439 | 39.2957 | 0 | 0 | 39.2957 | 0 | 0 | 0 | 0 | 0 | 121.5439 | 0 | 173.8478 | 13.63% | 0 | 2.2582 | 6.25 | 10% | 41.5538
8651 | 759 | 415 | 86 | 3.6 | 15.2 | 0 | 0 | 0 | 176.0693 | 41.6095 | 13.6316 | 0 | 41.6095 | 0 | 0 | 0 | 0 | 0 | 176.0693 | 0 | 349.9171 | 27.43% | 0 | 0 | 6.25 | 10% | 41.6095
8652 | 810 | 493 | 93 | 4 | 16 | 0 | 0 | 0 | 203.3936 | 40.4034 | 23.7686 | 0 | 40.4034 | 0 | 0 | 0 | 0 | 0 | 203.3936 | 0 | 553.3106 | 43.38% | 0 | 0 | 6.25 | 10% | 40.4034
8653 | 832 | 509 | 91 | 4.1 | 17.4 | 0 | 0 | 0 | 213.7308 | 53.5788 | 13.9314 | 14.6377 | 38.9411 | 0 | 0 | 0 | 0 | 0 | 213.7308 | 0 | 767.0415 | 60.14% | 14.6377 | 0 | 19.476 | 31.16% | 38.9411
8654 | 795 | 454 | 88 | 4.2 | 18.3 | 0 | 0 | 0 | 201.3448 | 63.3339 | 0.28291 | 25 | 38.3339 | 0 | 0 | 0 | 0 | 0 | 201.3448 | 0 | 968.3863 | 75.92% | 25 | 0 | 42.065 | 67.3% | 38.3339
8655 | 715 | 353 | 86 | 4.6 | 18.7 | 0 | 0 | 0 | 170.7474 | 54.6206 | 0 | 15.699 | 38.9216 | 0 | 0 | 0 | 0 | 0 | 170.7474 | 0 | 1139.1337 | 89.31% | 15.699 | 0 | 56.25 | 90% | 38.9216
8656 | 474 | 196 | 76 | 4.6 | 17.7 | 0 | 0 | 0 | 91.965 | 34.033 | 0 | 0 | 34.033 | 0 | 0 | 0 | 0 | 0 | 91.965 | 0 | 1231.0988 | 96.52% | 0 | 7.3662 | 48.0975 | 76.96% | 41.3992
8657 | 74 | 41 | 31 | 3.5 | 15.4 | 0 | 0 | 0 | 0 | 5.4995 | 0 | 0 | 5.4995 | 0 | 0 | 0 | 92.5941 | 36.5445 | 0 | 92.5941 | 1138.5047 | 89.26% | 0 | 0 | 48.0975 | 76.96% | 42.044
8658 | 0 | 0 | 0 | 3 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.471 | 42.232 | 0 | 105.471 | 1033.0337 | 80.99% | 0 | 0 | 48.0975 | 76.96% | 42.232
8659 | 0 | 0 | 0 | 2.5 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1623 | 41.6791 | 0 | 104.1623 | 928.8714 | 72.82% | 0 | 0 | 48.0975 | 76.96% | 41.6791
8660 | 0 | 0 | 0 | 3 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.6703 | 39.2907 | 0 | 98.6703 | 830.201 | 65.09% | 0 | 0 | 48.0975 | 76.96% | 39.2907
8661 | 0 | 0 | 0 | 3.2 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3244 | 36.0889 | 0 | 91.3244 | 738.8766 | 57.93% | 0 | 0 | 48.0975 | 76.96% | 36.0889
8662 | 0 | 0 | 0 | 2.4 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.059 | 33.3843 | 0 | 85.059 | 653.8176 | 51.26% | 0 | 0 | 48.0975 | 76.96% | 33.3843
8663 | 0 | 0 | 0 | 2.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.7464 | 30.656 | 0 | 78.7464 | 575.0712 | 45.09% | 0 | 0 | 48.0975 | 76.96% | 30.656
8664 | 0 | 0 | 0 | 1.3 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.8018 | 28.9499 | 0 | 74.8018 | 500.2694 | 39.22% | 0 | 0 | 48.0975 | 76.96% | 28.9499
8665 | 0 | 0 | 0 | 2.3 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.5374 | 27.9569 | 0 | 72.5374 | 427.7319 | 33.53% | 0 | 0 | 48.0975 | 76.96% | 27.9569
8666 | 0 | 0 | 0 | 2.2 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427.7319 | 33.53% | 0 | 21.0367 | 24.8155 | 39.7% | 21.0367
8667 | 0 | 0 | 0 | 3.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427.7319 | 33.53% | 0 | 0 | 24.8155 | 39.7% | 0
8668 | 0 | 0 | 0 | 2.1 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6404 | 28.8831 | 0 | 74.6404 | 353.0915 | 27.68% | 0 | 0 | 24.8155 | 39.7% | 28.8831
8669 | 0 | 0 | 0 | 1.7 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.1237 | 30.8384 | 0 | 79.1237 | 273.9678 | 21.48% | 0 | 0 | 24.8155 | 39.7% | 30.8384
8670 | 0 | 0 | 0 | 1.8 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.5373 | 33.2102 | 0 | 84.5373 | 189.4305 | 14.85% | 0 | 0 | 24.8155 | 39.7% | 33.2102
8671 | 0 | 0 | 0 | 2.1 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8252 | 36.3869 | 0 | 91.8252 | 97.6053 | 7.652% | 0 | 0 | 24.8155 | 39.7% | 36.3869
8672 | 138 | 20 | 10 | 2.2 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6053 | 38.9077 | 0 | 97.6053 | 0 | 0% | 0 | 0 | 24.8155 | 39.7% | 38.9077
8673 | 626 | 157 | 36 | 2.2 | 10.8 | 0 | 0 | 0 | 83.4294 | 22.5351 | 0 | 0 | 22.5351 | 0 | 0 | 0 | 0 | 0 | 83.4294 | 0 | 83.4294 | 6.541% | 0 | 16.7751 | 6.25 | 10% | 39.3102
8674 | 801 | 315 | 50 | 1.9 | 13.5 | 0 | 0 | 0 | 160.3327 | 38.8687 | 5.4225 | 0 | 38.8687 | 0 | 0 | 0 | 0 | 0 | 160.3327 | 0 | 243.762 | 19.11% | 0 | 0 | 6.25 | 10% | 38.8687
8675 | 888 | 440 | 56 | 3.1 | 15.3 | 0 | 0 | 0 | 209.3629 | 38.8631 | 19.7911 | 0 | 38.8631 | 0 | 0 | 0 | 0 | 0 | 209.3629 | 0 | 453.125 | 35.52% | 0 | 0 | 6.25 | 10% | 38.8631
8676 | 923 | 512 | 58 | 3.1 | 16.3 | 0 | 0 | 0 | 86.5212 | 38.1626 | 28.6232 | 0 | 38.1626 | 0 | 0 | 0 | 0 | 0 | 86.5212 | 0 | 539.6461 | 42.31% | 0 | 0 | 6.25 | 10% | 38.1626
8677 | 935 | 526 | 57 | 1.4 | 17.4 | 0 | 0 | 0 | 244.528 | 43.5318 | 24.0314 | 6.9248 | 36.607 | 0 | 0 | 0 | 0 | 0 | 244.528 | 0 | 784.1741 | 61.48% | 6.9248 | 0 | 12.507 | 20.01% | 36.607
8678 | 914 | 475 | 55 | 1 | 18.9 | 0 | 0 | 0 | 236.4622 | 60.7128 | 3.3115 | 25 | 35.7128 | 0 | 0 | 0 | 0 | 0 | 236.4622 | 0 | 1020.6363 | 80.02% | 25 | 0 | 35.096 | 56.15% | 35.7128
8679 | 857 | 369 | 50 | 0.9 | 19.8 | 0 | 0 | 0 | 211.1313 | 55.8493 | 0 | 19.8593 | 35.99 | 0 | 0 | 0 | 0 | 0 | 211.1313 | 0 | 1231.7675 | 96.57% | 19.8593 | 0 | 53.0401 | 84.86% | 35.99
8680 | 709 | 216 | 42 | 4.1 | 17.4 | 0 | 0 | 0 | 0 | 42.3516 | 0 | 3.5525 | 38.7991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.7675 | 96.57% | 3.5525 | 0 | 56.25 | 90% | 38.7991
8681 | 313 | 56 | 20 | 5 | 13.2 | 0 | 0 | 0 | 0 | 14.8511 | 0 | 0 | 14.8511 | 0 | 0 | 0 | 66.2347 | 25.1513 | 0 | 66.2347 | 1165.5329 | 91.38% | 0 | 0 | 56.25 | 90% | 40.0023
8682 | 0 | 0 | 0 | 4.1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.7231 | 15.8199 | 0 | 44.7231 | 1120.8097 | 87.87% | 0 | 25 | 28.5817 | 45.73% | 40.8199
8683 | 0 | 0 | 0 | 4.1 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5555 | 35.8219 | 0 | 90.5555 | 1030.2543 | 80.77% | 0 | 4.8197 | 23.2476 | 37.2% | 40.6416
8684 | 0 | 0 | 0 | 3.4 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.4548 | 38.838 | 0 | 97.4548 | 932.7994 | 73.13% | 0 | 0 | 23.2476 | 37.2% | 38.838
8685 | 0 | 0 | 0 | 3.1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8331 | 35.9454 | 0 | 90.8331 | 841.9664 | 66.01% | 0 | 0 | 23.2476 | 37.2% | 35.9454
8686 | 0 | 0 | 0 | 2.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9104 | 32.9261 | 0 | 83.9104 | 758.0559 | 59.43% | 0 | 0 | 23.2476 | 37.2% | 32.9261
8687 | 0 | 0 | 0 | 3.5 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.8182 | 30.2688 | 0 | 77.8182 | 680.2377 | 53.33% | 0 | 0 | 23.2476 | 37.2% | 30.2688
8688 | 0 | 0 | 0 | 2.1 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.6417 | 28.4555 | 0 | 73.6417 | 606.596 | 47.56% | 0 | 0 | 23.2476 | 37.2% | 28.4555
8689 | 0 | 0 | 0 | 2 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.9249 | 27.2703 | 0 | 70.9249 | 535.6711 | 42% | 0 | 0 | 23.2476 | 37.2% | 27.2703
8690 | 0 | 0 | 0 | 1.7 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.8857 | 26.8163 | 0 | 69.8857 | 465.7854 | 36.52% | 0 | 0 | 23.2476 | 37.2% | 26.8163
8691 | 0 | 0 | 0 | 1.8 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2645 | 26.982 | 0 | 70.2645 | 395.5209 | 31.01% | 0 | 0 | 23.2476 | 37.2% | 26.982
8692 | 0 | 0 | 0 | 1.9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.77 | 27.638 | 0 | 71.77 | 323.7509 | 25.38% | 0 | 0 | 23.2476 | 37.2% | 27.638
8693 | 0 | 0 | 0 | 2 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.4902 | 28.8246 | 0 | 74.4902 | 249.2608 | 19.54% | 0 | 0 | 23.2476 | 37.2% | 28.8246
8694 | 0 | 0 | 0 | 2.2 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3385 | 30.0669 | 0 | 77.3385 | 171.9223 | 13.48% | 0 | 0 | 23.2476 | 37.2% | 30.0669
8695 | 0 | 0 | 0 | 2.6 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.827 | 32.4623 | 0 | 82.827 | 89.0953 | 6.985% | 0 | 0 | 23.2476 | 37.2% | 32.4623
8696 | 32 | 14 | 11 | 1.9 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.0953 | 35.1962 | 0 | 89.0953 | 0 | 0% | 0 | 0 | 23.2476 | 37.2% | 35.1962
8697 | 537 | 152 | 46 | 2.1 | 7.5 | 0 | 0 | 0 | 0 | 20.8795 | 0 | 0 | 20.8795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 15.3583 | 6.25 | 10% | 36.2379
8698 | 762 | 317 | 64 | 2 | 10.7 | 0 | 0 | 0 | 151.435 | 36.1042 | 7.8718 | 0 | 36.1042 | 0 | 0 | 0 | 0 | 0 | 151.435 | 0 | 151.435 | 11.87% | 0 | 0 | 6.25 | 10% | 36.1042
8699 | 821 | 466 | 109 | 3.1 | 12.6 | 0 | 0 | 0 | 101.1293 | 36.5331 | 24.2018 | 0 | 36.5331 | 0 | 0 | 0 | 0 | 0 | 101.1293 | 0 | 252.5643 | 19.8% | 0 | 0 | 6.25 | 10% | 36.5331
8700 | 755 | 479 | 104 | 3.4 | 13 | 0 | 0 | 0 | 188.8739 | 36.3228 | 26.0097 | 0 | 36.3228 | 0 | 0 | 0 | 0 | 0 | 188.8739 | 0 | 441.4382 | 34.61% | 0 | 0 | 6.25 | 10% | 36.3228
8701 | 873 | 521 | 82 | 3.1 | 13.3 | 0 | 0 | 0 | 226.1391 | 35.6345 | 33.9874 | 0.90352 | 34.731 | 0 | 0 | 0 | 0 | 0 | 226.1391 | 0 | 667.5773 | 52.34% | 0.90352 | 0 | 7.0664 | 11.31% | 34.731
8702 | 890 | 475 | 64 | 2.7 | 14.1 | 0 | 0 | 0 | 228.95 | 58.8508 | 7.969 | 25 | 33.8508 | 0 | 0 | 0 | 0 | 0 | 228.95 | 0 | 896.5274 | 70.29% | 25 | 0 | 29.6554 | 47.45% | 33.8508
8703 | 816 | 366 | 61 | 4.2 | 14.4 | 0 | 0 | 0 | 198.497 | 58.3106 | 0 | 24.0016 | 34.309 | 0 | 0 | 0 | 0 | 0 | 198.497 | 0 | 1095.0243 | 85.85% | 24.0016 | 0 | 51.3423 | 82.15% | 34.309
8704 | 684 | 217 | 48 | 4.2 | 13.8 | 0 | 0 | 0 | 142.3484 | 42.7404 | 0 | 5.4315 | 37.3089 | 0 | 0 | 0 | 0 | 0 | 142.3484 | 0 | 1237.3727 | 97.01% | 5.4315 | 0 | 56.25 | 90% | 37.3089
8705 | 305 | 57 | 22 | 3 | 12.3 | 0 | 0 | 0 | 38.1375 | 14.8285 | 0 | 0 | 14.8285 | 0 | 0 | 0 | 0 | 0 | 38.1375 | 0 | 1275.5102 | 100% | 0 | 23.9051 | 29.7934 | 47.67% | 38.7336
8706 | 0 | 0 | 0 | 2.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.8643 | 18.4997 | 0 | 50.8643 | 1224.6459 | 96.01% | 0 | 7.4719 | 21.524 | 34.44% | 25.9716
8707 | 0 | 0 | 0 | 2.1 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6897 | 40.2419 | 0 | 100.6897 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 40.2419
8708 | 0 | 0 | 0 | 1.6 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8709 | 0 | 0 | 0 | 1.7 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8710 | 0 | 0 | 0 | 2.9 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8711 | 0 | 0 | 0 | 2.9 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8712 | 0 | 0 | 0 | 1.4 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8713 | 0 | 0 | 0 | 1.8 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8714 | 0 | 0 | 0 | 1.6 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8715 | 0 | 0 | 0 | 2.3 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8716 | 0 | 0 | 0 | 2.2 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2737e-13 | 0 | 0 | 2.2737e-13 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8717 | 0 | 0 | 0 | 1 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.9561 | 88.12% | 0 | 0 | 21.524 | 34.44% | 0
8718 | 0 | 0 | 0 | 0.4 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2867 | 38.3395 | 0 | 96.2867 | 1027.6694 | 80.57% | 0 | 0 | 21.524 | 34.44% | 38.3395
8719 | 0 | 0 | 0 | 0.9 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1348 | 41.7655 | 0 | 104.1348 | 923.5346 | 72.41% | 0 | 0 | 21.524 | 34.44% | 41.7655
8720 | 0 | 6 | 6 | 1 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.5755 | 43.2654 | 0 | 107.5755 | 815.9591 | 63.97% | 0 | 0 | 21.524 | 34.44% | 43.2654
8721 | 0 | 47 | 47 | 1 | 8.8 | 0 | 0 | 0 | 0 | 3.5067 | 0 | 0 | 3.5067 | 0 | 0 | 0 | 99.2036 | 39.6 | 0 | 99.2036 | 716.7555 | 56.19% | 0 | 0 | 21.524 | 34.44% | 43.1067
8722 | 7 | 159 | 154 | 1 | 10.1 | 0 | 0 | 0 | 0 | 13.4677 | 0 | 0 | 13.4677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.7555 | 56.19% | 0 | 0 | 21.524 | 34.44% | 13.4677
8723 | 21 | 254 | 241 | 1.4 | 11.6 | 0 | 0 | 0 | 0 | 21.3247 | 0 | 0 | 21.3247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.7555 | 56.19% | 0 | 0 | 21.524 | 34.44% | 21.3247
8724 | 7 | 273 | 266 | 0.8 | 12.4 | 0 | 0 | 0 | 0 | 21.3981 | 0 | 0 | 21.3981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.7555 | 56.19% | 0 | 0 | 21.524 | 34.44% | 21.3981
8725 | 116 | 336 | 273 | 1.6 | 12.7 | 0 | 0 | 0 | 0 | 31.381 | 0 | 0 | 31.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.7555 | 56.19% | 0 | 0 | 21.524 | 34.44% | 31.381
8726 | 749 | 545 | 197 | 1.8 | 13.6 | 0 | 0 | 0 | 190.5385 | 64.5121 | 3.8676 | 25 | 39.5121 | 0 | 0 | 0 | 0 | 0 | 190.5385 | 0 | 907.294 | 71.13% | 25 | 0 | 44.113 | 70.58% | 39.5121
8727 | 611 | 393 | 159 | 1.5 | 14.1 | 0 | 0 | 0 | 145.8564 | 53.3526 | 0 | 13.4324 | 39.9202 | 0 | 0 | 0 | 0 | 0 | 145.8564 | 0 | 1053.1504 | 82.57% | 13.4324 | 0 | 56.25 | 90% | 39.9202
8728 | 546 | 222 | 82 | 1.4 | 13.9 | 0 | 0 | 0 | 111.7628 | 38.1133 | 0 | 0 | 38.1133 | 0 | 0 | 0 | 0 | 0 | 111.7628 | 0 | 1164.9131 | 91.33% | 0 | 4.3527 | 51.4328 | 82.29% | 42.466
8729 | 226 | 52 | 27 | 0.4 | 13 | 0 | 0 | 0 | 0 | 12.2977 | 0 | 0 | 12.2977 | 0 | 0 | 0 | 79.6186 | 30.9817 | 0 | 79.6186 | 1085.2945 | 85.09% | 0 | 0 | 51.4328 | 82.29% | 43.2793
8730 | 0 | 0 | 0 | 1.3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.3968 | 43.5816 | 0 | 108.3968 | 976.8978 | 76.59% | 0 | 0 | 51.4328 | 82.29% | 43.5816
8731 | 0 | 0 | 0 | 1.1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.6706 | 43.2807 | 0 | 107.6706 | 869.2272 | 68.15% | 0 | 0 | 51.4328 | 82.29% | 43.2807
8732 | 0 | 0 | 0 | 1.5 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.8884 | 40.7809 | 0 | 101.8884 | 767.3389 | 60.16% | 0 | 0 | 51.4328 | 82.29% | 40.7809
8733 | 0 | 0 | 0 | 1.4 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.3389 | 60.16% | 0 | 15.755 | 33.9962 | 54.39% | 15.755
8734 | 0 | 0 | 0 | 2.2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.3389 | 60.16% | 0 | 0 | 33.9962 | 54.39% | 0
8735 | 0 | 0 | 0 | 2.9 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.3389 | 60.16% | 0 | 0 | 33.9962 | 54.39% | 0
8736 | 0 | 0 | 0 | 2.7 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.3389 | 60.16% | 0 | 0 | 33.9962 | 54.39% | 0
8737 | 0 | 0 | 0 | 1.7 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.3389 | 60.16% | 0 | 0 | 33.9962 | 54.39% | 0
8738 | 0 | 0 | 0 | 2.4 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.3389 | 60.16% | 0 | 0 | 33.9962 | 54.39% | 0
8739 | 0 | 0 | 0 | 1.9 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1369e-13 | 0 | 0 | 1.1369e-13 | 767.3389 | 60.16% | 0 | 0 | 33.9962 | 54.39% | 0
8740 | 0 | 0 | 0 | 1.2 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.3389 | 60.16% | 0 | 0 | 33.9962 | 54.39% | 0
8741 | 0 | 0 | 0 | 1.8 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.3389 | 60.16% | 0 | 0 | 33.9962 | 54.39% | 0
8742 | 0 | 0 | 0 | 2.2 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767.3389 | 60.16% | 0 | 0 | 33.9962 | 54.39% | 0
8743 | 0 | 0 | 0 | 2.1 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.8203 | 39.4453 | 0 | 98.8203 | 668.5185 | 52.41% | 0 | 0 | 33.9962 | 54.39% | 39.4453
8744 | 1 | 9 | 9 | 1.4 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.7417 | 41.5844 | 0 | 103.7417 | 564.7769 | 44.28% | 0 | 0 | 33.9962 | 54.39% | 41.5844
8745 | 13 | 90 | 86 | 0.8 | 6.5 | 0 | 0 | 0 | 0 | 10.6355 | 0 | 0 | 10.6355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564.7769 | 44.28% | 0 | 0 | 33.9962 | 54.39% | 10.6355
8746 | 14 | 163 | 158 | 1.1 | 8.2 | 0 | 0 | 0 | 0 | 14.3957 | 0 | 0 | 14.3957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564.7769 | 44.28% | 0 | 0 | 33.9962 | 54.39% | 14.3957
8747 | 12 | 238 | 230 | 0.7 | 10.5 | 0 | 0 | 0 | 0 | 19.5404 | 0 | 0 | 19.5404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564.7769 | 44.28% | 0 | 0 | 33.9962 | 54.39% | 19.5404
8748 | 23 | 282 | 267 | 1.2 | 12.2 | 0 | 0 | 0 | 0 | 22.6624 | 0 | 0 | 22.6624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564.7769 | 44.28% | 0 | 0 | 33.9962 | 54.39% | 22.6624
8749 | 589 | 483 | 183 | 1.4 | 12.9 | 0 | 0 | 0 | 147.7614 | 58.0769 | 0 | 20.3321 | 37.7448 | 0 | 0 | 0 | 0 | 0 | 147.7614 | 0 | 712.5382 | 55.86% | 20.3321 | 0 | 52.3675 | 83.79% | 37.7448
8750 | 366 | 334 | 159 | 1.7 | 13.2 | 0 | 0 | 0 | 84.0831 | 41.3342 | 0 | 4.2969 | 37.0373 | 0 | 0 | 0 | 0 | 0 | 84.0831 | 0 | 796.6213 | 62.46% | 4.2969 | 0 | 56.25 | 90% | 37.0373
8751 | 132 | 165 | 117 | 1.3 | 12.9 | 0 | 0 | 0 | 0 | 18.0956 | 0 | 0 | 18.0956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 796.6213 | 62.46% | 0 | 16.2974 | 38.2132 | 61.14% | 34.393
8752 | 471 | 207 | 83 | 1.6 | 13.5 | 0 | 0 | 0 | 94.1413 | 34.5449 | 0 | 0 | 34.5449 | 0 | 0 | 0 | 0 | 0 | 94.1413 | 0 | 890.7626 | 69.84% | 0 | 6.2916 | 31.25 | 50% | 40.8366
8753 | 248 | 56 | 27 | 2 | 11.8 | 0 | 0 | 0 | 0 | 13.3602 | 0 | 0 | 13.3602 | 0 | 0 | 0 | 74.2873 | 28.6866 | 0 | 74.2873 | 816.4753 | 64.01% | 0 | 0 | 31.25 | 50% | 42.0468
8754 | 0 | 0 | 0 | 1.3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.1949 | 40.8923 | 0 | 102.1949 | 714.2804 | 56% | 0 | 0 | 31.25 | 50% | 40.8923
8755 | 0 | 0 | 0 | 0.8 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.2804 | 56% | 0 | 0 | 31.25 | 50% | 0
8756 | 0 | 0 | 0 | 1.2 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.2804 | 56% | 0 | 0 | 31.25 | 50% | 0
8757 | 0 | 0 | 0 | 0.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.2804 | 56% | 0 | 0 | 31.25 | 50% | 0
8758 | 0 | 0 | 0 | 0.8 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.2804 | 56% | 0 | 0 | 31.25 | 50% | 0
8759 | 0 | 0 | 0 | 0.6 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 714.2804 | 56% | 0 | 0 | 31.25 | 50% | 0

## 2.3 - Output Operation - YACOP
Hours | DNI | GHI | DHI | Wspd | T_amb | Q_out_SF | P_intercept_defocus_SF | PV_AC_out | PV_AC_curtail | Q_in_PB | P_net_PB | TES_ch | TES_disch | TES_SOC | BESS_ch | BESS_disch | BESS_SOC | Q_out_heater | P_injected_to_grid | Legend
h | W/m2 | W/m2 | W/m2 | m/s | C | MW | MW | MW | MW | MW | MW | MW | MW | % | MW | MW | % | MW | MW | Symbol | Description | Unit
0 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 42.6363 | 0 | 0 | 38.2928 | 47% | 0 | 25 | 10% | 0 | 23.4043 | DNI | Direct Normal Irradiance | W/m2
1 | 0 | 0 | 0 | 0.5 | 5.4 | 0 | 0 | 0 | 0 | 54.0101 | 10.5837 | 0 | 49.3825 | 43% | 0 | 0 | 10% | 0 | 8.9713 | GHI | Global Horizontal Irradiance | W/m2
2 | 0 | 0 | 0 | 0.9 | 5.2 | 0 | 0 | 0 | 0 | 72.159 | 28.5554 | 0 | 66.8674 | 38% | 0 | 0 | 10% | 0 | 27.1253 | DHI | Diffuse Horizontal Irradiance | W/m2
3 | 0 | 0 | 0 | 0.7 | 5.1 | 0 | 0 | 0 | 0 | 71.6435 | 28.3297 | 0 | 66.7591 | 33% | 0 | 0 | 10% | 0 | 26.7477 | Wspd | Wind Speed | m/s
4 | 0 | 0 | 0 | 1.2 | 5.3 | 0 | 0 | 0 | 0 | 72.5096 | 28.7103 | 0 | 67.9181 | 28% | 0 | 0 | 10% | 0 | 27.001 | T_amb | Ambient Temperature | C
5 | 0 | 0 | 0 | 1.8 | 5.6 | 0 | 0 | 0 | 0 | 74.1902 | 29.4534 | 0 | 69.8299 | 22% | 0 | 0 | 10% | 0 | 27.6347 | Q_out_SF | Power Output Solar Field | MW
6 | 0 | 0 | 0 | 1.5 | 5.4 | 0 | 0 | 0 | 0 | 74.1676 | 29.4493 | 0 | 70.0474 | 17% | 0 | 0 | 10% | 0 | 27.5381 | P_intercept_defocus_SF | Intercept power defocussed | MW
7 | 0 | 0 | 0 | 0.8 | 5 | 0 | 0 | 0 | 0 | 76.3914 | 30.4582 | 0 | 72.4392 | 11% | 0 | 0 | 10% | 0 | 28.4644 | PV_AC_out | PV AC power output | MW
8 | 154 | 18 | 8 | 0.7 | 4.6 | 0 | 4.1224 | 0 | 0 | 81.5385 | 32.8055 | 0 | 77.7177 | 6% | 0 | 0 | 10% | 0 | 30.734 | PV_AC_curtail | PV AC power curtailed | MW
9 | 699 | 158 | 31 | 0.3 | 9.5 | 95.2307 | 24.2999 | 26.2718 | 0 | 42.7335 | 15.6736 | 60.0661 | 7.7002 | 9% | 7.837 | 0 | 20.66% | 0 | 32.5227 | Q_in_PB | Thermal Power to the PB | MW
10 | 873 | 324 | 42 | 0.2 | 14.6 | 193.1074 | 0 | 44.9376 | 4.2707 | 42.5447 | 15.3991 | 151.2416 | 0 | 21% | 25 | 0 | 54.66% | 0 | 33.1738 | P_net_PB | PB Net electric power output | MW
11 | 945 | 454 | 47 | 0.8 | 16.7 | 237.8643 | 0 | 46.094 | 19.1863 | 42.5821 | 15.3117 | 196.4602 | 0 | 36% | 25 | 0 | 88.66% | 0 | 33.8209 | TES_ch | Heat flow into TES | MW
12 | 974 | 529 | 49 | 2.5 | 17.5 | 254.1037 | 0 | 22.1469 | 51.9453 | 42.5969 | 15.2743 | 212.9046 | 0 | 52% | 0.98649 | 0 | 90% | 0 | 33.6749 | TES_disch | Heat flow out of TES | MW
13 | 979 | 543 | 49 | 3.2 | 18.5 | 256.893 | 0 | 19.5862 | 55.5138 | 42.6027 | 15.2199 | 215.5705 | 0 | 68% | 0 | 0 | 90% | 0 | 31.9964 | TES_SOC | State of charge TES
14 | 959 | 494 | 48 | 3.1 | 19.2 | 245.4054 | 0 | 18.8378 | 50.5411 | 42.6055 | 15.1794 | 203.9619 | 0 | 83% | 0 | 0 | 90% | 0 | 31.2931 | BESS_ch | Electric power into BESS | MW
15 | 907 | 387 | 44 | 4 | 18.9 | 212.3408 | 0 | 17.9695 | 38.1622 | 42.6065 | 15.1979 | 170.6928 | 0 | 96% | 0 | 0 | 90% | 0 | 31.8841 | BESS_disch | Electric power drawn from BESS | MW
16 | 788 | 235 | 36 | 3.8 | 18.3 | 102.8042 | 60.8675 | 19.5668 | 16.309 | 42.6061 | 15.2328 | 61.0764 | 0 | 100% | 0 | 0 | 90% | 0 | 35.6781 | BESS_SOC | BESS state of charge
17 | 440 | 68 | 18 | 3 | 16.1 | 0 | 60.7757 | 9.1179 | 0 | 42.6038 | 15.3501 | 0 | 41.1126 | 97% | 0 | 15.2756 | 65.56% | 0 | 37.679 | Q_out_heater | Electric Heater Output Power | MW
18 | 1 | 0 | 0 | 1.3 | 12.1 | 0 | 0 | 0 | 0 | 46.2548 | 17.0397 | 0 | 44.6211 | 94% | 0 | 25 | 25.56% | 0 | 39.1228 | P_to_grid | Gross power at grid connection | MW
19 | 0 | 0 | 0 | 0.2 | 9.7 | 0 | 0 | 0 | 0 | 82.5129 | 32.857 | 0 | 84.1897 | 88% | 0 | 9.7244 | 10% | 0 | 39.6647
20 | 0 | 0 | 0 | 0.7 | 7.7 | 0 | 0 | 0 | 0 | 101.146 | 41.0667 | 0 | 102.5383 | 80% | 0 | 0 | 10% | 0 | 38.5235
21 | 0 | 0 | 0 | 1.1 | 7.6 | 0 | 0 | 0 | 0 | 93.9086 | 38.0214 | 0 | 93.1234 | 73% | 0 | 0 | 10% | 0 | 35.6988
22 | 0 | 0 | 0 | 1.4 | 7.3 | 0 | 0 | 0 | 0 | 85.907 | 34.6295 | 0 | 83.3369 | 67% | 0 | 0 | 10% | 0 | 32.3331
23 | 0 | 0 | 0 | 1.7 | 7.3 | 0 | 0 | 0 | 0 | 80.2145 | 32.1267 | 0 | 77.3668 | 61% | 0 | 0 | 10% | 0 | 29.7569
24 | 0 | 0 | 0 | 2.1 | 7.4 | 0 | 0 | 0 | 0 | 76.7303 | 30.5454 | 0 | 74.0838 | 55% | 0 | 0 | 10% | 0 | 28.1013
25 | 0 | 0 | 0 | 1.2 | 6.6 | 0 | 0 | 0 | 0 | 75.3105 | 29.9311 | 0 | 72.8114 | 50% | 0 | 0 | 10% | 0 | 27.4304
26 | 0 | 0 | 0 | 1.1 | 6.1 | 0 | 0 | 0 | 0 | 75.0216 | 29.8159 | 0 | 72.6365 | 45% | 0 | 0 | 10% | 0 | 27.2703
27 | 0 | 0 | 0 | 2.4 | 7.1 | 0 | 0 | 0 | 0 | 77.9094 | 31.0891 | 0 | 75.6353 | 39% | 0 | 0 | 10% | 0 | 28.5042
28 | 0 | 0 | 0 | 2.2 | 7.3 | 0 | 0 | 0 | 0 | 86.76 | 34.9919 | 0 | 85.3376 | 33% | 0 | 0 | 10% | 0 | 32.3663
29 | 0 | 0 | 0 | 1.8 | 6.9 | 0 | 0 | 0 | 0 | 99.3974 | 40.3574 | 0 | 100.6962 | 25% | 0 | 0 | 10% | 0 | 37.7085
30 | 0 | 0 | 0 | 2.9 | 6.7 | 0 | 0 | 0 | 0 | 110.3394 | 44.9649 | 0 | 113.6277 | 17% | 0 | 0 | 10% | 0 | 42.3603
31 | 0 | 0 | 0 | 2.5 | 6.9 | 0 | 0 | 0 | 0 | 119.1701 | 48.6497 | 0 | 123.8105 | 7% | 0 | 0 | 10% | 0 | 46.1269
32 | 154 | 18 | 8 | 2.9 | 7.7 | 0 | 4.0192 | 0 | 0 | 94.1472 | 38.4441 | 0 | 98.0443 | 0% | 0 | 0 | 10% | 0 | 36.0879
33 | 705 | 159 | 31 | 0.8 | 10.9 | 96.0399 | 24.359 | 26.3485 | 0 | 0 | 0 | 92.7631 | 0 | 7% | 0 | 0 | 10% | 0 | 24.7817
34 | 879 | 327 | 42 | 1 | 14.6 | 194.1625 | 0 | 49.5265 | 0 | 0 | 0 | 191.885 | 0 | 21% | 0 | 0 | 10% | 0 | 47.3972
35 | 952 | 458 | 48 | 0.9 | 17.2 | 239.7725 | 0 | 65.7988 | 0 | 0 | 0 | 238.1607 | 0 | 39% | 16.8201 | 0 | 32.88% | 0 | 46.404
36 | 980 | 534 | 51 | 1.4 | 18.4 | 256.4382 | 0 | 74.2744 | 0.3547 | 0 | 0 | 255.1189 | 0 | 59% | 25 | 0 | 66.88% | 0 | 46.5003
37 | 976 | 546 | 53 | 2.6 | 18.2 | 256.4934 | 0 | 64.9638 | 10.1362 | 0 | 0 | 255.3217 | 0 | 78% | 17.0035 | 0 | 90% | 0 | 45.1246
38 | 947 | 495 | 53 | 2.5 | 18.6 | 242.4902 | 0 | 47.0867 | 22.2057 | 0 | 0 | 241.4073 | 0 | 96% | 0 | 0 | 90% | 0 | 44.3467
39 | 854 | 377 | 50 | 2.6 | 18.6 | 93.7887 | 123.9256 | 43.879 | 9.5385 | 42.6 | 2.3723 | 52.8167 | 0 | 100% | 0 | 0 | 90% | 0 | 44.7075
40 | 729 | 229 | 44 | 2.4 | 17.6 | 42.1585 | 120.1637 | 31.632 | 2.2831 | 42.5986 | 15.2694 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 47.6136
41 | 376 | 67 | 23 | 1.7 | 15.7 | 0 | 50.3 | 7.8585 | 0 | 47.9987 | 17.6231 | 0 | 46.4697 | 97% | 0 | 25 | 50% | 0 | 48.4133
42 | 1 | 1 | 0 | 2.6 | 11.6 | 0 | 0 | 0 | 0 | 69.1376 | 26.9926 | 0 | 67.7913 | 92% | 0 | 25 | 10% | 0 | 49.0497
43 | 0 | 0 | 0 | 2.1 | 9.6 | 0 | 0 | 0 | 0 | 126.2492 | 51.484 | 0 | 134.71 | 82% | 0 | 0 | 10% | 0 | 48.5581
44 | 0 | 0 | 0 | 2.5 | 9.5 | 0 | 0 | 0 | 0 | 117.0342 | 47.6574 | 0 | 119.3984 | 73% | 0 | 0 | 10% | 0 | 45.6047
45 | 0 | 0 | 0 | 3 | 9.2 | 0 | 0 | 0 | 0 | 106.4984 | 43.2672 | 0 | 106.1561 | 65% | 0 | 0 | 10% | 0 | 41.4163
46 | 0 | 0 | 0 | 3 | 8.6 | 0 | 0 | 0 | 0 | 97.7039 | 39.5832 | 0 | 95.7448 | 57% | 0 | 0 | 10% | 0 | 37.7514
47 | 0 | 0 | 0 | 3 | 7.5 | 0 | 0 | 0 | 0 | 89.7347 | 36.2463 | 0 | 86.5065 | 51% | 0 | 0 | 10% | 0 | 34.364
48 | 0 | 0 | 0 | 2.7 | 6.9 | 0 | 0 | 0 | 0 | 85.9504 | 34.661 | 0 | 82.3421 | 44% | 0 | 0 | 10% | 0 | 32.6865
49 | 0 | 0 | 0 | 3.1 | 6.8 | 0 | 0 | 0 | 0 | 84.057 | 33.8644 | 0 | 80.4286 | 38% | 0 | 0 | 10% | 0 | 31.7958
50 | 0 | 0 | 0 | 2.6 | 5.2 | 0 | 0 | 0 | 0 | 83.8167 | 33.8049 | 0 | 80.403 | 32% | 0 | 0 | 10% | 0 | 31.6509
51 | 0 | 0 | 0 | 2.4 | 5.6 | 0 | 0 | 0 | 0 | 86.0618 | 34.7442 | 0 | 83.242 | 26% | 0 | 0 | 10% | 0 | 32.5161
52 | 0 | 0 | 0 | 2.9 | 5.6 | 0 | 0 | 0 | 0 | 93.8806 | 38.072 | 0 | 92.8733 | 19% | 0 | 0 | 10% | 0 | 35.782
53 | 0 | 0 | 0 | 2.8 | 5.3 | 0 | 0 | 0 | 0 | 105.899 | 43.1502 | 0 | 107.1814 | 11% | 0 | 0 | 10% | 0 | 40.8362
54 | 0 | 0 | 0 | 2.8 | 5.2 | 0 | 0 | 0 | 0 | 117.0298 | 47.8118 | 0 | 120.2006 | 2% | 0 | 0 | 10% | 0 | 45.5205
55 | 0 | 0 | 0 | 2.5 | 4.9 | 0 | 0 | 0 | 0 | 23.0549 | 9.4325 | 0 | 23.8573 | 0% | 0 | 0 | 10% | 0 | 7.3635
56 | 8 | 9 | 8 | 2.6 | 4.3 | 0 | 0.20479 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0174
57 | 599 | 148 | 38 | 1.4 | 7.1 | 78.8909 | 20.4748 | 22.639 | 0 | 0 | 0 | 75.9494 | 0 | 6% | 0 | 0 | 10% | 0 | 21.2395
58 | 788 | 314 | 58 | 4.1 | 10.3 | 170.2698 | 2.98e-14 | 46.3144 | 0 | 0 | 0 | 167.6619 | 0 | 19% | 0 | 0 | 10% | 0 | 44.3913
59 | 835 | 439 | 76 | 5.2 | 11.7 | 205.1301 | 0 | 61.4474 | 0 | 0 | 0 | 203.4137 | 0 | 34% | 10.961 | 0 | 24.91% | 0 | 48.2202
60 | 417 | 400 | 191 | 3.9 | 12.5 | 97.6219 | 0 | 45.2351 | 0 | 0 | 0 | 96.9895 | 0 | 41% | 0 | 3.7339 | 18.93% | 0 | 47.6532
61 | 540 | 454 | 178 | 4.8 | 12.6 | 132.1958 | 0 | 55.324 | 0 | 42.5674 | 3.1023 | 91.0645 | 0 | 48% | 22.5345 | 0 | 49.58% | 0 | 33.8343
62 | 525 | 425 | 172 | 3.7 | 13.1 | 125.7864 | 0 | 50.633 | 0 | 42.5721 | 15.4724 | 84.8685 | 0 | 55% | 18.3877 | 0 | 74.59% | 0 | 46.1154
63 | 464 | 297 | 119 | 2.9 | 12.9 | 100.6541 | 0 | 35.7458 | 0 | 42.5757 | 15.4815 | 59.7586 | 0 | 59% | 3.2036 | 0 | 78.94% | 0 | 46.6539
64 | 514 | 206 | 80 | 2.9 | 12.8 | 95.1058 | 0 | 26.3419 | 0 | 42.5767 | 15.4857 | 53.9079 | 0 | 63% | 0 | 8.5805 | 65.22% | 0 | 49.0928
65 | 140 | 63 | 42 | 4 | 11.6 | 0 | 23.767 | 3.084 | 0 | 61.1405 | 23.4781 | 0 | 58.6257 | 59% | 0 | 25 | 25.21% | 0 | 49.99
66 | 0 | 1 | 0 | 3 | 10 | 0 | 0 | 0 | 0 | 105.8064 | 42.7321 | 0 | 109.3793 | 51% | 0 | 9.5094 | 10% | 0 | 49.6277
67 | 0 | 0 | 0 | 2.5 | 9.9 | 0 | 0 | 0 | 0 | 127.5027 | 51.9926 | 0 | 133.716 | 41% | 0 | 0 | 10% | 0 | 49.5349
68 | 0 | 0 | 0 | 2.7 | 9.7 | 0 | 0 | 0 | 0 | 119.9335 | 48.8529 | 0 | 123.4355 | 31% | 0 | 0 | 10% | 0 | 46.6264
69 | 0 | 0 | 0 | 2.1 | 8.4 | 0 | 0 | 0 | 0 | 109.5921 | 44.5918 | 0 | 110.6173 | 23% | 0 | 0 | 10% | 0 | 42.4943
70 | 0 | 0 | 0 | 2.2 | 7.8 | 0 | 0 | 0 | 0 | 100.2784 | 40.6993 | 0 | 99.4317 | 15% | 0 | 0 | 10% | 0 | 38.6563
71 | 0 | 0 | 0 | 2.2 | 7 | 0 | 0 | 0 | 0 | 92.4993 | 37.4429 | 0 | 90.2738 | 8% | 0 | 0 | 10% | 0 | 35.4073
72 | 0 | 0 | 0 | 1.3 | 6.2 | 0 | 0 | 0 | 0 | 88.314 | 35.6852 | 0 | 85.3363 | 2% | 0 | 0 | 10% | 0 | 33.6238
73 | 0 | 0 | 0 | 1 | 6.1 | 0 | 0 | 0 | 0 | 27.3397 | 11.0374 | 0 | 26.3415 | 0% | 0 | 0 | 10% | 0 | 8.9992
74 | 0 | 0 | 0 | 1.2 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9966
75 | 0 | 0 | 0 | 1.1 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.98
76 | 0 | 0 | 0 | 1.3 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9637
77 | 0 | 0 | 0 | 2.1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9478
78 | 0 | 0 | 0 | 2.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9321
79 | 0 | 0 | 0 | 2.2 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9167
80 | 97 | 16 | 10 | 2.4 | 4.4 | 0 | 2.4513 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9016
81 | 580 | 156 | 47 | 1.6 | 6.5 | 75.8405 | 19.7445 | 22.6966 | 0 | 0 | 0 | 72.1702 | 0 | 6% | 0 | 0 | 10% | 0 | 21.3417
82 | 806 | 330 | 65 | 0.9 | 9 | 176.6206 | 0 | 48.4598 | 0 | 0 | 0 | 172.893 | 0 | 19% | 0 | 0 | 10% | 0 | 46.4745
83 | 898 | 456 | 62 | 1 | 11.5 | 225.1132 | 0 | 64.5927 | 0 | 42.4396 | 0 | 183.4213 | 0 | 33% | 16.8126 | 0 | 32.87% | 0 | 44.7923
84 | 944 | 535 | 61 | 1.4 | 12.5 | 246.6067 | 0 | 61.2908 | 13.0649 | 42.5226 | 13.7704 | 205.4013 | 0 | 48% | 24.8685 | 0 | 66.69% | 0 | 47.4266
85 | 944 | 547 | 61 | 1.8 | 13.3 | 248.3327 | 0 | 50.5052 | 24.5948 | 42.5553 | 15.4581 | 207.1185 | 0 | 64% | 17.1425 | 0 | 90% | 0 | 46.0686
86 | 927 | 501 | 60 | 1.9 | 14 | 237.7314 | 0 | 32.6744 | 37.1189 | 42.5678 | 15.4342 | 196.5046 | 0 | 79% | 0 | 0 | 90% | 0 | 45.4401
87 | 883 | 397 | 53 | 2 | 14.7 | 208.9339 | 0 | 32.8153 | 23.9148 | 42.5768 | 15.4063 | 167.5455 | 0 | 91% | 0 | 0 | 90% | 0 | 45.8166
88 | 761 | 243 | 44 | 2.8 | 14.3 | 150.3914 | 0 | 32.1839 | 4.074 | 42.5815 | 15.4258 | 108.7175 | 0 | 99% | 0 | 0 | 90% | 0 | 48.6899
89 | 407 | 72 | 23 | 2.9 | 12.2 | 0 | 56.2243 | 8.9862 | 0 | 47.6741 | 17.643 | 0 | 46.1515 | 96% | 0 | 25 | 50% | 0 | 49.5631
90 | 0 | 1 | 1 | 2.5 | 9.3 | 0 | 0 | 0 | 0 | 70.4149 | 27.6612 | 0 | 69.1123 | 91% | 0 | 25 | 10% | 0 | 49.7115
91 | 0 | 0 | 0 | 0.2 | 7 | 0 | 0 | 0 | 0 | 127.0154 | 51.9118 | 0 | 135.6523 | 81% | 0 | 0 | 10% | 0 | 48.9822
92 | 0 | 0 | 0 | 0.9 | 5.5 | 0 | 0 | 0 | 0 | 118.4877 | 48.4077 | 0 | 121.181 | 72% | 0 | 0 | 10% | 0 | 46.3366
93 | 0 | 0 | 0 | 1.1 | 5.2 | 0 | 0 | 0 | 0 | 109.8718 | 44.8117 | 0 | 110.073 | 63% | 0 | 0 | 10% | 0 | 42.9553
94 | 0 | 0 | 0 | 2.1 | 4.9 | 0 | 0 | 0 | 0 | 102.1114 | 41.5586 | 0 | 100.8238 | 56% | 0 | 0 | 10% | 0 | 39.7452
95 | 0 | 0 | 0 | 1.6 | 3.9 | 0 | 0 | 0 | 0 | 94.2639 | 38.2724 | 0 | 91.7958 | 49% | 0 | 0 | 10% | 0 | 36.4357
96 | 0 | 0 | 0 | 1.6 | 3.8 | 0 | 0 | 0 | 0 | 88.7511 | 35.925 | 0 | 85.3837 | 42% | 0 | 0 | 10% | 0 | 34.0265
97 | 0 | 0 | 0 | 0.8 | 2.7 | 0 | 0 | 0 | 0 | 86.1357 | 34.8366 | 0 | 82.5756 | 36% | 0 | 0 | 10% | 0 | 32.8533
98 | 0 | 0 | 0 | 0.3 | 1.5 | 0 | 0 | 0 | 0 | 85.26 | 34.4857 | 0 | 81.8047 | 30% | 0 | 0 | 10% | 0 | 32.4198
99 | 0 | 0 | 0 | 0.9 | 2.1 | 0 | 0 | 0 | 0 | 85.0413 | 34.3844 | 0 | 81.7645 | 23% | 0 | 0 | 10% | 0 | 32.2469
100 | 0 | 0 | 0 | 1.8 | 2.2 | 0 | 0 | 0 | 0 | 87.1443 | 35.274 | 0 | 84.4268 | 17% | 0 | 0 | 10% | 0 | 33.0723
101 | 0 | 0 | 0 | 1.4 | 2.2 | 0 | 0 | 0 | 0 | 92.0878 | 37.3789 | 0 | 90.5346 | 10% | 0 | 0 | 10% | 0 | 35.1255
102 | 0 | 0 | 0 | 0.8 | 1.5 | 0 | 0 | 0 | 0 | 97.3458 | 39.6171 | 0 | 96.8551 | 3% | 0 | 0 | 10% | 0 | 37.3385
103 | 0 | 0 | 0 | 1.2 | 1 | 0 | 0 | 0 | 0 | 37.9475 | 15.4955 | 0 | 38.3747 | 0% | 0 | 0 | 10% | 0 | 13.3092
104 | 156 | 18 | 8 | 1.5 | 2 | 0 | 3.9181 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1161
105 | 694 | 159 | 32 | 0.4 | 5.8 | 94.1131 | 24.279 | 26.1828 | 0 | 0 | 0 | 90.5866 | 0 | 7% | 0 | 0 | 10% | 0 | 24.6358
106 | 871 | 329 | 43 | 0.7 | 10.8 | 192.531 | 0 | 49.5686 | 0 | 0 | 0 | 189.9654 | 0 | 21% | 4.3396 | 0 | 15.9% | 0 | 43.1111
107 | 941 | 461 | 48 | 0.7 | 13.6 | 237.1176 | 0 | 65.6704 | 0 | 0 | 0 | 235.3554 | 0 | 39% | 20.8459 | 0 | 44.25% | 0 | 42.27
108 | 968 | 537 | 52 | 1.8 | 13.8 | 253.3381 | 0 | 70.5571 | 4.3855 | 0 | 0 | 251.9206 | 0 | 58% | 25 | 0 | 78.25% | 0 | 42.808
109 | 977 | 553 | 52 | 2 | 14.4 | 257.7134 | 0 | 52.7975 | 22.3025 | 0 | 0 | 256.468 | 0 | 77% | 8.638 | 0 | 90% | 0 | 41.3083
110 | 957 | 505 | 51 | 2.5 | 15.3 | 246.0174 | 0 | 43.0637 | 27.8103 | 0 | 0 | 244.8706 | 0 | 96% | 0 | 0 | 90% | 0 | 40.2862
111 | 910 | 400 | 47 | 3.4 | 15.4 | 95.5016 | 139.2692 | 41.2 | 16.6599 | 42.5936 | 0.55862 | 54.7712 | 0 | 100% | 0 | 0 | 90% | 0 | 40.1614
112 | 798 | 248 | 39 | 2.6 | 15.2 | 42.1584 | 139.1861 | 26.4587 | 11.2052 | 42.5922 | 15.389 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.5605
113 | 463 | 77 | 21 | 2.9 | 13.1 | 42.1585 | 19.9544 | 10.5138 | 0 | 42.5898 | 15.4788 | 0 | 0 | 100% | 0 | 16.4397 | 63.7% | 0 | 43.1455
114 | 1 | 1 | 1 | 1.5 | 9.2 | 0 | 0 | 0 | 0 | 54.9656 | 20.9021 | 0 | 53.4434 | 96% | 0 | 25 | 23.7% | 0 | 43.8489
115 | 0 | 0 | 0 | 0.7 | 7.4 | 0 | 0 | 0 | 0 | 96.1256 | 38.7343 | 0 | 99.7514 | 89% | 0 | 8.5603 | 10% | 0 | 44.3346
116 | 0 | 0 | 0 | 0.9 | 6.1 | 0 | 0 | 0 | 0 | 111.3299 | 45.3963 | 0 | 113.7884 | 80% | 0 | 0 | 10% | 0 | 43.0825
117 | 0 | 0 | 0 | 0.9 | 4.7 | 0 | 0 | 0 | 0 | 105.2133 | 42.8769 | 0 | 105.4122 | 72% | 0 | 0 | 10% | 0 | 40.8504
118 | 0 | 0 | 0 | 0.9 | 3.7 | 0 | 0 | 0 | 0 | 98.0221 | 39.8581 | 0 | 96.6158 | 65% | 0 | 0 | 10% | 0 | 37.8959
119 | 0 | 0 | 0 | 1.1 | 4.6 | 0 | 0 | 0 | 0 | 90.4804 | 36.6426 | 0 | 87.7739 | 58% | 0 | 0 | 10% | 0 | 34.6525
120 | 0 | 0 | 0 | 1.8 | 5.2 | 0 | 0 | 0 | 0 | 85.2997 | 34.4308 | 0 | 81.8955 | 52% | 0 | 0 | 10% | 0 | 32.3617
121 | 0 | 0 | 0 | 2.5 | 6.2 | 0 | 0 | 0 | 0 | 82.3502 | 33.1369 | 0 | 78.8662 | 46% | 0 | 0 | 10% | 0 | 30.9729
122 | 0 | 0 | 0 | 2.4 | 6.1 | 0 | 0 | 0 | 0 | 81.044 | 32.5425 | 0 | 77.8125 | 40% | 0 | 0 | 10% | 0 | 30.2921
123 | 0 | 0 | 0 | 2 | 6.1 | 0 | 0 | 0 | 0 | 80.9235 | 32.4883 | 0 | 77.887 | 34% | 0 | 0 | 10% | 0 | 30.1682
124 | 0 | 0 | 0 | 2.5 | 6 | 0 | 0 | 0 | 0 | 81.6817 | 32.8387 | 0 | 78.8055 | 28% | 0 | 0 | 10% | 0 | 30.4607
125 | 0 | 0 | 0 | 2.4 | 5.5 | 0 | 0 | 0 | 0 | 84.6171 | 34.1365 | 0 | 82.1716 | 22% | 0 | 0 | 10% | 0 | 31.707
126 | 0 | 0 | 0 | 1.3 | 4.8 | 0 | 0 | 0 | 0 | 87.3196 | 35.2977 | 0 | 85.4837 | 16% | 0 | 0 | 10% | 0 | 32.8308
127 | 0 | 0 | 0 | 1.2 | 3.8 | 0 | 0 | 0 | 0 | 93.8754 | 38.1131 | 0 | 93.5829 | 9% | 0 | 0 | 10% | 0 | 35.6177
128 | 164 | 18 | 8 | 1.5 | 5.4 | 0 | 4.1221 | 0 | 0 | 100.8763 | 41.0275 | 0 | 101.845 | 1% | 0 | 0 | 10% | 0 | 38.5349
129 | 717 | 161 | 31 | 0.8 | 8.9 | 97.7541 | 24.9587 | 25.7053 | 1.0629 | 42.3942 | 15.5586 | 62.0344 | 7.533 | 5% | 0 | 0 | 10% | 0 | 39.6155
130 | 888 | 331 | 42 | 0.7 | 13.3 | 196.8619 | 0 | 50.0754 | 0 | 43.7759 | 15.9624 | 153.347 | 0 | 17% | 24.8944 | 0 | 43.86% | 0 | 38.9703
131 | 958 | 465 | 48 | 0.9 | 16.1 | 241.8811 | 0 | 50.7393 | 15.674 | 42.5857 | 15.3436 | 200.1107 | 0 | 32% | 25 | 0 | 77.86% | 0 | 38.4925
132 | 989 | 544 | 51 | 1.5 | 17.1 | 259.6851 | 0 | 33.939 | 41.161 | 42.602 | 15.298 | 218.1001 | 0 | 48% | 8.9292 | 0 | 90% | 0 | 37.5232
133 | 991 | 560 | 52 | 0.7 | 19 | 262.7648 | 0 | 23.4011 | 51.6989 | 42.6058 | 15.1918 | 221.1324 | 0 | 64% | 0 | 0 | 90% | 0 | 35.758
134 | 957 | 508 | 53 | 2 | 19.1 | 246.8096 | 0 | 22.5307 | 47.8503 | 42.6081 | 15.1865 | 205.1107 | 0 | 79% | 0 | 0 | 90% | 0 | 35.0044
135 | 897 | 400 | 50 | 3.3 | 18.6 | 213.1216 | 0 | 21.4538 | 35.4213 | 42.6087 | 15.2162 | 171.2763 | 0 | 92% | 0 | 0 | 90% | 0 | 35.5344
136 | 771 | 246 | 42 | 3.3 | 17.6 | 153.917 | 0 | 21.5978 | 14.8014 | 42.6083 | 15.2729 | 111.972 | 0 | 100% | 0 | 0 | 90% | 0 | 39.1341
137 | 432 | 76 | 23 | 1.5 | 15.1 | 0 | 61.4496 | 9.7476 | 0 | 42.6062 | 15.3988 | 0 | 41.1132 | 97% | 0 | 18.3845 | 60.59% | 0 | 41.4684
138 | 1 | 1 | 1 | 2.9 | 11.3 | 0 | 0 | 0 | 0 | 55.0325 | 20.8455 | 0 | 53.3603 | 93% | 0 | 25 | 20.59% | 0 | 42.9257
139 | 0 | 0 | 0 | 1 | 8.4 | 0 | 0 | 0 | 0 | 98.7672 | 39.8536 | 0 | 102.5896 | 86% | 0 | 6.6155 | 10% | 0 | 43.5332
140 | 0 | 0 | 0 | 0.6 | 6.7 | 0 | 0 | 0 | 0 | 110.5682 | 45.0585 | 0 | 113.1105 | 77% | 0 | 0 | 10% | 0 | 42.6868
141 | 0 | 0 | 0 | 0.7 | 5.1 | 0 | 0 | 0 | 0 | 102.834 | 41.8581 | 0 | 102.8359 | 70% | 0 | 0 | 10% | 0 | 39.7553
142 | 0 | 0 | 0 | 1.6 | 4.8 | 0 | 0 | 0 | 0 | 94.1214 | 38.1917 | 0 | 92.3981 | 63% | 0 | 0 | 10% | 0 | 36.1439
143 | 0 | 0 | 0 | 1.7 | 5.6 | 0 | 0 | 0 | 0 | 87.8537 | 35.5016 | 0 | 84.9456 | 56% | 0 | 0 | 10% | 0 | 33.4161
144 | 0 | 0 | 0 | 0.6 | 4.1 | 0 | 0 | 0 | 0 | 83.9802 | 33.8975 | 0 | 80.6535 | 50% | 0 | 0 | 10% | 0 | 31.731
145 | 0 | 0 | 0 | 2.3 | 4.6 | 0 | 0 | 0 | 0 | 82.4339 | 33.2124 | 0 | 79.2122 | 44% | 0 | 0 | 10% | 0 | 30.9592
146 | 0 | 0 | 0 | 2.8 | 6.1 | 0 | 0 | 0 | 0 | 82.2108 | 33.0748 | 0 | 79.1983 | 38% | 0 | 0 | 10% | 0 | 30.7483
147 | 0 | 0 | 0 | 1.5 | 4.2 | 0 | 0 | 0 | 0 | 84.7849 | 34.236 | 0 | 82.2501 | 32% | 0 | 0 | 10% | 0 | 31.8467
148 | 0 | 0 | 0 | 1 | 3.4 | 0 | 0 | 0 | 0 | 91.863 | 37.2584 | 0 | 90.9081 | 25% | 0 | 0 | 10% | 0 | 34.8177
149 | 0 | 0 | 0 | 0.6 | 3.1 | 0 | 0 | 0 | 0 | 101.9543 | 41.5332 | 0 | 103.0102 | 17% | 0 | 0 | 10% | 0 | 39.0783
150 | 0 | 0 | 0 | 0.9 | 3 | 0 | 0 | 0 | 0 | 109.3164 | 44.6325 | 0 | 111.6172 | 9% | 0 | 0 | 10% | 0 | 42.2107
151 | 0 | 0 | 0 | 0.8 | 2.7 | 0 | 0 | 0 | 0 | 116.012 | 47.4473 | 0 | 119.3461 | 0% | 0 | 0 | 10% | 0 | 45.0779
152 | 151 | 18 | 8 | 0.5 | 3.4 | 0 | 3.8245 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.125
153 | 685 | 158 | 33 | 0.5 | 7.6 | 92.7959 | 23.842 | 25.6107 | 0 | 0 | 0 | 89.4821 | 0 | 7% | 0 | 0 | 10% | 0 | 24.0749
154 | 860 | 326 | 45 | 0.7 | 12 | 190.1021 | 0 | 48.8343 | 0 | 0 | 0 | 187.6759 | 0 | 21% | 0 | 0 | 10% | 0 | 46.7386
155 | 933 | 458 | 50 | 0.7 | 14.9 | 235.1829 | 0 | 65.0288 | 0 | 0 | 0 | 233.4896 | 0 | 39% | 16.3212 | 0 | 32.2% | 0 | 46.1718
156 | 963 | 537 | 53 | 1.5 | 16.2 | 252.5193 | 0 | 74.0206 | 0.14649 | 0 | 0 | 251.1419 | 0 | 58% | 25 | 0 | 66.2% | 0 | 46.2808
157 | 966 | 553 | 55 | 1.6 | 16.3 | 255.3863 | 0 | 65.4293 | 9.6707 | 0 | 0 | 254.1679 | 0 | 77% | 17.5023 | 0 | 90% | 0 | 45.1007
158 | 939 | 504 | 55 | 1.4 | 17.4 | 242.1732 | 0 | 47.0042 | 22.6954 | 0 | 0 | 241.0582 | 0 | 95% | 0 | 0 | 90% | 0 | 44.2659
159 | 875 | 397 | 52 | 3.8 | 16.9 | 107.6596 | 116.2064 | 44.9292 | 11.0963 | 42.5965 | 1.3607 | 66.7488 | 0 | 100% | 0 | 0 | 90% | 0 | 44.5404
160 | 745 | 244 | 44 | 4 | 16.1 | 42.1583 | 127.2717 | 31.8809 | 3.6372 | 42.5953 | 15.3471 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 47.9405
161 | 410 | 76 | 24 | 4.4 | 14 | 0 | 57.9855 | 9.2516 | 0 | 47.8513 | 17.6417 | 0 | 46.3229 | 97% | 0 | 25 | 50% | 0 | 49.8276
162 | 1 | 1 | 1 | 3.5 | 10.5 | 0 | 0 | 0 | 0 | 71.3105 | 28.0062 | 0 | 70.0079 | 91% | 0 | 25 | 10% | 0 | 50.062
163 | 0 | 0 | 0 | 1.7 | 7.6 | 0 | 0 | 0 | 0 | 127.5978 | 52.132 | 0 | 136.3413 | 81% | 0 | 0 | 10% | 0 | 49.2103
164 | 0 | 0 | 0 | 2 | 7.3 | 0 | 0 | 0 | 0 | 120.3979 | 49.1444 | 0 | 123.272 | 72% | 0 | 0 | 10% | 0 | 47.107
165 | 0 | 0 | 0 | 1.9 | 6.1 | 0 | 0 | 0 | 0 | 109.009 | 44.4256 | 0 | 108.8714 | 64% | 0 | 0 | 10% | 0 | 42.6166
166 | 0 | 0 | 0 | 1.1 | 5 | 0 | 0 | 0 | 0 | 101.0365 | 41.1013 | 0 | 99.443 | 56% | 0 | 0 | 10% | 0 | 39.3176
167 | 0 | 0 | 0 | 2.2 | 5.3 | 0 | 0 | 0 | 0 | 93.7742 | 38.0321 | 0 | 91.1576 | 49% | 0 | 0 | 10% | 0 | 36.2105
168 | 0 | 0 | 0 | 1.7 | 4.7 | 0 | 0 | 0 | 0 | 90.2168 | 36.5285 | 0 | 87.1004 | 43% | 0 | 0 | 10% | 0 | 34.636
169 | 0 | 0 | 0 | 1.8 | 4.2 | 0 | 0 | 0 | 0 | 88.3797 | 35.7588 | 0 | 85.1684 | 36% | 0 | 0 | 10% | 0 | 33.7874
170 | 0 | 0 | 0 | 1.6 | 4.2 | 0 | 0 | 0 | 0 | 88.9436 | 35.9987 | 0 | 86.0722 | 30% | 0 | 0 | 10% | 0 | 33.9519
171 | 0 | 0 | 0 | 1.5 | 3.8 | 0 | 0 | 0 | 0 | 91.9467 | 37.2866 | 0 | 89.8803 | 23% | 0 | 0 | 10% | 0 | 35.1773
172 | 0 | 0 | 0 | 2.2 | 2.7 | 0 | 0 | 0 | 0 | 101.7304 | 41.4466 | 0 | 101.5972 | 15% | 0 | 0 | 10% | 0 | 39.2879
173 | 0 | 0 | 0 | 1.9 | 2.9 | 0 | 0 | 0 | 0 | 118.6965 | 48.5609 | 0 | 121.636 | 6% | 0 | 0 | 10% | 0 | 46.3833
174 | 0 | 0 | 0 | 2.1 | 2.4 | 0 | 0 | 0 | 0 | 73.8218 | 30.2472 | 0 | 76.2618 | 0% | 0 | 0 | 10% | 0 | 28.2223
175 | 0 | 0 | 0 | 2.7 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8793
176 | 124 | 17 | 8 | 2.7 | 2.8 | 0 | 3.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8649
177 | 625 | 152 | 37 | 2.7 | 5.7 | 82.2658 | 21.5936 | 23.4805 | 0 | 0 | 0 | 79.0952 | 0 | 6% | 0 | 0 | 10% | 0 | 22.0751
178 | 818 | 320 | 51 | 2.3 | 9.3 | 179.1248 | 0 | 47.2743 | 0 | 0 | 0 | 176.3862 | 0 | 20% | 0 | 0 | 10% | 0 | 45.2622
179 | 896 | 452 | 60 | 2.6 | 10.9 | 224.1138 | 0 | 64.2666 | 0 | 0 | 0 | 222.2769 | 0 | 37% | 12.7666 | 0 | 27.36% | 0 | 49.0472
180 | 932 | 531 | 62 | 1.9 | 12 | 243.65 | 0 | 73.7294 | 0 | 0 | 0 | 242.1703 | 0 | 55% | 22.2294 | 0 | 57.59% | 0 | 48.8245
181 | 946 | 549 | 61 | 1.2 | 13.3 | 250.1732 | 0 | 74.9201 | 0.17987 | 0 | 0 | 248.8591 | 0 | 74% | 23.8275 | 0 | 90% | 0 | 48.3081
182 | 934 | 505 | 57 | 1 | 14.5 | 241.1897 | 0 | 51.8944 | 18.4014 | 0 | 0 | 240.0077 | 0 | 92% | 0 | 0 | 90% | 0 | 49.1487
183 | 871 | 399 | 55 | 2.9 | 14.9 | 143.2783 | 74.6218 | 51.7982 | 4.7971 | 42.5909 | 0 | 102.6453 | 0 | 100% | 0 | 0 | 90% | 0 | 49.4739
184 | 742 | 247 | 47 | 3.9 | 14 | 42.1307 | 127.1198 | 34.009 | 2.0698 | 42.5908 | 15.0998 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 49.7573
185 | 428 | 80 | 25 | 3.7 | 11.9 | 0 | 61.5106 | 10.0591 | 0 | 46.1176 | 16.9988 | 0 | 44.5967 | 97% | 0 | 24.9981 | 50% | 0 | 49.9961
186 | 1 | 1 | 1 | 2.3 | 9 | 0 | 0 | 0 | 0 | 71.1718 | 28.0072 | 0 | 69.86 | 92% | 0 | 25 | 10% | 0 | 50.0657
187 | 0 | 0 | 0 | 1.7 | 7.8 | 0 | 0 | 0 | 0 | 127.5809 | 52.1176 | 0 | 136.3184 | 82% | 0 | 0 | 10% | 0 | 49.1977
188 | 0 | 0 | 0 | 1 | 6.4 | 0 | 0 | 0 | 0 | 126.2641 | 51.6188 | 0 | 130.2355 | 72% | 0 | 0 | 10% | 0 | 49.5815
189 | 0 | 0 | 0 | 1 | 5.4 | 0 | 0 | 0 | 0 | 113.875 | 46.4826 | 0 | 114.2604 | 63% | 0 | 0 | 10% | 0 | 44.7368
190 | 0 | 0 | 0 | 1.3 | 4.8 | 0 | 0 | 0 | 0 | 104.9618 | 42.7682 | 0 | 103.7455 | 55% | 0 | 0 | 10% | 0 | 41.069
191 | 0 | 0 | 0 | 1.3 | 4.4 | 0 | 0 | 0 | 0 | 97.3934 | 39.5782 | 0 | 94.9715 | 48% | 0 | 0 | 10% | 0 | 37.8536
192 | 0 | 0 | 0 | 1.4 | 4 | 0 | 0 | 0 | 0 | 92.8695 | 37.6756 | 0 | 89.9337 | 41% | 0 | 0 | 10% | 0 | 35.8858
193 | 0 | 0 | 0 | 1.1 | 3.2 | 0 | 0 | 0 | 0 | 91.5474 | 37.1275 | 0 | 88.5867 | 34% | 0 | 0 | 10% | 0 | 35.2622
194 | 0 | 0 | 0 | 2.3 | 4 | 0 | 0 | 0 | 0 | 91.4171 | 37.0564 | 0 | 88.652 | 27% | 0 | 0 | 10% | 0 | 35.1223
195 | 0 | 0 | 0 | 2.4 | 4.7 | 0 | 0 | 0 | 0 | 93.6898 | 38.0123 | 0 | 91.6068 | 20% | 0 | 0 | 10% | 0 | 36.0177
196 | 0 | 0 | 0 | 2.6 | 5 | 0 | 0 | 0 | 0 | 103.0653 | 41.9621 | 0 | 102.7454 | 12% | 0 | 0 | 10% | 0 | 39.916
197 | 0 | 0 | 0 | 2.5 | 5.5 | 0 | 0 | 0 | 0 | 119.6129 | 48.8778 | 0 | 122.2178 | 3% | 0 | 0 | 10% | 0 | 46.8057
198 | 0 | 0 | 0 | 2.2 | 5.4 | 0 | 0 | 0 | 0 | 40.1191 | 16.4147 | 0 | 41.2996 | 0% | 0 | 0 | 10% | 0 | 14.5321
199 | 0 | 0 | 0 | 2.6 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8058
200 | 152 | 17 | 7 | 3 | 7.1 | 0 | 3.9887 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7928
201 | 686 | 157 | 31 | 2.8 | 9.4 | 92.1513 | 23.7305 | 25.1184 | 0 | 0 | 0 | 88.5457 | 0 | 7% | 0 | 0 | 10% | 0 | 23.6415
202 | 867 | 327 | 42 | 0.7 | 14.1 | 192.0023 | 0 | 48.4884 | 0 | 0 | 0 | 189.2844 | 0 | 21% | 0 | 0 | 10% | 0 | 46.3533
203 | 933 | 458 | 48 | 1 | 15.7 | 235.1933 | 0 | 64.6133 | 0 | 0 | 0 | 233.3792 | 0 | 39% | 13.1133 | 0 | 27.84% | 0 | 48.9347
204 | 956 | 535 | 52 | 1.2 | 17.5 | 251.065 | 0 | 73.257 | 0 | 0 | 0 | 249.6116 | 0 | 58% | 21.8526 | 0 | 57.56% | 0 | 48.6454
205 | 953 | 550 | 55 | 3.3 | 17.2 | 251.3113 | 0 | 74.4284 | 0.51681 | 0 | 0 | 250.0346 | 0 | 77% | 23.8555 | 0 | 90% | 0 | 47.7609
206 | 926 | 502 | 55 | 3.7 | 17.2 | 237.6791 | 0 | 51.5107 | 17.4282 | 0 | 0 | 236.5241 | 0 | 95% | 0 | 0 | 90% | 0 | 48.7836
207 | 882 | 402 | 50 | 3.6 | 16.8 | 100.7204 | 127.6809 | 51.0553 | 5.4855 | 42.5913 | 0 | 60.3887 | 0 | 100% | 0 | 0 | 90% | 0 | 49.1433
208 | 773 | 252 | 41 | 4 | 16 | 42.1436 | 135.3295 | 34.8624 | 2.069 | 42.5896 | 14.7219 | 0 | 0 | 100% | 0.69267 | 0.58877 | 90% | 0 | 50.039
209 | 483 | 84 | 23 | 4 | 14.4 | 42.1584 | 26.1519 | 11.5532 | 0 | 42.5878 | 15.4236 | 0 | 0 | 100% | 0 | 22.3803 | 54.19% | 0 | 50.0699
210 | 1 | 1 | 1 | 1 | 11.3 | 0 | 0 | 0 | 0 | 69.3589 | 27.1038 | 0 | 68.1115 | 95% | 0 | 25 | 14.19% | 0 | 50.0545
211 | 0 | 0 | 0 | 0.4 | 9.3 | 0 | 0 | 0 | 0 | 121.6472 | 49.5228 | 0 | 129.4074 | 86% | 0 | 2.6197 | 10% | 0 | 49.2135
212 | 0 | 0 | 0 | 1.8 | 8.5 | 0 | 0 | 0 | 0 | 124.9983 | 51.0128 | 0 | 128.4384 | 76% | 0 | 0 | 10% | 0 | 49.042
213 | 0 | 0 | 0 | 1.2 | 7.9 | 0 | 0 | 0 | 0 | 112.4962 | 45.8248 | 0 | 112.3812 | 67% | 0 | 0 | 10% | 0 | 44.1443
214 | 0 | 0 | 0 | 1.6 | 8.6 | 0 | 0 | 0 | 0 | 103.8744 | 42.1884 | 0 | 102.3093 | 59% | 0 | 0 | 10% | 0 | 40.5294
215 | 0 | 0 | 0 | 2.4 | 8.6 | 0 | 0 | 0 | 0 | 97.1247 | 39.3399 | 0 | 94.6023 | 52% | 0 | 0 | 10% | 0 | 37.6349
216 | 0 | 0 | 0 | 1.7 | 6.3 | 0 | 0 | 0 | 0 | 92.723 | 37.5565 | 0 | 89.7331 | 45% | 0 | 0 | 10% | 0 | 35.7762
217 | 0 | 0 | 0 | 1.8 | 7.2 | 0 | 0 | 0 | 0 | 91.5487 | 37.0291 | 0 | 88.5899 | 38% | 0 | 0 | 10% | 0 | 35.1658
218 | 0 | 0 | 0 | 3.1 | 7.5 | 0 | 0 | 0 | 0 | 91.5468 | 37.0189 | 0 | 88.8236 | 32% | 0 | 0 | 10% | 0 | 35.0825
219 | 0 | 0 | 0 | 2.8 | 6.9 | 0 | 0 | 0 | 0 | 93.7916 | 37.9972 | 0 | 91.7528 | 25% | 0 | 0 | 10% | 0 | 35.9987
220 | 0 | 0 | 0 | 2.3 | 6.1 | 0 | 0 | 0 | 0 | 103.4758 | 42.106 | 0 | 103.262 | 17% | 0 | 0 | 10% | 0 | 40.0556
221 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 120.2847 | 49.1715 | 0 | 123.02 | 7% | 0 | 0 | 10% | 0 | 47.0985
222 | 0 | 0 | 0 | 1.2 | 4.3 | 0 | 0 | 0 | 0 | 93.2239 | 38.1647 | 0 | 95.9506 | 0% | 0 | 0 | 10% | 0 | 36.2067
223 | 0 | 0 | 0 | 3.1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7746
224 | 154 | 18 | 8 | 2.1 | 4.3 | 0 | 4.1525 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7623
225 | 690 | 159 | 32 | 1.8 | 8.2 | 93.2066 | 24.0487 | 25.4676 | 0 | 0 | 0 | 89.617 | 0 | 7% | 0 | 0 | 10% | 0 | 23.9848
226 | 869 | 330 | 44 | 3.7 | 10.2 | 190.8513 | 2.98e-14 | 49.437 | 0 | 0 | 0 | 188.2302 | 0 | 21% | 0 | 0 | 10% | 0 | 47.3096
227 | 932 | 461 | 51 | 4.9 | 11.3 | 232.2955 | 0 | 65.814 | 0 | 0 | 0 | 230.5251 | 0 | 39% | 14.314 | 0 | 29.47% | 0 | 48.9586
228 | 956 | 539 | 55 | 5.1 | 12 | 248.4678 | 0 | 74.945 | 0 | 0 | 0 | 247.0307 | 0 | 58% | 23.445 | 0 | 61.35% | 0 | 48.763
229 | 944 | 554 | 62 | 5.7 | 12.1 | 246.8058 | 0 | 72.5773 | 2.5227 | 0 | 0 | 245.5535 | 0 | 77% | 21.0646 | 0 | 90% | 0 | 48.738
230 | 922 | 509 | 61 | 5.3 | 11.9 | 235.3102 | 0 | 52.2561 | 18.3672 | 0 | 0 | 234.1537 | 0 | 95% | 0 | 0 | 90% | 0 | 49.551
231 | 861 | 404 | 59 | 5.3 | 11.8 | 111.7397 | 108.4076 | 52.0148 | 5.1709 | 42.5921 | 0 | 71.3542 | 0 | 100% | 0 | 0 | 90% | 0 | 49.9939
232 | 725 | 253 | 52 | 6 | 10.7 | 42.0402 | 123.4108 | 33.91 | 2.4399 | 42.5911 | 15.3996 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 49.9189
233 | 400 | 85 | 31 | 5.7 | 9 | 0 | 57.4003 | 9.746 | 0 | 46.5616 | 17.2929 | 0 | 45.0384 | 97% | 0 | 25 | 50% | 0 | 49.9828
234 | 1 | 2 | 1 | 3.9 | 7.1 | 0 | 0 | 0 | 0 | 71.0389 | 28.0123 | 0 | 69.7274 | 92% | 0 | 25 | 10% | 0 | 50.0695
235 | 0 | 0 | 0 | 2.7 | 6.1 | 0 | 0 | 0 | 0 | 127.6022 | 52.1871 | 0 | 136.324 | 82% | 0 | 0 | 10% | 0 | 49.2658
236 | 0 | 0 | 0 | 2.2 | 6.1 | 0 | 0 | 0 | 0 | 127.4483 | 52.123 | 0 | 131.6735 | 72% | 0 | 0 | 10% | 0 | 50.0811
237 | 0 | 0 | 0 | 1.5 | 3.9 | 0 | 0 | 0 | 0 | 115.1779 | 47.068 | 0 | 115.7469 | 63% | 0 | 0 | 10% | 0 | 45.3315
238 | 0 | 0 | 0 | 1.2 | 2.9 | 0 | 0 | 0 | 0 | 105.9038 | 43.2057 | 0 | 104.7598 | 55% | 0 | 0 | 10% | 0 | 41.5239
239 | 0 | 0 | 0 | 1.7 | 3.3 | 0 | 0 | 0 | 0 | 98.9357 | 40.2521 | 0 | 96.6787 | 47% | 0 | 0 | 10% | 0 | 38.5464
240 | 0 | 0 | 0 | 2.3 | 2.1 | 0 | 0 | 0 | 0 | 94.773 | 38.5209 | 0 | 92.1042 | 40% | 0 | 0 | 10% | 0 | 36.7548
241 | 0 | 0 | 0 | 3.1 | 2.9 | 0 | 0 | 0 | 0 | 93.3498 | 37.9033 | 0 | 90.6525 | 33% | 0 | 0 | 10% | 0 | 36.0696
242 | 0 | 0 | 0 | 1.6 | 1.8 | 0 | 0 | 0 | 0 | 93.0484 | 37.7938 | 0 | 90.4882 | 26% | 0 | 0 | 10% | 0 | 35.8984
243 | 0 | 0 | 0 | 1.9 | 1.1 | 0 | 0 | 0 | 0 | 95.5474 | 38.8635 | 0 | 93.6052 | 19% | 0 | 0 | 10% | 0 | 36.9117
244 | 0 | 0 | 0 | 1.9 | 0.5 | 0 | 0 | 0 | 0 | 105.4027 | 43.0387 | 0 | 105.3487 | 11% | 0 | 0 | 10% | 0 | 41.0367
245 | 0 | 0 | 0 | 2.6 | 1 | 0 | 0 | 0 | 0 | 122.1109 | 50.0208 | 0 | 124.8844 | 2% | 0 | 0 | 10% | 0 | 47.9962
246 | 0 | 0 | 0 | 2.1 | 0.7 | 0 | 0 | 0 | 0 | 20.2622 | 8.307 | 0 | 20.7976 | 0% | 0 | 0 | 10% | 0 | 6.5001
247 | 0 | 0 | 0 | 1.7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7644
248 | 119 | 17 | 9 | 1.7 | 0.8 | 0 | 3.316 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7522
249 | 620 | 154 | 38 | 2.3 | 3.9 | 81.8098 | 21.5806 | 23.3445 | 0 | 0 | 0 | 78.5677 | 0 | 6% | 0 | 0 | 10% | 0 | 21.9596
250 | 809 | 323 | 55 | 1.1 | 7.1 | 178.1293 | 0 | 47.4094 | 0 | 0 | 0 | 175.3159 | 0 | 20% | 0 | 0 | 10% | 0 | 45.3989
251 | 902 | 460 | 61 | 0.6 | 9.5 | 227.2839 | 0 | 65.1392 | 0 | 0 | 0 | 225.3652 | 0 | 37% | 13.6392 | 0 | 28.55% | 0 | 49.0089
252 | 930 | 538 | 65 | 1.1 | 9.8 | 244.194 | 0 | 74.5678 | 0 | 0 | 0 | 242.6995 | 0 | 55% | 23.0678 | 0 | 59.92% | 0 | 48.8081
253 | 945 | 559 | 65 | 1.6 | 10.5 | 250.5181 | 0 | 73.7036 | 1.3964 | 0 | 0 | 249.19 | 0 | 74% | 22.1165 | 0 | 90% | 0 | 48.7847
254 | 922 | 514 | 65 | 2 | 11.2 | 238.2035 | 0 | 52.6032 | 18.7728 | 0 | 0 | 237.0231 | 0 | 93% | 0 | 0 | 90% | 0 | 49.8745
255 | 843 | 406 | 66 | 3.6 | 11.3 | 137.9829 | 74.1997 | 52.2848 | 4.6749 | 42.5891 | 0 | 97.4978 | 0 | 100% | 0 | 0 | 90% | 0 | 50.0064
256 | 726 | 258 | 55 | 4.2 | 10.6 | 42.1291 | 124.6983 | 34.8948 | 1.9945 | 42.5885 | 14.7648 | 0 | 0 | 100% | 0.87883 | 0.747 | 90% | 0 | 50.0256
257 | 422 | 87 | 30 | 3.6 | 9.2 | 0 | 61.7754 | 10.5001 | 0 | 45.287 | 16.7468 | 0 | 43.7709 | 97% | 0 | 24.7946 | 50.33% | 0 | 49.9876
258 | 1 | 2 | 2 | 2.3 | 6.6 | 0 | 0 | 0 | 0 | 71.0035 | 28.0109 | 0 | 69.6857 | 92% | 0 | 25 | 10.33% | 0 | 50.0704
259 | 0 | 0 | 0 | 2.8 | 5.7 | 0 | 0 | 0 | 0 | 127.6002 | 52.1986 | 0 | 136.3098 | 82% | 0 | 0 | 10.33% | 0 | 49.279
260 | 0 | 0 | 0 | 1.3 | 4.4 | 0 | 0 | 0 | 0 | 126.3065 | 51.6953 | 0 | 130.2599 | 72% | 0 | 0 | 10.33% | 0 | 49.6588
261 | 0 | 0 | 0 | 0.8 | 3 | 0 | 0 | 0 | 0 | 115.8212 | 47.3584 | 0 | 116.5575 | 63% | 0 | 0 | 10.33% | 0 | 45.6105
262 | 0 | 0 | 0 | 1.5 | 1.5 | 0 | 0 | 0 | 0 | 108.232 | 44.2049 | 0 | 107.438 | 55% | 0 | 0 | 10.33% | 0 | 42.5183
263 | 0 | 0 | 0 | 1.3 | 1.4 | 0 | 0 | 0 | 0 | 100.2835 | 40.8556 | 0 | 98.2053 | 47% | 0 | 0 | 10.33% | 0 | 39.1599
264 | 0 | 0 | 0 | 0.9 | 1 | 0 | 0 | 0 | 0 | 94.2292 | 38.3095 | 0 | 91.4216 | 40% | 0 | 0 | 10.33% | 0 | 36.5617
265 | 0 | 0 | 0 | 2.2 | 2.3 | 0 | 0 | 0 | 0 | 91.4166 | 37.0881 | 0 | 88.2676 | 33% | 0 | 0 | 10.33% | 0 | 35.2704
266 | 0 | 0 | 0 | 1.5 | 1.5 | 0 | 0 | 0 | 0 | 90.2283 | 36.5948 | 0 | 87.0819 | 27% | 0 | 0 | 10.33% | 0 | 34.704
267 | 0 | 0 | 0 | 0.9 | -0.4 | 0 | 0 | 0 | 0 | 89.7489 | 36.4174 | 0 | 86.7205 | 20% | 0 | 0 | 10.33% | 0 | 34.4604
268 | 0 | 0 | 0 | 0.8 | -1.1 | 0 | 0 | 0 | 0 | 92.3637 | 37.5431 | 0 | 90.0657 | 13% | 0 | 0 | 10.33% | 0 | 35.5237
269 | 0 | 0 | 0 | 0.5 | -0.8 | 0 | 0 | 0 | 0 | 97.9652 | 39.9107 | 0 | 96.7986 | 6% | 0 | 0 | 10.33% | 0 | 37.8442
270 | 0 | 0 | 0 | 1.1 | -0.2 | 0 | 0 | 0 | 0 | 75.6679 | 30.8977 | 0 | 75.7632 | 0% | 0 | 0 | 10.33% | 0 | 28.8492
271 | 0 | 0 | 0 | 0.5 | -0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.33% | 0 | -1.9323
272 | 138 | 18 | 9 | 1 | -0.2 | 0 | 3.9948 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.33% | 0 | -1.9169
273 | 657 | 158 | 35 | 1 | 3.6 | 88.3568 | 23.1133 | 24.6152 | 0 | 0 | 0 | 84.9262 | 0 | 7% | 0 | 0 | 10.33% | 0 | 23.147
274 | 840 | 328 | 48 | 1 | 7.1 | 185.9551 | 0 | 48.4994 | 0 | 0 | 0 | 183.2499 | 0 | 21% | 0 | 0 | 10.33% | 0 | 46.428
275 | 924 | 464 | 53 | 0.7 | 10 | 233.4575 | 0 | 65.743 | 0 | 0 | 0 | 231.6029 | 0 | 38% | 17.8014 | 0 | 34.54% | 0 | 45.4055
276 | 961 | 547 | 55 | 1.3 | 11.1 | 253.1844 | 0 | 73.333 | 1.767 | 0 | 0 | 251.7031 | 0 | 57% | 25 | 0 | 68.54% | 0 | 45.5691
277 | 963 | 564 | 57 | 1.1 | 11.9 | 256.2473 | 0 | 62.5654 | 12.5346 | 0 | 0 | 254.9709 | 0 | 77% | 15.7805 | 0 | 90% | 0 | 43.9299
278 | 943 | 519 | 56 | 1.6 | 12.6 | 244.7423 | 0 | 45.4744 | 26.3102 | 0 | 0 | 243.5732 | 0 | 95% | 0 | 0 | 90% | 0 | 42.6921
279 | 884 | 414 | 53 | 2.4 | 13.1 | 104.354 | 126.6234 | 44.6468 | 13.4722 | 42.5912 | 0 | 63.8543 | 0 | 100% | 0 | 0 | 90% | 0 | 42.704
280 | 765 | 263 | 46 | 3.7 | 11.9 | 42.1587 | 135.1662 | 29.9483 | 8.0139 | 42.59 | 15.341 | 0 | 0 | 100% | 0.11703 | 0.099475 | 90% | 0 | 45.9709
281 | 471 | 91 | 27 | 3.7 | 10.3 | 42.1587 | 25.6035 | 11.9572 | 0 | 42.5878 | 15.5813 | 0 | 0 | 100% | 0 | 19.4616 | 58.86% | 0 | 47.7139
282 | 2 | 2 | 2 | 2.4 | 7.5 | 0 | 0 | 0 | 0 | 65.5006 | 25.5475 | 0 | 64.1672 | 95% | 0 | 25 | 18.86% | 0 | 48.5002
283 | 0 | 0 | 0 | 1.1 | 5.5 | 0 | 0 | 0 | 0 | 112.5389 | 45.7749 | 0 | 118.6936 | 87% | 0 | 5.5384 | 10% | 0 | 48.3771
284 | 0 | 0 | 0 | 0.7 | 4.5 | 0 | 0 | 0 | 0 | 118.6837 | 48.5163 | 0 | 121.5392 | 77% | 0 | 0 | 10% | 0 | 46.4217
285 | 0 | 0 | 0 | 0.5 | 3.5 | 0 | 0 | 0 | 0 | 110.4324 | 45.0872 | 0 | 110.603 | 69% | 0 | 0 | 10% | 0 | 43.2635
286 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 101.1598 | 41.1976 | 0 | 99.5764 | 61% | 0 | 0 | 10% | 0 | 39.4212
287 | 0 | 0 | 0 | 0.5 | 2.1 | 0 | 0 | 0 | 0 | 93.6973 | 38.0653 | 0 | 91.069 | 54% | 0 | 0 | 10% | 0 | 36.2461
288 | 0 | 0 | 0 | 1.1 | 2.2 | 0 | 0 | 0 | 0 | 88.7259 | 35.9436 | 0 | 85.3545 | 48% | 0 | 0 | 10% | 0 | 34.0473
289 | 0 | 0 | 0 | 0.7 | 0.6 | 0 | 0 | 0 | 0 | 86.3303 | 34.9508 | 0 | 82.8317 | 42% | 0 | 0 | 10% | 0 | 32.9607
290 | 0 | 0 | 0 | 0.3 | 0.6 | 0 | 0 | 0 | 0 | 85.0525 | 34.41 | 0 | 81.6053 | 35% | 0 | 0 | 10% | 0 | 32.333
291 | 0 | 0 | 0 | 1.2 | 1.5 | 0 | 0 | 0 | 0 | 85.1583 | 34.4426 | 0 | 81.9592 | 29% | 0 | 0 | 10% | 0 | 32.2884
292 | 0 | 0 | 0 | 0.5 | 0.3 | 0 | 0 | 0 | 0 | 86.7805 | 35.1467 | 0 | 84.0588 | 23% | 0 | 0 | 10% | 0 | 32.9273
293 | 0 | 0 | 0 | 0.6 | 0.9 | 0 | 0 | 0 | 0 | 90.0833 | 36.5431 | 0 | 88.1591 | 16% | 0 | 0 | 10% | 0 | 34.2731
294 | 0 | 0 | 0 | 0.5 | -0.4 | 0 | 0 | 0 | 0 | 93.0291 | 37.819 | 0 | 91.8445 | 9% | 0 | 0 | 10% | 0 | 35.5199
295 | 0 | 0 | 0 | 0.4 | -0.3 | 0 | 0 | 0 | 0 | 99.8696 | 40.709 | 0 | 99.9787 | 2% | 0 | 0 | 10% | 0 | 38.3904
296 | 159 | 19 | 8 | 0.7 | 0.8 | 0 | 4.8035 | 0 | 0 | 22.1106 | 9.0341 | 0 | 22.4568 | 0% | 0 | 0 | 10% | 0 | 6.8457
297 | 696 | 163 | 32 | 0.5 | 5 | 95.0887 | 24.6158 | 25.8365 | 0 | 0 | 0 | 91.6807 | 0 | 7% | 0 | 0 | 10% | 0 | 24.2735
298 | 873 | 335 | 43 | 1.1 | 9.4 | 194.2806 | 0 | 49.6028 | 0 | 0 | 0 | 191.8464 | 0 | 21% | 5.3808 | 0 | 17.32% | 0 | 42.0911
299 | 947 | 472 | 49 | 1.8 | 11.7 | 239.4288 | 0 | 66.664 | 0 | 0 | 0 | 237.7386 | 0 | 39% | 22.2799 | 0 | 47.62% | 0 | 41.8117
300 | 978 | 555 | 52 | 2.6 | 13.6 | 257.6112 | 0 | 70.6768 | 4.4232 | 0 | 0 | 256.2314 | 0 | 59% | 25 | 0 | 81.62% | 0 | 42.8912
301 | 981 | 573 | 53 | 4.1 | 14.5 | 259.8562 | 0 | 50.1204 | 24.9796 | 0 | 0 | 258.6465 | 0 | 78% | 6.1628 | 0 | 90% | 0 | 41.0904
302 | 962 | 529 | 53 | 4.2 | 15.3 | 248.8481 | 0 | 42.7154 | 29.7441 | 0 | 0 | 247.7239 | 0 | 97% | 0 | 0 | 90% | 0 | 39.9127
303 | 914 | 425 | 49 | 3.6 | 15.8 | 83.4158 | 160.0404 | 39.7997 | 19.5961 | 42.5968 | 1.6284 | 42.6342 | 0 | 100% | 0 | 0 | 90% | 0 | 40.0328
304 | 813 | 274 | 41 | 3.3 | 16.1 | 42.1583 | 147.9562 | 27.7027 | 11.9425 | 42.5951 | 15.347 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.7622
305 | 548 | 99 | 25 | 3.6 | 14.1 | 42.1584 | 42.3957 | 14.2258 | 0 | 42.5927 | 15.4388 | 0 | 0 | 100% | 0 | 16.3254 | 63.88% | 0 | 46.7029
306 | 6 | 2 | 2 | 2.1 | 10.1 | 0 | 0 | 0 | 0 | 65.1786 | 25.3094 | 0 | 63.8368 | 95% | 0 | 25 | 23.88% | 0 | 48.256
307 | 0 | 0 | 0 | 0.2 | 8.1 | 0 | 0 | 0 | 0 | 104.929 | 42.4299 | 0 | 109.8111 | 87% | 0 | 8.6746 | 10% | 0 | 48.1746
308 | 0 | 0 | 0 | 0.9 | 6.4 | 0 | 0 | 0 | 0 | 118.945 | 48.5704 | 0 | 122.3625 | 78% | 0 | 0 | 10% | 0 | 46.3653
309 | 0 | 0 | 0 | 1 | 5.5 | 0 | 0 | 0 | 0 | 108.7795 | 44.3464 | 0 | 108.9064 | 70% | 0 | 0 | 10% | 0 | 42.4705
310 | 0 | 0 | 0 | 1.9 | 5.8 | 0 | 0 | 0 | 0 | 99.753 | 40.5381 | 0 | 98.123 | 62% | 0 | 0 | 10% | 0 | 38.711
311 | 0 | 0 | 0 | 2.7 | 7.3 | 0 | 0 | 0 | 0 | 92.5792 | 37.4644 | 0 | 89.89 | 55% | 0 | 0 | 10% | 0 | 35.5939
312 | 0 | 0 | 0 | 2.9 | 7.5 | 0 | 0 | 0 | 0 | 89.304 | 36.0636 | 0 | 86.2216 | 49% | 0 | 0 | 10% | 0 | 34.112
313 | 0 | 0 | 0 | 2.4 | 6.1 | 0 | 0 | 0 | 0 | 88.0282 | 35.5638 | 0 | 84.975 | 42% | 0 | 0 | 10% | 0 | 33.5273
314 | 0 | 0 | 0 | 1.4 | 4.7 | 0 | 0 | 0 | 0 | 88.0211 | 35.5957 | 0 | 85.1964 | 36% | 0 | 0 | 10% | 0 | 33.4849
315 | 0 | 0 | 0 | 1.7 | 4.9 | 0 | 0 | 0 | 0 | 90.8435 | 36.7919 | 0 | 88.7741 | 29% | 0 | 0 | 10% | 0 | 34.6177
316 | 0 | 0 | 0 | 2.8 | 5.6 | 0 | 0 | 0 | 0 | 101.4778 | 41.2737 | 0 | 101.5658 | 22% | 0 | 0 | 10% | 0 | 39.0492
317 | 0 | 0 | 0 | 2.8 | 6.3 | 0 | 0 | 0 | 0 | 118.711 | 48.4779 | 0 | 121.9464 | 12% | 0 | 0 | 10% | 0 | 46.2437
318 | 0 | 0 | 0 | 3.4 | 6.7 | 0 | 0 | 0 | 0 | 127.3087 | 52.0466 | 0 | 131.8155 | 2% | 0 | 0 | 10% | 0 | 49.8779
319 | 0 | 0 | 0 | 0.9 | 4.2 | 0 | 0 | 0 | 0 | 29.3173 | 12.0028 | 0 | 30.2279 | 0% | 0 | 0 | 10% | 0 | 10.0893
320 | 159 | 19 | 8 | 1.2 | 5.5 | 0 | 5.0333 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8542
321 | 680 | 159 | 31 | 2 | 9.8 | 92.2667 | 23.725 | 24.5415 | 0 | 0 | 0 | 88.8298 | 0 | 7% | 0 | 0 | 10% | 0 | 23.0537
322 | 854 | 328 | 42 | 0.7 | 14.7 | 190.0555 | 0 | 47.434 | 0 | 0 | 0 | 187.5174 | 0 | 21% | 0 | 0 | 10% | 0 | 45.3205
323 | 924 | 462 | 48 | 1.4 | 16.2 | 233.4846 | 2.98e-14 | 63.9004 | 0 | 0 | 0 | 231.7502 | 0 | 39% | 12.4004 | 0 | 26.86% | 0 | 48.9562
324 | 951 | 542 | 51 | 2.1 | 17.5 | 250.5629 | 0 | 73.0002 | 0 | 0 | 0 | 249.154 | 0 | 58% | 21.527 | 0 | 56.14% | 0 | 48.7258
325 | 957 | 561 | 52 | 2.3 | 18.2 | 254.6339 | 0 | 75.1 | 0 | 0 | 0 | 253.3725 | 0 | 77% | 24.6122 | 0 | 89.61% | 0 | 47.6522
326 | 934 | 517 | 53 | 3 | 18.6 | 242.2291 | 0 | 51.5375 | 18.0725 | 0 | 0 | 241.0414 | 0 | 95% | 0.28394 | 0 | 90% | 0 | 48.4884
327 | 885 | 415 | 49 | 2.9 | 18.9 | 100.0498 | 133.3117 | 50.0828 | 6.8183 | 42.5948 | 0.402 | 59.6204 | 0 | 100% | 0 | 0 | 90% | 0 | 48.5951
328 | 779 | 267 | 42 | 3 | 18.2 | 42.1033 | 140.1793 | 34.154 | 3.5636 | 42.5935 | 15.2341 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 50.0623
329 | 519 | 97 | 25 | 2.4 | 16.2 | 42.1592 | 37.7403 | 13.183 | 0 | 42.5911 | 15.3404 | 0 | 0 | 100% | 0 | 20.8313 | 56.67% | 0 | 50.0671
330 | 10 | 2 | 2 | 1 | 13 | 0 | 0 | 0 | 0 | 69.5462 | 27.1026 | 0 | 68.302 | 95% | 0 | 25 | 16.67% | 0 | 50.051
331 | 0 | 0 | 0 | 1.5 | 10.9 | 0 | 0 | 0 | 0 | 118.1656 | 47.9595 | 0 | 125.2875 | 86% | 0 | 4.1687 | 10% | 0 | 49.2051
332 | 0 | 0 | 0 | 1.6 | 10.5 | 0 | 0 | 0 | 0 | 124.9934 | 50.9162 | 0 | 128.6971 | 76% | 0 | 0 | 10% | 0 | 48.8959
333 | 0 | 0 | 0 | 2 | 9.8 | 0 | 0 | 0 | 0 | 112.8236 | 45.8824 | 0 | 112.8737 | 67% | 0 | 0 | 10% | 0 | 44.1764
334 | 0 | 0 | 0 | 3 | 11.4 | 0 | 0 | 0 | 0 | 104.2456 | 42.2154 | 0 | 102.8097 | 59% | 0 | 0 | 10% | 0 | 40.541
335 | 0 | 0 | 0 | 2.3 | 10.4 | 0 | 0 | 0 | 0 | 97.0272 | 39.2216 | 0 | 94.5226 | 52% | 0 | 0 | 10% | 0 | 37.5078
336 | 0 | 0 | 0 | 2 | 9.6 | 0 | 0 | 0 | 0 | 93.2239 | 37.6549 | 0 | 90.3693 | 45% | 0 | 0 | 10% | 0 | 35.8658
337 | 0 | 0 | 0 | 2.7 | 9 | 0 | 0 | 0 | 0 | 92.107 | 37.2041 | 0 | 89.2767 | 38% | 0 | 0 | 10% | 0 | 35.3364
338 | 0 | 0 | 0 | 3 | 9.9 | 0 | 0 | 0 | 0 | 92.0678 | 37.1498 | 0 | 89.4536 | 32% | 0 | 0 | 10% | 0 | 35.2129
339 | 0 | 0 | 0 | 2.7 | 9.1 | 0 | 0 | 0 | 0 | 94.3521 | 38.157 | 0 | 92.4046 | 25% | 0 | 0 | 10% | 0 | 36.1608
340 | 0 | 0 | 0 | 2.8 | 8.7 | 0 | 0 | 0 | 0 | 103.5462 | 42.0477 | 0 | 103.3247 | 17% | 0 | 0 | 10% | 0 | 40.0025
341 | 0 | 0 | 0 | 2.8 | 8.5 | 0 | 0 | 0 | 0 | 120.3613 | 49.0848 | 0 | 123.1029 | 7% | 0 | 0 | 10% | 0 | 47.0167
342 | 0 | 0 | 0 | 2.5 | 8.3 | 0 | 0 | 0 | 0 | 93.5698 | 38.209 | 0 | 96.3235 | 0% | 0 | 0 | 10% | 0 | 36.2556
343 | 0 | 0 | 0 | 2.8 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7692
344 | 39 | 17 | 15 | 2.6 | 6.9 | 0 | 1.2981 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.757
345 | 274 | 129 | 71 | 2 | 8.5 | 0 | 56.7535 | 11.2346 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.4897
346 | 703 | 315 | 75 | 2.8 | 11.4 | 123.796 | 31.4048 | 42.6157 | 0 | 0 | 0 | 118.8153 | 0 | 9% | 0 | 0 | 10% | 0 | 40.8724
347 | 715 | 435 | 110 | 4.6 | 13.6 | 174.7756 | 0 | 56.131 | 0 | 0 | 0 | 172.779 | 0 | 22% | 4.631 | 0 | 16.3% | 0 | 49.5081
348 | 907 | 564 | 92 | 5.2 | 14.7 | 235.8571 | 0 | 74.89 | 0 | 0 | 0 | 233.8998 | 0 | 40% | 23.794 | 0 | 48.66% | 0 | 48.5189
349 | 718 | 504 | 117 | 4.9 | 14.7 | 184.8273 | 0 | 64.0472 | 0 | 0 | 0 | 183.7451 | 0 | 54% | 13.591 | 0 | 67.14% | 0 | 48.3102
350 | 701 | 520 | 166 | 4.8 | 15.2 | 176.0081 | 5.87e-16 | 62.7358 | 0.70457 | 42.573 | 1.0168 | 135.5571 | 0 | 65% | 16.8075 | 0 | 90% | 0 | 44.3746
351 | 502 | 362 | 151 | 4.9 | 14.6 | 113.0573 | 0 | 34.885 | 7.0536 | 42.5788 | 15.4115 | 72.784 | 0 | 70% | 0 | 0 | 90% | 0 | 48.7884
352 | 346 | 213 | 109 | 4.9 | 13.4 | 59.7459 | 0 | 21.3712 | 0 | 42.58 | 15.463 | 19.3801 | 0 | 72% | 0 | 14.2378 | 67.22% | 0 | 50.074
353 | 201 | 94 | 58 | 4.4 | 12 | 0 | 36.6686 | 6.217 | 0 | 53.6925 | 20.2366 | 0 | 50.8586 | 68% | 0 | 25 | 27.22% | 0 | 50.0758
354 | 1 | 2 | 2 | 3.4 | 9.7 | 0 | 0 | 0 | 0 | 102.7964 | 41.459 | 0 | 105.3289 | 60% | 0 | 10.7622 | 10% | 0 | 49.764
355 | 0 | 0 | 0 | 2.9 | 8.1 | 0 | 0 | 0 | 0 | 127.5338 | 52.0867 | 0 | 133.0314 | 50% | 0 | 0 | 10% | 0 | 49.7776
356 | 0 | 0 | 0 | 2.3 | 8.3 | 0 | 0 | 0 | 0 | 125.7601 | 51.339 | 0 | 129.6952 | 40% | 0 | 0 | 10% | 0 | 49.2607
357 | 0 | 0 | 0 | 1.9 | 7.7 | 0 | 0 | 0 | 0 | 113.3301 | 46.1817 | 0 | 114.274 | 32% | 0 | 0 | 10% | 0 | 44.2591
358 | 0 | 0 | 0 | 1.8 | 6.7 | 0 | 0 | 0 | 0 | 104.6785 | 42.5964 | 0 | 104.0047 | 24% | 0 | 0 | 10% | 0 | 40.724
359 | 0 | 0 | 0 | 1.9 | 6.3 | 0 | 0 | 0 | 0 | 97.7195 | 39.6682 | 0 | 95.7956 | 16% | 0 | 0 | 10% | 0 | 37.8005
360 | 0 | 0 | 0 | 2.2 | 6 | 0 | 0 | 0 | 0 | 93.6214 | 37.9514 | 0 | 91.1528 | 9% | 0 | 0 | 10% | 0 | 36.0569
361 | 0 | 0 | 0 | 2.5 | 5.6 | 0 | 0 | 0 | 0 | 92.1431 | 37.3312 | 0 | 89.4913 | 2% | 0 | 0 | 10% | 0 | 35.3973
362 | 0 | 0 | 0 | 0.4 | 4.4 | 0 | 0 | 0 | 0 | 32.7103 | 13.2632 | 0 | 31.8212 | 0% | 0 | 0 | 10% | 0 | 11.3565
363 | 0 | 0 | 0 | 0.6 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8593
364 | 0 | 0 | 0 | 0.3 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8453
365 | 0 | 0 | 0 | 0.4 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8316
366 | 0 | 0 | 0 | 1 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8182
367 | 0 | 0 | 0 | 2 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8049
368 | 33 | 13 | 10 | 1.5 | 3.8 | 0 | 1.1583 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.792
369 | 328 | 122 | 56 | 0.4 | 5.1 | 0 | 56.9533 | 12.5906 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 10.8133
370 | 598 | 301 | 94 | 0.6 | 9.6 | 128.2272 | 0 | 37.8428 | 0 | 0 | 0 | 122.0414 | 0 | 10% | 0 | 0 | 10% | 0 | 36.3079
371 | 778 | 450 | 96 | 1.6 | 11.3 | 194.2102 | 0 | 60.036 | 0 | 0 | 0 | 191.1982 | 0 | 24% | 8.536 | 0 | 21.61% | 0 | 49.3373
372 | 808 | 524 | 101 | 2.8 | 12.5 | 210.1581 | 0 | 68.2232 | 0 | 0 | 0 | 208.2596 | 0 | 40% | 16.7232 | 0 | 44.35% | 0 | 49.1566
373 | 804 | 553 | 118 | 3 | 13.4 | 211.1377 | 0 | 71.8083 | 0 | 0 | 0 | 209.5843 | 0 | 56% | 20.774 | 0 | 72.61% | 0 | 48.6465
374 | 561 | 450 | 161 | 3.5 | 13.8 | 138.3692 | 0 | 52.9678 | 0.61699 | 42.5481 | 0 | 98.0238 | 0 | 64% | 12.7903 | 0 | 90% | 0 | 37.9307
375 | 371 | 319 | 157 | 3.7 | 13.6 | 79.5471 | 0 | 33.54 | 0 | 45.4634 | 13.3037 | 36.1804 | 0 | 66% | 0 | 0 | 90% | 0 | 45.5482
376 | 343 | 216 | 112 | 3.8 | 13.1 | 60.2281 | 0 | 21.5094 | 0 | 42.5556 | 15.4664 | 19.6131 | 0 | 68% | 0 | 14.0979 | 67.44% | 0 | 50.0742
377 | 163 | 92 | 67 | 3.5 | 12.4 | 0 | 29.9275 | 5.712 | 0 | 54.8739 | 20.7314 | 0 | 51.9913 | 64% | 0 | 25 | 27.44% | 0 | 50.0766
378 | 2 | 3 | 3 | 3.1 | 10.5 | 0 | 0 | 0 | 0 | 102.4405 | 41.2713 | 0 | 104.8528 | 56% | 0 | 10.9021 | 10% | 0 | 49.7318
379 | 0 | 0 | 0 | 1.4 | 9.3 | 0 | 0 | 0 | 0 | 127.4414 | 51.9964 | 0 | 132.9584 | 46% | 0 | 0 | 10% | 0 | 49.6818
380 | 0 | 0 | 0 | 1.5 | 8.6 | 0 | 0 | 0 | 0 | 125.364 | 51.162 | 0 | 129.3184 | 36% | 0 | 0 | 10% | 0 | 49.0633
381 | 0 | 0 | 0 | 1.5 | 7.7 | 0 | 0 | 0 | 0 | 113.1891 | 46.1235 | 0 | 114.2245 | 28% | 0 | 0 | 10% | 0 | 44.1734
382 | 0 | 0 | 0 | 0.7 | 7.6 | 0 | 0 | 0 | 0 | 104.7063 | 42.5799 | 0 | 104.1437 | 20% | 0 | 0 | 10% | 0 | 40.6809
383 | 0 | 0 | 0 | 1 | 7.3 | 0 | 0 | 0 | 0 | 97.6868 | 39.6247 | 0 | 95.8416 | 12% | 0 | 0 | 10% | 0 | 37.7341
384 | 0 | 0 | 0 | 0.6 | 6.7 | 0 | 0 | 0 | 0 | 93.8294 | 38.0218 | 0 | 91.4825 | 5% | 0 | 0 | 10% | 0 | 36.1074
385 | 0 | 0 | 0 | 0.8 | 6.7 | 0 | 0 | 0 | 0 | 71.4242 | 28.9201 | 0 | 69.4719 | 0% | 0 | 0 | 10% | 0 | 26.9914
386 | 0 | 0 | 0 | 1.5 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8544
387 | 0 | 0 | 0 | 2.2 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8405
388 | 0 | 0 | 0 | 1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.827
389 | 0 | 0 | 0 | 1.5 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8136
390 | 0 | 0 | 0 | 0.7 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8005
391 | 0 | 0 | 0 | 0.7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7877
392 | 108 | 25 | 18 | 1.7 | 4.5 | 0 | 4.0069 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.775
393 | 315 | 151 | 88 | 0.8 | 7.3 | 0 | 54.4389 | 13.649 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 11.8884
394 | 696 | 380 | 141 | 0.3 | 11.2 | 152.5171 | 0 | 48.3991 | 0 | 0 | 0 | 144.9106 | 0 | 11% | 0 | 0 | 10% | 0 | 46.6525
395 | 526 | 365 | 121 | 1.4 | 12.3 | 125.8598 | 0 | 42.9496 | 0 | 0 | 0 | 124.1066 | 0 | 21% | 0 | 0 | 10% | 0 | 41.3952
396 | 855 | 555 | 105 | 2.2 | 13.2 | 224.0082 | 0 | 72.4782 | 0 | 0 | 0 | 221.1748 | 0 | 38% | 20.9782 | 0 | 38.53% | 0 | 49.0414
397 | 793 | 591 | 160 | 1.5 | 14.3 | 209.1697 | 0 | 74.431 | 0 | 0 | 0 | 207.6162 | 0 | 54% | 22.931 | 0 | 69.72% | 0 | 49.1337
398 | 594 | 491 | 186 | 2.9 | 14.6 | 148.2301 | 0 | 56.3407 | 2.0078 | 42.5398 | 0 | 107.8163 | 0 | 62% | 14.9143 | 0 | 90% | 0 | 39.0876
399 | 350 | 350 | 196 | 1.6 | 14.7 | 75.5129 | 0 | 35.7941 | 0 | 42.5482 | 11.6268 | 34.9856 | 0 | 65% | 0 | 0 | 90% | 0 | 46.152
400 | 7 | 86 | 82 | 3.4 | 13.5 | 0 | 1.7263 | 0.20967 | 0 | 67.1848 | 26.0356 | 0 | 63.8023 | 60% | 0 | 25 | 50% | 0 | 50.0454
401 | 91 | 78 | 67 | 4.4 | 12.4 | 0 | 16.8162 | 3.5594 | 0 | 61.7691 | 23.712 | 0 | 58.5877 | 55% | 0 | 25 | 10% | 0 | 50.0579
402 | 3 | 3 | 3 | 3.9 | 10.7 | 0 | 0 | 0 | 0 | 127.4034 | 51.9105 | 0 | 133.2687 | 45% | 0 | 0 | 10% | 0 | 49.529
403 | 0 | 0 | 0 | 3.5 | 10.1 | 0 | 0 | 0 | 0 | 127.3867 | 51.9352 | 0 | 132.0669 | 35% | 0 | 0 | 10% | 0 | 49.7774
404 | 0 | 0 | 0 | 2.9 | 9.9 | 0 | 0 | 0 | 0 | 125.9092 | 51.33 | 0 | 129.4808 | 25% | 0 | 0 | 10% | 0 | 49.324
405 | 0 | 0 | 0 | 2.5 | 8.2 | 0 | 0 | 0 | 0 | 114.2484 | 46.5492 | 0 | 115.1608 | 17% | 0 | 0 | 10% | 0 | 44.6611
406 | 0 | 0 | 0 | 1.8 | 7.2 | 0 | 0 | 0 | 0 | 105.2417 | 42.8204 | 0 | 104.5331 | 9% | 0 | 0 | 10% | 0 | 40.9753
407 | 0 | 0 | 0 | 1.4 | 7.3 | 0 | 0 | 0 | 0 | 98.5605 | 39.9942 | 0 | 96.6531 | 1% | 0 | 0 | 10% | 0 | 38.1531
408 | 0 | 0 | 0 | 1.5 | 7.2 | 0 | 0 | 0 | 0 | 16.4806 | 6.6771 | 0 | 16.0475 | 0% | 0 | 0 | 10% | 0 | 4.9117
409 | 0 | 0 | 0 | 1.6 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.735
410 | 0 | 0 | 0 | 2.2 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7234
411 | 0 | 0 | 0 | 0.9 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.712
412 | 0 | 0 | 0 | 2.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7008
413 | 0 | 0 | 0 | 1.8 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6899
414 | 0 | 0 | 0 | 1.5 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6791
415 | 0 | 0 | 0 | 0.3 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6685
416 | 0 | 8 | 8 | 0.5 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6581
417 | 214 | 141 | 88 | 0.2 | 7.5 | 0 | 44.6322 | 10.6101 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 8.9622
418 | 547 | 281 | 95 | 1.5 | 10.3 | 94.1452 | 24.0303 | 34.6162 | 0 | 0 | 0 | 89.1329 | 0 | 7% | 0 | 0 | 10% | 0 | 33.1445
419 | 799 | 460 | 94 | 2.3 | 11.8 | 199.8842 | 0 | 60.778 | 0 | 0 | 0 | 195.9199 | 0 | 22% | 9.278 | 0 | 22.62% | 0 | 49.2832
420 | 716 | 522 | 142 | 3.8 | 12.3 | 184.0014 | 0 | 65.3912 | 0 | 0 | 0 | 182.1523 | 0 | 36% | 13.8912 | 0 | 41.51% | 0 | 49.3907
421 | 735 | 570 | 168 | 3.6 | 12.9 | 191.725 | 0 | 70.5284 | 0 | 42.4919 | 0 | 151.0064 | 0 | 48% | 22.5921 | 0 | 72.23% | 0 | 45.2052
422 | 759 | 544 | 155 | 3.5 | 13.2 | 194.3846 | -8.13e-15 | 52.2562 | 15.9223 | 42.5312 | 11.2365 | 153.6066 | 0 | 60% | 13.0623 | 0 | 90% | 0 | 48.0254
423 | 85 | 278 | 236 | 3.2 | 12.8 | 0 | 24.2466 | 20.1034 | 0 | 42.5418 | 15.473 | 0 | 39.4859 | 57% | 0 | 15.0994 | 65.84% | 0 | 49.6651
424 | 82 | 179 | 149 | 3.8 | 12.2 | 0 | 20.2909 | 10.5192 | 0 | 45.1484 | 16.5761 | 0 | 42.0845 | 53% | 0 | 25 | 25.84% | 0 | 50.0706
425 | 6 | 42 | 41 | 3.3 | 11.2 | 0 | 1.116 | 0 | 0 | 104.451 | 42.0911 | 0 | 106.2294 | 45% | 0 | 9.9006 | 10% | 0 | 49.7885
426 | 0 | 2 | 2 | 2.7 | 10.2 | 0 | 0 | 0 | 0 | 127.3628 | 51.9202 | 0 | 131.9003 | 35% | 0 | 0 | 10% | 0 | 49.791
427 | 0 | 0 | 0 | 2.6 | 9.7 | 0 | 0 | 0 | 0 | 127.34 | 51.9358 | 0 | 131.0899 | 25% | 0 | 0 | 10% | 0 | 49.9511
428 | 0 | 0 | 0 | 1.9 | 9.5 | 0 | 0 | 0 | 0 | 123.6133 | 50.3937 | 0 | 126.073 | 16% | 0 | 0 | 10% | 0 | 48.517
429 | 0 | 0 | 0 | 1.2 | 9.1 | 0 | 0 | 0 | 0 | 113.8955 | 46.3657 | 0 | 114.3301 | 7% | 0 | 0 | 10% | 0 | 44.5654
430 | 0 | 0 | 0 | 0.6 | 8.6 | 0 | 0 | 0 | 0 | 90.3494 | 36.7247 | 0 | 89.5588 | 0% | 0 | 0 | 10% | 0 | 34.9714
431 | 0 | 0 | 0 | 0.5 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6354
432 | 0 | 0 | 0 | 2.5 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6256
433 | 0 | 0 | 0 | 2.2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6161
434 | 0 | 0 | 0 | 1.6 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6068
435 | 0 | 0 | 0 | 0.8 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5976
436 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5887
437 | 0 | 0 | 0 | 1.6 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5799
438 | 0 | 0 | 0 | 1.1 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5712
439 | 0 | 0 | 0 | 1.4 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5627
440 | 154 | 22 | 11 | 1.4 | 3.6 | 0 | 6.4167 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5544
441 | 551 | 154 | 44 | 1.4 | 6.8 | 73.1369 | 19.0726 | 20.5351 | 0 | 0 | 0 | 69.1825 | 0 | 5% | 0 | 0 | 10% | 0 | 19.2591
442 | 806 | 338 | 59 | 1.5 | 10.7 | 179.4683 | 0 | 47.036 | 0 | 0 | 0 | 175.1181 | 0 | 19% | 0 | 0 | 10% | 0 | 45.0035
443 | 831 | 462 | 77 | 3.4 | 12.3 | 208.0976 | 0 | 61.2407 | 0 | 42.3999 | 0 | 166.9252 | 0 | 32% | 15.5201 | 0 | 31.11% | 0 | 42.8594
444 | 872 | 547 | 84 | 4.3 | 13 | 227.9389 | 0 | 71.7274 | 0 | 0 | 0 | 226.0465 | 0 | 49% | 23.8317 | 0 | 63.52% | 0 | 45.3592
445 | 850 | 566 | 99 | 3.4 | 13.7 | 225.0251 | 0 | 66.7433 | 6.3521 | 0 | 0 | 223.5124 | 0 | 67% | 19.4717 | 0 | 90% | 0 | 44.7141
446 | 668 | 476 | 126 | 3.7 | 14 | 168.9781 | 0 | 37.5333 | 20.773 | 42.5517 | 8.2576 | 128.6051 | 0 | 76% | 0 | 0 | 90% | 0 | 43.4995
447 | 686 | 423 | 125 | 3.8 | 14 | 164.7605 | 2.98e-14 | 30.1201 | 22.3334 | 42.5578 | 15.4305 | 124.0615 | 0 | 86% | 0 | 0 | 90% | 0 | 43.5353
448 | 197 | 163 | 93 | 4 | 12.5 | 0 | 48.9146 | 12.4052 | 0 | 42.5627 | 15.492 | 0 | 39.9965 | 83% | 0 | 19.4999 | 58.8% | 0 | 46.0643
449 | 0 | 34 | 34 | 3.4 | 10.8 | 0 | 0 | 0 | 0 | 64.7021 | 25.0652 | 0 | 61.9228 | 78% | 0 | 25 | 18.8% | 0 | 47.6797
450 | 0 | 3 | 3 | 1.5 | 9.9 | 0 | 0 | 0 | 0 | 111.4105 | 45.1356 | 0 | 115.738 | 70% | 0 | 5.5001 | 10% | 0 | 48.0725
451 | 0 | 0 | 0 | 1.6 | 9.4 | 0 | 0 | 0 | 0 | 122.0803 | 49.7594 | 0 | 126.2443 | 60% | 0 | 0 | 10% | 0 | 47.5096
452 | 0 | 0 | 0 | 1 | 9.4 | 0 | 0 | 0 | 0 | 116.2229 | 47.3254 | 0 | 118.224 | 51% | 0 | 0 | 10% | 0 | 45.3046
453 | 0 | 0 | 0 | 0.6 | 9.2 | 0 | 0 | 0 | 0 | 108.032 | 43.9082 | 0 | 108.1184 | 43% | 0 | 0 | 10% | 0 | 41.994
454 | 0 | 0 | 0 | 0.7 | 8.7 | 0 | 0 | 0 | 0 | 100.1915 | 40.6296 | 0 | 98.7896 | 35% | 0 | 0 | 10% | 0 | 38.7451
455 | 0 | 0 | 0 | 0.5 | 8.3 | 0 | 0 | 0 | 0 | 92.6715 | 37.4721 | 0 | 90.0584 | 28% | 0 | 0 | 10% | 0 | 35.5726
456 | 0 | 0 | 0 | 0.8 | 7.9 | 0 | 0 | 0 | 0 | 87.4557 | 35.2689 | 0 | 83.9824 | 22% | 0 | 0 | 10% | 0 | 33.3233
457 | 0 | 0 | 0 | 0.9 | 8 | 0 | 0 | 0 | 0 | 84.4732 | 34.0053 | 0 | 80.7062 | 16% | 0 | 0 | 10% | 0 | 31.9952
458 | 0 | 0 | 0 | 0.9 | 8.7 | 0 | 0 | 0 | 0 | 83.5135 | 33.5763 | 0 | 79.8026 | 10% | 0 | 0 | 10% | 0 | 31.4981
459 | 0 | 0 | 0 | 1.7 | 9.4 | 0 | 0 | 0 | 0 | 83.6077 | 33.59 | 0 | 80.0996 | 4% | 0 | 0 | 10% | 0 | 31.4488
460 | 0 | 0 | 0 | 4.6 | 10.4 | 0 | 0 | 0 | 0 | 51.6449 | 20.742 | 0 | 49.7701 | 0% | 0 | 0 | 10% | 0 | 18.5758
461 | 0 | 0 | 0 | 5.1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1094
462 | 0 | 0 | 0 | 2.5 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0907
463 | 0 | 0 | 0 | 1.6 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0724
464 | 12 | 8 | 7 | 1.1 | 8.1 | 0 | 0.5308 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0543
465 | 0 | 43 | 43 | 2.4 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0365
466 | 0 | 131 | 130 | 5.5 | 12.3 | 0 | 0 | 2.8976 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.87877
467 | 9 | 185 | 179 | 5 | 13.2 | 0 | 2.6286 | 6.638 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.6362
468 | 83 | 255 | 208 | 6.6 | 14.6 | 0 | 25.2142 | 16.9304 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 14.9455
469 | 1 | 130 | 128 | 5.2 | 13.5 | 0 | 0.30699 | 2.3253 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.35681
470 | 0 | 137 | 135 | 2.4 | 13.4 | 0 | 0 | 2.7487 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.79623
471 | 22 | 113 | 102 | 2 | 13.7 | 0 | 6.3015 | 3.068 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 1.1314
472 | 0 | 92 | 91 | 3.1 | 13.5 | 0 | 0 | 0.45812 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.463
473 | 14 | 27 | 26 | 6.5 | 12.4 | 0 | 2.6382 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.906
474 | 16 | 4 | 4 | 5.2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8911
475 | 0 | 0 | 0 | 2.4 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8765
476 | 0 | 0 | 0 | 4 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8621
477 | 0 | 0 | 0 | 1.6 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8482
478 | 0 | 0 | 0 | 1.8 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8344
479 | 0 | 0 | 0 | 2.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8209
480 | 0 | 0 | 0 | 1 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8078
481 | 0 | 0 | 0 | 0.7 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7948
482 | 0 | 0 | 0 | 1.2 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7821
483 | 0 | 0 | 0 | 1.2 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7696
484 | 0 | 0 | 0 | 0.8 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7573
485 | 0 | 0 | 0 | 0.9 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7453
486 | 0 | 0 | 0 | 1.2 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7335
487 | 0 | 0 | 0 | 1.3 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7219
488 | 193 | 23 | 9 | 1.1 | 3.5 | 0 | 9.0692 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7105
489 | 708 | 174 | 32 | 1.1 | 7 | 98.7727 | 25.4597 | 25.8789 | 0 | 0 | 0 | 90.1595 | 0 | 7% | 0 | 0 | 10% | 0 | 24.355
490 | 875 | 350 | 44 | 3.2 | 10.2 | 196.3688 | 0 | 49.6692 | 0 | 0 | 0 | 189.851 | 0 | 22% | 0 | 0 | 10% | 0 | 47.487
491 | 945 | 490 | 49 | 4 | 12.4 | 239.3409 | 0 | 66.6433 | 0 | 42.1788 | 0 | 196.5953 | 0 | 37% | 17.9942 | 0 | 34.47% | 0 | 45.5065
492 | 977 | 581 | 57 | 4.3 | 13 | 258.6898 | 0 | 75.1 | 0 | 0 | 0 | 255.9033 | 0 | 57% | 23.6 | 0 | 66.57% | 0 | 48.676
493 | 868 | 562 | 79 | 3.9 | 13.5 | 230.6024 | 0 | 68.6381 | 3.9713 | 0 | 0 | 228.6862 | 0 | 75% | 17.2294 | 0 | 90% | 0 | 48.7934
494 | 564 | 441 | 148 | 4.3 | 13.5 | 139.7858 | 0 | 51.1254 | 1.9425 | 0 | 0 | 138.6774 | 0 | 85% | 0 | 0 | 90% | 0 | 49.3546
495 | 918 | 482 | 79 | 5.3 | 13.7 | 226.03 | 0 | 49.6226 | 15.1171 | 42.4971 | 2.7324 | 184.3356 | 0 | 99% | 0 | 0 | 90% | 0 | 49.3228
496 | 828 | 317 | 57 | 4.6 | 12.8 | 51.5076 | 145.8903 | 34.4602 | 9.4122 | 42.5135 | 15.4627 | 10.5076 | 0 | 100% | 0 | 0 | 90% | 0 | 50.0509
497 | 562 | 124 | 33 | 5.4 | 11.4 | 42.1615 | 50.1855 | 16.2795 | 0 | 42.5135 | 15.515 | 0 | 0 | 100% | 0 | 17.5651 | 61.9% | 0 | 50.073
498 | 52 | 6 | 3 | 3.7 | 9.9 | 0 | 0 | 0 | 0 | 69.1946 | 27.0995 | 0 | 67.9461 | 95% | 0 | 25 | 21.9% | 0 | 50.0555
499 | 0 | 0 | 0 | 1.8 | 8.3 | 0 | 0 | 0 | 0 | 110.5792 | 44.8484 | 0 | 116.3194 | 86% | 0 | 7.4349 | 10% | 0 | 49.3676
500 | 0 | 0 | 0 | 0.7 | 6.4 | 0 | 0 | 0 | 0 | 124.8107 | 51.0147 | 0 | 129.0499 | 77% | 0 | 0 | 10% | 0 | 48.8792
501 | 0 | 0 | 0 | 1 | 4.8 | 0 | 0 | 0 | 0 | 112.518 | 45.9323 | 0 | 112.8247 | 68% | 0 | 0 | 10% | 0 | 44.1642
502 | 0 | 0 | 0 | 1.5 | 4.7 | 0 | 0 | 0 | 0 | 104.3617 | 42.5192 | 0 | 103.1641 | 60% | 0 | 0 | 10% | 0 | 40.7999
503 | 0 | 0 | 0 | 1.6 | 4.4 | 0 | 0 | 0 | 0 | 96.9431 | 39.391 | 0 | 94.5734 | 53% | 0 | 0 | 10% | 0 | 37.6444
504 | 0 | 0 | 0 | 1.7 | 3.6 | 0 | 0 | 0 | 0 | 93.2315 | 37.8419 | 0 | 90.5117 | 46% | 0 | 0 | 10% | 0 | 36.0252
505 | 0 | 0 | 0 | 1.4 | 3.9 | 0 | 0 | 0 | 0 | 91.844 | 37.2434 | 0 | 89.0721 | 39% | 0 | 0 | 10% | 0 | 35.3532
506 | 0 | 0 | 0 | 0.9 | 2.4 | 0 | 0 | 0 | 0 | 91.8659 | 37.2817 | 0 | 89.3167 | 32% | 0 | 0 | 10% | 0 | 35.3239
507 | 0 | 0 | 0 | 1.2 | 2.7 | 0 | 0 | 0 | 0 | 94.546 | 38.4179 | 0 | 92.7222 | 25% | 0 | 0 | 10% | 0 | 36.402
508 | 0 | 0 | 0 | 2.5 | 4.3 | 0 | 0 | 0 | 0 | 103.8776 | 42.3255 | 0 | 103.8262 | 17% | 0 | 0 | 10% | 0 | 40.2639
509 | 0 | 0 | 0 | 1.5 | 3.6 | 0 | 0 | 0 | 0 | 120.8115 | 49.4276 | 0 | 123.7076 | 8% | 0 | 0 | 10% | 0 | 47.347
510 | 0 | 0 | 0 | 2.3 | 3.5 | 0 | 0 | 0 | 0 | 99.5134 | 40.7548 | 0 | 102.4337 | 0% | 0 | 0 | 10% | 0 | 38.7829
511 | 0 | 0 | 0 | 1.5 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7737
512 | 192 | 41 | 27 | 1.3 | 3.8 | 0 | 9.5882 | 1.1998 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.56156
513 | 288 | 165 | 115 | 4.8 | 8.2 | 0 | 49.6909 | 15.6738 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 13.9266
514 | 11 | 150 | 145 | 6.1 | 8.8 | 0 | 2.8922 | 4.5938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 2.8567
515 | 0 | 157 | 155 | 4.3 | 9.7 | 0 | 0 | 4.2852 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 2.5598
516 | 12 | 219 | 210 | 4.8 | 10.4 | 0 | 3.656 | 9.2019 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 7.488
517 | 7 | 280 | 272 | 3.2 | 11.2 | 0 | 2.156 | 14.3736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 12.671
518 | 5 | 217 | 211 | 2.6 | 11.3 | 0 | 1.5091 | 8.8306 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 7.139
519 | 0 | 127 | 125 | 2.2 | 10.9 | 0 | 0 | 2.2629 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.58211
520 | 0 | 114 | 112 | 2.6 | 11 | 0 | 0 | 1.7949 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.12475
521 | 110 | 54 | 41 | 4.4 | 11 | 0 | 21.0023 | 2.1302 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.47048
522 | 14 | 4 | 3 | 6 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6496
523 | 0 | 0 | 0 | 6.2 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6396
524 | 0 | 0 | 0 | 8.4 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6298
525 | 0 | 0 | 0 | 9.7 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6201
526 | 0 | 0 | 0 | 9.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6107
527 | 0 | 0 | 0 | 8.4 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6014
528 | 0 | 0 | 0 | 8.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5923
529 | 0 | 0 | 0 | 8.4 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5834
530 | 0 | 0 | 0 | 6 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5746
531 | 0 | 0 | 0 | 8.6 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.566
532 | 0 | 0 | 0 | 6.4 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5576
533 | 0 | 0 | 0 | 3.6 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5494
534 | 0 | 0 | 0 | 2.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5413
535 | 0 | 0 | 0 | 1.1 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5334
536 | 0 | 9 | 9 | 2.9 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5256
537 | 325 | 129 | 52 | 9.5 | 9.3 | 0 | 57.7507 | 11.8462 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 10.3294
538 | 546 | 289 | 84 | 11.9 | 10.1 | 108.2707 | 0 | 33.7148 | 0 | 0 | 0 | 98.9704 | 0 | 8% | 0 | 0 | 10% | 0 | 32.343
539 | 507 | 420 | 174 | 13.5 | 11.5 | 0 | 0 | 47.4318 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | 46.8704
540 | 617 | 527 | 185 | 13.5 | 12.8 | 0 | 0 | 62.3589 | 0 | 0 | 0 | 0 | 0 | 8% | 10.8589 | 0 | 24.77% | 0 | 49.9942
541 | 423 | 498 | 251 | 13.8 | 13.3 | 0 | 0 | 51.5 | 1.9345 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 24.77% | 0 | 50.0021
542 | 423 | 527 | 293 | 10.4 | 14.4 | 77.0106 | 20.9606 | 55.1872 | 0 | 0 | 0 | 72.8846 | 0 | 14% | 3.8887 | 0 | 30.06% | 0 | 49.9959
543 | 294 | 362 | 219 | 8.3 | 14.8 | 56.362 | 0 | 34.1818 | 0 | 41.9347 | 0 | 16.5225 | 0 | 15% | 0 | 0 | 30.06% | 0 | 32.7133
544 | 63 | 176 | 155 | 8.5 | 14.5 | 0 | 15.8625 | 9.8477 | 0 | 64.6528 | 15.4324 | 0 | 61.9013 | 10% | 0 | 12.5354 | 10% | 0 | 36.7725
545 | 32 | 58 | 53 | 9.9 | 13.1 | 0 | 6.1501 | 0.096818 | 0 | 125.7354 | 51.0839 | 0 | 128.4592 | 0% | 0 | 0 | 10% | 0 | 49.3798
546 | 42 | 10 | 8 | 11.8 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5587
547 | 0 | 0 | 0 | 8.8 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5504
548 | 0 | 0 | 0 | 9.4 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5422
549 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5342
550 | 0 | 0 | 0 | 8.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5264
551 | 0 | 0 | 0 | 6.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5187
552 | 0 | 0 | 0 | 4.4 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5111
553 | 0 | 0 | 0 | 6.7 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5037
554 | 0 | 0 | 0 | 7.3 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4964
555 | 0 | 0 | 0 | 7.8 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4893
556 | 0 | 0 | 0 | 5.8 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4824
557 | 0 | 0 | 0 | 4.6 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4755
558 | 0 | 0 | 0 | 5.1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4688
559 | 0 | 0 | 0 | 4.2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4622
560 | 0 | 12 | 12 | 5 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4557
561 | 6 | 103 | 100 | 7 | 14.3 | 0 | 1.2749 | 1.8794 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.43009
562 | 58 | 234 | 209 | 6.5 | 15.4 | 0 | 15.3201 | 15.1813 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 13.7382
563 | 219 | 383 | 270 | 6.5 | 17 | 0 | 53.34 | 34.2474 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 32.8115
564 | 331 | 488 | 298 | 7 | 18 | 72.5094 | 0 | 48.2646 | 0 | 0 | 0 | 66.9863 | 0 | 6% | 0 | 0 | 10% | 0 | 47.2034
565 | 393 | 522 | 291 | 5.9 | 18.7 | 92.8329 | 0 | 53.7496 | 0 | 0 | 0 | 89.2581 | 0 | 13% | 3.146 | 0 | 14.28% | 0 | 49.3462
566 | 480 | 506 | 244 | 4.7 | 19.1 | 116.3805 | 0 | 54.6069 | 0 | 42.0331 | 0 | 75.1064 | 0 | 19% | 19.2482 | 0 | 40.46% | 0 | 33.3444
567 | 343 | 412 | 252 | 3.7 | 18.6 | 73.5771 | 1.49e-14 | 40.1824 | 0 | 42.2627 | 7.5859 | 33.4379 | 0 | 21% | 5.0997 | 0 | 47.39% | 0 | 41.2951
568 | 272 | 279 | 188 | 4.9 | 18.5 | 0 | 55.2198 | 25.0516 | 0 | 42.3094 | 15.1151 | 0 | 38.8021 | 18% | 0 | 10.6246 | 30.39% | 0 | 50.0508
569 | 217 | 136 | 99 | 6.7 | 17.5 | 0 | 41.9813 | 9.6695 | 0 | 75.6011 | 29.4465 | 0 | 73.4296 | 13% | 0 | 12.7452 | 10% | 0 | 50.0774
570 | 18 | 11 | 10 | 5.9 | 16 | 0 | 0 | 0 | 0 | 126.4791 | 51.1603 | 0 | 129.7057 | 3% | 0 | 0 | 10% | 0 | 49.2682
571 | 0 | 0 | 0 | 5.1 | 15.4 | 0 | 0 | 0 | 0 | 33.7094 | 13.6484 | 0 | 34.468 | 0% | 0 | 0 | 10% | 0 | 11.9713
572 | 0 | 0 | 0 | 4.6 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6152
573 | 0 | 0 | 0 | 3.8 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6058
574 | 0 | 0 | 0 | 2.8 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5966
575 | 0 | 0 | 0 | 2.3 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5876
576 | 0 | 0 | 0 | 2.3 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5788
577 | 0 | 0 | 0 | 1.6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5701
578 | 0 | 0 | 0 | 1.3 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5616
579 | 0 | 0 | 0 | 1.8 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5533
580 | 0 | 0 | 0 | 1.9 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5451
581 | 0 | 0 | 0 | 0.9 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5371
582 | 0 | 0 | 0 | 1.6 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5292
583 | 0 | 0 | 0 | 1.9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5215
584 | 185 | 25 | 10 | 1.9 | 11.3 | 0 | 11.088 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5139
585 | 686 | 176 | 33 | 2.8 | 14.7 | 96.5245 | 24.4368 | 24.3008 | 0 | 0 | 0 | 90.261 | 0 | 7% | 0 | 0 | 10% | 0 | 22.8308
586 | 856 | 351 | 43 | 2.8 | 17.2 | 193.8722 | 0 | 47.3201 | 0 | 0 | 0 | 189.1681 | 0 | 22% | 0 | 0 | 10% | 0 | 45.147
587 | 927 | 490 | 49 | 2.3 | 18.5 | 236.8121 | 0 | 64.2355 | 0 | 42.346 | 0 | 195.2026 | 0 | 37% | 15.8328 | 0 | 31.53% | 0 | 45.2664
588 | 950 | 573 | 53 | 2.6 | 19.4 | 254.036 | 0 | 65.5419 | 8.029 | 42.4766 | 9.3224 | 213.0378 | 0 | 54% | 24.0266 | 0 | 64.21% | 0 | 47.8182
589 | 964 | 604 | 57 | 3 | 19.8 | 260.995 | 0 | 53.511 | 21.589 | 42.5172 | 15.1109 | 220.0187 | 0 | 70% | 18.9642 | 0 | 90% | 0 | 46.7419
590 | 904 | 557 | 73 | 3.6 | 20.2 | 237.9793 | 0 | 33.6872 | 36.8519 | 42.5386 | 15.093 | 197.0796 | 0 | 85% | 0 | 0 | 90% | 0 | 46.0695
591 | 886 | 459 | 59 | 3.6 | 19.8 | 220.7995 | 0 | 32.276 | 27.1437 | 42.5528 | 15.1235 | 179.4882 | 0 | 99% | 0 | 0 | 90% | 0 | 45.9023
592 | 813 | 310 | 45 | 2.9 | 19.3 | 56.8405 | 139.29 | 31.7848 | 9.3328 | 42.5618 | 15.1576 | 15.333 | 0 | 100% | 0 | 0 | 90% | 0 | 47.5481
593 | 607 | 135 | 30 | 2.3 | 18.4 | 42.1531 | 64.7348 | 17.3851 | 0 | 42.5606 | 15.2107 | 0 | 0 | 100% | 0 | 16.6751 | 63.32% | 0 | 49.9828
594 | 76 | 9 | 5 | 1.5 | 15.6 | 0 | 0 | 0 | 0 | 69.8946 | 27.1186 | 0 | 68.6575 | 95% | 0 | 25 | 23.32% | 0 | 50.0648
595 | 0 | 0 | 0 | 1.1 | 13.2 | 0 | 0 | 0 | 0 | 108.2064 | 43.5741 | 0 | 113.6031 | 87% | 0 | 8.3249 | 10% | 0 | 48.9877
596 | 0 | 0 | 0 | 0.7 | 11.3 | 0 | 0 | 0 | 0 | 119.0563 | 48.4059 | 0 | 122.3027 | 77% | 0 | 0 | 10% | 0 | 46.2485
597 | 0 | 0 | 0 | 0.9 | 10 | 0 | 0 | 0 | 0 | 109.4125 | 44.4486 | 0 | 109.553 | 69% | 0 | 0 | 10% | 0 | 42.5962
598 | 0 | 0 | 0 | 0.8 | 9.6 | 0 | 0 | 0 | 0 | 103.2027 | 41.8638 | 0 | 102.1214 | 61% | 0 | 0 | 10% | 0 | 40.0553
599 | 0 | 0 | 0 | 2.3 | 9.7 | 0 | 0 | 0 | 0 | 96.5256 | 39.0441 | 0 | 94.375 | 54% | 0 | 0 | 10% | 0 | 37.2163
600 | 0 | 0 | 0 | 1.9 | 9.6 | 0 | 0 | 0 | 0 | 91.3824 | 36.8711 | 0 | 88.4954 | 47% | 0 | 0 | 10% | 0 | 34.9857
601 | 0 | 0 | 0 | 2.7 | 9.3 | 0 | 0 | 0 | 0 | 89.0685 | 35.9003 | 0 | 85.9758 | 41% | 0 | 0 | 10% | 0 | 33.9379
602 | 0 | 0 | 0 | 2.9 | 9.8 | 0 | 0 | 0 | 0 | 88.5534 | 35.6612 | 0 | 85.6 | 34% | 0 | 0 | 10% | 0 | 33.6235
603 | 0 | 0 | 0 | 2.1 | 8.5 | 0 | 0 | 0 | 0 | 87.8871 | 35.4306 | 0 | 85.003 | 28% | 0 | 0 | 10% | 0 | 33.3303
604 | 0 | 0 | 0 | 1.8 | 7.8 | 0 | 0 | 0 | 0 | 90.08 | 36.3867 | 0 | 87.8034 | 21% | 0 | 0 | 10% | 0 | 34.2278
605 | 0 | 0 | 0 | 2.1 | 7.1 | 0 | 0 | 0 | 0 | 95.198 | 38.5851 | 0 | 94.1054 | 14% | 0 | 0 | 10% | 0 | 36.3815
606 | 0 | 0 | 0 | 2.7 | 7.9 | 0 | 0 | 0 | 0 | 100.7365 | 40.8923 | 0 | 100.6539 | 6% | 0 | 0 | 10% | 0 | 38.6716
607 | 0 | 0 | 0 | 1.6 | 6.5 | 0 | 0 | 0 | 0 | 82.2177 | 33.5065 | 0 | 83.3727 | 0% | 0 | 0 | 10% | 0 | 31.3277
608 | 203 | 28 | 11 | 1.5 | 6.8 | 0 | 12.9213 | 0.10287 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9317
609 | 711 | 184 | 34 | 0.6 | 11.1 | 101.8036 | 25.8257 | 25.8079 | 0 | 0 | 0 | 98.0082 | 0 | 7% | 0 | 0 | 10% | 0 | 24.2116
610 | 872 | 361 | 45 | 0.6 | 14.8 | 199.6957 | 0 | 48.9666 | 0 | 0 | 0 | 197.2228 | 0 | 22% | 3.7663 | 0 | 15.12% | 0 | 43.0108
611 | 941 | 502 | 51 | 3.8 | 16.3 | 240.2104 | 0 | 66.0501 | 0 | 0 | 0 | 238.5101 | 0 | 41% | 21.1826 | 0 | 43.93% | 0 | 42.2744
612 | 972 | 590 | 53 | 4.2 | 17.2 | 259.6697 | 0 | 70.225 | 4.875 | 0 | 0 | 258.2545 | 0 | 60% | 25 | 0 | 77.93% | 0 | 42.4052
613 | 978 | 614 | 55 | 4.2 | 17.7 | 264.6303 | 0 | 52.25 | 22.85 | 0 | 0 | 263.3965 | 0 | 80% | 8.8746 | 0 | 90% | 0 | 40.4439
614 | 961 | 572 | 54 | 4.2 | 18.1 | 254.1959 | 0 | 42.2241 | 31.3161 | 0 | 0 | 253.0527 | 0 | 99% | 0 | 0 | 90% | 0 | 39.3526
615 | 919 | 471 | 51 | 4.7 | 17.9 | 51.8138 | 205.7201 | 38.9249 | 22.4236 | 42.595 | 1.0325 | 11.5847 | 0 | 100% | 0 | 0 | 90% | 0 | 38.9296
616 | 828 | 319 | 45 | 4.7 | 17.4 | 42.1582 | 160.7753 | 25.046 | 17.3079 | 42.5929 | 15.2783 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.0365
617 | 611 | 139 | 31 | 4.2 | 16 | 42.1583 | 65.6426 | 17.8494 | 0 | 42.5905 | 15.3504 | 0 | 0 | 100% | 0 | 10.0967 | 73.84% | 0 | 44.0089
618 | 83 | 10 | 5 | 3.2 | 13.2 | 0 | 0 | 0 | 0 | 57.8065 | 21.9587 | 0 | 56.3181 | 96% | 0 | 25 | 33.84% | 0 | 44.899
619 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 83.2165 | 32.995 | 0 | 84.9761 | 90% | 0 | 14.9033 | 10% | 0 | 44.9543
620 | 0 | 0 | 0 | 0.5 | 9.5 | 0 | 0 | 0 | 0 | 112.3573 | 45.7007 | 0 | 115.8764 | 81% | 0 | 0 | 10% | 0 | 43.1877
621 | 0 | 0 | 0 | 1.7 | 8 | 0 | 0 | 0 | 0 | 104.2555 | 42.3726 | 0 | 104.5904 | 73% | 0 | 0 | 10% | 0 | 40.2628
622 | 0 | 0 | 0 | 0.6 | 7.8 | 0 | 0 | 0 | 0 | 96.5047 | 39.1078 | 0 | 95.0983 | 66% | 0 | 0 | 10% | 0 | 37.0787
623 | 0 | 0 | 0 | 0.5 | 7.5 | 0 | 0 | 0 | 0 | 90.364 | 36.514 | 0 | 87.8551 | 59% | 0 | 0 | 10% | 0 | 34.4581
624 | 0 | 0 | 0 | 1.3 | 7.5 | 0 | 0 | 0 | 0 | 86.0615 | 34.6894 | 0 | 82.965 | 53% | 0 | 0 | 10% | 0 | 32.5631
625 | 0 | 0 | 0 | 2.2 | 6.8 | 0 | 0 | 0 | 0 | 83.077 | 33.4512 | 0 | 79.7373 | 47% | 0 | 0 | 10% | 0 | 31.2424
626 | 0 | 0 | 0 | 1.2 | 6.9 | 0 | 0 | 0 | 0 | 82.4952 | 33.185 | 0 | 79.381 | 41% | 0 | 0 | 10% | 0 | 30.8939
627 | 0 | 0 | 0 | 1.2 | 7.2 | 0 | 0 | 0 | 0 | 82.6805 | 33.2619 | 0 | 79.7538 | 35% | 0 | 0 | 10% | 0 | 30.9049
628 | 0 | 0 | 0 | 2.3 | 7.3 | 0 | 0 | 0 | 0 | 83.9605 | 33.8097 | 0 | 81.3566 | 29% | 0 | 0 | 10% | 0 | 31.3974
629 | 0 | 0 | 0 | 2.9 | 7 | 0 | 0 | 0 | 0 | 86.6697 | 34.9644 | 0 | 84.6818 | 23% | 0 | 0 | 10% | 0 | 32.508
630 | 0 | 0 | 0 | 2.8 | 7.4 | 0 | 0 | 0 | 0 | 89.4399 | 36.1271 | 0 | 88.0863 | 16% | 0 | 0 | 10% | 0 | 33.6447
631 | 0 | 0 | 0 | 1.7 | 8.5 | 0 | 0 | 0 | 0 | 96.4362 | 39.0568 | 0 | 96.6033 | 9% | 0 | 0 | 10% | 0 | 36.5561
632 | 156 | 25 | 12 | 2.8 | 9.7 | 0 | 10.5393 | 0 | 0 | 103.2211 | 41.8707 | 0 | 104.6574 | 1% | 0 | 0 | 10% | 0 | 39.3823
633 | 697 | 187 | 37 | 4.7 | 13 | 98.0506 | 25.2042 | 25.3828 | 0 | 46.0315 | 16.9222 | 59.6405 | 8.3505 | 5% | 0 | 0 | 10% | 0 | 40.6552
634 | 893 | 373 | 48 | 6.4 | 16.4 | 201.3259 | 0 | 50.4315 | 0 | 43.9689 | 15.8993 | 157.6411 | 0 | 17% | 23.7212 | 0 | 42.26% | 0 | 40.3965
635 | 965 | 519 | 54 | 8.8 | 18.7 | 242.9725 | 0 | 53.1782 | 14.5982 | 42.5909 | 15.204 | 201.2701 | 0 | 32% | 25 | 0 | 76.26% | 0 | 40.7805
636 | 1002 | 615 | 61 | 10.1 | 20.1 | 263.6111 | 0 | 38.1764 | 36.9236 | 42.6047 | 15.1231 | 222.0499 | 0 | 48% | 10.1023 | 0 | 90% | 0 | 40.3748
637 | 991 | 642 | 74 | 10.4 | 20 | 263.5574 | 0 | 26.0561 | 49.0439 | 42.6079 | 15.1307 | 221.9697 | 0 | 65% | 0 | 0 | 90% | 0 | 38.3423
638 | 989 | 642 | 107 | 8.7 | 20.1 | 258.8605 | 0 | 24.9581 | 50.1419 | 42.6096 | 15.1248 | 217.1403 | 0 | 81% | 0 | 0 | 90% | 0 | 37.2561
639 | 780 | 475 | 119 | 5.6 | 19.6 | 191.5493 | 0 | 23.2881 | 35.516 | 42.6101 | 15.1563 | 149.8472 | 0 | 92% | 0 | 0 | 90% | 0 | 37.3
640 | 841 | 330 | 49 | 7 | 17.6 | 157.5721 | 26.5286 | 22.7254 | 20.9481 | 42.609 | 15.2732 | 115.5255 | 0 | 100% | 0 | 0 | 90% | 0 | 39.7815
641 | 643 | 147 | 33 | 6.9 | 15.7 | 42.1533 | 71.9843 | 19.3563 | 0 | 42.6078 | 15.3709 | 0 | 0 | 100% | 0 | 7.8722 | 77.4% | 0 | 43.3119
642 | 96 | 11 | 5 | 6.1 | 13.4 | 0 | 0 | 0 | 0 | 58.5386 | 22.2657 | 0 | 57.0603 | 96% | 0 | 25 | 37.4% | 0 | 45.2066
643 | 0 | 0 | 0 | 2.1 | 11.9 | 0 | 0 | 0 | 0 | 78.7884 | 31.0506 | 0 | 79.8555 | 90% | 0 | 17.1278 | 10% | 0 | 45.2389
644 | 0 | 0 | 0 | 1 | 11.1 | 0 | 0 | 0 | 0 | 113.9829 | 46.3014 | 0 | 118.186 | 81% | 0 | 0 | 10% | 0 | 43.7067
645 | 0 | 0 | 0 | 0.8 | 9.2 | 0 | 0 | 0 | 0 | 103.6574 | 42.0714 | 0 | 103.9118 | 73% | 0 | 0 | 10% | 0 | 39.9491
646 | 0 | 0 | 0 | 1 | 7.7 | 0 | 0 | 0 | 0 | 95.2674 | 38.5905 | 0 | 93.7168 | 66% | 0 | 0 | 10% | 0 | 36.5458
647 | 0 | 0 | 0 | 1 | 7.7 | 0 | 0 | 0 | 0 | 89.3297 | 36.0671 | 0 | 86.6835 | 60% | 0 | 0 | 10% | 0 | 33.9888
648 | 0 | 0 | 0 | 1.5 | 7 | 0 | 0 | 0 | 0 | 86.0814 | 34.713 | 0 | 83.0755 | 53% | 0 | 0 | 10% | 0 | 32.5574
649 | 0 | 0 | 0 | 1.3 | 6.3 | 0 | 0 | 0 | 0 | 84.9916 | 34.272 | 0 | 82.042 | 47% | 0 | 0 | 10% | 0 | 32.0353
650 | 0 | 0 | 0 | 1.6 | 7.7 | 0 | 0 | 0 | 0 | 85.6509 | 34.5094 | 0 | 83.0234 | 41% | 0 | 0 | 10% | 0 | 32.2028
651 | 0 | 0 | 0 | 1.2 | 7.7 | 0 | 0 | 0 | 0 | 88.8514 | 35.8652 | 0 | 86.9973 | 34% | 0 | 0 | 10% | 0 | 33.5033
652 | 0 | 0 | 0 | 1.2 | 6.8 | 0 | 0 | 0 | 0 | 99.7772 | 40.5202 | 0 | 100.2227 | 27% | 0 | 0 | 10% | 0 | 38.1178
653 | 0 | 0 | 0 | 1.6 | 5.4 | 0 | 0 | 0 | 0 | 116.327 | 47.5126 | 0 | 119.886 | 18% | 0 | 0 | 10% | 0 | 45.1187
654 | 0 | 0 | 0 | 1.5 | 5.9 | 0 | 0 | 0 | 0 | 126.1728 | 51.5987 | 0 | 131.1664 | 8% | 0 | 0 | 10% | 0 | 49.2865
655 | 0 | 0 | 0 | 1.2 | 6.3 | 0 | 0 | 0 | 0 | 102.7708 | 42.026 | 0 | 106.515 | 0% | 0 | 0 | 10% | 0 | 39.8768
656 | 213 | 30 | 11 | 1.3 | 6.4 | 0 | 15.2635 | 0.24383 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.686
657 | 730 | 193 | 36 | 1.4 | 10.6 | 105.434 | 26.8626 | 26.9192 | 0 | 0 | 0 | 101.6489 | 0 | 8% | 0 | 0 | 10% | 0 | 25.3069
658 | 831 | 367 | 61 | 0.6 | 13.7 | 190.5678 | 0 | 48.5098 | 0 | 0 | 0 | 188.3912 | 0 | 22% | 0 | 0 | 10% | 0 | 46.393
659 | 896 | 503 | 67 | 2.1 | 15.6 | 229.4259 | 0 | 64.802 | 0 | 0 | 0 | 227.8029 | 0 | 39% | 13.302 | 0 | 28.09% | 0 | 48.9972
660 | 1001 | 617 | 60 | 7.1 | 17.7 | 266.1869 | 0 | 75.1 | 0 | 0 | 0 | 264.7142 | 0 | 60% | 24.4573 | 0 | 61.35% | 0 | 47.7553
661 | 914 | 634 | 103 | 8.3 | 18.7 | 243.4725 | 0 | 72.1848 | 2.9152 | 0 | 0 | 242.3551 | 0 | 78% | 21.0642 | 0 | 90% | 0 | 48.3886
662 | 942 | 592 | 77 | 6.6 | 19.9 | 247.6716 | 0 | 50.729 | 23.7562 | 0 | 0 | 246.4839 | 0 | 97% | 0 | 0 | 90% | 0 | 47.9165
663 | 946 | 492 | 53 | 7.8 | 20.3 | 84.3924 | 175.8081 | 48.3419 | 14.979 | 42.5975 | 1.0972 | 43.9579 | 0 | 100% | 0 | 0 | 90% | 0 | 47.7626
664 | 862 | 341 | 49 | 9.3 | 19.7 | 42.1588 | 170.1774 | 33.552 | 11.1551 | 42.5958 | 15.145 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 49.4086
665 | 577 | 141 | 34 | 7.9 | 18.2 | 42.1581 | 58.042 | 16.8962 | 0 | 42.5934 | 15.2341 | 0 | 0 | 100% | 0 | 17.2214 | 62.45% | 0 | 50.0636
666 | 46 | 10 | 6 | 6.4 | 15.5 | 0 | 0 | 0 | 0 | 69.8913 | 27.1199 | 0 | 68.6532 | 95% | 0 | 25 | 22.45% | 0 | 50.0659
667 | 0 | 0 | 0 | 3.8 | 13.7 | 0 | 0 | 0 | 0 | 110.1086 | 44.3573 | 0 | 115.741 | 86% | 0 | 7.7786 | 10% | 0 | 49.2238
668 | 0 | 0 | 0 | 4.7 | 12.7 | 0 | 0 | 0 | 0 | 121.0084 | 49.1298 | 0 | 124.5272 | 77% | 0 | 0 | 10% | 0 | 46.9899
669 | 0 | 0 | 0 | 2.1 | 12 | 0 | 0 | 0 | 0 | 109.3138 | 44.3007 | 0 | 109.2811 | 69% | 0 | 0 | 10% | 0 | 42.4824
670 | 0 | 0 | 0 | 1.1 | 10.3 | 0 | 0 | 0 | 0 | 101.09 | 40.9375 | 0 | 99.5198 | 61% | 0 | 0 | 10% | 0 | 39.1537
671 | 0 | 0 | 0 | 2.1 | 10.6 | 0 | 0 | 0 | 0 | 95.0851 | 38.3963 | 0 | 92.7084 | 54% | 0 | 0 | 10% | 0 | 36.5694
672 | 0 | 0 | 0 | 1.7 | 10.5 | 0 | 0 | 0 | 0 | 91.5784 | 36.9126 | 0 | 88.7503 | 47% | 0 | 0 | 10% | 0 | 35.0173
673 | 0 | 0 | 0 | 1.9 | 10.3 | 0 | 0 | 0 | 0 | 90.4117 | 36.426 | 0 | 87.594 | 41% | 0 | 0 | 10% | 0 | 34.4545
674 | 0 | 0 | 0 | 1.6 | 10.7 | 0 | 0 | 0 | 0 | 90.2748 | 36.3495 | 0 | 87.643 | 34% | 0 | 0 | 10% | 0 | 34.3108
675 | 0 | 0 | 0 | 2 | 9.3 | 0 | 0 | 0 | 0 | 92.4883 | 37.3548 | 0 | 90.5041 | 27% | 0 | 0 | 10% | 0 | 35.258
676 | 0 | 0 | 0 | 1.3 | 8.3 | 0 | 0 | 0 | 0 | 102.0387 | 41.425 | 0 | 101.9212 | 19% | 0 | 0 | 10% | 0 | 39.28
677 | 0 | 0 | 0 | 1.7 | 7.6 | 0 | 0 | 0 | 0 | 117.7889 | 48.0503 | 0 | 120.5179 | 10% | 0 | 0 | 10% | 0 | 45.8903
678 | 0 | 0 | 0 | 1.3 | 7.1 | 0 | 0 | 0 | 0 | 126.2193 | 51.5784 | 0 | 130.2063 | 0% | 0 | 0 | 10% | 0 | 49.4699
679 | 0 | 0 | 0 | 1.3 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8385
680 | 104 | 30 | 22 | 2 | 6.9 | 0 | 7.8988 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8248
681 | 37 | 96 | 88 | 1.8 | 9.9 | 0 | 8.0209 | 2.6803 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.86904
682 | 20 | 160 | 149 | 3.5 | 12.1 | 0 | 5.3522 | 5.1091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.3111
683 | 21 | 199 | 185 | 4.5 | 12.6 | 0 | 6.2032 | 7.6961 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 5.911
684 | 91 | 242 | 185 | 2.9 | 13.9 | 0 | 28.0436 | 16.587 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 14.8146
685 | 742 | 544 | 109 | 6.1 | 17.4 | 159.3587 | 39.922 | 65.0122 | 0 | 0 | 0 | 152.2467 | 0 | 12% | 14.0367 | 0 | 29.09% | 0 | 48.9224
686 | 720 | 509 | 111 | 11.7 | 18.3 | 180.13 | 0 | 61.2646 | 0.033724 | 42.4275 | 1.2941 | 139.0941 | 0 | 23% | 15.0462 | 0 | 49.55% | 0 | 44.9743
687 | 434 | 365 | 153 | 12 | 17.1 | 92.0627 | 1.49e-14 | 38.1044 | 0 | 42.513 | 15.266 | 51.9489 | 0 | 27% | 2.9623 | 0 | 53.58% | 0 | 49.1191
688 | 515 | 272 | 94 | 11.4 | 16 | 98.4013 | 0 | 29.8542 | 0 | 42.5286 | 15.3281 | 57.6227 | 0 | 31% | 0 | 6.1954 | 43.67% | 0 | 50.0364
689 | 351 | 142 | 70 | 12.4 | 14.6 | 0 | 0 | 12.0173 | 0 | 48.7427 | 18.078 | 0 | 46.0997 | 28% | 0 | 21.043 | 10% | 0 | 50.0104
690 | 3 | 7 | 7 | 10.6 | 12.9 | 0 | 0 | 0 | 0 | 127.3506 | 51.7541 | 0 | 132.2348 | 18% | 0 | 0 | 10% | 0 | 49.5417
691 | 0 | 0 | 0 | 7.1 | 12.6 | 0 | 0 | 0 | 0 | 127.3015 | 51.7539 | 0 | 131.5115 | 8% | 0 | 0 | 10% | 0 | 49.6639
692 | 0 | 0 | 0 | 0 | 12.5 | 0 | 0 | 0 | 0 | 97.3414 | 39.5417 | 0 | 99.469 | 0% | 0 | 0 | 10% | 0 | 37.5995
693 | 0 | 0 | 0 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7607
694 | 0 | 0 | 0 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7488
695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7373
696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7257
697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7142
698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.703
699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.692
700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6813
701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6707
702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6603
703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6501
704 | 0 | 14 | 14 | 5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6399
705 | 8 | 95 | 91 | 8.6 | 11.7 | 0 | 1.742 | 1.0501 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.57975
706 | 283 | 296 | 182 | 10 | 13 | 0 | 64.9496 | 26.7443 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 25.1256
707 | 451 | 458 | 230 | 11 | 14.3 | 99.225 | 0 | 48.5135 | 0 | 0 | 0 | 93.2405 | 0 | 7% | 0 | 0 | 10% | 0 | 47.2244
708 | 516 | 525 | 227 | 11.8 | 14.9 | 122.9764 | 0 | 57.309 | 0 | 0 | 0 | 120.0312 | 0 | 17% | 6.7854 | 0 | 19.23% | 0 | 48.9977
709 | 282 | 470 | 298 | 9.6 | 14.8 | 58.4175 | 0 | 44.9395 | 0 | 42.3119 | 0 | 18.6759 | 0 | 18% | 9.9381 | 0 | 32.74% | 0 | 33.5152
710 | 168 | 372 | 273 | 8.4 | 15.5 | 0 | 51.444 | 31.664 | 0 | 43.9888 | 9.8628 | 0 | 40.5379 | 15% | 0 | 7.8231 | 20.23% | 0 | 48.3319
711 | 132 | 283 | 214 | 7.8 | 15.7 | 0 | 38.4496 | 21.36 | 0 | 59.82 | 22.8321 | 0 | 55.999 | 11% | 0 | 6.3918 | 10% | 0 | 48.7482
712 | 1 | 119 | 117 | 5.9 | 14.6 | 0 | 0.25819 | 1.9687 | 0 | 123.5249 | 50.0451 | 0 | 126.6507 | 1% | 0 | 0 | 10% | 0 | 50.0132
713 | 0 | 53 | 52 | 6.5 | 13.6 | 0 | 0 | 0 | 0 | 13.1412 | 5.3352 | 0 | 13.4937 | 0% | 0 | 0 | 10% | 0 | 3.5698
714 | 0 | 4 | 4 | 6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7343
715 | 0 | 0 | 0 | 6.8 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7226
716 | 0 | 0 | 0 | 8 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7112
717 | 0 | 0 | 0 | 7.3 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7
718 | 0 | 0 | 0 | 4.7 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.689
719 | 0 | 0 | 0 | 5.9 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6782
720 | 0 | 0 | 0 | 5 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6677
721 | 0 | 0 | 0 | 7.7 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6573
722 | 0 | 0 | 0 | 6 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6471
723 | 0 | 0 | 0 | 8.7 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6371
724 | 0 | 0 | 0 | 7 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6274
725 | 0 | 0 | 0 | 4 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6178
726 | 0 | 0 | 0 | 4.8 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6084
727 | 0 | 0 | 0 | 4 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5992
728 | 0 | 15 | 15 | 1.4 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5901
729 | 0 | 44 | 44 | 2.1 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5813
730 | 177 | 203 | 134 | 3.7 | 13.1 | 0 | 47.6426 | 14.8069 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 13.2345
731 | 0 | 156 | 154 | 3.4 | 14.6 | 0 | 0 | 4.0035 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 2.4397
732 | 97 | 307 | 247 | 7.2 | 17.3 | 0 | 29.9983 | 21.5596 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 20.0043
733 | 356 | 508 | 290 | 10.2 | 18.9 | 64.8664 | 17.6598 | 49.3067 | 1.4089 | 0 | 0 | 60.0062 | 0 | 5% | 0 | 0 | 10% | 0 | 48.1102
734 | 529 | 457 | 159 | 10.4 | 19.3 | 127.0973 | 0 | 49.386 | 1.6466 | 0 | 0 | 122.3582 | 0 | 15% | 0 | 0 | 10% | 0 | 47.8261
735 | 908 | 492 | 59 | 9.4 | 19.5 | 223.7751 | 0 | 61.7905 | 0 | 42.1294 | 0 | 180.6344 | 0 | 29% | 15.5809 | 0 | 31.19% | 0 | 43.2174
736 | 677 | 336 | 93 | 10.1 | 18.6 | 139.7862 | -1.57e-14 | 39.1157 | 0 | 42.6063 | 7.2624 | 98.9865 | 0 | 36% | 3.3295 | 0 | 35.72% | 0 | 41.0456
737 | 228 | 115 | 78 | 9.7 | 16.9 | 0 | 46.1848 | 8.697 | 0 | 68.0281 | 26.2074 | 0 | 65.7299 | 31% | 0 | 16.0738 | 10% | 0 | 50.078
738 | 51 | 14 | 10 | 8 | 16.2 | 0 | 0.49476 | 0 | 0 | 126.9631 | 51.3383 | 0 | 130.5708 | 21% | 0 | 0 | 10% | 0 | 49.3914
739 | 0 | 0 | 0 | 9.2 | 15 | 0 | 0 | 0 | 0 | 126.9298 | 51.4246 | 0 | 130.0106 | 11% | 0 | 0 | 10% | 0 | 49.5691
740 | 0 | 0 | 0 | 8.9 | 14.8 | 0 | 0 | 0 | 0 | 120.5283 | 48.785 | 0 | 121.9914 | 2% | 0 | 0 | 10% | 0 | 47.009
741 | 0 | 0 | 0 | 5.2 | 13.8 | 0 | 0 | 0 | 0 | 22.4674 | 9.0853 | 0 | 22.369 | 0% | 0 | 0 | 10% | 0 | 7.4828
742 | 0 | 0 | 0 | 4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5639
743 | 0 | 0 | 0 | 4.9 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5555
744 | 0 | 0 | 0 | 5.9 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5472
745 | 0 | 0 | 0 | 7 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5392
746 | 0 | 0 | 0 | 7.5 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5312
747 | 0 | 0 | 0 | 5.2 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5235
748 | 0 | 0 | 0 | 5.5 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5159
749 | 0 | 0 | 0 | 7.2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5084
750 | 0 | 0 | 0 | 5.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5011
751 | 0 | 0 | 0 | 7.6 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4939
752 | 51 | 31 | 27 | 9.8 | 14.1 | 0 | 4.5876 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4868
753 | 478 | 196 | 79 | 8.8 | 14.8 | 60.7478 | 16.7076 | 20.0751 | 0 | 0 | 0 | 57.1781 | 0 | 5% | 0 | 0 | 10% | 0 | 18.9234
754 | 59 | 150 | 129 | 7.7 | 14.7 | 0 | 15.9278 | 6.8254 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | 6.2889
755 | 10 | 136 | 129 | 7.4 | 14.7 | 0 | 2.9668 | 2.8779 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | 1.4043
756 | 245 | 316 | 171 | 12.2 | 15.1 | 0 | 0 | 29.1889 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | 27.7222
757 | 776 | 593 | 129 | 13.3 | 16.6 | 0 | 0 | 71.3 | 0 | 0 | 0 | 0 | 0 | 5% | 22.3729 | 0 | 40.43% | 0 | 47.4672
758 | 950 | 606 | 72 | 12.1 | 16.8 | 0 | 0 | 73.402 | 1.698 | 0 | 0 | 0 | 0 | 5% | 25 | 0 | 74.43% | 0 | 46.9489
759 | 858 | 480 | 71 | 13.2 | 15.2 | 0 | 0 | 59.6532 | 0.78156 | 0 | 0 | 0 | 0 | 5% | 11.4506 | 0 | 90% | 0 | 46.7564
760 | 855 | 352 | 51 | 12.8 | 14.5 | 0 | 0 | 45.6822 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 3.7311 | 84.03% | 0 | 47.9731
761 | 650 | 165 | 36 | 11 | 13.3 | 80.0978 | 21.8059 | 20.3823 | 0 | 0 | 0 | 75.913 | 0 | 11% | 0 | 25 | 44.03% | 0 | 44.0642
762 | 46 | 11 | 7 | 12.5 | 11.8 | 0 | 0 | 0 | 0 | 35.7716 | 0 | 0 | 32.5463 | 8% | 0 | 21.2689 | 10% | 0 | 20.316
763 | 0 | 0 | 0 | 10.7 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4946
764 | 0 | 0 | 0 | 10.6 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.487
765 | 0 | 0 | 0 | 6.9 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4797
766 | 0 | 0 | 0 | 9.9 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4724
767 | 0 | 0 | 0 | 10.6 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4652
768 | 0 | 0 | 0 | 9.1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4583
769 | 0 | 0 | 0 | 7.8 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4514
770 | 0 | 0 | 0 | 11.7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4447
771 | 0 | 0 | 0 | 6.3 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4382
772 | 0 | 0 | 0 | 5.5 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4318
773 | 0 | 0 | 0 | 6.2 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4255
774 | 0 | 0 | 0 | 6.8 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4193
775 | 0 | 0 | 0 | 7.2 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -1.4133
776 | 226 | 32 | 14 | 6.7 | 8.3 | 0 | 21.4681 | 0.76812 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | -0.63925
777 | 304 | 117 | 47 | 6 | 9 | 0 | 56.08 | 10.2048 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | 8.8041
778 | 657 | 327 | 65 | 6.2 | 10.4 | 144.9895 | 0 | 38.4766 | 0 | 0 | 0 | 136.9908 | 0 | 19% | 0 | 0 | 10% | 0 | 36.7651
779 | 897 | 558 | 103 | 6 | 11.4 | 228.0906 | 0 | 70.0982 | 0 | 42.0534 | 0 | 184.8625 | 0 | 33% | 21.6564 | 0 | 39.45% | 0 | 45.3866
780 | 945 | 630 | 83 | 3.9 | 11.8 | 255.3226 | 0 | 64.7628 | 10.3372 | 42.3416 | 7.6277 | 213.696 | 0 | 50% | 25 | 0 | 73.45% | 0 | 44.2941
781 | 869 | 621 | 97 | 4.5 | 12.3 | 234.6677 | 0 | 41.6989 | 33.4011 | 42.4308 | 15.4516 | 193.5561 | 0 | 65% | 12.1671 | 0 | 90% | 0 | 42.3145
782 | 968 | 638 | 88 | 4.9 | 12.7 | 258.9776 | 0 | 28.8817 | 46.2183 | 42.4661 | 15.4493 | 217.6186 | 0 | 82% | 0 | 0 | 90% | 0 | 41.4177
783 | 514 | 362 | 115 | 4.2 | 11.7 | 121.7181 | 0 | 27.1317 | 13.513 | 42.4993 | 15.4989 | 81.19 | 0 | 88% | 0 | 0 | 90% | 0 | 41.032
784 | 712 | 332 | 70 | 7.3 | 11.5 | 152.0127 | 0 | 29.0082 | 10.7804 | 42.5082 | 15.5095 | 110.1463 | 0 | 96% | 0 | 0 | 90% | 0 | 42.6469
785 | 569 | 162 | 49 | 6.1 | 10.2 | 88.8336 | 0 | 18.8218 | 0 | 42.518 | 15.5593 | 47.0269 | 0 | 99% | 0 | 10.2906 | 73.53% | 0 | 45.7424
786 | 12 | 8 | 7 | 8.7 | 8.6 | 0 | 0.25432 | 0 | 0 | 61.1457 | 23.609 | 0 | 59.7213 | 95% | 0 | 25 | 33.53% | 0 | 46.5554
787 | 0 | 0 | 0 | 5.8 | 7.9 | 0 | 0 | 0 | 0 | 86.5164 | 34.5473 | 0 | 88.6311 | 89% | 0 | 14.7094 | 10% | 0 | 46.3153
788 | 0 | 0 | 0 | 5.7 | 7.9 | 0 | 0 | 0 | 0 | 115.1688 | 46.9465 | 0 | 119.2544 | 80% | 0 | 0 | 10% | 0 | 44.4452
789 | 0 | 0 | 0 | 3.4 | 7.7 | 0 | 0 | 0 | 0 | 107.3427 | 43.6795 | 0 | 108.1115 | 71% | 0 | 0 | 10% | 0 | 41.6018
790 | 0 | 0 | 0 | 2.5 | 8.2 | 0 | 0 | 0 | 0 | 99.9047 | 40.5285 | 0 | 98.9041 | 64% | 0 | 0 | 10% | 0 | 38.5504
791 | 0 | 0 | 0 | 5.2 | 8 | 0 | 0 | 0 | 0 | 92.2801 | 37.3172 | 0 | 89.9578 | 57% | 0 | 0 | 10% | 0 | 35.3321
792 | 0 | 0 | 0 | 5.7 | 7.4 | 0 | 0 | 0 | 0 | 87.3596 | 35.2449 | 0 | 84.2596 | 51% | 0 | 0 | 10% | 0 | 33.1981
793 | 0 | 0 | 0 | 4.6 | 7 | 0 | 0 | 0 | 0 | 84.2687 | 33.9508 | 0 | 80.8909 | 44% | 0 | 0 | 10% | 0 | 31.822
794 | 0 | 0 | 0 | 2.8 | 6.7 | 0 | 0 | 0 | 0 | 83.6238 | 33.6872 | 0 | 80.3874 | 38% | 0 | 0 | 10% | 0 | 31.4755
795 | 0 | 0 | 0 | 2.7 | 6.6 | 0 | 0 | 0 | 0 | 84.2377 | 33.9493 | 0 | 81.3091 | 32% | 0 | 0 | 10% | 0 | 31.667
796 | 0 | 0 | 0 | 3.7 | 6.3 | 0 | 0 | 0 | 0 | 85.9257 | 34.6713 | 0 | 83.4579 | 26% | 0 | 0 | 10% | 0 | 32.3325
797 | 0 | 0 | 0 | 2.6 | 5.9 | 0 | 0 | 0 | 0 | 88.7815 | 35.8936 | 0 | 86.9899 | 19% | 0 | 0 | 10% | 0 | 33.5129
798 | 0 | 0 | 0 | 3.1 | 6.5 | 0 | 0 | 0 | 0 | 91.0128 | 36.8271 | 0 | 89.764 | 13% | 0 | 0 | 10% | 0 | 34.4241
799 | 0 | 0 | 0 | 3 | 5.9 | 0 | 0 | 0 | 0 | 98.3177 | 39.9361 | 0 | 98.5608 | 5% | 0 | 0 | 10% | 0 | 37.5142
800 | 281 | 41 | 15 | 3.4 | 5.7 | 0 | 28.16 | 1.6799 | 0 | 70.0415 | 28.4923 | 0 | 70.608 | 0% | 0 | 0 | 10% | 0 | 27.8176
801 | 751 | 215 | 39 | 2.4 | 7.5 | 111.9233 | 28.7159 | 28.5108 | 0 | 0 | 0 | 107.8475 | 0 | 8% | 0 | 0 | 10% | 0 | 26.7927
802 | 895 | 399 | 50 | 3.3 | 8.8 | 208.9699 | -2.98e-14 | 52.315 | 0 | 0 | 0 | 206.6353 | 0 | 24% | 9.5333 | 0 | 22.96% | 0 | 40.5236
803 | 975 | 550 | 54 | 3.9 | 9.8 | 252.6175 | 0 | 69.4074 | 1.6057 | 0 | 0 | 250.9445 | 0 | 43% | 25 | 0 | 56.96% | 0 | 41.7181
804 | 1005 | 642 | 56 | 4.9 | 10.7 | 272.0678 | 0 | 68.6865 | 6.4135 | 0 | 0 | 270.6879 | 0 | 63% | 24.2903 | 0 | 90% | 0 | 41.476
805 | 1012 | 669 | 58 | 4.8 | 11.7 | 276.1005 | 0 | 42.5856 | 32.5144 | 0 | 0 | 274.8673 | 0 | 83% | 0 | 0 | 90% | 0 | 39.5725
806 | 1001 | 629 | 56 | 5.1 | 12.1 | 221.0458 | 52.5633 | 41.043 | 34.057 | 0 | 0 | 220.1077 | 0 | 100% | 0 | 0 | 90% | 0 | 38.4901
807 | 961 | 524 | 54 | 4.3 | 12.4 | 0 | 268.5234 | 39.6093 | 27.2964 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.1025
808 | 883 | 368 | 47 | 3.3 | 12.4 | 40.9329 | 183.4612 | 40.1912 | 7.1982 | 42.5925 | 0.97597 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.0793
809 | 711 | 179 | 34 | 3.7 | 11.5 | 42.1586 | 94.8264 | 22.7653 | 0 | 42.5903 | 15.5394 | 0 | 0 | 100% | 0 | 5.554 | 81.11% | 0 | 44.5722
810 | 176 | 22 | 8 | 2.3 | 9.5 | 0 | 4.7641 | 0 | 0 | 61.6928 | 23.808 | 0 | 60.2716 | 96% | 0 | 25 | 41.11% | 0 | 46.7562
811 | 0 | 0 | 0 | 1.7 | 8.1 | 0 | 0 | 0 | 0 | 76.5525 | 30.2532 | 0 | 77.0128 | 90% | 0 | 19.446 | 10% | 0 | 46.7713
812 | 0 | 0 | 0 | 1.7 | 6.4 | 0 | 0 | 0 | 0 | 117.1511 | 47.8246 | 0 | 122.3766 | 81% | 0 | 0 | 10% | 0 | 45.1545
813 | 0 | 0 | 0 | 1.1 | 5.4 | 0 | 0 | 0 | 0 | 107.4292 | 43.7848 | 0 | 108.3384 | 73% | 0 | 0 | 10% | 0 | 41.6703
814 | 0 | 0 | 0 | 1.7 | 4.6 | 0 | 0 | 0 | 0 | 98.0313 | 39.8421 | 0 | 96.7595 | 65% | 0 | 0 | 10% | 0 | 37.8441
815 | 0 | 0 | 0 | 0.8 | 2.9 | 0 | 0 | 0 | 0 | 91.809 | 37.244 | 0 | 89.4748 | 59% | 0 | 0 | 10% | 0 | 35.2245
816 | 0 | 0 | 0 | 1.9 | 2.7 | 0 | 0 | 0 | 0 | 88.3482 | 35.7743 | 0 | 85.5266 | 52% | 0 | 0 | 10% | 0 | 33.69
817 | 0 | 0 | 0 | 1.2 | 2 | 0 | 0 | 0 | 0 | 87.0826 | 35.2494 | 0 | 84.2582 | 46% | 0 | 0 | 10% | 0 | 33.0903
818 | 0 | 0 | 0 | 0.9 | 2.1 | 0 | 0 | 0 | 0 | 86.8359 | 35.1434 | 0 | 84.1665 | 39% | 0 | 0 | 10% | 0 | 32.9183
819 | 0 | 0 | 0 | 2.1 | 2.1 | 0 | 0 | 0 | 0 | 90.264 | 36.6005 | 0 | 88.4469 | 33% | 0 | 0 | 10% | 0 | 34.3168
820 | 0 | 0 | 0 | 2.8 | 2.7 | 0 | 0 | 0 | 0 | 100.9433 | 41.1132 | 0 | 101.3225 | 25% | 0 | 0 | 10% | 0 | 38.7882
821 | 0 | 0 | 0 | 2.5 | 1.8 | 0 | 0 | 0 | 0 | 118.3739 | 48.4482 | 0 | 121.9643 | 16% | 0 | 0 | 10% | 0 | 46.1251
822 | 0 | 0 | 0 | 1.9 | 1.2 | 0 | 0 | 0 | 0 | 127.3933 | 52.2215 | 0 | 132.2326 | 6% | 0 | 0 | 10% | 0 | 49.9773
823 | 0 | 0 | 0 | 1.4 | 1 | 0 | 0 | 0 | 0 | 74.8979 | 30.7047 | 0 | 77.3972 | 0% | 0 | 0 | 10% | 0 | 28.6663
824 | 299 | 43 | 14 | 2.5 | 2 | 0 | 31.5791 | 1.9357 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.045775
825 | 789 | 223 | 37 | 1.3 | 6.1 | 119.2 | 30.7031 | 30.1471 | 0 | 0 | 0 | 114.8281 | 0 | 9% | 0 | 0 | 10% | 0 | 28.4186
826 | 929 | 411 | 47 | 0.9 | 9.7 | 219.5241 | 0 | 54.0577 | 0 | 0 | 0 | 217.2149 | 0 | 25% | 2.5577 | 0 | 13.48% | 0 | 49.118
827 | 989 | 558 | 52 | 3.4 | 11.2 | 257.2685 | 0 | 71.6383 | 0 | 0 | 0 | 255.6584 | 0 | 45% | 20.1383 | 0 | 40.87% | 0 | 48.7296
828 | 1012 | 648 | 55 | 3.5 | 12.8 | 275.4095 | 0 | 75.1 | 0 | 0 | 0 | 274.0492 | 0 | 66% | 23.6 | 0 | 72.96% | 0 | 48.5064
829 | 1006 | 671 | 59 | 3.9 | 13.6 | 275.4651 | 2.9e-14 | 64.0178 | 11.0822 | 0 | 0 | 274.2728 | 0 | 87% | 12.5275 | 0 | 90% | 0 | 48.4223
830 | 992 | 629 | 58 | 4.6 | 14.3 | 177.8687 | 98.1477 | 50.9356 | 24.1644 | 0 | 0 | 177.1184 | 0 | 100% | 0 | 0 | 90% | 0 | 48.7561
831 | 950 | 523 | 54 | 4.8 | 14.3 | 40.9288 | 231.8103 | 48.7331 | 17.0735 | 42.5966 | 0.84443 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 48.4995
832 | 863 | 365 | 48 | 4.4 | 14.1 | 42.1584 | 177.4111 | 33.6106 | 12.5277 | 42.5942 | 15.4393 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 49.7628
833 | 669 | 176 | 36 | 4.3 | 12.8 | 42.1585 | 86.335 | 21.2843 | 0 | 42.5918 | 15.4912 | 0 | 0 | 100% | 0 | 12.5835 | 69.87% | 0 | 50.0722
834 | 157 | 22 | 9 | 3.3 | 10.4 | 0 | 5.1843 | 0 | 0 | 69.2659 | 27.103 | 0 | 68.0166 | 95% | 0 | 25 | 29.87% | 0 | 50.0564
835 | 0 | 0 | 0 | 1.7 | 8.3 | 0 | 0 | 0 | 0 | 99.4902 | 40.1121 | 0 | 103.1739 | 87% | 0 | 12.4165 | 10% | 0 | 49.6227
836 | 0 | 0 | 0 | 0.5 | 6.6 | 0 | 0 | 0 | 0 | 123.8494 | 50.6054 | 0 | 128.7597 | 78% | 0 | 0 | 10% | 0 | 48.2841
837 | 0 | 0 | 0 | 0.9 | 5.3 | 0 | 0 | 0 | 0 | 111.6605 | 45.5574 | 0 | 112.2588 | 69% | 0 | 0 | 10% | 0 | 43.681
838 | 0 | 0 | 0 | 1.2 | 4.4 | 0 | 0 | 0 | 0 | 103.85 | 42.3061 | 0 | 102.8582 | 61% | 0 | 0 | 10% | 0 | 40.5021
839 | 0 | 0 | 0 | 2.4 | 5.8 | 0 | 0 | 0 | 0 | 96.9163 | 39.3426 | 0 | 94.7836 | 54% | 0 | 0 | 10% | 0 | 37.5233
840 | 0 | 0 | 0 | 2.2 | 5.6 | 0 | 0 | 0 | 0 | 93.0621 | 37.7201 | 0 | 90.4875 | 47% | 0 | 0 | 10% | 0 | 35.8414
841 | 0 | 0 | 0 | 1.2 | 4.6 | 0 | 0 | 0 | 0 | 91.5822 | 37.1127 | 0 | 88.9162 | 40% | 0 | 0 | 10% | 0 | 35.1661
842 | 0 | 0 | 0 | 0.7 | 4.1 | 0 | 0 | 0 | 0 | 91.5376 | 37.1051 | 0 | 89.066 | 34% | 0 | 0 | 10% | 0 | 35.0949
843 | 0 | 0 | 0 | 1.1 | 3.7 | 0 | 0 | 0 | 0 | 93.9091 | 38.1271 | 0 | 92.1322 | 27% | 0 | 0 | 10% | 0 | 36.0621
844 | 0 | 0 | 0 | 1.8 | 4.3 | 0 | 0 | 0 | 0 | 103.3881 | 42.1147 | 0 | 103.3902 | 19% | 0 | 0 | 10% | 0 | 40.0061
845 | 0 | 0 | 0 | 1.5 | 3.8 | 0 | 0 | 0 | 0 | 119.2431 | 48.7681 | 0 | 122.0344 | 10% | 0 | 0 | 10% | 0 | 46.6457
846 | 0 | 0 | 0 | 1.1 | 4.4 | 0 | 0 | 0 | 0 | 127.3053 | 52.1146 | 0 | 131.2777 | 0% | 0 | 0 | 10% | 0 | 50.044
847 | 0 | 0 | 0 | 0.9 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7994
848 | 282 | 43 | 15 | 0.2 | 3.8 | 0 | 31.3572 | 1.7197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.066915
849 | 740 | 215 | 38 | 0.6 | 10.5 | 112.0638 | 28.5611 | 27.6437 | 0 | 0 | 0 | 107.7169 | 0 | 8% | 0 | 0 | 10% | 0 | 25.9949
850 | 898 | 402 | 46 | 0.7 | 14 | 212.4669 | 0 | 51.2855 | 0 | 0 | 0 | 209.9908 | 0 | 24% | 0 | 0 | 10% | 0 | 48.9618
851 | 964 | 549 | 51 | 1 | 15.9 | 252.137 | 0 | 68.6561 | 0 | 0 | 0 | 250.4473 | 0 | 43% | 17.1561 | 0 | 33.33% | 0 | 48.7713
852 | 992 | 639 | 54 | 2.3 | 17.4 | 270.9288 | 0 | 75.1 | 0 | 0 | 0 | 269.5236 | 0 | 64% | 23.5209 | 0 | 65.32% | 0 | 48.6221
853 | 999 | 666 | 55 | 2.8 | 18.2 | 274.6619 | 0 | 68.8375 | 6.2625 | 0 | 0 | 273.427 | 0 | 85% | 18.1465 | 0 | 90% | 0 | 47.629
854 | 985 | 626 | 55 | 2.8 | 18.9 | 203.6638 | 69.5172 | 49.5483 | 25.5517 | 0 | 0 | 202.7864 | 0 | 100% | 0 | 0 | 90% | 0 | 47.1189
855 | 951 | 524 | 52 | 4.2 | 18.8 | 40.7802 | 232.9051 | 47.854 | 16.9705 | 42.595 | 0.13738 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 46.9115
856 | 877 | 371 | 46 | 4.6 | 18.5 | 42.1581 | 181.9945 | 32.2016 | 13.9709 | 42.5926 | 15.2163 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 48.1299
857 | 700 | 182 | 34 | 4.2 | 17 | 42.1582 | 94.2415 | 22.0047 | 0 | 42.5902 | 15.2993 | 0 | 0 | 100% | 0 | 12.0495 | 70.72% | 0 | 50.0657
858 | 185 | 24 | 9 | 2.8 | 14 | 0 | 7.2229 | 0 | 0 | 69.6639 | 27.1018 | 0 | 68.4219 | 95% | 0 | 25 | 30.72% | 0 | 50.0489
859 | 0 | 0 | 0 | 1.6 | 10.5 | 0 | 0 | 0 | 0 | 98.3606 | 39.5368 | 0 | 101.8336 | 88% | 0 | 12.9505 | 10% | 0 | 49.5839
860 | 0 | 0 | 0 | 0.9 | 8.6 | 0 | 0 | 0 | 0 | 122.9625 | 50.1609 | 0 | 127.8044 | 78% | 0 | 0 | 10% | 0 | 47.8203
861 | 0 | 0 | 0 | 0.8 | 7.2 | 0 | 0 | 0 | 0 | 110.6742 | 45.087 | 0 | 111.1956 | 69% | 0 | 0 | 10% | 0 | 43.1905
862 | 0 | 0 | 0 | 0.8 | 6.4 | 0 | 0 | 0 | 0 | 102.7673 | 41.7948 | 0 | 101.6644 | 62% | 0 | 0 | 10% | 0 | 39.9682
863 | 0 | 0 | 0 | 0.4 | 5 | 0 | 0 | 0 | 0 | 96.1251 | 39.0305 | 0 | 93.9724 | 54% | 0 | 0 | 10% | 0 | 37.184
864 | 0 | 0 | 0 | 0.5 | 5 | 0 | 0 | 0 | 0 | 92.1253 | 37.3354 | 0 | 89.4467 | 48% | 0 | 0 | 10% | 0 | 35.4298
865 | 0 | 0 | 0 | 1.1 | 6.2 | 0 | 0 | 0 | 0 | 90.9057 | 36.7844 | 0 | 88.2062 | 41% | 0 | 0 | 10% | 0 | 34.8076
866 | 0 | 0 | 0 | 0.8 | 5.9 | 0 | 0 | 0 | 0 | 91.1679 | 36.9048 | 0 | 88.7274 | 34% | 0 | 0 | 10% | 0 | 34.8635
867 | 0 | 0 | 0 | 0.4 | 5.6 | 0 | 0 | 0 | 0 | 93.3257 | 37.834 | 0 | 91.5207 | 27% | 0 | 0 | 10% | 0 | 35.7398
868 | 0 | 0 | 0 | 0.5 | 5.9 | 0 | 0 | 0 | 0 | 102.5185 | 41.7062 | 0 | 102.4662 | 20% | 0 | 0 | 10% | 0 | 39.5687
869 | 0 | 0 | 0 | 0.3 | 5.8 | 0 | 0 | 0 | 0 | 118.3036 | 48.3239 | 0 | 121.0779 | 10% | 0 | 0 | 10% | 0 | 46.1728
870 | 0 | 0 | 0 | 0.5 | 5.3 | 0 | 0 | 0 | 0 | 126.7511 | 51.8586 | 0 | 130.7723 | 0% | 0 | 0 | 10% | 0 | 49.7597
871 | 0 | 0 | 0 | 0.6 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8275
872 | 279 | 44 | 15 | 1 | 7 | 0 | 32.6293 | 1.6385 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.17553
873 | 734 | 216 | 37 | 0.3 | 13.2 | 112.0632 | 28.2434 | 27.0332 | 0 | 0 | 0 | 107.8429 | 0 | 9% | 0 | 0 | 10% | 0 | 25.3815
874 | 877 | 398 | 48 | 0.6 | 15.7 | 207.9317 | 0 | 49.9651 | 0 | 0 | 0 | 205.5172 | 0 | 24% | 0 | 0 | 10% | 0 | 47.6823
875 | 949 | 545 | 51 | 1.6 | 17.9 | 248.0888 | 0 | 67.1683 | 0 | 0 | 0 | 246.385 | 0 | 43% | 16.6633 | 0 | 32.66% | 0 | 47.815
876 | 979 | 635 | 53 | 2.2 | 18.8 | 267.5701 | 0 | 75.1 | 0 | 0 | 0 | 266.1491 | 0 | 64% | 24.5745 | 0 | 66.08% | 0 | 47.6026
877 | 988 | 662 | 54 | 2.5 | 19.4 | 272.0767 | 0 | 67.3301 | 7.7699 | 0 | 0 | 270.8308 | 0 | 84% | 17.5857 | 0 | 90% | 0 | 46.7099
878 | 977 | 624 | 53 | 3.4 | 19.9 | 208.3597 | 61.9833 | 48.635 | 26.465 | 0 | 0 | 207.4467 | 0 | 100% | 0 | 0 | 90% | 0 | 46.1642
879 | 932 | 519 | 52 | 4 | 20 | 40.8262 | 227.7147 | 46.7088 | 16.5779 | 42.5939 | 0.13671 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.7976
880 | 859 | 367 | 46 | 5.2 | 19.3 | 42.158 | 177.8634 | 31.1477 | 13.9129 | 42.5916 | 15.1682 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 47.0277
881 | 696 | 183 | 34 | 5.4 | 17.8 | 42.1581 | 93.8817 | 21.8243 | 0 | 42.5892 | 15.2552 | 0 | 0 | 100% | 0 | 12.2727 | 70.36% | 0 | 50.0643
882 | 190 | 25 | 9 | 3.9 | 15.3 | 0 | 8.574 | 0 | 0 | 69.864 | 27.1193 | 0 | 68.6256 | 95% | 0 | 25 | 30.36% | 0 | 50.0663
883 | 0 | 0 | 0 | 1.3 | 12.8 | 0 | 0 | 0 | 0 | 98.9696 | 39.6737 | 0 | 102.5453 | 87% | 0 | 12.7273 | 10% | 0 | 49.4982
884 | 0 | 0 | 0 | 0.5 | 10 | 0 | 0 | 0 | 0 | 120.1295 | 48.9199 | 0 | 124.3563 | 78% | 0 | 0 | 10% | 0 | 46.5922
885 | 0 | 0 | 0 | 0.6 | 9 | 0 | 0 | 0 | 0 | 108.444 | 44.0879 | 0 | 108.7338 | 70% | 0 | 0 | 10% | 0 | 42.1607
886 | 0 | 0 | 0 | 0.3 | 8.5 | 0 | 0 | 0 | 0 | 100.9111 | 40.9392 | 0 | 99.6356 | 62% | 0 | 0 | 10% | 0 | 39.0715
887 | 0 | 0 | 0 | 1.5 | 8.5 | 0 | 0 | 0 | 0 | 94.7927 | 38.3635 | 0 | 92.6171 | 55% | 0 | 0 | 10% | 0 | 36.4692
888 | 0 | 0 | 0 | 1.3 | 8.2 | 0 | 0 | 0 | 0 | 91.1778 | 36.8371 | 0 | 88.469 | 48% | 0 | 0 | 10% | 0 | 34.8837
889 | 0 | 0 | 0 | 1.8 | 9.2 | 0 | 0 | 0 | 0 | 89.6785 | 36.1622 | 0 | 86.8973 | 42% | 0 | 0 | 10% | 0 | 34.1379
890 | 0 | 0 | 0 | 2.4 | 8.8 | 0 | 0 | 0 | 0 | 89.9581 | 36.297 | 0 | 87.4398 | 35% | 0 | 0 | 10% | 0 | 34.2065
891 | 0 | 0 | 0 | 1.6 | 7.8 | 0 | 0 | 0 | 0 | 92.1047 | 37.2471 | 0 | 90.2048 | 28% | 0 | 0 | 10% | 0 | 35.1026
892 | 0 | 0 | 0 | 1.6 | 7.3 | 0 | 0 | 0 | 0 | 101.1384 | 41.0797 | 0 | 101.0238 | 21% | 0 | 0 | 10% | 0 | 38.891
893 | 0 | 0 | 0 | 2.4 | 8 | 0 | 0 | 0 | 0 | 116.4162 | 47.4656 | 0 | 119.1076 | 12% | 0 | 0 | 10% | 0 | 45.2647
894 | 0 | 0 | 0 | 2 | 7.3 | 0 | 0 | 0 | 0 | 125.2027 | 51.1472 | 0 | 129.1987 | 2% | 0 | 0 | 10% | 0 | 48.9991
895 | 0 | 0 | 0 | 2.2 | 7.3 | 0 | 0 | 0 | 0 | 24.1724 | 9.8781 | 0 | 24.9241 | 0% | 0 | 0 | 10% | 0 | 7.9768
896 | 109 | 39 | 28 | 2.3 | 9.2 | 0 | 13.3938 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8506
897 | 436 | 188 | 76 | 1.4 | 12.1 | 60.8164 | 15.7332 | 18.347 | 0 | 0 | 0 | 58.5412 | 0 | 4% | 0 | 0 | 10% | 0 | 17.1337
898 | 749 | 406 | 102 | 1 | 15.9 | 175.6035 | 0 | 47.9655 | 0 | 0 | 0 | 172.2651 | 0 | 18% | 0 | 0 | 10% | 0 | 45.9919
899 | 616 | 472 | 145 | 0.8 | 17.9 | 155.6173 | 0 | 50.6299 | 1.3791 | 0 | 0 | 154.3227 | 0 | 29% | 0 | 0 | 10% | 0 | 48.8012
900 | 815 | 620 | 128 | 1.7 | 19.2 | 220.1514 | 0 | 72.5488 | 0 | 0 | 0 | 218.3284 | 0 | 46% | 23.8498 | 0 | 42.44% | 0 | 46.2604
901 | 772 | 653 | 170 | 2.5 | 19.4 | 209.0309 | 0 | 73.9001 | 0.65354 | 0 | 0 | 207.8032 | 0 | 62% | 25 | 0 | 76.44% | 0 | 46.5245
902 | 773 | 589 | 134 | 3.6 | 19.6 | 205.8919 | 0 | 57.8429 | 10.6264 | 0 | 0 | 204.6837 | 0 | 78% | 9.9737 | 0 | 90% | 0 | 45.4823
903 | 916 | 522 | 59 | 3.6 | 19.8 | 234.53 | 0 | 48.417 | 14.6435 | 42.5868 | 0.34832 | 193.7334 | 0 | 92% | 0 | 0 | 90% | 0 | 45.5811
904 | 822 | 366 | 53 | 3.6 | 19.4 | 144.5362 | 48.7586 | 32.4724 | 11.2631 | 42.5911 | 15.1619 | 103.3489 | 0 | 100% | 0 | 0 | 90% | 0 | 46.5946
905 | 638 | 181 | 40 | 3.7 | 17.8 | 42.153 | 82.483 | 20.2667 | 0 | 42.5912 | 15.2559 | 0 | 0 | 100% | 0 | 13.8296 | 67.87% | 0 | 50.0643
906 | 175 | 26 | 11 | 2.3 | 15 | 0 | 8.9714 | 0 | 0 | 69.7828 | 27.1 | 0 | 68.5429 | 95% | 0 | 25 | 27.87% | 0 | 50.0467
907 | 0 | 0 | 0 | 0.6 | 12.2 | 0 | 0 | 0 | 0 | 102.4418 | 41.187 | 0 | 106.6573 | 87% | 0 | 11.1704 | 10% | 0 | 49.4516
908 | 0 | 0 | 0 | 0.9 | 10.7 | 0 | 0 | 0 | 0 | 120.1696 | 48.9003 | 0 | 124.119 | 78% | 0 | 0 | 10% | 0 | 46.6335
909 | 0 | 0 | 0 | 1.8 | 9.9 | 0 | 0 | 0 | 0 | 108.907 | 44.2411 | 0 | 109.1378 | 70% | 0 | 0 | 10% | 0 | 42.3453
910 | 0 | 0 | 0 | 2.2 | 10.4 | 0 | 0 | 0 | 0 | 101.8038 | 41.2341 | 0 | 100.5883 | 62% | 0 | 0 | 10% | 0 | 39.3915
911 | 0 | 0 | 0 | 3 | 11.7 | 0 | 0 | 0 | 0 | 95.2751 | 38.4199 | 0 | 93.0708 | 55% | 0 | 0 | 10% | 0 | 36.5531
912 | 0 | 0 | 0 | 1.8 | 10.1 | 0 | 0 | 0 | 0 | 91.394 | 36.853 | 0 | 88.6396 | 48% | 0 | 0 | 10% | 0 | 34.9257
913 | 0 | 0 | 0 | 1.2 | 9.3 | 0 | 0 | 0 | 0 | 89.4837 | 36.0751 | 0 | 86.5818 | 41% | 0 | 0 | 10% | 0 | 34.0754
914 | 0 | 0 | 0 | 1.6 | 7.8 | 0 | 0 | 0 | 0 | 89.6711 | 36.2106 | 0 | 87.0257 | 35% | 0 | 0 | 10% | 0 | 34.1407
915 | 0 | 0 | 0 | 1.8 | 8.6 | 0 | 0 | 0 | 0 | 91.9901 | 37.1697 | 0 | 90.0072 | 28% | 0 | 0 | 10% | 0 | 35.0417
916 | 0 | 0 | 0 | 2.3 | 9.6 | 0 | 0 | 0 | 0 | 101.3387 | 41.0766 | 0 | 101.208 | 20% | 0 | 0 | 10% | 0 | 38.9016
917 | 0 | 0 | 0 | 2.5 | 9.4 | 0 | 0 | 0 | 0 | 117.1616 | 47.7165 | 0 | 119.9249 | 11% | 0 | 0 | 10% | 0 | 45.5274
918 | 0 | 0 | 0 | 2.4 | 9 | 0 | 0 | 0 | 0 | 125.1007 | 51.0369 | 0 | 129.0238 | 1% | 0 | 0 | 10% | 0 | 48.9027
919 | 0 | 0 | 0 | 2.4 | 8.7 | 0 | 0 | 0 | 0 | 17.8104 | 7.2705 | 0 | 18.3581 | 0% | 0 | 0 | 10% | 0 | 5.3875
920 | 255 | 46 | 17 | 2.8 | 9 | 0 | 32.8888 | 1.4693 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.37332
921 | 708 | 221 | 43 | 1.3 | 12.2 | 108.5486 | 27.425 | 26.6937 | 0 | 0 | 0 | 104.4778 | 0 | 8% | 0 | 0 | 10% | 0 | 25.0691
922 | 859 | 407 | 56 | 2.8 | 14.5 | 203.6499 | 0 | 50.0666 | 0 | 0 | 0 | 201.2593 | 0 | 23% | 0 | 0 | 10% | 0 | 47.8261
923 | 932 | 555 | 62 | 3.4 | 16 | 243.1904 | 0 | 67.7291 | 0 | 0 | 0 | 241.5104 | 0 | 42% | 17.9371 | 0 | 34.39% | 0 | 47.1523
924 | 960 | 646 | 67 | 1.5 | 17.2 | 262.9008 | 0 | 74.5118 | 0.5882 | 0 | 0 | 261.4921 | 0 | 62% | 25 | 0 | 68.39% | 0 | 46.6396
925 | 966 | 672 | 68 | 1.6 | 18.6 | 266.8358 | 0 | 64.3625 | 10.7375 | 0 | 0 | 265.6032 | 0 | 82% | 15.8865 | 0 | 90% | 0 | 45.499
926 | 950 | 631 | 68 | 2.6 | 19.3 | 258.2454 | 0 | 46.8374 | 28.2626 | 42.5932 | 1.5257 | 217.5656 | 0 | 99% | 0 | 0 | 90% | 0 | 44.9771
927 | 933 | 534 | 59 | 3.5 | 19.6 | 60.8828 | 206.1632 | 29.3845 | 35.0678 | 42.5963 | 15.1514 | 19.8891 | 0 | 100% | 0 | 0 | 90% | 0 | 44.5669
928 | 860 | 380 | 51 | 4.3 | 19.3 | 42.1597 | 180.0228 | 29.6791 | 16.1755 | 42.5942 | 15.1691 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.5601
929 | 670 | 189 | 38 | 3.9 | 18 | 42.1581 | 90.6433 | 21.3096 | 0 | 42.5918 | 15.2451 | 0 | 0 | 100% | 0 | 11.4664 | 71.65% | 0 | 48.7332
930 | 171 | 26 | 11 | 2.9 | 14.5 | 0 | 9.8244 | 0 | 0 | 67.5578 | 26.1481 | 0 | 66.2797 | 95% | 0 | 25 | 31.65% | 0 | 49.0906
931 | 0 | 0 | 0 | 1 | 11 | 0 | 0 | 0 | 0 | 94.3298 | 37.7653 | 0 | 97.3733 | 88% | 0 | 13.5336 | 10% | 0 | 48.3891
932 | 0 | 0 | 0 | 1.2 | 9.3 | 0 | 0 | 0 | 0 | 117.4764 | 47.8501 | 0 | 121.4178 | 79% | 0 | 0 | 10% | 0 | 45.4745
933 | 0 | 0 | 0 | 1.2 | 9 | 0 | 0 | 0 | 0 | 107.675 | 43.7669 | 0 | 108.0733 | 71% | 0 | 0 | 10% | 0 | 41.7844
934 | 0 | 0 | 0 | 0.4 | 8.4 | 0 | 0 | 0 | 0 | 101.6633 | 41.2606 | 0 | 100.699 | 63% | 0 | 0 | 10% | 0 | 39.347
935 | 0 | 0 | 0 | 0.2 | 6.5 | 0 | 0 | 0 | 0 | 94.9618 | 38.5008 | 0 | 92.9143 | 56% | 0 | 0 | 10% | 0 | 36.5775
936 | 0 | 0 | 0 | 1 | 5.4 | 0 | 0 | 0 | 0 | 90.4927 | 36.6291 | 0 | 87.7224 | 49% | 0 | 0 | 10% | 0 | 34.6531
937 | 0 | 0 | 0 | 1.4 | 5.1 | 0 | 0 | 0 | 0 | 88.2609 | 35.6881 | 0 | 85.2898 | 43% | 0 | 0 | 10% | 0 | 33.6398
938 | 0 | 0 | 0 | 1.8 | 7.1 | 0 | 0 | 0 | 0 | 87.1786 | 35.1755 | 0 | 84.2263 | 36% | 0 | 0 | 10% | 0 | 33.0571
939 | 0 | 0 | 0 | 0.9 | 6.5 | 0 | 0 | 0 | 0 | 86.6532 | 34.9705 | 0 | 83.7951 | 30% | 0 | 0 | 10% | 0 | 32.79
940 | 0 | 0 | 0 | 1.7 | 6.8 | 0 | 0 | 0 | 0 | 89.2032 | 36.0441 | 0 | 87.0034 | 24% | 0 | 0 | 10% | 0 | 33.8059
941 | 0 | 0 | 0 | 2.3 | 6.5 | 0 | 0 | 0 | 0 | 93.8728 | 38.0443 | 0 | 92.8237 | 17% | 0 | 0 | 10% | 0 | 35.7655
942 | 0 | 0 | 0 | 2.9 | 7.4 | 0 | 0 | 0 | 0 | 99.386 | 40.3376 | 0 | 99.3166 | 9% | 0 | 0 | 10% | 0 | 38.0449
943 | 0 | 0 | 0 | 2.3 | 6.9 | 0 | 0 | 0 | 0 | 108.8206 | 44.3251 | 0 | 110.4943 | 1% | 0 | 0 | 10% | 0 | 42.0298
944 | 290 | 52 | 18 | 2.3 | 7.6 | 0 | 39.2194 | 2.1118 | 0 | 9.2428 | 3.7635 | 0 | 9.3774 | 0% | 0 | 0 | 10% | 0 | 3.7692
945 | 750 | 234 | 43 | 0.9 | 9.8 | 116.7708 | 29.5442 | 28.8347 | 0 | 0 | 0 | 112.5748 | 0 | 9% | 0 | 0 | 10% | 0 | 27.1011
946 | 898 | 424 | 55 | 0.7 | 14.7 | 215.6572 | 0 | 52.4848 | 0 | 0 | 0 | 213.386 | 0 | 25% | 7.7148 | 0 | 20.49% | 0 | 42.439
947 | 963 | 574 | 61 | 1.7 | 16.7 | 253.453 | 0 | 69.9359 | 0 | 0 | 0 | 251.8599 | 0 | 44% | 23.9969 | 0 | 53.13% | 0 | 43.2244
948 | 997 | 669 | 63 | 2.2 | 18 | 273.4018 | 0 | 70.0038 | 5.0962 | 0 | 0 | 272.0432 | 0 | 64% | 25 | 0 | 87.13% | 0 | 42.053
949 | 1000 | 694 | 65 | 2.8 | 18.1 | 276.1169 | 0 | 45.3974 | 29.7026 | 0 | 0 | 274.9236 | 0 | 85% | 2.1118 | 0 | 90% | 0 | 40.2467
950 | 987 | 654 | 64 | 2.9 | 19 | 199.3465 | 76.1236 | 41.4109 | 33.6891 | 0 | 0 | 198.512 | 0 | 100% | 0 | 0 | 90% | 0 | 39.0452
951 | 937 | 546 | 63 | 3.4 | 19 | 0 | 264.5487 | 40.001 | 25.4259 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.5408
952 | 832 | 385 | 61 | 4.1 | 18 | 40.697 | 174.8153 | 41.087 | 4.4909 | 42.5942 | 0.233 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.1715
953 | 624 | 192 | 48 | 3.8 | 16.1 | 42.1583 | 81.059 | 20.7408 | 0 | 42.5919 | 15.3458 | 0 | 0 | 100% | 0 | 6.8854 | 78.98% | 0 | 43.6845
954 | 153 | 28 | 14 | 2.3 | 13.4 | 0 | 9.7434 | 0 | 0 | 57.1653 | 21.6721 | 0 | 55.6682 | 96% | 0 | 25 | 38.98% | 0 | 44.6128
955 | 0 | 0 | 0 | 1.1 | 11 | 0 | 0 | 0 | 0 | 74.8971 | 29.4251 | 0 | 75.532 | 90% | 0 | 18.1146 | 10% | 0 | 44.5984
956 | 0 | 0 | 0 | 0.9 | 9.5 | 0 | 0 | 0 | 0 | 111.9924 | 45.548 | 0 | 116.008 | 82% | 0 | 0 | 10% | 0 | 42.9035
957 | 0 | 0 | 0 | 0.8 | 8.8 | 0 | 0 | 0 | 0 | 103.5295 | 42.0344 | 0 | 103.9691 | 74% | 0 | 0 | 10% | 0 | 39.8611
958 | 0 | 0 | 0 | 0.5 | 7.5 | 0 | 0 | 0 | 0 | 96.4659 | 39.1015 | 0 | 95.241 | 67% | 0 | 0 | 10% | 0 | 37.0211
959 | 0 | 0 | 0 | 1 | 7.7 | 0 | 0 | 0 | 0 | 90.1721 | 36.4258 | 0 | 87.7581 | 60% | 0 | 0 | 10% | 0 | 34.3303
960 | 0 | 0 | 0 | 0.4 | 6.6 | 0 | 0 | 0 | 0 | 84.6565 | 34.1225 | 0 | 81.43 | 54% | 0 | 0 | 10% | 0 | 31.9627
961 | 0 | 0 | 0 | 1.1 | 6.2 | 0 | 0 | 0 | 0 | 82.8863 | 33.3826 | 0 | 79.6584 | 48% | 0 | 0 | 10% | 0 | 31.1335
962 | 0 | 0 | 0 | 1 | 6.2 | 0 | 0 | 0 | 0 | 81.7971 | 32.8838 | 0 | 78.792 | 42% | 0 | 0 | 10% | 0 | 30.557
963 | 0 | 0 | 0 | 0.9 | 5.4 | 0 | 0 | 0 | 0 | 81.4701 | 32.7552 | 0 | 78.6379 | 36% | 0 | 0 | 10% | 0 | 30.3665
964 | 0 | 0 | 0 | 0.7 | 6.3 | 0 | 0 | 0 | 0 | 82.8682 | 33.3742 | 0 | 80.1853 | 30% | 0 | 0 | 10% | 0 | 30.9334
965 | 0 | 0 | 0 | 0.5 | 4.9 | 0 | 0 | 0 | 0 | 85.3692 | 34.4688 | 0 | 83.2347 | 24% | 0 | 0 | 10% | 0 | 31.9825
966 | 0 | 0 | 0 | 1 | 5.6 | 0 | 0 | 0 | 0 | 87.972 | 35.5548 | 0 | 86.4217 | 17% | 0 | 0 | 10% | 0 | 33.0399
967 | 0 | 0 | 0 | 0.7 | 5.5 | 0 | 0 | 0 | 0 | 94.7494 | 38.4415 | 0 | 94.7525 | 10% | 0 | 0 | 10% | 0 | 35.9052
968 | 295 | 68 | 34 | 0.9 | 7.6 | 0 | 41.7916 | 2.7551 | 0 | 95.2995 | 38.6115 | 0 | 95.3098 | 3% | 0 | 0 | 10% | 0 | 38.8525
969 | 631 | 222 | 52 | 0.9 | 12.1 | 96.8262 | 24.5118 | 24.3044 | 0 | 47.339 | 17.5074 | 57.4741 | 8.6745 | 7% | 0 | 0 | 10% | 0 | 40.1574
970 | 908 | 435 | 57 | 2.5 | 16.1 | 218.2214 | 0 | 51.9157 | 1.2776 | 42.523 | 15.321 | 175.5402 | 0 | 20% | 25 | 0 | 44% | 0 | 39.8802
971 | 957 | 591 | 75 | 4.3 | 17.6 | 250.6905 | 0 | 52.8125 | 18.1364 | 42.582 | 15.2635 | 208.8992 | 0 | 36% | 25 | 0 | 78% | 0 | 40.404
972 | 976 | 667 | 67 | 2.7 | 18.3 | 267.7045 | 0 | 36.6887 | 38.4113 | 42.5995 | 15.2304 | 226.0285 | 0 | 52% | 8.8235 | 0 | 90% | 0 | 40.2339
973 | 957 | 707 | 98 | 2.7 | 19.5 | 264.4821 | 0 | 25.9569 | 49.1431 | 42.6038 | 15.1602 | 222.7827 | 0 | 69% | 0 | 0 | 90% | 0 | 38.2616
974 | 764 | 605 | 140 | 3.2 | 19.8 | 204.5481 | 0 | 24.1825 | 44.3209 | 42.6064 | 15.1426 | 162.9284 | 0 | 81% | 0 | 0 | 90% | 0 | 37.0012
975 | 664 | 506 | 154 | 2.9 | 19.9 | 166.9114 | 0 | 22.5014 | 31.9915 | 42.6064 | 15.1364 | 125.0221 | 0 | 90% | 0 | 0 | 90% | 0 | 37.0476
976 | 683 | 368 | 98 | 2.2 | 19.7 | 154.3795 | 0 | 22.1388 | 18.3933 | 42.6056 | 15.1485 | 112.2273 | 0 | 98% | 0 | 0 | 90% | 0 | 38.7693
977 | 444 | 191 | 79 | 3.9 | 18.9 | 71.226 | 0 | 16.5232 | 0 | 42.6046 | 15.1972 | 29.574 | 0 | 100% | 0 | 9.7627 | 74.38% | 0 | 42.6171
978 | 8 | 21 | 20 | 1.8 | 16.7 | 0 | 0.55958 | 0 | 0 | 56.8398 | 21.3672 | 0 | 55.3352 | 96% | 0 | 25 | 34.38% | 0 | 44.3058
979 | 0 | 0 | 0 | 1.8 | 14.7 | 0 | 0 | 0 | 0 | 81.4107 | 32.034 | 0 | 82.9723 | 90% | 0 | 15.2373 | 10% | 0 | 44.3292
980 | 0 | 0 | 0 | 0.6 | 12.9 | 0 | 0 | 0 | 0 | 111.69 | 45.2362 | 0 | 115.1067 | 82% | 0 | 0 | 10% | 0 | 42.7151
981 | 0 | 0 | 0 | 1.2 | 11.7 | 0 | 0 | 0 | 0 | 102.8549 | 41.61 | 0 | 102.9228 | 74% | 0 | 0 | 10% | 0 | 39.4953
982 | 0 | 0 | 0 | 0.6 | 10.4 | 0 | 0 | 0 | 0 | 94.4632 | 38.1444 | 0 | 92.8058 | 67% | 0 | 0 | 10% | 0 | 36.0963
983 | 0 | 0 | 0 | 1.3 | 9.8 | 0 | 0 | 0 | 0 | 88.8214 | 35.7719 | 0 | 86.1119 | 60% | 0 | 0 | 10% | 0 | 33.6841
984 | 0 | 0 | 0 | 1.9 | 9.7 | 0 | 0 | 0 | 0 | 85.3894 | 34.3241 | 0 | 82.3073 | 54% | 0 | 0 | 10% | 0 | 32.1559
985 | 0 | 0 | 0 | 2.1 | 9.5 | 0 | 0 | 0 | 0 | 84.398 | 33.9144 | 0 | 81.4017 | 48% | 0 | 0 | 10% | 0 | 31.6617
986 | 0 | 0 | 0 | 2.4 | 9.6 | 0 | 0 | 0 | 0 | 84.5035 | 33.9551 | 0 | 81.734 | 42% | 0 | 0 | 10% | 0 | 31.6314
987 | 0 | 0 | 0 | 2.2 | 7.8 | 0 | 0 | 0 | 0 | 87.4021 | 35.2474 | 0 | 85.3331 | 35% | 0 | 0 | 10% | 0 | 32.8644
988 | 0 | 0 | 0 | 1.5 | 7.6 | 0 | 0 | 0 | 0 | 98.1063 | 39.7896 | 0 | 98.3407 | 28% | 0 | 0 | 10% | 0 | 37.3611
989 | 0 | 0 | 0 | 1.5 | 8.1 | 0 | 0 | 0 | 0 | 113.9516 | 46.4279 | 0 | 117.1626 | 19% | 0 | 0 | 10% | 0 | 44.0058
990 | 0 | 0 | 0 | 1.5 | 7.6 | 0 | 0 | 0 | 0 | 122.0164 | 49.8083 | 0 | 126.3605 | 10% | 0 | 0 | 10% | 0 | 47.4659
991 | 0 | 0 | 0 | 1.1 | 7.4 | 0 | 0 | 0 | 0 | 125.7138 | 51.3564 | 0 | 130.2776 | 0% | 0 | 0 | 10% | 0 | 49.1108
992 | 275 | 54 | 20 | 1.4 | 8 | 0 | 40.77 | 2.0354 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.072569
993 | 717 | 234 | 46 | 1.8 | 12.1 | 111.8849 | 28.3405 | 27.5228 | 0 | 0 | 0 | 107.8747 | 0 | 8% | 0 | 0 | 10% | 0 | 25.8515
994 | 829 | 407 | 59 | 1.4 | 15.3 | 199.0419 | 0 | 48.5388 | 0 | 0 | 0 | 196.8891 | 0 | 23% | 0 | 0 | 10% | 0 | 46.3476
995 | 926 | 563 | 61 | 2.2 | 17.2 | 243.6446 | 0 | 67.1641 | 0 | 0 | 0 | 242.0037 | 0 | 41% | 17.4523 | 0 | 33.73% | 0 | 47.0796
996 | 961 | 655 | 62 | 1.7 | 18.4 | 263.8857 | 0 | 74.636 | 0.46396 | 0 | 0 | 262.5205 | 0 | 61% | 25 | 0 | 67.73% | 0 | 46.7675
997 | 963 | 680 | 65 | 1.6 | 19.2 | 266.8462 | 0 | 65.2186 | 9.8814 | 0 | 0 | 265.6475 | 0 | 82% | 16.3712 | 0 | 90% | 0 | 45.884
998 | 939 | 653 | 83 | 4.4 | 19.5 | 244.3443 | 11.1091 | 48.0339 | 27.0661 | 0 | 0 | 243.2826 | 0 | 100% | 0 | 0 | 90% | 0 | 45.2443
999 | 862 | 592 | 139 | 5.5 | 18.9 | 41.2022 | 208.3895 | 44.491 | 23.8115 | 42.5984 | 1.3507 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.91
1000 | 275 | 334 | 214 | 4.4 | 18.2 | 0 | 61.0138 | 27.3635 | 0 | 42.5953 | 15.2347 | 0 | 41.1041 | 97% | 0 | 4.9497 | 82.08% | 0 | 45.4821
1001 | 48 | 109 | 96 | 5 | 16.2 | 0 | 10.4324 | 3.1951 | 0 | 62.6233 | 23.8878 | 0 | 61.0666 | 93% | 0 | 25 | 42.08% | 0 | 49.1568
1002 | 1 | 25 | 25 | 3.6 | 15.1 | 0 | 0.076244 | 0 | 0 | 82.7643 | 32.6428 | 0 | 83.3686 | 86% | 0 | 20.0503 | 10% | 0 | 49.7908
1003 | 0 | 0 | 0 | 3.1 | 14.1 | 0 | 0 | 0 | 0 | 127.5225 | 51.7362 | 0 | 135.1861 | 76% | 0 | 0 | 10% | 0 | 49.0395
1004 | 0 | 0 | 0 | 2.8 | 13.4 | 0 | 0 | 0 | 0 | 117.5757 | 47.6593 | 0 | 120.0409 | 67% | 0 | 0 | 10% | 0 | 45.6012
1005 | 0 | 0 | 0 | 2.6 | 12.8 | 0 | 0 | 0 | 0 | 106.6087 | 43.1248 | 0 | 106.3784 | 59% | 0 | 0 | 10% | 0 | 41.2463
1006 | 0 | 0 | 0 | 4.2 | 11 | 0 | 0 | 0 | 0 | 100.3226 | 40.5798 | 0 | 98.8763 | 52% | 0 | 0 | 10% | 0 | 38.722
1007 | 0 | 0 | 0 | 4.2 | 10.4 | 0 | 0 | 0 | 0 | 94.6241 | 38.2126 | 0 | 92.367 | 45% | 0 | 0 | 10% | 0 | 36.3272
1008 | 0 | 0 | 0 | 4.4 | 10.9 | 0 | 0 | 0 | 0 | 91.0988 | 36.69 | 0 | 88.2967 | 38% | 0 | 0 | 10% | 0 | 34.7531
1009 | 0 | 0 | 0 | 3 | 10.4 | 0 | 0 | 0 | 0 | 89.4361 | 36.0073 | 0 | 86.5073 | 31% | 0 | 0 | 10% | 0 | 34.0073
1010 | 0 | 0 | 0 | 3.5 | 9.9 | 0 | 0 | 0 | 0 | 89.694 | 36.1401 | 0 | 87.0097 | 25% | 0 | 0 | 10% | 0 | 34.0779
1011 | 0 | 0 | 0 | 3.4 | 9.6 | 0 | 0 | 0 | 0 | 92.0398 | 37.1515 | 0 | 90.0077 | 18% | 0 | 0 | 10% | 0 | 35.0359
1012 | 0 | 0 | 0 | 3.8 | 9.4 | 0 | 0 | 0 | 0 | 101.3124 | 41.0749 | 0 | 101.1041 | 10% | 0 | 0 | 10% | 0 | 38.9127
1013 | 0 | 0 | 0 | 3.6 | 9.5 | 0 | 0 | 0 | 0 | 116.7215 | 47.5299 | 0 | 119.3435 | 1% | 0 | 0 | 10% | 0 | 45.3483
1014 | 0 | 0 | 0 | 3.4 | 9.6 | 0 | 0 | 0 | 0 | 14.3449 | 5.8484 | 0 | 14.7817 | 0% | 0 | 0 | 10% | 0 | 3.8828
1015 | 0 | 0 | 0 | 2.3 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9294
1016 | 0 | 13 | 13 | 2.2 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9141
1017 | 18 | 95 | 88 | 3.3 | 9.8 | 0 | 4.1851 | 0.86052 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.0384
1018 | 52 | 265 | 237 | 5 | 11 | 0 | 14.558 | 16.585 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 14.7009
1019 | 403 | 561 | 326 | 5.7 | 12.1 | 75.8624 | 19.9665 | 54.0947 | 0 | 0 | 0 | 72.5964 | 0 | 6% | 4.1389 | 0 | 15.63% | 0 | 48.6081
1020 | 762 | 620 | 140 | 5.4 | 12.7 | 202.9135 | 0 | 71.0813 | 0 | 0 | 0 | 199.1466 | 0 | 21% | 22.652 | 0 | 46.44% | 0 | 46.2095
1021 | 910 | 687 | 99 | 6.4 | 13.4 | 247.7567 | 0 | 73.8676 | 1.2324 | 0 | 0 | 245.7031 | 0 | 40% | 25 | 0 | 80.44% | 0 | 46.1966
1022 | 897 | 650 | 101 | 6.6 | 13.5 | 240.2853 | 0 | 55.4782 | 19.6218 | 0 | 0 | 238.8538 | 0 | 58% | 7.0326 | 0 | 90% | 0 | 45.7858
1023 | 847 | 556 | 107 | 6 | 13.4 | 215.2685 | -2.98e-14 | 48.3851 | 16.4564 | 42.566 | 0 | 174.6185 | 0 | 71% | 0 | 0 | 90% | 0 | 45.4125
1024 | 754 | 390 | 89 | 5.6 | 13.1 | 170.5594 | 1.65e-15 | 33.3148 | 11.7284 | 42.5871 | 14.6235 | 129.5967 | 0 | 81% | 0.22108 | 0.18792 | 90% | 0 | 45.8259
1025 | 561 | 191 | 57 | 5.5 | 12.3 | 94.5731 | 0 | 19.4651 | 0 | 42.5792 | 15.5057 | 53.8173 | 0 | 85% | 0 | 15.9232 | 64.52% | 0 | 49.5671
1026 | 149 | 32 | 17 | 4.8 | 10.8 | 0 | 12.3021 | 0 | 0 | 68.4765 | 26.7364 | 0 | 66.2747 | 80% | 0 | 25 | 24.52% | 0 | 50.0658
1027 | 0 | 0 | 0 | 3.4 | 9 | 0 | 0 | 0 | 0 | 106.5215 | 43.0776 | 0 | 110.6971 | 72% | 0 | 9.0768 | 10% | 0 | 49.4493
1028 | 0 | 0 | 0 | 3.4 | 7.3 | 0 | 0 | 0 | 0 | 118.0256 | 48.1583 | 0 | 121.9897 | 63% | 0 | 0 | 10% | 0 | 45.7845
1029 | 0 | 0 | 0 | 2.4 | 6.2 | 0 | 0 | 0 | 0 | 106.6476 | 43.4363 | 0 | 107.4229 | 55% | 0 | 0 | 10% | 0 | 41.3092
1030 | 0 | 0 | 0 | 1.8 | 6.3 | 0 | 0 | 0 | 0 | 100.0086 | 40.6324 | 0 | 99.2545 | 47% | 0 | 0 | 10% | 0 | 38.5744
1031 | 0 | 0 | 0 | 1.7 | 6.6 | 0 | 0 | 0 | 0 | 94.1408 | 38.1536 | 0 | 92.3924 | 40% | 0 | 0 | 10% | 0 | 36.1016
1032 | 0 | 0 | 0 | 1.1 | 6.1 | 0 | 0 | 0 | 0 | 90.5117 | 36.6199 | 0 | 88.0622 | 33% | 0 | 0 | 10% | 0 | 34.541
1033 | 0 | 0 | 0 | 1.6 | 6 | 0 | 0 | 0 | 0 | 89.1697 | 36.0523 | 0 | 86.5954 | 27% | 0 | 0 | 10% | 0 | 33.9276
1034 | 0 | 0 | 0 | 2.3 | 6 | 0 | 0 | 0 | 0 | 89.0516 | 36.0026 | 0 | 86.596 | 20% | 0 | 0 | 10% | 0 | 33.8319
1035 | 0 | 0 | 0 | 1.8 | 5.1 | 0 | 0 | 0 | 0 | 91.519 | 37.0766 | 0 | 89.7076 | 13% | 0 | 0 | 10% | 0 | 34.8624
1036 | 0 | 0 | 0 | 2.2 | 4.7 | 0 | 0 | 0 | 0 | 100.5293 | 40.8973 | 0 | 100.5157 | 6% | 0 | 0 | 10% | 0 | 38.6447
1037 | 0 | 0 | 0 | 1.9 | 4.8 | 0 | 0 | 0 | 0 | 74.9753 | 30.6364 | 0 | 76.9044 | 0% | 0 | 0 | 10% | 0 | 28.4434
1038 | 0 | 0 | 0 | 1.8 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0497
1039 | 0 | 0 | 0 | 2.3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0321
1040 | 256 | 56 | 22 | 1.9 | 4 | 0 | 41.447 | 1.8829 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.13184
1041 | 722 | 249 | 53 | 2.7 | 7.6 | 113.0409 | 29.1299 | 29.0051 | 0 | 0 | 0 | 108.4706 | 0 | 8% | 0 | 0 | 10% | 0 | 27.3128
1042 | 857 | 438 | 70 | 5.5 | 10.2 | 204.3401 | 0 | 51.0234 | 1.5266 | 0 | 0 | 201.783 | 0 | 24% | 0 | 0 | 10% | 0 | 48.7883
1043 | 939 | 587 | 69 | 6 | 11.4 | 245.2623 | 0 | 70.5225 | 0 | 0 | 0 | 243.4424 | 0 | 42% | 21.0518 | 0 | 38.63% | 0 | 46.827
1044 | 982 | 682 | 67 | 5.9 | 12.7 | 267.1844 | 0 | 74.4206 | 0.67943 | 0 | 0 | 265.6754 | 0 | 62% | 25 | 0 | 72.63% | 0 | 46.5248
1045 | 1001 | 713 | 64 | 6.4 | 13.8 | 274.2085 | 0 | 61.4205 | 13.6795 | 0 | 0 | 272.9121 | 0 | 83% | 12.7718 | 0 | 90% | 0 | 45.6161
1046 | 980 | 671 | 66 | 6.5 | 14.3 | 226.8441 | 41.9673 | 47.7386 | 27.3614 | 0 | 0 | 225.8233 | 0 | 100% | 0 | 0 | 90% | 0 | 45.1127
1047 | 946 | 567 | 63 | 7.2 | 14 | 41.1213 | 234.6318 | 45.4839 | 22.0105 | 42.5891 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.6605
1048 | 875 | 410 | 56 | 6.9 | 13.4 | 42.1609 | 187.7746 | 30.4189 | 18.1217 | 42.5866 | 14.1334 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.2224
1049 | 703 | 215 | 44 | 6.2 | 12.3 | 42.1586 | 102.1044 | 23.8199 | 0 | 42.5846 | 15.5076 | 0 | 0 | 100% | 0 | 9.0625 | 75.5% | 0 | 49.1035
1050 | 203 | 38 | 16 | 5.8 | 10.2 | 0 | 18.0476 | 0 | 0 | 69.243 | 27.1024 | 0 | 67.9935 | 95% | 0 | 25 | 35.5% | 0 | 50.0566
1051 | 0 | 0 | 0 | 4.4 | 8.3 | 0 | 0 | 0 | 0 | 90.6349 | 36.3212 | 0 | 92.8674 | 88% | 0 | 15.9375 | 10% | 0 | 49.3576
1052 | 0 | 0 | 0 | 4.6 | 7.7 | 0 | 0 | 0 | 0 | 117.9427 | 48.1092 | 0 | 122.3624 | 79% | 0 | 0 | 10% | 0 | 45.6488
1053 | 0 | 0 | 0 | 4.1 | 7.4 | 0 | 0 | 0 | 0 | 106.6117 | 43.3829 | 0 | 107.0016 | 71% | 0 | 0 | 10% | 0 | 41.3628
1054 | 0 | 0 | 0 | 3 | 6.5 | 0 | 0 | 0 | 0 | 99.671 | 40.4836 | 0 | 98.4884 | 63% | 0 | 0 | 10% | 0 | 38.5358
1055 | 0 | 0 | 0 | 2.4 | 6.2 | 0 | 0 | 0 | 0 | 93.5527 | 37.9138 | 0 | 91.4151 | 56% | 0 | 0 | 10% | 0 | 35.9471
1056 | 0 | 0 | 0 | 3.4 | 6.1 | 0 | 0 | 0 | 0 | 90.0406 | 36.4189 | 0 | 87.342 | 50% | 0 | 0 | 10% | 0 | 34.396
1057 | 0 | 0 | 0 | 2.9 | 5.3 | 0 | 0 | 0 | 0 | 88.6046 | 35.8293 | 0 | 85.8466 | 43% | 0 | 0 | 10% | 0 | 33.7366
1058 | 0 | 0 | 0 | 2 | 4.7 | 0 | 0 | 0 | 0 | 88.2821 | 35.7068 | 0 | 85.6594 | 37% | 0 | 0 | 10% | 0 | 33.5504
1059 | 0 | 0 | 0 | 2.3 | 4.5 | 0 | 0 | 0 | 0 | 90.6105 | 36.7018 | 0 | 88.6271 | 30% | 0 | 0 | 10% | 0 | 34.4892
1060 | 0 | 0 | 0 | 2.1 | 4.3 | 0 | 0 | 0 | 0 | 99.5666 | 40.4985 | 0 | 99.4262 | 23% | 0 | 0 | 10% | 0 | 38.2414
1061 | 0 | 0 | 0 | 1.8 | 3.3 | 0 | 0 | 0 | 0 | 115.5551 | 47.2419 | 0 | 118.3926 | 14% | 0 | 0 | 10% | 0 | 44.9735
1062 | 0 | 0 | 0 | 2.3 | 3.1 | 0 | 0 | 0 | 0 | 123.1236 | 50.4012 | 0 | 126.9808 | 4% | 0 | 0 | 10% | 0 | 48.1948
1063 | 0 | 0 | 0 | 1.9 | 3.3 | 0 | 0 | 0 | 0 | 52.658 | 21.5627 | 0 | 54.3046 | 0% | 0 | 0 | 10% | 0 | 19.5648
1064 | 264 | 59 | 24 | 1.7 | 3.4 | 0 | 43.3852 | 2.1428 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.24635
1065 | 716 | 250 | 52 | 2.3 | 7.8 | 112.5954 | 29.0083 | 28.6351 | 0 | 0 | 0 | 108.4213 | 0 | 8% | 0 | 0 | 10% | 0 | 26.964
1066 | 866 | 439 | 64 | 4.6 | 11 | 207.8669 | 0 | 52.3988 | 0 | 0 | 0 | 205.5362 | 0 | 24% | 2.5149 | 0 | 13.42% | 0 | 47.6087
1067 | 938 | 589 | 68 | 5.6 | 12.1 | 245.8354 | 0 | 70.2697 | 0 | 0 | 0 | 244.1903 | 0 | 43% | 20.974 | 0 | 41.95% | 0 | 46.6351
1068 | 964 | 682 | 73 | 5.6 | 13.3 | 262.4996 | 0 | 74.3039 | 0.79605 | 0 | 0 | 261.1223 | 0 | 62% | 25 | 0 | 75.94% | 0 | 46.439
1069 | 972 | 709 | 74 | 6 | 14.4 | 266.8752 | 0 | 59.019 | 16.081 | 0 | 0 | 265.6565 | 0 | 83% | 10.3346 | 0 | 90% | 0 | 45.7104
1070 | 946 | 665 | 77 | 6.4 | 14.8 | 255.3244 | 0 | 46.5478 | 28.5522 | 42.5942 | 1.9245 | 214.5615 | 0 | 99% | 0 | 0 | 90% | 0 | 45.1321
1071 | 902 | 560 | 75 | 6.8 | 14.7 | 55.9831 | 204.5819 | 29.4608 | 35.9863 | 42.5969 | 15.4136 | 14.9727 | 0 | 100% | 0 | 0 | 90% | 0 | 45.0158
1072 | 821 | 404 | 67 | 6.5 | 14.2 | 42.1597 | 173.6973 | 29.1632 | 17.233 | 42.5946 | 15.435 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.3111
1073 | 638 | 212 | 53 | 6.2 | 12.9 | 42.1585 | 87.8828 | 22.22 | 0 | 42.5922 | 15.4875 | 0 | 0 | 100% | 0 | 10.5584 | 73.11% | 0 | 48.9793
1074 | 168 | 38 | 19 | 5.8 | 10.8 | 0 | 16.0036 | 0 | 0 | 69.3039 | 27.1021 | 0 | 68.0552 | 95% | 0 | 25 | 33.11% | 0 | 50.0556
1075 | 0 | 0 | 0 | 3.9 | 9.2 | 0 | 0 | 0 | 0 | 93.849 | 37.6522 | 0 | 96.6926 | 88% | 0 | 14.4416 | 10% | 0 | 49.1906
1076 | 0 | 0 | 0 | 3.8 | 9 | 0 | 0 | 0 | 0 | 117.9238 | 48.0495 | 0 | 122.0451 | 79% | 0 | 0 | 10% | 0 | 45.6528
1077 | 0 | 0 | 0 | 3 | 9 | 0 | 0 | 0 | 0 | 106.8528 | 43.4239 | 0 | 107.1488 | 71% | 0 | 0 | 10% | 0 | 41.4351
1078 | 0 | 0 | 0 | 1.8 | 8.1 | 0 | 0 | 0 | 0 | 100.5954 | 40.821 | 0 | 99.4848 | 63% | 0 | 0 | 10% | 0 | 38.8958
1079 | 0 | 0 | 0 | 2.1 | 8 | 0 | 0 | 0 | 0 | 94.3432 | 38.1931 | 0 | 92.2709 | 56% | 0 | 0 | 10% | 0 | 36.2515
1080 | 0 | 0 | 0 | 2 | 7.7 | 0 | 0 | 0 | 0 | 90.6577 | 36.6327 | 0 | 87.9863 | 49% | 0 | 0 | 10% | 0 | 34.6372
1081 | 0 | 0 | 0 | 2.3 | 6.5 | 0 | 0 | 0 | 0 | 88.9089 | 35.9264 | 0 | 86.1121 | 43% | 0 | 0 | 10% | 0 | 33.8621
1082 | 0 | 0 | 0 | 2 | 5.5 | 0 | 0 | 0 | 0 | 88.9941 | 35.9897 | 0 | 86.4187 | 36% | 0 | 0 | 10% | 0 | 33.8593
1083 | 0 | 0 | 0 | 1.8 | 4.8 | 0 | 0 | 0 | 0 | 91.1458 | 36.923 | 0 | 89.1792 | 30% | 0 | 0 | 10% | 0 | 34.7375
1084 | 0 | 0 | 0 | 2.3 | 4.6 | 0 | 0 | 0 | 0 | 100.2877 | 40.7959 | 0 | 100.1748 | 22% | 0 | 0 | 10% | 0 | 38.5653
1085 | 0 | 0 | 0 | 2.2 | 4.7 | 0 | 0 | 0 | 0 | 115.6332 | 47.241 | 0 | 118.3568 | 13% | 0 | 0 | 10% | 0 | 45
1086 | 0 | 0 | 0 | 1.8 | 4 | 0 | 0 | 0 | 0 | 122.7567 | 50.2274 | 0 | 126.4295 | 3% | 0 | 0 | 10% | 0 | 48.0453
1087 | 0 | 0 | 0 | 1.6 | 3.5 | 0 | 0 | 0 | 0 | 44.0191 | 18.0245 | 0 | 45.3816 | 0% | 0 | 0 | 10% | 0 | 16.0568
1088 | 218 | 59 | 30 | 1.7 | 5.2 | 0 | 36.1141 | 1.8491 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.033438
1089 | 617 | 245 | 70 | 2.3 | 8.1 | 95.5535 | 24.6461 | 26.0143 | 0 | 0 | 0 | 92.0161 | 0 | 7% | 0 | 0 | 10% | 0 | 24.4932
1090 | 777 | 432 | 90 | 4.5 | 10.5 | 185.0285 | 0 | 49.5532 | 0 | 0 | 0 | 182.6457 | 0 | 21% | 0 | 0 | 10% | 0 | 47.4856
1091 | 858 | 581 | 98 | 5.8 | 11.6 | 223.1796 | 0 | 67.4707 | 0 | 0 | 0 | 221.4951 | 0 | 38% | 18.0086 | 0 | 34.49% | 0 | 47.0156
1092 | 897 | 674 | 102 | 6.5 | 12.2 | 242.3063 | 0 | 74.0671 | 1.0329 | 0 | 0 | 240.8887 | 0 | 56% | 25 | 0 | 68.49% | 0 | 46.4024
1093 | 908 | 698 | 101 | 6.6 | 12.8 | 247.8031 | 0 | 63.7967 | 11.3033 | 0 | 0 | 246.5547 | 0 | 75% | 15.8149 | 0 | 90% | 0 | 45.2076
1094 | 896 | 660 | 98 | 7.1 | 13.7 | 240.2709 | 0 | 45.7472 | 29.3528 | 42.5909 | 1.8342 | 199.5762 | 0 | 90% | 0 | 0 | 90% | 0 | 44.3957
1095 | 860 | 558 | 91 | 7.2 | 13.9 | 172.8941 | 54.5516 | 29.9145 | 34.3184 | 42.5945 | 15.4479 | 131.717 | 0 | 100% | 0 | 0 | 90% | 0 | 43.9143
1096 | 779 | 402 | 79 | 6.9 | 14.1 | 42.1531 | 162.6165 | 28.293 | 16.8789 | 42.5949 | 15.4395 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.4454
1097 | 611 | 213 | 58 | 6.4 | 13.3 | 42.1585 | 82.2051 | 21.5511 | 0 | 42.5925 | 15.4716 | 0 | 0 | 100% | 0 | 10.2248 | 73.64% | 0 | 47.9606
1098 | 162 | 38 | 19 | 5.3 | 11.2 | 0 | 16.4632 | 0 | 0 | 66.2697 | 25.7426 | 0 | 64.9561 | 95% | 0 | 25 | 33.64% | 0 | 48.6914
1099 | 0 | 0 | 0 | 4.2 | 9.1 | 0 | 0 | 0 | 0 | 89.6661 | 35.8496 | 0 | 92.0216 | 89% | 0 | 14.7752 | 10% | 0 | 47.7103
1100 | 0 | 0 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 115.3463 | 47.0149 | 0 | 119.1832 | 80% | 0 | 0 | 10% | 0 | 44.5684
1101 | 0 | 0 | 0 | 3.1 | 7.5 | 0 | 0 | 0 | 0 | 106.0141 | 43.13 | 0 | 106.4126 | 72% | 0 | 0 | 10% | 0 | 41.0845
1102 | 0 | 0 | 0 | 2.5 | 7.4 | 0 | 0 | 0 | 0 | 100.0212 | 40.6027 | 0 | 98.9843 | 64% | 0 | 0 | 10% | 0 | 38.6319
1103 | 0 | 0 | 0 | 1.8 | 6 | 0 | 0 | 0 | 0 | 93.4625 | 37.8806 | 0 | 91.3528 | 57% | 0 | 0 | 10% | 0 | 35.8992
1104 | 0 | 0 | 0 | 2.6 | 6.3 | 0 | 0 | 0 | 0 | 88.7349 | 35.8578 | 0 | 85.8221 | 51% | 0 | 0 | 10% | 0 | 33.823
1105 | 0 | 0 | 0 | 2.4 | 6.2 | 0 | 0 | 0 | 0 | 86.5709 | 34.9433 | 0 | 83.502 | 44% | 0 | 0 | 10% | 0 | 32.8316
1106 | 0 | 0 | 0 | 2 | 5.8 | 0 | 0 | 0 | 0 | 85.5204 | 34.5097 | 0 | 82.4894 | 38% | 0 | 0 | 10% | 0 | 32.3252
1107 | 0 | 0 | 0 | 2.9 | 5.6 | 0 | 0 | 0 | 0 | 85.3855 | 34.4579 | 0 | 82.5223 | 32% | 0 | 0 | 10% | 0 | 32.2093
1108 | 0 | 0 | 0 | 3 | 5.7 | 0 | 0 | 0 | 0 | 87.6463 | 35.4132 | 0 | 85.3628 | 25% | 0 | 0 | 10% | 0 | 33.1083
1109 | 0 | 0 | 0 | 3.8 | 5.9 | 0 | 0 | 0 | 0 | 92.7209 | 37.5688 | 0 | 91.6402 | 18% | 0 | 0 | 10% | 0 | 35.2219
1110 | 0 | 0 | 0 | 3.7 | 6 | 0 | 0 | 0 | 0 | 98.1452 | 39.8574 | 0 | 98.1027 | 11% | 0 | 0 | 10% | 0 | 37.4979
1111 | 0 | 1 | 1 | 3.7 | 6 | 0 | 0 | 0 | 0 | 107.2112 | 43.6802 | 0 | 108.877 | 3% | 0 | 0 | 10% | 0 | 41.3217
1112 | 291 | 71 | 32 | 3.6 | 6.2 | 0 | 48.6 | 2.9608 | 0 | 38.0359 | 15.487 | 0 | 38.432 | 0% | 0 | 0 | 10% | 0 | 16.2424
1113 | 682 | 266 | 73 | 4.6 | 9.4 | 106.3146 | 27.5721 | 29.1894 | 0 | 0 | 0 | 102.5688 | 0 | 8% | 0 | 0 | 10% | 0 | 27.5356
1114 | 812 | 454 | 94 | 7 | 12.1 | 192.5532 | 0 | 52.0738 | 0 | 0 | 0 | 190.4035 | 0 | 22% | 8.2263 | 0 | 21.19% | 0 | 41.7286
1115 | 734 | 542 | 125 | 8.4 | 13 | 186.3265 | 0 | 60.9503 | 0 | 0 | 0 | 185.0364 | 0 | 36% | 17.457 | 0 | 44.93% | 0 | 41.3977
1116 | 686 | 632 | 187 | 9.4 | 13.6 | 178.0235 | 0 | 68.27 | 0.4598 | 0 | 0 | 176.8434 | 0 | 49% | 25 | 0 | 78.93% | 0 | 41.2243
1117 | 734 | 678 | 186 | 9.1 | 14.4 | 194.3186 | 0 | 49.7798 | 24.7883 | 0 | 0 | 193.0898 | 0 | 64% | 8.1403 | 0 | 90% | 0 | 39.4126
1118 | 841 | 682 | 149 | 8.7 | 15 | 222.911 | -2.98e-14 | 40.7355 | 34.3645 | 0 | 0 | 221.5609 | 0 | 81% | 0 | 0 | 90% | 0 | 38.2163
1119 | 719 | 531 | 130 | 7.8 | 15.4 | 179.7724 | 0 | 38.3448 | 19.4999 | 42.5924 | 1.8451 | 138.8677 | 0 | 91% | 0 | 0 | 90% | 0 | 37.602
1120 | 562 | 360 | 121 | 7.4 | 15 | 122.5337 | 0 | 24.4013 | 11.5719 | 42.5937 | 15.399 | 81.3411 | 0 | 97% | 0 | 0 | 90% | 0 | 38.7759
1121 | 270 | 160 | 86 | 7.4 | 12.8 | 0 | 47.1826 | 10.8984 | 0 | 42.5924 | 15.4914 | 0 | 41.1169 | 94% | 0 | 18.2302 | 60.83% | 0 | 42.5495
1122 | 3 | 24 | 24 | 6.2 | 10.3 | 0 | 0.32399 | 0 | 0 | 57.3505 | 21.8966 | 0 | 55.7491 | 90% | 0 | 25 | 20.83% | 0 | 43.9473
1123 | 0 | 0 | 0 | 4.7 | 9.2 | 0 | 0 | 0 | 0 | 99.042 | 39.936 | 0 | 102.9977 | 83% | 0 | 6.7698 | 10% | 0 | 43.7505
1124 | 0 | 0 | 0 | 5.2 | 8.8 | 0 | 0 | 0 | 0 | 108.8432 | 44.2622 | 0 | 111.4383 | 74% | 0 | 0 | 10% | 0 | 41.8008
1125 | 0 | 0 | 0 | 4 | 8.1 | 0 | 0 | 0 | 0 | 101.3157 | 41.125 | 0 | 101.4344 | 67% | 0 | 0 | 10% | 0 | 38.9148
1126 | 0 | 0 | 0 | 4.4 | 7.2 | 0 | 0 | 0 | 0 | 94.0175 | 38.0822 | 0 | 92.6246 | 60% | 0 | 0 | 10% | 0 | 35.9335
1127 | 0 | 0 | 0 | 2.4 | 6.4 | 0 | 0 | 0 | 0 | 88.0887 | 35.5806 | 0 | 85.481 | 53% | 0 | 0 | 10% | 0 | 33.4156
1128 | 0 | 0 | 0 | 2.7 | 6 | 0 | 0 | 0 | 0 | 83.8414 | 33.7951 | 0 | 80.6738 | 47% | 0 | 0 | 10% | 0 | 31.569
1129 | 0 | 0 | 0 | 2.7 | 5.8 | 0 | 0 | 0 | 0 | 81.388 | 32.7067 | 0 | 78.3019 | 41% | 0 | 0 | 10% | 0 | 30.4069
1130 | 0 | 0 | 0 | 3.5 | 5.7 | 0 | 0 | 0 | 0 | 80.2526 | 32.1916 | 0 | 77.3437 | 35% | 0 | 0 | 10% | 0 | 29.8285
1131 | 0 | 0 | 0 | 3.6 | 5.7 | 0 | 0 | 0 | 0 | 80.4328 | 32.2747 | 0 | 77.6683 | 30% | 0 | 0 | 10% | 0 | 29.8587
1132 | 0 | 0 | 0 | 3.2 | 5.6 | 0 | 0 | 0 | 0 | 81.6274 | 32.824 | 0 | 78.9891 | 24% | 0 | 0 | 10% | 0 | 30.3628
1133 | 0 | 0 | 0 | 2.7 | 5.2 | 0 | 0 | 0 | 0 | 84.025 | 33.8941 | 0 | 81.6909 | 18% | 0 | 0 | 10% | 0 | 31.3925
1134 | 0 | 0 | 0 | 2.1 | 5.1 | 0 | 0 | 0 | 0 | 86.4194 | 34.9097 | 0 | 84.6128 | 11% | 0 | 0 | 10% | 0 | 32.377
1135 | 0 | 0 | 0 | 2.4 | 5.4 | 0 | 0 | 0 | 0 | 94.1099 | 38.1761 | 0 | 94.0832 | 4% | 0 | 0 | 10% | 0 | 35.6152
1136 | 11 | 42 | 40 | 2.6 | 6.3 | 0 | 1.8522 | 0 | 0 | 55.2322 | 22.4433 | 0 | 55.7979 | 0% | 0 | 0 | 10% | 0 | 19.9633
1137 | 57 | 153 | 136 | 2.9 | 8.6 | 0 | 13.52 | 6.7875 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.406
1138 | 72 | 222 | 183 | 3.6 | 10.5 | 0 | 20.3357 | 12.0872 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.7298
1139 | 431 | 469 | 217 | 5.6 | 12 | 83.4322 | 21.8013 | 46.2553 | 0 | 0 | 0 | 80.2172 | 0 | 6% | 6.3884 | 0 | 18.69% | 0 | 38.3802
1140 | 666 | 663 | 225 | 6.7 | 13.2 | 174.8298 | 0 | 65.2405 | 6.6142 | 0 | 0 | 172.1407 | 0 | 19% | 25 | 0 | 52.69% | 0 | 38.2965
1141 | 708 | 677 | 198 | 6.5 | 14 | 189.2773 | 0 | 63.6955 | 9.705 | 0 | 0 | 187.6734 | 0 | 33% | 25 | 0 | 86.69% | 0 | 36.5939
1142 | 680 | 624 | 188 | 6.6 | 14.5 | 178.1335 | 0 | 40.1301 | 27.0326 | 0 | 0 | 176.8184 | 0 | 46% | 2.4351 | 0 | 90% | 0 | 35.6651
1143 | 792 | 560 | 120 | 6 | 15 | 202.2857 | -4.05e-15 | 36.1006 | 26.488 | 42.5674 | 2.0933 | 160.7196 | 0 | 58% | 0 | 0 | 90% | 0 | 35.4679
1144 | 697 | 400 | 103 | 6.2 | 14.6 | 158.867 | 0 | 23.2394 | 19.5916 | 42.5762 | 15.4105 | 117.5916 | 0 | 67% | 0 | 0 | 90% | 0 | 36.746
1145 | 444 | 201 | 82 | 5.9 | 13.6 | 73.044 | 0 | 17.2163 | 0 | 42.5803 | 15.455 | 32.014 | 0 | 69% | 0 | 9.8162 | 74.29% | 0 | 41.3766
1146 | 67 | 35 | 26 | 5 | 11.6 | 0 | 7.6628 | 0 | 0 | 54.1193 | 20.441 | 0 | 52.0609 | 66% | 0 | 25 | 34.29% | 0 | 43.6545
1147 | 0 | 0 | 0 | 3.4 | 9.6 | 0 | 0 | 0 | 0 | 78.7771 | 31.1767 | 0 | 79.5599 | 60% | 0 | 15.1838 | 10% | 0 | 43.5832
1148 | 0 | 0 | 0 | 2.4 | 8.5 | 0 | 0 | 0 | 0 | 109.6789 | 44.6235 | 0 | 113.3737 | 51% | 0 | 0 | 10% | 0 | 41.9185
1149 | 0 | 0 | 0 | 2.7 | 8.3 | 0 | 0 | 0 | 0 | 101.4594 | 41.1788 | 0 | 102.6867 | 44% | 0 | 0 | 10% | 0 | 38.6706
1150 | 0 | 0 | 0 | 2.6 | 8.2 | 0 | 0 | 0 | 0 | 93.5217 | 37.8372 | 0 | 92.9127 | 37% | 0 | 0 | 10% | 0 | 35.4168
1151 | 0 | 0 | 0 | 2.6 | 7.1 | 0 | 0 | 0 | 0 | 88.0451 | 35.5429 | 0 | 86.1464 | 30% | 0 | 0 | 10% | 0 | 33.144
1152 | 0 | 0 | 0 | 2.7 | 6.4 | 0 | 0 | 0 | 0 | 84.8136 | 34.1955 | 0 | 82.3592 | 24% | 0 | 0 | 10% | 0 | 31.7791
1153 | 0 | 0 | 0 | 2.4 | 6 | 0 | 0 | 0 | 0 | 83.5437 | 33.6709 | 0 | 80.9629 | 18% | 0 | 0 | 10% | 0 | 31.2226
1154 | 0 | 0 | 0 | 2.6 | 6.2 | 0 | 0 | 0 | 0 | 83.5865 | 33.6841 | 0 | 81.1106 | 12% | 0 | 0 | 10% | 0 | 31.2019
1155 | 0 | 0 | 0 | 2.5 | 5.6 | 0 | 0 | 0 | 0 | 86.6463 | 34.9938 | 0 | 84.8266 | 6% | 0 | 0 | 10% | 0 | 32.477
1156 | 0 | 0 | 0 | 2.2 | 5.9 | 0 | 0 | 0 | 0 | 74.833 | 30.3822 | 0 | 75.1951 | 0% | 0 | 0 | 10% | 0 | 27.8665
1157 | 0 | 0 | 0 | 2.2 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.392
1158 | 0 | 0 | 0 | 2.6 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3678
1159 | 0 | 1 | 1 | 2.9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3442
1160 | 50 | 63 | 54 | 2.4 | 5.4 | 0 | 8.4892 | 0.35819 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9627
1161 | 288 | 238 | 149 | 3.2 | 8.8 | 0 | 57.5299 | 18.3988 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 16.1044
1162 | 290 | 369 | 234 | 5.5 | 11.3 | 56.2828 | 0 | 32.0029 | 0 | 0 | 0 | 53.8441 | 0 | 4% | 0 | 0 | 10% | 0 | 31.1008
1163 | 359 | 484 | 271 | 6.4 | 12.7 | 81.6636 | -1.49e-14 | 45.7958 | 0 | 0 | 0 | 79.4463 | 0 | 10% | 0 | 0 | 10% | 0 | 44.6678
1164 | 483 | 634 | 309 | 6.8 | 13.7 | 120.9873 | 0 | 63.8135 | 0 | 0 | 0 | 118.7614 | 0 | 19% | 15.4201 | 0 | 30.97% | 0 | 46.9133
1165 | 512 | 680 | 325 | 6.7 | 14.6 | 130.9948 | 0 | 67.2455 | 0 | 0 | 0 | 129.3621 | 0 | 29% | 19.8132 | 0 | 57.92% | 0 | 45.8485
1166 | 208 | 471 | 328 | 6.9 | 14.6 | 0 | 51.8633 | 40.2835 | 0 | 42.4971 | 0 | 0 | 39.9962 | 26% | 8.4637 | 0 | 69.43% | 0 | 29.9184
1167 | 200 | 438 | 319 | 6.4 | 14.6 | 0 | 46.9376 | 36.5984 | 0 | 43.7255 | 14.6594 | 0 | 41.224 | 23% | 5.0999 | 0 | 76.36% | 0 | 43.7651
1168 | 95 | 256 | 208 | 6 | 14 | 0 | 26.2568 | 15.4267 | 0 | 42.4754 | 15.4007 | 0 | 40.0593 | 20% | 0 | 17.1141 | 48.98% | 0 | 45.5606
1169 | 18 | 119 | 113 | 5.7 | 12.5 | 0 | 4.081 | 2.4746 | 0 | 64.47 | 24.88 | 0 | 61.9572 | 15% | 0 | 24.3632 | 10% | 0 | 49.2771
1170 | 2 | 28 | 27 | 5 | 11.2 | 0 | 0.24148 | 0 | 0 | 127.0793 | 51.7508 | 0 | 133.6984 | 5% | 0 | 0 | 10% | 0 | 49.1747
1171 | 0 | 0 | 0 | 3.7 | 9.9 | 0 | 0 | 0 | 0 | 63.7761 | 26.0035 | 0 | 66.6363 | 0% | 0 | 0 | 10% | 0 | 23.6997
1172 | 0 | 0 | 0 | 2.8 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1678
1173 | 0 | 0 | 0 | 3.5 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.148
1174 | 0 | 0 | 0 | 3.3 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1285
1175 | 0 | 0 | 0 | 2.3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1094
1176 | 0 | 0 | 0 | 2.6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0907
1177 | 0 | 0 | 0 | 2.1 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0723
1178 | 0 | 0 | 0 | 2.1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0543
1179 | 0 | 0 | 0 | 1.6 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0366
1180 | 0 | 0 | 0 | 1.8 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0193
1181 | 0 | 0 | 0 | 1.3 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0023
1182 | 0 | 0 | 0 | 2 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9854
1183 | 0 | 0 | 0 | 2.4 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.969
1184 | 47 | 57 | 49 | 2.1 | 6.6 | 0 | 8.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9529
1185 | 191 | 227 | 162 | 1.9 | 9.1 | 0 | 45.6914 | 15.2203 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 13.2834
1186 | 436 | 401 | 193 | 1.9 | 12.1 | 79.5364 | 20.3579 | 37.7261 | 0 | 0 | 0 | 74.6275 | 0 | 6% | 0 | 0 | 10% | 0 | 36.3375
1187 | 576 | 586 | 244 | 3.8 | 13.2 | 146.3882 | 0 | 59.7776 | 0 | 0 | 0 | 142.4862 | 0 | 17% | 10.1921 | 0 | 23.86% | 0 | 47.8686
1188 | 593 | 646 | 248 | 4.7 | 14.1 | 155.3605 | 2.98e-14 | 67.3568 | 0 | 0 | 0 | 152.9953 | 0 | 29% | 19.4138 | 0 | 50.26% | 0 | 46.1243
1189 | 524 | 635 | 271 | 4.6 | 14.6 | 136.5301 | 2.98e-14 | 64.6075 | 0 | 0 | 0 | 134.8818 | 0 | 39% | 17.6543 | 0 | 74.27% | 0 | 45.2871
1190 | 494 | 605 | 277 | 4.1 | 15.1 | 125.9802 | 0 | 57.7867 | 2.0622 | 0 | 0 | 124.4957 | 0 | 48% | 11.5633 | 0 | 90% | 0 | 44.6397
1191 | 569 | 563 | 239 | 3.8 | 15.3 | 142.0978 | 0 | 46.837 | 9.7294 | 42.4757 | 0 | 101.0006 | 0 | 56% | 0 | 0 | 90% | 0 | 44.5747
1192 | 441 | 383 | 189 | 4.3 | 14.9 | 95.2493 | 0 | 35.4672 | 0 | 42.4998 | 8.0789 | 54.4169 | 0 | 60% | 2.3402 | 5.4056 | 84.53% | 0 | 45.0488
1193 | 248 | 195 | 123 | 5.2 | 13.4 | 0 | 56.5545 | 13.0374 | 0 | 42.5051 | 15.4358 | 0 | 39.8628 | 57% | 0 | 21.7287 | 49.77% | 0 | 48.9141
1194 | 15 | 42 | 39 | 4.8 | 11 | 0 | 1.9067 | 0 | 0 | 70.3049 | 27.5423 | 0 | 67.3705 | 52% | 0 | 24.8548 | 10% | 0 | 50.0947
1195 | 0 | 0 | 0 | 3.6 | 9.4 | 0 | 0 | 0 | 0 | 126.3693 | 51.5463 | 0 | 132.3184 | 42% | 0 | 0 | 10% | 0 | 49.1016
1196 | 0 | 0 | 0 | 3.1 | 8.4 | 0 | 0 | 0 | 0 | 116.5101 | 47.489 | 0 | 119.3835 | 33% | 0 | 0 | 10% | 0 | 45.2757
1197 | 0 | 0 | 0 | 1.3 | 8.2 | 0 | 0 | 0 | 0 | 105.4022 | 42.8528 | 0 | 105.7958 | 25% | 0 | 0 | 10% | 0 | 40.7555
1198 | 0 | 0 | 0 | 2.1 | 8.3 | 0 | 0 | 0 | 0 | 99.1979 | 40.2282 | 0 | 98.2693 | 18% | 0 | 0 | 10% | 0 | 38.1664
1199 | 0 | 0 | 0 | 1.9 | 7.4 | 0 | 0 | 0 | 0 | 92.9744 | 37.6361 | 0 | 90.9713 | 11% | 0 | 0 | 10% | 0 | 35.5775
1200 | 0 | 0 | 0 | 1.9 | 6.9 | 0 | 0 | 0 | 0 | 89.076 | 35.992 | 0 | 86.3347 | 4% | 0 | 0 | 10% | 0 | 33.9115
1201 | 0 | 0 | 0 | 1.7 | 6.1 | 0 | 0 | 0 | 0 | 55.6965 | 22.5032 | 0 | 53.8842 | 0% | 0 | 0 | 10% | 0 | 20.4156
1202 | 0 | 0 | 0 | 1.9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0262
1203 | 0 | 0 | 0 | 1.5 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0091
1204 | 0 | 0 | 0 | 2 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9923
1205 | 0 | 0 | 0 | 2 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9758
1206 | 0 | 0 | 0 | 2.2 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9596
1207 | 0 | 0 | 0 | 1.8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9437
1208 | 54 | 55 | 46 | 2.3 | 4.6 | 0 | 9.3231 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.928
1209 | 304 | 225 | 129 | 1.2 | 7.7 | 0 | 61.9498 | 17.5126 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 15.6024
1210 | 493 | 416 | 184 | 2.1 | 10.6 | 113.1301 | 0 | 40.4873 | 0 | 0 | 0 | 107.3505 | 0 | 8% | 0 | 0 | 10% | 0 | 39.0884
1211 | 608 | 572 | 211 | 4.2 | 12 | 155.2943 | 0 | 60.0718 | 0 | 0 | 0 | 152.4484 | 0 | 20% | 11.0486 | 0 | 25.03% | 0 | 47.2206
1212 | 654 | 662 | 224 | 3.6 | 13 | 174.5589 | -2.98e-14 | 70.9809 | 0 | 0 | 0 | 172.5291 | 0 | 33% | 23.7293 | 0 | 57.3% | 0 | 45.2526
1213 | 679 | 692 | 224 | 2.4 | 14.1 | 184.4849 | 0 | 71.5176 | 1.4779 | 0 | 0 | 182.7819 | 0 | 47% | 24.0456 | 0 | 90% | 0 | 45.3562
1214 | 664 | 652 | 216 | 1.8 | 14.9 | 177.611 | 0 | 47.0169 | 20.9938 | 42.5194 | 0 | 136.7295 | 0 | 58% | 0 | 0 | 90% | 0 | 44.4203
1215 | 575 | 528 | 197 | 2.7 | 15.4 | 144.8793 | 0 | 34.3495 | 19.4939 | 42.5399 | 11.4935 | 103.9173 | 0 | 65% | 0 | 0 | 90% | 0 | 43.9233
1216 | 59 | 180 | 150 | 3.7 | 14.4 | 0 | 16.3933 | 8.0406 | 0 | 42.546 | 15.4085 | 0 | 39.9068 | 62% | 0 | 22.1699 | 54.53% | 0 | 44.3295
1217 | 1 | 85 | 84 | 4.6 | 13 | 0 | 0.22913 | 0.11011 | 0 | 65.8363 | 25.4628 | 0 | 62.8472 | 58% | 0 | 25 | 14.53% | 0 | 48.2702
1218 | 3 | 29 | 29 | 4.1 | 11.4 | 0 | 0.40042 | 0 | 0 | 120.9141 | 49.104 | 0 | 126.1907 | 48% | 0 | 2.8301 | 10% | 0 | 49.4776
1219 | 0 | 0 | 0 | 3.8 | 9.7 | 0 | 0 | 0 | 0 | 125.875 | 51.3251 | 0 | 130.6519 | 38% | 0 | 0 | 10% | 0 | 49.0871
1220 | 0 | 0 | 0 | 2.9 | 8.9 | 0 | 0 | 0 | 0 | 117.6809 | 47.9542 | 0 | 120.0347 | 29% | 0 | 0 | 10% | 0 | 45.8913
1221 | 0 | 0 | 0 | 3.1 | 8.5 | 0 | 0 | 0 | 0 | 107.4246 | 43.6839 | 0 | 107.5859 | 21% | 0 | 0 | 10% | 0 | 41.7126
1222 | 0 | 0 | 0 | 2 | 8 | 0 | 0 | 0 | 0 | 101.1147 | 41.0473 | 0 | 100.0566 | 13% | 0 | 0 | 10% | 0 | 39.1015
1223 | 0 | 0 | 0 | 2.4 | 8.7 | 0 | 0 | 0 | 0 | 95.295 | 38.5703 | 0 | 93.2895 | 6% | 0 | 0 | 10% | 0 | 36.6217
1224 | 0 | 0 | 0 | 2.2 | 9.1 | 0 | 0 | 0 | 0 | 83.9145 | 33.9019 | 0 | 81.6897 | 0% | 0 | 0 | 10% | 0 | 31.9361
1225 | 0 | 0 | 0 | 1.7 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8843
1226 | 0 | 0 | 0 | 2.1 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8699
1227 | 0 | 0 | 0 | 0.9 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8558
1228 | 0 | 0 | 0 | 2.3 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8418
1229 | 0 | 0 | 0 | 3.3 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8281
1230 | 0 | 0 | 0 | 2.4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8148
1231 | 0 | 1 | 1 | 1.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8017
1232 | 95 | 67 | 51 | 3 | 5.9 | 0 | 16.5412 | 0.85761 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.93108
1233 | 375 | 246 | 128 | 2.6 | 8.4 | 53.8984 | 14.306 | 20.5605 | 0 | 0 | 0 | 51.1927 | 0 | 4% | 0 | 0 | 10% | 0 | 19.4147
1234 | 572 | 439 | 169 | 4.3 | 10.8 | 132.8715 | 0 | 44.5932 | 0 | 0 | 0 | 129.1327 | 0 | 14% | 0 | 0 | 10% | 0 | 42.9972
1235 | 670 | 590 | 191 | 4.6 | 12.2 | 172.8973 | -2.98e-14 | 61.959 | 0 | 42.3717 | 0 | 131.3548 | 0 | 24% | 16.8189 | 0 | 32.87% | 0 | 42.628
1236 | 712 | 680 | 202 | 4.9 | 13.2 | 190.7295 | 0 | 59.4638 | 13.218 | 42.4859 | 13.3207 | 149.6795 | 0 | 35% | 24.9429 | 0 | 66.8% | 0 | 45.5847
1237 | 732 | 709 | 202 | 4.5 | 14 | 198.9678 | 0 | 48.5736 | 26.5264 | 42.5306 | 15.4207 | 157.9027 | 0 | 47% | 17.0617 | 0 | 90% | 0 | 44.6559
1238 | 713 | 668 | 198 | 3.3 | 14.8 | 191.468 | 0 | 30.848 | 40.1191 | 42.5489 | 15.3917 | 150.4472 | 0 | 59% | 0 | 0 | 90% | 0 | 44.0232
1239 | 680 | 566 | 176 | 3 | 15.4 | 174.794 | 0 | 30.3819 | 28.5203 | 42.5621 | 15.3687 | 133.7078 | 0 | 69% | 0 | 0 | 90% | 0 | 43.6821
1240 | 584 | 409 | 150 | 3.8 | 15.3 | 133.4188 | 0 | 30.3653 | 10.2226 | 42.5695 | 15.3761 | 92.3415 | 0 | 76% | 0 | 0 | 90% | 0 | 44.0582
1241 | 394 | 218 | 106 | 4.8 | 14.1 | 65.3449 | 0 | 16.911 | 0 | 42.5726 | 15.4315 | 24.3854 | 0 | 78% | 0 | 16.7878 | 63.14% | 0 | 48.0877
1242 | 84 | 46 | 35 | 4.8 | 11.9 | 0 | 11.7452 | 0 | 0 | 67.756 | 26.3687 | 0 | 65.7962 | 73% | 0 | 25 | 23.14% | 0 | 49.5911
1243 | 0 | 0 | 0 | 4 | 9.7 | 0 | 0 | 0 | 0 | 106.7717 | 43.1497 | 0 | 111.3148 | 65% | 0 | 8.2122 | 10% | 0 | 48.5803
1244 | 0 | 0 | 0 | 2.8 | 8.4 | 0 | 0 | 0 | 0 | 116.6563 | 47.548 | 0 | 120.8795 | 56% | 0 | 0 | 10% | 0 | 45.0557
1245 | 0 | 0 | 0 | 2.3 | 7.3 | 0 | 0 | 0 | 0 | 105.9909 | 43.1278 | 0 | 107.1997 | 47% | 0 | 0 | 10% | 0 | 40.8627
1246 | 0 | 0 | 0 | 1.8 | 7 | 0 | 0 | 0 | 0 | 99.3386 | 40.3292 | 0 | 98.9212 | 40% | 0 | 0 | 10% | 0 | 38.1454
1247 | 0 | 0 | 0 | 2.3 | 6.8 | 0 | 0 | 0 | 0 | 93.3701 | 37.8194 | 0 | 91.8285 | 33% | 0 | 0 | 10% | 0 | 35.656
1248 | 0 | 0 | 0 | 2.1 | 6.7 | 0 | 0 | 0 | 0 | 89.4487 | 36.1512 | 0 | 87.1052 | 26% | 0 | 0 | 10% | 0 | 33.9733
1249 | 0 | 0 | 0 | 1.3 | 5.5 | 0 | 0 | 0 | 0 | 88.2933 | 35.6933 | 0 | 85.8361 | 20% | 0 | 0 | 10% | 0 | 33.4783
1250 | 0 | 0 | 0 | 3.2 | 6.7 | 0 | 0 | 0 | 0 | 88.3473 | 35.6846 | 0 | 86.0163 | 13% | 0 | 0 | 10% | 0 | 33.4317
1251 | 0 | 0 | 0 | 3.1 | 7.1 | 0 | 0 | 0 | 0 | 90.955 | 36.7825 | 0 | 89.2731 | 7% | 0 | 0 | 10% | 0 | 34.493
1252 | 0 | 0 | 0 | 2.9 | 7.1 | 0 | 0 | 0 | 0 | 89.429 | 36.3203 | 0 | 89.6186 | 0% | 0 | 0 | 10% | 0 | 34.013
1253 | 0 | 0 | 0 | 3.2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1677
1254 | 0 | 0 | 0 | 2.2 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1478
1255 | 0 | 1 | 1 | 2.6 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1283
1256 | 226 | 82 | 47 | 1.2 | 6.8 | 0 | 39.687 | 2.9505 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.84141
1257 | 577 | 278 | 96 | 0.6 | 9.1 | 92.4259 | 23.5605 | 26.493 | 0 | 0 | 0 | 88.5373 | 0 | 7% | 0 | 0 | 10% | 0 | 24.9652
1258 | 778 | 479 | 110 | 0.8 | 13.4 | 190.5915 | 0 | 52.0383 | 0 | 0 | 0 | 187.6295 | 0 | 21% | 3.553 | 0 | 14.83% | 0 | 46.3845
1259 | 937 | 647 | 90 | 0.9 | 16 | 252.4677 | 0 | 72.4646 | 0 | 0 | 0 | 250.3433 | 0 | 40% | 24.4126 | 0 | 48.03% | 0 | 45.359
1260 | 995 | 744 | 78 | 1.3 | 17.9 | 276.7936 | 0 | 72.9106 | 2.1894 | 0 | 0 | 275.186 | 0 | 61% | 25 | 0 | 82.03% | 0 | 44.9408
1261 | 996 | 766 | 78 | 2.5 | 18.7 | 278.9446 | 0 | 52.708 | 22.392 | 0 | 0 | 277.6128 | 0 | 82% | 5.8579 | 0 | 90% | 0 | 43.79
1262 | 983 | 723 | 77 | 3.4 | 19.5 | 244.0494 | 29.3286 | 45.8375 | 29.2625 | 0 | 0 | 242.9405 | 0 | 100% | 0 | 0 | 90% | 0 | 43.0594
1263 | 944 | 614 | 73 | 4.5 | 19.2 | 0 | 273.3519 | 43.6818 | 24.2061 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4224
1264 | 863 | 449 | 67 | 4.1 | 18.4 | 40.7562 | 192.8517 | 43.5166 | 5.0201 | 42.5823 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4474
1265 | 685 | 245 | 54 | 3.9 | 17.6 | 42.1646 | 106.551 | 23.7025 | 0 | 42.5799 | 12.3873 | 0 | 0 | 100% | 0 | 9.2758 | 75.16% | 0 | 45.9836
1266 | 225 | 53 | 22 | 3.2 | 15.4 | 0 | 32.8872 | 0.4148 | 0 | 62.3661 | 23.8266 | 0 | 60.9595 | 96% | 0 | 25 | 35.16% | 0 | 47.1803
1267 | 0 | 0 | 0 | 1.7 | 11.8 | 0 | 0 | 0 | 0 | 84.982 | 33.7128 | 0 | 86.7815 | 89% | 0 | 15.7242 | 10% | 0 | 46.5082
1268 | 0 | 0 | 0 | 0.9 | 9.4 | 0 | 0 | 0 | 0 | 113.2767 | 46.0902 | 0 | 116.9689 | 80% | 0 | 0 | 10% | 0 | 43.5816
1269 | 0 | 0 | 0 | 0.6 | 8.2 | 0 | 0 | 0 | 0 | 104.1018 | 42.3002 | 0 | 104.3714 | 73% | 0 | 0 | 10% | 0 | 40.2002
1270 | 0 | 0 | 0 | 0.8 | 7.7 | 0 | 0 | 0 | 0 | 98.6869 | 40.0303 | 0 | 97.6407 | 65% | 0 | 0 | 10% | 0 | 38.0025
1271 | 0 | 0 | 0 | 1 | 7.4 | 0 | 0 | 0 | 0 | 92.3423 | 37.3606 | 0 | 90.185 | 58% | 0 | 0 | 10% | 0 | 35.3243
1272 | 0 | 0 | 0 | 0.7 | 7.3 | 0 | 0 | 0 | 0 | 87.8408 | 35.4496 | 0 | 84.9518 | 52% | 0 | 0 | 10% | 0 | 33.3585
1273 | 0 | 0 | 0 | 1 | 6.9 | 0 | 0 | 0 | 0 | 85.9812 | 34.6748 | 0 | 82.9915 | 46% | 0 | 0 | 10% | 0 | 32.5077
1274 | 0 | 0 | 0 | 1.2 | 6.8 | 0 | 0 | 0 | 0 | 84.9456 | 34.2401 | 0 | 81.9868 | 39% | 0 | 0 | 10% | 0 | 32.0032
1275 | 0 | 0 | 0 | 2.5 | 7.5 | 0 | 0 | 0 | 0 | 84.7763 | 34.1477 | 0 | 81.97 | 33% | 0 | 0 | 10% | 0 | 31.8494
1276 | 0 | 0 | 0 | 2.7 | 8.4 | 0 | 0 | 0 | 0 | 87.5993 | 35.3117 | 0 | 85.4705 | 27% | 0 | 0 | 10% | 0 | 32.9583
1277 | 0 | 0 | 0 | 1.3 | 7.4 | 0 | 0 | 0 | 0 | 91.4836 | 36.9968 | 0 | 90.2719 | 20% | 0 | 0 | 10% | 0 | 34.6082
1278 | 0 | 0 | 0 | 1.9 | 7.7 | 0 | 0 | 0 | 0 | 96.9901 | 39.3183 | 0 | 96.9107 | 13% | 0 | 0 | 10% | 0 | 36.9151
1279 | 1 | 1 | 1 | 1.3 | 7.1 | 0 | 0 | 0 | 0 | 105.784 | 43.0505 | 0 | 107.3933 | 5% | 0 | 0 | 10% | 0 | 40.6499
1280 | 471 | 97 | 32 | 1.7 | 9.2 | 49.1093 | 12.9364 | 6.8372 | 0 | 91.2664 | 36.8441 | 0 | 42.2974 | 2% | 0 | 0 | 10% | 0 | 42.3858
1281 | 805 | 311 | 59 | 1.3 | 14.8 | 166.156 | 0 | 33.2606 | 0 | 43.3272 | 15.7142 | 122.1422 | 0 | 11% | 4.5981 | 0 | 16.25% | 0 | 42.4807
1282 | 911 | 505 | 71 | 1.2 | 18.1 | 226.2825 | 0 | 53.5644 | 2.0447 | 42.5841 | 15.2366 | 184.5559 | 0 | 25% | 25 | 0 | 50.25% | 0 | 41.352
1283 | 958 | 654 | 80 | 1.5 | 20.4 | 258.5081 | 0 | 53.7413 | 18.3838 | 42.6019 | 15.1024 | 217.0067 | 0 | 41% | 25 | 0 | 84.25% | 0 | 41.0811
1284 | 990 | 752 | 85 | 2.2 | 22.3 | 275.383 | 0 | 32.2735 | 42.8265 | 42.6085 | 14.9744 | 233.9438 | 0 | 58% | 4.2254 | 0 | 90% | 0 | 40.0707
1285 | 982 | 776 | 93 | 2 | 23.2 | 275.7889 | 0 | 26.4746 | 48.6254 | 42.6104 | 14.9078 | 234.2448 | 0 | 76% | 0 | 0 | 90% | 0 | 38.4002
1286 | 910 | 716 | 111 | 3.6 | 23.7 | 250.017 | 0 | 24.9937 | 50.1063 | 42.6113 | 14.8695 | 208.355 | 0 | 91% | 0 | 0 | 90% | 0 | 37.098
1287 | 690 | 560 | 156 | 4.6 | 23.4 | 166.2171 | 13.2842 | 19.9411 | 36.759 | 42.6109 | 14.8925 | 124.3778 | 0 | 100% | 0 | 0 | 90% | 0 | 36.7901
1288 | 546 | 412 | 162 | 4.9 | 22.5 | 42.1527 | 100.2858 | 21.5203 | 16.8151 | 42.6097 | 14.96 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.1914
1289 | 221 | 203 | 133 | 4.8 | 20.4 | 0 | 51.1853 | 12.4017 | 0 | 42.6061 | 15.1039 | 0 | 41.1147 | 97% | 0 | 15.3354 | 65.46% | 0 | 40.7847
1290 | 32 | 50 | 44 | 3 | 17.9 | 0 | 4.8798 | 0 | 0 | 54.4235 | 20.2598 | 0 | 52.7549 | 93% | 0 | 25 | 25.46% | 0 | 42.339
1291 | 0 | 0 | 0 | 1.3 | 13.3 | 0 | 0 | 0 | 0 | 89.5917 | 35.6666 | 0 | 92.2055 | 86% | 0 | 9.6646 | 10% | 0 | 42.4018
1292 | 0 | 0 | 0 | 0.7 | 11.2 | 0 | 0 | 0 | 0 | 106.543 | 43.1896 | 0 | 108.8056 | 78% | 0 | 0 | 10% | 0 | 40.7104
1293 | 0 | 0 | 0 | 1 | 10.2 | 0 | 0 | 0 | 0 | 98.903 | 40.0196 | 0 | 98.5869 | 71% | 0 | 0 | 10% | 0 | 37.8068
1294 | 0 | 0 | 0 | 1.6 | 10.8 | 0 | 0 | 0 | 0 | 92.6108 | 37.337 | 0 | 90.971 | 64% | 0 | 0 | 10% | 0 | 35.1673
1295 | 0 | 0 | 0 | 1.3 | 10.1 | 0 | 0 | 0 | 0 | 86.4218 | 34.743 | 0 | 83.6201 | 58% | 0 | 0 | 10% | 0 | 32.5443
1296 | 0 | 0 | 0 | 0.9 | 9.3 | 0 | 0 | 0 | 0 | 81.974 | 32.861 | 0 | 78.8252 | 52% | 0 | 0 | 10% | 0 | 30.5885
1297 | 0 | 0 | 0 | 1.3 | 9.3 | 0 | 0 | 0 | 0 | 80.4345 | 32.158 | 0 | 77.5086 | 46% | 0 | 0 | 10% | 0 | 29.807
1298 | 0 | 0 | 0 | 1.7 | 9.7 | 0 | 0 | 0 | 0 | 79.7893 | 31.8486 | 0 | 77.0324 | 40% | 0 | 0 | 10% | 0 | 29.436
1299 | 0 | 0 | 0 | 2.3 | 10.1 | 0 | 0 | 0 | 0 | 80.0501 | 31.9516 | 0 | 77.4299 | 34% | 0 | 0 | 10% | 0 | 29.4887
1300 | 0 | 0 | 0 | 2.5 | 9.8 | 0 | 0 | 0 | 0 | 81.3731 | 32.569 | 0 | 78.8733 | 29% | 0 | 0 | 10% | 0 | 30.0635
1301 | 0 | 0 | 0 | 3.7 | 10.6 | 0 | 0 | 0 | 0 | 83.058 | 33.3045 | 0 | 80.6838 | 23% | 0 | 0 | 10% | 0 | 30.7629
1302 | 0 | 0 | 0 | 4.4 | 10 | 0 | 0 | 0 | 0 | 85.387 | 34.3131 | 0 | 83.5155 | 16% | 0 | 0 | 10% | 0 | 31.7395
1303 | 1 | 2 | 2 | 4 | 9.1 | 0 | 0 | 0 | 0 | 92.8377 | 37.5142 | 0 | 92.6525 | 9% | 0 | 0 | 10% | 0 | 34.9125
1304 | 325 | 89 | 40 | 4.3 | 9.9 | 0 | 58.059 | 4.2657 | 0 | 88.011 | 35.4288 | 0 | 86.6388 | 3% | 0 | 0 | 10% | 0 | 37.1225
1305 | 660 | 288 | 75 | 4.4 | 13.4 | 107.1257 | 27.3422 | 28.4581 | 0 | 42.8313 | 15.5745 | 70.8971 | 7.8807 | 8% | 4.5925 | 0 | 16.25% | 0 | 37.6928
1306 | 810 | 481 | 90 | 5.1 | 15.7 | 197.2311 | 0 | 48.9822 | 2.5027 | 42.5322 | 15.3436 | 154.8449 | 0 | 19% | 25 | 0 | 50.25% | 0 | 37.1566
1307 | 905 | 640 | 92 | 7.2 | 16.6 | 239.0673 | 0 | 49.567 | 20.6333 | 42.5804 | 15.3162 | 197.0874 | 0 | 34% | 25 | 0 | 84.25% | 0 | 37.3251
1308 | 937 | 739 | 100 | 7 | 17 | 256.5008 | 0 | 28.4855 | 46.6145 | 42.5975 | 15.3019 | 214.719 | 0 | 50% | 4.231 | 0 | 90% | 0 | 36.8113
1309 | 922 | 769 | 120 | 7 | 16.9 | 254.5964 | 0 | 22.7284 | 52.3716 | 42.6027 | 15.3088 | 212.7707 | 0 | 65% | 0 | 0 | 90% | 0 | 35.2863
1310 | 815 | 681 | 134 | 6.7 | 16.9 | 219.1788 | 0 | 21.3454 | 51.48 | 42.6054 | 15.3098 | 177.3683 | 0 | 78% | 0 | 0 | 90% | 0 | 34.2073
1311 | 864 | 622 | 115 | 6.6 | 17.4 | 225.2992 | 0 | 18.7756 | 47.8707 | 42.606 | 15.283 | 183.1139 | 0 | 92% | 0 | 0 | 90% | 0 | 33.8945
1312 | 811 | 450 | 83 | 7 | 17 | 154.9918 | 42.7138 | 17.8573 | 29.4082 | 42.6061 | 15.305 | 113.0739 | 0 | 100% | 0 | 0 | 90% | 0 | 34.7216
1313 | 469 | 208 | 66 | 6.3 | 15.5 | 42.1532 | 52.472 | 16.4786 | 0 | 42.6051 | 15.3795 | 0 | 0 | 100% | 0 | 6.5737 | 79.48% | 0 | 39.1446
1314 | 113 | 45 | 28 | 4.7 | 13.5 | 0 | 17.9452 | 0 | 0 | 50.8287 | 18.9315 | 0 | 49.2946 | 96% | 0 | 25 | 39.48% | 0 | 41.8777
1315 | 0 | 0 | 0 | 5.2 | 10.5 | 0 | 0 | 0 | 0 | 67.7831 | 26.3858 | 0 | 67.9069 | 91% | 0 | 18.4263 | 10% | 0 | 41.8702
1316 | 0 | 0 | 0 | 4.5 | 9 | 0 | 0 | 0 | 0 | 105.9274 | 43.0376 | 0 | 108.9639 | 83% | 0 | 0 | 10% | 0 | 40.3445
1317 | 0 | 0 | 0 | 2.3 | 8.3 | 0 | 0 | 0 | 0 | 97.4165 | 39.4729 | 0 | 97.0686 | 76% | 0 | 0 | 10% | 0 | 37.2008
1318 | 0 | 0 | 0 | 1.8 | 8.4 | 0 | 0 | 0 | 0 | 90.4833 | 36.533 | 0 | 88.5587 | 69% | 0 | 0 | 10% | 0 | 34.3141
1319 | 0 | 0 | 0 | 1.3 | 7.8 | 0 | 0 | 0 | 0 | 85.4365 | 34.415 | 0 | 82.686 | 63% | 0 | 0 | 10% | 0 | 32.1478
1320 | 0 | 0 | 0 | 1.7 | 6.5 | 0 | 0 | 0 | 0 | 82.1513 | 33.0351 | 0 | 79.2315 | 57% | 0 | 0 | 10% | 0 | 30.6885
1321 | 0 | 0 | 0 | 2.2 | 6.4 | 0 | 0 | 0 | 0 | 81.5029 | 32.7415 | 0 | 78.796 | 51% | 0 | 0 | 10% | 0 | 30.3192
1322 | 0 | 0 | 0 | 1.2 | 5.3 | 0 | 0 | 0 | 0 | 81.8371 | 32.9232 | 0 | 79.2934 | 45% | 0 | 0 | 10% | 0 | 30.4428
1323 | 0 | 0 | 0 | 0.8 | 4.7 | 0 | 0 | 0 | 0 | 85.0114 | 34.3206 | 0 | 82.9629 | 39% | 0 | 0 | 10% | 0 | 31.7911
1324 | 0 | 0 | 0 | 1.5 | 5.2 | 0 | 0 | 0 | 0 | 95.6306 | 38.8179 | 0 | 95.943 | 32% | 0 | 0 | 10% | 0 | 36.2476
1325 | 0 | 0 | 0 | 2.7 | 5.8 | 0 | 0 | 0 | 0 | 110.3447 | 44.9939 | 0 | 113.4322 | 24% | 0 | 0 | 10% | 0 | 42.4414
1326 | 0 | 0 | 0 | 2.8 | 6.6 | 0 | 0 | 0 | 0 | 118.7358 | 48.4783 | 0 | 123.0532 | 14% | 0 | 0 | 10% | 0 | 46.0122
1327 | 0 | 1 | 1 | 4.1 | 6.7 | 0 | 0 | 0 | 0 | 122.311 | 49.9632 | 0 | 126.7724 | 5% | 0 | 0 | 10% | 0 | 47.6035
1328 | 309 | 95 | 41 | 2.5 | 7.4 | 0 | 55.6786 | 4.0965 | 0 | 63.6259 | 25.9279 | 0 | 64.7728 | 0% | 0 | 0 | 10% | 0 | 27.8669
1329 | 696 | 299 | 71 | 3 | 9.3 | 115.0337 | 29.3821 | 30.2385 | 0 | 0 | 0 | 111.0714 | 0 | 8% | 0 | 0 | 10% | 0 | 28.5246
1330 | 869 | 497 | 75 | 4 | 12.5 | 214.096 | 0 | 54.4131 | 0 | 0 | 0 | 211.9358 | 0 | 24% | 6.3224 | 0 | 18.6% | 0 | 45.7719
1331 | 949 | 652 | 74 | 4.1 | 15.3 | 254.6046 | 0 | 72.1202 | 0 | 0 | 0 | 253.058 | 0 | 44% | 24.1714 | 0 | 51.47% | 0 | 45.2215
1332 | 979 | 746 | 77 | 5.3 | 17 | 270.2726 | 0 | 72.9988 | 2.1012 | 0 | 0 | 268.9766 | 0 | 64% | 25 | 0 | 85.47% | 0 | 45.0744
1333 | 985 | 772 | 77 | 5.7 | 17.3 | 274.0661 | 0 | 50.5471 | 24.5529 | 0 | 0 | 272.902 | 0 | 85% | 3.3297 | 0 | 90% | 0 | 44.1938
1334 | 984 | 733 | 72 | 5.6 | 17.3 | 205.0241 | 71.3683 | 45.77 | 29.33 | 0 | 0 | 204.176 | 0 | 100% | 0 | 0 | 90% | 0 | 43.3492
1335 | 957 | 627 | 67 | 5.1 | 17.1 | 0 | 278.5976 | 44.2294 | 24.5411 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.8342
1336 | 898 | 466 | 59 | 4.8 | 16.7 | 40.7371 | 203.798 | 43.1163 | 6.974 | 42.5971 | 0.81049 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.7085
1337 | 771 | 267 | 45 | 4.7 | 16 | 42.1584 | 128.9345 | 26.3282 | 0 | 42.5947 | 15.352 | 0 | 0 | 100% | 0 | 3.9974 | 83.6% | 0 | 46.3901
1338 | 318 | 68 | 22 | 4.3 | 13.7 | 0 | 51.6409 | 1.6137 | 0 | 62.0457 | 23.7725 | 0 | 60.6316 | 96% | 0 | 25 | 43.6% | 0 | 48.3271
1339 | 0 | 0 | 0 | 3.2 | 10.9 | 0 | 0 | 0 | 0 | 75.0461 | 29.5038 | 0 | 75.066 | 90% | 0 | 21.0026 | 10% | 0 | 47.5815
1340 | 0 | 0 | 0 | 3 | 9 | 0 | 0 | 0 | 0 | 114.0547 | 46.4335 | 0 | 118.8422 | 81% | 0 | 0 | 10% | 0 | 43.7115
1341 | 0 | 0 | 0 | 2.3 | 7.5 | 0 | 0 | 0 | 0 | 102.5562 | 41.67 | 0 | 102.8503 | 74% | 0 | 0 | 10% | 0 | 39.4829
1342 | 0 | 0 | 0 | 1.7 | 7.1 | 0 | 0 | 0 | 0 | 96.4672 | 39.1153 | 0 | 95.3282 | 66% | 0 | 0 | 10% | 0 | 37.0108
1343 | 0 | 0 | 0 | 1.1 | 6.3 | 0 | 0 | 0 | 0 | 90.7782 | 36.7264 | 0 | 88.5503 | 60% | 0 | 0 | 10% | 0 | 34.6119
1344 | 0 | 0 | 0 | 1.1 | 5.5 | 0 | 0 | 0 | 0 | 87.5527 | 35.3771 | 0 | 84.868 | 53% | 0 | 0 | 10% | 0 | 33.2051
1345 | 0 | 0 | 0 | 1.3 | 5.2 | 0 | 0 | 0 | 0 | 86.4159 | 34.9031 | 0 | 83.7294 | 47% | 0 | 0 | 10% | 0 | 32.6632
1346 | 0 | 0 | 0 | 2.3 | 5.8 | 0 | 0 | 0 | 0 | 86.5734 | 34.9551 | 0 | 84.0955 | 41% | 0 | 0 | 10% | 0 | 32.6552
1347 | 0 | 0 | 0 | 1.7 | 6 | 0 | 0 | 0 | 0 | 88.811 | 35.8994 | 0 | 86.9128 | 34% | 0 | 0 | 10% | 0 | 33.5501
1348 | 0 | 0 | 0 | 1.4 | 4.6 | 0 | 0 | 0 | 0 | 97.5624 | 39.6458 | 0 | 97.5499 | 27% | 0 | 0 | 10% | 0 | 37.2578
1349 | 0 | 0 | 0 | 0.8 | 3.8 | 0 | 0 | 0 | 0 | 111.8559 | 45.6784 | 0 | 114.5094 | 18% | 0 | 0 | 10% | 0 | 43.2911
1350 | 0 | 0 | 0 | 2.3 | 5.2 | 0 | 0 | 0 | 0 | 118.3921 | 48.378 | 0 | 121.9495 | 9% | 0 | 0 | 10% | 0 | 46.0587
1351 | 3 | 2 | 2 | 2.2 | 6 | 0 | 0 | 0 | 0 | 114.7754 | 46.9014 | 0 | 118.2837 | 0% | 0 | 0 | 10% | 0 | 44.6774
1352 | 481 | 103 | 32 | 1.4 | 8.4 | 52.2763 | 13.7253 | 7.1085 | 0 | 0 | 0 | 50.4855 | 0 | 4% | 0 | 0 | 10% | 0 | 5.9416
1353 | 786 | 310 | 51 | 1.1 | 11.8 | 164.2619 | 0 | 32.0215 | 0 | 0 | 0 | 161.0144 | 0 | 16% | 0 | 0 | 10% | 0 | 30.1612
1354 | 912 | 506 | 59 | 2.8 | 14.5 | 227.0543 | 0 | 55.2484 | 0 | 0 | 0 | 225.188 | 0 | 33% | 7.4431 | 0 | 20.12% | 0 | 45.3461
1355 | 970 | 658 | 63 | 4.7 | 16.5 | 260.3229 | 0 | 72.3889 | 0 | 0 | 0 | 258.8604 | 0 | 53% | 24.7485 | 0 | 53.78% | 0 | 44.8316
1356 | 992 | 751 | 66 | 4 | 18.1 | 275.3636 | 0 | 72.8749 | 2.2251 | 0 | 0 | 274.0837 | 0 | 74% | 25 | 0 | 87.78% | 0 | 44.8708
1357 | 997 | 775 | 67 | 5.4 | 19.1 | 278.0109 | 0 | 48.5466 | 26.5534 | 0 | 0 | 276.8501 | 0 | 95% | 1.6319 | 0 | 90% | 0 | 43.8229
1358 | 984 | 732 | 66 | 6.2 | 19.3 | 72.9432 | 216.9588 | 44.5043 | 30.5957 | 0 | 0 | 72.6459 | 0 | 100% | 0 | 0 | 90% | 0 | 43.1367
1359 | 957 | 628 | 62 | 7 | 19.1 | 0 | 278.8168 | 44.4507 | 23.3683 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.665
1360 | 900 | 469 | 56 | 7.1 | 18.5 | 40.4198 | 204.647 | 43.8517 | 5.7433 | 42.5942 | 0.070016 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.61
1361 | 763 | 269 | 46 | 6.3 | 17.3 | 42.1582 | 127.1595 | 25.9676 | 0 | 42.5919 | 15.2834 | 0 | 0 | 100% | 0 | 4.5155 | 82.78% | 0 | 46.4788
1362 | 333 | 70 | 21 | 4.3 | 15.7 | 0 | 54.4451 | 1.7318 | 0 | 61.9921 | 23.6481 | 0 | 60.5771 | 96% | 0 | 25 | 42.77% | 0 | 48.3195
1363 | 0 | 0 | 0 | 2.2 | 12.9 | 0 | 0 | 0 | 0 | 75.9864 | 29.805 | 0 | 76.1932 | 90% | 0 | 20.4845 | 10% | 0 | 47.3644
1364 | 0 | 0 | 0 | 2.2 | 10.3 | 0 | 0 | 0 | 0 | 113.8705 | 46.2961 | 0 | 118.5144 | 81% | 0 | 0 | 10% | 0 | 43.5982
1365 | 0 | 0 | 0 | 1.3 | 9.5 | 0 | 0 | 0 | 0 | 102.7789 | 41.6873 | 0 | 103.0872 | 73% | 0 | 0 | 10% | 0 | 39.5084
1366 | 0 | 0 | 0 | 0.6 | 7.6 | 0 | 0 | 0 | 0 | 96.3151 | 39.0347 | 0 | 95.1209 | 66% | 0 | 0 | 10% | 0 | 36.9388
1367 | 0 | 0 | 0 | 0.4 | 6.2 | 0 | 0 | 0 | 0 | 90.7661 | 36.7243 | 0 | 88.5193 | 60% | 0 | 0 | 10% | 0 | 34.6149
1368 | 0 | 0 | 0 | 0.7 | 5.5 | 0 | 0 | 0 | 0 | 87.5362 | 35.3702 | 0 | 84.8357 | 53% | 0 | 0 | 10% | 0 | 33.2024
1369 | 0 | 0 | 0 | 0.4 | 5.6 | 0 | 0 | 0 | 0 | 86.7546 | 35.0367 | 0 | 84.1203 | 47% | 0 | 0 | 10% | 0 | 32.7999
1370 | 0 | 0 | 0 | 0.5 | 5 | 0 | 0 | 0 | 0 | 86.9181 | 35.1213 | 0 | 84.4894 | 40% | 0 | 0 | 10% | 0 | 32.8261
1371 | 0 | 0 | 0 | 0.8 | 5.5 | 0 | 0 | 0 | 0 | 89.4229 | 36.1722 | 0 | 87.6315 | 34% | 0 | 0 | 10% | 0 | 33.8287
1372 | 0 | 0 | 0 | 2.2 | 6.3 | 0 | 0 | 0 | 0 | 98.4229 | 39.9645 | 0 | 98.5366 | 26% | 0 | 0 | 10% | 0 | 37.5848
1373 | 0 | 0 | 0 | 0.9 | 4.9 | 0 | 0 | 0 | 0 | 111.7486 | 45.6068 | 0 | 114.3286 | 18% | 0 | 0 | 10% | 0 | 43.232
1374 | 0 | 0 | 0 | 1 | 4.8 | 0 | 0 | 0 | 0 | 118.3185 | 48.3583 | 0 | 121.8157 | 9% | 0 | 0 | 10% | 0 | 46.0492
1375 | 10 | 2 | 2 | 1.2 | 5.3 | 0 | 0 | 0 | 0 | 111.5905 | 45.617 | 0 | 114.9263 | 0% | 0 | 0 | 10% | 0 | 43.4075
1376 | 567 | 113 | 28 | 0.4 | 8.2 | 65.0213 | 16.8633 | 8.6545 | 0 | 0 | 0 | 62.7875 | 0 | 5% | 0 | 0 | 10% | 0 | 7.3786
1377 | 830 | 321 | 45 | 0.9 | 13.8 | 175.4423 | 0 | 33.3004 | 0 | 0 | 0 | 172.5566 | 0 | 18% | 0 | 0 | 10% | 0 | 31.3354
1378 | 935 | 515 | 53 | 1 | 16.9 | 234.7764 | 0 | 55.7623 | 0 | 0 | 0 | 232.9846 | 0 | 36% | 8.132 | 0 | 21.06% | 0 | 45.0958
1379 | 986 | 667 | 58 | 1.7 | 18 | 267.3105 | 0 | 72.8427 | 0 | 0 | 0 | 265.872 | 0 | 56% | 24.0832 | 0 | 53.81% | 0 | 45.8787
1380 | 1001 | 756 | 62 | 1.7 | 19.1 | 279.6901 | 0 | 72.4242 | 2.6758 | 0 | 0 | 278.4354 | 0 | 77% | 25 | 0 | 87.81% | 0 | 44.37
1381 | 1001 | 779 | 64 | 2 | 20.1 | 282.1299 | 0 | 48.2712 | 26.8288 | 0 | 0 | 280.9783 | 0 | 98% | 1.6083 | 0 | 90% | 0 | 43.5211
1382 | 980 | 734 | 67 | 4.8 | 19.5 | 25.3597 | 268.6244 | 44.0008 | 31.0992 | 0 | 0 | 25.2585 | 0 | 100% | 0 | 0 | 90% | 0 | 42.8532
1383 | 945 | 627 | 65 | 4.6 | 19.1 | 0 | 275.35 | 44.1113 | 23.1507 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.3755
1384 | 877 | 466 | 60 | 5 | 18.7 | 40.3714 | 198.9353 | 43.7117 | 4.8768 | 42.5941 | 0.042477 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4415
1385 | 736 | 267 | 48 | 4.7 | 17.8 | 42.1426 | 121.7476 | 25.0083 | 0 | 42.5917 | 15.2561 | 0 | 0 | 100% | 0 | 5.3227 | 81.48% | 0 | 46.2886
1386 | 304 | 71 | 23 | 3.5 | 16.1 | 0 | 50.0374 | 1.435 | 0 | 62.1752 | 23.7062 | 0 | 60.764 | 96% | 0 | 25 | 41.48% | 0 | 48.08
1387 | 0 | 0 | 0 | 2.4 | 12.9 | 0 | 0 | 0 | 0 | 76.2921 | 29.9271 | 0 | 76.6948 | 90% | 0 | 19.6773 | 10% | 0 | 46.6795
1388 | 0 | 0 | 0 | 0.7 | 10.2 | 0 | 0 | 0 | 0 | 112.9965 | 45.9355 | 0 | 117.3385 | 81% | 0 | 0 | 10% | 0 | 43.2638
1389 | 0 | 0 | 0 | 0.9 | 9.2 | 0 | 0 | 0 | 0 | 102.7292 | 41.6794 | 0 | 103.0327 | 73% | 0 | 0 | 10% | 0 | 39.4992
1390 | 0 | 0 | 0 | 0.6 | 8 | 0 | 0 | 0 | 0 | 96.9599 | 39.2926 | 0 | 95.879 | 66% | 0 | 0 | 10% | 0 | 37.1945
1391 | 0 | 0 | 0 | 1.1 | 8.5 | 0 | 0 | 0 | 0 | 91.7899 | 37.0865 | 0 | 89.7484 | 59% | 0 | 0 | 10% | 0 | 34.9805
1392 | 0 | 0 | 0 | 1 | 8.3 | 0 | 0 | 0 | 0 | 88.33 | 35.6231 | 0 | 85.738 | 53% | 0 | 0 | 10% | 0 | 33.4679
1393 | 0 | 0 | 0 | 0.9 | 7.6 | 0 | 0 | 0 | 0 | 87.5697 | 35.3249 | 0 | 85.0336 | 47% | 0 | 0 | 10% | 0 | 33.1044
1394 | 0 | 0 | 0 | 1.1 | 7.3 | 0 | 0 | 0 | 0 | 87.3315 | 35.2338 | 0 | 84.9163 | 40% | 0 | 0 | 10% | 0 | 32.9585
1395 | 0 | 0 | 0 | 0.7 | 7.4 | 0 | 0 | 0 | 0 | 89.3276 | 36.0778 | 0 | 87.4488 | 34% | 0 | 0 | 10% | 0 | 33.7547
1396 | 0 | 0 | 0 | 0.9 | 7.5 | 0 | 0 | 0 | 0 | 96.8141 | 39.2495 | 0 | 96.5675 | 26% | 0 | 0 | 10% | 0 | 36.8896
1397 | 0 | 0 | 0 | 0.5 | 6.5 | 0 | 0 | 0 | 0 | 106.9733 | 43.5643 | 0 | 108.6382 | 18% | 0 | 0 | 10% | 0 | 41.2052
1398 | 0 | 0 | 0 | 1.5 | 8.1 | 0 | 0 | 0 | 0 | 113.1052 | 46.0744 | 0 | 115.6461 | 9% | 0 | 0 | 10% | 0 | 43.7621
1399 | 22 | 3 | 3 | 1.2 | 8 | 0 | 0 | 0 | 0 | 116.8294 | 47.6379 | 0 | 119.7888 | 0% | 0 | 0 | 10% | 0 | 45.3857
1400 | 584 | 120 | 29 | 0.6 | 9.9 | 68.1738 | 17.5187 | 9.1029 | 0 | 0 | 0 | 65.8496 | 0 | 5% | 0 | 0 | 10% | 0 | 7.7953
1401 | 849 | 334 | 47 | 0.2 | 16.3 | 181.121 | 0 | 34.2181 | 0 | 0 | 0 | 178.2634 | 0 | 19% | 0 | 0 | 10% | 0 | 32.2036
1402 | 950 | 530 | 55 | 0.6 | 20.1 | 239.624 | 0 | 56.4879 | 0 | 0 | 0 | 237.8507 | 0 | 37% | 10.4384 | 0 | 24.2% | 0 | 43.4716
1403 | 995 | 681 | 60 | 1.7 | 22 | 270.1859 | 0 | 72.3427 | 0.58888 | 0 | 0 | 268.7632 | 0 | 57% | 25 | 0 | 58.2% | 0 | 44.4352
1404 | 1011 | 772 | 65 | 3.2 | 22.6 | 282.0392 | -3.85e-15 | 69.5258 | 5.5742 | 0 | 0 | 280.7964 | 0 | 79% | 23.3852 | 0 | 90% | 0 | 43.0601
1405 | 1001 | 795 | 74 | 3.7 | 23.2 | 281.355 | 0 | 45.4276 | 29.6724 | 0 | 0 | 280.2073 | 0 | 100% | 0 | 0 | 90% | 0 | 42.2963
1406 | 969 | 751 | 86 | 4.6 | 23.7 | 0 | 293.3505 | 42.6818 | 32.4182 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.6057
1407 | 954 | 644 | 70 | 5.5 | 23.7 | 0 | 278.382 | 42.8618 | 24.6383 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.1084
1408 | 866 | 478 | 71 | 5.8 | 23.2 | 40.4167 | 195.9653 | 42.3471 | 6.0271 | 42.5937 | 0.13469 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.1722
1409 | 627 | 264 | 71 | 4.1 | 22.3 | 42.0252 | 95.8393 | 22.5506 | 0 | 42.5914 | 14.9684 | 0 | 0 | 100% | 0 | 6.8398 | 79.06% | 0 | 44.9659
1410 | 263 | 81 | 38 | 3.2 | 19.8 | 0 | 43.5762 | 1.6803 | 0 | 58.7909 | 22.0235 | 0 | 57.3191 | 96% | 0 | 25 | 39.06% | 0 | 46.6327
1411 | 1 | 0 | 0 | 1.9 | 14.4 | 0 | 0 | 0 | 0 | 78.3043 | 30.7043 | 0 | 79.1828 | 90% | 0 | 18.1602 | 10% | 0 | 45.9247
1412 | 0 | 0 | 0 | 1.1 | 11.9 | 0 | 0 | 0 | 0 | 111.7075 | 45.3054 | 0 | 115.5798 | 81% | 0 | 0 | 10% | 0 | 42.6805
1413 | 0 | 0 | 0 | 0.7 | 11.2 | 0 | 0 | 0 | 0 | 102.3452 | 41.4224 | 0 | 102.5693 | 73% | 0 | 0 | 10% | 0 | 39.243
1414 | 0 | 0 | 0 | 0.8 | 10.7 | 0 | 0 | 0 | 0 | 96.7181 | 39.077 | 0 | 95.6142 | 66% | 0 | 0 | 10% | 0 | 36.9745
1415 | 0 | 0 | 0 | 1.4 | 11.2 | 0 | 0 | 0 | 0 | 92.0862 | 37.0946 | 0 | 90.1301 | 59% | 0 | 0 | 10% | 0 | 34.9827
1416 | 0 | 0 | 0 | 1.2 | 10.3 | 0 | 0 | 0 | 0 | 88.585 | 35.6503 | 0 | 86.0482 | 53% | 0 | 0 | 10% | 0 | 33.4933
1417 | 0 | 0 | 0 | 1.1 | 10.3 | 0 | 0 | 0 | 0 | 87.2497 | 35.0851 | 0 | 84.6506 | 46% | 0 | 0 | 10% | 0 | 32.8659
1418 | 0 | 0 | 0 | 1.1 | 10.2 | 0 | 0 | 0 | 0 | 87.3474 | 35.1313 | 0 | 84.9399 | 40% | 0 | 0 | 10% | 0 | 32.8548
1419 | 0 | 0 | 0 | 1 | 9.5 | 0 | 0 | 0 | 0 | 89.556 | 36.0981 | 0 | 87.7289 | 33% | 0 | 0 | 10% | 0 | 33.7738
1420 | 0 | 0 | 0 | 0.6 | 7.6 | 0 | 0 | 0 | 0 | 97.6011 | 39.5774 | 0 | 97.4955 | 26% | 0 | 0 | 10% | 0 | 37.2167
1421 | 0 | 0 | 0 | 2 | 9 | 0 | 0 | 0 | 0 | 109.2603 | 44.4304 | 0 | 111.3189 | 18% | 0 | 0 | 10% | 0 | 42.0716
1422 | 0 | 0 | 0 | 1.6 | 9.5 | 0 | 0 | 0 | 0 | 115.8593 | 47.1699 | 0 | 118.9039 | 9% | 0 | 0 | 10% | 0 | 44.8649
1423 | 20 | 5 | 5 | 0.8 | 8.3 | 0 | 0 | 0 | 0 | 113.4488 | 46.2705 | 0 | 116.6856 | 0% | 0 | 0 | 10% | 0 | 44.0476
1424 | 397 | 112 | 42 | 0.9 | 11.2 | 0 | 63.0257 | 6.0343 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.0481
1425 | 756 | 329 | 68 | 0.8 | 16 | 159.7523 | 0 | 32.1334 | 0 | 0 | 0 | 154.0327 | 0 | 12% | 0 | 0 | 10% | 0 | 30.3363
1426 | 773 | 520 | 127 | 0.8 | 19.7 | 192.2532 | -2.98e-14 | 52.7089 | 0 | 0 | 0 | 190.4844 | 0 | 26% | 5.3282 | 0 | 17.25% | 0 | 45.2431
1427 | 494 | 561 | 248 | 1.5 | 20.8 | 125.664 | 0 | 52.9415 | 0 | 0 | 0 | 124.8116 | 0 | 36% | 6.1676 | 0 | 25.63% | 0 | 45.2108
1428 | 626 | 675 | 229 | 2.8 | 20.9 | 168.7638 | 0 | 67.7371 | 0 | 0 | 0 | 167.1936 | 0 | 48% | 22.4636 | 0 | 56.18% | 0 | 43.307
1429 | 730 | 766 | 231 | 3.4 | 21.7 | 201.1378 | 0 | 69.8136 | 5.2864 | 0 | 0 | 199.7072 | 0 | 63% | 24.864 | 0 | 90% | 0 | 42.6566
1430 | 523 | 671 | 300 | 3.9 | 22.2 | 136.2611 | 0 | 43.6266 | 19.4412 | 0 | 0 | 135.4519 | 0 | 74% | 0 | 0 | 90% | 0 | 41.9156
1431 | 427 | 578 | 313 | 4.6 | 22 | 102.8121 | -1.36e-14 | 42.2201 | 9.6921 | 42.5875 | 1.259 | 62.2852 | 0 | 78% | 0 | 0 | 90% | 0 | 41.61
1432 | 257 | 368 | 236 | 4.2 | 20.8 | 0 | 59.0989 | 27.1477 | 0.12465 | 44.2211 | 15.7439 | 0 | 41.5833 | 75% | 0 | 0 | 90% | 0 | 41.5397
1433 | 18 | 143 | 137 | 3.6 | 17.9 | 0 | 4.2558 | 3.7292 | 0 | 50.4378 | 18.5349 | 0 | 47.7385 | 72% | 0 | 25 | 50% | 0 | 44.919
1434 | 27 | 47 | 42 | 2.5 | 15.8 | 0 | 4.5029 | 0 | 0 | 62.3668 | 23.7992 | 0 | 59.7124 | 67% | 0 | 25 | 10% | 0 | 46.3526
1435 | 0 | 0 | 0 | 1.4 | 13.9 | 0 | 0 | 0 | 0 | 118.1834 | 47.8762 | 0 | 123.1176 | 58% | 0 | 0 | 10% | 0 | 45.2959
1436 | 0 | 0 | 0 | 0.3 | 13 | 0 | 0 | 0 | 0 | 110.5494 | 44.7549 | 0 | 112.7396 | 50% | 0 | 0 | 10% | 0 | 42.4439
1437 | 0 | 0 | 0 | 0.3 | 13.1 | 0 | 0 | 0 | 0 | 102.6949 | 41.4612 | 0 | 102.9342 | 42% | 0 | 0 | 10% | 0 | 39.2722
1438 | 0 | 0 | 0 | 1.5 | 13.1 | 0 | 0 | 0 | 0 | 97.3311 | 39.2035 | 0 | 96.4187 | 35% | 0 | 0 | 10% | 0 | 37.0548
1439 | 0 | 0 | 0 | 1.1 | 13.2 | 0 | 0 | 0 | 0 | 91.6484 | 36.7994 | 0 | 89.6453 | 28% | 0 | 0 | 10% | 0 | 34.6552
1440 | 0 | 0 | 0 | 1.2 | 13 | 0 | 0 | 0 | 0 | 88.1223 | 35.3167 | 0 | 85.487 | 21% | 0 | 0 | 10% | 0 | 33.1465
1441 | 0 | 0 | 0 | 2 | 13.5 | 0 | 0 | 0 | 0 | 85.9753 | 34.3811 | 0 | 83.0719 | 15% | 0 | 0 | 10% | 0 | 32.1709
1442 | 0 | 0 | 0 | 2 | 13.6 | 0 | 0 | 0 | 0 | 85.2242 | 34.0596 | 0 | 82.3249 | 9% | 0 | 0 | 10% | 0 | 31.805
1443 | 0 | 0 | 0 | 2.3 | 12.9 | 0 | 0 | 0 | 0 | 85.1065 | 34.0521 | 0 | 82.3143 | 3% | 0 | 0 | 10% | 0 | 31.7556
1444 | 0 | 0 | 0 | 2.1 | 12.1 | 0 | 0 | 0 | 0 | 36.6055 | 14.6833 | 0 | 35.6326 | 0% | 0 | 0 | 10% | 0 | 12.4043
1445 | 0 | 0 | 0 | 2.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2247
1446 | 0 | 0 | 0 | 1 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2039
1447 | 0 | 2 | 2 | 2 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1833
1448 | 394 | 112 | 41 | 1.4 | 11.1 | 0 | 63.1062 | 5.9489 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.7889
1449 | 703 | 319 | 73 | 1 | 16 | 148.1141 | 2.98e-14 | 30.4088 | 0 | 0 | 0 | 141.8623 | 0 | 11% | 0 | 0 | 10% | 0 | 28.7206
1450 | 785 | 502 | 99 | 0.7 | 18.8 | 196.1003 | 0 | 50.6493 | 0 | 42.8468 | 3.6066 | 153.8016 | 0 | 22% | 23.6651 | 0 | 42.19% | 0 | 28.0093
1451 | 846 | 655 | 117 | 2.4 | 20.7 | 227.2433 | 0 | 52.8413 | 14.7912 | 42.5263 | 15.056 | 185.6075 | 0 | 36% | 25 | 0 | 76.19% | 0 | 40.4089
1452 | 709 | 697 | 189 | 5.1 | 20.7 | 192.0131 | 0 | 36.4658 | 33.8339 | 42.5659 | 15.07 | 150.6969 | 0 | 48% | 10.1584 | 0 | 90% | 0 | 39.1867
1453 | 682 | 722 | 217 | 5.1 | 21 | 185.4309 | 0 | 24.6385 | 47.1481 | 42.5748 | 15.0536 | 144.0305 | 0 | 58% | 0 | 0 | 90% | 0 | 37.554
1454 | 304 | 532 | 307 | 3.8 | 20.8 | 71.5838 | 0 | 22.5345 | 23.6433 | 42.5818 | 15.0691 | 30.7562 | 0 | 61% | 0 | 0 | 90% | 0 | 36.506
1455 | 322 | 491 | 289 | 3.3 | 20.8 | 74.0387 | 1.49e-14 | 21.7986 | 20.2726 | 42.5804 | 15.0686 | 32.4318 | 0 | 63% | 0 | 0 | 90% | 0 | 35.7548
1456 | 298 | 373 | 227 | 4.7 | 19.1 | 59.493 | 0 | 21.664 | 7.798 | 42.5793 | 15.1762 | 17.9658 | 0 | 64% | 0 | 0 | 90% | 0 | 35.8617
1457 | 326 | 225 | 117 | 3.6 | 18.3 | 0 | 64.1372 | 14.9495 | 0 | 42.5762 | 15.2221 | 0 | 40.8109 | 61% | 0 | 10.9003 | 72.56% | 0 | 39.1816
1458 | 58 | 56 | 46 | 3.5 | 16.6 | 0 | 9.7356 | 0 | 0 | 51.4551 | 19.0447 | 0 | 49.5862 | 58% | 0 | 25 | 32.56% | 0 | 41.2272
1459 | 0 | 0 | 0 | 2.2 | 15 | 0 | 0 | 0 | 0 | 75.8799 | 29.6738 | 0 | 76.715 | 52% | 0 | 14.0997 | 10% | 0 | 40.9164
1460 | 0 | 0 | 0 | 0.1 | 13.2 | 0 | 0 | 0 | 0 | 104.0219 | 42.0154 | 0 | 106.9395 | 44% | 0 | 0 | 10% | 0 | 39.2198
1461 | 0 | 0 | 0 | 0.5 | 11.6 | 0 | 0 | 0 | 0 | 98.1913 | 39.6507 | 0 | 99.2681 | 37% | 0 | 0 | 10% | 0 | 37.0051
1462 | 0 | 0 | 0 | 0.5 | 11.1 | 0 | 0 | 0 | 0 | 91.9728 | 37.0527 | 0 | 91.4919 | 30% | 0 | 0 | 10% | 0 | 34.4849
1463 | 0 | 0 | 0 | 0.4 | 9.3 | 0 | 0 | 0 | 0 | 86.2727 | 34.7156 | 0 | 84.4721 | 24% | 0 | 0 | 10% | 0 | 32.1759
1464 | 0 | 0 | 0 | 0.5 | 9.1 | 0 | 0 | 0 | 0 | 82.0673 | 32.9182 | 0 | 79.6805 | 18% | 0 | 0 | 10% | 0 | 30.3702
1465 | 0 | 0 | 0 | 0.8 | 9.2 | 0 | 0 | 0 | 0 | 80.4749 | 32.1876 | 0 | 78.1401 | 12% | 0 | 0 | 10% | 0 | 29.615
1466 | 0 | 0 | 0 | 1.3 | 9.7 | 0 | 0 | 0 | 0 | 79.7959 | 31.8601 | 0 | 77.5131 | 6% | 0 | 0 | 10% | 0 | 29.265
1467 | 0 | 0 | 0 | 0.7 | 8.8 | 0 | 0 | 0 | 0 | 79.8039 | 31.9028 | 0 | 77.5731 | 0% | 0 | 0 | 10% | 0 | 29.2867
1468 | 0 | 0 | 0 | 0.5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5369
1469 | 0 | 0 | 0 | 1.1 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5099
1470 | 0 | 0 | 0 | 0.5 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4835
1471 | 40 | 5 | 4 | 0.4 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4574
1472 | 560 | 129 | 33 | 1 | 11.3 | 66.8198 | 17.1727 | 8.9746 | 0 | 0 | 0 | 64.0972 | 0 | 5% | 0 | 0 | 10% | 0 | 7.6103
1473 | 812 | 339 | 51 | 0.9 | 16.4 | 174.96 | 0 | 33.1131 | 0 | 0 | 0 | 171.484 | 0 | 18% | 0 | 0 | 10% | 0 | 31.1788
1474 | 917 | 534 | 60 | 0.6 | 20.7 | 232.4123 | 0 | 53.925 | 1.1115 | 42.4917 | 2.6551 | 190.1354 | 0 | 32% | 22.6749 | 0 | 40.84% | 0 | 30.9829
1475 | 962 | 682 | 66 | 1.2 | 22.1 | 261.9477 | 0 | 49.142 | 22.1136 | 42.5426 | 14.9661 | 219.9443 | 0 | 49% | 25 | 0 | 74.84% | 0 | 36.3097
1476 | 979 | 771 | 71 | 1.5 | 22.8 | 275.0959 | 0 | 35.1458 | 39.9542 | 42.5727 | 14.9248 | 233.2087 | 0 | 66% | 11.1487 | 0 | 90% | 0 | 35.9653
1477 | 986 | 798 | 73 | 4 | 23.2 | 277.3285 | 0 | 22.5403 | 52.5597 | 42.5818 | 14.8977 | 235.4007 | 0 | 83% | 0 | 0 | 90% | 0 | 34.438
1478 | 982 | 757 | 69 | 4.1 | 23.5 | 272.5401 | 0 | 15.0858 | 60.0142 | 42.589 | 14.8771 | 230.4025 | 0 | 100% | 0 | 0 | 90% | 0 | 33.4299
1479 | 954 | 651 | 66 | 4.7 | 23.7 | 41.3302 | 244.7426 | 17.3457 | 49.7488 | 42.593 | 14.8631 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.9196
1480 | 902 | 491 | 57 | 5.2 | 23.2 | 42.1521 | 205.6302 | 18.1316 | 30.8719 | 42.5907 | 14.9009 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.7433
1481 | 805 | 295 | 44 | 5.2 | 21.8 | 42.1578 | 140.991 | 22.1494 | 4.723 | 42.5885 | 15.0034 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.864
1482 | 417 | 86 | 23 | 4 | 19.5 | 0 | 57.3228 | 2.8295 | 0 | 43.6518 | 15.5911 | 0 | 42.1465 | 97% | 0 | 24.3974 | 50.96% | 0 | 40.7489
1483 | 0 | 1 | 0 | 3.4 | 17 | 0 | 0 | 0 | 0 | 50.805 | 18.7432 | 0 | 49.1416 | 94% | 0 | 25 | 10.96% | 0 | 40.8245
1484 | 0 | 0 | 0 | 3.5 | 16.1 | 0 | 0 | 0 | 0 | 105.0027 | 42.2224 | 0 | 108.8571 | 86% | 0 | 0 | 10.96% | 0 | 39.2834
1485 | 0 | 0 | 0 | 2.1 | 14 | 0 | 0 | 0 | 0 | 95.8148 | 38.5106 | 0 | 95.5162 | 78% | 0 | 0 | 10.96% | 0 | 36.1518
1486 | 0 | 0 | 0 | 0.8 | 11.7 | 0 | 0 | 0 | 0 | 88.9717 | 35.7455 | 0 | 86.9855 | 72% | 0 | 0 | 10.96% | 0 | 33.455
1487 | 0 | 0 | 0 | 0.8 | 10.4 | 0 | 0 | 0 | 0 | 83.7927 | 33.6213 | 0 | 81.0025 | 66% | 0 | 0 | 10.96% | 0 | 31.2795
1488 | 0 | 0 | 0 | 1.9 | 10.5 | 0 | 0 | 0 | 0 | 81.6693 | 32.6725 | 0 | 78.9886 | 60% | 0 | 0 | 10.96% | 0 | 30.2467
1489 | 0 | 0 | 0 | 0.8 | 8.8 | 0 | 0 | 0 | 0 | 80.366 | 32.1477 | 0 | 77.8609 | 54% | 0 | 0 | 10.96% | 0 | 29.6565
1490 | 0 | 0 | 0 | 0.8 | 8.4 | 0 | 0 | 0 | 0 | 81.0677 | 32.4829 | 0 | 78.7051 | 48% | 0 | 0 | 10.96% | 0 | 29.9412
1491 | 0 | 0 | 0 | 1.7 | 8.8 | 0 | 0 | 0 | 0 | 83.8738 | 33.7222 | 0 | 81.7982 | 42% | 0 | 0 | 10.96% | 0 | 31.1388
1492 | 0 | 0 | 0 | 2.3 | 9.3 | 0 | 0 | 0 | 0 | 93.8591 | 37.9404 | 0 | 94.0489 | 35% | 0 | 0 | 10.96% | 0 | 35.3177
1493 | 0 | 0 | 0 | 2.1 | 9.7 | 0 | 0 | 0 | 0 | 104.8192 | 42.5445 | 0 | 107.0959 | 27% | 0 | 0 | 10.96% | 0 | 39.9463
1494 | 0 | 0 | 0 | 2.2 | 9.5 | 0 | 0 | 0 | 0 | 111.6049 | 45.3881 | 0 | 114.7985 | 19% | 0 | 0 | 10.96% | 0 | 42.8661
1495 | 18 | 4 | 3 | 2.3 | 9.8 | 0 | 0 | 0 | 0 | 117.4112 | 47.8022 | 0 | 121.3464 | 10% | 0 | 0 | 10.96% | 0 | 45.3658
1496 | 460 | 123 | 34 | 2.1 | 11.1 | 52.6183 | 13.7218 | 6.8832 | 0 | 99.9804 | 40.4347 | 0 | 49.119 | 6% | 0 | 0 | 10.96% | 0 | 45.9851
1497 | 807 | 343 | 55 | 1.3 | 16.3 | 174.344 | 0 | 32.435 | 0.94256 | 42.5034 | 15.3037 | 131.2534 | 0 | 16% | 0 | 0 | 10.96% | 0 | 45.7618
1498 | 901 | 536 | 68 | 1.1 | 18.9 | 228.2427 | 0 | 55.2409 | 0 | 44.602 | 16.02 | 184.627 | 0 | 30% | 23.2704 | 0 | 42.61% | 0 | 45.5062
1499 | 957 | 696 | 80 | 1.7 | 20.7 | 260.4496 | 0 | 58.1536 | 14.5868 | 42.5918 | 15.0792 | 218.9673 | 0 | 46% | 25 | 0 | 76.61% | 0 | 45.4364
1500 | 984 | 784 | 77 | 2.2 | 21.8 | 276.3346 | 3.61e-14 | 42.0516 | 33.0484 | 42.6023 | 15.0082 | 234.8849 | 0 | 64% | 9.8441 | 0 | 90% | 0 | 44.2356
1501 | 972 | 798 | 81 | 2.7 | 22.5 | 274.3181 | 0 | 31.2666 | 43.8334 | 42.6052 | 14.9584 | 232.8011 | 0 | 81% | 0 | 0 | 90% | 0 | 43.2406
1502 | 955 | 754 | 82 | 2.8 | 23.7 | 265.9579 | 0 | 28.0825 | 47.0175 | 42.607 | 14.868 | 224.1929 | 0 | 97% | 0 | 0 | 90% | 0 | 42.5051
1503 | 896 | 642 | 88 | 3.7 | 23.6 | 77.8276 | 185.0943 | 26.77 | 38.3031 | 42.6077 | 14.8759 | 36.3279 | 0 | 100% | 0 | 0 | 90% | 0 | 42.1619
1504 | 547 | 439 | 166 | 4.5 | 23.1 | 42.1523 | 102.8622 | 26.8134 | 11.7654 | 42.6054 | 14.9137 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.438
1505 | 424 | 233 | 109 | 5.2 | 21 | 42.1579 | 44.3044 | 17.8151 | 0 | 42.6028 | 15.0635 | 0 | 0 | 100% | 0 | 11.8699 | 71.01% | 0 | 45.4599
1506 | 258 | 87 | 46 | 3.3 | 18.8 | 0 | 43.8596 | 1.9483 | 0 | 59.1617 | 22.2483 | 0 | 57.6927 | 96% | 0 | 25 | 31.01% | 0 | 47.1283
1507 | 1 | 1 | 1 | 1.5 | 14.9 | 0 | 0 | 0 | 0 | 90.6854 | 35.9782 | 0 | 93.4244 | 89% | 0 | 13.1301 | 10% | 0 | 46.1657
1508 | 0 | 0 | 0 | 1.9 | 13.1 | 0 | 0 | 0 | 0 | 111.5846 | 45.1792 | 0 | 114.4852 | 80% | 0 | 0 | 10% | 0 | 42.7726
1509 | 0 | 0 | 0 | 0.9 | 12.2 | 0 | 0 | 0 | 0 | 101.1331 | 40.855 | 0 | 100.6953 | 73% | 0 | 0 | 10% | 0 | 38.7849
1510 | 0 | 0 | 0 | 1.3 | 12 | 0 | 0 | 0 | 0 | 95.2636 | 38.3985 | 0 | 93.7044 | 66% | 0 | 0 | 10% | 0 | 36.3566
1511 | 0 | 0 | 0 | 1 | 12.1 | 0 | 0 | 0 | 0 | 90.3227 | 36.2971 | 0 | 87.8707 | 59% | 0 | 0 | 10% | 0 | 34.2204
1512 | 0 | 0 | 0 | 2.4 | 12.6 | 0 | 0 | 0 | 0 | 87.166 | 34.9328 | 0 | 84.3196 | 53% | 0 | 0 | 10% | 0 | 32.7883
1513 | 0 | 0 | 0 | 2.2 | 12.1 | 0 | 0 | 0 | 0 | 85.9584 | 34.451 | 0 | 83.1214 | 46% | 0 | 0 | 10% | 0 | 32.2324
1514 | 0 | 0 | 0 | 1.3 | 10.8 | 0 | 0 | 0 | 0 | 86.1377 | 34.5921 | 0 | 83.5278 | 40% | 0 | 0 | 10% | 0 | 32.3081
1515 | 0 | 0 | 0 | 2.1 | 11.6 | 0 | 0 | 0 | 0 | 88.3942 | 35.5069 | 0 | 86.3712 | 34% | 0 | 0 | 10% | 0 | 33.1694
1516 | 0 | 0 | 0 | 1.3 | 10.9 | 0 | 0 | 0 | 0 | 96.2447 | 38.8696 | 0 | 95.963 | 26% | 0 | 0 | 10% | 0 | 36.4912
1517 | 0 | 0 | 0 | 1.8 | 10.5 | 0 | 0 | 0 | 0 | 107.9498 | 43.8138 | 0 | 109.8645 | 18% | 0 | 0 | 10% | 0 | 41.4334
1518 | 0 | 0 | 0 | 2.3 | 10.6 | 0 | 0 | 0 | 0 | 114.4398 | 46.5216 | 0 | 117.3026 | 9% | 0 | 0 | 10% | 0 | 44.1931
1519 | 23 | 6 | 5 | 2.2 | 10.8 | 0 | 0 | 0 | 0 | 118.166 | 48.0655 | 0 | 121.3998 | 0% | 0 | 0 | 10% | 0 | 45.804
1520 | 13 | 64 | 63 | 2.3 | 12 | 0 | 2.5106 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0172
1521 | 1 | 137 | 135 | 1.8 | 14.2 | 0 | 0.2549 | 2.853 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.85312
1522 | 21 | 258 | 242 | 1.8 | 16.1 | 0 | 6.1279 | 11.4245 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.4414
1523 | 204 | 519 | 376 | 1.1 | 18.2 | 0 | 52.4424 | 42.0011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 40.037
1524 | 333 | 581 | 328 | 1.7 | 19.6 | 81.9279 | 0 | 51.465 | 0 | 0 | 0 | 78.5971 | 0 | 6% | 5.7276 | 0 | 17.79% | 0 | 44.6086
1525 | 600 | 693 | 239 | 3.4 | 20.5 | 162.2077 | 0 | 68.0431 | 0 | 0 | 0 | 159.1496 | 0 | 18% | 23.1613 | 0 | 49.29% | 0 | 43.0291
1526 | 574 | 649 | 235 | 2.5 | 21.3 | 152.8489 | 0 | 62.5698 | 0 | 0 | 0 | 151.385 | 0 | 30% | 18.5214 | 0 | 74.48% | 0 | 42.2509
1527 | 432 | 525 | 247 | 3.5 | 21.3 | 105.5226 | 0 | 44.1184 | 1.9899 | 42.5348 | 1.3148 | 64.9174 | 0 | 35% | 11.4132 | 0 | 90% | 0 | 32.1543
1528 | 269 | 344 | 206 | 4.4 | 20.6 | 0 | 62.8662 | 25.7085 | 0 | 45.6019 | 16.3359 | 0 | 42.6206 | 32% | 0 | 1.5412 | 87.53% | 0 | 42.4055
1529 | 241 | 212 | 134 | 3.6 | 20 | 0 | 57.7293 | 12.9067 | 0 | 42.5336 | 15.1044 | 0 | 39.7411 | 29% | 0 | 19.9153 | 55.67% | 0 | 45.7977
1530 | 94 | 73 | 55 | 2.9 | 18.8 | 0 | 16.0796 | 0.3976 | 0 | 64.2253 | 24.4372 | 0 | 60.9795 | 24% | 0 | 25 | 15.67% | 0 | 47.6304
1531 | 0 | 1 | 0 | 1.8 | 16.6 | 0 | 0 | 0 | 0 | 112.649 | 45.2585 | 0 | 115.8964 | 15% | 0 | 3.5435 | 10% | 0 | 46.4578
1532 | 0 | 0 | 0 | 1 | 14.4 | 0 | 0 | 0 | 0 | 112.3657 | 45.4182 | 0 | 114.4846 | 7% | 0 | 0 | 10% | 0 | 43.1703
1533 | 0 | 0 | 0 | 0.6 | 13.3 | 0 | 0 | 0 | 0 | 86.0165 | 34.7296 | 0 | 86.1908 | 0% | 0 | 0 | 10% | 0 | 32.5802
1534 | 0 | 0 | 0 | 0.3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0163
1535 | 0 | 0 | 0 | 0.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9994
1536 | 0 | 0 | 0 | 0.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9827
1537 | 0 | 0 | 0 | 0.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9664
1538 | 0 | 0 | 0 | 1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9503
1539 | 0 | 0 | 0 | 0.6 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9346
1540 | 0 | 0 | 0 | 1.3 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9192
1541 | 0 | 0 | 0 | 0.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9041
1542 | 0 | 0 | 0 | 1.1 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8892
1543 | 0 | 4 | 4 | 0.8 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8746
1544 | 109 | 91 | 65 | 3.8 | 10.2 | 0 | 21.233 | 1.644 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.21625
1545 | 295 | 292 | 180 | 5.7 | 14.8 | 0 | 64.5715 | 20.9901 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 19.1462
1546 | 324 | 484 | 305 | 5.9 | 17.2 | 67.7219 | 0 | 39.7066 | 0 | 0 | 0 | 63.903 | 0 | 5% | 0 | 0 | 10% | 0 | 38.6973
1547 | 101 | 423 | 349 | 5.1 | 18.1 | 0 | 31.4007 | 29.7971 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | 28.9049
1548 | 294 | 615 | 387 | 5.7 | 20.2 | 55.0557 | 14.4888 | 53.1477 | 0 | 0 | 0 | 52.6121 | 0 | 9% | 5.7863 | 0 | 17.87% | 0 | 46.2038
1549 | 240 | 566 | 376 | 7.1 | 22.1 | 0 | 63.7779 | 46.077 | 1.0189 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 17.87% | 0 | 45.1805
1550 | 313 | 595 | 358 | 8.9 | 22.4 | 69.6303 | 1.49e-14 | 51.1068 | 0 | 0 | 0 | 66.2628 | 0 | 14% | 5.5621 | 0 | 25.43% | 0 | 44.5166
1551 | 9 | 300 | 290 | 10.9 | 20.3 | 0 | 2.7623 | 14.2589 | 0 | 42.2417 | 0 | 0 | 39.0378 | 11% | 0 | 9.6461 | 10% | 0 | 22.4693
1552 | 541 | 538 | 274 | 11.4 | 19.6 | 96.647 | 25.2464 | 47.7992 | 0 | 42.5678 | 8.7118 | 61.9954 | 7.1059 | 15% | 17.0022 | 0 | 33.12% | 0 | 37.7177
1553 | 189 | 177 | 103 | 10.6 | 17.8 | 0 | 45.4171 | 8.681 | 0 | 65.7112 | 25.2267 | 0 | 63.6975 | 11% | 0 | 14.4518 | 10% | 0 | 47.2774
1554 | 9 | 38 | 37 | 11.6 | 16.2 | 0 | 1.549 | 0 | 0 | 126.4254 | 51.1184 | 0 | 130.7893 | 1% | 0 | 0 | 10% | 0 | 48.9881
1555 | 0 | 2 | 2 | 10.6 | 15.8 | 0 | 0 | 0 | 0 | 7.0181 | 2.8374 | 0 | 7.1945 | 0% | 0 | 0 | 10% | 0 | 0.97997
1556 | 0 | 0 | 0 | 7.4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8338
1557 | 0 | 0 | 0 | 7.5 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8202
1558 | 0 | 0 | 0 | 8.2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.807
1559 | 0 | 0 | 0 | 7.5 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.794
1560 | 0 | 0 | 0 | 7.5 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7812
1561 | 0 | 0 | 0 | 5.5 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7687
1562 | 0 | 0 | 0 | 2.3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7564
1563 | 0 | 0 | 0 | 1.3 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7444
1564 | 0 | 0 | 0 | 1.9 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7326
1565 | 0 | 0 | 0 | 1.6 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7211
1566 | 0 | 0 | 0 | 2.3 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7098
1567 | 0 | 4 | 3 | 2.1 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6986
1568 | 35 | 79 | 70 | 1 | 8.6 | 0 | 6.8766 | 0.41466 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.273
1569 | 219 | 251 | 167 | 1.2 | 10.8 | 0 | 56.3476 | 16.1929 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 14.5161
1570 | 691 | 514 | 135 | 1.3 | 13.6 | 139.9652 | 34.9446 | 48.3688 | 1.0084 | 0 | 0 | 130.7939 | 0 | 10% | 0 | 0 | 10% | 0 | 46.4955
1571 | 951 | 718 | 91 | 1.5 | 15.3 | 259.369 | 0 | 74.4451 | 0.44098 | 42.1366 | 0 | 215.8345 | 0 | 27% | 25 | 0 | 44% | 0 | 46.144
1572 | 528 | 552 | 161 | 2.1 | 15.6 | 140.4263 | 0 | 53.1039 | 0 | 0 | 0 | 139.1938 | 0 | 38% | 6.9641 | 0 | 53.47% | 0 | 44.4279
1573 | 897 | 837 | 159 | 4.1 | 16.6 | 251.019 | 0 | 63.3106 | 11.7894 | 42.4876 | 8.6046 | 209.5679 | 0 | 54% | 25 | 0 | 87.47% | 0 | 43.9126
1574 | 245 | 373 | 190 | 3.7 | 16.2 | 54.0161 | 0 | 28.7956 | 1.5032 | 42.5191 | 15.3145 | 14.2575 | 0 | 55% | 0 | 0 | 87.47% | 0 | 43.1616
1575 | 29 | 119 | 99 | 2.6 | 15.2 | 0 | 8.9065 | 2.8732 | 0 | 43.9093 | 15.9382 | 0 | 40.9506 | 52% | 0 | 25 | 47.47% | 0 | 42.6899
1576 | 111 | 230 | 165 | 4.1 | 15.4 | 0 | 31.5288 | 12.4304 | 0 | 42.5147 | 15.3515 | 0 | 39.7036 | 49% | 0 | 17.0724 | 20.16% | 0 | 42.7412
1577 | 441 | 258 | 125 | 2.9 | 15.8 | 66.2966 | 16.882 | 19.8341 | 0 | 56.4236 | 21.3228 | 18.6705 | 7.3274 | 50% | 0 | 6.347 | 10% | 0 | 46.1235
1578 | 288 | 107 | 58 | 1.2 | 15.6 | 0 | 49.8711 | 2.8631 | 0 | 115.3189 | 46.5566 | 0 | 118.5112 | 41% | 0 | 0 | 10% | 0 | 48.0194
1579 | 0 | 1 | 1 | 1.3 | 13.2 | 0 | 0 | 0 | 0 | 121.2453 | 49.1969 | 0 | 125.1352 | 31% | 0 | 0 | 10% | 0 | 46.9511
1580 | 0 | 0 | 0 | 1.2 | 11.7 | 0 | 0 | 0 | 0 | 113.1067 | 45.9045 | 0 | 114.8224 | 23% | 0 | 0 | 10% | 0 | 43.795
1581 | 0 | 0 | 0 | 1.3 | 10.3 | 0 | 0 | 0 | 0 | 102.8329 | 41.6779 | 0 | 102.4577 | 15% | 0 | 0 | 10% | 0 | 39.6406
1582 | 0 | 0 | 0 | 0.8 | 8.5 | 0 | 0 | 0 | 0 | 97.0475 | 39.315 | 0 | 95.5903 | 8% | 0 | 0 | 10% | 0 | 37.2914
1583 | 0 | 0 | 0 | 1.7 | 8.4 | 0 | 0 | 0 | 0 | 91.4735 | 36.962 | 0 | 89.0382 | 1% | 0 | 0 | 10% | 0 | 34.9302
1584 | 0 | 0 | 0 | 1.2 | 7.7 | 0 | 0 | 0 | 0 | 10.0188 | 4.0431 | 0 | 9.6764 | 0% | 0 | 0 | 10% | 0 | 2.0783
1585 | 0 | 0 | 0 | 2.1 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9384
1586 | 0 | 0 | 0 | 2 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.923
1587 | 0 | 0 | 0 | 2.3 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9077
1588 | 0 | 0 | 0 | 2.6 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8928
1589 | 0 | 0 | 0 | 1.3 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8783
1590 | 0 | 0 | 0 | 2.4 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8639
1591 | 58 | 10 | 7 | 1.1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8498
1592 | 531 | 147 | 43 | 1.4 | 7.8 | 65.4841 | 17.1221 | 9.4789 | 0 | 0 | 0 | 62.2053 | 0 | 5% | 0 | 0 | 10% | 0 | 8.2223
1593 | 769 | 358 | 66 | 1.3 | 11.2 | 168.6762 | 0 | 33.5219 | 0 | 0 | 0 | 164.5623 | 0 | 18% | 0 | 0 | 10% | 0 | 31.6075
1594 | 885 | 554 | 75 | 1 | 14.2 | 225.9054 | 0 | 56.0666 | 0 | 42.4136 | 0 | 184.0914 | 0 | 32% | 23.5798 | 0 | 42.07% | 0 | 29.4903
1595 | 935 | 704 | 82 | 2.6 | 15.7 | 254.5524 | 0 | 59.8117 | 12.8406 | 42.5134 | 13.4456 | 213.3462 | 0 | 48% | 24.8667 | 0 | 75.89% | 0 | 45.5416
1596 | 950 | 794 | 91 | 3.2 | 16.4 | 266.2431 | 0 | 41.942 | 33.158 | 42.5521 | 15.3162 | 225.0439 | 0 | 65% | 10.377 | 0 | 90% | 0 | 43.9551
1597 | 910 | 806 | 113 | 3 | 17 | 256.0023 | 0 | 30.4365 | 44.6635 | 42.5657 | 15.2905 | 214.8037 | 0 | 81% | 0 | 0 | 90% | 0 | 42.8789
1598 | 360 | 549 | 277 | 2.8 | 17.2 | 89.6232 | 0 | 28.2625 | 20.284 | 42.576 | 15.2832 | 48.9368 | 0 | 85% | 0 | 0 | 90% | 0 | 42.267
1599 | 124 | 329 | 249 | 2 | 16.8 | 0 | 38.1076 | 22.6762 | 0 | 42.575 | 15.304 | 0 | 40.5991 | 82% | 0 | 5.366 | 81.41% | 0 | 41.6164
1600 | 597 | 461 | 165 | 3.4 | 17.1 | 114.9573 | 28.466 | 33.9856 | 8.1763 | 43.2135 | 15.5514 | 79.8626 | 7.9335 | 87% | 6.3129 | 0 | 90% | 0 | 41.3131
1601 | 660 | 299 | 80 | 4.5 | 16.1 | 130.2471 | 0 | 24.7845 | 0 | 42.5733 | 15.3391 | 88.264 | 0 | 93% | 0 | 4.3855 | 82.98% | 0 | 44.1965
1602 | 304 | 89 | 36 | 3.9 | 14.3 | 0 | 52.9583 | 1.9811 | 0 | 55.3637 | 20.8567 | 0 | 53.8752 | 90% | 0 | 25 | 42.98% | 0 | 45.7631
1603 | 1 | 1 | 1 | 1.8 | 12.1 | 0 | 0 | 0 | 0 | 69.8147 | 27.1827 | 0 | 69.7745 | 84% | 0 | 20.6145 | 10% | 0 | 44.8177
1604 | 0 | 0 | 0 | 0.5 | 10.9 | 0 | 0 | 0 | 0 | 111.5412 | 45.2921 | 0 | 116.3192 | 76% | 0 | 0 | 10% | 0 | 42.4452
1605 | 0 | 0 | 0 | 1.2 | 9.9 | 0 | 0 | 0 | 0 | 102.4268 | 41.5217 | 0 | 103.5325 | 68% | 0 | 0 | 10% | 0 | 39.117
1606 | 0 | 0 | 0 | 1.6 | 9.3 | 0 | 0 | 0 | 0 | 97.103 | 39.3032 | 0 | 96.6979 | 61% | 0 | 0 | 10% | 0 | 37.024
1607 | 0 | 0 | 0 | 2.2 | 9.3 | 0 | 0 | 0 | 0 | 91.339 | 36.8643 | 0 | 89.6719 | 54% | 0 | 0 | 10% | 0 | 34.6179
1608 | 0 | 0 | 0 | 2.5 | 9.3 | 0 | 0 | 0 | 0 | 86.8602 | 34.9635 | 0 | 84.3536 | 48% | 0 | 0 | 10% | 0 | 32.6948
1609 | 0 | 0 | 0 | 2.5 | 9.2 | 0 | 0 | 0 | 0 | 84.8853 | 34.1335 | 0 | 82.176 | 42% | 0 | 0 | 10% | 0 | 31.814
1610 | 0 | 0 | 0 | 1.7 | 7.6 | 0 | 0 | 0 | 0 | 84.1701 | 33.8887 | 0 | 81.49 | 35% | 0 | 0 | 10% | 0 | 31.517
1611 | 0 | 0 | 0 | 1.8 | 7.1 | 0 | 0 | 0 | 0 | 84.2081 | 33.9208 | 0 | 81.6689 | 29% | 0 | 0 | 10% | 0 | 31.5026
1612 | 0 | 0 | 0 | 1.4 | 6.9 | 0 | 0 | 0 | 0 | 86.8193 | 35.0309 | 0 | 84.8779 | 23% | 0 | 0 | 10% | 0 | 32.5705
1613 | 0 | 0 | 0 | 0.7 | 5.1 | 0 | 0 | 0 | 0 | 89.0406 | 36.0217 | 0 | 87.6151 | 16% | 0 | 0 | 10% | 0 | 33.5371
1614 | 0 | 0 | 0 | 0.6 | 4.5 | 0 | 0 | 0 | 0 | 94.8613 | 38.5129 | 0 | 94.7655 | 9% | 0 | 0 | 10% | 0 | 36.0104
1615 | 89 | 12 | 7 | 0.5 | 4.8 | 0 | 0 | 0 | 0 | 102.8647 | 41.8842 | 0 | 104.2661 | 2% | 0 | 0 | 10% | 0 | 39.3867
1616 | 618 | 160 | 37 | 0.7 | 9.5 | 79.9266 | 20.5396 | 10.9824 | 0 | 79.0736 | 31.5503 | 15.6937 | 14.7266 | 2% | 0 | 0 | 10% | 0 | 40.9786
1617 | 839 | 375 | 53 | 0.9 | 14.4 | 186.9254 | 0 | 35.2953 | 0 | 43.8083 | 15.9273 | 143.2937 | 0 | 12% | 8.2695 | 0 | 21.25% | 0 | 40.875
1618 | 934 | 572 | 60 | 4 | 16.8 | 238.4032 | 0 | 52.5996 | 4.7782 | 42.6019 | 15.3137 | 196.6681 | 0 | 27% | 25 | 0 | 55.25% | 0 | 40.3631
1619 | 979 | 722 | 65 | 5.1 | 17.7 | 265.8113 | 0 | 52.5975 | 21.3774 | 42.6097 | 15.268 | 224.1994 | 0 | 44% | 25 | 0 | 89.25% | 0 | 40.043
1620 | 999 | 811 | 67 | 4.7 | 19 | 279.0983 | 0 | 27.436 | 47.664 | 42.6125 | 15.1942 | 237.5306 | 0 | 61% | 0.55399 | 0 | 90% | 0 | 39.0997
1621 | 999 | 834 | 70 | 5.8 | 19.4 | 279.6518 | 0 | 25.1516 | 49.9484 | 42.6134 | 15.1698 | 237.9399 | 0 | 79% | 0 | 0 | 90% | 0 | 37.3089
1622 | 985 | 788 | 71 | 5.5 | 19.4 | 273.1491 | 0 | 21.389 | 53.711 | 42.6134 | 15.1698 | 231.2339 | 0 | 96% | 0 | 0 | 90% | 0 | 36.2006
1623 | 957 | 679 | 67 | 4.7 | 19.4 | 99.3141 | 180.2038 | 19.9485 | 48.3345 | 42.6128 | 15.1696 | 57.7538 | 0 | 100% | 0 | 0 | 90% | 0 | 35.6305
1624 | 894 | 513 | 62 | 4.6 | 19.4 | 42.1525 | 205.5975 | 19.775 | 29.6493 | 42.6106 | 15.1688 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.6557
1625 | 777 | 313 | 53 | 4.2 | 18.6 | 42.1581 | 138.0171 | 22.6723 | 3.9364 | 42.6078 | 15.2159 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.6002
1626 | 437 | 100 | 29 | 4.1 | 16.9 | 0 | 63.4142 | 3.3578 | 0 | 42.6042 | 15.3094 | 0 | 41.113 | 97% | 0 | 24.1418 | 51.37% | 0 | 40.7436
1627 | 1 | 1 | 1 | 3.2 | 14.1 | 0 | 0 | 0 | 0 | 50.1586 | 18.6093 | 0 | 48.4982 | 93% | 0 | 25 | 11.37% | 0 | 40.6904
1628 | 0 | 0 | 0 | 2.2 | 11.9 | 0 | 0 | 0 | 0 | 104.0444 | 42.1017 | 0 | 107.6476 | 86% | 0 | 0 | 11.37% | 0 | 39.1629
1629 | 0 | 0 | 0 | 1.2 | 10.5 | 0 | 0 | 0 | 0 | 96.5365 | 39.0096 | 0 | 96.4602 | 78% | 0 | 0 | 11.37% | 0 | 36.6217
1630 | 0 | 0 | 0 | 1.2 | 9.5 | 0 | 0 | 0 | 0 | 90.1381 | 36.3432 | 0 | 88.4211 | 72% | 0 | 0 | 11.37% | 0 | 34.0415
1631 | 0 | 0 | 0 | 0.3 | 8 | 0 | 0 | 0 | 0 | 84.6849 | 34.0912 | 0 | 82.0198 | 66% | 0 | 0 | 11.37% | 0 | 31.7556
1632 | 0 | 0 | 0 | 1.3 | 7.9 | 0 | 0 | 0 | 0 | 80.9108 | 32.4254 | 0 | 78.1841 | 60% | 0 | 0 | 11.37% | 0 | 30.014
1633 | 0 | 0 | 0 | 1.1 | 8.2 | 0 | 0 | 0 | 0 | 79.2107 | 31.6415 | 0 | 76.6637 | 54% | 0 | 0 | 11.37% | 0 | 29.163
1634 | 0 | 0 | 0 | 1.2 | 8.2 | 0 | 0 | 0 | 0 | 78.2279 | 31.1964 | 0 | 75.8123 | 48% | 0 | 0 | 11.37% | 0 | 28.6674
1635 | 0 | 0 | 0 | 0.5 | 7.2 | 0 | 0 | 0 | 0 | 78.5048 | 31.3548 | 0 | 76.1971 | 43% | 0 | 0 | 11.37% | 0 | 28.7851
1636 | 0 | 0 | 0 | 1.8 | 8.2 | 0 | 0 | 0 | 0 | 80.2731 | 32.127 | 0 | 78.0676 | 37% | 0 | 0 | 11.37% | 0 | 29.523
1637 | 0 | 0 | 0 | 1.2 | 8.3 | 0 | 0 | 0 | 0 | 80.9501 | 32.4332 | 0 | 78.8198 | 31% | 0 | 0 | 11.37% | 0 | 29.8024
1638 | 0 | 0 | 0 | 1.4 | 8.1 | 0 | 0 | 0 | 0 | 83.6404 | 33.6491 | 0 | 81.7165 | 25% | 0 | 0 | 11.37% | 0 | 30.993
1639 | 104 | 14 | 7 | 0.6 | 7.8 | 0 | 0.55664 | 0 | 0 | 90.6047 | 36.6087 | 0 | 90.1735 | 18% | 0 | 0 | 11.37% | 0 | 33.9263
1640 | 637 | 165 | 35 | 0.7 | 10.5 | 83.7917 | 21.3354 | 11.2655 | 0 | 66.8103 | 26.015 | 29.1755 | 12.5283 | 20% | 0 | 0 | 11.37% | 0 | 35.6729
1641 | 842 | 378 | 50 | 0.8 | 16.1 | 188.7673 | 2.98e-14 | 35.0097 | 0 | 43.9856 | 15.9224 | 144.4924 | 0 | 30% | 12.6459 | 0 | 28.57% | 0 | 36.181
1642 | 926 | 571 | 58 | 0.9 | 19.2 | 238.7477 | 0 | 48.0747 | 8.2014 | 42.5591 | 15.1628 | 196.4589 | 0 | 45% | 25 | 0 | 62.57% | 0 | 35.6697
1643 | 971 | 720 | 63 | 2.7 | 20.7 | 265.8464 | 0 | 43.9197 | 28.5841 | 42.5802 | 15.0751 | 223.7124 | 0 | 61% | 20.168 | 0 | 90% | 0 | 35.9835
1644 | 984 | 806 | 68 | 4.2 | 20.6 | 275.5811 | 0 | 23.4791 | 51.6209 | 42.5889 | 15.0847 | 233.4617 | 0 | 78% | 0 | 0 | 90% | 0 | 35.6056
1645 | 978 | 826 | 74 | 4.3 | 21.1 | 275.3688 | 0 | 18.3293 | 56.7707 | 42.5948 | 15.0538 | 233.1175 | 0 | 95% | 0 | 0 | 90% | 0 | 34.1592
1646 | 965 | 781 | 74 | 4.6 | 21.6 | 104.2662 | 188.1236 | 17.6347 | 57.4653 | 42.5985 | 15.0207 | 62.6769 | 0 | 100% | 0 | 0 | 90% | 0 | 33.1599
1647 | 937 | 674 | 70 | 5.9 | 21 | 42.1523 | 239.6088 | 16.9833 | 49.7355 | 42.5968 | 15.0614 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.7561
1648 | 881 | 512 | 63 | 5.6 | 21.4 | 42.1579 | 201.9796 | 17.4096 | 30.9622 | 42.5944 | 15.033 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.1539
1649 | 767 | 311 | 51 | 4.5 | 21.5 | 42.1578 | 136.027 | 21.1977 | 4.4922 | 42.592 | 15.0253 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.9343
1650 | 455 | 101 | 29 | 3.3 | 20.4 | 42.1579 | 20.7728 | 3.5068 | 0 | 42.5898 | 15.0981 | 0 | 0 | 100% | 0 | 20.841 | 56.65% | 0 | 40.1575
1651 | 2 | 2 | 1 | 2 | 16.5 | 0 | 0 | 0 | 0 | 47.1655 | 17.232 | 0 | 45.6394 | 97% | 0 | 25 | 16.65% | 0 | 40.1751
1652 | 0 | 0 | 0 | 1 | 13.6 | 0 | 0 | 0 | 0 | 93.4803 | 37.4351 | 0 | 96.1208 | 90% | 0 | 4.159 | 10% | 0 | 38.6401
1653 | 0 | 0 | 0 | 0.4 | 12.5 | 0 | 0 | 0 | 0 | 94.4266 | 38.0194 | 0 | 94.0017 | 83% | 0 | 0 | 10% | 0 | 35.6326
1654 | 0 | 0 | 0 | 0.6 | 12.1 | 0 | 0 | 0 | 0 | 88.1171 | 35.3625 | 0 | 86.048 | 76% | 0 | 0 | 10% | 0 | 33.0471
1655 | 0 | 0 | 0 | 0.2 | 11.4 | 0 | 0 | 0 | 0 | 83.6748 | 33.5248 | 0 | 80.985 | 70% | 0 | 0 | 10% | 0 | 31.1459
1656 | 0 | 0 | 0 | 0.7 | 11.7 | 0 | 0 | 0 | 0 | 81.3947 | 32.4893 | 0 | 78.8362 | 64% | 0 | 0 | 10% | 0 | 30.0245
1657 | 0 | 0 | 0 | 0.8 | 11.5 | 0 | 0 | 0 | 0 | 80.2063 | 31.9572 | 0 | 77.8179 | 58% | 0 | 0 | 10% | 0 | 29.4286
1658 | 0 | 0 | 0 | 2.8 | 12.9 | 0 | 0 | 0 | 0 | 80.7403 | 32.1282 | 0 | 78.4857 | 53% | 0 | 0 | 10% | 0 | 29.5519
1659 | 0 | 0 | 0 | 2.5 | 13.1 | 0 | 0 | 0 | 0 | 83.7837 | 33.4811 | 0 | 81.7971 | 46% | 0 | 0 | 10% | 0 | 30.8658
1660 | 0 | 0 | 0 | 1.6 | 11.9 | 0 | 0 | 0 | 0 | 93.7055 | 37.7497 | 0 | 93.9646 | 40% | 0 | 0 | 10% | 0 | 35.0981
1661 | 0 | 0 | 0 | 1.1 | 11.6 | 0 | 0 | 0 | 0 | 105.7808 | 42.852 | 0 | 108.3522 | 31% | 0 | 0 | 10% | 0 | 40.23
1662 | 0 | 0 | 0 | 1.8 | 11.7 | 0 | 0 | 0 | 0 | 113.1469 | 45.9202 | 0 | 116.7038 | 23% | 0 | 0 | 10% | 0 | 43.3877
1663 | 110 | 15 | 7 | 0.6 | 10.7 | 0 | 1.4386 | 0 | 0 | 117.0039 | 47.5879 | 0 | 120.8466 | 14% | 0 | 0 | 10% | 0 | 45.1583
1664 | 619 | 165 | 37 | 0.7 | 14.9 | 81.9219 | 20.6508 | 10.8843 | 0 | 90.1816 | 36.0735 | 7.791 | 16.771 | 13% | 0 | 0 | 10% | 0 | 45.3947
1665 | 821 | 376 | 52 | 0.6 | 19.8 | 184.5391 | 2.98e-14 | 32.3068 | 1.5605 | 42.5235 | 15.1131 | 142.266 | 0 | 24% | 0 | 0 | 10% | 0 | 45.3375
1666 | 909 | 566 | 61 | 0.8 | 22.3 | 234.5073 | 0 | 54.9836 | 0 | 45.3394 | 16.0965 | 190.1356 | 0 | 38% | 23.3173 | 0 | 41.71% | 0 | 45.2094
1667 | 941 | 709 | 70 | 2.4 | 24 | 257.462 | 0 | 57.8064 | 12.3782 | 42.5853 | 14.8372 | 215.9218 | 0 | 54% | 25 | 0 | 75.71% | 0 | 44.8608
1668 | 940 | 794 | 86 | 6.8 | 23.2 | 260.6297 | 0 | 41.9805 | 33.1195 | 42.5962 | 14.9028 | 219.077 | 0 | 70% | 10.5063 | 0 | 90% | 0 | 43.5317
1669 | 918 | 818 | 108 | 7.2 | 22 | 255.2174 | 0 | 30.443 | 44.657 | 42.5996 | 14.9935 | 213.5762 | 0 | 86% | 0 | 0 | 90% | 0 | 42.6241
1670 | 885 | 776 | 123 | 7.2 | 20.8 | 229.6604 | 14.9433 | 24.7952 | 50.3048 | 42.602 | 15.0763 | 187.7545 | 0 | 100% | 0 | 0 | 90% | 0 | 41.9261
1671 | 827 | 667 | 130 | 7.5 | 19.9 | 42.1525 | 205.0172 | 25.4348 | 39.1156 | 42.6028 | 15.1351 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2817
1672 | 763 | 492 | 101 | 7.2 | 18.6 | 42.1581 | 167.5445 | 25.0251 | 20.7704 | 42.6002 | 15.2132 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.9502
1673 | 642 | 296 | 76 | 6.9 | 17.5 | 42.1582 | 103.9696 | 23.4505 | 0 | 42.5976 | 15.2746 | 0 | 0 | 100% | 0 | 4.7551 | 82.39% | 0 | 44.1923
1674 | 330 | 95 | 40 | 5.9 | 15.9 | 0 | 45.3224 | 2.4489 | 0 | 56.288 | 21.1732 | 0 | 54.78 | 96% | 0 | 25 | 42.39% | 0 | 46.5465
1675 | 0 | 2 | 2 | 5 | 13.6 | 0 | 0 | 0 | 0 | 72.0898 | 28.0815 | 0 | 72.155 | 91% | 0 | 20.2449 | 10% | 0 | 45.3857
1676 | 0 | 0 | 0 | 4 | 12 | 0 | 0 | 0 | 0 | 110.5308 | 44.8083 | 0 | 114.5553 | 82% | 0 | 0 | 10% | 0 | 42.0919
1677 | 0 | 0 | 0 | 3.7 | 11.4 | 0 | 0 | 0 | 0 | 100.4528 | 40.6126 | 0 | 100.4931 | 75% | 0 | 0 | 10% | 0 | 38.3857
1678 | 0 | 0 | 0 | 3.2 | 10.7 | 0 | 0 | 0 | 0 | 95.006 | 38.3579 | 0 | 93.8183 | 68% | 0 | 0 | 10% | 0 | 36.2022
1679 | 0 | 0 | 0 | 3.2 | 10.3 | 0 | 0 | 0 | 0 | 89.8893 | 36.2032 | 0 | 87.6536 | 61% | 0 | 0 | 10% | 0 | 34.037
1680 | 0 | 0 | 0 | 2 | 10.5 | 0 | 0 | 0 | 0 | 86.8575 | 34.9096 | 0 | 84.212 | 55% | 0 | 0 | 10% | 0 | 32.6862
1681 | 0 | 0 | 0 | 1.6 | 9.3 | 0 | 0 | 0 | 0 | 85.915 | 34.5631 | 0 | 83.2981 | 48% | 0 | 0 | 10% | 0 | 32.2735
1682 | 0 | 0 | 0 | 1.6 | 8.6 | 0 | 0 | 0 | 0 | 85.759 | 34.5243 | 0 | 83.2823 | 42% | 0 | 0 | 10% | 0 | 32.1779
1683 | 0 | 0 | 0 | 2 | 7.8 | 0 | 0 | 0 | 0 | 87.8607 | 35.4421 | 0 | 85.9234 | 36% | 0 | 0 | 10% | 0 | 33.0471
1684 | 0 | 0 | 0 | 1.9 | 7.6 | 0 | 0 | 0 | 0 | 96.3753 | 39.0613 | 0 | 96.3206 | 28% | 0 | 0 | 10% | 0 | 36.6281
1685 | 0 | 0 | 0 | 1.3 | 8 | 0 | 0 | 0 | 0 | 107.8766 | 43.8914 | 0 | 109.9782 | 20% | 0 | 0 | 10% | 0 | 41.465
1686 | 0 | 0 | 0 | 1.5 | 8.3 | 0 | 0 | 0 | 0 | 114.6317 | 46.7056 | 0 | 117.7157 | 11% | 0 | 0 | 10% | 0 | 44.3381
1687 | 92 | 16 | 9 | 0.3 | 6.8 | 0 | 1.931 | 0 | 0 | 117.4118 | 47.9222 | 0 | 120.6515 | 2% | 0 | 0 | 10% | 0 | 45.6306
1688 | 590 | 170 | 43 | 0.2 | 10.6 | 78.2275 | 19.9663 | 10.9301 | 0 | 90.2892 | 36.3662 | 4.4411 | 16.873 | 1% | 0 | 0 | 10% | 0 | 45.7801
1689 | 818 | 385 | 58 | 0.5 | 15.1 | 184.7416 | 0 | 34.945 | 0 | 43.5268 | 15.779 | 141.8184 | 0 | 12% | 2.9086 | 0 | 13.96% | 0 | 45.7396
1690 | 920 | 582 | 66 | 2 | 17.6 | 237.4655 | 0 | 57.1683 | 0 | 43.5012 | 15.6393 | 195.2621 | 0 | 27% | 24.7705 | 0 | 47.64% | 0 | 45.472
1691 | 967 | 731 | 70 | 4.1 | 19.7 | 264.0337 | 0 | 57.6787 | 15.6045 | 42.611 | 15.1504 | 222.8089 | 0 | 43% | 25 | 0 | 81.64% | 0 | 44.9985
1692 | 985 | 819 | 74 | 4.5 | 20.6 | 275.5679 | 1.46e-14 | 37.538 | 37.562 | 42.6135 | 15.0934 | 234.3301 | 0 | 61% | 6.1444 | 0 | 90% | 0 | 43.5134
1693 | 980 | 837 | 77 | 4.8 | 21.2 | 275.4095 | 0 | 30.5475 | 44.5525 | 42.6139 | 15.0536 | 234.0516 | 0 | 78% | 0 | 0 | 90% | 0 | 42.6046
1694 | 961 | 789 | 79 | 4.4 | 21.8 | 267.5347 | 0 | 29.5652 | 45.5348 | 42.6138 | 15.0123 | 225.9356 | 0 | 95% | 0 | 0 | 90% | 0 | 41.9665
1695 | 918 | 676 | 79 | 4.5 | 22.4 | 108.4786 | 157.976 | 26.2832 | 39.5637 | 42.613 | 14.9686 | 66.8648 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8194
1696 | 855 | 512 | 72 | 4.3 | 21.7 | 42.1524 | 195.3773 | 25.9835 | 21.5747 | 42.611 | 15.0182 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.7129
1697 | 747 | 314 | 57 | 4.3 | 20.6 | 42.1579 | 132.174 | 25.4165 | 0 | 42.6081 | 15.0916 | 0 | 0 | 100% | 0 | 3.5092 | 84.39% | 0 | 44.7287
1698 | 428 | 103 | 34 | 4.1 | 17.3 | 0 | 63.1546 | 3.4135 | 0 | 55.7816 | 20.8806 | 0 | 54.2673 | 96% | 0 | 25 | 44.39% | 0 | 47.2134
1699 | 4 | 2 | 2 | 2.5 | 14.3 | 0 | 0 | 0 | 0 | 70.8511 | 27.514 | 0 | 70.5688 | 91% | 0 | 21.4908 | 10% | 0 | 46.0637
1700 | 0 | 0 | 0 | 1.5 | 12.5 | 0 | 0 | 0 | 0 | 111.7838 | 45.3001 | 0 | 116.2678 | 82% | 0 | 0 | 10% | 0 | 42.5355
1701 | 0 | 0 | 0 | 1.2 | 11.3 | 0 | 0 | 0 | 0 | 101.5027 | 41.0604 | 0 | 101.7508 | 75% | 0 | 0 | 10% | 0 | 38.8307
1702 | 0 | 0 | 0 | 1.1 | 11.2 | 0 | 0 | 0 | 0 | 95.8945 | 38.7054 | 0 | 94.8057 | 67% | 0 | 0 | 10% | 0 | 36.5606
1703 | 0 | 0 | 0 | 0.8 | 10.3 | 0 | 0 | 0 | 0 | 90.4605 | 36.4454 | 0 | 88.2841 | 61% | 0 | 0 | 10% | 0 | 34.295
1704 | 0 | 0 | 0 | 1.2 | 12.3 | 0 | 0 | 0 | 0 | 88.1575 | 35.3683 | 0 | 85.6957 | 54% | 0 | 0 | 10% | 0 | 33.162
1705 | 0 | 0 | 0 | 1.7 | 12.6 | 0 | 0 | 0 | 0 | 87.3374 | 35.0052 | 0 | 84.9014 | 48% | 0 | 0 | 10% | 0 | 32.7394
1706 | 0 | 0 | 0 | 2.9 | 13.5 | 0 | 0 | 0 | 0 | 87.8153 | 35.1554 | 0 | 85.6263 | 42% | 0 | 0 | 10% | 0 | 32.8378
1707 | 0 | 0 | 0 | 2.4 | 15.6 | 0 | 0 | 0 | 0 | 90.4419 | 36.1336 | 0 | 88.9125 | 35% | 0 | 0 | 10% | 0 | 33.7751
1708 | 0 | 0 | 0 | 1.2 | 14 | 0 | 0 | 0 | 0 | 98.0356 | 39.4427 | 0 | 98.0957 | 28% | 0 | 0 | 10% | 0 | 37.0577
1709 | 0 | 0 | 0 | 1.8 | 15.5 | 0 | 0 | 0 | 0 | 109.8128 | 44.2697 | 0 | 112.0483 | 19% | 0 | 0 | 10% | 0 | 41.8919
1710 | 0 | 0 | 0 | 1.1 | 14.6 | 0 | 0 | 0 | 0 | 116.1004 | 46.9625 | 0 | 119.2474 | 10% | 0 | 0 | 10% | 0 | 44.6447
1711 | 79 | 17 | 11 | 1.2 | 13.5 | 0 | 2.2963 | 0 | 0 | 119.2247 | 48.3377 | 0 | 122.5756 | 1% | 0 | 0 | 10% | 0 | 46.0939
1712 | 516 | 164 | 43 | 1.7 | 16.4 | 63.7576 | 20.5258 | 9.0563 | 0 | 11.2305 | 4.5015 | 61.6191 | 11.1417 | 5% | 0 | 0 | 10% | 0 | 12.2208
1713 | 903 | 414 | 50 | 5.7 | 20.9 | 203.0656 | 0 | 37.6319 | 0 | 0 | 0 | 199.8685 | 0 | 20% | 0 | 0 | 10% | 0 | 35.4243
1714 | 976 | 618 | 66 | 7.6 | 22.8 | 249.2548 | 0 | 59.9993 | 0 | 0 | 0 | 247.6381 | 0 | 39% | 12.3245 | 0 | 26.76% | 0 | 45.0041
1715 | 977 | 802 | 129 | 9.5 | 24.1 | 262.4473 | 0 | 73.7942 | 1.3058 | 0 | 0 | 261.1612 | 0 | 58% | 25 | 0 | 60.76% | 0 | 45.9513
1716 | 1036 | 850 | 62 | 7.4 | 24.7 | 287.0972 | -8.35e-15 | 69.0678 | 6.0322 | 0 | 0 | 285.8431 | 0 | 80% | 21.499 | 0 | 90% | 0 | 44.431
1717 | 1007 | 858 | 73 | 6.2 | 24.9 | 264.9832 | 18.4455 | 46.5002 | 28.5998 | 0 | 0 | 263.9437 | 0 | 100% | 0 | 0 | 90% | 0 | 43.5164
1718 | 907 | 789 | 112 | 6.9 | 23.1 | 0 | 275.8939 | 43.7459 | 31.3541 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.6161
1719 | 352 | 410 | 183 | 6.5 | 21 | 40.8252 | 53.2832 | 34.5948 | 0 | 42.5993 | 1.4824 | 0 | 0 | 100% | 0.63952 | 8.1823 | 77.78% | 0 | 42.3617
1720 | 434 | 445 | 218 | 5.3 | 20.8 | 42.1593 | 70.0076 | 35.5402 | 0.5184 | 42.5969 | 15.0745 | 0 | 0 | 100% | 8.9867 | 0 | 90% | 0 | 42.3394
1721 | 108 | 152 | 115 | 6.8 | 17.9 | 0 | 26.509 | 5.9744 | 0 | 45.7231 | 16.5498 | 0 | 44.2042 | 97% | 0 | 24.891 | 50.17% | 0 | 45.3591
1722 | 155 | 66 | 41 | 5.4 | 16.1 | 0 | 27.7929 | 0.25555 | 0 | 67.2039 | 25.8984 | 0 | 65.7862 | 92% | 0 | 25 | 10.17% | 0 | 48.2169
1723 | 2 | 2 | 2 | 4.7 | 14 | 0 | 0 | 0 | 0 | 122.4366 | 49.6316 | 0 | 130.0384 | 82% | 0 | 0 | 10.17% | 0 | 46.7042
1724 | 0 | 0 | 0 | 3.8 | 12.3 | 0 | 0 | 0 | 0 | 111.5367 | 45.2098 | 0 | 113.1007 | 74% | 0 | 0 | 10.17% | 0 | 43.1076
1725 | 0 | 0 | 0 | 4 | 11 | 0 | 0 | 0 | 0 | 101.8381 | 41.219 | 0 | 101.0196 | 66% | 0 | 0 | 10.17% | 0 | 39.278
1726 | 0 | 0 | 0 | 3.2 | 10.5 | 0 | 0 | 0 | 0 | 96.1788 | 38.86 | 0 | 94.3958 | 59% | 0 | 0 | 10.17% | 0 | 36.9162
1727 | 0 | 0 | 0 | 3.1 | 10.1 | 0 | 0 | 0 | 0 | 91.5799 | 36.9318 | 0 | 89.076 | 52% | 0 | 0 | 10.17% | 0 | 34.944
1728 | 0 | 0 | 0 | 1.9 | 8.9 | 0 | 0 | 0 | 0 | 88.4219 | 35.6404 | 0 | 85.4992 | 46% | 0 | 0 | 10.17% | 0 | 33.5878
1729 | 0 | 0 | 0 | 0.8 | 8.7 | 0 | 0 | 0 | 0 | 87.4093 | 35.2188 | 0 | 84.5219 | 39% | 0 | 0 | 10.17% | 0 | 33.0943
1730 | 0 | 0 | 0 | 0.7 | 7.3 | 0 | 0 | 0 | 0 | 87.3562 | 35.2444 | 0 | 84.6515 | 33% | 0 | 0 | 10.17% | 0 | 33.0567
1731 | 0 | 0 | 0 | 0.3 | 6 | 0 | 0 | 0 | 0 | 89.6987 | 36.2771 | 0 | 87.6164 | 26% | 0 | 0 | 10.17% | 0 | 34.0343
1732 | 0 | 0 | 0 | 0.8 | 6.2 | 0 | 0 | 0 | 0 | 97.6491 | 39.6416 | 0 | 97.2619 | 19% | 0 | 0 | 10.17% | 0 | 37.3552
1733 | 0 | 0 | 0 | 1.8 | 6.6 | 0 | 0 | 0 | 0 | 108.6148 | 44.2473 | 0 | 110.2716 | 11% | 0 | 0 | 10.17% | 0 | 41.9523
1734 | 0 | 0 | 0 | 2.1 | 6.7 | 0 | 0 | 0 | 0 | 115.6751 | 47.2015 | 0 | 118.4501 | 2% | 0 | 0 | 10.17% | 0 | 44.9436
1735 | 155 | 21 | 10 | 1.6 | 6 | 0 | 5.7806 | 0 | 0 | 22.2801 | 9.1005 | 0 | 22.8445 | 0% | 0 | 0 | 10.17% | 0 | 7.0521
1736 | 669 | 187 | 39 | 1.6 | 10 | 91.6255 | 23.4857 | 12.6435 | 0 | 0 | 0 | 88.3769 | 0 | 7% | 0 | 0 | 10.17% | 0 | 11.1367
1737 | 871 | 408 | 52 | 1.2 | 13.1 | 199.4256 | 0 | 37.3095 | 0 | 0 | 0 | 196.8869 | 0 | 22% | 0 | 0 | 10.17% | 0 | 35.1244
1738 | 951 | 602 | 59 | 1.5 | 14.8 | 247.5613 | 0 | 59.1867 | 0 | 0 | 0 | 245.8754 | 0 | 40% | 11.7529 | 0 | 26.16% | 0 | 44.7745
1739 | 990 | 750 | 64 | 1.1 | 16.1 | 272.9179 | 0 | 73.5911 | 1.5089 | 0 | 0 | 271.5211 | 0 | 61% | 25 | 0 | 60.16% | 0 | 45.6469
1740 | 1003 | 835 | 68 | 1.6 | 17.4 | 282.669 | 0 | 69.0341 | 6.0659 | 0 | 0 | 281.4352 | 0 | 82% | 21.9423 | 0 | 90% | 0 | 43.9902
1741 | 1003 | 856 | 69 | 3.5 | 18.3 | 236.5419 | 50.9286 | 45.8755 | 29.2245 | 0 | 0 | 235.5746 | 0 | 100% | 0 | 0 | 90% | 0 | 43.155
1742 | 986 | 807 | 71 | 4.8 | 18.7 | 0 | 301.0578 | 43.7298 | 31.3702 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4779
1743 | 954 | 696 | 69 | 5.5 | 18.2 | 0 | 280.9088 | 43.6538 | 24.6771 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.965
1744 | 894 | 530 | 63 | 5.4 | 17.5 | 40.3237 | 209.1421 | 43.1653 | 6.3548 | 42.5919 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8512
1745 | 783 | 327 | 52 | 5 | 16.6 | 47.0896 | 136.2973 | 26.5597 | 0 | 47.4345 | 16.5721 | 0 | 0 | 100% | 0 | 0.93298 | 88.51% | 0 | 44.6902
1746 | 508 | 113 | 31 | 3.7 | 15.3 | 46.8518 | 27.8603 | 4.2999 | 0 | 47.3159 | 17.347 | 0 | 0 | 100% | 0 | 25 | 48.51% | 0 | 47.346
1747 | 9 | 3 | 2 | 2.2 | 13 | 0 | 0 | 0 | 0 | 63.0116 | 24.2169 | 0 | 61.9076 | 95% | 0 | 24.067 | 10% | 0 | 46.2251
1748 | 0 | 0 | 0 | 0.8 | 11.3 | 0 | 0 | 0 | 0 | 112.9211 | 45.8464 | 0 | 118.2313 | 87% | 0 | 0 | 10% | 0 | 42.9542
1749 | 0 | 0 | 0 | 0.6 | 10.3 | 0 | 0 | 0 | 0 | 102.0606 | 41.3472 | 0 | 102.0212 | 79% | 0 | 0 | 10% | 0 | 39.226
1750 | 0 | 0 | 0 | 0.9 | 9 | 0 | 0 | 0 | 0 | 96.3863 | 39.0142 | 0 | 95.0618 | 72% | 0 | 0 | 10% | 0 | 36.9618
1751 | 0 | 0 | 0 | 1 | 8.4 | 0 | 0 | 0 | 0 | 91.1027 | 36.7974 | 0 | 88.8373 | 65% | 0 | 0 | 10% | 0 | 34.7182
1752 | 0 | 0 | 0 | 0.9 | 8 | 0 | 0 | 0 | 0 | 88.3971 | 35.6624 | 0 | 85.8086 | 59% | 0 | 0 | 10% | 0 | 33.5136
1753 | 0 | 0 | 0 | 0.8 | 7.6 | 0 | 0 | 0 | 0 | 87.2861 | 35.2046 | 0 | 84.7111 | 52% | 0 | 0 | 10% | 0 | 32.9833
1754 | 0 | 0 | 0 | 1.9 | 7.2 | 0 | 0 | 0 | 0 | 87.0361 | 35.1118 | 0 | 84.6014 | 46% | 0 | 0 | 10% | 0 | 32.8286
1755 | 0 | 0 | 0 | 1.7 | 8.6 | 0 | 0 | 0 | 0 | 89.4464 | 36.0868 | 0 | 87.6444 | 39% | 0 | 0 | 10% | 0 | 33.7514
1756 | 0 | 0 | 0 | 1.5 | 7 | 0 | 0 | 0 | 0 | 97.7073 | 39.6421 | 0 | 97.6769 | 32% | 0 | 0 | 10% | 0 | 37.27
1757 | 0 | 0 | 0 | 1.2 | 7 | 0 | 0 | 0 | 0 | 108.145 | 44.0382 | 0 | 110.0439 | 24% | 0 | 0 | 10% | 0 | 41.6752
1758 | 0 | 0 | 0 | 1 | 6.2 | 0 | 0 | 0 | 0 | 114.8636 | 46.8759 | 0 | 117.7384 | 15% | 0 | 0 | 10% | 0 | 44.5689
1759 | 189 | 23 | 10 | 0.8 | 7.3 | 0 | 8.6286 | 0 | 0 | 117.6159 | 47.9897 | 0 | 120.6385 | 6% | 0 | 0 | 10% | 0 | 45.7566
1760 | 695 | 195 | 38 | 0.4 | 12.4 | 97.3173 | 24.6114 | 13.1533 | 0 | 86.016 | 34.4638 | 27.0919 | 15.7465 | 7% | 0 | 0 | 10% | 0 | 45.9542
1761 | 876 | 414 | 52 | 0.4 | 17.2 | 202.1111 | 0 | 37.1428 | 0 | 43.7875 | 15.7824 | 159.0339 | 0 | 19% | 4.8181 | 0 | 16.55% | 0 | 45.8644
1762 | 958 | 611 | 59 | 1.6 | 19.3 | 250.1724 | 0 | 57.9709 | 0.92181 | 42.5882 | 15.167 | 208.8315 | 0 | 34% | 25 | 0 | 50.55% | 0 | 45.4432
1763 | 1001 | 762 | 64 | 2.6 | 20.8 | 275.5508 | 0 | 57.8042 | 17.2958 | 42.6017 | 15.0762 | 234.31 | 0 | 52% | 25 | 0 | 84.55% | 0 | 44.9249
1764 | 1020 | 851 | 66 | 2.1 | 22.1 | 287.4389 | 0 | 35.3564 | 39.7436 | 42.6075 | 14.9889 | 246.183 | 0 | 70% | 4.0055 | 0 | 90% | 0 | 43.236
1765 | 1021 | 872 | 67 | 2.2 | 22.8 | 289.2137 | 0 | 30.2637 | 44.8363 | 42.6093 | 14.9376 | 247.7804 | 0 | 89% | 0 | 0 | 90% | 0 | 42.0548
1766 | 1007 | 823 | 66 | 3.4 | 23.6 | 193.6321 | 100.279 | 26.346 | 48.754 | 42.6102 | 14.8768 | 151.9837 | 0 | 100% | 0 | 0 | 90% | 0 | 41.3134
1767 | 974 | 709 | 65 | 3.9 | 24 | 42.152 | 252.3485 | 25.234 | 42.8623 | 42.6093 | 14.8456 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.7903
1768 | 916 | 541 | 61 | 2 | 23.9 | 42.1576 | 214.4772 | 24.8243 | 24.7134 | 42.6065 | 14.8523 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.3874
1769 | 800 | 334 | 52 | 3.8 | 22.8 | 43.7715 | 145.5539 | 26.5997 | 0 | 44.1935 | 15.5844 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.8936
1770 | 525 | 118 | 31 | 3.6 | 20.7 | 42.1225 | 38.5141 | 4.3863 | 0 | 42.6012 | 15.0826 | 0 | 0 | 100% | 0 | 25 | 50% | 0 | 45.1803
1771 | 10 | 2 | 2 | 2.3 | 17.8 | 0 | 0 | 0 | 0 | 56.2475 | 21.0516 | 0 | 54.7391 | 96% | 0 | 25 | 10% | 0 | 43.9854
1772 | 0 | 0 | 0 | 0.7 | 15.5 | 0 | 0 | 0 | 0 | 109.5848 | 44.1728 | 0 | 114.5121 | 88% | 0 | 0 | 10% | 0 | 41.2008
1773 | 0 | 0 | 0 | 1.2 | 14.2 | 0 | 0 | 0 | 0 | 100.0397 | 40.2693 | 0 | 99.9121 | 80% | 0 | 0 | 10% | 0 | 38.0697
1774 | 0 | 0 | 0 | 0.8 | 12.4 | 0 | 0 | 0 | 0 | 95.3337 | 38.405 | 0 | 94.1155 | 73% | 0 | 0 | 10% | 0 | 36.2757
1775 | 0 | 0 | 0 | 1 | 11.5 | 0 | 0 | 0 | 0 | 90.112 | 36.2389 | 0 | 87.8614 | 66% | 0 | 0 | 10% | 0 | 34.0935
1776 | 0 | 0 | 0 | 1.8 | 11.7 | 0 | 0 | 0 | 0 | 86.5549 | 34.723 | 0 | 83.8258 | 60% | 0 | 0 | 10% | 0 | 32.5112
1777 | 0 | 0 | 0 | 1.3 | 10.4 | 0 | 0 | 0 | 0 | 84.725 | 34.0137 | 0 | 81.9054 | 54% | 0 | 0 | 10% | 0 | 31.725
1778 | 0 | 0 | 0 | 1 | 9.6 | 0 | 0 | 0 | 0 | 83.7641 | 33.6434 | 0 | 80.9855 | 48% | 0 | 0 | 10% | 0 | 31.2855
1779 | 0 | 0 | 0 | 1.1 | 9.4 | 0 | 0 | 0 | 0 | 83.5536 | 33.5631 | 0 | 80.9107 | 42% | 0 | 0 | 10% | 0 | 31.1461
1780 | 0 | 0 | 0 | 1.3 | 9.3 | 0 | 0 | 0 | 0 | 85.6975 | 34.4717 | 0 | 83.5788 | 36% | 0 | 0 | 10% | 0 | 32.0038
1781 | 0 | 0 | 0 | 1 | 7.9 | 0 | 0 | 0 | 0 | 87.6577 | 35.3531 | 0 | 86.0031 | 29% | 0 | 0 | 10% | 0 | 32.8543
1782 | 0 | 0 | 0 | 1.9 | 9.3 | 0 | 0 | 0 | 0 | 94.1735 | 38.0737 | 0 | 94.0466 | 22% | 0 | 0 | 10% | 0 | 35.5513
1783 | 198 | 26 | 11 | 0.4 | 8.4 | 0 | 10.7178 | 0 | 0 | 101.7933 | 41.3179 | 0 | 103.0335 | 14% | 0 | 0 | 10% | 0 | 38.8063
1784 | 700 | 202 | 40 | 1.4 | 12.5 | 98.7162 | 24.9888 | 13.516 | 0 | 72.7459 | 28.5551 | 39.009 | 13.3609 | 16% | 0 | 0 | 10% | 0 | 40.364
1785 | 880 | 422 | 52 | 0.9 | 17.1 | 203.9621 | 0 | 37.4345 | 0 | 44.207 | 15.9617 | 159.9205 | 0 | 28% | 10.971 | 0 | 24.92% | 0 | 40.1736
1786 | 965 | 620 | 58 | 0.9 | 20.4 | 253.0075 | 0 | 52.1114 | 7.0135 | 42.5679 | 15.0904 | 211.0725 | 0 | 44% | 25 | 0 | 58.92% | 0 | 39.491
1787 | 1007 | 770 | 61 | 1.4 | 22.1 | 278.2559 | 5.45e-14 | 50.2975 | 24.8025 | 42.5869 | 14.9817 | 236.4486 | 0 | 62% | 22.8525 | 0 | 90% | 0 | 39.4539
1788 | 1027 | 858 | 63 | 2.8 | 23 | 289.2591 | 0 | 26.5267 | 48.5733 | 42.5951 | 14.9178 | 247.4386 | 0 | 80% | 0 | 0 | 90% | 0 | 38.3395
1789 | 1031 | 881 | 64 | 3.2 | 23.8 | 291.7357 | 0 | 20.8194 | 54.2806 | 42.5999 | 14.8578 | 249.7241 | 0 | 98% | 0 | 0 | 90% | 0 | 36.6739
1790 | 1021 | 833 | 63 | 5.4 | 24 | 66.6112 | 249.2186 | 19.9833 | 55.1167 | 42.6025 | 14.8433 | 25.1927 | 0 | 100% | 0 | 0 | 90% | 0 | 35.3567
1791 | 988 | 718 | 62 | 5.9 | 24.1 | 42.152 | 256.5466 | 19.5899 | 49.1566 | 42.6003 | 14.8345 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.135
1792 | 924 | 547 | 58 | 6 | 23.8 | 42.1577 | 216.5195 | 19.6056 | 30.043 | 42.5977 | 14.857 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.1734
1793 | 806 | 339 | 50 | 5.6 | 22.8 | 42.1577 | 149.1091 | 22.2348 | 4.326 | 42.5953 | 14.9327 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.8784
1794 | 522 | 121 | 32 | 4.4 | 21.4 | 42.1579 | 37.8741 | 4.3494 | 0 | 42.5929 | 15.0325 | 0 | 0 | 100% | 0 | 20.5388 | 57.14% | 0 | 40.6319
1795 | 17 | 3 | 3 | 3.6 | 18.6 | 0 | 0 | 0 | 0 | 48.3271 | 17.6034 | 0 | 46.7969 | 97% | 0 | 25 | 17.14% | 0 | 40.5434
1796 | 0 | 0 | 0 | 2.1 | 15.5 | 0 | 0 | 0 | 0 | 93.1789 | 37.1746 | 0 | 95.8409 | 90% | 0 | 4.4612 | 10% | 0 | 38.6808
1797 | 0 | 0 | 0 | 1 | 13.4 | 0 | 0 | 0 | 0 | 95.1666 | 38.276 | 0 | 94.8699 | 82% | 0 | 0 | 10% | 0 | 35.8877
1798 | 0 | 0 | 0 | 0.3 | 12.3 | 0 | 0 | 0 | 0 | 89.0583 | 35.7497 | 0 | 87.1461 | 76% | 0 | 0 | 10% | 0 | 33.4435
1799 | 0 | 0 | 0 | 0.2 | 11.3 | 0 | 0 | 0 | 0 | 84.0605 | 33.6919 | 0 | 81.3724 | 70% | 0 | 0 | 10% | 0 | 31.3332
1800 | 0 | 0 | 0 | 0.7 | 10.3 | 0 | 0 | 0 | 0 | 80.8246 | 32.2942 | 0 | 78.2014 | 64% | 0 | 0 | 10% | 0 | 29.8499
1801 | 0 | 0 | 0 | 1 | 10.3 | 0 | 0 | 0 | 0 | 79.194 | 31.5522 | 0 | 76.7488 | 58% | 0 | 0 | 10% | 0 | 29.0406
1802 | 0 | 0 | 0 | 0.7 | 10 | 0 | 0 | 0 | 0 | 78.5153 | 31.2583 | 0 | 76.1987 | 53% | 0 | 0 | 10% | 0 | 28.6971
1803 | 0 | 0 | 0 | 1.6 | 10.3 | 0 | 0 | 0 | 0 | 78.721 | 31.3388 | 0 | 76.5069 | 47% | 0 | 0 | 10% | 0 | 28.7392
1804 | 0 | 0 | 0 | 2.6 | 10.8 | 0 | 0 | 0 | 0 | 80.0847 | 31.9371 | 0 | 77.9644 | 41% | 0 | 0 | 10% | 0 | 29.3059
1805 | 0 | 0 | 0 | 2.4 | 10.8 | 0 | 0 | 0 | 0 | 80.1156 | 31.952 | 0 | 78.0559 | 35% | 0 | 0 | 10% | 0 | 29.2969
1806 | 0 | 0 | 0 | 1.7 | 10 | 0 | 0 | 0 | 0 | 83.7581 | 33.626 | 0 | 81.9372 | 29% | 0 | 0 | 10% | 0 | 30.9461
1807 | 203 | 28 | 11 | 2.1 | 9.7 | 0 | 12.7294 | 0 | 0 | 90.102 | 36.3228 | 0 | 89.6334 | 23% | 0 | 0 | 10% | 0 | 33.6207
1808 | 720 | 210 | 39 | 1.5 | 14.1 | 102.9734 | 25.9117 | 13.9187 | 0 | 61.247 | 23.4076 | 52.1763 | 11.3545 | 26% | 0 | 0 | 10% | 0 | 35.5596
1809 | 897 | 434 | 53 | 0.7 | 18.9 | 209.3775 | 0 | 38.2299 | 0 | 44.8797 | 16.1374 | 164.3052 | 0 | 38% | 15.7643 | 0 | 31.44% | 0 | 36.3041
1810 | 971 | 632 | 61 | 2.7 | 21.8 | 254.1169 | 0 | 48.8683 | 10.7781 | 42.5576 | 14.9925 | 211.807 | 0 | 53% | 25 | 0 | 65.44% | 0 | 36.1409
1811 | 989 | 771 | 69 | 1.7 | 23.9 | 273.521 | 0 | 42.6795 | 31.5248 | 42.5779 | 14.8424 | 231.3406 | 0 | 70% | 18.0592 | 0 | 90% | 0 | 36.5312
1812 | 1001 | 856 | 75 | 4.7 | 25.4 | 280.612 | 0 | 23.3742 | 51.7258 | 42.5858 | 14.7248 | 238.4035 | 0 | 88% | 0 | 0 | 90% | 0 | 36.2954
1813 | 1006 | 877 | 74 | 4.1 | 25.5 | 207.0353 | 88.0131 | 18.096 | 57.004 | 42.5925 | 14.7189 | 165.0063 | 0 | 100% | 0 | 0 | 90% | 0 | 34.479
1814 | 980 | 821 | 76 | 4.7 | 25.6 | 42.1519 | 264.3541 | 17.8643 | 57.2357 | 42.5935 | 14.7111 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.2857
1815 | 952 | 711 | 74 | 5.2 | 25.9 | 42.1575 | 245.5669 | 17.4081 | 49.4457 | 42.5912 | 14.6856 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.8039
1816 | 909 | 549 | 65 | 6 | 25.8 | 42.1575 | 212.4865 | 18.0006 | 31.0652 | 42.589 | 14.693 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.4039
1817 | 786 | 343 | 59 | 5.8 | 24.9 | 42.1576 | 144.509 | 21.1009 | 5.2636 | 42.5868 | 14.766 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.5773
1818 | 501 | 125 | 39 | 4.7 | 23.4 | 42.1577 | 33.8528 | 4.4129 | 0 | 42.5847 | 14.8833 | 0 | 0 | 100% | 0 | 20.047 | 57.93% | 0 | 40.0539
1819 | 13 | 3 | 3 | 2.2 | 20.7 | 0 | 0 | 0 | 0 | 47.3465 | 17.0555 | 0 | 45.8196 | 97% | 0 | 25 | 17.93% | 0 | 39.9937
1820 | 0 | 0 | 0 | 1.7 | 18.4 | 0 | 0 | 0 | 0 | 91.1901 | 36.1189 | 0 | 93.5917 | 90% | 0 | 4.953 | 10% | 0 | 38.121
1821 | 0 | 0 | 0 | 1.3 | 17.1 | 0 | 0 | 0 | 0 | 94.5438 | 37.7668 | 0 | 94.227 | 83% | 0 | 0 | 10% | 0 | 35.3558
1822 | 0 | 0 | 0 | 1.3 | 14.4 | 0 | 0 | 0 | 0 | 88.1498 | 35.2414 | 0 | 86.1283 | 76% | 0 | 0 | 10% | 0 | 32.9141
1823 | 0 | 0 | 0 | 1.2 | 13.6 | 0 | 0 | 0 | 0 | 83.7708 | 33.4458 | 0 | 81.1239 | 70% | 0 | 0 | 10% | 0 | 31.0588
1824 | 0 | 0 | 0 | 1.8 | 13.6 | 0 | 0 | 0 | 0 | 81.4821 | 32.4263 | 0 | 78.9407 | 64% | 0 | 0 | 10% | 0 | 29.956
1825 | 0 | 0 | 0 | 1.7 | 12.8 | 0 | 0 | 0 | 0 | 80.4899 | 32.0193 | 0 | 78.1176 | 59% | 0 | 0 | 10% | 0 | 29.4858
1826 | 0 | 0 | 0 | 2 | 12.6 | 0 | 0 | 0 | 0 | 81.1323 | 32.3239 | 0 | 78.8938 | 53% | 0 | 0 | 10% | 0 | 29.7432
1827 | 0 | 0 | 0 | 3.7 | 11.4 | 0 | 0 | 0 | 0 | 83.596 | 33.4927 | 0 | 81.5869 | 47% | 0 | 0 | 10% | 0 | 30.8741
1828 | 0 | 0 | 0 | 3.6 | 11.4 | 0 | 0 | 0 | 0 | 91.975 | 37.0383 | 0 | 91.8112 | 40% | 0 | 0 | 10% | 0 | 34.3853
1829 | 0 | 0 | 0 | 2.5 | 10.8 | 0 | 0 | 0 | 0 | 101.8027 | 41.2159 | 0 | 103.562 | 32% | 0 | 0 | 10% | 0 | 38.5834
1830 | 0 | 0 | 0 | 3.2 | 10 | 0 | 0 | 0 | 0 | 109.3621 | 44.4284 | 0 | 112.3214 | 24% | 0 | 0 | 10% | 0 | 41.8648
1831 | 72 | 24 | 16 | 4 | 9 | 0 | 5.1385 | 0 | 0 | 113.505 | 46.2059 | 0 | 116.8467 | 15% | 0 | 0 | 10% | 0 | 43.7332
1832 | 442 | 183 | 73 | 4.3 | 11.2 | 56.5745 | 15.0666 | 9.9664 | 0 | 88.3085 | 35.4945 | 0 | 31.4566 | 13% | 0 | 0 | 10% | 0 | 44.1084
1833 | 435 | 375 | 195 | 6 | 13.6 | 89.3607 | 0 | 29.1261 | 0 | 45.1295 | 16.5132 | 45.2816 | 0 | 16% | 0 | 0 | 10% | 0 | 44.3974
1834 | 338 | 449 | 240 | 6.2 | 14.2 | 73.7273 | 0 | 35.4817 | 0 | 42.5302 | 15.4117 | 32.6338 | 0 | 18% | 5.5065 | 0 | 17.49% | 0 | 44.2835
1835 | 652 | 694 | 224 | 6.8 | 15.6 | 170.6972 | 0 | 55.6874 | 8.2443 | 42.5395 | 15.351 | 127.8538 | 0 | 28% | 25 | 0 | 51.49% | 0 | 44.0868
1836 | 446 | 662 | 301 | 8 | 14.9 | 111.8486 | 0 | 53.8982 | 5.4334 | 42.5653 | 15.3932 | 70.7045 | 0 | 33% | 25 | 0 | 85.49% | 0 | 42.8446
1837 | 798 | 917 | 268 | 7.8 | 16.2 | 218.6208 | 0 | 32.0151 | 43.0849 | 42.5729 | 15.3339 | 176.7829 | 0 | 46% | 3.317 | 0 | 90% | 0 | 41.624
1838 | 208 | 492 | 322 | 7.8 | 15.5 | 0 | 53.1068 | 27.1391 | 10.8334 | 42.582 | 15.3711 | 0 | 40.5381 | 43% | 0 | 0 | 90% | 0 | 40.8067
1839 | 312 | 546 | 328 | 7.7 | 15.6 | 67.9223 | 0 | 26.0013 | 18.5989 | 42.5764 | 15.3643 | 24.928 | 0 | 45% | 0 | 0 | 90% | 0 | 40.327
1840 | 36 | 225 | 204 | 7.3 | 14.3 | 0 | 10.3757 | 10.4397 | 0 | 42.573 | 15.4227 | 0 | 40.6583 | 42% | 0 | 16.0072 | 64.39% | 0 | 40.0951
1841 | 1 | 157 | 155 | 6.9 | 13.2 | 0 | 0.24894 | 4.0446 | 0 | 44.6929 | 16.3449 | 0 | 42.7488 | 39% | 0 | 25 | 24.39% | 0 | 42.6685
1842 | 0 | 37 | 36 | 5.7 | 12.1 | 0 | 0 | 0 | 0 | 97.747 | 39.1976 | 0 | 100.9253 | 32% | 0 | 8.9928 | 10% | 0 | 45.3832
1843 | 0 | 1 | 1 | 5.6 | 11.4 | 0 | 0 | 0 | 0 | 115.9182 | 47.0964 | 0 | 120.8125 | 23% | 0 | 0 | 10% | 0 | 44.3905
1844 | 0 | 0 | 0 | 4.6 | 11.1 | 0 | 0 | 0 | 0 | 108.014 | 43.8101 | 0 | 110.6141 | 14% | 0 | 0 | 10% | 0 | 41.2633
1845 | 0 | 0 | 0 | 3.7 | 10.8 | 0 | 0 | 0 | 0 | 98.9284 | 40.0043 | 0 | 99.3543 | 7% | 0 | 0 | 10% | 0 | 37.553
1846 | 0 | 0 | 0 | 2.8 | 10.8 | 0 | 0 | 0 | 0 | 93.4848 | 37.7153 | 0 | 92.789 | 0% | 0 | 0 | 10% | 0 | 35.3023
1847 | 0 | 0 | 0 | 2.8 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2845
1848 | 0 | 0 | 0 | 2.7 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2623
1849 | 0 | 0 | 0 | 2.4 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2407
1850 | 0 | 0 | 0 | 2.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2194
1851 | 0 | 0 | 0 | 2.2 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1985
1852 | 0 | 0 | 0 | 1.8 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.178
1853 | 0 | 0 | 0 | 1.5 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1579
1854 | 0 | 0 | 0 | 1.5 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1382
1855 | 0 | 12 | 12 | 1.3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1189
1856 | 27 | 112 | 103 | 1.2 | 10.5 | 0 | 5.8609 | 1.9911 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.10877
1857 | 15 | 213 | 203 | 2.1 | 11.2 | 0 | 4.0615 | 7.9026 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 5.8213
1858 | 0 | 280 | 276 | 1.2 | 12.2 | 0 | 0 | 12.5944 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 10.5315
1859 | 6 | 398 | 387 | 2.1 | 13.4 | 0 | 1.8902 | 22.2642 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 20.2193
1860 | 69 | 499 | 434 | 3.7 | 14.6 | 0 | 22.1669 | 35.7647 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 33.7375
1861 | 140 | 499 | 375 | 5.6 | 14.7 | 0 | 45.1982 | 38.1707 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 36.1607
1862 | 296 | 581 | 347 | 4 | 15.4 | 56.4235 | 14.7247 | 49.1364 | 0 | 0 | 0 | 52.9706 | 0 | 4% | 9.0579 | 0 | 22.32% | 0 | 38.8805
1863 | 14 | 225 | 212 | 4 | 15.4 | 0 | 4.329 | 8.3651 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 7.6993 | 10% | 0 | 15.0203
1864 | 1 | 125 | 122 | 5.7 | 13.7 | 0 | 0.28858 | 1.8556 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -0.11945
1865 | 93 | 141 | 104 | 5.7 | 12.7 | 0 | 23.2142 | 4.6153 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | 2.6571
1866 | 69 | 78 | 63 | 6.3 | 11.7 | 0 | 12.779 | 0.17746 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.7643
1867 | 0 | 2 | 2 | 5.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.9257
1868 | 0 | 0 | 0 | 5.1 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.9098
1869 | 0 | 0 | 0 | 4.3 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.8943
1870 | 0 | 0 | 0 | 3 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.879
1871 | 0 | 0 | 0 | 3 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.8641
1872 | 0 | 0 | 0 | 2.1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.8495
1873 | 0 | 0 | 0 | 2.6 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.8352
1874 | 0 | 0 | 0 | 2.7 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.8211
1875 | 0 | 0 | 0 | 2.1 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.8073
1876 | 0 | 0 | 0 | 1.3 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.7938
1877 | 0 | 0 | 0 | 0.9 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.7806
1878 | 0 | 0 | 0 | 1.2 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.7676
1879 | 207 | 36 | 16 | 2.1 | 6.3 | 0 | 18.4011 | 0 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | -1.7548
1880 | 682 | 223 | 50 | 2.7 | 8.5 | 98.4287 | 25.3609 | 14.3704 | 0 | 0 | 0 | 92.0675 | 0 | 11% | 0 | 0 | 10% | 0 | 12.8404
1881 | 839 | 465 | 95 | 5.7 | 10.7 | 192.3924 | 0 | 40.7132 | 0 | 0 | 0 | 186.7558 | 0 | 26% | 0 | 0 | 10% | 0 | 38.562
1882 | 755 | 563 | 113 | 5.3 | 11.9 | 191.6956 | 0 | 52.0719 | 0 | 0 | 0 | 188.5475 | 0 | 41% | 4.3469 | 0 | 15.91% | 0 | 45.5455
1883 | 628 | 699 | 238 | 5.7 | 12.8 | 164.597 | 2.98e-14 | 65.0562 | 0 | 0 | 0 | 162.4644 | 0 | 53% | 17.4847 | 0 | 39.69% | 0 | 45.6163
1884 | 708 | 828 | 263 | 6.4 | 14.1 | 191.6907 | 0 | 71.8518 | 3.2482 | 0 | 0 | 189.3402 | 0 | 68% | 25 | 0 | 73.69% | 0 | 44.6208
1885 | 187 | 500 | 339 | 6.6 | 13.2 | 0 | 46.8605 | 39.0237 | 0 | 0 | 0 | 0 | 0 | 68% | 0 | 5.4969 | 64.9% | 0 | 43.6843
1886 | 555 | 780 | 346 | 8.1 | 12.5 | 142.8056 | 0 | 63.1488 | 7.9575 | 0 | 0 | 138.0105 | 0 | 78% | 18.4588 | 0 | 90% | 0 | 42.926
1887 | 548 | 680 | 305 | 7.1 | 12.9 | 136.8019 | 0 | 44.631 | 15.5475 | 42.4441 | 0 | 96.1257 | 0 | 86% | 0 | 0 | 90% | 0 | 42.3762
1888 | 611 | 544 | 202 | 7.1 | 13.4 | 143.5128 | 0 | 38.562 | 7.2385 | 42.4649 | 5.6649 | 102.1213 | 0 | 93% | 0 | 0 | 90% | 0 | 42.1066
1889 | 179 | 198 | 118 | 7.4 | 11.7 | 0 | 44.8012 | 9.0996 | 0 | 42.475 | 15.49 | 0 | 40.3125 | 90% | 0 | 21.8571 | 55.03% | 0 | 44.8486
1890 | 103 | 77 | 55 | 6.1 | 9.7 | 0 | 19.1746 | 0.11231 | 0 | 66.3287 | 25.8374 | 0 | 64.1551 | 86% | 0 | 25 | 15.03% | 0 | 48.3173
1891 | 0 | 2 | 2 | 5 | 8.8 | 0 | 0 | 0 | 0 | 115.152 | 46.8085 | 0 | 120.8672 | 77% | 0 | 3.1429 | 10% | 0 | 47.1965
1892 | 0 | 0 | 0 | 4.5 | 8.3 | 0 | 0 | 0 | 0 | 112.181 | 45.681 | 0 | 114.5146 | 68% | 0 | 0 | 10% | 0 | 43.4368
1893 | 0 | 0 | 0 | 4.6 | 8.3 | 0 | 0 | 0 | 0 | 101.7819 | 41.3195 | 0 | 101.443 | 60% | 0 | 0 | 10% | 0 | 39.2615
1894 | 0 | 0 | 0 | 2.3 | 7.6 | 0 | 0 | 0 | 0 | 96.0665 | 38.9346 | 0 | 94.6177 | 53% | 0 | 0 | 10% | 0 | 36.901
1895 | 0 | 0 | 0 | 1.3 | 6.2 | 0 | 0 | 0 | 0 | 91.2308 | 36.9281 | 0 | 88.9266 | 46% | 0 | 0 | 10% | 0 | 34.8723
1896 | 0 | 0 | 0 | 1.9 | 5.1 | 0 | 0 | 0 | 0 | 88.0571 | 35.6066 | 0 | 85.2714 | 40% | 0 | 0 | 10% | 0 | 33.5018
1897 | 0 | 0 | 0 | 1 | 4.9 | 0 | 0 | 0 | 0 | 86.812 | 35.0834 | 0 | 83.9782 | 33% | 0 | 0 | 10% | 0 | 32.9192
1898 | 0 | 0 | 0 | 1.5 | 3.5 | 0 | 0 | 0 | 0 | 87.1953 | 35.2758 | 0 | 84.6028 | 27% | 0 | 0 | 10% | 0 | 33.055
1899 | 0 | 0 | 0 | 4 | 7.1 | 0 | 0 | 0 | 0 | 89.8669 | 36.3229 | 0 | 87.9507 | 20% | 0 | 0 | 10% | 0 | 34.0539
1900 | 0 | 0 | 0 | 5.1 | 7.8 | 0 | 0 | 0 | 0 | 98.0495 | 39.7648 | 0 | 97.8497 | 13% | 0 | 0 | 10% | 0 | 37.4574
1901 | 0 | 0 | 0 | 3.7 | 7.6 | 0 | 0 | 0 | 0 | 108.6066 | 44.2147 | 0 | 110.3785 | 5% | 0 | 0 | 10% | 0 | 41.9018
1902 | 0 | 0 | 0 | 4.2 | 7.8 | 0 | 0 | 0 | 0 | 59.8593 | 24.4126 | 0 | 61.45 | 0% | 0 | 0 | 10% | 0 | 22.2335
1903 | 192 | 36 | 16 | 3.9 | 8.1 | 0 | 18.7647 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0644
1904 | 688 | 225 | 47 | 4.1 | 9.4 | 99.6344 | 25.7326 | 14.2797 | 0 | 0 | 0 | 95.7004 | 0 | 7% | 0 | 0 | 10% | 0 | 12.6975
1905 | 853 | 446 | 66 | 6.6 | 10.5 | 195.6852 | 0 | 38.7006 | 0 | 0 | 0 | 193.0357 | 0 | 22% | 0 | 0 | 10% | 0 | 36.5496
1906 | 791 | 591 | 114 | 6.7 | 11.2 | 200.7229 | -1.48e-14 | 54.8204 | 0 | 43.0322 | 7.9446 | 159.08 | 0 | 34% | 22.1083 | 0 | 40.07% | 0 | 38.1405
1907 | 271 | 437 | 240 | 6 | 11.5 | 59.4561 | 0 | 35.649 | 0 | 42.5592 | 15.528 | 19.2488 | 0 | 35% | 4.1889 | 0 | 45.76% | 0 | 45.9988
1908 | 232 | 540 | 347 | 6.4 | 12.5 | 0 | 61.1527 | 44.7883 | 0 | 43.1398 | 15.7305 | 0 | 40.5065 | 32% | 14.7161 | 0 | 65.78% | 0 | 44.4806
1909 | 31 | 320 | 287 | 5.9 | 12.5 | 0 | 10.0133 | 18.5482 | 0 | 42.549 | 15.4871 | 0 | 39.9849 | 29% | 0 | 11.8308 | 46.85% | 0 | 43.5851
1910 | 360 | 565 | 278 | 6.4 | 13.3 | 70.4711 | 18.6093 | 48.5373 | 0 | 42.7676 | 15.5465 | 35.7197 | 7.6498 | 32% | 19.7199 | 0 | 73.67% | 0 | 42.9484
1911 | 176 | 413 | 282 | 6.8 | 13.2 | 0 | 54.4725 | 28.3317 | 0.86178 | 42.8004 | 15.5638 | 0 | 40.3913 | 28% | 0 | 0 | 73.67% | 0 | 42.4515
1912 | 737 | 563 | 159 | 5.9 | 13.7 | 145.7065 | 36.7857 | 40.614 | 8.57 | 43.191 | 15.7047 | 109.8485 | 7.7216 | 36% | 12.0089 | 0 | 90% | 0 | 42.2057
1913 | 427 | 240 | 95 | 5.8 | 12.9 | 79.7802 | 0 | 16.456 | 0 | 42.5495 | 15.472 | 38.9073 | 0 | 39% | 0 | 14.1207 | 67.41% | 0 | 44.8835
1914 | 423 | 126 | 47 | 6.2 | 11.9 | 0 | 65.7989 | 3.8461 | 0 | 55.5883 | 21.0619 | 0 | 53.1889 | 35% | 0 | 25 | 27.41% | 0 | 48.2684
1915 | 17 | 5 | 4 | 4.9 | 10 | 0 | 0 | 0 | 0 | 96.918 | 38.925 | 0 | 99.3907 | 28% | 0 | 10.8793 | 10% | 0 | 47.1509
1916 | 0 | 0 | 0 | 3.5 | 9 | 0 | 0 | 0 | 0 | 113.3743 | 46.1503 | 0 | 117.1446 | 19% | 0 | 0 | 10% | 0 | 43.5747
1917 | 0 | 0 | 0 | 2.8 | 9.2 | 0 | 0 | 0 | 0 | 103.7004 | 42.093 | 0 | 105.0855 | 11% | 0 | 0 | 10% | 0 | 39.6448
1918 | 0 | 0 | 0 | 2.8 | 9.5 | 0 | 0 | 0 | 0 | 97.8911 | 39.6287 | 0 | 97.8941 | 4% | 0 | 0 | 10% | 0 | 37.2402
1919 | 0 | 0 | 0 | 3.7 | 8.8 | 0 | 0 | 0 | 0 | 49.8634 | 20.1492 | 0 | 49.2344 | 0% | 0 | 0 | 10% | 0 | 17.8435
1920 | 0 | 0 | 0 | 2.8 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2318
1921 | 0 | 0 | 0 | 3.8 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2108
1922 | 0 | 0 | 0 | 1.9 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1901
1923 | 0 | 0 | 0 | 0.6 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1699
1924 | 0 | 0 | 0 | 1.2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1501
1925 | 0 | 0 | 0 | 3.4 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1305
1926 | 0 | 0 | 0 | 2.8 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1111
1927 | 34 | 25 | 20 | 2.7 | 7.7 | 0 | 3.6246 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0923
1928 | 454 | 208 | 84 | 2.5 | 8.5 | 61.7429 | 16.2007 | 11.3156 | 0 | 0 | 0 | 58.6925 | 0 | 5% | 0 | 0 | 10% | 0 | 10.053
1929 | 689 | 451 | 137 | 3.9 | 11.2 | 156.8032 | 0 | 36.9554 | 0 | 0 | 0 | 152.8406 | 0 | 16% | 0 | 0 | 10% | 0 | 35.1611
1930 | 721 | 580 | 134 | 4.9 | 12.3 | 182.9806 | 0 | 52.2856 | 0 | 42.4016 | 0 | 141.1857 | 0 | 27% | 19.5922 | 0 | 36.65% | 0 | 30.105
1931 | 883 | 779 | 130 | 5.9 | 13.5 | 239.7663 | 0 | 60.3516 | 13.9494 | 42.4997 | 12.9951 | 198.1628 | 0 | 42% | 25 | 0 | 70.64% | 0 | 45.6473
1932 | 903 | 862 | 134 | 6 | 14.4 | 250.9923 | 0 | 45.5591 | 29.5409 | 42.5442 | 15.4078 | 209.471 | 0 | 58% | 14.2314 | 0 | 90% | 0 | 43.9856
1933 | 892 | 883 | 149 | 6.1 | 15.3 | 248.9401 | 0 | 30.2985 | 44.8015 | 42.5603 | 15.3728 | 207.4342 | 0 | 73% | 0 | 0 | 90% | 0 | 42.9224
1934 | 855 | 844 | 173 | 5.5 | 16.4 | 235.1968 | 0 | 29.2914 | 45.8086 | 42.5726 | 15.3235 | 193.5804 | 0 | 87% | 0 | 0 | 90% | 0 | 41.9781
1935 | 743 | 681 | 168 | 5.8 | 16.6 | 195.0591 | 0 | 25.3006 | 36.9789 | 42.5794 | 15.3158 | 153.2449 | 0 | 99% | 0 | 0 | 90% | 0 | 41.5097
1936 | 693 | 549 | 164 | 6.5 | 16.3 | 58.2687 | 130.7329 | 25.113 | 21.3033 | 42.5829 | 15.3324 | 16.7426 | 0 | 100% | 0 | 0 | 90% | 0 | 41.0492
1937 | 378 | 282 | 130 | 6.3 | 15.5 | 42.1534 | 36.322 | 17.1479 | 0 | 42.5812 | 15.3708 | 0 | 0 | 100% | 0 | 10.237 | 73.62% | 0 | 43.4684
1938 | 198 | 99 | 59 | 5.9 | 13.6 | 0 | 37.2354 | 1.5145 | 0 | 56.9503 | 21.5709 | 0 | 55.4506 | 96% | 0 | 25 | 33.62% | 0 | 46.0271
1939 | 1 | 5 | 4 | 4.1 | 11.8 | 0 | 0 | 0 | 0 | 84.0463 | 33.3203 | 0 | 85.9122 | 90% | 0 | 14.763 | 10% | 0 | 45.1374
1940 | 0 | 0 | 0 | 3 | 11.2 | 0 | 0 | 0 | 0 | 110.3691 | 44.7861 | 0 | 113.4424 | 81% | 0 | 0 | 10% | 0 | 42.2873
1941 | 0 | 0 | 0 | 3.6 | 10.9 | 0 | 0 | 0 | 0 | 101.6839 | 41.1593 | 0 | 101.5933 | 74% | 0 | 0 | 10% | 0 | 39.0292
1942 | 0 | 0 | 0 | 3.3 | 10.2 | 0 | 0 | 0 | 0 | 96.5096 | 39.0139 | 0 | 95.281 | 66% | 0 | 0 | 10% | 0 | 36.9375
1943 | 0 | 0 | 0 | 2.8 | 9.7 | 0 | 0 | 0 | 0 | 91.2211 | 36.7969 | 0 | 89.0192 | 60% | 0 | 0 | 10% | 0 | 34.7041
1944 | 0 | 0 | 0 | 2.5 | 9 | 0 | 0 | 0 | 0 | 86.7995 | 34.9499 | 0 | 83.9083 | 53% | 0 | 0 | 10% | 0 | 32.8014
1945 | 0 | 0 | 0 | 2.1 | 8.7 | 0 | 0 | 0 | 0 | 85.0936 | 34.2401 | 0 | 82.133 | 47% | 0 | 0 | 10% | 0 | 32.0157
1946 | 0 | 0 | 0 | 1 | 8.6 | 0 | 0 | 0 | 0 | 83.9915 | 33.779 | 0 | 81.0475 | 41% | 0 | 0 | 10% | 0 | 31.4864
1947 | 0 | 0 | 0 | 0.9 | 8.6 | 0 | 0 | 0 | 0 | 83.8472 | 33.7185 | 0 | 81.0554 | 35% | 0 | 0 | 10% | 0 | 31.3655
1948 | 0 | 0 | 0 | 0.7 | 7.3 | 0 | 0 | 0 | 0 | 86.1544 | 34.7366 | 0 | 83.9234 | 29% | 0 | 0 | 10% | 0 | 32.3303
1949 | 0 | 0 | 0 | 1 | 6.8 | 0 | 0 | 0 | 0 | 88.2306 | 35.6319 | 0 | 86.4996 | 22% | 0 | 0 | 10% | 0 | 33.1919
1950 | 0 | 0 | 0 | 2.1 | 7.3 | 0 | 0 | 0 | 0 | 95.2828 | 38.6135 | 0 | 95.1444 | 15% | 0 | 0 | 10% | 0 | 36.1456
1951 | 127 | 36 | 21 | 1 | 7.3 | 0 | 14.6693 | 0 | 0 | 103.1638 | 41.9382 | 0 | 104.4963 | 7% | 0 | 0 | 10% | 0 | 39.4759
1952 | 549 | 218 | 68 | 2.7 | 10.5 | 78.3846 | 20.2502 | 12.443 | 0 | 76.1675 | 30.1877 | 16.6618 | 14.0829 | 7% | 0 | 0 | 10% | 0 | 41.101
1953 | 659 | 405 | 99 | 6 | 13 | 147.8114 | 0 | 32.165 | 0 | 42.5105 | 15.454 | 105.7277 | 0 | 15% | 4.759 | 0 | 16.47% | 0 | 41.1149
1954 | 435 | 522 | 257 | 6.5 | 14.1 | 101.3623 | 0 | 43.5642 | 0 | 42.561 | 15.4273 | 60.2918 | 0 | 20% | 16.9706 | 0 | 39.55% | 0 | 40.6737
1955 | 313 | 564 | 321 | 6.5 | 14.5 | 71.1884 | -1.49e-14 | 46.159 | 0 | 42.5693 | 15.4125 | 30.0862 | 0 | 22% | 19.9058 | 0 | 66.62% | 0 | 40.5855
1956 | 377 | 589 | 279 | 7.3 | 15 | 91.7665 | 1.49e-14 | 42.5554 | 8.6294 | 42.5695 | 15.3903 | 50.0472 | 0 | 26% | 17.1881 | 0 | 90% | 0 | 39.5
1957 | 76 | 468 | 397 | 7.4 | 12.1 | 0 | 24.5613 | 23.7601 | 9.1171 | 42.5686 | 15.5094 | 0 | 40.4761 | 23% | 0 | 0 | 90% | 0 | 37.6104
1958 | 307 | 709 | 451 | 6.1 | 13.4 | 57.6292 | 15.4839 | 22.3446 | 36.8033 | 42.5568 | 15.4546 | 22.9544 | 7.5149 | 24% | 0 | 0 | 90% | 0 | 36.4498
1959 | 13 | 269 | 255 | 5.4 | 12.6 | 0 | 4.0273 | 11.5621 | 0 | 42.5543 | 15.4852 | 0 | 40.5519 | 21% | 0 | 10.3523 | 73.44% | 0 | 35.6901
1960 | 4 | 134 | 130 | 5.3 | 12.6 | 0 | 1.1599 | 2.4342 | 0 | 42.5438 | 15.4814 | 0 | 40.5545 | 18% | 0 | 20.2508 | 41.03% | 0 | 35.5015
1961 | 0 | 45 | 45 | 5 | 11.6 | 0 | 0 | 0 | 0 | 55.396 | 21.087 | 0 | 54.2958 | 14% | 0 | 19.3969 | 10% | 0 | 37.7863
1962 | 0 | 54 | 53 | 4.6 | 11.7 | 0 | 0 | 0 | 0 | 107.4657 | 43.5492 | 0 | 110.8696 | 6% | 0 | 0 | 10% | 0 | 40.7789
1963 | 0 | 3 | 3 | 4.1 | 11.5 | 0 | 0 | 0 | 0 | 73.3564 | 29.7329 | 0 | 75.3821 | 0% | 0 | 0 | 10% | 0 | 27.1194
1964 | 0 | 0 | 0 | 3.6 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4663
1965 | 0 | 0 | 0 | 3.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4407
1966 | 0 | 0 | 0 | 3.1 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4156
1967 | 0 | 0 | 0 | 2.5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3911
1968 | 0 | 0 | 0 | 1.9 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3671
1969 | 0 | 0 | 0 | 3.5 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3433
1970 | 0 | 0 | 0 | 3.6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.32
1971 | 0 | 0 | 0 | 3.7 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2971
1972 | 0 | 0 | 0 | 3.1 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2748
1973 | 0 | 0 | 0 | 2.9 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2529
1974 | 0 | 0 | 0 | 2.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2314
1975 | 9 | 30 | 29 | 3.3 | 10.4 | 0 | 1.1198 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2102
1976 | 50 | 125 | 113 | 4.7 | 12.6 | 0 | 11.2163 | 2.9402 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.75087
1977 | 0 | 118 | 116 | 5.6 | 13 | 0 | 0 | 1.5029 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.66606
1978 | 30 | 243 | 218 | 5.4 | 13.9 | 0 | 9.0352 | 11.3498 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.2009
1979 | 8 | 292 | 280 | 5.5 | 15 | 0 | 2.5237 | 13.0558 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 10.9266
1980 | 83 | 537 | 458 | 6.1 | 16.2 | 0 | 26.7074 | 38.3563 | 0.42347 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 36.2463
1981 | 2 | 387 | 377 | 6.1 | 16.5 | 0 | 0.64652 | 20.4678 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 18.3767
1982 | 1 | 181 | 178 | 7 | 16 | 0 | 0.31936 | 5.1756 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.1029
1983 | 4 | 267 | 260 | 6.4 | 16 | 0 | 1.2397 | 11.1904 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.1358
1984 | 16 | 256 | 244 | 6 | 16.2 | 0 | 4.6452 | 10.6975 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 8.6607
1985 | 3 | 143 | 140 | 5.6 | 15.7 | 0 | 0.75872 | 2.9938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.97435
1986 | 0 | 52 | 51 | 4.9 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0024
1987 | 0 | 4 | 4 | 3.8 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9858
1988 | 0 | 0 | 0 | 3.3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9694
1989 | 0 | 0 | 0 | 3.2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9533
1990 | 0 | 0 | 0 | 1.7 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9375
1991 | 0 | 0 | 0 | 0.8 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.922
1992 | 0 | 0 | 0 | 1.4 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9068
1993 | 0 | 0 | 0 | 2.3 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8919
1994 | 0 | 0 | 0 | 1.6 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8772
1995 | 0 | 0 | 0 | 1.4 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8629
1996 | 0 | 0 | 0 | 1.6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8488
1997 | 0 | 0 | 0 | 1.9 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8351
1998 | 0 | 0 | 0 | 1.7 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8215
1999 | 177 | 57 | 36 | 1.9 | 10.5 | 0 | 23.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8082
2000 | 590 | 236 | 70 | 2.6 | 13.4 | 86.4312 | 22.0367 | 13.632 | 0 | 0 | 0 | 77.8496 | 0 | 6% | 0 | 0 | 10% | 0 | 12.2048
2001 | 770 | 447 | 87 | 5.1 | 16.3 | 177.7306 | 0 | 36.0965 | 0 | 0 | 0 | 170.2922 | 0 | 20% | 0 | 0 | 10% | 0 | 34.0917
2002 | 856 | 637 | 98 | 6.2 | 17.5 | 220.2643 | 0 | 56.8129 | 0 | 42.033 | 0 | 176.9129 | 0 | 34% | 14.2989 | 0 | 29.45% | 0 | 39.5604
2003 | 903 | 767 | 55 | 6 | 18.3 | 245.9017 | 0 | 63.7524 | 3.7631 | 42.3141 | 5.431 | 203.6457 | 0 | 49% | 21.8338 | 0 | 59.14% | 0 | 44.3126
2004 | 924 | 741 | 75 | 5.4 | 19 | 258.0599 | 0 | 53.6985 | 21.4015 | 42.4018 | 15.1191 | 216.1015 | 0 | 66% | 22.6908 | 0 | 90% | 0 | 43.2761
2005 | 929 | 871 | 108 | 6.1 | 20.1 | 260.2648 | 0 | 30.092 | 45.008 | 42.4563 | 15.0704 | 218.4511 | 0 | 82% | 0 | 0 | 90% | 0 | 42.2702
2006 | 912 | 824 | 111 | 6.6 | 20.2 | 251.4732 | 0 | 28.773 | 46.327 | 42.4913 | 15.0763 | 209.5495 | 0 | 98% | 0 | 0 | 90% | 0 | 41.6126
2007 | 876 | 711 | 105 | 7.4 | 20.2 | 72.918 | 186.4333 | 25.5711 | 39.2374 | 42.5149 | 15.0846 | 31.3479 | 0 | 100% | 0 | 0 | 90% | 0 | 41.1851
2008 | 820 | 551 | 95 | 7.7 | 19.6 | 42.1526 | 188.3606 | 25.0093 | 21.8926 | 42.5152 | 15.1225 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.8434
2009 | 696 | 349 | 79 | 7.2 | 18.7 | 42.1581 | 124.7014 | 24.5989 | 0 | 42.5151 | 15.177 | 0 | 0 | 100% | 0 | 2.7271 | 85.64% | 0 | 43.2148
2010 | 398 | 135 | 55 | 7.2 | 16.6 | 0 | 62.7882 | 3.7239 | 0 | 52.8381 | 19.6555 | 0 | 51.3059 | 96% | 0 | 25 | 45.64% | 0 | 46.3042
2011 | 26 | 8 | 6 | 5.1 | 14.5 | 0 | 0 | 0 | 0 | 66.8989 | 25.8103 | 0 | 66.2682 | 91% | 0 | 22.2729 | 10% | 0 | 45.1408
2012 | 0 | 0 | 0 | 3.4 | 12.5 | 0 | 0 | 0 | 0 | 109.6427 | 44.4095 | 0 | 113.9247 | 83% | 0 | 0 | 10% | 0 | 41.6008
2013 | 0 | 0 | 0 | 3.8 | 11.4 | 0 | 0 | 0 | 0 | 99.4588 | 40.1971 | 0 | 99.5181 | 75% | 0 | 0 | 10% | 0 | 37.9258
2014 | 0 | 0 | 0 | 3.4 | 10.4 | 0 | 0 | 0 | 0 | 93.3381 | 37.671 | 0 | 92.0031 | 69% | 0 | 0 | 10% | 0 | 35.478
2015 | 0 | 0 | 0 | 1.9 | 10.6 | 0 | 0 | 0 | 0 | 89.0535 | 35.8383 | 0 | 86.8323 | 62% | 0 | 0 | 10% | 0 | 33.6279
2016 | 0 | 0 | 0 | 1.6 | 10.1 | 0 | 0 | 0 | 0 | 86.1216 | 34.6202 | 0 | 83.5099 | 56% | 0 | 0 | 10% | 0 | 32.3539
2017 | 0 | 0 | 0 | 2.3 | 10.1 | 0 | 0 | 0 | 0 | 85.0681 | 34.1756 | 0 | 82.4595 | 49% | 0 | 0 | 10% | 0 | 31.8451
2018 | 0 | 0 | 0 | 3.4 | 10.9 | 0 | 0 | 0 | 0 | 85.4393 | 34.2964 | 0 | 83.0644 | 43% | 0 | 0 | 10% | 0 | 31.9094
2019 | 0 | 0 | 0 | 3.8 | 10.9 | 0 | 0 | 0 | 0 | 87.9931 | 35.3762 | 0 | 86.2396 | 37% | 0 | 0 | 10% | 0 | 32.9441
2020 | 0 | 0 | 0 | 3 | 10.1 | 0 | 0 | 0 | 0 | 96.0329 | 38.8223 | 0 | 96.0642 | 30% | 0 | 0 | 10% | 0 | 36.3587
2021 | 0 | 0 | 0 | 2.9 | 9.4 | 0 | 0 | 0 | 0 | 105.7459 | 42.9484 | 0 | 107.6192 | 22% | 0 | 0 | 10% | 0 | 40.498
2022 | 0 | 0 | 0 | 3.3 | 9.8 | 0 | 0 | 0 | 0 | 113.2486 | 46.0651 | 0 | 116.2348 | 13% | 0 | 0 | 10% | 0 | 43.6692
2023 | 38 | 52 | 46 | 3.1 | 10.1 | 0 | 5.4065 | 0 | 0 | 115.6399 | 47.0535 | 0 | 118.7334 | 4% | 0 | 0 | 10% | 0 | 44.7346
2024 | 233 | 193 | 122 | 4.5 | 13.6 | 0 | 52.8059 | 8.2708 | 0 | 50.3985 | 20.2865 | 0 | 50.015 | 0% | 0 | 0 | 10% | 0 | 26.4112
2025 | 275 | 323 | 200 | 6.9 | 16.1 | 0 | 64.7037 | 21.5988 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 19.5325
2026 | 69 | 348 | 301 | 7.6 | 16 | 0 | 20.8206 | 20.7078 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 18.6567
2027 | 312 | 654 | 412 | 8.1 | 16.6 | 56.517 | 15.4113 | 53.46 | 0 | 0 | 0 | 54.2368 | 0 | 4% | 7.6405 | 0 | 20.39% | 0 | 44.6151
2028 | 377 | 754 | 439 | 9.8 | 18.1 | 89.5401 | 0 | 64.6511 | 0 | 0 | 0 | 87.573 | 0 | 11% | 19.9974 | 0 | 47.59% | 0 | 43.4475
2029 | 565 | 906 | 432 | 10.7 | 18.1 | 146.1365 | 0 | 69.2766 | 5.8234 | 0 | 0 | 143.8137 | 0 | 22% | 25 | 0 | 81.59% | 0 | 42.5613
2030 | 437 | 746 | 398 | 9.7 | 17.5 | 106.7143 | 0 | 49.4372 | 15.4514 | 0 | 0 | 105.482 | 0 | 30% | 6.1857 | 0 | 90% | 0 | 41.8689
2031 | 479 | 738 | 396 | 9.9 | 16.9 | 114.9181 | 0 | 41.3168 | 20.7958 | 42.5276 | 2.0255 | 73.9057 | 0 | 35% | 0 | 0 | 90% | 0 | 41.4191
2032 | 191 | 428 | 312 | 9.2 | 15.8 | 0 | 55.5791 | 26.9489 | 1.9458 | 42.5378 | 15.3409 | 0 | 39.7985 | 32% | 0 | 0 | 90% | 0 | 41.0589
2033 | 12 | 148 | 142 | 9 | 14.1 | 0 | 3.0502 | 3.3757 | 0 | 47.0303 | 17.2863 | 0 | 44.1771 | 29% | 0 | 25 | 50% | 0 | 43.4563
2034 | 0 | 70 | 69 | 8.9 | 13.2 | 0 | 0 | 0 | 0 | 63.1791 | 24.2892 | 0 | 60.0983 | 24% | 0 | 25 | 10% | 0 | 47.0148
2035 | 0 | 3 | 3 | 8.4 | 12.5 | 0 | 0 | 0 | 0 | 118.5384 | 48.12 | 0 | 122.6006 | 15% | 0 | 0 | 10% | 0 | 45.7082
2036 | 0 | 0 | 0 | 7.6 | 12.6 | 0 | 0 | 0 | 0 | 109.1193 | 44.1858 | 0 | 110.8298 | 7% | 0 | 0 | 10% | 0 | 41.8982
2037 | 0 | 0 | 0 | 7.3 | 12.4 | 0 | 0 | 0 | 0 | 91.2574 | 36.8372 | 0 | 90.9932 | 0% | 0 | 0 | 10% | 0 | 34.6284
2038 | 0 | 0 | 0 | 5.6 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0763
2039 | 0 | 0 | 0 | 6.8 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0582
2040 | 0 | 0 | 0 | 7.6 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0404
2041 | 0 | 0 | 0 | 8.1 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0229
2042 | 0 | 0 | 0 | 7.9 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0058
2043 | 0 | 0 | 0 | 6.7 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.989
2044 | 0 | 0 | 0 | 7.5 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9725
2045 | 0 | 0 | 0 | 6.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9564
2046 | 0 | 0 | 0 | 6.4 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9405
2047 | 210 | 51 | 24 | 7 | 9.3 | 0 | 31.7523 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9249
2048 | 659 | 251 | 59 | 7.9 | 10.6 | 95.6542 | 25.3459 | 14.8151 | 0 | 0 | 0 | 90.5762 | 0 | 7% | 0 | 0 | 10% | 0 | 13.2892
2049 | 862 | 477 | 71 | 8.3 | 12 | 199.3036 | 0 | 39.8515 | 0 | 0 | 0 | 195.3773 | 0 | 22% | 0 | 0 | 10% | 0 | 37.6595
2050 | 927 | 665 | 83 | 7.8 | 13.2 | 239.4135 | 0 | 61.0826 | 0 | 42.4272 | 0 | 197.6401 | 0 | 37% | 17.8297 | 0 | 34.25% | 0 | 40.1288
2051 | 961 | 805 | 90 | 7.9 | 14.5 | 261.242 | 0 | 72.8886 | 2.2114 | 0 | 0 | 259.3731 | 0 | 57% | 25 | 0 | 68.25% | 0 | 45.0617
2052 | 976 | 885 | 92 | 8.3 | 15.2 | 270.5709 | 0 | 62.6431 | 12.4569 | 0 | 0 | 269.0359 | 0 | 77% | 15.9938 | 0 | 90% | 0 | 43.668
2053 | 995 | 911 | 88 | 9 | 16.3 | 276.4229 | 0 | 45.7294 | 29.3706 | 0 | 0 | 274.9795 | 0 | 98% | 0 | 0 | 90% | 0 | 42.6482
2054 | 959 | 860 | 103 | 9.6 | 16.3 | 26.3623 | 263.5117 | 42.8908 | 32.2092 | 0 | 0 | 26.2345 | 0 | 100% | 0 | 0 | 90% | 0 | 41.7293
2055 | 898 | 752 | 124 | 8.8 | 15.9 | 0 | 265.2944 | 43.0181 | 25.9399 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2643
2056 | 838 | 576 | 104 | 8.2 | 15.6 | 40.6252 | 195.7879 | 39.5707 | 9.6532 | 42.5637 | 2.621 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.9632
2057 | 736 | 367 | 78 | 8.4 | 14.6 | 44.8618 | 132.4652 | 26.2076 | 0 | 45.4232 | 16.5885 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.3844
2058 | 495 | 151 | 48 | 7.5 | 13.3 | 45.0695 | 31.5316 | 4.5702 | 0 | 45.4854 | 16.6713 | 0 | 0 | 100% | 0 | 25 | 50% | 0 | 46.9494
2059 | 45 | 10 | 7 | 7 | 11.4 | 0 | 0 | 0 | 0 | 59.4788 | 22.7689 | 0 | 58.0172 | 96% | 0 | 25 | 10% | 0 | 45.7129
2060 | 0 | 0 | 0 | 5.2 | 10.4 | 0 | 0 | 0 | 0 | 111.0955 | 45.1314 | 0 | 116.3393 | 87% | 0 | 0 | 10% | 0 | 42.1655
2061 | 0 | 0 | 0 | 3.4 | 9.9 | 0 | 0 | 0 | 0 | 99.638 | 40.3449 | 0 | 99.3545 | 80% | 0 | 0 | 10% | 0 | 38.171
2062 | 0 | 0 | 0 | 1.8 | 8.8 | 0 | 0 | 0 | 0 | 94.1257 | 38.0732 | 0 | 92.692 | 73% | 0 | 0 | 10% | 0 | 35.9551
2063 | 0 | 0 | 0 | 1.7 | 7.7 | 0 | 0 | 0 | 0 | 89.8827 | 36.304 | 0 | 87.6127 | 66% | 0 | 0 | 10% | 0 | 34.155
2064 | 0 | 0 | 0 | 1.8 | 7 | 0 | 0 | 0 | 0 | 86.8625 | 35.0453 | 0 | 84.2168 | 60% | 0 | 0 | 10% | 0 | 32.8288
2065 | 0 | 0 | 0 | 1.3 | 5.9 | 0 | 0 | 0 | 0 | 85.6475 | 34.5616 | 0 | 83.0039 | 54% | 0 | 0 | 10% | 0 | 32.2716
2066 | 0 | 0 | 0 | 2.3 | 6.8 | 0 | 0 | 0 | 0 | 85.7152 | 34.5658 | 0 | 83.2719 | 47% | 0 | 0 | 10% | 0 | 32.2127
2067 | 0 | 0 | 0 | 2.5 | 7 | 0 | 0 | 0 | 0 | 88.1741 | 35.602 | 0 | 86.3517 | 41% | 0 | 0 | 10% | 0 | 33.1977
2068 | 0 | 0 | 0 | 2 | 7.2 | 0 | 0 | 0 | 0 | 96.0943 | 38.9575 | 0 | 96.036 | 34% | 0 | 0 | 10% | 0 | 36.5186
2069 | 0 | 0 | 0 | 1.1 | 5 | 0 | 0 | 0 | 0 | 105.7295 | 43.0877 | 0 | 107.4928 | 26% | 0 | 0 | 10% | 0 | 40.6613
2070 | 0 | 0 | 0 | 0.5 | 4.1 | 0 | 0 | 0 | 0 | 113.1004 | 46.1943 | 0 | 115.9332 | 17% | 0 | 0 | 10% | 0 | 43.8234
2071 | 323 | 61 | 21 | 1 | 5.7 | 0 | 50.7822 | 0 | 0 | 115.5649 | 47.1863 | 0 | 118.5119 | 8% | 0 | 0 | 10% | 0 | 44.8928
2072 | 745 | 266 | 48 | 0.5 | 9.7 | 115.7707 | 29.3653 | 16.3106 | 0 | 77.1171 | 30.6501 | 52.3479 | 13.989 | 11% | 0 | 0 | 10% | 0 | 45.1412
2073 | 893 | 485 | 61 | 1.4 | 12.2 | 213.4602 | 0 | 40.4764 | 0 | 43.7723 | 16.0045 | 170.3717 | 0 | 24% | 9.1141 | 0 | 22.39% | 0 | 45.0192
2074 | 965 | 676 | 68 | 4.9 | 14.5 | 253.2294 | 0 | 57.2494 | 4.7275 | 42.5761 | 15.4149 | 211.7697 | 0 | 40% | 25 | 0 | 56.39% | 0 | 44.9376
2075 | 983 | 812 | 79 | 5.5 | 15.4 | 269.9081 | 0 | 57.1125 | 17.9875 | 42.5932 | 15.3799 | 228.5445 | 0 | 57% | 24.7094 | 0 | 90% | 0 | 44.8745
2076 | 983 | 890 | 89 | 6.5 | 15.7 | 274.4695 | 0 | 31.0124 | 44.0876 | 42.6003 | 15.3682 | 233.0619 | 0 | 74% | 0 | 0 | 90% | 0 | 43.4003
2077 | 993 | 910 | 86 | 6 | 16.2 | 279.0204 | 0 | 30.1855 | 44.9145 | 42.6038 | 15.345 | 237.3889 | 0 | 92% | 0 | 0 | 90% | 0 | 42.4827
2078 | 988 | 862 | 82 | 6.9 | 16.2 | 155.6576 | 135.8868 | 26.1859 | 48.9141 | 42.6057 | 15.3457 | 113.9586 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8272
2079 | 965 | 751 | 77 | 7.3 | 15.9 | 42.1527 | 250.7649 | 25.2017 | 44.1569 | 42.6045 | 15.3602 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2745
2080 | 900 | 582 | 74 | 7.4 | 15.7 | 42.1583 | 212.9907 | 24.6619 | 25.2756 | 42.6019 | 15.3688 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.7433
2081 | 808 | 378 | 61 | 7.8 | 14.8 | 42.1584 | 155.5123 | 26.8085 | 0.40844 | 42.5992 | 15.41 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.9312
2082 | 580 | 160 | 40 | 7.6 | 13.2 | 42.1585 | 55.4307 | 5.1589 | 0 | 42.5967 | 15.4772 | 0 | 0 | 100% | 0 | 25 | 50% | 0 | 46.3493
2083 | 70 | 11 | 6 | 5.8 | 11.2 | 0 | 0 | 0 | 0 | 59.0404 | 22.5834 | 0 | 57.5711 | 96% | 0 | 25 | 10% | 0 | 45.5284
2084 | 0 | 0 | 0 | 3.6 | 10.4 | 0 | 0 | 0 | 0 | 110.8886 | 45.0438 | 0 | 116.0716 | 87% | 0 | 0 | 10% | 0 | 42.0767
2085 | 0 | 0 | 0 | 2.9 | 9.4 | 0 | 0 | 0 | 0 | 99.7324 | 40.405 | 0 | 99.4705 | 80% | 0 | 0 | 10% | 0 | 38.2258
2086 | 0 | 0 | 0 | 3.1 | 8.1 | 0 | 0 | 0 | 0 | 94.6782 | 38.3296 | 0 | 93.3293 | 73% | 0 | 0 | 10% | 0 | 36.2079
2087 | 0 | 0 | 0 | 2.3 | 7.2 | 0 | 0 | 0 | 0 | 90.1643 | 36.4384 | 0 | 87.9293 | 66% | 0 | 0 | 10% | 0 | 34.2915
2088 | 0 | 0 | 0 | 2.1 | 6.9 | 0 | 0 | 0 | 0 | 87.2747 | 35.2212 | 0 | 84.6799 | 60% | 0 | 0 | 10% | 0 | 33.0083
2089 | 0 | 0 | 0 | 0.8 | 5.8 | 0 | 0 | 0 | 0 | 86.4834 | 34.9164 | 0 | 83.9608 | 53% | 0 | 0 | 10% | 0 | 32.6316
2090 | 0 | 0 | 0 | 1.4 | 6.4 | 0 | 0 | 0 | 0 | 86.318 | 34.8305 | 0 | 83.9398 | 47% | 0 | 0 | 10% | 0 | 32.4873
2091 | 0 | 0 | 0 | 1 | 5 | 0 | 0 | 0 | 0 | 88.3451 | 35.7264 | 0 | 86.5015 | 41% | 0 | 0 | 10% | 0 | 33.3344
2092 | 0 | 0 | 0 | 1.9 | 5.8 | 0 | 0 | 0 | 0 | 96.4281 | 39.1379 | 0 | 96.373 | 33% | 0 | 0 | 10% | 0 | 36.7101
2093 | 0 | 0 | 0 | 2.6 | 6 | 0 | 0 | 0 | 0 | 106.1362 | 43.2297 | 0 | 107.9083 | 25% | 0 | 0 | 10% | 0 | 40.8141
2094 | 0 | 0 | 0 | 3.5 | 7.6 | 0 | 0 | 0 | 0 | 113.3975 | 46.2145 | 0 | 116.2215 | 17% | 0 | 0 | 10% | 0 | 43.8545
2095 | 54 | 56 | 48 | 4.6 | 9.6 | 0 | 8.5781 | 0 | 0 | 116.1129 | 47.2716 | 0 | 119.106 | 8% | 0 | 0 | 10% | 0 | 44.9878
2096 | 74 | 159 | 138 | 5 | 10.7 | 0 | 17.025 | 5.0462 | 0 | 104.8387 | 42.5076 | 0 | 105.4144 | 0% | 0 | 0 | 10% | 0 | 45.3653
2097 | 502 | 437 | 188 | 6.2 | 12.1 | 88.6563 | 23.1799 | 32.2156 | 0 | 0 | 0 | 85.6044 | 0 | 6% | 0 | 0 | 10% | 0 | 30.7344
2098 | 653 | 624 | 201 | 7 | 13.2 | 163.2275 | 0 | 53.1831 | 0 | 0 | 0 | 161.176 | 0 | 18% | 6.567 | 0 | 18.93% | 0 | 44.7541
2099 | 651 | 756 | 259 | 7.5 | 14.3 | 170.3251 | 0 | 66.8362 | 0 | 0 | 0 | 168.9794 | 0 | 31% | 20.7436 | 0 | 47.14% | 0 | 44.1417
2100 | 760 | 850 | 220 | 7.5 | 15.5 | 206.9137 | 0 | 70.8076 | 4.2924 | 0 | 0 | 205.4316 | 0 | 47% | 25 | 0 | 81.14% | 0 | 43.5002
2101 | 828 | 914 | 219 | 7.7 | 15.8 | 228.291 | 0 | 51.4205 | 23.6795 | 0 | 0 | 227.0528 | 0 | 64% | 6.5129 | 0 | 90% | 0 | 42.3582
2102 | 729 | 837 | 250 | 7.6 | 16.1 | 195.7287 | 0 | 43.7933 | 31.3067 | 0 | 0 | 194.7193 | 0 | 79% | 0 | 0 | 90% | 0 | 41.5206
2103 | 770 | 736 | 189 | 8.4 | 15.7 | 200.7803 | 0 | 43.3527 | 22.2551 | 0 | 0 | 199.6087 | 0 | 94% | 0 | 0 | 90% | 0 | 41.0039
2104 | 288 | 397 | 226 | 8 | 14.9 | 56.3439 | 0 | 27.391 | 0.11055 | 42.5961 | 1.3644 | 16.1712 | 0 | 95% | 0 | 13.3112 | 68.7% | 0 | 40.6397
2105 | 433 | 309 | 143 | 7.5 | 14.3 | 81.8792 | 0 | 19.7552 | 0 | 42.5941 | 15.4304 | 39.8301 | 0 | 98% | 0 | 7.4007 | 56.86% | 0 | 42.3784
2106 | 400 | 158 | 71 | 7.5 | 13.3 | 0 | 64.4775 | 4.598 | 0 | 47.4357 | 17.4963 | 0 | 45.9231 | 94% | 0 | 25 | 16.86% | 0 | 45.0231
2107 | 28 | 16 | 14 | 6.8 | 11.9 | 0 | 0 | 0 | 0 | 106.0565 | 42.8153 | 0 | 111.1312 | 86% | 0 | 4.2881 | 10% | 0 | 44.1199
2108 | 0 | 0 | 0 | 6.1 | 11.2 | 0 | 0 | 0 | 0 | 107.1915 | 43.4602 | 0 | 108.6616 | 78% | 0 | 0 | 10% | 0 | 41.2037
2109 | 0 | 0 | 0 | 6.1 | 10.5 | 0 | 0 | 0 | 0 | 99.2585 | 40.1552 | 0 | 98.4634 | 71% | 0 | 0 | 10% | 0 | 38.089
2110 | 0 | 0 | 0 | 5.1 | 9.7 | 0 | 0 | 0 | 0 | 94.9766 | 38.3921 | 0 | 93.4425 | 64% | 0 | 0 | 10% | 0 | 36.3299
2111 | 0 | 0 | 0 | 3.7 | 8.6 | 0 | 0 | 0 | 0 | 89.8756 | 36.268 | 0 | 87.3855 | 57% | 0 | 0 | 10% | 0 | 34.1753
2112 | 0 | 0 | 0 | 3.8 | 7.9 | 0 | 0 | 0 | 0 | 85.8551 | 34.5893 | 0 | 82.8168 | 51% | 0 | 0 | 10% | 0 | 32.4316
2113 | 0 | 0 | 0 | 2.3 | 7.3 | 0 | 0 | 0 | 0 | 84.0866 | 33.8618 | 0 | 80.9825 | 45% | 0 | 0 | 10% | 0 | 31.6267
2114 | 0 | 0 | 0 | 3.1 | 7 | 0 | 0 | 0 | 0 | 83.0919 | 33.4522 | 0 | 80.0322 | 39% | 0 | 0 | 10% | 0 | 31.147
2115 | 0 | 0 | 0 | 2.6 | 7 | 0 | 0 | 0 | 0 | 82.8095 | 33.3271 | 0 | 79.9079 | 33% | 0 | 0 | 10% | 0 | 30.9605
2116 | 0 | 0 | 0 | 2.2 | 7.5 | 0 | 0 | 0 | 0 | 84.5861 | 34.0673 | 0 | 82.1087 | 27% | 0 | 0 | 10% | 0 | 31.6472
2117 | 0 | 0 | 0 | 2.3 | 7.5 | 0 | 0 | 0 | 0 | 86.8778 | 35.0365 | 0 | 84.9336 | 20% | 0 | 0 | 10% | 0 | 32.5774
2118 | 0 | 0 | 0 | 2.9 | 7.5 | 0 | 0 | 0 | 0 | 93.9544 | 38.0486 | 0 | 93.6673 | 13% | 0 | 0 | 10% | 0 | 35.5573
2119 | 188 | 58 | 31 | 2.9 | 7.9 | 0 | 30.1696 | 0 | 0 | 101.1779 | 41.0777 | 0 | 102.1881 | 6% | 0 | 0 | 10% | 0 | 38.5902
2120 | 520 | 239 | 80 | 4.5 | 10.6 | 75.5571 | 19.7988 | 12.8847 | 0 | 73.3026 | 28.8998 | 16.1876 | 13.5712 | 6% | 0 | 0 | 10% | 0 | 40.2783
2121 | 630 | 461 | 146 | 6.2 | 12.4 | 142.7987 | 0 | 34.9577 | 0 | 42.5172 | 15.4793 | 100.6991 | 0 | 13% | 8.4555 | 0 | 21.5% | 0 | 40.2837
2122 | 363 | 566 | 332 | 6.8 | 13.6 | 81.5838 | 1.49e-14 | 44.9894 | 0 | 42.5667 | 15.4501 | 40.6238 | 0 | 16% | 19.2309 | 0 | 47.65% | 0 | 40.0369
2123 | 741 | 749 | 183 | 7 | 15.1 | 197.5245 | 0 | 51.5379 | 16.4959 | 42.5695 | 15.3856 | 154.5158 | 0 | 28% | 25 | 0 | 81.65% | 0 | 39.7427
2124 | 651 | 793 | 250 | 8.1 | 15.8 | 173.971 | 0 | 31.6221 | 39.7311 | 42.5893 | 15.3595 | 132.3695 | 0 | 38% | 6.1371 | 0 | 90% | 0 | 38.8466
2125 | 836 | 860 | 154 | 8.7 | 16 | 230.1212 | 0 | 24.2626 | 50.8374 | 42.5936 | 15.3516 | 188.0611 | 0 | 52% | 0 | 0 | 90% | 0 | 37.1044
2126 | 859 | 833 | 143 | 7.8 | 16.2 | 234.5442 | 0 | 23.2434 | 51.8566 | 42.5992 | 15.3434 | 192.7007 | 0 | 66% | 0 | 0 | 90% | 0 | 36.014
2127 | 823 | 721 | 136 | 7.6 | 16.2 | 217.2101 | 0 | 22.3324 | 41.6755 | 42.6022 | 15.3444 | 175.3393 | 0 | 79% | 0 | 0 | 90% | 0 | 35.2453
2128 | 607 | 526 | 170 | 7.1 | 15.9 | 144.6989 | 0 | 20.5451 | 20.5134 | 42.6033 | 15.3598 | 102.9208 | 0 | 86% | 0 | 0 | 90% | 0 | 35.3609
2129 | 373 | 318 | 159 | 7 | 15.2 | 68.2571 | -1.49e-14 | 18.5347 | 0 | 42.6024 | 15.3927 | 26.594 | 0 | 88% | 0 | 2.817 | 85.49% | 0 | 37.3841
2130 | 56 | 101 | 86 | 6.3 | 13.7 | 0 | 10.9414 | 0.8243 | 0 | 45.6484 | 16.7267 | 0 | 44.1659 | 85% | 0 | 24.869 | 45.7% | 0 | 40.3494
2131 | 0 | 7 | 7 | 6 | 12.1 | 0 | 0 | 0 | 0 | 55.6129 | 21.063 | 0 | 54.7189 | 81% | 0 | 22.3139 | 10% | 0 | 40.3923
2132 | 0 | 0 | 0 | 5.5 | 11.2 | 0 | 0 | 0 | 0 | 102.9523 | 41.6783 | 0 | 106.2978 | 73% | 0 | 0 | 10% | 0 | 38.7286
2133 | 0 | 0 | 0 | 4.7 | 11.1 | 0 | 0 | 0 | 0 | 95.8815 | 38.7053 | 0 | 96.5239 | 66% | 0 | 0 | 10% | 0 | 36.0766
2134 | 0 | 0 | 0 | 4.9 | 10.8 | 0 | 0 | 0 | 0 | 89.7996 | 36.1414 | 0 | 88.7102 | 59% | 0 | 0 | 10% | 0 | 33.6215
2135 | 0 | 0 | 0 | 3.9 | 10.4 | 0 | 0 | 0 | 0 | 84.0248 | 33.7186 | 0 | 81.7491 | 53% | 0 | 0 | 10% | 0 | 31.2123
2136 | 0 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 81.191 | 32.4749 | 0 | 78.8315 | 47% | 0 | 0 | 10% | 0 | 29.9319
2137 | 0 | 0 | 0 | 2.6 | 9.9 | 0 | 0 | 0 | 0 | 79.4111 | 31.6685 | 0 | 77.133 | 42% | 0 | 0 | 10% | 0 | 29.0898
2138 | 0 | 0 | 0 | 3 | 9.7 | 0 | 0 | 0 | 0 | 78.7758 | 31.3889 | 0 | 76.5701 | 36% | 0 | 0 | 10% | 0 | 28.7804
2139 | 0 | 0 | 0 | 1.5 | 9.4 | 0 | 0 | 0 | 0 | 79.6691 | 31.8078 | 0 | 77.5377 | 30% | 0 | 0 | 10% | 0 | 29.1727
2140 | 0 | 0 | 0 | 1.7 | 9.1 | 0 | 0 | 0 | 0 | 81.2349 | 32.5353 | 0 | 79.1773 | 24% | 0 | 0 | 10% | 0 | 29.8769
2141 | 0 | 0 | 0 | 2.1 | 9.2 | 0 | 0 | 0 | 0 | 81.1398 | 32.4891 | 0 | 79.1232 | 18% | 0 | 0 | 10% | 0 | 29.8132
2142 | 0 | 0 | 0 | 2.5 | 9.2 | 0 | 0 | 0 | 0 | 86.132 | 34.6613 | 0 | 84.794 | 12% | 0 | 0 | 10% | 0 | 31.962
2143 | 0 | 8 | 8 | 2.2 | 9.5 | 0 | 0 | 0 | 0 | 92.48 | 37.3455 | 0 | 92.5838 | 5% | 0 | 0 | 10% | 0 | 34.6343
2144 | 0 | 22 | 22 | 2.9 | 9.5 | 0 | 0 | 0 | 0 | 70.6147 | 28.579 | 0 | 71.3288 | 0% | 0 | 0 | 10% | 0 | 25.9303
2145 | 0 | 43 | 43 | 1.9 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5241
2146 | 0 | 59 | 57 | 1.5 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4974
2147 | 0 | 84 | 81 | 1.3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4711
2148 | 0 | 70 | 69 | 0.8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4454
2149 | 0 | 89 | 88 | 0.9 | 11.5 | 0 | 0 | 0.099497 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3207
2150 | 0 | 83 | 82 | 2.3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3954
2151 | 0 | 65 | 63 | 1.8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3711
2152 | 0 | 44 | 43 | 1.6 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3474
2153 | 0 | 41 | 40 | 1.1 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3241
2154 | 1 | 37 | 36 | 1.7 | 11.6 | 0 | 0.19627 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3012
2155 | 0 | 3 | 3 | 1.1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2787
2156 | 0 | 0 | 0 | 0.7 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2567
2157 | 0 | 0 | 0 | 0.5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2351
2158 | 0 | 0 | 0 | 0.9 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2139
2159 | 0 | 0 | 0 | 0.7 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1932
2160 | 0 | 0 | 0 | 0.5 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1728
2161 | 0 | 0 | 0 | 0.1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1528
2162 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1332
2163 | 0 | 0 | 0 | 0.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1139
2164 | 0 | 0 | 0 | 0.4 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0951
2165 | 0 | 0 | 0 | 0.5 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0767
2166 | 0 | 0 | 0 | 1.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0585
2167 | 195 | 67 | 34 | 1.8 | 10.1 | 0 | 31.9217 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0407
2168 | 523 | 272 | 106 | 1.2 | 11.6 | 78.7593 | 20.0564 | 14.9904 | 0 | 0 | 0 | 72.7607 | 0 | 6% | 0 | 0 | 10% | 0 | 13.5925
2169 | 218 | 351 | 252 | 1.1 | 13.4 | 0 | 47.2275 | 22.7354 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | 21.6523
2170 | 311 | 482 | 266 | 1.5 | 14.8 | 70.6739 | 0 | 35.6007 | 0 | 0 | 0 | 66.4892 | 0 | 11% | 0 | 0 | 10% | 0 | 34.5706
2171 | 821 | 797 | 160 | 2.4 | 16.1 | 224.7799 | 0 | 71.3065 | 0 | 41.9592 | 0 | 178.7538 | 0 | 25% | 23.9355 | 0 | 42.55% | 0 | 44.4281
2172 | 929 | 916 | 137 | 2.4 | 17.2 | 262.5433 | 0 | 65.4784 | 9.6216 | 42.3644 | 6.3498 | 220.1356 | 0 | 41% | 25 | 0 | 76.55% | 0 | 43.7026
2173 | 926 | 928 | 139 | 3.8 | 18.1 | 261.9054 | 0 | 40.4402 | 34.6598 | 42.4639 | 15.1936 | 220.0591 | 0 | 58% | 9.888 | 0 | 90% | 0 | 42.8876
2174 | 918 | 874 | 130 | 5 | 18.5 | 254.6974 | 0 | 29.9076 | 45.1924 | 42.5001 | 15.1832 | 212.9768 | 0 | 74% | 0 | 0 | 90% | 0 | 42.2804
2175 | 527 | 582 | 190 | 6.3 | 18.1 | 132.5898 | 0 | 27.8932 | 18.7759 | 42.5271 | 15.2162 | 91.5041 | 0 | 81% | 0 | 0 | 90% | 0 | 41.4321
2176 | 545 | 503 | 197 | 4.3 | 18.1 | 130.4024 | 0 | 28.2879 | 11.367 | 42.5347 | 15.2189 | 88.5911 | 0 | 87% | 0 | 0 | 90% | 0 | 41.8579
2177 | 587 | 406 | 158 | 2.8 | 18.3 | 123.9406 | 0 | 26.1597 | 0 | 42.5407 | 15.2094 | 81.8394 | 0 | 93% | 0 | 3.4087 | 84.55% | 0 | 44.6242
2178 | 23 | 63 | 56 | 5.1 | 16 | 0 | 4.5345 | 0 | 0 | 62.198 | 23.725 | 0 | 60.8257 | 89% | 0 | 25 | 44.55% | 0 | 46.6434
2179 | 0 | 7 | 7 | 3 | 14.5 | 0 | 0 | 0 | 0 | 63.7254 | 24.4569 | 0 | 63.1632 | 84% | 0 | 21.5913 | 10% | 0 | 43.0847
2180 | 0 | 0 | 0 | 1.9 | 14 | 0 | 0 | 0 | 0 | 104.2691 | 42.0686 | 0 | 107.7009 | 76% | 0 | 0 | 10% | 0 | 39.1888
2181 | 0 | 0 | 0 | 2.7 | 12.6 | 0 | 0 | 0 | 0 | 96.6896 | 38.9644 | 0 | 97.125 | 69% | 0 | 0 | 10% | 0 | 36.4433
2182 | 0 | 0 | 0 | 3 | 12 | 0 | 0 | 0 | 0 | 91.2262 | 36.6891 | 0 | 90.1585 | 62% | 0 | 0 | 10% | 0 | 34.2676
2183 | 0 | 0 | 0 | 2.5 | 11.4 | 0 | 0 | 0 | 0 | 87.935 | 35.3241 | 0 | 86.1278 | 56% | 0 | 0 | 10% | 0 | 32.9103
2184 | 0 | 0 | 0 | 1.7 | 11 | 0 | 0 | 0 | 0 | 86.3194 | 34.6617 | 0 | 84.2682 | 50% | 0 | 0 | 10% | 0 | 32.2226
2185 | 0 | 0 | 0 | 1.4 | 10.5 | 0 | 0 | 0 | 0 | 85.9713 | 34.5376 | 0 | 83.9449 | 43% | 0 | 0 | 10% | 0 | 32.0665
2186 | 0 | 0 | 0 | 0.9 | 10.2 | 0 | 0 | 0 | 0 | 87.7984 | 35.3244 | 0 | 86.2145 | 37% | 0 | 0 | 10% | 0 | 32.823
2187 | 0 | 0 | 0 | 1.1 | 9.9 | 0 | 0 | 0 | 0 | 96.0714 | 38.8462 | 0 | 96.321 | 30% | 0 | 0 | 10% | 0 | 36.3202
2188 | 0 | 0 | 0 | 0.8 | 9 | 0 | 0 | 0 | 0 | 108.4901 | 44.1099 | 0 | 111.0723 | 21% | 0 | 0 | 10% | 0 | 41.6002
2189 | 0 | 0 | 0 | 1.1 | 8.5 | 0 | 0 | 0 | 0 | 115.1211 | 46.9043 | 0 | 118.6398 | 13% | 0 | 0 | 10% | 0 | 44.4681
2190 | 0 | 0 | 0 | 1.4 | 8 | 0 | 0 | 0 | 0 | 117.6451 | 47.9775 | 0 | 121.2124 | 3% | 0 | 0 | 10% | 0 | 45.6297
2191 | 134 | 73 | 31 | 1.2 | 8.4 | 0 | 22.1502 | 0 | 0 | 43.1686 | 17.6024 | 0 | 44.3966 | 0% | 0 | 0 | 10% | 0 | 15.4631
2192 | 570 | 283 | 60 | 0.5 | 11.4 | 87.8223 | 22.2871 | 12.8207 | 0 | 0 | 0 | 84.6596 | 0 | 6% | 0 | 0 | 10% | 0 | 11.3393
2193 | 768 | 500 | 119 | 1 | 14.2 | 183.6032 | 0 | 39.7013 | 0 | 0 | 0 | 181.1274 | 0 | 20% | 0 | 0 | 10% | 0 | 37.6609
2194 | 663 | 596 | 158 | 1.8 | 16.1 | 170.9832 | 0 | 49.9516 | 0 | 0 | 0 | 169.7012 | 0 | 33% | 2.8606 | 0 | 13.89% | 0 | 45.132
2195 | 868 | 810 | 141 | 2.9 | 17.9 | 238.66 | 0 | 71.8293 | 1.1672 | 0 | 0 | 236.9094 | 0 | 51% | 25 | 0 | 47.89% | 0 | 44.2298
2196 | 968 | 942 | 132 | 3.1 | 19.6 | 273.7022 | 5.96e-14 | 71.5065 | 3.5935 | 0 | 0 | 272.2673 | 0 | 71% | 25 | 0 | 81.89% | 0 | 43.5314
2197 | 910 | 957 | 183 | 2.8 | 20.7 | 257.8536 | 0 | 51.8072 | 23.2928 | 0 | 0 | 256.6794 | 0 | 91% | 5.9629 | 0 | 90% | 0 | 42.9542
2198 | 938 | 914 | 153 | 2.7 | 21.6 | 121.4771 | 153.843 | 44.0343 | 31.0657 | 0 | 0 | 120.9286 | 0 | 100% | 0 | 0 | 90% | 0 | 42.3962
2199 | 645 | 754 | 282 | 4.8 | 21.9 | 41.011 | 151.5715 | 42.0999 | 20.9093 | 42.5941 | 0.54963 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.6759
2200 | 402 | 490 | 252 | 5.8 | 20.7 | 42.1579 | 62.7929 | 26.3163 | 9.0393 | 42.5919 | 15.0792 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.1069
2201 | 247 | 271 | 171 | 5.2 | 19.7 | 0 | 50.722 | 14.3912 | 0 | 42.5888 | 15.1425 | 0 | 41.0976 | 97% | 0 | 17.0801 | 62.67% | 0 | 44.5454
2202 | 206 | 130 | 76 | 3.9 | 18.9 | 0 | 40.7937 | 2.1133 | 0 | 59.3629 | 22.3279 | 0 | 57.7421 | 93% | 0 | 25 | 22.67% | 0 | 46.5174
2203 | 1 | 10 | 10 | 2.5 | 17.1 | 0 | 0.007945 | 0 | 0 | 95.9734 | 38.1442 | 0 | 99.4432 | 85% | 0 | 7.9199 | 10% | 0 | 43.1363
2204 | 0 | 0 | 0 | 1.8 | 16.1 | 0 | 0 | 0 | 0 | 104.1751 | 41.8736 | 0 | 105.6813 | 78% | 0 | 0 | 10% | 0 | 39.4683
2205 | 0 | 0 | 0 | 1.1 | 14.9 | 0 | 0 | 0 | 0 | 97.3374 | 39.0883 | 0 | 96.7272 | 70% | 0 | 0 | 10% | 0 | 36.8821
2206 | 0 | 0 | 0 | 0.9 | 14 | 0 | 0 | 0 | 0 | 91.8961 | 36.8546 | 0 | 90.146 | 63% | 0 | 0 | 10% | 0 | 34.6729
2207 | 0 | 0 | 0 | 1.5 | 13.8 | 0 | 0 | 0 | 0 | 88.713 | 35.5171 | 0 | 86.4101 | 57% | 0 | 0 | 10% | 0 | 33.2986
2208 | 0 | 0 | 0 | 0.9 | 12.2 | 0 | 0 | 0 | 0 | 87.2786 | 35.0032 | 0 | 84.8664 | 51% | 0 | 0 | 10% | 0 | 32.7298
2209 | 0 | 0 | 0 | 0.5 | 12.1 | 0 | 0 | 0 | 0 | 86.9124 | 34.8543 | 0 | 84.5867 | 44% | 0 | 0 | 10% | 0 | 32.5291
2210 | 0 | 0 | 0 | 0.8 | 11.7 | 0 | 0 | 0 | 0 | 88.6674 | 35.6178 | 0 | 86.8185 | 38% | 0 | 0 | 10% | 0 | 33.2472
2211 | 0 | 0 | 0 | 0.6 | 10.8 | 0 | 0 | 0 | 0 | 96.563 | 39.0084 | 0 | 96.4516 | 31% | 0 | 0 | 10% | 0 | 36.6018
2212 | 0 | 0 | 0 | 1.5 | 11.1 | 0 | 0 | 0 | 0 | 108.7262 | 44.1074 | 0 | 110.8844 | 22% | 0 | 0 | 10% | 0 | 41.7054
2213 | 0 | 0 | 0 | 2 | 11 | 0 | 0 | 0 | 0 | 115.435 | 46.918 | 0 | 118.5676 | 13% | 0 | 0 | 10% | 0 | 44.5775
2214 | 0 | 1 | 1 | 2 | 10.6 | 0 | 0 | 0 | 0 | 118.0621 | 48.0326 | 0 | 121.2949 | 4% | 0 | 0 | 10% | 0 | 45.7706
2215 | 368 | 82 | 30 | 1.6 | 11.1 | 0 | 50.3842 | 0 | 0 | 52.5093 | 21.3531 | 0 | 53.7948 | 0% | 0 | 0 | 10% | 0 | 19.2807
2216 | 727 | 289 | 56 | 0.6 | 15.1 | 143.2972 | 0 | 16.5434 | 0 | 0 | 0 | 138.3551 | 0 | 11% | 0 | 0 | 10% | 0 | 14.8879
2217 | 874 | 502 | 63 | 0.7 | 16.9 | 211.8261 | 0 | 39.4153 | 0 | 0 | 0 | 209.7676 | 0 | 26% | 0 | 0 | 10% | 0 | 37.1064
2218 | 948 | 690 | 67 | 1.7 | 19.1 | 252.2082 | 0 | 59.9931 | 0 | 0 | 0 | 250.6768 | 0 | 45% | 12.8089 | 0 | 27.42% | 0 | 44.4671
2219 | 976 | 825 | 72 | 2.4 | 20.2 | 270.8467 | 0 | 72.3311 | 2.3071 | 0 | 0 | 269.5405 | 0 | 66% | 25 | 0 | 61.42% | 0 | 44.3889
2220 | 993 | 907 | 75 | 4.8 | 21.1 | 279.3465 | 0 | 67.457 | 7.643 | 0 | 0 | 278.1547 | 0 | 87% | 21.0146 | 0 | 90% | 0 | 43.3539
2221 | 981 | 918 | 83 | 6.7 | 21 | 173.133 | 113.0436 | 44.9835 | 30.1165 | 0 | 0 | 172.4319 | 0 | 100% | 0 | 0 | 90% | 0 | 42.8535
2222 | 932 | 857 | 100 | 4.8 | 21.3 | 0 | 284.4901 | 43.9655 | 31.1345 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4591
2223 | 858 | 735 | 117 | 5.3 | 21.9 | 0 | 253.4402 | 43.6224 | 19.652 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.0019
2224 | 838 | 581 | 92 | 6.2 | 22.4 | 40.2618 | 198.3285 | 43.8184 | 2.4133 | 42.5933 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.5039
2225 | 742 | 378 | 72 | 5.8 | 22.6 | 42.1345 | 141.5038 | 24.3712 | 0 | 42.5909 | 14.4694 | 0 | 0 | 100% | 0 | 5.2319 | 81.63% | 0 | 44.7015
2226 | 484 | 159 | 48 | 5.5 | 21.5 | 47.1435 | 31.5242 | 3.883 | 0 | 47.4884 | 17.0489 | 0 | 0 | 100% | 0 | 25 | 41.63% | 0 | 46.6283
2227 | 78 | 15 | 9 | 5 | 19.9 | 0 | 0.97451 | 0 | 0 | 66.0644 | 25.1176 | 0 | 66.1372 | 95% | 0 | 19.7681 | 10% | 0 | 42.8164
2228 | 0 | 0 | 0 | 5.4 | 19.5 | 0 | 0 | 0 | 0 | 104.9871 | 41.9489 | 0 | 107.6739 | 87% | 0 | 0 | 10% | 0 | 39.3015
2229 | 0 | 0 | 0 | 4.2 | 18.3 | 0 | 0 | 0 | 0 | 97.7789 | 39.0263 | 0 | 97.1812 | 80% | 0 | 0 | 10% | 0 | 36.8443
2230 | 0 | 0 | 0 | 3.2 | 17 | 0 | 0 | 0 | 0 | 92.1692 | 36.7694 | 0 | 90.3892 | 73% | 0 | 0 | 10% | 0 | 34.6199
2231 | 0 | 0 | 0 | 2.5 | 15.4 | 0 | 0 | 0 | 0 | 88.7584 | 35.4343 | 0 | 86.4245 | 67% | 0 | 0 | 10% | 0 | 33.2336
2232 | 0 | 0 | 0 | 2.5 | 14.5 | 0 | 0 | 0 | 0 | 87.2299 | 34.847 | 0 | 84.8178 | 60% | 0 | 0 | 10% | 0 | 32.576
2233 | 0 | 0 | 0 | 1.5 | 13.6 | 0 | 0 | 0 | 0 | 87.0262 | 34.8165 | 0 | 84.7636 | 54% | 0 | 0 | 10% | 0 | 32.4831
2234 | 0 | 0 | 0 | 1.6 | 12.8 | 0 | 0 | 0 | 0 | 88.8568 | 35.6376 | 0 | 87.1028 | 47% | 0 | 0 | 10% | 0 | 33.2547
2235 | 0 | 0 | 0 | 1.5 | 11.5 | 0 | 0 | 0 | 0 | 96.7568 | 39.0532 | 0 | 96.7401 | 40% | 0 | 0 | 10% | 0 | 36.6358
2236 | 0 | 0 | 0 | 1.7 | 10.9 | 0 | 0 | 0 | 0 | 109.5553 | 44.4635 | 0 | 111.9026 | 32% | 0 | 0 | 10% | 0 | 42.0586
2237 | 0 | 0 | 0 | 3.5 | 10.9 | 0 | 0 | 0 | 0 | 116.691 | 47.4474 | 0 | 120.0434 | 23% | 0 | 0 | 10% | 0 | 45.1196
2238 | 0 | 1 | 1 | 2.8 | 9.9 | 0 | 0 | 0 | 0 | 120.2137 | 48.9611 | 0 | 123.741 | 13% | 0 | 0 | 10% | 0 | 46.726
2239 | 41 | 47 | 38 | 3.3 | 10.5 | 0 | 6.9071 | 0 | 0 | 120.564 | 49.0766 | 0 | 123.7101 | 4% | 0 | 0 | 10% | 0 | 46.9295
2240 | 265 | 226 | 141 | 4.4 | 11.9 | 0 | 51.726 | 10.4726 | 0 | 51.347 | 20.6986 | 0 | 50.3716 | 0% | 0 | 0 | 10% | 0 | 29.1947
2241 | 122 | 312 | 252 | 4.8 | 12.6 | 0 | 34.2202 | 17.3561 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 15.4499
2242 | 24 | 331 | 310 | 4.4 | 13.1 | 0 | 7.3027 | 16.2799 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 14.3886
2243 | 450 | 713 | 350 | 5.8 | 14 | 91.692 | 23.6606 | 58.7963 | 0 | 0 | 0 | 88.159 | 0 | 7% | 13.3579 | 0 | 28.17% | 0 | 43.9543
2244 | 112 | 595 | 489 | 5.1 | 14.2 | 0 | 36.1642 | 43.7053 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 28.17% | 0 | 42.7764
2245 | 38 | 404 | 364 | 5 | 14.2 | 0 | 12.318 | 25.4191 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 11.3542 | 10% | 0 | 34.9155
2246 | 1 | 155 | 152 | 4.3 | 13.6 | 0 | 0.31954 | 3.572 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | 1.7254
2247 | 0 | 91 | 90 | 4.8 | 13.2 | 0 | 0 | 0.16945 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.6624
2248 | 0 | 47 | 46 | 4.3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.8175
2249 | 0 | 23 | 23 | 3.1 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.8034
2250 | 0 | 7 | 7 | 1.6 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7896
2251 | 0 | 0 | 0 | 2.6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7761
2252 | 0 | 0 | 0 | 3 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7629
2253 | 0 | 0 | 0 | 2.3 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7499
2254 | 0 | 0 | 0 | 2.4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7372
2255 | 0 | 0 | 0 | 2.5 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7247
2256 | 0 | 0 | 0 | 2.9 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7126
2257 | 0 | 0 | 0 | 1.4 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7007
2258 | 0 | 0 | 0 | 1.1 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.689
2259 | 0 | 0 | 0 | 1.1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.6776
2260 | 0 | 0 | 0 | 0.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.6664
2261 | 0 | 0 | 0 | 0.6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.6553
2262 | 1 | 1 | 1 | 0.4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.6446
2263 | 64 | 58 | 49 | 0.4 | 7.9 | 0 | 10.8821 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.634
2264 | 1 | 119 | 117 | 1.3 | 9.9 | 0 | 0.23786 | 1.596 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -0.027628
2265 | 582 | 412 | 98 | 2.5 | 12.1 | 109.632 | 27.7903 | 28.6796 | 0 | 0 | 0 | 104.1286 | 0 | 15% | 0 | 0 | 10% | 0 | 27.0701
2266 | 804 | 694 | 151 | 5.8 | 14.7 | 208.1844 | 0 | 59.3631 | 0 | 0 | 0 | 203.8341 | 0 | 31% | 10.3242 | 0 | 24.04% | 0 | 46.7255
2267 | 722 | 767 | 204 | 8.2 | 15.2 | 190.9655 | 0 | 68.0601 | 0 | 0 | 0 | 188.6183 | 0 | 45% | 20.8716 | 0 | 52.43% | 0 | 44.9955
2268 | 458 | 794 | 392 | 9.6 | 14 | 114.3262 | 0 | 66.921 | 0 | 42.4139 | 0 | 74.2093 | 0 | 51% | 24.9191 | 0 | 86.32% | 0 | 39.9829
2269 | 75 | 360 | 291 | 8.1 | 13.8 | 0 | 24.3178 | 22.0169 | 0 | 42.4398 | 6.452 | 0 | 39.1642 | 48% | 0 | 16.8248 | 59.4% | 0 | 44.1351
2270 | 1 | 230 | 226 | 7.4 | 12.9 | 0 | 0.31956 | 8.4487 | 0 | 42.435 | 15.4304 | 0 | 39.259 | 45% | 0 | 21.7067 | 24.67% | 0 | 43.7139
2271 | 1 | 141 | 139 | 6.5 | 10.1 | 0 | 0.31081 | 2.8324 | 0 | 83.7194 | 33.3735 | 0 | 82.6667 | 39% | 0 | 9.1661 | 10% | 0 | 43.3474
2272 | 3 | 209 | 205 | 4.4 | 10.7 | 0 | 0.88023 | 7.1411 | 0 | 95.1706 | 38.433 | 0 | 93.5286 | 32% | 0 | 0 | 10% | 0 | 43.5429
2273 | 145 | 266 | 198 | 4.5 | 12 | 0 | 37.7309 | 12.6773 | 0 | 85.763 | 34.381 | 0 | 82.3564 | 25% | 0 | 0 | 10% | 0 | 45.0151
2274 | 214 | 137 | 80 | 5 | 12.6 | 0 | 42.9335 | 2.3964 | 0 | 114.0138 | 46.2332 | 0 | 116.1398 | 17% | 0 | 0 | 10% | 0 | 46.4711
2275 | 96 | 17 | 9 | 7.4 | 11.4 | 0 | 2.0832 | 0 | 0 | 111.3622 | 45.1961 | 0 | 112.693 | 8% | 0 | 0 | 10% | 0 | 43.1028
2276 | 0 | 0 | 0 | 8.6 | 10.5 | 0 | 0 | 0 | 0 | 104.0018 | 42.1689 | 0 | 103.8917 | 0% | 0 | 0 | 10% | 0 | 40.1265
2277 | 0 | 0 | 0 | 5.6 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8901
2278 | 0 | 0 | 0 | 4.6 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8755
2279 | 0 | 0 | 0 | 2.8 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8613
2280 | 0 | 0 | 0 | 1.6 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8472
2281 | 0 | 0 | 0 | 3.1 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8335
2282 | 0 | 0 | 0 | 6.1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8199
2283 | 0 | 0 | 0 | 5.9 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8067
2284 | 0 | 0 | 0 | 6.9 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7936
2285 | 0 | 0 | 0 | 6.6 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7809
2286 | 3 | 1 | 1 | 7.4 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7683
2287 | 462 | 101 | 31 | 7.6 | 9.4 | 0 | 68.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7542
2288 | 783 | 322 | 59 | 8.5 | 11.1 | 151.5989 | 0 | 18.7784 | 0 | 0 | 0 | 142.9082 | 0 | 11% | 0 | 0 | 10% | 0 | 17.0391
2289 | 903 | 527 | 60 | 9.9 | 12.5 | 213.2095 | 0 | 41.309 | 0 | 0 | 0 | 209.7141 | 0 | 27% | 0 | 0 | 10% | 0 | 38.967
2290 | 961 | 710 | 65 | 8.8 | 14 | 250.5567 | 0 | 61.7158 | 0 | 42.434 | 0 | 209.0341 | 0 | 44% | 21.9719 | 0 | 39.88% | 0 | 36.4897
2291 | 896 | 813 | 109 | 6.9 | 15.3 | 243.7456 | 0 | 68.8487 | 3.9651 | 0 | 0 | 242.0314 | 0 | 62% | 25 | 0 | 73.88% | 0 | 41.1534
2292 | 677 | 774 | 196 | 4.9 | 15.7 | 184.8505 | 0 | 53.2635 | 15.5892 | 0 | 0 | 183.5653 | 0 | 76% | 11.8516 | 0 | 90% | 0 | 39.2276
2293 | 303 | 511 | 244 | 6.4 | 15.9 | 70.6928 | 0 | 38.979 | 2.1468 | 0 | 0 | 70.1712 | 0 | 81% | 0 | 0 | 90% | 0 | 37.8751
2294 | 552 | 619 | 170 | 8.9 | 15.7 | 141.7186 | -1.15e-14 | 33.3582 | 19.7709 | 42.5491 | 5.9079 | 100.3099 | 0 | 89% | 0 | 0 | 90% | 0 | 37.1693
2295 | 193 | 287 | 137 | 7.5 | 14.8 | 0 | 46.5705 | 17.9619 | 0 | 42.5522 | 15.393 | 0 | 40.0011 | 86% | 0 | 5.1168 | 81.81% | 0 | 37.1126
2296 | 35 | 259 | 233 | 8.1 | 13.2 | 0 | 10.2714 | 12.0251 | 0 | 42.5493 | 15.46 | 0 | 40.1663 | 83% | 0 | 12.5705 | 61.7% | 0 | 37.6637
2297 | 6 | 71 | 68 | 6.9 | 11.2 | 0 | 1.5647 | 0 | 0 | 45.9763 | 16.9604 | 0 | 43.6553 | 80% | 0 | 25 | 21.7% | 0 | 39.463
2298 | 70 | 67 | 54 | 7.6 | 9.8 | 0 | 14.1035 | 0 | 0 | 93.2472 | 37.4451 | 0 | 95.1714 | 73% | 0 | 7.3128 | 10% | 0 | 42.1276
2299 | 5 | 11 | 10 | 5 | 9.2 | 0 | 0.13175 | 0 | 0 | 104.5392 | 42.4474 | 0 | 106.1903 | 65% | 0 | 0 | 10% | 0 | 40.0204
2300 | 0 | 0 | 0 | 7.7 | 9.4 | 0 | 0 | 0 | 0 | 99.5892 | 40.3469 | 0 | 99.6552 | 57% | 0 | 0 | 10% | 0 | 38.062
2301 | 0 | 0 | 0 | 6.8 | 8.8 | 0 | 0 | 0 | 0 | 92.3366 | 37.3108 | 0 | 90.8495 | 50% | 0 | 0 | 10% | 0 | 35.0777
2302 | 0 | 0 | 0 | 6.6 | 8.8 | 0 | 0 | 0 | 0 | 86.5367 | 34.8474 | 0 | 83.9006 | 44% | 0 | 0 | 10% | 0 | 32.6015
2303 | 0 | 0 | 0 | 7.8 | 8.4 | 0 | 0 | 0 | 0 | 81.8336 | 32.8376 | 0 | 78.727 | 38% | 0 | 0 | 10% | 0 | 30.5427
2304 | 0 | 0 | 0 | 8.1 | 9.2 | 0 | 0 | 0 | 0 | 79.9703 | 31.9578 | 0 | 77.0342 | 32% | 0 | 0 | 10% | 0 | 29.6025
2305 | 0 | 0 | 0 | 7.5 | 8.7 | 0 | 0 | 0 | 0 | 79.197 | 31.6258 | 0 | 76.398 | 27% | 0 | 0 | 10% | 0 | 29.22
2306 | 0 | 0 | 0 | 6.9 | 8.9 | 0 | 0 | 0 | 0 | 79.0061 | 31.5331 | 0 | 76.3212 | 21% | 0 | 0 | 10% | 0 | 29.0844
2307 | 0 | 0 | 0 | 8.4 | 9.6 | 0 | 0 | 0 | 0 | 80.2657 | 32.08 | 0 | 77.6851 | 15% | 0 | 0 | 10% | 0 | 29.5929
2308 | 0 | 0 | 0 | 7.9 | 9.4 | 0 | 0 | 0 | 0 | 81.8523 | 32.8155 | 0 | 79.3688 | 9% | 0 | 0 | 10% | 0 | 30.2944
2309 | 0 | 0 | 0 | 8.6 | 9.5 | 0 | 0 | 0 | 0 | 83.9478 | 33.7305 | 0 | 81.7599 | 3% | 0 | 0 | 10% | 0 | 31.1786
2310 | 9 | 1 | 1 | 9.7 | 9.5 | 0 | 0 | 0 | 0 | 40.0763 | 16.172 | 0 | 39.7987 | 0% | 0 | 0 | 10% | 0 | 13.6557
2311 | 475 | 101 | 27 | 9.7 | 10 | 0 | 71.1855 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4437
2312 | 774 | 319 | 57 | 10.1 | 11.3 | 149.2106 | 0 | 18.3839 | 0 | 0 | 0 | 143.5951 | 0 | 11% | 0 | 0 | 10% | 0 | 16.6999
2313 | 722 | 573 | 194 | 10.8 | 12.8 | 165.7585 | 0 | 44.1649 | 0 | 0 | 0 | 164.0123 | 0 | 23% | 4.5217 | 0 | 16.15% | 0 | 37.7711
2314 | 891 | 748 | 141 | 11.5 | 14 | 228.6173 | 0 | 57.5193 | 6.4906 | 42.5478 | 7.542 | 186.702 | 0 | 37% | 23.8739 | 0 | 48.62% | 0 | 38.4423
2315 | 971 | 877 | 110 | 11.6 | 15.3 | 261.9135 | 0 | 50.7957 | 24.3043 | 42.5684 | 15.3757 | 220.032 | 0 | 53% | 25 | 0 | 82.62% | 0 | 38.3628
2316 | 970 | 956 | 125 | 12 | 16.1 | 266.8007 | 0 | 29.3461 | 45.7539 | 42.5855 | 15.3435 | 225.0165 | 0 | 70% | 5.4279 | 0 | 90% | 0 | 36.374
2317 | 958 | 985 | 152 | 10.8 | 17 | 265.5939 | 0 | 22.8242 | 52.2758 | 42.5916 | 15.2997 | 223.7064 | 0 | 86% | 0 | 0 | 90% | 0 | 35.2261
2318 | 971 | 990 | 186 | 9.8 | 17.6 | 226.5352 | 46.2167 | 17.9417 | 57.1583 | 42.5962 | 15.2686 | 184.4937 | 0 | 100% | 0 | 0 | 90% | 0 | 35.1443
2319 | 820 | 936 | 331 | 9.6 | 18.3 | 42.1526 | 204.7408 | 19.6627 | 55.4373 | 42.5975 | 15.2297 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.6043
2320 | 839 | 797 | 293 | 8.3 | 18.9 | 42.1581 | 196.3046 | 20.8644 | 42.2666 | 42.5951 | 15.1938 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.77
2321 | 455 | 399 | 202 | 9 | 18 | 42.1581 | 62.1642 | 23.4077 | 0.57415 | 42.5926 | 15.2455 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.3651
2322 | 296 | 175 | 95 | 7.6 | 16.9 | 0 | 46.7234 | 4.081 | 0 | 43.9826 | 15.8779 | 0 | 42.4768 | 97% | 0 | 24.4763 | 50.84% | 0 | 42.3698
2323 | 14 | 19 | 18 | 4.6 | 16 | 0 | 0.43438 | 0 | 0 | 49.8589 | 18.3908 | 0 | 48.2071 | 93% | 0 | 25 | 10.84% | 0 | 40.468
2324 | 0 | 0 | 0 | 3.6 | 15.4 | 0 | 0 | 0 | 0 | 101.3175 | 40.7227 | 0 | 104.2869 | 86% | 0 | 0 | 10.84% | 0 | 37.7844
2325 | 0 | 0 | 0 | 1.6 | 15.1 | 0 | 0 | 0 | 0 | 92.8656 | 37.1948 | 0 | 92.2819 | 79% | 0 | 0 | 10.84% | 0 | 34.748
2326 | 0 | 0 | 0 | 0.5 | 14.4 | 0 | 0 | 0 | 0 | 86.8341 | 34.6859 | 0 | 84.7575 | 72% | 0 | 0 | 10.84% | 0 | 32.2931
2327 | 0 | 0 | 0 | 0.8 | 14 | 0 | 0 | 0 | 0 | 83.5301 | 33.3212 | 0 | 81.013 | 66% | 0 | 0 | 10.84% | 0 | 30.8755
2328 | 0 | 0 | 0 | 0.9 | 13.3 | 0 | 0 | 0 | 0 | 82.0406 | 32.6988 | 0 | 79.6198 | 61% | 0 | 0 | 10.84% | 0 | 30.1869
2329 | 0 | 0 | 0 | 1.2 | 12.9 | 0 | 0 | 0 | 0 | 82.32 | 32.8504 | 0 | 80.0466 | 55% | 0 | 0 | 10.84% | 0 | 30.2864
2330 | 0 | 0 | 0 | 1 | 11.9 | 0 | 0 | 0 | 0 | 84.9794 | 34.0495 | 0 | 83.1814 | 48% | 0 | 0 | 10.84% | 0 | 31.4439
2331 | 0 | 0 | 0 | 1.4 | 11.5 | 0 | 0 | 0 | 0 | 94.9909 | 38.312 | 0 | 95.4511 | 41% | 0 | 0 | 10.84% | 0 | 35.6758
2332 | 0 | 0 | 0 | 1.2 | 11.3 | 0 | 0 | 0 | 0 | 109.1217 | 44.2608 | 0 | 112.2243 | 33% | 0 | 0 | 10.84% | 0 | 41.6584
2333 | 0 | 0 | 0 | 0.7 | 10.9 | 0 | 0 | 0 | 0 | 117.2453 | 47.6773 | 0 | 121.4822 | 24% | 0 | 0 | 10.84% | 0 | 45.1788
2334 | 0 | 1 | 1 | 0.8 | 11.1 | 0 | 0 | 0 | 0 | 121.4192 | 49.3997 | 0 | 125.8702 | 14% | 0 | 0 | 10.84% | 0 | 47.0203
2335 | 35 | 65 | 58 | 1.3 | 12 | 0 | 6.1127 | 0 | 0 | 123.265 | 50.1145 | 0 | 127.5257 | 5% | 0 | 0 | 10.84% | 0 | 47.8449
2336 | 208 | 263 | 182 | 1.3 | 15 | 0 | 50.144 | 11.5227 | 0 | 63.4409 | 25.4597 | 0 | 62.5865 | 0% | 0 | 0 | 10.84% | 0 | 34.9014
2337 | 167 | 425 | 333 | 4.5 | 17.7 | 0 | 47.22 | 26.4376 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.84% | 0 | 24.4423
2338 | 228 | 537 | 369 | 6.9 | 18.3 | 0 | 58.6956 | 37.5229 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.84% | 0 | 35.5467
2339 | 795 | 814 | 180 | 5.5 | 19.4 | 214.9298 | 0 | 70.9241 | 0 | 0 | 0 | 206.7694 | 0 | 16% | 24.0325 | 0 | 43.52% | 0 | 44.6175
2340 | 886 | 919 | 157 | 4.2 | 20.4 | 248.9676 | 0 | 72.1863 | 2.9137 | 0 | 0 | 247.0972 | 0 | 35% | 25 | 0 | 77.52% | 0 | 44.5252
2341 | 935 | 1028 | 213 | 4.3 | 21.4 | 264.6253 | 0 | 55.8722 | 19.2278 | 0 | 0 | 263.2697 | 0 | 55% | 9.1749 | 0 | 90% | 0 | 43.8288
2342 | 778 | 875 | 224 | 3.7 | 21.7 | 213.9039 | 0 | 45.5371 | 29.5629 | 0 | 0 | 212.8934 | 0 | 71% | 0 | 0 | 90% | 0 | 43.106
2343 | 630 | 689 | 223 | 6.1 | 21.5 | 162.4867 | 0 | 44.4454 | 11.1923 | 0 | 0 | 161.5886 | 0 | 83% | 0 | 0 | 90% | 0 | 42.4731
2344 | 897 | 623 | 87 | 7.1 | 21.7 | 224.6059 | -1.8e-15 | 45.0952 | 3.5709 | 42.5913 | 0.90556 | 183.3788 | 0 | 97% | 0 | 0 | 90% | 0 | 42.9368
2345 | 736 | 402 | 80 | 8.2 | 21.7 | 84.6121 | 89.6418 | 24.3885 | 0 | 42.5939 | 15.0122 | 43.2258 | 0 | 100% | 0 | 6.4099 | 79.74% | 0 | 45.4556
2346 | 33 | 77 | 67 | 6.6 | 19.8 | 0 | 6.7047 | 0 | 0 | 65.3009 | 24.842 | 0 | 63.9628 | 95% | 0 | 25 | 39.74% | 0 | 47.7763
2347 | 3 | 10 | 10 | 4.2 | 17.7 | 0 | 0.10718 | 0 | 0 | 72.5356 | 28.0466 | 0 | 72.8757 | 90% | 0 | 18.5901 | 10% | 0 | 43.7254
2348 | 0 | 0 | 0 | 3.8 | 17.3 | 0 | 0 | 0 | 0 | 106.5707 | 42.7809 | 0 | 109.602 | 82% | 0 | 0 | 10% | 0 | 40.1189
2349 | 0 | 0 | 0 | 3.4 | 16.3 | 0 | 0 | 0 | 0 | 98.3978 | 39.4326 | 0 | 98.2258 | 74% | 0 | 0 | 10% | 0 | 37.1608
2350 | 0 | 0 | 0 | 4.2 | 15.5 | 0 | 0 | 0 | 0 | 92.4398 | 36.9867 | 0 | 90.918 | 68% | 0 | 0 | 10% | 0 | 34.7758
2351 | 0 | 0 | 0 | 4.4 | 15.5 | 0 | 0 | 0 | 0 | 89.0659 | 35.5575 | 0 | 86.9027 | 61% | 0 | 0 | 10% | 0 | 33.3198
2352 | 0 | 0 | 0 | 4.9 | 15 | 0 | 0 | 0 | 0 | 87.6971 | 35.0126 | 0 | 85.4254 | 55% | 0 | 0 | 10% | 0 | 32.7222
2353 | 0 | 0 | 0 | 5.4 | 14.2 | 0 | 0 | 0 | 0 | 87.2339 | 34.8677 | 0 | 85.0211 | 48% | 0 | 0 | 10% | 0 | 32.5279
2354 | 0 | 0 | 0 | 3.6 | 13.5 | 0 | 0 | 0 | 0 | 89.2138 | 35.7476 | 0 | 87.5249 | 42% | 0 | 0 | 10% | 0 | 33.3639
2355 | 0 | 0 | 0 | 2.5 | 13.4 | 0 | 0 | 0 | 0 | 97.376 | 39.2037 | 0 | 97.4487 | 34% | 0 | 0 | 10% | 0 | 36.7884
2356 | 0 | 0 | 0 | 4.9 | 13.2 | 0 | 0 | 0 | 0 | 109.7581 | 44.4124 | 0 | 112.1185 | 26% | 0 | 0 | 10% | 0 | 42.0088
2357 | 0 | 0 | 0 | 6.3 | 13.1 | 0 | 0 | 0 | 0 | 117.4646 | 47.6357 | 0 | 120.9684 | 17% | 0 | 0 | 10% | 0 | 45.3011
2358 | 15 | 3 | 2 | 4.3 | 12.5 | 0 | 0 | 0 | 0 | 120.7563 | 49.0401 | 0 | 124.4239 | 8% | 0 | 0 | 10% | 0 | 46.7947
2359 | 505 | 110 | 30 | 6.5 | 13.4 | 50.4579 | 13.7909 | 0 | 0 | 120.0575 | 48.6908 | 0 | 74.273 | 2% | 0 | 0 | 10% | 0 | 47.3704
2360 | 790 | 326 | 53 | 6.1 | 14.9 | 158.0276 | 0 | 18.3691 | 0 | 78.8956 | 31.178 | 80.0601 | 0 | 8% | 0 | 0 | 10% | 0 | 47.6471
2361 | 900 | 539 | 64 | 7.9 | 16 | 215.8843 | 0 | 41.1801 | 0 | 43.8458 | 15.866 | 173.4582 | 0 | 21% | 6.8443 | 0 | 19.31% | 0 | 47.8262
2362 | 959 | 723 | 69 | 6.9 | 17 | 252.6154 | 0 | 59.7034 | 1.6979 | 42.6091 | 15.306 | 211.5271 | 0 | 37% | 25 | 0 | 53.31% | 0 | 47.282
2363 | 995 | 861 | 71 | 7.8 | 18 | 271.9179 | 0 | 58.397 | 16.703 | 42.6124 | 15.2525 | 230.8281 | 0 | 54% | 25 | 0 | 87.31% | 0 | 45.7164
2364 | 1011 | 941 | 73 | 7.3 | 18.9 | 282.6075 | 0 | 34.6501 | 40.4499 | 42.6137 | 15.2005 | 241.4523 | 0 | 72% | 1.9793 | 0 | 90% | 0 | 44.805
2365 | 991 | 970 | 108 | 6.8 | 19.6 | 278.4957 | 0 | 31.8355 | 43.2645 | 42.6139 | 15.1576 | 237.1336 | 0 | 90% | 0 | 0 | 90% | 0 | 43.9408
2366 | 830 | 927 | 237 | 6.8 | 20.4 | 175.6223 | 60.015 | 28.4139 | 46.6861 | 42.6133 | 15.1065 | 134.0382 | 0 | 100% | 0 | 0 | 90% | 0 | 44.0646
2367 | 934 | 796 | 110 | 10.1 | 20.3 | 42.1526 | 240.7292 | 27.9213 | 39.8631 | 42.612 | 15.1125 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.7453
2368 | 929 | 630 | 74 | 10.5 | 19.4 | 42.158 | 222.9429 | 28.0828 | 21.4442 | 42.6091 | 15.1683 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.9628
2369 | 835 | 425 | 68 | 8.7 | 18.6 | 42.1581 | 168.4756 | 27.1573 | 0 | 42.6063 | 15.2153 | 0 | 0 | 100% | 0 | 2.6481 | 85.76% | 0 | 45.7326
2370 | 662 | 200 | 43 | 6.8 | 17.7 | 45.3266 | 76.883 | 5.5177 | 0 | 45.7221 | 16.553 | 0 | 0 | 100% | 0 | 25 | 45.76% | 0 | 47.7768
2371 | 135 | 23 | 10 | 5.7 | 15.8 | 0 | 5.4605 | 0 | 0 | 61.9833 | 23.6229 | 0 | 61.3187 | 96% | 0 | 22.3519 | 10% | 0 | 43.9132
2372 | 0 | 0 | 0 | 5 | 14.9 | 0 | 0 | 0 | 0 | 106.5495 | 42.9565 | 0 | 110.1194 | 87% | 0 | 0 | 10% | 0 | 40.1643
2373 | 0 | 0 | 0 | 4.6 | 14.4 | 0 | 0 | 0 | 0 | 98.4033 | 39.5682 | 0 | 97.9902 | 80% | 0 | 0 | 10% | 0 | 37.3644
2374 | 0 | 0 | 0 | 5.6 | 14 | 0 | 0 | 0 | 0 | 93.075 | 37.3552 | 0 | 91.5109 | 73% | 0 | 0 | 10% | 0 | 35.2002
2375 | 0 | 0 | 0 | 4.1 | 13.6 | 0 | 0 | 0 | 0 | 89.5196 | 35.8695 | 0 | 87.3041 | 67% | 0 | 0 | 10% | 0 | 33.677
2376 | 0 | 0 | 0 | 3.5 | 12.7 | 0 | 0 | 0 | 0 | 88.0471 | 35.2994 | 0 | 85.7408 | 60% | 0 | 0 | 10% | 0 | 33.042
2377 | 0 | 0 | 0 | 3.4 | 12.5 | 0 | 0 | 0 | 0 | 88.0315 | 35.3041 | 0 | 85.9001 | 54% | 0 | 0 | 10% | 0 | 32.9883
2378 | 0 | 0 | 0 | 1.5 | 12.1 | 0 | 0 | 0 | 0 | 89.6455 | 36.0102 | 0 | 87.9756 | 47% | 0 | 0 | 10% | 0 | 33.6495
2379 | 0 | 0 | 0 | 1.6 | 11.3 | 0 | 0 | 0 | 0 | 97.695 | 39.4576 | 0 | 97.7521 | 40% | 0 | 0 | 10% | 0 | 37.0643
2380 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | 0 | 0 | 110.1311 | 44.7486 | 0 | 112.4668 | 31% | 0 | 0 | 10% | 0 | 42.3694
2381 | 0 | 0 | 0 | 2 | 9.8 | 0 | 0 | 0 | 0 | 117.7731 | 47.9514 | 0 | 121.2041 | 22% | 0 | 0 | 10% | 0 | 45.6469
2382 | 16 | 3 | 2 | 5.4 | 11 | 0 | 0 | 0 | 0 | 120.914 | 49.1953 | 0 | 124.452 | 13% | 0 | 0 | 10% | 0 | 46.9848
2383 | 534 | 116 | 27 | 8.2 | 12.4 | 53.4485 | 14.9397 | 0 | 0 | 119.9238 | 48.7011 | 0 | 71.0091 | 7% | 0 | 0 | 10% | 0 | 47.3631
2384 | 820 | 334 | 46 | 7.2 | 13.9 | 164.6811 | 0 | 18.7315 | 0 | 77.2406 | 30.4882 | 88.4727 | 0 | 14% | 0 | 0 | 10% | 0 | 47.2558
2385 | 927 | 550 | 55 | 7.9 | 15.3 | 223.4845 | 2.98e-14 | 41.8208 | 0 | 43.9575 | 15.9468 | 180.8793 | 0 | 28% | 8.129 | 0 | 21.05% | 0 | 47.1811
2386 | 970 | 729 | 63 | 7.8 | 16.6 | 255.1157 | 0 | 59.2498 | 2.3913 | 42.5974 | 15.3223 | 214.0205 | 0 | 44% | 25 | 0 | 55.05% | 0 | 46.8053
2387 | 994 | 931 | 135 | 6.4 | 17.9 | 273.0042 | 0 | 57.8274 | 17.2726 | 42.6046 | 15.2552 | 231.8871 | 0 | 61% | 25 | 0 | 89.05% | 0 | 45.1224
2388 | 935 | 994 | 184 | 5.5 | 19.2 | 262.7662 | 0 | 32.8785 | 42.2215 | 42.608 | 15.1802 | 221.5722 | 0 | 78% | 0.6945 | 0 | 90% | 0 | 44.4712
2389 | 993 | 1029 | 160 | 5.9 | 20.4 | 279.934 | 0 | 31.8199 | 43.2801 | 42.609 | 15.1049 | 238.3844 | 0 | 96% | 0 | 0 | 90% | 0 | 43.8513
2390 | 664 | 879 | 317 | 5.7 | 19.3 | 100.4352 | 92.8587 | 27.6457 | 47.2643 | 42.6093 | 15.1745 | 58.8427 | 0 | 100% | 0 | 0 | 90% | 0 | 43.4316
2391 | 173 | 348 | 217 | 3.8 | 18.1 | 0 | 53.7379 | 22.5645 | 0 | 42.6067 | 15.2447 | 0 | 41.1153 | 97% | 0 | 6.9606 | 78.86% | 0 | 42.7182
2392 | 797 | 578 | 104 | 5.7 | 18.8 | 84.9483 | 131.352 | 36.3665 | 8.2239 | 43.2059 | 15.4512 | 49.0866 | 8.0871 | 100% | 8.1889 | 0 | 90% | 0 | 43.1888
2393 | 637 | 337 | 69 | 6.2 | 17.8 | 42.1581 | 115.7054 | 19.9262 | 0 | 42.6021 | 15.2598 | 0 | 0 | 100% | 0 | 9.2362 | 75.22% | 0 | 45.1342
2394 | 671 | 202 | 42 | 4.5 | 17.1 | 43.3924 | 82.9774 | 5.5082 | 0 | 43.8156 | 15.7965 | 0 | 0 | 100% | 0 | 25 | 35.22% | 0 | 47.016
2395 | 66 | 19 | 13 | 3.1 | 15.4 | 0 | 2.9823 | 0 | 0 | 75.9613 | 29.6548 | 0 | 77.301 | 94% | 0 | 15.7638 | 10% | 0 | 43.3513
2396 | 0 | 0 | 0 | 3.5 | 14.4 | 0 | 0 | 0 | 0 | 105.6709 | 42.6274 | 0 | 107.6491 | 86% | 0 | 0 | 10% | 0 | 40.1883
2397 | 0 | 0 | 0 | 6.1 | 12.8 | 0 | 0 | 0 | 0 | 98.211 | 39.5895 | 0 | 97.3533 | 79% | 0 | 0 | 10% | 0 | 37.4964
2398 | 0 | 0 | 0 | 3.3 | 9.5 | 0 | 0 | 0 | 0 | 91.8867 | 37.0875 | 0 | 89.8268 | 72% | 0 | 0 | 10% | 0 | 34.9994
2399 | 0 | 0 | 0 | 2 | 10.5 | 0 | 0 | 0 | 0 | 88.9992 | 35.8159 | 0 | 86.5695 | 66% | 0 | 0 | 10% | 0 | 33.6567
2400 | 0 | 0 | 0 | 2.3 | 10.4 | 0 | 0 | 0 | 0 | 87.504 | 35.1873 | 0 | 85.0211 | 59% | 0 | 0 | 10% | 0 | 32.9523
2401 | 0 | 0 | 0 | 3.6 | 10.8 | 0 | 0 | 0 | 0 | 87.2794 | 35.0742 | 0 | 84.9546 | 53% | 0 | 0 | 10% | 0 | 32.7734
2402 | 0 | 0 | 0 | 1.8 | 10.4 | 0 | 0 | 0 | 0 | 89.4036 | 35.9928 | 0 | 87.6595 | 46% | 0 | 0 | 10% | 0 | 33.6392
2403 | 0 | 0 | 0 | 2 | 9.9 | 0 | 0 | 0 | 0 | 97.4468 | 39.422 | 0 | 97.442 | 39% | 0 | 0 | 10% | 0 | 37.0332
2404 | 0 | 0 | 0 | 1.1 | 9.1 | 0 | 0 | 0 | 0 | 109.602 | 44.5678 | 0 | 111.8309 | 31% | 0 | 0 | 10% | 0 | 42.1911
2405 | 0 | 0 | 0 | 1.1 | 7.9 | 0 | 0 | 0 | 0 | 116.7812 | 47.6201 | 0 | 120.0364 | 22% | 0 | 0 | 10% | 0 | 45.315
2406 | 31 | 4 | 2 | 0.7 | 7.6 | 0 | 0 | 0 | 0 | 119.8118 | 48.891 | 0 | 123.1566 | 12% | 0 | 0 | 10% | 0 | 46.6751
2407 | 558 | 119 | 27 | 0.8 | 10.4 | 61.8791 | 16.0098 | 0.098791 | 0 | 118.4737 | 48.2136 | 0 | 61.1865 | 8% | 0 | 0 | 10% | 0 | 46.8995
2408 | 821 | 336 | 43 | 1 | 13.7 | 170.4671 | 0 | 18.5552 | 0 | 76.7577 | 30.2817 | 94.9448 | 0 | 15% | 0 | 0 | 10% | 0 | 46.8204
2409 | 927 | 550 | 51 | 1 | 16.2 | 229.3988 | 0 | 41.3321 | 0 | 44.3082 | 16.0477 | 186.4524 | 0 | 29% | 8.2256 | 0 | 21.19% | 0 | 46.6426
2410 | 980 | 735 | 59 | 1.5 | 17.2 | 263.2183 | 0 | 58.814 | 2.9937 | 42.5981 | 15.2912 | 222.0939 | 0 | 46% | 25 | 0 | 55.19% | 0 | 46.2632
2411 | 895 | 881 | 162 | 1.8 | 18.4 | 247.979 | 0 | 57.3466 | 17.7534 | 42.6052 | 15.2266 | 206.9825 | 0 | 61% | 25 | 0 | 89.19% | 0 | 44.8429
2412 | 893 | 977 | 201 | 3.7 | 19.2 | 251.8573 | 0 | 32.4332 | 42.6668 | 42.6076 | 15.1801 | 210.6354 | 0 | 77% | 0.59795 | 0 | 90% | 0 | 44.2275
2413 | 998 | 1015 | 140 | 4.7 | 19.4 | 282.4511 | 5.96e-14 | 31.6463 | 43.4537 | 42.6085 | 15.1681 | 240.8256 | 0 | 95% | 0 | 0 | 90% | 0 | 43.7207
2414 | 939 | 950 | 163 | 4.2 | 20 | 111.5502 | 172.3702 | 27.9758 | 47.1242 | 42.6092 | 15.1312 | 69.9704 | 0 | 100% | 0 | 0 | 90% | 0 | 43.3827
2415 | 534 | 618 | 221 | 3.8 | 19.9 | 42.1525 | 114.7374 | 26.8809 | 22.3575 | 42.6073 | 15.1367 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.7292
2416 | 848 | 712 | 197 | 4.5 | 20.5 | 42.1579 | 199.9892 | 26.9882 | 28.1628 | 42.6046 | 15.0968 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.7965
2417 | 707 | 404 | 106 | 4.3 | 20.1 | 42.158 | 135.6217 | 25.3248 | 0 | 42.6019 | 15.1221 | 0 | 0 | 100% | 0 | 3.3914 | 84.57% | 0 | 44.5498
2418 | 688 | 217 | 51 | 4.2 | 19.1 | 42.158 | 89.0028 | 6.1937 | 0 | 42.5994 | 15.1834 | 0 | 0 | 100% | 0 | 24.5573 | 45.28% | 0 | 46.6461
2419 | 160 | 26 | 10 | 3.9 | 17.1 | 0 | 7.9902 | 0 | 0 | 61.5969 | 23.3873 | 0 | 60.9906 | 96% | 0 | 22.0513 | 10% | 0 | 43.3749
2420 | 0 | 0 | 0 | 2.3 | 15.5 | 0 | 0 | 0 | 0 | 106.6657 | 42.9596 | 0 | 110.2068 | 87% | 0 | 0 | 10% | 0 | 40.1806
2421 | 0 | 0 | 0 | 1.8 | 14 | 0 | 0 | 0 | 0 | 98.7987 | 39.7615 | 0 | 98.427 | 80% | 0 | 0 | 10% | 0 | 37.5661
2422 | 0 | 0 | 0 | 0.7 | 12.9 | 0 | 0 | 0 | 0 | 92.7078 | 37.2658 | 0 | 91.0224 | 73% | 0 | 0 | 10% | 0 | 35.1225
2423 | 0 | 0 | 0 | 1 | 11.9 | 0 | 0 | 0 | 0 | 88.7388 | 35.6361 | 0 | 86.3577 | 67% | 0 | 0 | 10% | 0 | 33.4474
2424 | 0 | 0 | 0 | 0.8 | 11.5 | 0 | 0 | 0 | 0 | 87.5172 | 35.1399 | 0 | 85.1286 | 60% | 0 | 0 | 10% | 0 | 32.8772
2425 | 0 | 0 | 0 | 0.8 | 10.9 | 0 | 0 | 0 | 0 | 87.3076 | 35.0815 | 0 | 85.0662 | 54% | 0 | 0 | 10% | 0 | 32.757
2426 | 0 | 0 | 0 | 0.9 | 10 | 0 | 0 | 0 | 0 | 88.9919 | 35.8367 | 0 | 87.23 | 47% | 0 | 0 | 10% | 0 | 33.4631
2427 | 0 | 0 | 0 | 1.6 | 9.2 | 0 | 0 | 0 | 0 | 96.7986 | 39.1795 | 0 | 96.7529 | 40% | 0 | 0 | 10% | 0 | 36.771
2428 | 0 | 0 | 0 | 1.5 | 9 | 0 | 0 | 0 | 0 | 108.3233 | 44.0383 | 0 | 110.4056 | 32% | 0 | 0 | 10% | 0 | 41.6431
2429 | 0 | 0 | 0 | 1.2 | 7.9 | 0 | 0 | 0 | 0 | 114.786 | 46.785 | 0 | 117.7407 | 23% | 0 | 0 | 10% | 0 | 44.4611
2430 | 29 | 4 | 3 | 1.1 | 7.8 | 0 | 0 | 0 | 0 | 118.0713 | 48.16 | 0 | 121.2242 | 14% | 0 | 0 | 10% | 0 | 45.9204
2431 | 523 | 122 | 32 | 0.9 | 11 | 57.7278 | 14.9615 | 0.20186 | 0 | 116.8949 | 47.5276 | 0 | 63.4741 | 9% | 0 | 0 | 10% | 0 | 46.3518
2432 | 792 | 338 | 52 | 1 | 14 | 164.5445 | 0 | 18.5319 | 0 | 75.6235 | 29.7559 | 89.9825 | 0 | 16% | 0 | 0 | 10% | 0 | 46.3275
2433 | 905 | 553 | 62 | 2.5 | 17.1 | 223.2032 | 0 | 41.1744 | 0 | 44.3252 | 16.0083 | 180.1533 | 0 | 29% | 8.7005 | 0 | 21.83% | 0 | 46.0274
2434 | 965 | 737 | 67 | 5.2 | 19.1 | 256.551 | 0 | 58.011 | 3.1747 | 42.5939 | 15.1814 | 215.3596 | 0 | 46% | 25 | 0 | 55.83% | 0 | 45.4136
2435 | 989 | 868 | 73 | 5.7 | 19.9 | 272.4639 | 0 | 56.7576 | 18.3424 | 42.6022 | 15.1349 | 231.273 | 0 | 63% | 25 | 0 | 89.83% | 0 | 43.9381
2436 | 989 | 942 | 83 | 5 | 20 | 278.8306 | 0 | 30.9124 | 44.1876 | 42.6061 | 15.1301 | 237.559 | 0 | 81% | 0.12303 | 0 | 90% | 0 | 42.8765
2437 | 988 | 955 | 87 | 5.3 | 20.4 | 279.0995 | 0 | 27.6708 | 47.4292 | 42.6078 | 15.1045 | 237.5149 | 0 | 98% | 0 | 0 | 90% | 0 | 42.2203
2438 | 969 | 904 | 92 | 6.9 | 20.3 | 63.6451 | 236.2949 | 25.8463 | 49.2537 | 42.6085 | 15.1113 | 22.2255 | 0 | 100% | 0 | 0 | 90% | 0 | 41.5069
2439 | 931 | 781 | 88 | 6.6 | 20 | 42.1524 | 240.2902 | 24.9496 | 40.2329 | 42.6061 | 15.1301 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.7912
2440 | 892 | 617 | 76 | 6 | 19.7 | 42.158 | 212.8798 | 24.7381 | 22.3881 | 42.6034 | 15.1477 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.5974
2441 | 806 | 414 | 63 | 5.5 | 19.3 | 44.4479 | 159.5999 | 25.2404 | 0 | 44.8555 | 16.0983 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.0474
2442 | 633 | 199 | 44 | 5.1 | 18.1 | 42.1086 | 77.0414 | 5.0182 | 0 | 42.5982 | 15.2416 | 0 | 0 | 100% | 0 | 23.2617 | 52.78% | 0 | 44.2335
2443 | 147 | 26 | 11 | 4.8 | 16 | 0 | 8.0414 | 0 | 0 | 50.0495 | 18.4804 | 0 | 48.5159 | 96% | 0 | 25 | 12.78% | 0 | 41.4234
2444 | 0 | 0 | 0 | 3.7 | 14.6 | 0 | 0 | 0 | 0 | 103.7928 | 41.8224 | 0 | 107.4724 | 89% | 0 | 0 | 12.78% | 0 | 38.8524
2445 | 0 | 0 | 0 | 3.2 | 13.8 | 0 | 0 | 0 | 0 | 97.2218 | 39.1122 | 0 | 96.9767 | 81% | 0 | 0 | 12.78% | 0 | 36.8072
2446 | 0 | 0 | 0 | 0.8 | 12.3 | 0 | 0 | 0 | 0 | 91.5528 | 36.8082 | 0 | 89.9113 | 75% | 0 | 0 | 12.78% | 0 | 34.5778
2447 | 0 | 0 | 0 | 1.2 | 11.8 | 0 | 0 | 0 | 0 | 87.3452 | 35.0517 | 0 | 84.9587 | 68% | 0 | 0 | 12.78% | 0 | 32.7828
2448 | 0 | 0 | 0 | 1.3 | 11.6 | 0 | 0 | 0 | 0 | 85.0477 | 34.0925 | 0 | 82.4579 | 62% | 0 | 0 | 12.78% | 0 | 31.7523
2449 | 0 | 0 | 0 | 0.7 | 10.1 | 0 | 0 | 0 | 0 | 83.8376 | 33.6534 | 0 | 81.239 | 56% | 0 | 0 | 12.78% | 0 | 31.2448
2450 | 0 | 0 | 0 | 1.6 | 9.6 | 0 | 0 | 0 | 0 | 83.5185 | 33.5401 | 0 | 81.0352 | 50% | 0 | 0 | 12.78% | 0 | 31.0727
2451 | 0 | 0 | 0 | 1.7 | 9.9 | 0 | 0 | 0 | 0 | 85.6334 | 34.4197 | 0 | 83.6687 | 44% | 0 | 0 | 12.78% | 0 | 31.9029
2452 | 0 | 0 | 0 | 2.2 | 9.9 | 0 | 0 | 0 | 0 | 88.8422 | 35.778 | 0 | 87.5968 | 37% | 0 | 0 | 12.78% | 0 | 33.2325
2453 | 0 | 0 | 0 | 1.1 | 9.2 | 0 | 0 | 0 | 0 | 93.7821 | 37.9114 | 0 | 93.6955 | 30% | 0 | 0 | 12.78% | 0 | 35.3573
2454 | 34 | 5 | 3 | 0.8 | 8.1 | 0 | 0 | 0 | 0 | 101.1867 | 41.0725 | 0 | 102.4181 | 22% | 0 | 0 | 12.78% | 0 | 38.5355
2455 | 529 | 126 | 33 | 0.6 | 11.3 | 59.3587 | 15.2949 | 0.30426 | 0 | 102.6873 | 41.5645 | 0 | 46.436 | 19% | 0 | 0 | 12.78% | 0 | 40.447
2456 | 788 | 342 | 54 | 0.7 | 16.3 | 164.671 | 0 | 18.4829 | 0 | 62.7638 | 23.9484 | 102.0374 | 0 | 27% | 0 | 0 | 12.78% | 0 | 40.501
2457 | 900 | 557 | 65 | 1.3 | 18.9 | 223.0837 | 0 | 40.9821 | 0 | 44.8935 | 16.1414 | 178.8309 | 0 | 40% | 14.4986 | 0 | 32.5% | 0 | 40.1806
2458 | 967 | 742 | 67 | 2.1 | 20.4 | 259.7968 | 0 | 52.5752 | 8.4783 | 42.5778 | 15.0939 | 217.9653 | 0 | 56% | 25 | 0 | 66.5% | 0 | 39.8722
2459 | 996 | 876 | 69 | 3.1 | 21.6 | 276.9349 | 0 | 44.0336 | 31.0664 | 42.5909 | 15.018 | 235.1261 | 0 | 74% | 17.2799 | 0 | 90% | 0 | 38.7817
2460 | 1001 | 949 | 74 | 3.9 | 22.4 | 283.4394 | 5.96e-14 | 25.0759 | 50.0241 | 42.5957 | 14.9625 | 241.5529 | 0 | 91% | 0 | 0 | 90% | 0 | 36.9646
2461 | 992 | 956 | 80 | 5.7 | 22.7 | 159.0865 | 139.0337 | 20.2915 | 54.8085 | 42.5998 | 14.9417 | 117.2918 | 0 | 100% | 0 | 0 | 90% | 0 | 36.041
2462 | 974 | 901 | 82 | 6.3 | 22.5 | 42.1522 | 262.7845 | 19.7235 | 55.3765 | 42.5991 | 14.9563 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.3907
2463 | 942 | 786 | 81 | 5.8 | 22.4 | 42.1578 | 243.8533 | 19.4997 | 45.1881 | 42.5966 | 14.9628 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.1735
2464 | 905 | 624 | 71 | 5.8 | 22.4 | 42.1578 | 216.8661 | 19.7111 | 27.1474 | 42.5942 | 14.962 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.384
2465 | 824 | 422 | 61 | 5.5 | 21.7 | 42.1578 | 167.3889 | 21.1904 | 4.2138 | 42.5918 | 15.0115 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.913
2466 | 644 | 202 | 41 | 5.3 | 20.3 | 42.1579 | 79.9106 | 4.8501 | 0 | 42.5896 | 15.1046 | 0 | 0 | 100% | 0 | 19.5928 | 58.65% | 0 | 40.259
2467 | 154 | 27 | 12 | 4.9 | 18.3 | 0 | 9.1594 | 0 | 0 | 44.3974 | 15.9722 | 0 | 42.8878 | 97% | 0 | 24.5605 | 19.36% | 0 | 38.4784
2468 | 0 | 0 | 0 | 3.4 | 16.6 | 0 | 0 | 0 | 0 | 84.3038 | 33.3317 | 0 | 85.6189 | 91% | 0 | 5.8467 | 10% | 0 | 36.2393
2469 | 0 | 0 | 0 | 1.2 | 14.8 | 0 | 0 | 0 | 0 | 91.0661 | 36.45 | 0 | 90.3278 | 84% | 0 | 0 | 10% | 0 | 33.9275
2470 | 0 | 0 | 0 | 1.5 | 13.3 | 0 | 0 | 0 | 0 | 85.3341 | 34.1204 | 0 | 83.2086 | 78% | 0 | 0 | 10% | 0 | 31.6568
2471 | 0 | 0 | 0 | 1.4 | 12.9 | 0 | 0 | 0 | 0 | 81.8051 | 32.6131 | 0 | 79.4388 | 72% | 0 | 0 | 10% | 0 | 30.0886
2472 | 0 | 0 | 0 | 1.4 | 12.6 | 0 | 0 | 0 | 0 | 80.1202 | 31.8605 | 0 | 77.912 | 66% | 0 | 0 | 10% | 0 | 29.2736
2473 | 0 | 0 | 0 | 2.3 | 13.8 | 0 | 0 | 0 | 0 | 79.0799 | 31.3212 | 0 | 76.9754 | 60% | 0 | 0 | 10% | 0 | 28.6921
2474 | 0 | 0 | 0 | 1.4 | 12.4 | 0 | 0 | 0 | 0 | 78.7884 | 31.2672 | 0 | 76.7622 | 55% | 0 | 0 | 10% | 0 | 28.6064
2475 | 0 | 0 | 0 | 0.9 | 11.4 | 0 | 0 | 0 | 0 | 79.9982 | 31.8686 | 0 | 78.0496 | 49% | 0 | 0 | 10% | 0 | 29.1822
2476 | 0 | 0 | 0 | 0.4 | 11.7 | 0 | 0 | 0 | 0 | 80.7371 | 32.1914 | 0 | 78.845 | 43% | 0 | 0 | 10% | 0 | 29.4856
2477 | 0 | 0 | 0 | 1.6 | 11.1 | 0 | 0 | 0 | 0 | 82.725 | 33.1324 | 0 | 80.9024 | 37% | 0 | 0 | 10% | 0 | 30.4094
2478 | 37 | 6 | 4 | 2.4 | 12.3 | 0 | 0 | 0 | 0 | 90.0858 | 36.1878 | 0 | 89.7719 | 30% | 0 | 0 | 10% | 0 | 33.4424
2479 | 493 | 132 | 44 | 1.2 | 14.5 | 54.9859 | 14.0522 | 0.63513 | 0 | 90.5733 | 36.2643 | 0 | 36.9408 | 28% | 0 | 0 | 10% | 0 | 35.4996
2480 | 709 | 331 | 65 | 0.8 | 17.9 | 147.2152 | 0 | 17.0757 | 0 | 55.937 | 20.9329 | 90.9144 | 0 | 34% | 0 | 0 | 10% | 0 | 36.2505
2481 | 877 | 550 | 66 | 2.1 | 20.6 | 217.07 | 0 | 39.6911 | 0 | 45.301 | 16.2019 | 171.7965 | 0 | 47% | 17.4134 | 0 | 33.68% | 0 | 36.0991
2482 | 935 | 730 | 72 | 3.2 | 22.3 | 250.472 | 0 | 48.9284 | 10.0437 | 42.5652 | 14.9592 | 208.182 | 0 | 62% | 25 | 0 | 67.68% | 0 | 36.1867
2483 | 965 | 862 | 75 | 3.6 | 23.7 | 268.0743 | 0 | 40.2366 | 32.6127 | 42.5802 | 14.8586 | 225.8058 | 0 | 79% | 16.4101 | 0 | 90% | 0 | 35.7908
2484 | 975 | 935 | 79 | 4.5 | 24.7 | 275.6804 | 0 | 18.5393 | 56.5607 | 42.5862 | 14.7817 | 233.3385 | 0 | 96% | 0 | 0 | 90% | 0 | 34.4013
2485 | 973 | 946 | 81 | 4.1 | 25.2 | 96.9897 | 204.8218 | 18.1434 | 56.9566 | 42.5918 | 14.7433 | 55.4255 | 0 | 100% | 0 | 0 | 90% | 0 | 33.3644
2486 | 963 | 892 | 78 | 5.5 | 25.6 | 42.1519 | 259.4199 | 17.4763 | 57.6237 | 42.5903 | 14.7099 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.8965
2487 | 940 | 780 | 74 | 5.6 | 25.6 | 42.1575 | 243.2388 | 17.4812 | 45.6039 | 42.5881 | 14.7092 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.9006
2488 | 892 | 616 | 68 | 5.5 | 25.8 | 42.1575 | 213.0998 | 18.064 | 27.1321 | 42.5859 | 14.692 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.4662
2489 | 805 | 414 | 58 | 5.9 | 24.7 | 42.1576 | 162.3553 | 19.9187 | 4.1802 | 42.5838 | 14.7809 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.4101
2490 | 606 | 198 | 45 | 5.1 | 23.4 | 42.1577 | 72.0448 | 4.5326 | 0 | 42.5818 | 14.8823 | 0 | 0 | 100% | 0 | 18.8632 | 59.82% | 0 | 38.9888
2491 | 67 | 22 | 14 | 3.1 | 20.9 | 0 | 4.3052 | 0 | 0 | 43.6826 | 15.5135 | 0 | 42.1794 | 97% | 0 | 24.4208 | 20.75% | 0 | 37.8756
2492 | 0 | 0 | 0 | 2.6 | 18.3 | 0 | 0 | 0 | 0 | 81.6164 | 32.0621 | 0 | 82.673 | 91% | 0 | 6.7159 | 10% | 0 | 35.8435
2493 | 0 | 0 | 0 | 0.9 | 16.9 | 0 | 0 | 0 | 0 | 90.6854 | 36.1481 | 0 | 89.9514 | 84% | 0 | 0 | 10% | 0 | 33.5999
2494 | 0 | 0 | 0 | 0.4 | 16.6 | 0 | 0 | 0 | 0 | 85.6312 | 34.0392 | 0 | 83.6353 | 78% | 0 | 0 | 10% | 0 | 31.5532
2495 | 0 | 0 | 0 | 0.9 | 16.3 | 0 | 0 | 0 | 0 | 82.2507 | 32.613 | 0 | 79.9256 | 72% | 0 | 0 | 10% | 0 | 30.0766
2496 | 0 | 0 | 0 | 0.8 | 15.4 | 0 | 0 | 0 | 0 | 81.6077 | 32.376 | 0 | 79.4456 | 66% | 0 | 0 | 10% | 0 | 29.7791
2497 | 0 | 0 | 0 | 1.1 | 15.9 | 0 | 0 | 0 | 0 | 81.341 | 32.2241 | 0 | 79.2858 | 60% | 0 | 0 | 10% | 0 | 29.5866
2498 | 0 | 0 | 0 | 1.1 | 15.5 | 0 | 0 | 0 | 0 | 83.1424 | 33.0671 | 0 | 81.2194 | 54% | 0 | 0 | 10% | 0 | 30.3984
2499 | 0 | 0 | 0 | 0.3 | 13.8 | 0 | 0 | 0 | 0 | 92.1766 | 36.9875 | 0 | 92.2417 | 47% | 0 | 0 | 10% | 0 | 34.2866
2500 | 0 | 0 | 0 | 1.7 | 14.5 | 0 | 0 | 0 | 0 | 101.3839 | 40.8167 | 0 | 103.1953 | 40% | 0 | 0 | 10% | 0 | 38.1532
2501 | 0 | 0 | 0 | 1.8 | 14.6 | 0 | 0 | 0 | 0 | 107.6938 | 43.456 | 0 | 110.4361 | 31% | 0 | 0 | 10% | 0 | 40.877
2502 | 3 | 5 | 5 | 1.5 | 13.8 | 0 | 0 | 0 | 0 | 112.4089 | 45.4782 | 0 | 115.6043 | 23% | 0 | 0 | 10% | 0 | 42.9959
2503 | 158 | 83 | 53 | 2.2 | 16.3 | 0 | 29.2077 | 0 | 0 | 115.274 | 46.483 | 0 | 118.5919 | 14% | 0 | 0 | 10% | 0 | 44.096
2504 | 452 | 345 | 177 | 1.3 | 20.5 | 71.6459 | 17.8368 | 17.7784 | 0 | 72.8388 | 28.1152 | 12.8406 | 13.0554 | 14% | 0 | 0 | 10% | 0 | 44.4567
2505 | 390 | 459 | 233 | 1.2 | 23.7 | 87.4771 | -1.49e-14 | 28.9563 | 0 | 47.9026 | 17.0588 | 41.1067 | 0 | 17% | 0 | 0 | 10% | 0 | 44.781
2506 | 402 | 637 | 341 | 2.6 | 25.2 | 97.683 | 0 | 46.107 | 0 | 43.3969 | 15.0729 | 55.4959 | 0 | 21% | 15.2096 | 0 | 30.69% | 0 | 44.6532
2507 | 560 | 793 | 331 | 3.4 | 26.3 | 148.0675 | 0 | 55.2428 | 8.134 | 42.5479 | 14.6371 | 106.1424 | 0 | 29% | 25 | 0 | 64.69% | 0 | 43.1171
2508 | 70 | 588 | 514 | 4.4 | 26.5 | 0 | 22.6511 | 39.7369 | 0 | 44.5108 | 15.4192 | 0 | 42.1365 | 26% | 11.5594 | 0 | 80.41% | 0 | 42.0679
2509 | 88 | 517 | 429 | 4.2 | 25.6 | 0 | 28.5487 | 33.8802 | 0 | 46.149 | 16.1657 | 0 | 43.7604 | 23% | 6.1443 | 0 | 88.76% | 0 | 41.4326
2510 | 171 | 519 | 363 | 3.5 | 26.6 | 0 | 54.6649 | 29.7272 | 5.4952 | 42.9938 | 14.794 | 0 | 40.7365 | 20% | 0.91026 | 0 | 90% | 0 | 41.1173
2511 | 212 | 526 | 366 | 5.3 | 27.5 | 0 | 55.051 | 28.3204 | 7.4855 | 42.5253 | 14.5269 | 0 | 40.3127 | 17% | 0 | 0 | 90% | 0 | 40.3323
2512 | 515 | 568 | 245 | 5.2 | 27.9 | 121.8885 | 0 | 27.4317 | 11.4811 | 42.5113 | 14.4875 | 77.8206 | 0 | 22% | 0 | 0 | 90% | 0 | 40.4175
2513 | 397 | 373 | 191 | 3.6 | 25.8 | 79.8171 | 0 | 19.8016 | 0 | 42.5386 | 14.6757 | 38.5312 | 0 | 25% | 0 | 8.6266 | 76.2% | 0 | 41.9488
2514 | 211 | 166 | 109 | 3.2 | 23.4 | 0 | 44.0513 | 3.4205 | 0 | 49.0279 | 17.5626 | 0 | 46.8821 | 22% | 0 | 25 | 36.2% | 0 | 44.2496
2515 | 24 | 22 | 20 | 2.5 | 20.4 | 0 | 1.657 | 0 | 0 | 71.2075 | 27.2968 | 0 | 71.1144 | 17% | 0 | 16.3734 | 10% | 0 | 40.9687
2516 | 0 | 0 | 0 | 1.3 | 17.8 | 0 | 0 | 0 | 0 | 101.5287 | 40.6354 | 0 | 103.4849 | 9% | 0 | 0 | 10% | 0 | 37.9206
2517 | 0 | 0 | 0 | 2.2 | 15.5 | 0 | 0 | 0 | 0 | 95.7079 | 38.3681 | 0 | 96.2275 | 2% | 0 | 0 | 10% | 0 | 35.7293
2518 | 0 | 0 | 0 | 2 | 14.1 | 0 | 0 | 0 | 0 | 23.2615 | 9.3213 | 0 | 23.0754 | 0% | 0 | 0 | 10% | 0 | 6.8141
2519 | 0 | 0 | 0 | 1.7 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4571
2520 | 0 | 0 | 0 | 1.5 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4317
2521 | 0 | 0 | 0 | 2.2 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4068
2522 | 0 | 0 | 0 | 1.2 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3822
2523 | 0 | 0 | 0 | 1.8 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3582
2524 | 0 | 0 | 0 | 2.1 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3347
2525 | 0 | 0 | 0 | 2.4 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3117
2526 | 13 | 4 | 4 | 1.4 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2891
2527 | 520 | 136 | 36 | 2.3 | 14.7 | 59.1547 | 15.2448 | 0.46283 | 0 | 0 | 0 | 56.2432 | 0 | 4% | 0 | 0 | 10% | 0 | -0.80536
2528 | 785 | 353 | 57 | 1 | 17.6 | 165.966 | 0 | 18.669 | 0 | 0 | 0 | 161.6304 | 0 | 17% | 0 | 0 | 10% | 0 | 16.8068
2529 | 889 | 563 | 67 | 1.7 | 19.9 | 221.1348 | 0 | 40.5045 | 0 | 0 | 0 | 218.553 | 0 | 33% | 0 | 0 | 10% | 0 | 38.1199
2530 | 926 | 737 | 80 | 1.7 | 21.5 | 248.6557 | 0 | 59.2192 | 0 | 42.4949 | 0 | 206.7603 | 0 | 49% | 17.111 | 0 | 33.27% | 0 | 38.9083
2531 | 941 | 867 | 94 | 2.9 | 22.3 | 261.334 | 0 | 70.7032 | 2.228 | 0 | 0 | 259.7119 | 0 | 68% | 25 | 0 | 67.27% | 0 | 42.8798
2532 | 937 | 949 | 121 | 3.9 | 22.8 | 265.0098 | 0 | 51.2131 | 23.8869 | 42.5613 | 10.2848 | 223.3598 | 0 | 85% | 16.7125 | 0 | 90% | 0 | 41.7027
2533 | 583 | 762 | 235 | 3.7 | 22.9 | 158.6173 | 0 | 28.0388 | 34.1088 | 42.5688 | 14.916 | 117.3552 | 0 | 93% | 0 | 0 | 90% | 0 | 41.0269
2534 | 917 | 892 | 114 | 5.2 | 23.2 | 132.9973 | 140.0891 | 25.3185 | 49.7482 | 42.5739 | 14.895 | 90.9626 | 0 | 100% | 0 | 0 | 90% | 0 | 40.6131
2535 | 912 | 784 | 98 | 6.4 | 22.7 | 42.1523 | 234.2216 | 24.2775 | 39.3482 | 42.5741 | 14.9327 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.9211
2536 | 669 | 588 | 165 | 6.4 | 22.3 | 42.1578 | 145.9453 | 24.1823 | 17.4171 | 42.5723 | 14.9617 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.855
2537 | 456 | 349 | 162 | 6.7 | 20.9 | 42.1579 | 65.2827 | 20.1103 | 0 | 42.5706 | 15.0586 | 0 | 0 | 100% | 0 | 5.3555 | 81.43% | 0 | 41.2358
2538 | 621 | 211 | 54 | 6 | 20 | 42.158 | 76.0067 | 5.1713 | 0 | 42.569 | 15.1169 | 0 | 0 | 100% | 0 | 22.4061 | 45.58% | 0 | 43.4059
2539 | 143 | 28 | 14 | 5.6 | 17.6 | 0 | 10.5574 | 0 | 0 | 54.565 | 20.3513 | 0 | 53.7312 | 96% | 0 | 22.2384 | 10% | 0 | 40.5307
2540 | 0 | 0 | 0 | 5.5 | 14.5 | 0 | 0 | 0 | 0 | 101.1105 | 40.7004 | 0 | 103.5618 | 88% | 0 | 0 | 10% | 0 | 37.8902
2541 | 0 | 0 | 0 | 3.6 | 13.3 | 0 | 0 | 0 | 0 | 94.879 | 38.1627 | 0 | 94.2911 | 81% | 0 | 0 | 10% | 0 | 35.8444
2542 | 0 | 0 | 0 | 3.4 | 12.2 | 0 | 0 | 0 | 0 | 89.3073 | 35.8619 | 0 | 87.3376 | 75% | 0 | 0 | 10% | 0 | 33.5911
2543 | 0 | 0 | 0 | 3.5 | 12.1 | 0 | 0 | 0 | 0 | 86.2684 | 34.5825 | 0 | 83.8855 | 69% | 0 | 0 | 10% | 0 | 32.2531
2544 | 0 | 0 | 0 | 3.1 | 11.7 | 0 | 0 | 0 | 0 | 85.1318 | 34.1241 | 0 | 82.7503 | 62% | 0 | 0 | 10% | 0 | 31.7251
2545 | 0 | 0 | 0 | 3.3 | 11.2 | 0 | 0 | 0 | 0 | 84.4623 | 33.8674 | 0 | 82.1283 | 56% | 0 | 0 | 10% | 0 | 31.4113
2546 | 0 | 0 | 0 | 2.7 | 10.9 | 0 | 0 | 0 | 0 | 86.015 | 34.5369 | 0 | 84.106 | 50% | 0 | 0 | 10% | 0 | 32.0322
2547 | 0 | 0 | 0 | 2.6 | 11.3 | 0 | 0 | 0 | 0 | 92.5987 | 37.3098 | 0 | 92.2058 | 43% | 0 | 0 | 10% | 0 | 34.7712
2548 | 0 | 0 | 0 | 2.5 | 10.8 | 0 | 0 | 0 | 0 | 100.55 | 40.6876 | 0 | 101.6479 | 35% | 0 | 0 | 10% | 0 | 38.1636
2549 | 0 | 0 | 0 | 2.6 | 10.4 | 0 | 0 | 0 | 0 | 106.3129 | 43.1368 | 0 | 108.3531 | 27% | 0 | 0 | 10% | 0 | 40.6673
2550 | 3 | 9 | 9 | 3 | 10.5 | 0 | 0 | 0 | 0 | 111.5755 | 45.3287 | 0 | 114.2484 | 19% | 0 | 0 | 10% | 0 | 42.9283
2551 | 163 | 137 | 101 | 3.2 | 11.5 | 0 | 30.5798 | 1.3859 | 0 | 110.1338 | 44.6738 | 0 | 112.1591 | 10% | 0 | 0 | 10% | 0 | 43.7431
2552 | 272 | 290 | 182 | 4.7 | 14 | 0 | 57.0363 | 13.3962 | 0 | 82.543 | 32.9012 | 0 | 79.1404 | 4% | 0 | 0 | 10% | 0 | 44.0815
2553 | 447 | 521 | 260 | 5.6 | 16.5 | 99.6601 | 0 | 34.6744 | 0 | 42.428 | 15.2664 | 56.6212 | 0 | 9% | 4.3821 | 0 | 15.96% | 0 | 44.2436
2554 | 483 | 675 | 320 | 6 | 18.6 | 118.2034 | 0 | 50.3561 | 0 | 42.5138 | 15.1823 | 76.7418 | 0 | 14% | 20.1515 | 0 | 43.37% | 0 | 43.8931
2555 | 582 | 815 | 326 | 6.4 | 20.4 | 151.8713 | 2.98e-14 | 54.1918 | 11.672 | 42.5512 | 15.0845 | 110.2656 | 0 | 23% | 25 | 0 | 77.37% | 0 | 42.4816
2556 | 574 | 875 | 355 | 7 | 21.4 | 152.4335 | 0 | 37.2921 | 34.6024 | 42.5758 | 15.0264 | 111.0662 | 0 | 31% | 9.29 | 0 | 90% | 0 | 41.2191
2557 | 458 | 829 | 407 | 7.7 | 21.7 | 117.1622 | 0 | 27.1497 | 38.9474 | 42.5826 | 15.0082 | 76.0135 | 0 | 37% | 0 | 0 | 90% | 0 | 40.6598
2558 | 585 | 842 | 334 | 8.2 | 22.3 | 152.6434 | 0 | 26.9649 | 41.1618 | 42.5849 | 14.9661 | 110.8325 | 0 | 45% | 0 | 0 | 90% | 0 | 40.1154
2559 | 286 | 612 | 385 | 8.4 | 22 | 60.7847 | 0 | 25.9067 | 17.8442 | 42.5889 | 14.9898 | 19.8528 | 0 | 46% | 0 | 0 | 90% | 0 | 39.9029
2560 | 219 | 490 | 348 | 7.9 | 21.1 | 0 | 51.233 | 26.6932 | 4.3016 | 42.5842 | 15.05 | 0 | 40.5879 | 43% | 0 | 0 | 90% | 0 | 39.9981
2561 | 188 | 350 | 262 | 7.6 | 19.6 | 0 | 49.7522 | 17.8303 | 0 | 42.5787 | 15.1451 | 0 | 40.6 | 40% | 0 | 10.6492 | 72.96% | 0 | 40.9575
2562 | 45 | 123 | 108 | 7.3 | 18.2 | 0 | 9.4645 | 1.4254 | 0 | 51.0997 | 18.8021 | 0 | 48.9949 | 37% | 0 | 25 | 32.96% | 0 | 42.536
2563 | 0 | 16 | 16 | 6.3 | 17 | 0 | 0 | 0 | 0 | 71.9861 | 27.9057 | 0 | 72.1829 | 31% | 0 | 14.3508 | 10% | 0 | 39.5151
2564 | 0 | 0 | 0 | 5.2 | 16.8 | 0 | 0 | 0 | 0 | 98.6251 | 39.4927 | 0 | 100.0593 | 24% | 0 | 0 | 10% | 0 | 36.7642
2565 | 0 | 0 | 0 | 3.5 | 17.2 | 0 | 0 | 0 | 0 | 92.9382 | 37.0833 | 0 | 92.9532 | 17% | 0 | 0 | 10% | 0 | 34.4315
2566 | 0 | 0 | 0 | 1.2 | 16.9 | 0 | 0 | 0 | 0 | 87.453 | 34.7871 | 0 | 86.1006 | 11% | 0 | 0 | 10% | 0 | 32.1735
2567 | 0 | 0 | 0 | 2 | 16.5 | 0 | 0 | 0 | 0 | 83.6915 | 33.2358 | 0 | 81.6139 | 5% | 0 | 0 | 10% | 0 | 30.6263
2568 | 0 | 0 | 0 | 1.3 | 16 | 0 | 0 | 0 | 0 | 63.091 | 25.0018 | 0 | 61.3861 | 0% | 0 | 0 | 10% | 0 | 22.3989
2569 | 0 | 0 | 0 | 1.7 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5295
2570 | 0 | 0 | 0 | 1.6 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5028
2571 | 0 | 0 | 0 | 2.1 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4766
2572 | 0 | 0 | 0 | 2.7 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4509
2573 | 0 | 0 | 0 | 1.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4257
2574 | 0 | 12 | 12 | 1.7 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4009
2575 | 4 | 31 | 30 | 1.7 | 13.2 | 0 | 0.75579 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3764
2576 | 0 | 41 | 41 | 1.4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3524
2577 | 0 | 29 | 29 | 2.4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3291
2578 | 0 | 28 | 28 | 4.2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3063
2579 | 0 | 49 | 49 | 3.1 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2839
2580 | 0 | 62 | 61 | 1.8 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2618
2581 | 0 | 109 | 107 | 2.8 | 10.7 | 0 | 0 | 1.0422 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.1978
2582 | 0 | 129 | 127 | 1.8 | 11.8 | 0 | 0 | 2.0842 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.13447
2583 | 225 | 532 | 354 | 4 | 13.2 | 0 | 58.829 | 36.7959 | 0.3469 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 34.6014
2584 | 574 | 555 | 193 | 4.1 | 14.5 | 138.834 | 0 | 39.6311 | 0 | 0 | 0 | 130.3819 | 0 | 10% | 3.4365 | 0 | 14.67% | 0 | 34.5871
2585 | 274 | 281 | 170 | 4.8 | 14.2 | 0 | 59.0912 | 14.4777 | 0 | 22.7402 | 0 | 0 | 21.3038 | 9% | 0 | 2.921 | 10% | 0 | 15.849
2586 | 578 | 209 | 60 | 3 | 14.5 | 95.8742 | 0 | 5.0522 | 0 | 0 | 0 | 91.3352 | 0 | 15% | 0 | 0 | 10% | 0 | 3.8094
2587 | 55 | 20 | 13 | 2.9 | 13.3 | 0 | 4.587 | 0 | 0 | 51.4565 | 6.5236 | 0 | 49.2254 | 12% | 0 | 0 | 10% | 0 | 4.7945
2588 | 0 | 0 | 0 | 2.3 | 12.8 | 0 | 0 | 0 | 0 | 92.0856 | 37.0237 | 0 | 90.8886 | 5% | 0 | 0 | 10% | 0 | 34.697
2589 | 0 | 0 | 0 | 1.9 | 12.1 | 0 | 0 | 0 | 0 | 65.7181 | 26.3722 | 0 | 64.0468 | 0% | 0 | 0 | 10% | 0 | 24.0717
2590 | 0 | 0 | 0 | 1.5 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2247
2591 | 0 | 0 | 0 | 0.9 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2038
2592 | 0 | 0 | 0 | 1.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1832
2593 | 0 | 0 | 0 | 2 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.163
2594 | 0 | 0 | 0 | 1.2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1432
2595 | 0 | 0 | 0 | 0.7 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1238
2596 | 0 | 0 | 0 | 0.6 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1048
2597 | 0 | 0 | 0 | 0.6 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0861
2598 | 0 | 5 | 5 | 0.9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0678
2599 | 0 | 56 | 56 | 0.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0498
2600 | 8 | 136 | 132 | 0.6 | 10.4 | 0 | 2.0155 | 2.4848 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.45278
2601 | 297 | 366 | 181 | 1 | 12.4 | 51.3108 | 13.2325 | 20.9944 | 0 | 0 | 0 | 48.2283 | 0 | 4% | 0 | 0 | 10% | 0 | 19.8336
2602 | 148 | 422 | 309 | 2.8 | 13.8 | 0 | 45.4441 | 26.6515 | 0 | 0 | 0 | 0 | 0 | 4% | 0 | 0 | 10% | 0 | 25.5906
2603 | 269 | 641 | 407 | 4 | 14.9 | 49.7153 | 13.0745 | 48.3735 | 0 | 0 | 0 | 47.3056 | 0 | 7% | 12.5088 | 0 | 27.01% | 0 | 34.7214
2604 | 179 | 672 | 501 | 4.8 | 15.2 | 0 | 57.9232 | 50.669 | 0 | 0 | 0 | 0 | 0 | 7% | 16.757 | 0 | 49.8% | 0 | 32.8653
2605 | 29 | 347 | 314 | 4.2 | 14.8 | 0 | 9.4073 | 19.4989 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 14.6349 | 26.39% | 0 | 32.157
2606 | 13 | 478 | 457 | 5.9 | 14.3 | 0 | 4.1564 | 27.4751 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 6.1885 | 16.48% | 0 | 31.7043
2607 | 48 | 420 | 374 | 3.9 | 14.7 | 0 | 14.8942 | 24.8921 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 4.0526 | 10% | 0 | 27.0067
2608 | 1 | 267 | 263 | 2.9 | 15 | 0 | 0.29415 | 10.8178 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | 8.8924
2609 | 0 | 139 | 137 | 2.4 | 14.3 | 0 | 0 | 2.5545 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | 0.64546
2610 | 0 | 70 | 69 | 1.2 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.893
2611 | 26 | 8 | 4 | 2.6 | 13.5 | 0 | 2.2927 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.8773
2612 | 0 | 0 | 0 | 1.5 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.8619
2613 | 0 | 0 | 0 | 1.9 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.8469
2614 | 0 | 0 | 0 | 1.4 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.8322
2615 | 0 | 0 | 0 | 0.7 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.8177
2616 | 0 | 0 | 0 | 1.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.8035
2617 | 0 | 0 | 0 | 0.9 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7896
2618 | 0 | 0 | 0 | 1.1 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.776
2619 | 0 | 0 | 0 | 0.8 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7627
2620 | 0 | 0 | 0 | 0.7 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7496
2621 | 0 | 0 | 0 | 0.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7368
2622 | 0 | 1 | 1 | 1.2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7243
2623 | 0 | 17 | 17 | 3.8 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.712
2624 | 0 | 42 | 42 | 4.9 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.7
2625 | 0 | 83 | 82 | 3.5 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | -1.6883
2626 | 0 | 164 | 162 | 1.9 | 10.5 | 0 | 0 | 4.1165 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | 2.4398
2627 | 1 | 360 | 353 | 0.8 | 11.6 | 0 | 0.31741 | 17.9747 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | 16.3094
2628 | 30 | 580 | 539 | 1 | 13.5 | 0 | 9.7078 | 36.3294 | 0 | 0 | 0 | 0 | 0 | 7% | 0 | 0 | 10% | 0 | 34.6752
2629 | 650 | 969 | 373 | 1.8 | 15.6 | 146.2625 | 36.2497 | 60.6755 | 14.4245 | 0 | 0 | 137.1732 | 0 | 18% | 25 | 0 | 44% | 0 | 33.7406
2630 | 810 | 949 | 247 | 4.9 | 17.7 | 222.2587 | 2.98e-14 | 61.2733 | 13.8267 | 41.9064 | 0 | 178.4392 | 0 | 32% | 25 | 0 | 78% | 0 | 33.2916
2631 | 73 | 313 | 250 | 4.4 | 17.2 | 0 | 22.6476 | 16.0311 | 0 | 42.226 | 5.3157 | 0 | 38.9219 | 29% | 0 | 13.0282 | 57.16% | 0 | 33.1925
2632 | 11 | 170 | 163 | 6.2 | 15.6 | 0 | 3.2362 | 4.5364 | 0 | 42.2183 | 15.2351 | 0 | 38.9938 | 26% | 0 | 15.7469 | 31.96% | 0 | 33.6757
2633 | 2 | 78 | 77 | 4.8 | 13.8 | 0 | 0.53056 | 0 | 0 | 61.1429 | 23.5301 | 0 | 58.4467 | 22% | 0 | 13.7249 | 10% | 0 | 35.3069
2634 | 0 | 69 | 68 | 4.3 | 13.5 | 0 | 0 | 0 | 0 | 99.4866 | 40.1001 | 0 | 98.6385 | 14% | 0 | 0 | 10% | 0 | 38.0599
2635 | 0 | 4 | 4 | 4.6 | 12.4 | 0 | 0 | 0 | 0 | 95.1814 | 38.3572 | 0 | 93.5945 | 7% | 0 | 0 | 10% | 0 | 36.3183
2636 | 0 | 0 | 0 | 4.1 | 11.7 | 0 | 0 | 0 | 0 | 89.629 | 36.0454 | 0 | 87.0073 | 0% | 0 | 0 | 10% | 0 | 33.9963
2637 | 0 | 0 | 0 | 3.8 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.97
2638 | 0 | 0 | 0 | 3 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9538
2639 | 0 | 0 | 0 | 3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9379
2640 | 0 | 0 | 0 | 2.8 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9223
2641 | 0 | 0 | 0 | 3.2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.907
2642 | 0 | 0 | 0 | 4.3 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.892
2643 | 0 | 0 | 0 | 4.6 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8774
2644 | 0 | 0 | 0 | 3.4 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.863
2645 | 0 | 0 | 0 | 4.4 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8488
2646 | 0 | 0 | 0 | 4.1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8349
2647 | 0 | 4 | 4 | 2.9 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8214
2648 | 0 | 19 | 19 | 3.8 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8081
2649 | 0 | 40 | 40 | 4.4 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7949
2650 | 0 | 68 | 68 | 3.3 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7821
2651 | 0 | 64 | 64 | 1.4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7695
2652 | 0 | 147 | 145 | 1 | 11.9 | 0 | 0 | 3.1172 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 1.36
2653 | 0 | 335 | 327 | 0.9 | 13.6 | 0 | 0 | 15.7598 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 14.0149
2654 | 1 | 325 | 319 | 0.9 | 14.7 | 0 | 0.31974 | 15.1144 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 13.3814
2655 | 1 | 275 | 270 | 1.1 | 15.2 | 0 | 0.31019 | 11.3517 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.6304
2656 | 1 | 241 | 237 | 0.9 | 15.4 | 0 | 0.29425 | 8.9328 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 7.2229
2657 | 1 | 111 | 110 | 1.8 | 15.3 | 0 | 0.26549 | 1.1283 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.5704
2658 | 2 | 97 | 96 | 3 | 14 | 0 | 0.42672 | 0.36576 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.322
2659 | 0 | 14 | 14 | 1.6 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.677
2660 | 0 | 0 | 0 | 0.7 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6664
2661 | 0 | 0 | 0 | 0.8 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.656
2662 | 0 | 0 | 0 | 0.3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6459
2663 | 0 | 0 | 0 | 0.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6359
2664 | 0 | 0 | 0 | 0.7 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6261
2665 | 0 | 0 | 0 | 0.3 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6165
2666 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6071
2667 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5979
2668 | 0 | 0 | 0 | 0.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5888
2669 | 0 | 0 | 0 | 0.5 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.58
2670 | 0 | 5 | 6 | 0.9 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5713
2671 | 5 | 79 | 76 | 1.1 | 11.3 | 0 | 0.97048 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5627
2672 | 223 | 285 | 179 | 1 | 13.4 | 0 | 56.7732 | 11.5528 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.9986
2673 | 572 | 594 | 251 | 1.2 | 15.6 | 111.7715 | 27.8416 | 40.2675 | 0.0047654 | 0 | 0 | 100.1518 | 0 | 9% | 0 | 0 | 10% | 0 | 38.6584
2674 | 475 | 711 | 350 | 1.8 | 16.4 | 118.8909 | 0 | 52.8282 | 0 | 0 | 0 | 114.3802 | 0 | 18% | 12.6185 | 0 | 27.16% | 0 | 38.7127
2675 | 102 | 627 | 526 | 2 | 16.9 | 0 | 32.3845 | 43.1654 | 0 | 0 | 0 | 0 | 0 | 18% | 4.7463 | 0 | 33.62% | 0 | 37.8018
2676 | 37 | 549 | 501 | 3.8 | 17.9 | 0 | 11.973 | 36.2487 | 0 | 41.8853 | 0 | 0 | 38.2518 | 15% | 13.7501 | 0 | 52.32% | 0 | 20.4255
2677 | 194 | 558 | 371 | 5.3 | 18.7 | 0 | 52.0205 | 39.5847 | 0 | 42.3592 | 5.3904 | 0 | 38.8341 | 12% | 17.944 | 0 | 76.72% | 0 | 25.0388
2678 | 0 | 166 | 163 | 3.4 | 17.5 | 0 | 0 | 4.0781 | 0 | 41.8468 | 15.0053 | 0 | 38.4178 | 9% | 0 | 17.652 | 48.48% | 0 | 35.0255
2679 | 0 | 174 | 171 | 3.3 | 17.1 | 0 | 0 | 4.545 | 0 | 41.8205 | 15.0174 | 0 | 38.4809 | 6% | 0 | 17.0764 | 21.15% | 0 | 34.8689
2680 | 21 | 219 | 202 | 2.6 | 17.8 | 0 | 6.1802 | 7.4132 | 0 | 60.1225 | 22.9079 | 0 | 56.3386 | 1% | 0 | 6.9715 | 10% | 0 | 35.4259
2681 | 3 | 140 | 137 | 3.5 | 17.3 | 0 | 0.7971 | 2.5791 | 0 | 17.5481 | 7.007 | 0 | 17.1494 | 0% | 0 | 0 | 10% | 0 | 7.7112
2682 | 28 | 78 | 71 | 1.4 | 17.2 | 0 | 5.9943 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8409
2683 | 15 | 23 | 21 | 1.2 | 16.2 | 0 | 1.5372 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8273
2684 | 0 | 0 | 0 | 0.9 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8139
2685 | 0 | 0 | 0 | 1.3 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8008
2686 | 0 | 0 | 0 | 1.2 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7879
2687 | 0 | 0 | 0 | 0.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7753
2688 | 0 | 0 | 0 | 1.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7629
2689 | 0 | 0 | 0 | 0.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7507
2690 | 0 | 0 | 0 | 1.4 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7388
2691 | 0 | 0 | 0 | 0.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.727
2692 | 0 | 0 | 0 | 0.8 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7156
2693 | 0 | 0 | 0 | 0.9 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7043
2694 | 3 | 8 | 8 | 0.9 | 10.7 | 0 | 0.060756 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6933
2695 | 284 | 146 | 82 | 2.7 | 13.2 | 0 | 55.4725 | 1.4717 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.21063
2696 | 163 | 218 | 162 | 9.1 | 15.1 | 0 | 41.6369 | 8.6341 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 6.9626
2697 | 1 | 200 | 198 | 9 | 15.4 | 0 | 0.28916 | 6.279 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.6179
2698 | 35 | 328 | 299 | 7.4 | 16 | 0 | 10.7496 | 17.1787 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 15.5279
2699 | 3 | 297 | 290 | 8.7 | 15.8 | 0 | 0.95261 | 12.9665 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 11.3257
2700 | 2 | 144 | 141 | 6.7 | 14.1 | 0 | 0.64719 | 2.9758 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 1.3449
2701 | 3 | 318 | 309 | 4.8 | 13.7 | 0 | 0.9731 | 14.5776 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 12.9563
2702 | 28 | 403 | 371 | 5.7 | 14.8 | 0 | 8.9533 | 23.7789 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 22.1672
2703 | 35 | 290 | 260 | 5.9 | 14.4 | 0 | 10.8529 | 14.3619 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 12.7594
2704 | 523 | 513 | 197 | 7.1 | 15.4 | 99.4323 | 25.7052 | 36.3645 | 0 | 0 | 0 | 90.2071 | 0 | 7% | 0 | 0 | 10% | 0 | 34.857
2705 | 666 | 405 | 88 | 7.3 | 16 | 143.6748 | 0 | 21.5576 | 0 | 0 | 0 | 138.6052 | 0 | 18% | 0 | 0 | 10% | 0 | 19.8422
2706 | 141 | 103 | 72 | 5.9 | 14.2 | 0 | 30.2534 | 0.68358 | 0 | 42.0556 | 0 | 0 | 38.523 | 15% | 0 | 0 | 10% | 0 | -0.52291
2707 | 66 | 27 | 22 | 6.6 | 12.8 | 0 | 7.0772 | 0 | 0 | 69.4892 | 18.4209 | 0 | 67.3188 | 10% | 0 | 0 | 10% | 0 | 16.3774
2708 | 0 | 0 | 0 | 5.3 | 12.1 | 0 | 0 | 0 | 0 | 98.1523 | 39.6298 | 0 | 96.3033 | 3% | 0 | 0 | 10% | 0 | 37.8047
2709 | 0 | 0 | 0 | 4.7 | 11.4 | 0 | 0 | 0 | 0 | 35.0972 | 14.1381 | 0 | 33.9663 | 0% | 0 | 0 | 10% | 0 | 12.3599
2710 | 0 | 0 | 0 | 4.7 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7314
2711 | 0 | 0 | 0 | 4.2 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7198
2712 | 0 | 0 | 0 | 3.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7085
2713 | 0 | 0 | 0 | 2.2 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6974
2714 | 0 | 0 | 0 | 1.4 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6865
2715 | 0 | 0 | 0 | 2 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6758
2716 | 0 | 0 | 0 | 2 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6653
2717 | 0 | 0 | 0 | 1.5 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6551
2718 | 115 | 19 | 9 | 0.7 | 6.4 | 0 | 3.055 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.645
2719 | 632 | 176 | 36 | 0.8 | 9.3 | 80.2416 | 20.6251 | 1.3207 | 0 | 0 | 0 | 75.1164 | 0 | 6% | 0 | 0 | 10% | 0 | -0.03023
2720 | 826 | 391 | 51 | 0.9 | 12.1 | 180.8406 | 0 | 19.9052 | 0 | 0 | 0 | 175.9088 | 0 | 20% | 0 | 0 | 10% | 0 | 17.8637
2721 | 914 | 598 | 59 | 3.4 | 13.3 | 228.672 | 0 | 41.8726 | 0 | 0 | 0 | 225.6219 | 0 | 37% | 0 | 0 | 10% | 0 | 39.3588
2722 | 957 | 771 | 66 | 4.2 | 15 | 255.7054 | 0 | 60.9266 | 0 | 42.4442 | 0 | 214.44 | 0 | 54% | 16.7983 | 0 | 32.85% | 0 | 40.7935
2723 | 968 | 901 | 83 | 4 | 15.9 | 268.4623 | 0 | 72.466 | 2.4918 | 0 | 0 | 266.5675 | 0 | 74% | 25 | 0 | 66.85% | 0 | 44.5023
2724 | 846 | 940 | 172 | 3.6 | 16.5 | 237.3852 | 0 | 63.2553 | 11.8447 | 0 | 0 | 235.9361 | 0 | 92% | 17.0252 | 0 | 90% | 0 | 43.5031
2725 | 827 | 925 | 168 | 4.5 | 17.3 | 103.9662 | 140.3134 | 44.4345 | 30.6655 | 0 | 0 | 103.3252 | 0 | 100% | 0 | 0 | 90% | 0 | 42.9537
2726 | 955 | 928 | 100 | 5.9 | 18.3 | 0 | 291.9579 | 43.9854 | 31.1146 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.5204
2727 | 932 | 810 | 92 | 5.8 | 19.1 | 0 | 275.5411 | 43.6422 | 20.5005 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.1673
2728 | 891 | 638 | 74 | 6 | 18.8 | 40.3834 | 215.0245 | 41.4147 | 4.0469 | 42.5403 | 2.3886 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.5677
2729 | 812 | 438 | 63 | 4.7 | 18.8 | 41.8657 | 166.6057 | 24.2477 | 0 | 42.5396 | 15.1799 | 0 | 0 | 100% | 0 | 4.2881 | 83.14% | 0 | 44.2258
2730 | 653 | 224 | 46 | 4.3 | 18.2 | 44.0413 | 85.4894 | 4.7056 | 0 | 44.3857 | 15.9737 | 0 | 0 | 100% | 0 | 25 | 43.14% | 0 | 46.3891
2731 | 204 | 41 | 16 | 3.4 | 16.7 | 0 | 22.8409 | 0 | 0 | 63.1134 | 24.0628 | 0 | 62.8615 | 95% | 0 | 20.7119 | 10% | 0 | 42.7128
2732 | 0 | 0 | 0 | 3.5 | 15.2 | 0 | 0 | 0 | 0 | 103.9303 | 41.8402 | 0 | 106.6317 | 88% | 0 | 0 | 10% | 0 | 39.1342
2733 | 0 | 0 | 0 | 4.8 | 14.5 | 0 | 0 | 0 | 0 | 95.8495 | 38.4937 | 0 | 95.0907 | 80% | 0 | 0 | 10% | 0 | 36.2712
2734 | 0 | 0 | 0 | 3.2 | 13.6 | 0 | 0 | 0 | 0 | 90.1774 | 36.1513 | 0 | 88.1599 | 74% | 0 | 0 | 10% | 0 | 33.9526
2735 | 0 | 0 | 0 | 1.8 | 12.7 | 0 | 0 | 0 | 0 | 86.8119 | 34.7801 | 0 | 84.3273 | 67% | 0 | 0 | 10% | 0 | 32.5173
2736 | 0 | 0 | 0 | 3.7 | 13.6 | 0 | 0 | 0 | 0 | 85.3239 | 34.1009 | 0 | 82.7983 | 61% | 0 | 0 | 10% | 0 | 31.7621
2737 | 0 | 0 | 0 | 6 | 14.4 | 0 | 0 | 0 | 0 | 85.1331 | 33.9725 | 0 | 82.7672 | 55% | 0 | 0 | 10% | 0 | 31.5684
2738 | 0 | 0 | 0 | 5.9 | 14.4 | 0 | 0 | 0 | 0 | 87.0085 | 34.7627 | 0 | 85.1451 | 49% | 0 | 0 | 10% | 0 | 32.3072
2739 | 0 | 0 | 0 | 4 | 13.8 | 0 | 0 | 0 | 0 | 95.1644 | 38.2536 | 0 | 95.1613 | 41% | 0 | 0 | 10% | 0 | 35.762
2740 | 0 | 0 | 0 | 3 | 13.3 | 0 | 0 | 0 | 0 | 104.3043 | 42.1315 | 0 | 105.9952 | 34% | 0 | 0 | 10% | 0 | 39.662
2741 | 0 | 0 | 0 | 3.4 | 12.9 | 0 | 0 | 0 | 0 | 112.7038 | 45.6636 | 0 | 115.6575 | 25% | 0 | 0 | 10% | 0 | 43.2566
2742 | 15 | 15 | 14 | 4.5 | 12.9 | 0 | 0.49272 | 0 | 0 | 117.3042 | 47.584 | 0 | 120.7372 | 16% | 0 | 0 | 10% | 0 | 45.264
2743 | 109 | 112 | 85 | 4.1 | 13.7 | 0 | 21.5506 | 0.3859 | 0 | 117.4483 | 47.589 | 0 | 120.4575 | 7% | 0 | 0 | 10% | 0 | 45.7465
2744 | 29 | 158 | 145 | 3.9 | 14.8 | 0 | 7.4557 | 3.9565 | 0 | 85.7598 | 34.6111 | 0 | 86.6184 | 0% | 0 | 0 | 10% | 0 | 36.4655
2745 | 170 | 355 | 244 | 7.5 | 15.8 | 0 | 49.2093 | 18.7533 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 16.7955
2746 | 280 | 548 | 328 | 8.4 | 17 | 47.1493 | 13.1168 | 37.3242 | 0 | 0 | 0 | 45.3797 | 0 | 3% | 0 | 0 | 10% | 0 | 36.2154
2747 | 685 | 876 | 287 | 8.9 | 18.7 | 180.1916 | 0 | 69.3833 | 0 | 0 | 0 | 175.9367 | 0 | 17% | 24.2174 | 0 | 42.94% | 0 | 43.1664
2748 | 885 | 986 | 178 | 9.4 | 20.1 | 244.2624 | 0 | 70.4871 | 4.6129 | 0 | 0 | 242.22 | 0 | 35% | 25 | 0 | 76.94% | 0 | 42.8654
2749 | 824 | 978 | 218 | 8.3 | 20.8 | 227.179 | 1.15e-14 | 54.4786 | 20.6214 | 0 | 0 | 225.8867 | 0 | 52% | 9.6061 | 0 | 90% | 0 | 42.3504
2750 | 350 | 595 | 277 | 5.7 | 20.2 | 84.4731 | 0 | 43.1303 | 0.56015 | 0 | 0 | 84.0051 | 0 | 59% | 0 | 0 | 90% | 0 | 41.9163
2751 | 146 | 391 | 274 | 6.1 | 20.2 | 0 | 45.2574 | 23.3594 | 0 | 0 | 0 | 0 | 0 | 59% | 0 | 18.9039 | 59.75% | 0 | 41.2356
2752 | 773 | 659 | 165 | 6.2 | 21.9 | 157.1598 | 38.6258 | 46.4105 | 0 | 42.7305 | 1.1172 | 120.2482 | 7.1657 | 67% | 18.6459 | 0 | 85.11% | 0 | 26.2567
2753 | 794 | 460 | 92 | 7.5 | 22.4 | 175.9731 | -2.98e-14 | 25.6063 | 0 | 42.5776 | 14.9561 | 135.112 | 0 | 78% | 0 | 4.1769 | 78.43% | 0 | 42.64
2754 | 690 | 232 | 43 | 7.8 | 20.7 | 117.1204 | 0 | 4.8296 | 0 | 47.3791 | 17.0598 | 71.6261 | 0 | 83% | 0 | 25 | 38.43% | 0 | 45.3457
2755 | 223 | 42 | 16 | 7.7 | 18.8 | 0 | 26.0213 | 0 | 0 | 68.4411 | 26.2127 | 0 | 67.987 | 78% | 0 | 17.7682 | 10% | 0 | 42.3144
2756 | 0 | 0 | 0 | 6.4 | 17.4 | 0 | 0 | 0 | 0 | 104.1822 | 41.7771 | 0 | 106.1814 | 70% | 0 | 0 | 10% | 0 | 39.2419
2757 | 0 | 0 | 0 | 4.9 | 16.3 | 0 | 0 | 0 | 0 | 96.9902 | 38.8442 | 0 | 96.7975 | 63% | 0 | 0 | 10% | 0 | 36.5015
2758 | 0 | 0 | 0 | 3.3 | 15.8 | 0 | 0 | 0 | 0 | 90.9453 | 36.3329 | 0 | 89.3557 | 56% | 0 | 0 | 10% | 0 | 34.0379
2759 | 0 | 0 | 0 | 2.3 | 14.5 | 0 | 0 | 0 | 0 | 87.2628 | 34.8611 | 0 | 84.9764 | 50% | 0 | 0 | 10% | 0 | 32.5468
2760 | 0 | 0 | 0 | 1.4 | 12.8 | 0 | 0 | 0 | 0 | 85.301 | 34.136 | 0 | 82.7807 | 43% | 0 | 0 | 10% | 0 | 31.7787
2761 | 0 | 0 | 0 | 1.7 | 12.1 | 0 | 0 | 0 | 0 | 85.5397 | 34.2753 | 0 | 83.2014 | 37% | 0 | 0 | 10% | 0 | 31.8704
2762 | 0 | 0 | 0 | 2.2 | 11.4 | 0 | 0 | 0 | 0 | 87.2692 | 35.0417 | 0 | 85.3697 | 31% | 0 | 0 | 10% | 0 | 32.5975
2763 | 0 | 0 | 0 | 2.2 | 11.4 | 0 | 0 | 0 | 0 | 94.7993 | 38.2375 | 0 | 94.6253 | 24% | 0 | 0 | 10% | 0 | 35.7599
2764 | 0 | 0 | 0 | 0.7 | 9.3 | 0 | 0 | 0 | 0 | 104.7166 | 42.519 | 0 | 106.4345 | 16% | 0 | 0 | 10% | 0 | 40.0466
2765 | 0 | 0 | 0 | 1.4 | 8.8 | 0 | 0 | 0 | 0 | 111.5971 | 45.4156 | 0 | 114.3341 | 7% | 0 | 0 | 10% | 0 | 42.9907
2766 | 111 | 22 | 10 | 1.8 | 9.2 | 0 | 4.3388 | 0 | 0 | 93.5941 | 38.1065 | 0 | 96.077 | 0% | 0 | 0 | 10% | 0 | 35.7889
2767 | 620 | 184 | 42 | 1.7 | 11.5 | 79.4445 | 20.3118 | 1.5836 | 0 | 0 | 0 | 76.717 | 0 | 6% | 0 | 0 | 10% | 0 | 0.16212
2768 | 801 | 400 | 63 | 0.9 | 14.7 | 176.2697 | 0 | 20.0194 | 0 | 0 | 0 | 173.8147 | 0 | 19% | 0 | 0 | 10% | 0 | 18.0514
2769 | 876 | 603 | 81 | 3 | 16.1 | 219.0958 | 0 | 41.5178 | 0 | 0 | 0 | 217.4509 | 0 | 35% | 0 | 0 | 10% | 0 | 39.1348
2770 | 909 | 783 | 105 | 3.8 | 17.2 | 242.5075 | 0 | 60.7122 | 0 | 0 | 0 | 241.1199 | 0 | 54% | 15.4574 | 0 | 31.02% | 0 | 42.6186
2771 | 939 | 915 | 114 | 3.6 | 18.3 | 260.5153 | 0 | 70.1982 | 4.5172 | 0 | 0 | 259.2243 | 0 | 73% | 25 | 0 | 65.02% | 0 | 42.3477
2772 | 948 | 997 | 132 | 2.6 | 19 | 269.0632 | 4.38e-14 | 62.7043 | 12.3957 | 0 | 0 | 267.8754 | 0 | 93% | 18.3661 | 0 | 90% | 0 | 41.3433
2773 | 719 | 879 | 211 | 2.1 | 19.9 | 90.7583 | 120.4259 | 41.7443 | 29.8106 | 0 | 0 | 90.3748 | 0 | 100% | 0 | 0 | 90% | 0 | 40.3923
2774 | 867 | 929 | 173 | 4.8 | 20.2 | 0 | 263.9324 | 41.8556 | 33.2444 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.8998
2775 | 897 | 827 | 130 | 4.2 | 20 | 0 | 264.7213 | 41.0372 | 23.5093 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.4045
2776 | 855 | 645 | 99 | 4.2 | 19.7 | 40.2695 | 204.786 | 40.8369 | 4.4834 | 42.5903 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.5226
2777 | 780 | 442 | 76 | 4.2 | 19.4 | 43.3544 | 156.5979 | 23.9915 | 0 | 43.7661 | 14.5097 | 0 | 0 | 100% | 0 | 1.2853 | 87.94% | 0 | 40.3804
2778 | 603 | 225 | 57 | 3.9 | 18.7 | 42.1295 | 77.1191 | 4.6445 | 0 | 42.5859 | 15.2022 | 0 | 0 | 100% | 0 | 22.5826 | 51.81% | 0 | 43.1413
2779 | 196 | 44 | 20 | 2.2 | 17.5 | 0 | 23.7934 | 0 | 0 | 49.2343 | 18.0528 | 0 | 47.7018 | 97% | 0 | 25 | 11.81% | 0 | 40.9961
2780 | 0 | 0 | 0 | 1.2 | 15.4 | 0 | 0 | 0 | 0 | 102.5296 | 41.2328 | 0 | 105.9066 | 89% | 0 | 0 | 11.81% | 0 | 38.2649
2781 | 0 | 0 | 0 | 1.2 | 14.1 | 0 | 0 | 0 | 0 | 95.7029 | 38.457 | 0 | 95.3008 | 82% | 0 | 0 | 11.81% | 0 | 36.1241
2782 | 0 | 0 | 0 | 1.7 | 13.2 | 0 | 0 | 0 | 0 | 89.7924 | 36.0099 | 0 | 87.9063 | 75% | 0 | 0 | 11.81% | 0 | 33.7422
2783 | 0 | 0 | 0 | 0.8 | 12.7 | 0 | 0 | 0 | 0 | 85.6977 | 34.3081 | 0 | 83.1772 | 69% | 0 | 0 | 11.81% | 0 | 31.9877
2784 | 0 | 0 | 0 | 2.3 | 12.7 | 0 | 0 | 0 | 0 | 83.2673 | 33.2859 | 0 | 80.5544 | 63% | 0 | 0 | 11.81% | 0 | 30.8889
2785 | 0 | 0 | 0 | 2.4 | 12.3 | 0 | 0 | 0 | 0 | 82.3586 | 32.9008 | 0 | 79.8083 | 57% | 0 | 0 | 11.81% | 0 | 30.4311
2786 | 0 | 0 | 0 | 1.1 | 12.1 | 0 | 0 | 0 | 0 | 82.0094 | 32.7522 | 0 | 79.61 | 51% | 0 | 0 | 11.81% | 0 | 30.2276
2787 | 0 | 0 | 0 | 1.1 | 11.3 | 0 | 0 | 0 | 0 | 84.0335 | 33.6817 | 0 | 81.9484 | 45% | 0 | 0 | 11.81% | 0 | 31.1125
2788 | 0 | 0 | 0 | 1.2 | 10.8 | 0 | 0 | 0 | 0 | 85.9004 | 34.4929 | 0 | 84.2407 | 38% | 0 | 0 | 11.81% | 0 | 31.8945
2789 | 0 | 0 | 0 | 1.1 | 10.1 | 0 | 0 | 0 | 0 | 90.7562 | 36.5831 | 0 | 90.1675 | 32% | 0 | 0 | 11.81% | 0 | 33.9663
2790 | 110 | 23 | 11 | 1.8 | 11 | 0 | 4.9802 | 0 | 0 | 97.4321 | 39.3647 | 0 | 98.2079 | 24% | 0 | 0 | 11.81% | 0 | 36.7558
2791 | 623 | 186 | 40 | 0.1 | 14 | 81.3268 | 20.4362 | 1.4934 | 0 | 95.9051 | 38.5514 | 1.0419 | 18.4058 | 23% | 0 | 0 | 11.81% | 0 | 38.4338
2792 | 815 | 401 | 55 | 1 | 16.8 | 180.2903 | 0 | 19.6328 | 0 | 56.6749 | 21.3118 | 123.887 | 0 | 32% | 0 | 0 | 11.81% | 0 | 38.8815
2793 | 902 | 607 | 64 | 1.9 | 18.9 | 227.0054 | 0 | 40.9079 | 0 | 45.0916 | 16.2236 | 182.4721 | 0 | 46% | 16.0797 | 0 | 33.68% | 0 | 38.5695
2794 | 953 | 782 | 68 | 2.4 | 19.9 | 256.2977 | 0 | 50.9621 | 8.7735 | 42.5735 | 15.1247 | 214.3222 | 0 | 62% | 25 | 0 | 67.68% | 0 | 38.3194
2795 | 984 | 909 | 68 | 2.5 | 20.6 | 274.484 | 0 | 41.5406 | 31.9164 | 42.5865 | 15.0839 | 232.4755 | 0 | 79% | 16.412 | 0 | 90% | 0 | 37.2443
2796 | 992 | 977 | 70 | 2.6 | 21.3 | 281.8533 | 0 | 20.4286 | 54.6714 | 42.5916 | 15.0389 | 239.753 | 0 | 97% | 0 | 0 | 90% | 0 | 35.6116
2797 | 988 | 981 | 72 | 2.7 | 21.7 | 87.7478 | 220.526 | 18.8618 | 56.2382 | 42.596 | 15.0129 | 46.232 | 0 | 100% | 0 | 0 | 90% | 0 | 34.3469
2798 | 977 | 926 | 72 | 3.9 | 22.2 | 42.1522 | 264.1712 | 18.0272 | 56.8341 | 42.5942 | 14.9768 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.7152
2799 | 958 | 814 | 68 | 4.9 | 22.4 | 42.1578 | 248.4184 | 17.9868 | 44.706 | 42.5919 | 14.9612 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.6591
2800 | 923 | 653 | 61 | 4.6 | 22 | 42.1578 | 223.0576 | 18.3135 | 26.8944 | 42.5896 | 14.99 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.0147
2801 | 848 | 453 | 54 | 5.7 | 20.8 | 42.1579 | 176.4107 | 19.4717 | 4.8196 | 42.5874 | 15.0711 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.2543
2802 | 690 | 236 | 43 | 5.4 | 19.6 | 42.158 | 96.8685 | 4.7617 | 0 | 42.5852 | 15.1474 | 0 | 0 | 100% | 0 | 17.7136 | 61.66% | 0 | 38.3346
2803 | 256 | 48 | 17 | 5.2 | 17.6 | 0 | 32.2781 | 0 | 0 | 42.5823 | 15.2636 | 0 | 41.091 | 97% | 0 | 24.0439 | 23.19% | 0 | 37.2551
2804 | 0 | 0 | 0 | 2.8 | 15.6 | 0 | 0 | 0 | 0 | 75.7875 | 29.7442 | 0 | 76.2331 | 91% | 0 | 8.2424 | 10% | 0 | 35.0596
2805 | 0 | 0 | 0 | 2.1 | 14.1 | 0 | 0 | 0 | 0 | 88.4691 | 35.3951 | 0 | 87.4701 | 85% | 0 | 0 | 10% | 0 | 32.7782
2806 | 0 | 0 | 0 | 1.7 | 12.9 | 0 | 0 | 0 | 0 | 82.504 | 32.9334 | 0 | 80.2953 | 79% | 0 | 0 | 10% | 0 | 30.3626
2807 | 0 | 0 | 0 | 0.8 | 12.8 | 0 | 0 | 0 | 0 | 79.5462 | 31.5886 | 0 | 77.4783 | 73% | 0 | 0 | 10% | 0 | 28.9554
2808 | 0 | 0 | 0 | 1.4 | 12.7 | 0 | 0 | 0 | 0 | 77.2186 | 30.5407 | 0 | 75.2282 | 68% | 0 | 0 | 10% | 0 | 27.8688
2809 | 0 | 0 | 0 | 1.6 | 12.4 | 0 | 0 | 0 | 0 | 76.3576 | 30.1692 | 0 | 74.4284 | 62% | 0 | 0 | 10% | 0 | 27.4695
2810 | 0 | 0 | 0 | 0.9 | 11.3 | 0 | 0 | 0 | 0 | 75.925 | 30.0306 | 0 | 74.0411 | 57% | 0 | 0 | 10% | 0 | 27.31
2811 | 0 | 0 | 0 | 0.9 | 10.4 | 0 | 0 | 0 | 0 | 76.6666 | 30.4063 | 0 | 74.8294 | 51% | 0 | 0 | 10% | 0 | 27.6684
2812 | 0 | 0 | 0 | 1.2 | 10.5 | 0 | 0 | 0 | 0 | 76.4884 | 30.3222 | 0 | 74.6763 | 46% | 0 | 0 | 10% | 0 | 27.5717
2813 | 0 | 0 | 0 | 1.7 | 11.1 | 0 | 0 | 0 | 0 | 79.4924 | 31.6551 | 0 | 77.7491 | 40% | 0 | 0 | 10% | 0 | 28.8906
2814 | 125 | 32 | 17 | 1.6 | 11.4 | 0 | 6.4243 | 0 | 0 | 84.1514 | 33.7271 | 0 | 82.7146 | 34% | 0 | 0 | 10% | 0 | 30.9489
2815 | 409 | 160 | 61 | 1.5 | 13.4 | 48.5349 | 12.5683 | 1.2681 | 0 | 82.2928 | 32.7954 | 0 | 33.6257 | 31% | 0 | 0 | 10% | 0 | 32.7203
2816 | 777 | 403 | 69 | 3 | 16.4 | 170.6794 | 0 | 19.689 | 0 | 43.2101 | 15.5878 | 126.0128 | 0 | 41% | 0 | 0 | 10% | 0 | 33.3337
2817 | 865 | 605 | 80 | 4.3 | 18.7 | 215.5767 | 0 | 40.4607 | 0 | 45.2716 | 16.3108 | 170.372 | 0 | 53% | 21.3073 | 0 | 38.98% | 0 | 33.0927
2818 | 963 | 791 | 67 | 4.3 | 20.6 | 257.9204 | 0 | 45.7646 | 14.3582 | 42.5614 | 15.075 | 215.4072 | 0 | 69% | 25 | 0 | 72.98% | 0 | 33.0681
2819 | 948 | 902 | 87 | 4.6 | 22 | 262.7218 | 0 | 31.8891 | 40.0653 | 42.5767 | 14.9855 | 220.324 | 0 | 85% | 12.5162 | 0 | 90% | 0 | 32.8754
2820 | 964 | 976 | 92 | 5.6 | 22.3 | 247.5725 | 27.5464 | 13.7064 | 61.3936 | 42.5827 | 14.9654 | 205.2702 | 0 | 100% | 0 | 0 | 90% | 0 | 31.5506
2821 | 908 | 958 | 118 | 6.6 | 22.3 | 42.1522 | 245.7443 | 14.9334 | 60.1666 | 42.5867 | 14.9668 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 30.6112
2822 | 923 | 932 | 121 | 7.2 | 22.7 | 42.1577 | 246.1903 | 14.5303 | 60.1116 | 42.5846 | 14.9364 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 30.1777
2823 | 937 | 829 | 96 | 7.1 | 22.9 | 42.1577 | 241.424 | 15.1142 | 48.4256 | 42.5825 | 14.9208 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 30.7459
2824 | 886 | 657 | 86 | 6.8 | 22.6 | 42.1578 | 211.5944 | 16.1166 | 29.1169 | 42.5805 | 14.9423 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 31.77
2825 | 789 | 453 | 79 | 6.5 | 21.6 | 42.1578 | 160.2414 | 18.1 | 6.0955 | 42.5786 | 15.0136 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.8249
2826 | 661 | 241 | 52 | 5.5 | 20.3 | 42.1579 | 90.5582 | 4.9428 | 0 | 42.5767 | 15.1 | 0 | 0 | 100% | 0 | 16.2588 | 63.99% | 0 | 37.0132
2827 | 227 | 50 | 21 | 5.1 | 18 | 0 | 29.6825 | 0 | 0 | 42.574 | 15.2388 | 0 | 41.0827 | 97% | 0 | 23.5177 | 26.36% | 0 | 36.7031
2828 | 0 | 0 | 0 | 4.6 | 15.4 | 0 | 0 | 0 | 0 | 69.7632 | 27.1572 | 0 | 69.7068 | 92% | 0 | 10.2235 | 10% | 0 | 34.4579
2829 | 0 | 0 | 0 | 2.4 | 13.8 | 0 | 0 | 0 | 0 | 86.6836 | 34.6598 | 0 | 85.5176 | 86% | 0 | 0 | 10% | 0 | 31.9801
2830 | 0 | 0 | 0 | 2.8 | 13.7 | 0 | 0 | 0 | 0 | 81.9926 | 32.654 | 0 | 79.9959 | 80% | 0 | 0 | 10% | 0 | 30.0104
2831 | 0 | 0 | 0 | 2.4 | 13.5 | 0 | 0 | 0 | 0 | 79.639 | 31.5925 | 0 | 77.7244 | 74% | 0 | 0 | 10% | 0 | 28.9068
2832 | 0 | 0 | 0 | 1.4 | 13 | 0 | 0 | 0 | 0 | 78.8628 | 31.2691 | 0 | 77.0084 | 68% | 0 | 0 | 10% | 0 | 28.5558
2833 | 0 | 0 | 0 | 1.4 | 13 | 0 | 0 | 0 | 0 | 78.5476 | 31.1268 | 0 | 76.7356 | 63% | 0 | 0 | 10% | 0 | 28.3942
2834 | 0 | 0 | 0 | 0.8 | 11.3 | 0 | 0 | 0 | 0 | 80.8905 | 32.2812 | 0 | 79.1517 | 57% | 0 | 0 | 10% | 0 | 29.5315
2835 | 0 | 0 | 0 | 1.4 | 12 | 0 | 0 | 0 | 0 | 89.4854 | 35.9494 | 0 | 89.153 | 50% | 0 | 0 | 10% | 0 | 33.1797
2836 | 0 | 0 | 0 | 2.4 | 13.8 | 0 | 0 | 0 | 0 | 98.7525 | 39.7572 | 0 | 100.3201 | 43% | 0 | 0 | 10% | 0 | 37.0164
2837 | 0 | 0 | 0 | 1.7 | 13 | 0 | 0 | 0 | 0 | 105.4295 | 42.6236 | 0 | 108.0942 | 35% | 0 | 0 | 10% | 0 | 39.9669
2838 | 0 | 15 | 15 | 2.3 | 13.3 | 0 | 0 | 0 | 0 | 108.5613 | 43.9075 | 0 | 111.3357 | 26% | 0 | 0 | 10% | 0 | 41.3559
2839 | 72 | 122 | 102 | 2.3 | 15.1 | 0 | 14.5572 | 0.86365 | 0 | 107.7396 | 43.4394 | 0 | 109.934 | 18% | 0 | 0 | 10% | 0 | 41.8498
2840 | 246 | 318 | 207 | 3.7 | 16.9 | 0 | 52.9566 | 13.8549 | 0 | 77.7478 | 30.542 | 0 | 74.739 | 12% | 0 | 0 | 10% | 0 | 42.0593
2841 | 521 | 548 | 220 | 4.5 | 18.7 | 121.9716 | 0 | 34.7434 | 0 | 42.4715 | 15.1614 | 78.1067 | 0 | 18% | 6.276 | 0 | 18.54% | 0 | 42.1212
2842 | 597 | 739 | 283 | 5.1 | 20.1 | 151.8698 | 0 | 53.664 | 0.85701 | 42.519 | 15.0926 | 110.0632 | 0 | 27% | 25 | 0 | 52.53% | 0 | 41.9615
2843 | 298 | 698 | 434 | 5.2 | 20.6 | 68.7857 | 0 | 51.202 | 0 | 42.5494 | 15.0707 | 27.971 | 0 | 29% | 24.0202 | 0 | 85.2% | 0 | 41.1885
2844 | 520 | 819 | 329 | 5.8 | 20.7 | 137.2353 | 0 | 30.2524 | 33.885 | 42.5534 | 15.0656 | 95.5074 | 0 | 36% | 3.5273 | 0 | 90% | 0 | 40.1204
2845 | 756 | 945 | 240 | 5.3 | 21.7 | 209.4741 | 2.98e-14 | 26.8395 | 48.2605 | 42.5635 | 15.0015 | 167.1912 | 0 | 48% | 0 | 0 | 90% | 0 | 39.5185
2846 | 317 | 674 | 385 | 4.5 | 21.9 | 75.6486 | 0 | 25.2671 | 24.1002 | 42.5773 | 14.9926 | 34.6339 | 0 | 51% | 0 | 0 | 90% | 0 | 39.1315
2847 | 291 | 579 | 341 | 4.3 | 21.8 | 65.5528 | 0 | 24.5053 | 14.9463 | 42.5765 | 14.9992 | 23.953 | 0 | 53% | 0 | 0 | 90% | 0 | 38.4737
2848 | 167 | 417 | 309 | 4.1 | 21.4 | 0 | 49.1916 | 23.9187 | 0.10342 | 45.4059 | 16.1957 | 0 | 43.5749 | 49% | 0 | 0 | 90% | 0 | 38.244
2849 | 404 | 362 | 179 | 4.6 | 20.7 | 66.86 | 16.9141 | 18.6596 | 0 | 42.5676 | 15.0707 | 31.5238 | 7.3942 | 51% | 0 | 7.4459 | 78.09% | 0 | 39.7181
2850 | 547 | 226 | 64 | 4.7 | 19.9 | 92.1484 | 0 | 4.3314 | 0 | 42.5678 | 15.1227 | 50.001 | 0 | 55% | 0 | 24.0726 | 39.57% | 0 | 42.2612
2851 | 247 | 58 | 27 | 4.4 | 18.1 | 0 | 33.4426 | 0 | 0 | 61.2794 | 23.239 | 0 | 61.1943 | 50% | 0 | 18.4815 | 10% | 0 | 39.7059
2852 | 0 | 0 | 0 | 4.3 | 15.2 | 0 | 0 | 0 | 0 | 97.8684 | 39.2904 | 0 | 99.9272 | 43% | 0 | 0 | 10% | 0 | 36.3648
2853 | 0 | 0 | 0 | 3.1 | 13.8 | 0 | 0 | 0 | 0 | 92.4027 | 37.0831 | 0 | 92.8367 | 36% | 0 | 0 | 10% | 0 | 34.2815
2854 | 0 | 0 | 0 | 2.1 | 13 | 0 | 0 | 0 | 0 | 87.1663 | 34.9121 | 0 | 86.185 | 30% | 0 | 0 | 10% | 0 | 32.1729
2855 | 0 | 0 | 0 | 1.9 | 12.4 | 0 | 0 | 0 | 0 | 84.1239 | 33.6633 | 0 | 82.4915 | 24% | 0 | 0 | 10% | 0 | 30.9401
2856 | 0 | 0 | 0 | 0.8 | 12.2 | 0 | 0 | 0 | 0 | 82.8844 | 33.1518 | 0 | 81.0435 | 18% | 0 | 0 | 10% | 0 | 30.4247
2857 | 0 | 0 | 0 | 1.2 | 11.5 | 0 | 0 | 0 | 0 | 82.7993 | 33.1503 | 0 | 80.9777 | 12% | 0 | 0 | 10% | 0 | 30.4128
2858 | 0 | 0 | 0 | 1 | 10.8 | 0 | 0 | 0 | 0 | 84.281 | 33.8123 | 0 | 82.7428 | 5% | 0 | 0 | 10% | 0 | 31.0629
2859 | 0 | 0 | 0 | 1.4 | 11.4 | 0 | 0 | 0 | 0 | 73.6569 | 29.6695 | 0 | 73.8441 | 0% | 0 | 0 | 10% | 0 | 26.9308
2860 | 0 | 0 | 0 | 1.8 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.6171
2861 | 0 | 0 | 0 | 1.3 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5888
2862 | 99 | 26 | 14 | 1.4 | 10.6 | 0 | 6.2765 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5608
2863 | 572 | 187 | 48 | 0.5 | 14.3 | 74.9421 | 18.8903 | 1.5468 | 0 | 0 | 0 | 71.9736 | 0 | 5% | 0 | 0 | 10% | 0 | 0.10084
2864 | 760 | 398 | 69 | 0.6 | 16.7 | 168.2646 | 0 | 19.1542 | 0 | 0 | 0 | 165.3343 | 0 | 18% | 0 | 0 | 10% | 0 | 17.2817
2865 | 848 | 600 | 84 | 1.6 | 18.7 | 212.8698 | 0 | 39.8642 | 0 | 0 | 0 | 210.9237 | 0 | 33% | 0 | 0 | 10% | 0 | 37.5706
2866 | 898 | 771 | 92 | 2.3 | 20 | 240.4849 | 0 | 57.5802 | 0.40623 | 42.5489 | 2.395 | 198.4929 | 0 | 48% | 18.522 | 0 | 35.19% | 0 | 38.4265
2867 | 924 | 894 | 99 | 2.6 | 21.3 | 257.0401 | 0 | 54.6151 | 16.4867 | 42.5683 | 15.0307 | 215.0797 | 0 | 64% | 25 | 0 | 69.19% | 0 | 41.8678
2868 | 938 | 965 | 102 | 2.6 | 22.5 | 266.3001 | 0 | 44.2037 | 30.8963 | 42.5826 | 14.9505 | 224.2625 | 0 | 81% | 15.3015 | 0 | 90% | 0 | 40.9578
2869 | 929 | 969 | 109 | 3.5 | 23.1 | 263.7627 | 0 | 25.0491 | 50.0509 | 42.5878 | 14.9075 | 221.6438 | 0 | 97% | 0 | 0 | 90% | 0 | 40.4637
2870 | 905 | 911 | 114 | 4.7 | 23.5 | 84.3688 | 192.2042 | 24.7164 | 47.4108 | 42.5925 | 14.8783 | 42.8352 | 0 | 100% | 0 | 0 | 90% | 0 | 40.0948
2871 | 864 | 797 | 118 | 5.1 | 23.5 | 42.1522 | 218.7254 | 23.695 | 36.2565 | 42.5908 | 14.8777 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.2835
2872 | 795 | 628 | 112 | 3.5 | 23.8 | 42.1577 | 185.0787 | 23.2093 | 18.8717 | 42.5886 | 14.8538 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.7738
2873 | 713 | 439 | 98 | 3.5 | 23.6 | 44.6843 | 137.4501 | 22.8078 | 0 | 45.0732 | 15.8847 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.3995
2874 | 501 | 273 | 124 | 5 | 21.4 | 42.1035 | 53.579 | 7.3073 | 0 | 42.5844 | 15.0295 | 0 | 0 | 100% | 0 | 18.2555 | 60.79% | 0 | 41.3035
2875 | 93 | 54 | 42 | 4.7 | 18.4 | 0 | 13.0204 | 0 | 0 | 45.0771 | 16.2501 | 0 | 43.5622 | 97% | 0 | 24.7429 | 21.2% | 0 | 38.9365
2876 | 0 | 0 | 0 | 3.7 | 15.8 | 0 | 0 | 0 | 0 | 80.8685 | 31.9081 | 0 | 81.8698 | 91% | 0 | 7.0016 | 10% | 0 | 35.9722
2877 | 0 | 0 | 0 | 3.8 | 14.4 | 0 | 0 | 0 | 0 | 91.3019 | 36.5761 | 0 | 90.751 | 84% | 0 | 0 | 10% | 0 | 34.0151
2878 | 0 | 0 | 0 | 3.9 | 13.3 | 0 | 0 | 0 | 0 | 85.9838 | 34.3943 | 0 | 84.0339 | 78% | 0 | 0 | 10% | 0 | 31.9139
2879 | 0 | 0 | 0 | 2.8 | 12.6 | 0 | 0 | 0 | 0 | 81.9482 | 32.6954 | 0 | 79.5911 | 72% | 0 | 0 | 10% | 0 | 30.1683
2880 | 0 | 0 | 0 | 2.7 | 11.9 | 0 | 0 | 0 | 0 | 80.1875 | 31.9289 | 0 | 77.9863 | 66% | 0 | 0 | 10% | 0 | 29.3398
2881 | 0 | 0 | 0 | 2.8 | 11.5 | 0 | 0 | 0 | 0 | 79.2923 | 31.5419 | 0 | 77.1955 | 60% | 0 | 0 | 10% | 0 | 28.9105
2882 | 0 | 0 | 0 | 2.9 | 11 | 0 | 0 | 0 | 0 | 77.9876 | 30.9755 | 0 | 75.9553 | 55% | 0 | 0 | 10% | 0 | 28.314
2883 | 0 | 0 | 0 | 2.2 | 10.8 | 0 | 0 | 0 | 0 | 77.3221 | 30.6843 | 0 | 75.3419 | 49% | 0 | 0 | 10% | 0 | 27.9991
2884 | 0 | 0 | 0 | 2.4 | 10.6 | 0 | 0 | 0 | 0 | 77.0988 | 30.5931 | 0 | 75.1621 | 44% | 0 | 0 | 10% | 0 | 27.8885
2885 | 0 | 0 | 0 | 3.8 | 10.7 | 0 | 0 | 0 | 0 | 80.0043 | 31.9065 | 0 | 78.1468 | 38% | 0 | 0 | 10% | 0 | 29.1826
2886 | 51 | 22 | 16 | 2.9 | 11.2 | 0 | 3.5327 | 0 | 0 | 85.088 | 34.1318 | 0 | 83.7167 | 32% | 0 | 0 | 10% | 0 | 31.3887
2887 | 430 | 182 | 70 | 2.9 | 12.9 | 52.3113 | 13.6179 | 1.7308 | 0 | 82.6292 | 32.9771 | 0 | 30.2055 | 29% | 0 | 0 | 10% | 0 | 33.3369
2888 | 729 | 398 | 78 | 3 | 15 | 159.6371 | 0 | 19.0551 | 0 | 46.391 | 16.9772 | 112.2949 | 0 | 38% | 0 | 0 | 10% | 0 | 34.1803
2889 | 845 | 604 | 85 | 3.9 | 17.9 | 210.8078 | 0 | 39.8661 | 0 | 44.9496 | 16.2243 | 165.9242 | 0 | 50% | 19.1721 | 0 | 36.07% | 0 | 34.5924
2890 | 891 | 779 | 101 | 4.8 | 20 | 236.7138 | 0 | 47.3456 | 10.9016 | 42.5609 | 15.1141 | 194.3586 | 0 | 64% | 25 | 0 | 70.07% | 0 | 34.8837
2891 | 810 | 869 | 164 | 5.2 | 21.5 | 221.1208 | 0 | 35.9813 | 31.5142 | 42.5754 | 15.0194 | 178.8639 | 0 | 77% | 14.6515 | 0 | 90% | 0 | 34.1943
2892 | 815 | 965 | 208 | 5.9 | 22.6 | 226.4454 | 0 | 17.1072 | 57.9928 | 42.5803 | 14.9423 | 184.0566 | 0 | 91% | 0 | 0 | 90% | 0 | 32.486
2893 | 826 | 952 | 181 | 6 | 23.2 | 169.3065 | 70.9514 | 15.1885 | 59.9115 | 42.5858 | 14.8991 | 127.272 | 0 | 100% | 0 | 0 | 90% | 0 | 31.5174
2894 | 862 | 906 | 143 | 5.7 | 23.8 | 42.1523 | 226.5397 | 15.5668 | 55.376 | 42.5867 | 14.8532 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 31.1306
2895 | 852 | 796 | 125 | 5.6 | 24.3 | 42.1576 | 214.8118 | 15.755 | 43.6708 | 42.5846 | 14.8131 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 31.2786
2896 | 875 | 651 | 82 | 5.6 | 24.3 | 42.1576 | 208.6455 | 16.448 | 27.242 | 42.5825 | 14.8124 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 31.9709
2897 | 815 | 457 | 66 | 5.8 | 23.7 | 42.1577 | 168.0526 | 18.3865 | 5.2172 | 42.5805 | 14.8587 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.9559
2898 | 645 | 241 | 52 | 5.4 | 21.8 | 42.1578 | 87.8571 | 4.6235 | 0 | 42.5786 | 14.9999 | 0 | 0 | 100% | 0 | 16.6239 | 63.4% | 0 | 36.9584
2899 | 80 | 34 | 22 | 5 | 19.1 | 0 | 11.5673 | 0 | 0 | 42.5759 | 15.175 | 0 | 41.0845 | 97% | 0 | 22.8074 | 26.91% | 0 | 35.9264
2900 | 0 | 0 | 0 | 5.6 | 16.3 | 0 | 0 | 0 | 0 | 66.9417 | 25.8903 | 0 | 66.5174 | 92% | 0 | 10.5687 | 10% | 0 | 33.5382
2901 | 0 | 0 | 0 | 5.2 | 14.7 | 0 | 0 | 0 | 0 | 85.1512 | 33.9591 | 0 | 83.8399 | 86% | 0 | 0 | 10% | 0 | 31.2286
2902 | 0 | 0 | 0 | 4.4 | 14.1 | 0 | 0 | 0 | 0 | 80.6437 | 32.0143 | 0 | 78.8055 | 80% | 0 | 0 | 10% | 0 | 29.3106
2903 | 0 | 0 | 0 | 4.4 | 13.5 | 0 | 0 | 0 | 0 | 78.0233 | 30.8601 | 0 | 76.2112 | 74% | 0 | 0 | 10% | 0 | 28.1315
2904 | 0 | 0 | 0 | 3.1 | 13.8 | 0 | 0 | 0 | 0 | 77.1531 | 30.451 | 0 | 75.3731 | 69% | 0 | 0 | 10% | 0 | 27.7042
2905 | 0 | 0 | 0 | 2.1 | 13.7 | 0 | 0 | 0 | 0 | 77.0249 | 30.3993 | 0 | 75.2731 | 63% | 0 | 0 | 10% | 0 | 27.6389
2906 | 0 | 0 | 0 | 2.1 | 13.3 | 0 | 0 | 0 | 0 | 78.786 | 31.2181 | 0 | 77.0835 | 58% | 0 | 0 | 10% | 0 | 28.4455
2907 | 0 | 0 | 0 | 2.3 | 13.2 | 0 | 0 | 0 | 0 | 87.2469 | 34.9344 | 0 | 86.4887 | 51% | 0 | 0 | 10% | 0 | 32.1451
2908 | 0 | 0 | 0 | 2.4 | 13.6 | 0 | 0 | 0 | 0 | 95.3136 | 38.3271 | 0 | 96.3315 | 44% | 0 | 0 | 10% | 0 | 35.5546
2909 | 0 | 0 | 0 | 2.4 | 13.3 | 0 | 0 | 0 | 0 | 102.1737 | 41.2299 | 0 | 104.2986 | 36% | 0 | 0 | 10% | 0 | 38.5277
2910 | 23 | 25 | 22 | 2.7 | 14.5 | 0 | 1.7258 | 0 | 0 | 105.6977 | 42.6337 | 0 | 108.1959 | 28% | 0 | 0 | 10% | 0 | 40.0255
2911 | 218 | 165 | 103 | 4.1 | 15.2 | 0 | 44.7474 | 1.8698 | 0 | 104.2299 | 41.9679 | 0 | 106.0173 | 20% | 0 | 0 | 10% | 0 | 41.3265
2912 | 426 | 335 | 138 | 2.2 | 18.3 | 70.3512 | 17.7084 | 14.4788 | 0 | 74.0221 | 28.789 | 10.4014 | 13.4713 | 20% | 0 | 0 | 10% | 0 | 41.8112
2913 | 574 | 547 | 193 | 6.1 | 20.1 | 135.3859 | 0 | 35.0302 | 0 | 43.4059 | 15.4557 | 92.3796 | 0 | 27% | 6.5498 | 0 | 18.91% | 0 | 42.2892
2914 | 762 | 771 | 190 | 6.7 | 21.5 | 197.9289 | 0 | 54.2865 | 2.9613 | 42.5387 | 15.0065 | 155.7561 | 0 | 39% | 25 | 0 | 52.91% | 0 | 42.0813
2915 | 522 | 745 | 290 | 7.2 | 22.3 | 133.8521 | 0 | 52.9719 | 3.6184 | 42.5628 | 14.9584 | 92.5658 | 0 | 46% | 25 | 0 | 86.91% | 0 | 41.2791
2916 | 326 | 752 | 435 | 6.8 | 22.9 | 77.5509 | 0 | 28.829 | 26.9652 | 42.5696 | 14.9163 | 35.9757 | 0 | 48% | 2.2737 | 0 | 90% | 0 | 40.3316
2917 | 141 | 589 | 446 | 7.1 | 23.2 | 0 | 45.7282 | 26.6304 | 13.6497 | 42.5681 | 14.8929 | 0 | 40.6298 | 45% | 0 | 0 | 90% | 0 | 39.753
2918 | 27 | 415 | 384 | 7.3 | 21.8 | 0 | 8.6252 | 21.5576 | 0 | 42.5629 | 14.9944 | 0 | 40.6391 | 42% | 0 | 5.6812 | 80.91% | 0 | 39.5304
2919 | 13 | 312 | 298 | 8.3 | 20.8 | 0 | 4.0257 | 13.7717 | 0 | 42.5553 | 15.0598 | 0 | 40.6488 | 39% | 0 | 12.7908 | 60.45% | 0 | 38.9074
2920 | 23 | 281 | 263 | 8.5 | 19.7 | 0 | 6.7776 | 11.5027 | 0 | 42.5473 | 15.1278 | 0 | 40.6558 | 36% | 0 | 15.0225 | 36.41% | 0 | 38.9274
2921 | 110 | 272 | 220 | 7.1 | 19.2 | 0 | 29.4512 | 11.1428 | 0 | 42.5387 | 15.1556 | 0 | 40.6604 | 33% | 0 | 16.4369 | 10.11% | 0 | 40.0003
2922 | 93 | 161 | 134 | 5.7 | 18.5 | 0 | 20.3483 | 2.9411 | 0 | 105.1169 | 42.0867 | 0 | 108.3851 | 25% | 0 | 0 | 10.11% | 0 | 42.1989
2923 | 38 | 40 | 34 | 4.8 | 17.3 | 0 | 5.6679 | 0 | 0 | 105.7639 | 42.4492 | 0 | 108.6682 | 17% | 0 | 0 | 10.11% | 0 | 39.7344
2924 | 0 | 0 | 0 | 3.4 | 15.4 | 0 | 0 | 0 | 0 | 97.3268 | 39.052 | 0 | 98.0453 | 10% | 0 | 0 | 10.11% | 0 | 36.4451
2925 | 0 | 0 | 0 | 3.8 | 14.8 | 0 | 0 | 0 | 0 | 92.2353 | 36.9523 | 0 | 91.7585 | 3% | 0 | 0 | 10.11% | 0 | 34.3936
2926 | 0 | 0 | 0 | 4.4 | 14.6 | 0 | 0 | 0 | 0 | 41.5199 | 16.6001 | 0 | 40.8759 | 0% | 0 | 0 | 10.11% | 0 | 14.1205
2927 | 0 | 0 | 0 | 3.1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.11% | 0 | -2.414
2928 | 0 | 0 | 0 | 2.3 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.11% | 0 | -2.3895
2929 | 0 | 0 | 0 | 1.5 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.11% | 0 | -2.3654
2930 | 0 | 0 | 0 | 1.2 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.11% | 0 | -2.3418
2931 | 0 | 0 | 0 | 0.8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.11% | 0 | -2.3186
2932 | 0 | 0 | 0 | 1.2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.11% | 0 | -2.2958
2933 | 0 | 0 | 0 | 1.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.11% | 0 | -2.2736
2934 | 105 | 27 | 15 | 2.4 | 11 | 0 | 8.4734 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.11% | 0 | -2.2516
2935 | 540 | 190 | 49 | 2.9 | 13.3 | 70.0331 | 17.9925 | 1.4369 | 0 | 0 | 0 | 66.5705 | 0 | 5% | 0 | 0 | 10.11% | 0 | 0.0812
2936 | 788 | 419 | 71 | 4.2 | 15.4 | 173.3432 | 2.98e-14 | 20.2017 | 0 | 0 | 0 | 169.3257 | 0 | 18% | 0 | 0 | 10.11% | 0 | 18.2685
2937 | 814 | 611 | 104 | 3.3 | 17.5 | 202.9794 | 0 | 39.8835 | 0 | 0 | 0 | 200.7286 | 0 | 33% | 0 | 0 | 10.11% | 0 | 37.6543
2938 | 924 | 797 | 91 | 1.4 | 19.7 | 248.3897 | 0 | 59.4922 | 0 | 42.4943 | 0 | 206.4435 | 0 | 49% | 18.2679 | 0 | 34.95% | 0 | 38.0241
2939 | 948 | 925 | 101 | 1.7 | 21.4 | 264.546 | 0 | 70.0281 | 2.8093 | 0 | 0 | 262.8968 | 0 | 68% | 25 | 0 | 68.95% | 0 | 42.1712
2940 | 861 | 956 | 157 | 2.2 | 22.3 | 243.0835 | 0 | 48.7924 | 26.3076 | 42.5607 | 10.4275 | 201.5397 | 0 | 83% | 15.475 | 0 | 90% | 0 | 40.8711
2941 | 860 | 953 | 150 | 4.1 | 22.5 | 242.1648 | 0 | 26.1483 | 48.9517 | 42.5676 | 14.9452 | 200.4378 | 0 | 98% | 0 | 0 | 90% | 0 | 40.3144
2942 | 902 | 937 | 138 | 5.9 | 22.1 | 65.5253 | 212.4191 | 24.4105 | 49.4367 | 42.5753 | 14.9776 | 24.0497 | 0 | 100% | 0 | 0 | 90% | 0 | 39.933
2943 | 481 | 603 | 222 | 7.1 | 19.9 | 42.1525 | 95.7657 | 23.6031 | 19.4786 | 42.5738 | 15.1248 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.4394
2944 | 427 | 436 | 162 | 6.9 | 18.9 | 42.1581 | 70.8974 | 23.4314 | 3.5416 | 42.572 | 15.1856 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.3288
2945 | 433 | 332 | 114 | 5.3 | 18.6 | 42.1581 | 61.0317 | 14.7893 | 0 | 42.5703 | 15.2025 | 0 | 0 | 100% | 0 | 9.1265 | 75.4% | 0 | 39.83
2946 | 449 | 225 | 86 | 4 | 18.8 | 42.1581 | 41.8813 | 4.3362 | 0 | 42.5686 | 15.1902 | 0 | 0 | 100% | 0 | 21.2335 | 41.42% | 0 | 41.4717
2947 | 1 | 11 | 11 | 4.8 | 16.1 | 0 | 0.15151 | 0 | 0 | 57.7504 | 21.8429 | 0 | 57.4208 | 96% | 0 | 19.6399 | 10% | 0 | 39.428
2948 | 0 | 0 | 0 | 4.2 | 14.3 | 0 | 0 | 0 | 0 | 97.8595 | 39.348 | 0 | 99.2208 | 88% | 0 | 0 | 10% | 0 | 36.6459
2949 | 0 | 0 | 0 | 3.6 | 14.1 | 0 | 0 | 0 | 0 | 92.5148 | 37.1119 | 0 | 91.5439 | 82% | 0 | 0 | 10% | 0 | 34.7579
2950 | 0 | 0 | 0 | 3.4 | 14.1 | 0 | 0 | 0 | 0 | 88.1148 | 35.2463 | 0 | 86.1193 | 75% | 0 | 0 | 10% | 0 | 32.9101
2951 | 0 | 0 | 0 | 5.2 | 13.8 | 0 | 0 | 0 | 0 | 84.4265 | 33.7102 | 0 | 81.9101 | 69% | 0 | 0 | 10% | 0 | 31.3182
2952 | 0 | 0 | 0 | 4.4 | 13.8 | 0 | 0 | 0 | 0 | 82.287 | 32.785 | 0 | 79.7332 | 63% | 0 | 0 | 10% | 0 | 30.3199
2953 | 0 | 0 | 0 | 4.1 | 13.6 | 0 | 0 | 0 | 0 | 81.5168 | 32.4446 | 0 | 79.1329 | 57% | 0 | 0 | 10% | 0 | 29.917
2954 | 0 | 0 | 0 | 4.1 | 12.8 | 0 | 0 | 0 | 0 | 81.4822 | 32.4749 | 0 | 79.2243 | 51% | 0 | 0 | 10% | 0 | 29.9011
2955 | 0 | 0 | 0 | 3.1 | 12.1 | 0 | 0 | 0 | 0 | 83.1542 | 33.2724 | 0 | 81.048 | 45% | 0 | 0 | 10% | 0 | 30.6615
2956 | 0 | 0 | 0 | 2.7 | 12.3 | 0 | 0 | 0 | 0 | 84.2429 | 33.7194 | 0 | 82.4048 | 39% | 0 | 0 | 10% | 0 | 31.0812
2957 | 0 | 0 | 0 | 3 | 12.4 | 0 | 0 | 0 | 0 | 90.6235 | 36.4112 | 0 | 90.1691 | 32% | 0 | 0 | 10% | 0 | 33.7485
2958 | 0 | 7 | 7 | 3 | 12.5 | 0 | 0 | 0 | 0 | 97.8329 | 39.4515 | 0 | 98.8472 | 25% | 0 | 0 | 10% | 0 | 36.801
2959 | 16 | 90 | 84 | 2.8 | 13 | 0 | 3.3149 | 0 | 0 | 102.6531 | 41.4533 | 0 | 104.4538 | 17% | 0 | 0 | 10% | 0 | 38.8507
2960 | 4 | 174 | 171 | 2.2 | 13.9 | 0 | 1.0449 | 4.5011 | 0 | 92.273 | 37.0261 | 0 | 91.6823 | 10% | 0 | 0 | 10% | 0 | 39.0092
2961 | 53 | 313 | 278 | 1.9 | 15.2 | 0 | 15.4011 | 14.9663 | 0 | 68.2606 | 26.4284 | 0 | 65.6317 | 6% | 0 | 0 | 10% | 0 | 38.9267
2962 | 18 | 372 | 352 | 2.8 | 15.8 | 0 | 5.5295 | 18.3537 | 0 | 59.682 | 22.653 | 0 | 57.0576 | 1% | 0 | 0 | 10% | 0 | 38.5234
2963 | 398 | 769 | 408 | 4.4 | 18 | 80.8696 | 20.5339 | 49.167 | 7.951 | 42.3523 | 15.1594 | 45.3323 | 7.3584 | 4% | 25 | 0 | 44% | 0 | 37.8108
2964 | 843 | 1004 | 217 | 6.5 | 18.8 | 234.1002 | 0 | 48.3905 | 26.7095 | 42.5027 | 15.1667 | 190.6495 | 0 | 18% | 25 | 0 | 78% | 0 | 36.0762
2965 | 898 | 992 | 150 | 6 | 19.3 | 251.9853 | 0 | 31.3213 | 43.7787 | 42.5913 | 15.1681 | 210.2602 | 0 | 34% | 8.8235 | 0 | 90% | 0 | 34.9839
2966 | 918 | 935 | 117 | 6.3 | 19.6 | 253.5581 | 0 | 21.9503 | 51.856 | 42.6007 | 15.1529 | 211.8448 | 0 | 50% | 0 | 0 | 90% | 0 | 34.3856
2967 | 895 | 824 | 112 | 7.2 | 19 | 237.6826 | 0 | 21.574 | 40.425 | 42.6055 | 15.1917 | 195.9598 | 0 | 64% | 0 | 0 | 90% | 0 | 34.1669
2968 | 839 | 659 | 107 | 6.8 | 18.5 | 210.1366 | 0 | 21.6697 | 22.7373 | 42.6071 | 15.2215 | 168.3406 | 0 | 76% | 0 | 0 | 90% | 0 | 34.5271
2969 | 718 | 454 | 101 | 6.7 | 17.8 | 159.1973 | 0 | 21.2811 | 2.0939 | 42.6072 | 15.2616 | 117.3541 | 0 | 85% | 0 | 0 | 90% | 0 | 35.6385
2970 | 70 | 123 | 97 | 6 | 15.9 | 0 | 15.3803 | 0.99938 | 0 | 42.6052 | 15.3605 | 0 | 41.1482 | 82% | 0 | 24.0869 | 51.46% | 0 | 38.3722
2971 | 0 | 27 | 27 | 4.3 | 15.1 | 0 | 0 | 0 | 0 | 42.6021 | 15.3974 | 0 | 41.1039 | 79% | 0 | 24.7867 | 11.8% | 0 | 37.2043
2972 | 0 | 0 | 0 | 2.4 | 15 | 0 | 0 | 0 | 0 | 94.4313 | 37.8651 | 0 | 96.1265 | 72% | 0 | 0 | 11.8% | 0 | 34.8676
2973 | 0 | 0 | 0 | 1.5 | 14.3 | 0 | 0 | 0 | 0 | 88.3552 | 35.3334 | 0 | 87.8232 | 66% | 0 | 0 | 11.8% | 0 | 32.5501
2974 | 0 | 0 | 0 | 1.3 | 13.4 | 0 | 0 | 0 | 0 | 83.1738 | 33.206 | 0 | 81.4273 | 59% | 0 | 0 | 11.8% | 0 | 30.4788
2975 | 0 | 0 | 0 | 0.8 | 12.9 | 0 | 0 | 0 | 0 | 80.1995 | 31.8788 | 0 | 78.4048 | 54% | 0 | 0 | 11.8% | 0 | 29.1428
2976 | 0 | 0 | 0 | 0.9 | 12.4 | 0 | 0 | 0 | 0 | 78.0581 | 30.9344 | 0 | 76.2545 | 48% | 0 | 0 | 11.8% | 0 | 28.1886
2977 | 0 | 0 | 0 | 1.2 | 12 | 0 | 0 | 0 | 0 | 76.9891 | 30.4736 | 0 | 75.1922 | 43% | 0 | 0 | 11.8% | 0 | 27.718
2978 | 0 | 0 | 0 | 1.1 | 12 | 0 | 0 | 0 | 0 | 77.1201 | 30.5335 | 0 | 75.3441 | 37% | 0 | 0 | 11.8% | 0 | 27.7681
2979 | 0 | 0 | 0 | 1.1 | 12 | 0 | 0 | 0 | 0 | 77.961 | 30.9141 | 0 | 76.213 | 31% | 0 | 0 | 11.8% | 0 | 28.1394
2980 | 0 | 0 | 0 | 1.1 | 12.1 | 0 | 0 | 0 | 0 | 77.396 | 30.6545 | 0 | 75.6505 | 26% | 0 | 0 | 11.8% | 0 | 27.8736
2981 | 0 | 0 | 0 | 1.4 | 12 | 0 | 0 | 0 | 0 | 80.5911 | 32.1113 | 0 | 78.9109 | 20% | 0 | 0 | 11.8% | 0 | 29.3195
2982 | 143 | 36 | 15 | 2.1 | 14 | 0 | 13.111 | 0 | 0 | 86.8028 | 34.7004 | 0 | 85.9406 | 14% | 0 | 0 | 11.8% | 0 | 31.8942
2983 | 647 | 212 | 44 | 1.1 | 17.4 | 88.8121 | 22.1068 | 1.9158 | 0 | 85.2078 | 33.8127 | 18.1732 | 16.0783 | 14% | 0 | 0 | 11.8% | 0 | 34.0369
2984 | 810 | 425 | 60 | 0.8 | 20.4 | 181.411 | 2.98e-14 | 19.5995 | 0 | 47.891 | 17.2991 | 133.3161 | 0 | 24% | 0 | 0 | 11.8% | 0 | 34.866
2985 | 897 | 628 | 67 | 0.8 | 22.8 | 227.1071 | -2.98e-14 | 40.0911 | 0 | 46.0269 | 16.3433 | 181.3253 | 0 | 37% | 18.9696 | 0 | 37.6% | 0 | 35.0165
2986 | 931 | 793 | 76 | 3.1 | 23.9 | 249.8265 | 0 | 47.7893 | 9.8657 | 42.5849 | 14.8448 | 207.6002 | 0 | 52% | 25 | 0 | 71.6% | 0 | 34.965
2987 | 920 | 908 | 103 | 6.6 | 22.9 | 252.7828 | 0 | 35.6477 | 34.6187 | 42.5955 | 14.9254 | 210.5912 | 0 | 68% | 13.5287 | 0 | 90% | 0 | 34.3157
2988 | 910 | 980 | 130 | 5.9 | 23 | 255.3207 | 0 | 18.6299 | 56.4701 | 42.5988 | 14.9191 | 213.057 | 0 | 83% | 0 | 0 | 90% | 0 | 32.9368
2989 | 903 | 997 | 149 | 6 | 23.6 | 253.7469 | 0 | 14.8603 | 60.2397 | 42.6014 | 14.8737 | 211.4798 | 0 | 99% | 0 | 0 | 90% | 0 | 32.1265
2990 | 700 | 848 | 218 | 5.6 | 23.8 | 61.0501 | 151.4391 | 16.4652 | 48.1732 | 42.6028 | 14.8588 | 19.5755 | 0 | 100% | 0 | 0 | 90% | 0 | 31.9071
2991 | 860 | 820 | 131 | 4.1 | 25.1 | 42.1524 | 217.4844 | 16.6188 | 43.232 | 42.6006 | 14.7546 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.0838
2992 | 829 | 658 | 109 | 5.4 | 25 | 42.1576 | 195.0419 | 17.4032 | 25.6003 | 42.5981 | 14.7619 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.8756
2993 | 724 | 449 | 92 | 4.8 | 23.9 | 42.1576 | 143.8869 | 18.9363 | 3.3793 | 42.5956 | 14.8486 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.4955
2994 | 578 | 239 | 63 | 4.9 | 22.2 | 42.1578 | 73.442 | 4.3438 | 0 | 42.5933 | 14.9765 | 0 | 0 | 100% | 0 | 17.7015 | 61.68% | 0 | 37.7328
2995 | 222 | 56 | 26 | 3.2 | 20 | 0 | 33.9721 | 0 | 0 | 42.9059 | 15.2534 | 0 | 41.4109 | 97% | 0 | 24.1644 | 23.02% | 0 | 37.3609
2996 | 0 | 0 | 0 | 2.4 | 17.3 | 0 | 0 | 0 | 0 | 75.4409 | 29.4923 | 0 | 75.8163 | 91% | 0 | 8.1341 | 10% | 0 | 34.699
2997 | 0 | 0 | 0 | 1 | 15.7 | 0 | 0 | 0 | 0 | 87.7647 | 34.9947 | 0 | 86.6463 | 85% | 0 | 0 | 10% | 0 | 32.3677
2998 | 0 | 0 | 0 | 1.1 | 14.6 | 0 | 0 | 0 | 0 | 83.3741 | 33.2187 | 0 | 81.2958 | 79% | 0 | 0 | 10% | 0 | 30.6258
2999 | 0 | 0 | 0 | 0.4 | 14.5 | 0 | 0 | 0 | 0 | 81.1322 | 32.2119 | 0 | 79.115 | 73% | 0 | 0 | 10% | 0 | 29.5677
3000 | 0 | 0 | 0 | 0.7 | 15 | 0 | 0 | 0 | 0 | 80.3878 | 31.8435 | 0 | 78.4576 | 67% | 0 | 0 | 10% | 0 | 29.1631
3001 | 0 | 0 | 0 | 1 | 15.7 | 0 | 0 | 0 | 0 | 80.7515 | 31.9666 | 0 | 78.8911 | 61% | 0 | 0 | 10% | 0 | 29.2609
3002 | 0 | 0 | 0 | 0.5 | 15.4 | 0 | 0 | 0 | 0 | 82.7094 | 32.8797 | 0 | 80.9281 | 55% | 0 | 0 | 10% | 0 | 30.154
3003 | 0 | 0 | 0 | 1.3 | 15.7 | 0 | 0 | 0 | 0 | 91.5462 | 36.5951 | 0 | 91.6209 | 49% | 0 | 0 | 10% | 0 | 33.8457
3004 | 0 | 0 | 0 | 0.7 | 14.6 | 0 | 0 | 0 | 0 | 101.0427 | 40.6656 | 0 | 102.9539 | 41% | 0 | 0 | 10% | 0 | 37.9566
3005 | 0 | 0 | 0 | 2 | 15.4 | 0 | 0 | 0 | 0 | 108.8266 | 43.8671 | 0 | 111.9469 | 33% | 0 | 0 | 10% | 0 | 41.2474
3006 | 121 | 36 | 18 | 2 | 15.7 | 0 | 11.7368 | 0 | 0 | 111.7315 | 45.0533 | 0 | 114.8995 | 24% | 0 | 0 | 10% | 0 | 42.5467
3007 | 594 | 209 | 52 | 1.2 | 18.8 | 80.7092 | 20.0844 | 1.881 | 0 | 105.9518 | 42.4083 | 0 | 29.3252 | 22% | 0 | 0 | 10% | 0 | 42.6992
3008 | 779 | 423 | 72 | 1.6 | 18.4 | 173.4469 | 0 | 19.7581 | 0 | 65.6037 | 25.0641 | 108.6882 | 0 | 30% | 0 | 0 | 10% | 0 | 42.7956
3009 | 860 | 623 | 86 | 1.9 | 19.3 | 216.3874 | -2.98e-14 | 40.2947 | 0 | 44.6904 | 16.0323 | 172.6225 | 0 | 43% | 11.493 | 0 | 25.63% | 0 | 42.4359
3010 | 904 | 791 | 96 | 3 | 20.7 | 241.8075 | 0 | 55.424 | 2.7221 | 42.5782 | 15.0744 | 200.1693 | 0 | 58% | 25 | 0 | 59.63% | 0 | 42.852
3011 | 937 | 917 | 97 | 3 | 23.6 | 260.6755 | 0 | 52.2855 | 18.5098 | 42.5887 | 14.8693 | 218.9621 | 0 | 74% | 22.3305 | 0 | 90% | 0 | 41.9786
3012 | 941 | 986 | 108 | 2.7 | 25.6 | 267.1277 | 0 | 29.2389 | 45.8611 | 42.5941 | 14.7113 | 225.3214 | 0 | 91% | 0 | 0 | 90% | 0 | 41.0229
3013 | 935 | 999 | 122 | 5.6 | 26.2 | 165.8311 | 112.5556 | 25.115 | 49.985 | 42.5982 | 14.6629 | 124.011 | 0 | 100% | 0 | 0 | 90% | 0 | 40.5214
3014 | 869 | 929 | 151 | 5.7 | 26.4 | 42.1519 | 228.6018 | 24.9964 | 45.8995 | 42.5978 | 14.6458 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.3523
3015 | 635 | 760 | 248 | 6.4 | 25.9 | 42.1575 | 145.8218 | 24.3334 | 29.586 | 42.5954 | 14.687 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.7306
3016 | 611 | 617 | 209 | 5.5 | 25 | 42.1576 | 129.0958 | 24.2962 | 15.4298 | 42.593 | 14.7602 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.7668
3017 | 440 | 394 | 174 | 5 | 23.9 | 42.1576 | 63.5689 | 18.9201 | 0 | 42.5907 | 14.8469 | 0 | 0 | 100% | 0 | 6.4722 | 79.64% | 0 | 40.9498
3018 | 377 | 243 | 126 | 4 | 22.4 | 42.1578 | 24.0591 | 5.8164 | 0 | 42.5885 | 14.96 | 0 | 0 | 100% | 0 | 21.7141 | 44.9% | 0 | 43.2014
3019 | 66 | 50 | 38 | 3 | 19.8 | 0 | 10.1494 | 0 | 0 | 56.1288 | 20.8781 | 0 | 55.4171 | 96% | 0 | 21.8137 | 10% | 0 | 40.6285
3020 | 0 | 0 | 0 | 1.7 | 17.6 | 0 | 0 | 0 | 0 | 99.7087 | 39.8852 | 0 | 101.7481 | 88% | 0 | 0 | 10% | 0 | 37.101
3021 | 0 | 0 | 0 | 1 | 16.6 | 0 | 0 | 0 | 0 | 93.1994 | 37.2339 | 0 | 92.3476 | 82% | 0 | 0 | 10% | 0 | 34.8899
3022 | 0 | 0 | 0 | 0.5 | 15.9 | 0 | 0 | 0 | 0 | 88.9162 | 35.4678 | 0 | 87.0127 | 75% | 0 | 0 | 10% | 0 | 33.1505
3023 | 0 | 0 | 0 | 0.3 | 15.2 | 0 | 0 | 0 | 0 | 86.2545 | 34.3916 | 0 | 83.9886 | 69% | 0 | 0 | 10% | 0 | 32.0225
3024 | 0 | 0 | 0 | 0.5 | 14.4 | 0 | 0 | 0 | 0 | 85.1831 | 33.9912 | 0 | 82.9029 | 63% | 0 | 0 | 10% | 0 | 31.5606
3025 | 0 | 0 | 0 | 0.7 | 13.3 | 0 | 0 | 0 | 0 | 84.8879 | 33.9332 | 0 | 82.7037 | 56% | 0 | 0 | 10% | 0 | 31.4512
3026 | 0 | 0 | 0 | 0.9 | 12.7 | 0 | 0 | 0 | 0 | 86.4776 | 34.6375 | 0 | 84.7101 | 50% | 0 | 0 | 10% | 0 | 32.1139
3027 | 0 | 0 | 0 | 0.9 | 13.4 | 0 | 0 | 0 | 0 | 93.1686 | 37.4341 | 0 | 92.9516 | 43% | 0 | 0 | 10% | 0 | 34.8821
3028 | 0 | 0 | 0 | 1.2 | 13.2 | 0 | 0 | 0 | 0 | 102.256 | 41.2704 | 0 | 103.7316 | 35% | 0 | 0 | 10% | 0 | 38.7376
3029 | 0 | 0 | 0 | 1.8 | 11.7 | 0 | 0 | 0 | 0 | 108.845 | 44.1234 | 0 | 111.3208 | 27% | 0 | 0 | 10% | 0 | 41.6543
3030 | 68 | 36 | 18 | 1.3 | 12.2 | 0 | 6.9487 | 0 | 0 | 112.4639 | 45.6055 | 0 | 115.2366 | 18% | 0 | 0 | 10% | 0 | 43.2185
3031 | 577 | 219 | 56 | 0.7 | 13.4 | 78.3639 | 19.76 | 2.0683 | 0 | 106.038 | 42.8511 | 0 | 31.3194 | 16% | 0 | 0 | 10% | 0 | 43.3609
3032 | 768 | 429 | 79 | 0.7 | 17.3 | 171.3725 | 0 | 20.0354 | 0 | 66.3571 | 25.4623 | 106.0295 | 0 | 24% | 0 | 0 | 10% | 0 | 43.4895
3033 | 914 | 643 | 70 | 1.9 | 21 | 231.1302 | 0 | 41.3497 | 0 | 45.1916 | 16.1288 | 186.9106 | 0 | 38% | 11.0748 | 0 | 25.06% | 0 | 43.8754
3034 | 941 | 810 | 86 | 3.3 | 22.6 | 252.3438 | 0 | 56.3054 | 2.9879 | 42.5834 | 14.9434 | 210.8911 | 0 | 54% | 25 | 0 | 59.06% | 0 | 43.5067
3035 | 925 | 923 | 111 | 3.7 | 24.1 | 256.5806 | 0 | 53.1931 | 17.6623 | 42.5938 | 14.8322 | 215.1059 | 0 | 70% | 22.7488 | 0 | 90% | 0 | 42.4682
3036 | 948 | 994 | 109 | 4.1 | 25 | 268.1921 | 0 | 29.7556 | 45.3444 | 42.5984 | 14.7621 | 226.5442 | 0 | 87% | 0 | 0 | 90% | 0 | 41.5796
3037 | 935 | 995 | 116 | 4.5 | 25 | 222.3189 | 48.4575 | 25.1954 | 49.9046 | 42.6016 | 14.7632 | 180.4884 | 0 | 100% | 0 | 0 | 90% | 0 | 41.1533
3038 | 940 | 937 | 98 | 4.6 | 25.8 | 42.1519 | 251.7042 | 25.8806 | 46.1769 | 42.6021 | 14.6976 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2884
3039 | 887 | 825 | 116 | 4.1 | 26.4 | 42.1574 | 225.9113 | 25.7032 | 34.2605 | 42.5996 | 14.6464 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.0597
3040 | 776 | 638 | 121 | 4.7 | 25.5 | 42.1575 | 179.3712 | 25.9198 | 14.9592 | 42.5971 | 14.7205 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.3506
3041 | 704 | 450 | 102 | 4.9 | 23.8 | 42.1577 | 138.6002 | 22.3098 | 0 | 42.5947 | 14.8559 | 0 | 0 | 100% | 0 | 5.0732 | 81.88% | 0 | 42.9496
3042 | 507 | 235 | 77 | 4.6 | 21.4 | 42.1579 | 57.0713 | 4.4249 | 0 | 42.5923 | 15.0323 | 0 | 0 | 100% | 0 | 23.9536 | 43.56% | 0 | 44.122
3043 | 120 | 49 | 30 | 2.9 | 19 | 0 | 18.543 | 0 | 0 | 58.7608 | 22.0576 | 0 | 58.2887 | 96% | 0 | 20.9732 | 10% | 0 | 40.968
3044 | 0 | 0 | 0 | 2 | 17.4 | 0 | 0 | 0 | 0 | 101.2357 | 40.5396 | 0 | 103.4278 | 88% | 0 | 0 | 10% | 0 | 37.801
3045 | 0 | 0 | 0 | 0.8 | 16.7 | 0 | 0 | 0 | 0 | 95.7475 | 38.2965 | 0 | 95.2172 | 81% | 0 | 0 | 10% | 0 | 36.0004
3046 | 0 | 0 | 0 | 0.7 | 16.4 | 0 | 0 | 0 | 0 | 90.8279 | 36.2421 | 0 | 89.0887 | 74% | 0 | 0 | 10% | 0 | 33.9949
3047 | 0 | 0 | 0 | 0.8 | 16.3 | 0 | 0 | 0 | 0 | 87.7856 | 34.9645 | 0 | 85.559 | 68% | 0 | 0 | 10% | 0 | 32.6729
3048 | 0 | 0 | 0 | 0.9 | 15.4 | 0 | 0 | 0 | 0 | 86.5421 | 34.4998 | 0 | 84.267 | 62% | 0 | 0 | 10% | 0 | 32.1462
3049 | 0 | 0 | 0 | 1.5 | 14.3 | 0 | 0 | 0 | 0 | 86.244 | 34.444 | 0 | 84.0726 | 55% | 0 | 0 | 10% | 0 | 32.0364
3050 | 0 | 0 | 0 | 1.5 | 14.3 | 0 | 0 | 0 | 0 | 87.7371 | 35.074 | 0 | 85.9813 | 49% | 0 | 0 | 10% | 0 | 32.623
3051 | 0 | 0 | 0 | 0.7 | 14.3 | 0 | 0 | 0 | 0 | 94.576 | 37.9733 | 0 | 94.4171 | 42% | 0 | 0 | 10% | 0 | 35.4915
3052 | 0 | 0 | 0 | 1 | 13.6 | 0 | 0 | 0 | 0 | 103.0611 | 41.5841 | 0 | 104.4305 | 34% | 0 | 0 | 10% | 0 | 39.1207
3053 | 0 | 0 | 0 | 1.3 | 12.6 | 0 | 0 | 0 | 0 | 109.3251 | 44.27 | 0 | 111.6164 | 26% | 0 | 0 | 10% | 0 | 41.8641
3054 | 117 | 42 | 25 | 1.2 | 12.8 | 0 | 12.5478 | 0 | 0 | 112.5575 | 45.6072 | 0 | 115.0993 | 17% | 0 | 0 | 10% | 0 | 43.2758
3055 | 326 | 173 | 92 | 0.7 | 17.7 | 0 | 57.7552 | 2.1571 | 0 | 109.7983 | 44.0891 | 0 | 111.4371 | 8% | 0 | 0 | 10% | 0 | 44.0025
3056 | 653 | 437 | 136 | 3.1 | 22.5 | 141.9808 | 0 | 20.555 | 0 | 67.1042 | 25.4344 | 73.7983 | 0 | 14% | 0 | 0 | 10% | 0 | 44.2652
3057 | 227 | 435 | 291 | 4.2 | 24.4 | 0 | 52.7067 | 24.0165 | 0 | 59.5025 | 21.9744 | 0 | 56.2952 | 10% | 0 | 0 | 10% | 0 | 44.7034
3058 | 423 | 594 | 248 | 4.2 | 25.1 | 102.4339 | 0 | 38.7239 | 0 | 43.4102 | 15.087 | 57.8217 | 0 | 14% | 7.8236 | 0 | 20.64% | 0 | 44.6512
3059 | 939 | 927 | 101 | 5.6 | 26.7 | 258.9574 | 0 | 56.1131 | 14.2567 | 42.5508 | 14.6043 | 215.8565 | 0 | 30% | 25 | 0 | 54.64% | 0 | 42.9755
3060 | 820 | 929 | 159 | 6.4 | 28.2 | 227.3671 | 0 | 55.0754 | 15.6502 | 42.5872 | 14.4869 | 186.1465 | 0 | 44% | 25 | 0 | 88.64% | 0 | 42.0632
3061 | 703 | 895 | 226 | 6.4 | 29.1 | 192.6984 | 0 | 30.6825 | 37.1364 | 42.5964 | 14.41 | 151.3123 | 0 | 56% | 0.99995 | 0 | 90% | 0 | 41.8934
3062 | 401 | 703 | 332 | 5 | 29.3 | 100.3446 | 0 | 28.435 | 21.0179 | 42.5991 | 14.3931 | 59.3587 | 0 | 60% | 0 | 0 | 90% | 0 | 41.4678
3063 | 867 | 830 | 131 | 5.1 | 30.1 | 231.4085 | 0 | 29.2737 | 29.7327 | 42.5975 | 14.3213 | 188.4281 | 0 | 74% | 0 | 0 | 90% | 0 | 41.0393
3064 | 789 | 657 | 129 | 6.8 | 30.4 | 196.9344 | 0 | 29.2602 | 12.1825 | 42.6003 | 14.2951 | 155.2038 | 0 | 85% | 0 | 0 | 90% | 0 | 41.2946
3065 | 723 | 453 | 94 | 8.2 | 30.1 | 160.0341 | 0 | 21.7708 | 0 | 42.6012 | 14.3225 | 118.085 | 0 | 94% | 0 | 6.081 | 80.27% | 0 | 42.4356
3066 | 445 | 216 | 65 | 8.6 | 28.6 | 69.8827 | 0 | 2.9591 | 0 | 44.6244 | 15.2705 | 26.2461 | 0 | 96% | 0 | 25 | 40.27% | 0 | 44.0159
3067 | 180 | 70 | 45 | 7.3 | 26.8 | 0 | 27.9483 | 0 | 0 | 65.6583 | 24.3475 | 0 | 65.8959 | 91% | 0 | 18.919 | 10% | 0 | 41.1739
3068 | 0 | 0 | 0 | 4.3 | 25.1 | 0 | 0 | 0 | 0 | 102.9045 | 40.5527 | 0 | 105.4823 | 83% | 0 | 0 | 10% | 0 | 37.8067
3069 | 0 | 0 | 0 | 3.3 | 23.4 | 0 | 0 | 0 | 0 | 96.5528 | 38.0891 | 0 | 96.3926 | 76% | 0 | 0 | 10% | 0 | 35.725
3070 | 0 | 0 | 0 | 4.7 | 22.5 | 0 | 0 | 0 | 0 | 91.8228 | 36.196 | 0 | 90.4452 | 69% | 0 | 0 | 10% | 0 | 33.9027
3071 | 0 | 0 | 0 | 5 | 22 | 0 | 0 | 0 | 0 | 88.7818 | 34.9623 | 0 | 86.7961 | 63% | 0 | 0 | 10% | 0 | 32.6535
3072 | 0 | 0 | 0 | 4.1 | 21.2 | 0 | 0 | 0 | 0 | 87.6046 | 34.5353 | 0 | 85.5144 | 56% | 0 | 0 | 10% | 0 | 32.1834
3073 | 0 | 0 | 0 | 5.1 | 20.9 | 0 | 0 | 0 | 0 | 87.3406 | 34.4493 | 0 | 85.3206 | 50% | 0 | 0 | 10% | 0 | 32.0562
3074 | 0 | 0 | 0 | 3.3 | 20.9 | 0 | 0 | 0 | 0 | 88.6627 | 35.0038 | 0 | 87.0078 | 44% | 0 | 0 | 10% | 0 | 32.5758
3075 | 0 | 0 | 0 | 3 | 20.5 | 0 | 0 | 0 | 0 | 95.3999 | 37.8677 | 0 | 95.2736 | 36% | 0 | 0 | 10% | 0 | 35.4124
3076 | 0 | 0 | 0 | 2.1 | 19.7 | 0 | 0 | 0 | 0 | 103.7084 | 41.3979 | 0 | 105.1063 | 29% | 0 | 0 | 10% | 0 | 38.9578
3077 | 0 | 0 | 0 | 3.1 | 19.8 | 0 | 0 | 0 | 0 | 110.5857 | 44.238 | 0 | 113.0154 | 20% | 0 | 0 | 10% | 0 | 41.8488
3078 | 9 | 26 | 25 | 1.8 | 19.8 | 0 | 1.0096 | 0 | 0 | 114.0159 | 45.658 | 0 | 116.7587 | 11% | 0 | 0 | 10% | 0 | 43.3396
3079 | 86 | 158 | 129 | 1.5 | 20.5 | 0 | 18.1663 | 2.0419 | 0 | 110.2995 | 44.0602 | 0 | 111.9877 | 3% | 0 | 0 | 10% | 0 | 43.8638
3080 | 401 | 405 | 215 | 1.2 | 22.9 | 66.3298 | 16.4047 | 18.4424 | 0 | 71.0923 | 27.1627 | 9.1188 | 12.5515 | 3% | 0 | 0 | 10% | 0 | 44.2365
3081 | 657 | 601 | 176 | 2 | 24.1 | 161.337 | 0 | 36.8324 | 0 | 44.1074 | 15.452 | 117.6481 | 0 | 11% | 5.879 | 0 | 18% | 0 | 44.5352
3082 | 809 | 766 | 136 | 1.7 | 25.2 | 214.9942 | 0 | 54.1168 | 0 | 45.6082 | 15.9744 | 170.6137 | 0 | 24% | 23.4288 | 0 | 49.86% | 0 | 44.298
3083 | 904 | 900 | 102 | 1.9 | 26.7 | 251.3323 | 0 | 56.1801 | 11.4797 | 42.6025 | 14.622 | 209.98 | 0 | 40% | 25 | 0 | 83.86% | 0 | 43.094
3084 | 947 | 977 | 89 | 2.1 | 28 | 269.1224 | 0 | 35.1075 | 39.9925 | 42.6087 | 14.512 | 227.8452 | 0 | 57% | 4.5157 | 0 | 90% | 0 | 42.1996
3085 | 777 | 937 | 201 | 3.7 | 28.4 | 217.2201 | 0 | 29.7353 | 40.907 | 42.6106 | 14.477 | 176.0445 | 0 | 70% | 0 | 0 | 90% | 0 | 41.7661
3086 | 778 | 886 | 189 | 3.9 | 28.8 | 213.7134 | 0 | 29.6626 | 36.136 | 42.6104 | 14.4414 | 172.1473 | 0 | 83% | 0 | 0 | 90% | 0 | 41.6804
3087 | 868 | 831 | 134 | 5.6 | 28.1 | 231.3032 | 0 | 27.0686 | 32.5241 | 42.6099 | 14.5035 | 189.3355 | 0 | 97% | 0 | 0 | 90% | 0 | 41.3703
3088 | 839 | 662 | 102 | 5.2 | 28.3 | 84.6828 | 148.6452 | 26.2099 | 15.9102 | 42.6095 | 14.4856 | 43.1099 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2404
3089 | 775 | 460 | 74 | 3.8 | 28.3 | 42.152 | 158.805 | 22.024 | 0 | 42.6074 | 14.4848 | 0 | 0 | 100% | 0 | 4.9031 | 82.16% | 0 | 42.1216
3090 | 639 | 251 | 53 | 3.5 | 28.2 | 42.1573 | 89.7556 | 4.274 | 0 | 42.6047 | 14.4928 | 0 | 0 | 100% | 0 | 24.1521 | 43.51% | 0 | 43.6286
3091 | 271 | 63 | 25 | 4 | 26.5 | 0 | 42.2778 | 0 | 0 | 60.1844 | 22.0466 | 0 | 59.7725 | 96% | 0 | 20.9448 | 10% | 0 | 40.9159
3092 | 0 | 0 | 0 | 1.9 | 23.6 | 0 | 0 | 0 | 0 | 101.6535 | 40.1876 | 0 | 103.8941 | 88% | 0 | 0 | 10% | 0 | 37.4592
3093 | 0 | 0 | 0 | 0.9 | 21.2 | 0 | 0 | 0 | 0 | 95.7264 | 37.9442 | 0 | 95.1489 | 81% | 0 | 0 | 10% | 0 | 35.6593
3094 | 0 | 0 | 0 | 0.9 | 21.2 | 0 | 0 | 0 | 0 | 91.6833 | 36.2486 | 0 | 90.108 | 74% | 0 | 0 | 10% | 0 | 34.0068
3095 | 0 | 0 | 0 | 1 | 20.6 | 0 | 0 | 0 | 0 | 88.121 | 34.7989 | 0 | 85.9026 | 68% | 0 | 0 | 10% | 0 | 32.5237
3096 | 0 | 0 | 0 | 0.6 | 19.7 | 0 | 0 | 0 | 0 | 86.8182 | 34.3217 | 0 | 84.5385 | 61% | 0 | 0 | 10% | 0 | 31.9844
3097 | 0 | 0 | 0 | 0.5 | 18.8 | 0 | 0 | 0 | 0 | 86.8397 | 34.396 | 0 | 84.7276 | 55% | 0 | 0 | 10% | 0 | 32.0039
3098 | 0 | 0 | 0 | 0.7 | 18 | 0 | 0 | 0 | 0 | 87.9785 | 34.9308 | 0 | 86.2089 | 48% | 0 | 0 | 10% | 0 | 32.4976
3099 | 0 | 0 | 0 | 1.8 | 18.6 | 0 | 0 | 0 | 0 | 94.5601 | 37.664 | 0 | 94.3344 | 41% | 0 | 0 | 10% | 0 | 35.1994
3100 | 0 | 0 | 0 | 2.4 | 18.8 | 0 | 0 | 0 | 0 | 103.8303 | 41.5209 | 0 | 105.3065 | 34% | 0 | 0 | 10% | 0 | 39.0707
3101 | 0 | 0 | 0 | 1.7 | 18.2 | 0 | 0 | 0 | 0 | 110.6107 | 44.3831 | 0 | 113.069 | 25% | 0 | 0 | 10% | 0 | 41.9918
3102 | 168 | 42 | 19 | 1.4 | 17.3 | 0 | 19.6505 | 0 | 0 | 113.254 | 45.5565 | 0 | 115.8409 | 16% | 0 | 0 | 10% | 0 | 43.2434
3103 | 647 | 223 | 47 | 0.9 | 20.9 | 90.747 | 22.331 | 2.0419 | 0 | 108.491 | 43.2789 | 0 | 21.8879 | 15% | 0 | 0 | 10% | 0 | 43.6658
3104 | 804 | 429 | 58 | 0.5 | 23.9 | 180.7093 | 0 | 18.9096 | 0 | 71.6918 | 27.3281 | 110.4282 | 0 | 23% | 0 | 0 | 10% | 0 | 44.1334
3105 | 893 | 629 | 63 | 1 | 25.7 | 226.0458 | 0 | 38.8684 | 0 | 45.9814 | 16.0864 | 181.3537 | 0 | 37% | 8.1818 | 0 | 21.13% | 0 | 44.2851
3106 | 940 | 797 | 66 | 1.3 | 27.2 | 253.0142 | 0 | 56.3011 | 0 | 43.8372 | 15.0778 | 210.4706 | 0 | 52% | 24.207 | 0 | 54.05% | 0 | 44.4193
3107 | 958 | 916 | 71 | 2.3 | 28.4 | 267.0989 | 0 | 56.372 | 12.2163 | 42.5991 | 14.4732 | 225.713 | 0 | 69% | 25 | 0 | 88.05% | 0 | 42.9378
3108 | 965 | 982 | 75 | 2.9 | 29.1 | 273.9495 | -3.42e-15 | 31.8585 | 43.2415 | 42.6033 | 14.4123 | 232.4454 | 0 | 87% | 1.4348 | 0 | 90% | 0 | 41.8375
3109 | 947 | 980 | 84 | 3.7 | 29.8 | 222.9665 | 52.504 | 26.4 | 48.4226 | 42.6054 | 14.3508 | 181.23 | 0 | 100% | 0 | 0 | 90% | 0 | 41.6189
3110 | 930 | 924 | 87 | 4.4 | 29.7 | 42.1516 | 248.4037 | 26.3357 | 42.7211 | 42.6055 | 14.3597 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.4047
3111 | 894 | 812 | 92 | 4.4 | 29.9 | 42.1571 | 227.9894 | 25.5564 | 31.8335 | 42.6028 | 14.341 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.6067
3112 | 845 | 652 | 86 | 3.9 | 29.9 | 42.1571 | 200.3538 | 25.3684 | 15.4227 | 42.6003 | 14.3402 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.4178
3113 | 652 | 429 | 96 | 4.9 | 28.8 | 42.1572 | 124.5207 | 19.6194 | 0 | 42.5978 | 14.4371 | 0 | 0 | 100% | 0 | 5.6888 | 80.9% | 0 | 40.4548
3114 | 455 | 238 | 90 | 3.9 | 27.7 | 42.1573 | 45.1949 | 4.2727 | 0 | 42.5954 | 14.5335 | 0 | 0 | 100% | 0 | 21.6044 | 46.33% | 0 | 41.1204
3115 | 225 | 68 | 37 | 3.1 | 26.1 | 0 | 35.2667 | 0 | 0 | 52.9796 | 19.0331 | 0 | 52.0229 | 96% | 0 | 22.7068 | 10% | 0 | 39.67
3116 | 0 | 1 | 1 | 1.8 | 23.4 | 0 | 0 | 0 | 0 | 101.1083 | 39.9807 | 0 | 103.6396 | 89% | 0 | 0 | 10% | 0 | 37.147
3117 | 0 | 0 | 0 | 0.5 | 22 | 0 | 0 | 0 | 0 | 96.034 | 38.0037 | 0 | 95.6626 | 81% | 0 | 0 | 10% | 0 | 35.6776
3118 | 0 | 0 | 0 | 1 | 21.3 | 0 | 0 | 0 | 0 | 91.0994 | 35.9947 | 0 | 89.4644 | 75% | 0 | 0 | 10% | 0 | 33.7344
3119 | 0 | 0 | 0 | 1.7 | 20.2 | 0 | 0 | 0 | 0 | 86.9478 | 34.3388 | 0 | 84.5785 | 68% | 0 | 0 | 10% | 0 | 32.0425
3120 | 0 | 0 | 0 | 1.3 | 19.8 | 0 | 0 | 0 | 0 | 84.5948 | 33.3855 | 0 | 82.0077 | 62% | 0 | 0 | 10% | 0 | 31.0202
3121 | 0 | 0 | 0 | 0.3 | 19.4 | 0 | 0 | 0 | 0 | 83.6542 | 33.0223 | 0 | 81.1032 | 56% | 0 | 0 | 10% | 0 | 30.5896
3122 | 0 | 0 | 0 | 2.1 | 19.9 | 0 | 0 | 0 | 0 | 83.3329 | 32.8529 | 0 | 80.8878 | 50% | 0 | 0 | 10% | 0 | 30.3644
3123 | 0 | 0 | 0 | 2.2 | 19.8 | 0 | 0 | 0 | 0 | 84.2095 | 33.2256 | 0 | 82.046 | 44% | 0 | 0 | 10% | 0 | 30.6915
3124 | 0 | 0 | 0 | 1.6 | 18.4 | 0 | 0 | 0 | 0 | 85.4124 | 33.8276 | 0 | 83.5561 | 38% | 0 | 0 | 10% | 0 | 31.2618
3125 | 0 | 0 | 0 | 2 | 18.9 | 0 | 0 | 0 | 0 | 91.7483 | 36.4563 | 0 | 91.3071 | 31% | 0 | 0 | 10% | 0 | 33.8633
3126 | 166 | 42 | 19 | 1.9 | 18.7 | 0 | 20.1895 | 0 | 0 | 99.0756 | 39.5391 | 0 | 100.0682 | 24% | 0 | 0 | 10% | 0 | 36.9558
3127 | 644 | 224 | 46 | 0.5 | 23.3 | 90.8743 | 22.161 | 1.9422 | 0 | 97.4062 | 38.4561 | 8.4675 | 18.2202 | 23% | 0 | 0 | 10% | 0 | 38.7157
3128 | 807 | 435 | 60 | 0.6 | 25.2 | 181.669 | 0 | 19.0392 | 0 | 59.8723 | 22.0559 | 122.3591 | 0 | 32% | 0 | 0 | 10% | 0 | 39.0117
3129 | 887 | 634 | 68 | 1.1 | 27.2 | 224.5447 | 0 | 38.7572 | 0 | 46.6545 | 16.2323 | 178.6143 | 0 | 45% | 13.3251 | 0 | 28.12% | 0 | 39.2
3130 | 929 | 800 | 74 | 2.2 | 28.7 | 249.565 | 0 | 52.6264 | 3.3059 | 42.5789 | 14.4396 | 207.6909 | 0 | 61% | 25 | 0 | 62.12% | 0 | 39.3585
3131 | 952 | 922 | 78 | 2.5 | 29.6 | 265.3377 | 0 | 47.3332 | 21.0429 | 42.5896 | 14.3632 | 223.4054 | 0 | 77% | 20.4984 | 0 | 90% | 0 | 38.3168
3132 | 944 | 987 | 97 | 3.7 | 30.5 | 267.4977 | 0 | 23.6478 | 51.2423 | 42.5944 | 14.2841 | 225.4881 | 0 | 94% | 0 | 0 | 90% | 0 | 36.5626
3133 | 752 | 892 | 175 | 2.6 | 30.6 | 128.0262 | 95.5719 | 20.2889 | 45.6026 | 42.598 | 14.2763 | 86.2972 | 0 | 100% | 0 | 0 | 90% | 0 | 35.4419
3134 | 874 | 912 | 125 | 4.2 | 30.3 | 42.1518 | 230.3112 | 19.8613 | 47.8103 | 42.5971 | 14.3031 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.8736
3135 | 891 | 813 | 93 | 4.4 | 30.2 | 42.1571 | 227.023 | 19.6402 | 37.4749 | 42.5947 | 14.3113 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.6607
3136 | 848 | 657 | 87 | 4.3 | 29.7 | 42.1572 | 201.2158 | 19.7854 | 21.1971 | 42.5924 | 14.3553 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.85
3137 | 776 | 464 | 74 | 5.4 | 28.9 | 42.1572 | 158.9514 | 20.4825 | 1.4265 | 42.5902 | 14.4257 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.6177
3138 | 645 | 258 | 55 | 6.7 | 25.9 | 42.1575 | 90.5175 | 4.4609 | 0 | 42.588 | 14.6845 | 0 | 0 | 100% | 0 | 17.6177 | 61.81% | 0 | 37.4733
3139 | 307 | 71 | 26 | 6.5 | 22.2 | 0 | 48.3433 | 0 | 0 | 42.5851 | 14.9736 | 0 | 41.0937 | 97% | 0 | 23.6503 | 23.97% | 0 | 36.5615
3140 | 0 | 1 | 1 | 5.7 | 19.9 | 0 | 0 | 0 | 0 | 73.7675 | 28.5947 | 0 | 74.0186 | 92% | 0 | 8.732 | 10% | 0 | 34.402
3141 | 0 | 0 | 0 | 4.6 | 18.6 | 0 | 0 | 0 | 0 | 88.3962 | 35.0634 | 0 | 87.4601 | 85% | 0 | 0 | 10% | 0 | 32.4226
3142 | 0 | 0 | 0 | 4.3 | 17.6 | 0 | 0 | 0 | 0 | 83.5523 | 33.1028 | 0 | 81.4887 | 79% | 0 | 0 | 10% | 0 | 30.5165
3143 | 0 | 0 | 0 | 3.2 | 17.4 | 0 | 0 | 0 | 0 | 80.2609 | 31.6365 | 0 | 78.2116 | 73% | 0 | 0 | 10% | 0 | 29.0002
3144 | 0 | 0 | 0 | 3.4 | 17.2 | 0 | 0 | 0 | 0 | 78.3259 | 30.7751 | 0 | 76.3542 | 68% | 0 | 0 | 10% | 0 | 28.1011
3145 | 0 | 0 | 0 | 2.7 | 17.4 | 0 | 0 | 0 | 0 | 77.3712 | 30.3335 | 0 | 75.4561 | 62% | 0 | 0 | 10% | 0 | 27.6329
3146 | 0 | 0 | 0 | 3.9 | 18.4 | 0 | 0 | 0 | 0 | 77.2423 | 30.2117 | 0 | 75.3745 | 56% | 0 | 0 | 10% | 0 | 27.4909
3147 | 0 | 0 | 0 | 4.5 | 19.1 | 0 | 0 | 0 | 0 | 77.4147 | 30.2428 | 0 | 75.5852 | 51% | 0 | 0 | 10% | 0 | 27.5063
3148 | 0 | 0 | 0 | 4.7 | 18.8 | 0 | 0 | 0 | 0 | 77.2165 | 30.1749 | 0 | 75.411 | 45% | 0 | 0 | 10% | 0 | 27.4261
3149 | 0 | 0 | 0 | 3.8 | 18.2 | 0 | 0 | 0 | 0 | 80.5756 | 31.7309 | 0 | 78.8465 | 39% | 0 | 0 | 10% | 0 | 28.9677
3150 | 158 | 40 | 19 | 2.8 | 16.2 | 0 | 19.9303 | 0 | 0 | 86.3328 | 34.3619 | 0 | 85.3226 | 33% | 0 | 0 | 10% | 0 | 31.5832
3151 | 587 | 218 | 52 | 4.1 | 17.3 | 79.9242 | 20.2417 | 1.8314 | 0 | 83.756 | 33.2107 | 11.0311 | 15.7199 | 33% | 0 | 0 | 10% | 0 | 33.4324
3152 | 766 | 432 | 72 | 5.2 | 19.1 | 168.8414 | -2.98e-14 | 19.1678 | 0 | 47.086 | 17.0451 | 121.5285 | 0 | 42% | 0 | 0 | 10% | 0 | 34.269
3153 | 847 | 629 | 84 | 6.1 | 20.4 | 210.2069 | 2.98e-14 | 38.9632 | 0 | 45.2815 | 16.207 | 165.0883 | 0 | 54% | 18.2376 | 0 | 34.8% | 0 | 34.6063
3154 | 892 | 793 | 92 | 6.2 | 21.5 | 235.7132 | 0 | 47.507 | 8.8068 | 42.5653 | 15.0158 | 193.3403 | 0 | 68% | 25 | 0 | 68.8% | 0 | 34.9511
3155 | 920 | 914 | 94 | 6.2 | 22.7 | 252.9591 | 0 | 37.077 | 31.6856 | 42.5779 | 14.934 | 210.5518 | 0 | 84% | 15.5859 | 0 | 90% | 0 | 34.82
3156 | 929 | 978 | 98 | 5.9 | 23.6 | 261.0132 | 0 | 15.6185 | 59.4815 | 42.5832 | 14.8674 | 218.6106 | 0 | 99% | 0 | 0 | 90% | 0 | 33.5447
3157 | 927 | 982 | 99 | 5.3 | 24.6 | 48.7008 | 244.5515 | 17.1047 | 57.9953 | 42.5881 | 14.7904 | 7.3325 | 0 | 100% | 0 | 0 | 90% | 0 | 32.5415
3158 | 914 | 926 | 98 | 5.1 | 25.4 | 42.152 | 243.0425 | 16.7893 | 52.7188 | 42.5861 | 14.7249 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.2246
3159 | 889 | 816 | 95 | 5.5 | 25.4 | 42.1575 | 226.1574 | 16.8772 | 41.0879 | 42.584 | 14.7242 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.3117
3160 | 853 | 662 | 86 | 5.5 | 25.1 | 42.1575 | 202.501 | 17.4772 | 24.2459 | 42.5819 | 14.7481 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.9358
3161 | 779 | 469 | 74 | 5.4 | 24.2 | 42.1576 | 159.8828 | 18.8367 | 3.4878 | 42.58 | 14.8194 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.3668
3162 | 635 | 261 | 58 | 5.3 | 22.5 | 42.1578 | 88.9582 | 4.5866 | 0 | 42.578 | 14.9489 | 0 | 0 | 100% | 0 | 16.7656 | 63.18% | 0 | 37.0121
3163 | 291 | 72 | 29 | 4.6 | 20.2 | 0 | 46.0346 | 0 | 0 | 42.5754 | 15.1061 | 0 | 41.084 | 97% | 0 | 23.9571 | 24.84% | 0 | 37.006
3164 | 0 | 1 | 1 | 3.9 | 18 | 0 | 0 | 0 | 0 | 72.3535 | 28.1154 | 0 | 72.5015 | 92% | 0 | 9.2773 | 10% | 0 | 34.4687
3165 | 0 | 0 | 0 | 1.9 | 16.6 | 0 | 0 | 0 | 0 | 87.7287 | 34.9209 | 0 | 86.6957 | 85% | 0 | 0 | 10% | 0 | 32.2674
3166 | 0 | 0 | 0 | 2 | 16 | 0 | 0 | 0 | 0 | 83.0954 | 33.0156 | 0 | 81.018 | 79% | 0 | 0 | 10% | 0 | 30.4084
3167 | 0 | 0 | 0 | 1.6 | 15.6 | 0 | 0 | 0 | 0 | 80.8337 | 32.0108 | 0 | 78.8543 | 73% | 0 | 0 | 10% | 0 | 29.3528
3168 | 0 | 0 | 0 | 1.5 | 14.9 | 0 | 0 | 0 | 0 | 80.0925 | 31.7168 | 0 | 78.1911 | 68% | 0 | 0 | 10% | 0 | 29.0256
3169 | 0 | 0 | 0 | 1 | 14.7 | 0 | 0 | 0 | 0 | 80.4042 | 31.871 | 0 | 78.5659 | 62% | 0 | 0 | 10% | 0 | 29.1563
3170 | 0 | 0 | 0 | 1 | 13.9 | 0 | 0 | 0 | 0 | 81.8724 | 32.5894 | 0 | 80.0996 | 56% | 0 | 0 | 10% | 0 | 29.8564
3171 | 0 | 0 | 0 | 2.5 | 14.1 | 0 | 0 | 0 | 0 | 89.9369 | 36.0181 | 0 | 89.6568 | 49% | 0 | 0 | 10% | 0 | 33.2633
3172 | 0 | 0 | 0 | 2.3 | 14.1 | 0 | 0 | 0 | 0 | 98.5073 | 39.6347 | 0 | 99.9624 | 42% | 0 | 0 | 10% | 0 | 36.9101
3173 | 0 | 0 | 0 | 1.8 | 12.6 | 0 | 0 | 0 | 0 | 105.3444 | 42.6124 | 0 | 107.9483 | 34% | 0 | 0 | 10% | 0 | 39.9663
3174 | 204 | 48 | 21 | 3 | 14.2 | 0 | 26.6257 | 0 | 0 | 108.6042 | 43.8641 | 0 | 111.3538 | 26% | 0 | 0 | 10% | 0 | 41.3196
3175 | 649 | 231 | 50 | 3.5 | 16.8 | 90.5208 | 22.8056 | 2.2488 | 0 | 102.8438 | 41.2642 | 3.3037 | 19.6059 | 24% | 0 | 0 | 10% | 0 | 41.8335
3176 | 818 | 446 | 64 | 4.4 | 17.9 | 182.2157 | 0 | 20.0982 | 0 | 63.8175 | 24.3153 | 119.1544 | 0 | 33% | 0 | 0 | 10% | 0 | 42.3106
3177 | 896 | 646 | 72 | 4.2 | 19.2 | 225.0828 | 0 | 40.4729 | 0 | 44.8939 | 16.1232 | 180.9922 | 0 | 47% | 11.0387 | 0 | 25.01% | 0 | 43.0794
3178 | 945 | 815 | 75 | 3.9 | 20.5 | 252.8916 | 0 | 56.1672 | 2.2548 | 42.5733 | 15.0858 | 211.1192 | 0 | 62% | 25 | 0 | 59.01% | 0 | 43.5025
3179 | 962 | 934 | 81 | 3.7 | 21.6 | 267.3596 | 0 | 53.1095 | 17.8843 | 42.585 | 15.0159 | 225.5396 | 0 | 79% | 22.7849 | 0 | 90% | 0 | 42.4294
3180 | 968 | 998 | 84 | 2.7 | 23.5 | 274.905 | 0 | 27.5719 | 47.5281 | 42.591 | 14.8778 | 232.9468 | 0 | 96% | 0 | 0 | 90% | 0 | 41.6562
3181 | 960 | 1000 | 89 | 4.5 | 24 | 91.2277 | 206.7982 | 26.0944 | 49.0056 | 42.5955 | 14.8408 | 49.6841 | 0 | 100% | 0 | 0 | 90% | 0 | 41.4144
3182 | 937 | 940 | 94 | 5.2 | 24.1 | 42.1521 | 250.4049 | 25.8941 | 45.2452 | 42.5938 | 14.8322 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.4369
3183 | 907 | 828 | 94 | 6.2 | 23.6 | 42.1577 | 231.6669 | 25.4089 | 33.9444 | 42.5914 | 14.8702 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.9899
3184 | 854 | 668 | 92 | 7.5 | 22.3 | 42.1578 | 202.425 | 25.0187 | 17.5816 | 42.5892 | 14.9676 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.6974
3185 | 760 | 471 | 86 | 7.3 | 21.2 | 42.1579 | 154.2528 | 22.8175 | 0 | 42.587 | 15.0441 | 0 | 0 | 100% | 0 | 2.6067 | 85.83% | 0 | 41.1796
3186 | 592 | 259 | 69 | 6.9 | 19.9 | 42.158 | 78.119 | 4.7208 | 0 | 42.5849 | 15.1287 | 0 | 0 | 100% | 0 | 21.6273 | 51.23% | 0 | 42.1885
3187 | 239 | 70 | 33 | 5.4 | 18.2 | 0 | 37.9803 | 0 | 0 | 47.5579 | 17.3034 | 0 | 46.0302 | 97% | 0 | 25 | 11.23% | 0 | 40.246
3188 | 0 | 1 | 1 | 3.7 | 16.2 | 0 | 0 | 0 | 0 | 99.7184 | 39.9932 | 0 | 102.4373 | 89% | 0 | 0 | 11.23% | 0 | 37.0298
3189 | 0 | 0 | 0 | 4 | 14.9 | 0 | 0 | 0 | 0 | 93.8262 | 37.6173 | 0 | 93.3143 | 82% | 0 | 0 | 11.23% | 0 | 35.2205
3190 | 0 | 0 | 0 | 4.3 | 14.1 | 0 | 0 | 0 | 0 | 88.9514 | 35.5993 | 0 | 87.1142 | 76% | 0 | 0 | 11.23% | 0 | 33.2646
3191 | 0 | 0 | 0 | 3.7 | 13.7 | 0 | 0 | 0 | 0 | 86.3122 | 34.5091 | 0 | 84.0992 | 69% | 0 | 0 | 11.23% | 0 | 32.1273
3192 | 0 | 0 | 0 | 3.9 | 13.2 | 0 | 0 | 0 | 0 | 85.2139 | 34.0763 | 0 | 82.9725 | 63% | 0 | 0 | 11.23% | 0 | 31.6356
3193 | 0 | 0 | 0 | 3.9 | 13 | 0 | 0 | 0 | 0 | 85.266 | 34.1102 | 0 | 83.1801 | 57% | 0 | 0 | 11.23% | 0 | 31.6195
3194 | 0 | 0 | 0 | 1.7 | 12.9 | 0 | 0 | 0 | 0 | 86.6877 | 34.7153 | 0 | 84.9781 | 51% | 0 | 0 | 11.23% | 0 | 32.1871
3195 | 0 | 0 | 0 | 2 | 12.7 | 0 | 0 | 0 | 0 | 92.7422 | 37.294 | 0 | 92.4295 | 44% | 0 | 0 | 11.23% | 0 | 34.7404
3196 | 0 | 0 | 0 | 2.2 | 12.4 | 0 | 0 | 0 | 0 | 101.11 | 40.8357 | 0 | 102.3627 | 36% | 0 | 0 | 11.23% | 0 | 38.2997
3197 | 0 | 0 | 0 | 2 | 11.3 | 0 | 0 | 0 | 0 | 107.5408 | 43.6019 | 0 | 109.8215 | 28% | 0 | 0 | 11.23% | 0 | 41.1247
3198 | 242 | 50 | 20 | 1.9 | 11.5 | 0 | 32.6101 | 0 | 0 | 110.8368 | 44.9663 | 0 | 113.3558 | 19% | 0 | 0 | 11.23% | 0 | 42.5682
3199 | 682 | 239 | 47 | 2.2 | 14.1 | 96.5463 | 24.3406 | 2.3364 | 0 | 104.8637 | 42.3131 | 7.5813 | 19.9756 | 18% | 0 | 0 | 11.23% | 0 | 42.9321
3200 | 840 | 454 | 60 | 3.3 | 16.2 | 188.685 | 0 | 20.5023 | 0 | 65.2029 | 25.0176 | 124.5985 | 0 | 28% | 0 | 0 | 11.23% | 0 | 43.3547
3201 | 922 | 656 | 66 | 4.4 | 18.1 | 231.9936 | 0 | 41.3277 | 0 | 44.8346 | 16.1639 | 188.2175 | 0 | 42% | 11.0858 | 0 | 26.3% | 0 | 43.864
3202 | 966 | 825 | 68 | 4.5 | 19.8 | 258.2532 | 0 | 56.8814 | 2.3413 | 42.583 | 15.1343 | 216.7318 | 0 | 58% | 25 | 0 | 60.3% | 0 | 44.2137
3203 | 985 | 945 | 71 | 4.3 | 21.1 | 273.2064 | 0 | 52.8329 | 19.044 | 42.5932 | 15.0532 | 231.623 | 0 | 75% | 21.8365 | 0 | 90% | 0 | 43.0792
3204 | 991 | 1010 | 74 | 2.9 | 22.1 | 281.2536 | 0 | 30.5748 | 44.5252 | 42.5978 | 14.9855 | 239.5419 | 0 | 93% | 0 | 0 | 90% | 0 | 42.4911
3205 | 986 | 1012 | 76 | 2.7 | 23.2 | 135.4032 | 165.4228 | 27.1892 | 47.9108 | 42.6012 | 14.9045 | 93.7242 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4678
3206 | 975 | 956 | 75 | 3.7 | 24.3 | 42.152 | 262.8199 | 26.9541 | 45.3308 | 42.6 | 14.8184 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4832
3207 | 952 | 844 | 73 | 4.5 | 24.8 | 42.1576 | 246.0447 | 26.4396 | 33.8108 | 42.5975 | 14.7777 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.9278
3208 | 916 | 686 | 68 | 4.2 | 24.5 | 42.1576 | 221.7428 | 26.1361 | 17.3051 | 42.5951 | 14.8008 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.6474
3209 | 853 | 492 | 59 | 3 | 24.4 | 42.1576 | 181.0993 | 23.4536 | 0 | 42.5927 | 14.8079 | 0 | 0 | 100% | 0 | 3.0071 | 85.19% | 0 | 41.9792
3210 | 703 | 274 | 49 | 2.3 | 24.2 | 42.1576 | 106.491 | 4.7009 | 0 | 42.5904 | 14.8231 | 0 | 0 | 100% | 0 | 22.8453 | 48.64% | 0 | 43.0798
3211 | 360 | 79 | 26 | 3.6 | 21.9 | 0 | 57.4656 | 0 | 0 | 52.1581 | 19.0158 | 0 | 50.8541 | 96% | 0 | 24.1476 | 10% | 0 | 41.0963
3212 | 0 | 1 | 1 | 2.4 | 19.4 | 0 | 0 | 0 | 0 | 101.7199 | 40.5873 | 0 | 104.7013 | 89% | 0 | 0 | 10% | 0 | 37.6726
3213 | 0 | 0 | 0 | 2.2 | 17.9 | 0 | 0 | 0 | 0 | 95.4799 | 38.0982 | 0 | 95.067 | 81% | 0 | 0 | 10% | 0 | 35.7574
3214 | 0 | 0 | 0 | 0.9 | 16.4 | 0 | 0 | 0 | 0 | 90.7119 | 36.1931 | 0 | 89.0506 | 75% | 0 | 0 | 10% | 0 | 33.9158
3215 | 0 | 0 | 0 | 1.1 | 15.3 | 0 | 0 | 0 | 0 | 87.8668 | 35.0644 | 0 | 85.7349 | 68% | 0 | 0 | 10% | 0 | 32.7489
3216 | 0 | 0 | 0 | 0.4 | 13.9 | 0 | 0 | 0 | 0 | 86.2873 | 34.4867 | 0 | 84.0228 | 62% | 0 | 0 | 10% | 0 | 32.115
3217 | 0 | 0 | 0 | 0.6 | 13.3 | 0 | 0 | 0 | 0 | 85.9374 | 34.3751 | 0 | 83.7644 | 56% | 0 | 0 | 10% | 0 | 31.9503
3218 | 0 | 0 | 0 | 0.5 | 12.8 | 0 | 0 | 0 | 0 | 87.0445 | 34.8712 | 0 | 85.2064 | 49% | 0 | 0 | 10% | 0 | 32.4037
3219 | 0 | 0 | 0 | 0.7 | 12.1 | 0 | 0 | 0 | 0 | 92.2995 | 37.139 | 0 | 91.6848 | 43% | 0 | 0 | 10% | 0 | 34.6405
3220 | 0 | 0 | 0 | 0.8 | 11.6 | 0 | 0 | 0 | 0 | 99.324 | 40.1279 | 0 | 100.0442 | 35% | 0 | 0 | 10% | 0 | 37.6367
3221 | 0 | 0 | 0 | 0.6 | 11.7 | 0 | 0 | 0 | 0 | 105.1796 | 42.5963 | 0 | 106.9341 | 27% | 0 | 0 | 10% | 0 | 40.1477
3222 | 241 | 51 | 21 | 0.5 | 12.9 | 0 | 33.4613 | 0 | 0 | 108.8308 | 44.0459 | 0 | 110.9248 | 19% | 0 | 0 | 10% | 0 | 41.6613
3223 | 659 | 235 | 49 | 1.2 | 16.1 | 93.5593 | 23.3733 | 2.2549 | 0 | 104.2099 | 41.8911 | 5.3078 | 19.7922 | 18% | 0 | 0 | 10% | 0 | 42.457
3224 | 816 | 447 | 63 | 1.4 | 19.1 | 183.8973 | 0 | 19.7979 | 0 | 67.0191 | 25.6421 | 118.0005 | 0 | 27% | 0 | 0 | 10% | 0 | 43.3162
3225 | 892 | 646 | 72 | 1.7 | 22.2 | 225.6792 | 0 | 39.7338 | 0 | 45.2707 | 16.0755 | 181.5 | 0 | 40% | 9.3599 | 0 | 22.73% | 0 | 43.9666
3226 | 914 | 807 | 88 | 3.1 | 24.1 | 244.5485 | 0 | 56.6575 | 0 | 43.1246 | 15.0481 | 202.5533 | 0 | 55% | 24.8252 | 0 | 56.49% | 0 | 44.2071
3227 | 887 | 921 | 130 | 4 | 26.3 | 244.8589 | 0 | 55.7887 | 12.344 | 42.5931 | 14.6527 | 203.3703 | 0 | 71% | 24.6384 | 0 | 90% | 0 | 43.1045
3228 | 897 | 978 | 126 | 4 | 28.8 | 252.974 | 0 | 30.7296 | 42.6819 | 42.5976 | 14.4371 | 211.2897 | 0 | 86% | 0 | 0 | 90% | 0 | 42.3738
3229 | 951 | 999 | 92 | 5.8 | 31.3 | 229.8858 | 44.1383 | 26.5776 | 48.0333 | 42.6006 | 14.2134 | 187.9466 | 0 | 100% | 0 | 0 | 90% | 0 | 42.2291
3230 | 948 | 947 | 86 | 6.7 | 32.4 | 42.1513 | 253.685 | 27.2883 | 41.8819 | 42.6015 | 14.1118 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.1088
3231 | 936 | 842 | 79 | 7.5 | 32.5 | 42.1569 | 240.5601 | 26.6907 | 31.4121 | 42.599 | 14.1016 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.5009
3232 | 905 | 685 | 70 | 7 | 32.4 | 42.1569 | 218.0149 | 26.4615 | 15.381 | 42.5966 | 14.1102 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2803
3233 | 809 | 481 | 68 | 5.5 | 32 | 42.1569 | 168.609 | 22.0974 | 0 | 42.5942 | 14.1468 | 0 | 0 | 100% | 0 | 4.9531 | 82.08% | 0 | 41.906
3234 | 640 | 281 | 70 | 4.6 | 28.6 | 42.1573 | 91.3665 | 5.0689 | 0 | 42.592 | 14.4529 | 0 | 0 | 100% | 0 | 22.6914 | 45.77% | 0 | 42.9227
3235 | 328 | 97 | 48 | 3 | 24.9 | 0 | 52.5896 | 0 | 0 | 56.3508 | 20.5627 | 0 | 55.5362 | 96% | 0 | 22.3555 | 10% | 0 | 40.8427
3236 | 0 | 1 | 1 | 2.1 | 22.1 | 0 | 0 | 0 | 0 | 101.4905 | 40.263 | 0 | 104.0102 | 88% | 0 | 0 | 10% | 0 | 37.4546
3237 | 0 | 0 | 0 | 1.4 | 21.9 | 0 | 0 | 0 | 0 | 96.0659 | 38.0257 | 0 | 95.6561 | 81% | 0 | 0 | 10% | 0 | 35.7118
3238 | 0 | 0 | 0 | 5.8 | 20.7 | 0 | 0 | 0 | 0 | 91.8309 | 36.3522 | 0 | 90.3358 | 74% | 0 | 0 | 10% | 0 | 34.0983
3239 | 0 | 0 | 0 | 6.8 | 17.4 | 0 | 0 | 0 | 0 | 87.9998 | 34.9807 | 0 | 85.7827 | 68% | 0 | 0 | 10% | 0 | 32.6992
3240 | 0 | 0 | 0 | 6.2 | 16.1 | 0 | 0 | 0 | 0 | 87.0201 | 34.6557 | 0 | 84.8042 | 62% | 0 | 0 | 10% | 0 | 32.3116
3241 | 0 | 0 | 0 | 5.2 | 15.8 | 0 | 0 | 0 | 0 | 86.8784 | 34.6158 | 0 | 84.7898 | 55% | 0 | 0 | 10% | 0 | 32.22
3242 | 0 | 0 | 0 | 4.1 | 15.1 | 0 | 0 | 0 | 0 | 88.2397 | 35.2355 | 0 | 86.5376 | 49% | 0 | 0 | 10% | 0 | 32.7991
3243 | 0 | 0 | 0 | 3.7 | 14.6 | 0 | 0 | 0 | 0 | 94.662 | 37.9895 | 0 | 94.4593 | 42% | 0 | 0 | 10% | 0 | 35.5243
3244 | 0 | 0 | 0 | 3.2 | 14.3 | 0 | 0 | 0 | 0 | 102.2174 | 41.1813 | 0 | 103.3478 | 34% | 0 | 0 | 10% | 0 | 38.7338
3245 | 0 | 0 | 0 | 3.4 | 14.1 | 0 | 0 | 0 | 0 | 108.4229 | 43.7952 | 0 | 110.5163 | 26% | 0 | 0 | 10% | 0 | 41.3982
3246 | 154 | 47 | 26 | 3.9 | 14.2 | 0 | 21.9896 | 0 | 0 | 111.9953 | 45.2771 | 0 | 114.417 | 17% | 0 | 0 | 10% | 0 | 42.9492
3247 | 540 | 224 | 68 | 4.3 | 16 | 72.7449 | 18.6692 | 2.3867 | 0 | 105.8667 | 42.593 | 0 | 36.3706 | 14% | 0 | 0 | 10% | 0 | 43.4796
3248 | 739 | 435 | 84 | 5.1 | 18.1 | 162.4244 | 0 | 19.2071 | 0 | 69.0272 | 26.5958 | 94.4996 | 0 | 21% | 0 | 0 | 10% | 0 | 43.8704
3249 | 848 | 636 | 88 | 5.1 | 19.8 | 211.2672 | 0 | 39.1482 | 0 | 44.5146 | 15.9281 | 167.8523 | 0 | 34% | 8.2421 | 0 | 21.21% | 0 | 44.4873
3250 | 900 | 803 | 91 | 4.4 | 21.7 | 239.3189 | 0 | 56.342 | 0 | 43.7149 | 15.4703 | 196.8134 | 0 | 49% | 24.4116 | 0 | 54.41% | 0 | 44.7811
3251 | 923 | 921 | 96 | 2.5 | 23.7 | 256.4427 | 0 | 56.2312 | 12.2641 | 42.5937 | 14.8633 | 214.998 | 0 | 65% | 25 | 0 | 88.41% | 0 | 43.2955
3252 | 926 | 983 | 101 | 1.5 | 26.1 | 263.0743 | 0 | 32.0114 | 42.2293 | 42.5994 | 14.6717 | 221.5597 | 0 | 81% | 1.1699 | 0 | 90% | 0 | 42.627
3253 | 925 | 987 | 103 | 4.6 | 26.6 | 261.4156 | 0 | 28.2874 | 46.4089 | 42.6021 | 14.6304 | 219.6372 | 0 | 98% | 0 | 0 | 90% | 0 | 42.442
3254 | 907 | 932 | 106 | 5.4 | 26.3 | 74.9142 | 202.8952 | 27.2377 | 41.7582 | 42.6038 | 14.6563 | 33.4273 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4063
3255 | 871 | 820 | 108 | 6.1 | 25.2 | 42.1521 | 220.3157 | 26.4109 | 31.0982 | 42.6016 | 14.7467 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8679
3256 | 830 | 663 | 98 | 6.3 | 23.7 | 42.1577 | 195.5987 | 26.2039 | 15.2195 | 42.5991 | 14.8652 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.7797
3257 | 722 | 470 | 96 | 6.1 | 22 | 42.1578 | 144.3756 | 22.1299 | 0 | 42.5966 | 14.9925 | 0 | 0 | 100% | 0 | 4.4533 | 82.88% | 0 | 42.2867
3258 | 527 | 264 | 92 | 6 | 20.5 | 42.1579 | 63.4941 | 5.4181 | 0 | 42.5942 | 15.0932 | 0 | 0 | 100% | 0 | 21.9354 | 47.78% | 0 | 43.158
3259 | 178 | 62 | 35 | 4.9 | 18.5 | 0 | 28.6643 | 0 | 0 | 51.7569 | 19.0835 | 0 | 50.5799 | 96% | 0 | 23.6113 | 10% | 0 | 40.635
3260 | 0 | 1 | 1 | 3 | 17.1 | 0 | 0 | 0 | 0 | 100.9966 | 40.4621 | 0 | 103.694 | 89% | 0 | 0 | 10% | 0 | 37.5776
3261 | 0 | 0 | 0 | 2.5 | 16.4 | 0 | 0 | 0 | 0 | 95.609 | 38.2599 | 0 | 95.2358 | 82% | 0 | 0 | 10% | 0 | 35.9134
3262 | 0 | 0 | 0 | 1.7 | 15.7 | 0 | 0 | 0 | 0 | 91.5904 | 36.6125 | 0 | 90.1273 | 75% | 0 | 0 | 10% | 0 | 34.3329
3263 | 0 | 0 | 0 | 0.7 | 14.8 | 0 | 0 | 0 | 0 | 88.6802 | 35.4399 | 0 | 86.6718 | 68% | 0 | 0 | 10% | 0 | 33.1352
3264 | 0 | 0 | 0 | 2.4 | 17.2 | 0 | 0 | 0 | 0 | 87.7779 | 34.9012 | 0 | 85.7437 | 62% | 0 | 0 | 10% | 0 | 32.546
3265 | 0 | 0 | 0 | 4.3 | 21.4 | 0 | 0 | 0 | 0 | 87.9993 | 34.6848 | 0 | 86.139 | 55% | 0 | 0 | 10% | 0 | 32.2862
3266 | 0 | 0 | 0 | 9 | 22.6 | 0 | 0 | 0 | 0 | 89.5625 | 35.238 | 0 | 88.1157 | 49% | 0 | 0 | 10% | 0 | 32.8079
3267 | 0 | 0 | 0 | 9.7 | 21.6 | 0 | 0 | 0 | 0 | 95.0604 | 37.6358 | 0 | 94.8696 | 42% | 0 | 0 | 10% | 0 | 35.1867
3268 | 0 | 0 | 0 | 6.9 | 20.1 | 0 | 0 | 0 | 0 | 102.1822 | 40.7264 | 0 | 103.2422 | 34% | 0 | 0 | 10% | 0 | 38.2954
3269 | 0 | 0 | 0 | 4.4 | 19.6 | 0 | 0 | 0 | 0 | 107.9783 | 43.178 | 0 | 109.9336 | 26% | 0 | 0 | 10% | 0 | 40.7959
3270 | 101 | 55 | 43 | 9.7 | 18.5 | 0 | 14.8056 | 0 | 0 | 111.2381 | 44.6189 | 0 | 113.4703 | 17% | 0 | 0 | 10% | 0 | 42.3026
3271 | 20 | 141 | 135 | 11.6 | 17.7 | 0 | 4.2983 | 2.0149 | 0 | 108.4267 | 43.5204 | 0 | 109.8337 | 9% | 0 | 0 | 10% | 0 | 43.2916
3272 | 74 | 291 | 248 | 9.8 | 18.1 | 0 | 19.5186 | 11.0869 | 0 | 87.7019 | 34.8118 | 0 | 84.9424 | 2% | 0 | 0 | 10% | 0 | 43.7368
3273 | 342 | 582 | 346 | 8.8 | 20.5 | 57.1424 | 15.5067 | 33.9734 | 0 | 42.7317 | 15.1586 | 22.8295 | 7.5153 | 4% | 3.9094 | 0 | 15.32% | 0 | 43.9667
3274 | 426 | 753 | 407 | 10.9 | 23.2 | 97.5449 | 0 | 50.8543 | 0 | 43.0325 | 15.0857 | 55.5172 | 0 | 8% | 21.0241 | 0 | 43.91% | 0 | 43.6059
3275 | 281 | 717 | 453 | 11.6 | 24.2 | 58.406 | 0 | 49.2414 | 0 | 42.548 | 14.8083 | 17.776 | 0 | 9% | 20.8971 | 0 | 72.33% | 0 | 42.1817
3276 | 176 | 678 | 495 | 10 | 25.2 | 0 | 56.9319 | 40.2989 | 5.5668 | 43.0692 | 14.9413 | 0 | 40.5125 | 6% | 12.9929 | 0 | 90% | 0 | 40.8659
3277 | 658 | 1037 | 395 | 5.2 | 26.1 | 147.4799 | 35.5578 | 27.59 | 47.51 | 42.5153 | 14.6428 | 110.0678 | 7.1614 | 14% | 0 | 0 | 90% | 0 | 40.1788
3278 | 262 | 717 | 467 | 4.6 | 24.8 | 59.0788 | 0 | 26.1551 | 23.2323 | 42.569 | 14.7678 | 18.5073 | 0 | 15% | 0 | 0 | 90% | 0 | 39.9455
3279 | 88 | 475 | 393 | 3.7 | 25.2 | 0 | 27.2132 | 26.0884 | 0.75547 | 43.0378 | 14.9258 | 0 | 40.6826 | 12% | 0 | 0 | 90% | 0 | 39.5007
3280 | 6 | 229 | 222 | 4.5 | 23.5 | 0 | 1.7724 | 7.7067 | 0 | 42.5461 | 14.8621 | 0 | 40.2315 | 9% | 0 | 19.1734 | 59.32% | 0 | 39.2932
3281 | 2 | 187 | 184 | 3.7 | 22 | 0 | 0.54077 | 5.0464 | 0 | 42.5208 | 14.9658 | 0 | 40.2376 | 6% | 0 | 22.1825 | 23.83% | 0 | 39.724
3282 | 298 | 205 | 109 | 2.5 | 22.5 | 0 | 56.3485 | 3.5508 | 0 | 79.811 | 30.9414 | 0 | 79.7842 | 0% | 0 | 8.644 | 10% | 0 | 40.5793
3283 | 64 | 48 | 41 | 4.1 | 20.9 | 0 | 10.3507 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4278
3284 | 0 | 2 | 2 | 3 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.403
3285 | 0 | 0 | 0 | 1.3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3787
3286 | 0 | 0 | 0 | 1.5 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3548
3287 | 0 | 0 | 0 | 3.3 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3312
3288 | 0 | 0 | 0 | 1.8 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3081
3289 | 0 | 0 | 0 | 2.2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2856
3290 | 0 | 0 | 0 | 2 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2634
3291 | 0 | 0 | 0 | 1.4 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2418
3292 | 0 | 0 | 0 | 1.8 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2204
3293 | 0 | 0 | 0 | 1.1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1996
3294 | 68 | 43 | 37 | 1.6 | 13.4 | 0 | 10.1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1789
3295 | 529 | 218 | 53 | 1 | 16.4 | 72.9672 | 18.3231 | 1.4717 | 0 | 0 | 0 | 69.0389 | 0 | 6% | 0 | 0 | 10% | 0 | 0.10482
3296 | 803 | 455 | 69 | 1 | 18.8 | 181.1984 | 0 | 19.7853 | 0 | 0 | 0 | 176.6865 | 0 | 19% | 0 | 0 | 10% | 0 | 17.7774
3297 | 857 | 660 | 101 | 1.5 | 20.5 | 216.3015 | 2.98e-14 | 40.4573 | 0 | 0 | 0 | 213.7585 | 0 | 35% | 0 | 0 | 10% | 0 | 38.1006
3298 | 864 | 791 | 102 | 2.1 | 21.3 | 230.4 | 0 | 54.792 | 0 | 42.474 | 0 | 188.6829 | 0 | 49% | 19.0058 | 0 | 35.85% | 0 | 32.7389
3299 | 896 | 946 | 141 | 3.8 | 21.8 | 247.5275 | 0 | 55.8734 | 14.5187 | 42.5249 | 9.6445 | 205.8758 | 0 | 65% | 25 | 0 | 69.85% | 0 | 37.6087
3300 | 745 | 925 | 211 | 3.6 | 22.5 | 207.0566 | 0 | 37.9277 | 32.0845 | 42.546 | 14.9376 | 165.5238 | 0 | 77% | 14.8177 | 0 | 90% | 0 | 35.6784
3301 | 651 | 884 | 252 | 3.8 | 22.9 | 178.9869 | 0 | 21.7839 | 43.9194 | 42.5548 | 14.9111 | 137.3989 | 0 | 87% | 0 | 0 | 90% | 0 | 34.5846
3302 | 599 | 789 | 238 | 4.5 | 22.9 | 159.7242 | 0 | 19.6397 | 37.3239 | 42.5617 | 14.9135 | 117.7815 | 0 | 96% | 0 | 0 | 90% | 0 | 34.3819
3303 | 669 | 808 | 255 | 2.8 | 23.4 | 95.0919 | 95.0924 | 18.7378 | 37.3845 | 42.5669 | 14.8771 | 53.2552 | 0 | 100% | 0 | 0 | 90% | 0 | 34.2946
3304 | 895 | 737 | 125 | 5 | 24.7 | 42.1526 | 215.4983 | 19.1539 | 27.6568 | 42.5666 | 14.775 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.6392
3305 | 827 | 504 | 78 | 6.1 | 23.9 | 42.1576 | 173.8381 | 19.7696 | 4.2454 | 42.5651 | 14.8379 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.3181
3306 | 705 | 288 | 55 | 6.5 | 22.7 | 42.1577 | 106.9181 | 5.0837 | 0 | 42.5635 | 14.929 | 0 | 0 | 100% | 0 | 16.3101 | 63.9% | 0 | 37.0336
3307 | 389 | 89 | 29 | 5.8 | 21.3 | 0 | 50.0904 | 0 | 0 | 42.5613 | 15.0282 | 0 | 41.0701 | 97% | 0 | 23.1159 | 26.92% | 0 | 36.0723
3308 | 0 | 1 | 1 | 5.4 | 19.8 | 0 | 0 | 0 | 0 | 68.2827 | 26.24 | 0 | 68.0752 | 92% | 0 | 10.574 | 10% | 0 | 33.893
3309 | 0 | 0 | 0 | 2.8 | 18.8 | 0 | 0 | 0 | 0 | 88.0617 | 34.9098 | 0 | 87.2599 | 86% | 0 | 0 | 10% | 0 | 32.2091
3310 | 0 | 0 | 0 | 3.4 | 18.3 | 0 | 0 | 0 | 0 | 83.1265 | 32.8795 | 0 | 81.114 | 80% | 0 | 0 | 10% | 0 | 30.2545
3311 | 0 | 0 | 0 | 2.5 | 17.6 | 0 | 0 | 0 | 0 | 79.967 | 31.4931 | 0 | 78.0099 | 74% | 0 | 0 | 10% | 0 | 28.8241
3312 | 0 | 0 | 0 | 1.9 | 17.1 | 0 | 0 | 0 | 0 | 78.0679 | 30.6678 | 0 | 76.1657 | 68% | 0 | 0 | 10% | 0 | 27.9685
3313 | 0 | 0 | 0 | 1.5 | 15.7 | 0 | 0 | 0 | 0 | 77.237 | 30.3799 | 0 | 75.379 | 63% | 0 | 0 | 10% | 0 | 27.6584
3314 | 0 | 0 | 0 | 1.5 | 15.6 | 0 | 0 | 0 | 0 | 76.9011 | 30.2354 | 0 | 75.0778 | 57% | 0 | 0 | 10% | 0 | 27.4972
3315 | 0 | 0 | 0 | 1.1 | 15.7 | 0 | 0 | 0 | 0 | 77.1006 | 30.3197 | 0 | 75.3091 | 51% | 0 | 0 | 10% | 0 | 27.568
3316 | 0 | 0 | 0 | 0.8 | 15 | 0 | 0 | 0 | 0 | 76.2881 | 29.9968 | 0 | 74.5066 | 46% | 0 | 0 | 10% | 0 | 27.2353
3317 | 0 | 0 | 0 | 1.1 | 15.2 | 0 | 0 | 0 | 0 | 80.0732 | 31.6947 | 0 | 78.371 | 40% | 0 | 0 | 10% | 0 | 28.9197
3318 | 0 | 21 | 21 | 1.8 | 15.3 | 0 | 0 | 0 | 0 | 85.6114 | 34.1176 | 0 | 84.4977 | 34% | 0 | 0 | 10% | 0 | 31.3291
3319 | 1 | 102 | 101 | 1.5 | 15.5 | 0 | 0.21564 | 0.48046 | 0 | 90.0356 | 35.9715 | 0 | 89.8538 | 27% | 0 | 0 | 10% | 0 | 33.6667
3320 | 347 | 367 | 196 | 1 | 18.1 | 56.0753 | 14.1356 | 15.5282 | 0 | 55.0927 | 20.5473 | 11.6218 | 10.2596 | 27% | 0 | 0 | 10% | 0 | 34.7132
3321 | 555 | 572 | 193 | 1.5 | 19.7 | 134.2327 | 0 | 33.1212 | 0 | 43.7377 | 15.6182 | 89.9966 | 0 | 34% | 11.9022 | 0 | 26.19% | 0 | 35.2121
3322 | 935 | 830 | 86 | 2.3 | 21.1 | 251.0364 | 0 | 48.1991 | 9.8397 | 42.5207 | 15.0276 | 207.774 | 0 | 49% | 25 | 0 | 60.19% | 0 | 35.5543
3323 | 971 | 952 | 80 | 3.2 | 22.3 | 270.2742 | 0 | 45.05 | 25.7102 | 42.5543 | 14.9554 | 227.8726 | 0 | 66% | 21.9213 | 0 | 90% | 0 | 35.1999
3324 | 974 | 1021 | 91 | 2.8 | 23.2 | 276.5828 | 5.96e-14 | 20.3338 | 54.7662 | 42.5694 | 14.8934 | 234.2166 | 0 | 83% | 0 | 0 | 90% | 0 | 33.5752
3325 | 970 | 1037 | 106 | 3.1 | 23.5 | 275.8998 | 0 | 13.5337 | 61.5663 | 42.5793 | 14.8737 | 233.4943 | 0 | 100% | 0 | 0 | 90% | 0 | 32.4004
3326 | 947 | 983 | 116 | 4 | 23.8 | 41.3256 | 254.625 | 16.4832 | 56.7265 | 42.5853 | 14.8527 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.0465
3327 | 916 | 852 | 98 | 5.8 | 23.9 | 42.1521 | 234.4814 | 16.7829 | 42.9394 | 42.5832 | 14.8442 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.3377
3328 | 839 | 681 | 104 | 4.9 | 23.3 | 42.1577 | 198.7325 | 17.5971 | 24.6831 | 42.5812 | 14.8898 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.1976
3329 | 790 | 491 | 79 | 3.9 | 23.5 | 42.1577 | 164.2304 | 18.8832 | 3.9974 | 42.5792 | 14.8737 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.4675
3330 | 686 | 290 | 60 | 4.5 | 23.6 | 42.1577 | 103.4268 | 5.1571 | 0 | 42.5773 | 14.8653 | 0 | 0 | 100% | 0 | 15.8712 | 64.61% | 0 | 36.6043
3331 | 112 | 67 | 47 | 5.6 | 21.9 | 0 | 18.2671 | 0 | 0 | 42.5747 | 14.9917 | 0 | 41.0812 | 97% | 0 | 23.6262 | 26.8% | 0 | 36.5604
3332 | 0 | 1 | 1 | 3.3 | 20.3 | 0 | 0 | 0 | 0 | 69.0456 | 26.5304 | 0 | 68.9357 | 92% | 0 | 10.5025 | 10% | 0 | 34.1143
3333 | 0 | 0 | 0 | 0.6 | 17.6 | 0 | 0 | 0 | 0 | 87.4973 | 34.756 | 0 | 86.4991 | 86% | 0 | 0 | 10% | 0 | 32.077
3334 | 0 | 0 | 0 | 0.9 | 18.2 | 0 | 0 | 0 | 0 | 82.9975 | 32.8312 | 0 | 80.9616 | 80% | 0 | 0 | 10% | 0 | 30.2061
3335 | 0 | 0 | 0 | 1.6 | 17.9 | 0 | 0 | 0 | 0 | 80.6875 | 31.799 | 0 | 78.7489 | 74% | 0 | 0 | 10% | 0 | 29.1269
3336 | 0 | 0 | 0 | 2.1 | 16.8 | 0 | 0 | 0 | 0 | 80.1669 | 31.6337 | 0 | 78.3003 | 68% | 0 | 0 | 10% | 0 | 28.9312
3337 | 0 | 0 | 0 | 2.2 | 16.4 | 0 | 0 | 0 | 0 | 80.4155 | 31.7721 | 0 | 78.6047 | 62% | 0 | 0 | 10% | 0 | 29.0483
3338 | 0 | 0 | 0 | 1.3 | 15.4 | 0 | 0 | 0 | 0 | 81.8976 | 32.5101 | 0 | 80.1488 | 56% | 0 | 0 | 10% | 0 | 29.7696
3339 | 0 | 0 | 0 | 1.2 | 15.1 | 0 | 0 | 0 | 0 | 89.9782 | 35.9715 | 0 | 89.7304 | 50% | 0 | 0 | 10% | 0 | 33.2104
3340 | 0 | 0 | 0 | 1.8 | 15.7 | 0 | 0 | 0 | 0 | 99.133 | 39.786 | 0 | 100.7358 | 42% | 0 | 0 | 10% | 0 | 37.0563
3341 | 0 | 0 | 0 | 1.5 | 15 | 0 | 0 | 0 | 0 | 107.0783 | 43.1715 | 0 | 110.0002 | 34% | 0 | 0 | 10% | 0 | 40.5242
3342 | 284 | 58 | 23 | 1.3 | 14.9 | 0 | 42.687 | 0 | 0 | 111.1072 | 44.8558 | 0 | 114.3013 | 26% | 0 | 0 | 10% | 0 | 42.318
3343 | 672 | 247 | 50 | 0.9 | 18.5 | 96.9347 | 23.9733 | 2.2948 | 0 | 106.1519 | 42.5153 | 6.2278 | 20.2147 | 25% | 0 | 0 | 10% | 0 | 43.0731
3344 | 824 | 459 | 64 | 0.7 | 21.2 | 186.7712 | -2.98e-14 | 19.7333 | 0 | 67.494 | 25.7046 | 120.1673 | 0 | 34% | 0 | 0 | 10% | 0 | 43.2853
3345 | 893 | 657 | 76 | 1.2 | 22.8 | 226.3727 | 0 | 39.6699 | 0 | 45.4152 | 16.0904 | 181.8638 | 0 | 47% | 9.6303 | 0 | 23.1% | 0 | 43.6356
3346 | 930 | 832 | 95 | 2.2 | 23.5 | 249.55 | 0 | 56.3768 | 1.557 | 42.5748 | 14.8721 | 207.8568 | 0 | 63% | 25 | 0 | 57.1% | 0 | 43.5251
3347 | 940 | 953 | 110 | 3.6 | 24.2 | 260.7474 | 0 | 54.4165 | 16.0079 | 42.5855 | 14.8214 | 218.9964 | 0 | 79% | 24.1932 | 0 | 90% | 0 | 42.1929
3348 | 952 | 1046 | 137 | 4.6 | 24.6 | 268.8726 | 0 | 27.9529 | 47.1471 | 42.5915 | 14.7916 | 226.9471 | 0 | 96% | 0 | 0 | 90% | 0 | 41.4193
3349 | 480 | 728 | 263 | 4 | 24.1 | 100.5345 | 32.5672 | 25.1796 | 27.6965 | 42.5952 | 14.8327 | 58.8871 | 0 | 100% | 0 | 0 | 90% | 0 | 41.0693
3350 | 406 | 691 | 315 | 3 | 24.1 | 42.1532 | 76.5854 | 25.3256 | 23.0362 | 42.5943 | 14.8324 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.8686
3351 | 760 | 842 | 219 | 3.5 | 24.8 | 42.1576 | 185.8825 | 24.7832 | 34.4521 | 42.5919 | 14.7758 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.2694
3352 | 739 | 652 | 141 | 5.1 | 24.5 | 42.1576 | 168.6104 | 24.4717 | 15.5519 | 42.5897 | 14.7989 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.9811
3353 | 82 | 270 | 224 | 4.9 | 23.7 | 0 | 22.2137 | 9.9928 | 0 | 42.5867 | 14.8609 | 0 | 41.0953 | 97% | 0 | 17.8565 | 61.43% | 0 | 40.6496
3354 | 522 | 271 | 99 | 3.6 | 24 | 75.8765 | 18.6613 | 5.4209 | 0 | 42.5836 | 14.8367 | 40.1102 | 7.3736 | 99% | 0 | 21.594 | 26.88% | 0 | 41.9205
3355 | 178 | 85 | 52 | 3.9 | 21.7 | 0 | 29.1515 | 0 | 0 | 84.1611 | 32.7973 | 0 | 86.6095 | 93% | 0 | 9.1625 | 12.22% | 0 | 39.8757
3356 | 0 | 2 | 2 | 2.6 | 20 | 0 | 0 | 0 | 0 | 97.929 | 38.9585 | 0 | 97.8645 | 86% | 0 | 0 | 12.22% | 0 | 36.6438
3357 | 0 | 0 | 0 | 1.7 | 19.6 | 0 | 0 | 0 | 0 | 93.0617 | 36.9578 | 0 | 91.6879 | 79% | 0 | 0 | 12.22% | 0 | 34.7538
3358 | 0 | 0 | 0 | 1.6 | 18.7 | 0 | 0 | 0 | 0 | 88.7057 | 35.1867 | 0 | 86.4722 | 72% | 0 | 0 | 12.22% | 0 | 32.9563
3359 | 0 | 0 | 0 | 2.2 | 17.4 | 0 | 0 | 0 | 0 | 86.0279 | 34.1527 | 0 | 83.5099 | 66% | 0 | 0 | 12.22% | 0 | 31.8493
3360 | 0 | 0 | 0 | 2.9 | 16.7 | 0 | 0 | 0 | 0 | 85.099 | 33.8097 | 0 | 82.635 | 60% | 0 | 0 | 12.22% | 0 | 31.4325
3361 | 0 | 0 | 0 | 2.8 | 16.7 | 0 | 0 | 0 | 0 | 85.4669 | 33.9642 | 0 | 83.245 | 54% | 0 | 0 | 12.22% | 0 | 31.5273
3362 | 0 | 0 | 0 | 2.7 | 16 | 0 | 0 | 0 | 0 | 86.4637 | 34.429 | 0 | 84.5507 | 47% | 0 | 0 | 12.22% | 0 | 31.9497
3363 | 0 | 0 | 0 | 1 | 15.2 | 0 | 0 | 0 | 0 | 92.8767 | 37.1947 | 0 | 92.4516 | 40% | 0 | 0 | 12.22% | 0 | 34.6813
3364 | 0 | 0 | 0 | 0.7 | 14.4 | 0 | 0 | 0 | 0 | 101.1958 | 40.7444 | 0 | 102.3297 | 33% | 0 | 0 | 12.22% | 0 | 38.2417
3365 | 0 | 0 | 0 | 1.1 | 14.2 | 0 | 0 | 0 | 0 | 108.7145 | 43.9096 | 0 | 111.0955 | 24% | 0 | 0 | 12.22% | 0 | 41.4561
3366 | 0 | 28 | 28 | 1.3 | 14 | 0 | 0 | 0 | 0 | 111.6011 | 45.1276 | 0 | 114.1573 | 16% | 0 | 0 | 12.22% | 0 | 42.7515
3367 | 113 | 160 | 125 | 1.3 | 16 | 0 | 24.4401 | 2.0533 | 0 | 108.3842 | 43.6384 | 0 | 109.9994 | 8% | 0 | 0 | 12.22% | 0 | 43.3965
3368 | 22 | 260 | 246 | 2.1 | 18.1 | 0 | 5.813 | 9.2956 | 0 | 92.2727 | 36.7409 | 0 | 90.6298 | 1% | 0 | 0 | 12.22% | 0 | 43.8194
3369 | 390 | 566 | 295 | 3.1 | 20.4 | 72.1739 | 18.066 | 30.6829 | 1.6853 | 42.3967 | 15.0297 | 37.3044 | 7.2274 | 3% | 0 | 0 | 12.22% | 0 | 44.3254
3370 | 794 | 811 | 177 | 3.8 | 22.3 | 209.1817 | 0 | 56.4288 | 0 | 42.5185 | 14.9428 | 166.3479 | 0 | 16% | 24.9514 | 0 | 46.15% | 0 | 44.1358
3371 | 921 | 966 | 138 | 4.5 | 23.6 | 254.1938 | 0 | 55.7851 | 15.5223 | 42.5913 | 14.8702 | 212.7333 | 0 | 32% | 25 | 0 | 80.15% | 0 | 42.9395
3372 | 287 | 490 | 214 | 6.6 | 23.3 | 65.9127 | 0 | 32.4698 | 0 | 42.6048 | 14.8981 | 25.5032 | 0 | 33% | 4.2731 | 0 | 85.97% | 0 | 42.0508
3373 | 2 | 80 | 77 | 4.4 | 16.5 | 0 | 0.64824 | 0 | 0 | 49.1898 | 18.0842 | 0 | 46.6376 | 30% | 0 | 25 | 45.97% | 0 | 41.5879
3374 | 365 | 634 | 301 | 3.3 | 18.8 | 74.0771 | 18.6301 | 44.741 | 0 | 42.9921 | 15.3633 | 39.0379 | 7.7656 | 32% | 17.1688 | 0 | 69.31% | 0 | 41.4737
3375 | 651 | 852 | 308 | 3.6 | 20.8 | 170.054 | 1.17e-14 | 42.8175 | 17.1511 | 42.5878 | 15.0713 | 127.955 | 0 | 42% | 15.2103 | 0 | 90% | 0 | 40.7107
3376 | 443 | 599 | 286 | 3.7 | 21.4 | 104.1215 | 0 | 26.8528 | 9.1272 | 42.5916 | 15.032 | 62.9663 | 0 | 46% | 0 | 0 | 90% | 0 | 40.5008
3377 | 24 | 162 | 149 | 3.8 | 20.4 | 0 | 6.5057 | 3.8961 | 0 | 42.5893 | 15.0979 | 0 | 40.5711 | 43% | 0 | 23.8592 | 51.82% | 0 | 41.1376
3378 | 252 | 228 | 139 | 3.9 | 20.7 | 0 | 57.2441 | 4.6917 | 0 | 42.5838 | 15.0764 | 0 | 40.5847 | 40% | 0 | 24.7096 | 12.29% | 0 | 41.8244
3379 | 21 | 44 | 40 | 3.8 | 19.3 | 0 | 3.4532 | 0 | 0 | 107.5694 | 43.033 | 0 | 110.9882 | 32% | 0 | 0 | 12.29% | 0 | 40.28
3380 | 0 | 2 | 2 | 3.8 | 17.5 | 0 | 0 | 0 | 0 | 99.0224 | 39.6064 | 0 | 100.093 | 25% | 0 | 0 | 12.29% | 0 | 36.9957
3381 | 0 | 0 | 0 | 3.9 | 16.1 | 0 | 0 | 0 | 0 | 94.1589 | 37.6773 | 0 | 94.0992 | 18% | 0 | 0 | 12.29% | 0 | 35.1303
3382 | 0 | 0 | 0 | 3 | 15.3 | 0 | 0 | 0 | 0 | 89.8118 | 35.8879 | 0 | 88.6246 | 11% | 0 | 0 | 12.29% | 0 | 33.3731
3383 | 0 | 0 | 0 | 2.5 | 14.9 | 0 | 0 | 0 | 0 | 86.8691 | 34.6722 | 0 | 85.0644 | 5% | 0 | 0 | 12.29% | 0 | 32.1611
3384 | 0 | 0 | 0 | 1.9 | 14.8 | 0 | 0 | 0 | 0 | 66.0859 | 26.3673 | 0 | 64.5936 | 0% | 0 | 0 | 12.29% | 0 | 23.8666
3385 | 0 | 0 | 0 | 1.3 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.29% | 0 | -2.4204
3386 | 0 | 0 | 0 | 1.9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.29% | 0 | -2.3958
3387 | 0 | 0 | 0 | 2.1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.29% | 0 | -2.3716
3388 | 0 | 0 | 0 | 2.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.29% | 0 | -2.3479
3389 | 0 | 0 | 0 | 1.1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.29% | 0 | -2.3246
3390 | 264 | 58 | 25 | 1.9 | 13.1 | 0 | 39.9595 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.29% | 0 | -2.3016
3391 | 640 | 243 | 53 | 0.6 | 16.7 | 91.9255 | 22.8898 | 2.23 | 0 | 0 | 0 | 87.824 | 0 | 7% | 0 | 0 | 12.29% | 0 | 0.6831
3392 | 797 | 453 | 68 | 0.7 | 19.2 | 180.2531 | 0 | 19.2994 | 0 | 0 | 0 | 177.2165 | 0 | 20% | 0 | 0 | 12.29% | 0 | 17.302
3393 | 871 | 646 | 77 | 1.2 | 21.1 | 220.3685 | 0 | 38.723 | 0 | 0 | 0 | 218.2991 | 0 | 36% | 0 | 0 | 12.29% | 0 | 36.3374
3394 | 914 | 811 | 83 | 1.7 | 22.5 | 245.0158 | 0 | 55.8272 | 0 | 42.5293 | 0 | 203.3039 | 0 | 52% | 13.4176 | 0 | 30.54% | 0 | 39.2369
3395 | 939 | 932 | 89 | 2.4 | 24.2 | 261.0274 | 0 | 68.3344 | 0 | 0 | 0 | 259.5224 | 0 | 71% | 23.5013 | 0 | 62.5% | 0 | 42.0061
3396 | 942 | 1000 | 102 | 3.1 | 25.3 | 267.0227 | 0 | 66.1197 | 8.9803 | 0 | 0 | 265.6845 | 0 | 91% | 20.2208 | 0 | 90% | 0 | 42.9558
3397 | 921 | 1006 | 122 | 4.7 | 25.8 | 122.0212 | 151.4424 | 44.3132 | 30.7868 | 0 | 0 | 121.4436 | 0 | 100% | 0 | 0 | 90% | 0 | 42.5773
3398 | 720 | 851 | 187 | 6.3 | 25.9 | 41.5278 | 180.3526 | 35.798 | 24.6202 | 42.5795 | 7.5501 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.5114
3399 | 830 | 866 | 181 | 4.2 | 26.6 | 42.1653 | 207.7142 | 26.5268 | 33.2295 | 42.578 | 14.6221 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.859
3400 | 775 | 683 | 148 | 4.5 | 26.2 | 42.1575 | 179.7423 | 26.2746 | 15.8724 | 42.5762 | 14.6553 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.64
3401 | 754 | 487 | 92 | 5.1 | 25.6 | 42.1575 | 154.3658 | 22.4583 | 0 | 42.5744 | 14.7044 | 0 | 0 | 100% | 0 | 4.2092 | 83.27% | 0 | 42.0822
3402 | 613 | 271 | 67 | 3.5 | 24.9 | 42.1576 | 87.2229 | 4.6401 | 0 | 42.5726 | 14.7611 | 0 | 0 | 100% | 0 | 22.6434 | 47.04% | 0 | 42.7551
3403 | 277 | 81 | 31 | 4.1 | 22.7 | 0 | 45.7315 | 0 | 0 | 54.292 | 19.8695 | 0 | 53.2577 | 96% | 0 | 23.1474 | 10% | 0 | 40.9489
3404 | 0 | 2 | 2 | 3.4 | 20.3 | 0 | 0 | 0 | 0 | 101.236 | 40.3132 | 0 | 103.8869 | 88% | 0 | 0 | 10% | 0 | 37.4586
3405 | 0 | 0 | 0 | 3.4 | 18.5 | 0 | 0 | 0 | 0 | 94.6034 | 37.6895 | 0 | 94.0202 | 81% | 0 | 0 | 10% | 0 | 35.3573
3406 | 0 | 0 | 0 | 2 | 17.3 | 0 | 0 | 0 | 0 | 89.7858 | 35.741 | 0 | 87.9578 | 75% | 0 | 0 | 10% | 0 | 33.4573
3407 | 0 | 0 | 0 | 1.8 | 16.4 | 0 | 0 | 0 | 0 | 86.6983 | 34.5012 | 0 | 84.4037 | 68% | 0 | 0 | 10% | 0 | 32.1691
3408 | 0 | 0 | 0 | 1 | 15.5 | 0 | 0 | 0 | 0 | 85.4999 | 34.056 | 0 | 83.1772 | 62% | 0 | 0 | 10% | 0 | 31.6594
3409 | 0 | 0 | 0 | 0.4 | 14.8 | 0 | 0 | 0 | 0 | 85.3102 | 34.0208 | 0 | 83.1138 | 56% | 0 | 0 | 10% | 0 | 31.5693
3410 | 0 | 0 | 0 | 0.6 | 14.4 | 0 | 0 | 0 | 0 | 86.7628 | 34.6575 | 0 | 84.9647 | 50% | 0 | 0 | 10% | 0 | 32.163
3411 | 0 | 0 | 0 | 1.5 | 14.7 | 0 | 0 | 0 | 0 | 92.6971 | 37.152 | 0 | 92.2765 | 43% | 0 | 0 | 10% | 0 | 34.628
3412 | 0 | 0 | 0 | 1.6 | 14.6 | 0 | 0 | 0 | 0 | 100.7282 | 40.5344 | 0 | 101.8115 | 35% | 0 | 0 | 10% | 0 | 38.0235
3413 | 0 | 0 | 0 | 1 | 13.7 | 0 | 0 | 0 | 0 | 107.3194 | 43.3637 | 0 | 109.4891 | 27% | 0 | 0 | 10% | 0 | 40.9049
3414 | 279 | 59 | 25 | 2.2 | 16 | 0 | 42.3658 | 0 | 0 | 111.1809 | 44.8015 | 0 | 113.7116 | 18% | 0 | 0 | 10% | 0 | 42.4168
3415 | 645 | 246 | 54 | 1.3 | 18.2 | 92.7173 | 22.9744 | 2.2729 | 0 | 106.482 | 42.6762 | 2.131 | 20.1274 | 17% | 0 | 0 | 10% | 0 | 43.2679
3416 | 797 | 455 | 68 | 1 | 21.5 | 180.1164 | 0 | 19.0947 | 0 | 70.2216 | 26.8878 | 111.0449 | 0 | 25% | 0 | 0 | 10% | 0 | 43.8874
3417 | 867 | 651 | 83 | 1 | 24.6 | 219.3768 | 0 | 38.5102 | 0 | 45.5986 | 16.0223 | 174.9013 | 0 | 39% | 7.4407 | 0 | 20.12% | 0 | 44.6662
3418 | 892 | 806 | 93 | 1.2 | 26.6 | 238.8747 | 0 | 54.4237 | 0 | 46.4214 | 16.1887 | 193.6999 | 0 | 53% | 23.159 | 0 | 51.62% | 0 | 44.8299
3419 | 941 | 936 | 89 | 1.6 | 27.7 | 262.0063 | 0 | 56.946 | 10.6587 | 42.5905 | 14.5318 | 220.4265 | 0 | 70% | 25 | 0 | 85.62% | 0 | 43.6238
3420 | 870 | 977 | 143 | 2.4 | 28.7 | 245.7396 | 0 | 34.3954 | 37.3048 | 42.597 | 14.4457 | 204.1067 | 0 | 85% | 3.2238 | 0 | 90% | 0 | 42.8902
3421 | 922 | 997 | 111 | 4.7 | 29.2 | 249.569 | 12.5156 | 26.2569 | 47.4575 | 42.5995 | 14.4021 | 207.6129 | 0 | 100% | 0 | 0 | 90% | 0 | 42.7023
3422 | 931 | 951 | 98 | 5.3 | 29.4 | 42.1516 | 248.2293 | 27.4476 | 41.343 | 42.6011 | 14.3849 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.5419
3423 | 896 | 834 | 96 | 6.2 | 29.3 | 42.1572 | 228.1117 | 26.7525 | 30.1147 | 42.5986 | 14.3929 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8548
3424 | 870 | 685 | 85 | 6.2 | 29 | 42.1572 | 208.0358 | 26.5486 | 14.7903 | 42.5962 | 14.4188 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.6769
3425 | 779 | 491 | 81 | 6 | 28.3 | 42.1573 | 161.2531 | 22.217 | 0 | 42.5938 | 14.4802 | 0 | 0 | 100% | 0 | 4.5854 | 82.66% | 0 | 41.9923
3426 | 626 | 282 | 69 | 5.5 | 27 | 42.1574 | 89.903 | 4.8571 | 0 | 42.5915 | 14.5929 | 0 | 0 | 100% | 0 | 22.5789 | 46.54% | 0 | 42.7388
3427 | 304 | 94 | 41 | 4.6 | 25.5 | 0 | 50.3864 | 0 | 0 | 55.1861 | 20.011 | 0 | 54.2394 | 96% | 0 | 22.8357 | 10% | 0 | 40.7756
3428 | 0 | 1 | 1 | 3.7 | 23.7 | 0 | 0 | 0 | 0 | 101.5738 | 40.1452 | 0 | 104.219 | 88% | 0 | 0 | 10% | 0 | 37.3094
3429 | 0 | 0 | 0 | 3.2 | 23 | 0 | 0 | 0 | 0 | 96.2371 | 37.9974 | 0 | 95.8815 | 81% | 0 | 0 | 10% | 0 | 35.677
3430 | 0 | 0 | 0 | 2.2 | 22.4 | 0 | 0 | 0 | 0 | 91.8713 | 36.2259 | 0 | 90.3903 | 74% | 0 | 0 | 10% | 0 | 33.9709
3431 | 0 | 0 | 0 | 2.1 | 20.6 | 0 | 0 | 0 | 0 | 88.5472 | 34.9783 | 0 | 86.441 | 68% | 0 | 0 | 10% | 0 | 32.6963
3432 | 0 | 0 | 0 | 1.1 | 18.4 | 0 | 0 | 0 | 0 | 87.2127 | 34.581 | 0 | 85.0165 | 62% | 0 | 0 | 10% | 0 | 32.2426
3433 | 0 | 0 | 0 | 0.1 | 17.4 | 0 | 0 | 0 | 0 | 86.7104 | 34.4392 | 0 | 84.5694 | 55% | 0 | 0 | 10% | 0 | 32.0501
3434 | 0 | 0 | 0 | 0.8 | 17.6 | 0 | 0 | 0 | 0 | 88.0537 | 34.9905 | 0 | 86.3006 | 49% | 0 | 0 | 10% | 0 | 32.5586
3435 | 0 | 0 | 0 | 1.6 | 16.4 | 0 | 0 | 0 | 0 | 93.5949 | 37.4175 | 0 | 93.1644 | 42% | 0 | 0 | 10% | 0 | 34.9559
3436 | 0 | 0 | 0 | 0.5 | 15.8 | 0 | 0 | 0 | 0 | 101.589 | 40.8093 | 0 | 102.6069 | 34% | 0 | 0 | 10% | 0 | 38.3578
3437 | 0 | 0 | 0 | 0.7 | 15.1 | 0 | 0 | 0 | 0 | 108.2401 | 43.6465 | 0 | 110.3337 | 26% | 0 | 0 | 10% | 0 | 41.2421
3438 | 93 | 65 | 50 | 0.8 | 16.9 | 0 | 14.1648 | 0 | 0 | 112.4575 | 45.259 | 0 | 115.0023 | 17% | 0 | 0 | 10% | 0 | 42.9231
3439 | 145 | 182 | 137 | 0.6 | 20.2 | 0 | 31.4812 | 2.7175 | 0 | 107.9586 | 43.1202 | 0 | 109.3275 | 9% | 0 | 0 | 10% | 0 | 43.5851
3440 | 61 | 250 | 219 | 0.4 | 22 | 0 | 16.133 | 8.6607 | 0 | 94.9649 | 37.5654 | 0 | 93.7457 | 2% | 0 | 0 | 10% | 0 | 44.0402
3441 | 33 | 299 | 273 | 1.1 | 23.8 | 0 | 9.622 | 12.7961 | 0 | 24.6368 | 9.6465 | 0 | 23.8437 | 0% | 0 | 0 | 10% | 0 | 20.3346
3442 | 15 | 325 | 309 | 1.8 | 24.8 | 0 | 4.6007 | 14.2026 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 12.1362
3443 | 190 | 611 | 426 | 2.1 | 26.2 | 0 | 49.4724 | 38.9061 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 36.8604
3444 | 298 | 751 | 452 | 2.3 | 27.6 | 72.2183 | 1.49e-14 | 51.989 | 0 | 0 | 0 | 69.4311 | 0 | 5% | 8.9431 | 0 | 22.16% | 0 | 42.0027
3445 | 208 | 727 | 513 | 2.1 | 28.3 | 0 | 54.1362 | 49.2127 | 0 | 0 | 0 | 0 | 0 | 5% | 6.9589 | 0 | 31.63% | 0 | 41.133
3446 | 52 | 492 | 438 | 7.7 | 25.9 | 0 | 16.5719 | 28.9259 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 13.5167 | 10% | 0 | 40.4284
3447 | 107 | 467 | 374 | 8.2 | 23.4 | 0 | 33.0823 | 27.1909 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | 25.1936
3448 | 463 | 597 | 281 | 7.6 | 23.3 | 86.9159 | 22.0365 | 36.3119 | 0 | 0 | 0 | 83.7085 | 0 | 12% | 0 | 0 | 10% | 0 | 34.8563
3449 | 235 | 338 | 206 | 7.6 | 21.4 | 0 | 50.4103 | 13.9309 | 0 | 43.23 | 0.74642 | 0 | 40.2563 | 9% | 0 | 0 | 10% | 0 | 13.0789
3450 | 2 | 69 | 68 | 6.8 | 19.1 | 0 | 0.45676 | 0 | 0 | 107.5582 | 43.0519 | 0 | 108.5263 | 0% | 0 | 0 | 10% | 0 | 40.8867
3451 | 10 | 46 | 44 | 7.2 | 18.2 | 0 | 1.6639 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9844
3452 | 0 | 2 | 2 | 6.4 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9679
3453 | 0 | 0 | 0 | 5.7 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9518
3454 | 0 | 0 | 0 | 4.4 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9359
3455 | 0 | 0 | 0 | 3.2 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9204
3456 | 0 | 0 | 0 | 3 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9051
3457 | 0 | 0 | 0 | 3.1 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8902
3458 | 0 | 0 | 0 | 2.2 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8756
3459 | 0 | 0 | 0 | 2 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8613
3460 | 0 | 0 | 0 | 1.5 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8472
3461 | 0 | 0 | 0 | 1.2 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8334
3462 | 325 | 62 | 23 | 0.4 | 13.4 | 0 | 49.6414 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8197
3463 | 625 | 245 | 60 | 0.6 | 17.1 | 89.6567 | 22.3577 | 2.287 | 0 | 0 | 0 | 84.5488 | 0 | 7% | 0 | 0 | 10% | 0 | 0.83217
3464 | 770 | 479 | 103 | 1.2 | 19.2 | 173.3479 | 0 | 20.9459 | 0 | 0 | 0 | 169.3882 | 0 | 20% | 0 | 0 | 10% | 0 | 18.9793
3465 | 888 | 658 | 75 | 1.7 | 20.6 | 224.5752 | 0 | 39.2099 | 0 | 0 | 0 | 221.77 | 0 | 37% | 0 | 0 | 10% | 0 | 36.748
3466 | 937 | 840 | 91 | 2.6 | 22.1 | 250.9325 | 0 | 57.8048 | 0 | 42.4652 | 0 | 209.5524 | 0 | 53% | 21.279 | 0 | 38.94% | 0 | 33.2529
3467 | 126 | 365 | 250 | 2.3 | 22 | 0 | 39.9552 | 20.0828 | 0 | 42.5122 | 9.6259 | 0 | 39.5192 | 50% | 0 | 9.6592 | 23.48% | 0 | 38.1218
3468 | 9 | 291 | 278 | 4.2 | 21.8 | 0 | 2.9105 | 12.125 | 0 | 49.2077 | 17.8469 | 0 | 46.164 | 47% | 0 | 8.428 | 10% | 0 | 36.3346
3469 | 27 | 312 | 280 | 3.7 | 21.6 | 0 | 8.751 | 15.1895 | 0 | 59.0789 | 22.0247 | 0 | 55.7555 | 42% | 0 | 0 | 10% | 0 | 35.077
3470 | 52 | 322 | 268 | 1.7 | 21.5 | 0 | 16.5711 | 15.7384 | 0 | 56.8877 | 21.1039 | 0 | 53.7488 | 38% | 0 | 0 | 10% | 0 | 34.6316
3471 | 31 | 266 | 237 | 2.1 | 21.7 | 0 | 9.5846 | 11.3431 | 0 | 67.2392 | 25.5577 | 0 | 64.1923 | 34% | 0 | 0 | 10% | 0 | 34.614
3472 | 14 | 184 | 172 | 3.2 | 20.9 | 0 | 4.1423 | 4.9914 | 0 | 82.217 | 32.2919 | 0 | 79.2961 | 28% | 0 | 0 | 10% | 0 | 34.9216
3473 | 83 | 177 | 127 | 2.9 | 20.6 | 0 | 22.5562 | 4.2423 | 0 | 85.3778 | 33.657 | 0 | 83.0448 | 21% | 0 | 0 | 10% | 0 | 35.4845
3474 | 100 | 144 | 105 | 4.1 | 19.1 | 0 | 22.8779 | 1.498 | 0 | 95.1974 | 37.8961 | 0 | 95.0451 | 14% | 0 | 0 | 10% | 0 | 36.9322
3475 | 122 | 59 | 39 | 3 | 18.7 | 0 | 20.376 | 0 | 0 | 97.71 | 38.9736 | 0 | 97.9367 | 7% | 0 | 0 | 10% | 0 | 36.5263
3476 | 0 | 2 | 2 | 2.3 | 17 | 0 | 0 | 0 | 0 | 92.9726 | 37.1202 | 0 | 92.2073 | 0% | 0 | 0 | 10% | 0 | 34.7058
3477 | 0 | 0 | 0 | 2.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2877
3478 | 0 | 0 | 0 | 1.5 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2656
3479 | 0 | 0 | 0 | 0.6 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2439
3480 | 0 | 0 | 0 | 1.1 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2225
3481 | 0 | 0 | 0 | 1.2 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2016
3482 | 0 | 0 | 0 | 1.6 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1811
3483 | 0 | 0 | 0 | 0.8 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.161
3484 | 0 | 0 | 0 | 0.6 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1413
3485 | 0 | 1 | 1 | 0.9 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1219
3486 | 318 | 62 | 24 | 0.8 | 13.7 | 0 | 48.7015 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1028
3487 | 664 | 250 | 49 | 0.8 | 17.9 | 96.3584 | 23.9138 | 2.0754 | 0 | 0 | 0 | 91.1388 | 0 | 7% | 0 | 0 | 10% | 0 | 0.52136
3488 | 799 | 455 | 64 | 0.8 | 20.6 | 180.8365 | 2.98e-14 | 18.732 | 0 | 0 | 0 | 177.2025 | 0 | 21% | 0 | 0 | 10% | 0 | 16.7158
3489 | 869 | 649 | 75 | 1 | 22.2 | 219.8607 | 0 | 37.9911 | 0 | 0 | 0 | 217.4175 | 0 | 37% | 2.8206 | 0 | 13.84% | 0 | 32.7728
3490 | 883 | 822 | 114 | 1.4 | 23.2 | 235.964 | 0 | 55.9277 | 0 | 0 | 0 | 234.0732 | 0 | 55% | 20.3886 | 0 | 41.57% | 0 | 32.9545
3491 | 161 | 475 | 325 | 2.6 | 23 | 0 | 51.0474 | 28.654 | 0 | 42.5231 | 0 | 0 | 39.7458 | 52% | 8.2942 | 0 | 52.84% | 0 | 18.6472
3492 | 458 | 751 | 302 | 4.6 | 23.7 | 97.8347 | 24.049 | 47.3676 | 6.1008 | 42.5187 | 10.0953 | 63.7234 | 7.1733 | 56% | 23.1481 | 0 | 84.33% | 0 | 32.5007
3493 | 763 | 988 | 249 | 6.4 | 24.1 | 210.4133 | 2.48e-14 | 23.5912 | 50.0941 | 42.5292 | 14.8097 | 168.7767 | 0 | 69% | 4.172 | 0 | 90% | 0 | 31.8367
3494 | 902 | 950 | 119 | 6.5 | 24.4 | 248.1123 | 0 | 19.4615 | 49.7292 | 42.5438 | 14.7909 | 206.2336 | 0 | 84% | 0 | 0 | 90% | 0 | 31.4955
3495 | 870 | 830 | 109 | 6.9 | 24.3 | 230.4193 | 0 | 17.6341 | 39.3337 | 42.5577 | 14.8037 | 188.5546 | 0 | 98% | 0 | 0 | 90% | 0 | 32.1226
3496 | 849 | 680 | 89 | 6.9 | 23.8 | 69.0818 | 170.1246 | 17.415 | 23.7719 | 42.5667 | 14.8462 | 27.5506 | 0 | 100% | 0 | 0 | 90% | 0 | 32.8091
3497 | 786 | 492 | 74 | 6.5 | 23.3 | 42.1524 | 163.4733 | 18.6084 | 3.6541 | 42.5655 | 14.8843 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.2035
3498 | 661 | 287 | 58 | 5.1 | 22.8 | 42.1577 | 99.24 | 4.8376 | 0 | 42.564 | 14.9217 | 0 | 0 | 100% | 0 | 15.5732 | 65.08% | 0 | 36.0434
3499 | 414 | 99 | 31 | 4.3 | 21.5 | 0 | 56.3153 | 0 | 0 | 42.5618 | 15.0146 | 0 | 41.0706 | 97% | 0 | 23.8396 | 26.94% | 0 | 36.7824
3500 | 1 | 3 | 3 | 3.2 | 19.6 | 0 | 0 | 0 | 0 | 69.8942 | 26.9401 | 0 | 69.95 | 92% | 0 | 10.5872 | 10% | 0 | 34.6051
3501 | 0 | 0 | 0 | 2.3 | 18.4 | 0 | 0 | 0 | 0 | 88.4686 | 35.1093 | 0 | 87.6335 | 85% | 0 | 0 | 10% | 0 | 32.4457
3502 | 0 | 0 | 0 | 1.6 | 16.9 | 0 | 0 | 0 | 0 | 83.4863 | 33.122 | 0 | 81.448 | 79% | 0 | 0 | 10% | 0 | 30.5262
3503 | 0 | 0 | 0 | 0.5 | 16 | 0 | 0 | 0 | 0 | 81.0292 | 32.0768 | 0 | 79.0129 | 73% | 0 | 0 | 10% | 0 | 29.4324
3504 | 0 | 0 | 0 | 0.8 | 15.1 | 0 | 0 | 0 | 0 | 80.0321 | 31.6789 | 0 | 78.0998 | 68% | 0 | 0 | 10% | 0 | 28.9981
3505 | 0 | 0 | 0 | 1 | 14.3 | 0 | 0 | 0 | 0 | 79.9967 | 31.711 | 0 | 78.1282 | 62% | 0 | 0 | 10% | 0 | 29.0047
3506 | 0 | 0 | 0 | 1 | 14.3 | 0 | 0 | 0 | 0 | 81.6466 | 32.4638 | 0 | 79.8512 | 56% | 0 | 0 | 10% | 0 | 29.7375
3507 | 0 | 0 | 0 | 0.7 | 13.6 | 0 | 0 | 0 | 0 | 88.7982 | 35.567 | 0 | 88.2459 | 49% | 0 | 0 | 10% | 0 | 32.8188
3508 | 0 | 0 | 0 | 0.8 | 13.8 | 0 | 0 | 0 | 0 | 97.6906 | 39.3117 | 0 | 99.0036 | 42% | 0 | 0 | 10% | 0 | 36.5837
3509 | 0 | 1 | 1 | 2.1 | 12.4 | 0 | 0 | 0 | 0 | 105.7399 | 42.7895 | 0 | 108.4573 | 34% | 0 | 0 | 10% | 0 | 40.1343
3510 | 359 | 65 | 22 | 2.5 | 14.5 | 0 | 55.1169 | 0 | 0 | 110.2512 | 44.5287 | 0 | 113.347 | 26% | 0 | 0 | 10% | 0 | 41.977
3511 | 706 | 258 | 43 | 1.6 | 17.3 | 103.0885 | 25.6082 | 2.0089 | 0 | 105.9833 | 42.541 | 12.2794 | 20.2127 | 25% | 0 | 0 | 10% | 0 | 42.7561
3512 | 850 | 467 | 52 | 1.6 | 20.3 | 193.1897 | -2.98e-14 | 19.1869 | 0 | 68.4998 | 26.2166 | 125.5187 | 0 | 34% | 0 | 0 | 10% | 0 | 43.1917
3513 | 911 | 660 | 61 | 1.3 | 22.9 | 231.2718 | 0 | 38.658 | 0 | 45.5089 | 16.1219 | 186.6287 | 0 | 48% | 8.3846 | 0 | 21.4% | 0 | 43.8557
3514 | 937 | 821 | 72 | 1.9 | 24.4 | 251.4501 | 0 | 55.5191 | 0 | 46.3281 | 16.3399 | 206.0783 | 0 | 64% | 24.9444 | 0 | 55.33% | 0 | 44.1682
3515 | 829 | 907 | 155 | 2.1 | 26.6 | 228.3646 | 0 | 56.1043 | 8.2894 | 42.583 | 14.6238 | 186.7411 | 0 | 78% | 25 | 0 | 89.33% | 0 | 43.1783
3516 | 932 | 999 | 104 | 3.6 | 27.8 | 263.7672 | 0 | 30.2735 | 43.0821 | 42.5885 | 14.5225 | 221.8281 | 0 | 94% | 0.49455 | 0 | 90% | 0 | 42.2794
3517 | 911 | 993 | 113 | 5.7 | 28.3 | 124.4695 | 151.9211 | 27.2006 | 45.6268 | 42.5935 | 14.4801 | 82.7549 | 0 | 100% | 0 | 0 | 90% | 0 | 42.3195
3518 | 729 | 843 | 169 | 5.9 | 28 | 42.1518 | 182.6502 | 26.9606 | 32.0071 | 42.5925 | 14.5065 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.1768
3519 | 927 | 847 | 78 | 6.2 | 28.9 | 42.1572 | 237.8569 | 26.5949 | 30.6529 | 42.5902 | 14.4257 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.73
3520 | 895 | 712 | 87 | 5.8 | 28.5 | 42.1573 | 215.868 | 26.4728 | 16.2748 | 42.588 | 14.4605 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.6429
3521 | 784 | 504 | 85 | 4.7 | 28.1 | 42.1573 | 163.5089 | 22.666 | 0 | 42.5859 | 14.4953 | 0 | 0 | 100% | 0 | 4.0942 | 83.45% | 0 | 41.9652
3522 | 543 | 315 | 119 | 4.6 | 26.5 | 42.1574 | 70.8125 | 6.8141 | 0 | 42.5839 | 14.6325 | 0 | 0 | 100% | 0 | 20.4924 | 50.66% | 0 | 42.6491
3523 | 247 | 100 | 60 | 3.8 | 24.4 | 0 | 41.5577 | 0 | 0 | 49.6148 | 17.7278 | 0 | 48.0816 | 96% | 0 | 25 | 10.66% | 0 | 40.6581
3524 | 2 | 6 | 6 | 2.8 | 20.7 | 0 | 0 | 0 | 0 | 100.8581 | 40.1216 | 0 | 103.8443 | 89% | 0 | 0 | 10.66% | 0 | 37.1556
3525 | 0 | 0 | 0 | 1.6 | 18.8 | 0 | 0 | 0 | 0 | 94.8128 | 37.7536 | 0 | 94.4132 | 82% | 0 | 0 | 10.66% | 0 | 35.3784
3526 | 0 | 0 | 0 | 0.6 | 18.2 | 0 | 0 | 0 | 0 | 89.9445 | 35.7442 | 0 | 88.2206 | 75% | 0 | 0 | 10.66% | 0 | 33.4379
3527 | 0 | 0 | 0 | 0.5 | 18 | 0 | 0 | 0 | 0 | 87.3672 | 34.6743 | 0 | 85.2447 | 69% | 0 | 0 | 10.66% | 0 | 32.327
3528 | 0 | 0 | 0 | 0.5 | 17.1 | 0 | 0 | 0 | 0 | 86.2485 | 34.2657 | 0 | 84.0772 | 63% | 0 | 0 | 10.66% | 0 | 31.8634
3529 | 0 | 0 | 0 | 0.7 | 17.2 | 0 | 0 | 0 | 0 | 86.2882 | 34.2758 | 0 | 84.2658 | 56% | 0 | 0 | 10.66% | 0 | 31.8256
3530 | 0 | 0 | 0 | 1 | 16.3 | 0 | 0 | 0 | 0 | 87.551 | 34.8668 | 0 | 85.8778 | 50% | 0 | 0 | 10.66% | 0 | 32.3804
3531 | 0 | 0 | 0 | 0.9 | 16.9 | 0 | 0 | 0 | 0 | 93.119 | 37.181 | 0 | 92.7513 | 43% | 0 | 0 | 10.66% | 0 | 34.6698
3532 | 0 | 0 | 0 | 1.1 | 16.5 | 0 | 0 | 0 | 0 | 101.288 | 40.6314 | 0 | 102.4269 | 35% | 0 | 0 | 10.66% | 0 | 38.1343
3533 | 0 | 1 | 1 | 4.8 | 16.5 | 0 | 0 | 0 | 0 | 108.369 | 43.5916 | 0 | 110.6602 | 27% | 0 | 0 | 10.66% | 0 | 41.147
3534 | 243 | 59 | 28 | 5.3 | 16.8 | 0 | 37.3934 | 0 | 0 | 111.9665 | 45.0631 | 0 | 114.565 | 18% | 0 | 0 | 10.66% | 0 | 42.6953
3535 | 598 | 243 | 59 | 5.2 | 18.2 | 83.1466 | 21.1979 | 1.9784 | 0 | 107.7162 | 43.1863 | 0 | 28.6035 | 16% | 0 | 0 | 10.66% | 0 | 43.5678
3536 | 767 | 450 | 73 | 4.6 | 20.4 | 170.6187 | 0 | 18.4147 | 0 | 72.0951 | 27.7905 | 99.713 | 0 | 24% | 0 | 0 | 10.66% | 0 | 44.193
3537 | 856 | 645 | 78 | 4.1 | 23.5 | 214.5016 | 0 | 37.2844 | 0 | 45.1926 | 15.9434 | 170.4295 | 0 | 37% | 5.9796 | 0 | 18.79% | 0 | 44.8688
3538 | 907 | 812 | 83 | 3.9 | 25.7 | 241.4681 | 0 | 54.2157 | 0 | 46.2819 | 16.2101 | 196.4352 | 0 | 51% | 22.8219 | 0 | 49.83% | 0 | 44.959
3539 | 882 | 932 | 130 | 3.6 | 27.4 | 243.2731 | 0 | 57.0964 | 9.0362 | 42.5923 | 14.5584 | 201.8463 | 0 | 66% | 25 | 0 | 83.83% | 0 | 43.9756
3540 | 763 | 962 | 225 | 4 | 28.6 | 212.1659 | 0 | 35.3972 | 34.7445 | 42.5978 | 14.4549 | 170.6118 | 0 | 79% | 4.5357 | 0 | 90% | 0 | 42.9078
3541 | 767 | 924 | 179 | 5.6 | 28.4 | 212.5754 | -2.98e-14 | 30.5504 | 35.6314 | 42.5994 | 14.4733 | 170.7832 | 0 | 92% | 0 | 0 | 90% | 0 | 42.6045
3542 | 806 | 904 | 158 | 5.8 | 28.4 | 157.0595 | 73.6394 | 27.0135 | 36.8795 | 42.6008 | 14.4737 | 115.1035 | 0 | 100% | 0 | 0 | 90% | 0 | 42.6264
3543 | 492 | 671 | 250 | 5.9 | 28 | 42.152 | 99.6716 | 26.9845 | 16.1347 | 42.6003 | 14.5091 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.2033
3544 | 327 | 439 | 205 | 5.3 | 26.9 | 42.1574 | 39.2406 | 23.2897 | 0 | 42.5978 | 14.6035 | 0 | 0 | 100% | 0 | 3.2078 | 84.87% | 0 | 41.8109
3545 | 225 | 279 | 162 | 5.1 | 26.1 | 0 | 48.2552 | 10.4283 | 0 | 42.5946 | 14.6701 | 0 | 41.1034 | 97% | 0 | 19.1355 | 54.25% | 0 | 42.1559
3546 | 382 | 247 | 107 | 4.3 | 26.1 | 63.4916 | 0 | 4.3947 | 0 | 42.5921 | 14.6692 | 20.2699 | 0 | 98% | 0 | 22.8742 | 17.65% | 0 | 42.581
3547 | 308 | 111 | 59 | 4 | 24.9 | 0 | 52.0062 | 0 | 0 | 97.0997 | 38.0022 | 0 | 100.2885 | 91% | 0 | 4.7825 | 10% | 0 | 40.8251
3548 | 2 | 6 | 5 | 3.9 | 22.5 | 0 | 0 | 0 | 0 | 100.2612 | 39.7138 | 0 | 100.3733 | 84% | 0 | 0 | 10% | 0 | 37.4658
3549 | 0 | 0 | 0 | 4.7 | 19.9 | 0 | 0 | 0 | 0 | 94.4343 | 37.5138 | 0 | 93.1189 | 77% | 0 | 0 | 10% | 0 | 35.3757
3550 | 0 | 0 | 0 | 5.6 | 18.1 | 0 | 0 | 0 | 0 | 90.2449 | 35.8777 | 0 | 88.0929 | 70% | 0 | 0 | 10% | 0 | 33.7143
3551 | 0 | 0 | 0 | 4.8 | 17 | 0 | 0 | 0 | 0 | 87.4068 | 34.7586 | 0 | 84.904 | 63% | 0 | 0 | 10% | 0 | 32.5279
3552 | 0 | 0 | 0 | 4.1 | 17.1 | 0 | 0 | 0 | 0 | 86.4136 | 34.3346 | 0 | 83.9462 | 57% | 0 | 0 | 10% | 0 | 32.0317
3553 | 0 | 0 | 0 | 3.6 | 17.2 | 0 | 0 | 0 | 0 | 86.1702 | 34.226 | 0 | 83.8356 | 51% | 0 | 0 | 10% | 0 | 31.8636
3554 | 0 | 0 | 0 | 4.7 | 17.3 | 0 | 0 | 0 | 0 | 87.4776 | 34.7687 | 0 | 85.5327 | 45% | 0 | 0 | 10% | 0 | 32.3585
3555 | 0 | 0 | 0 | 4.6 | 16.8 | 0 | 0 | 0 | 0 | 93.1791 | 37.2131 | 0 | 92.5843 | 38% | 0 | 0 | 10% | 0 | 34.767
3556 | 0 | 0 | 0 | 5.2 | 16.2 | 0 | 0 | 0 | 0 | 101.6708 | 40.8142 | 0 | 102.6657 | 30% | 0 | 0 | 10% | 0 | 38.37
3557 | 0 | 1 | 1 | 4 | 15.6 | 0 | 0 | 0 | 0 | 108.6149 | 43.7639 | 0 | 110.7524 | 22% | 0 | 0 | 10% | 0 | 41.3617
3558 | 292 | 66 | 29 | 3 | 16.1 | 0 | 45.029 | 0 | 0 | 111.7979 | 45.0498 | 0 | 114.2041 | 13% | 0 | 0 | 10% | 0 | 42.7142
3559 | 650 | 254 | 55 | 4.8 | 18.8 | 92.3165 | 23.3034 | 2.2018 | 0 | 107.0142 | 42.8477 | 1.3614 | 20.1726 | 12% | 0 | 0 | 10% | 0 | 43.3774
3560 | 767 | 458 | 82 | 6.3 | 19.8 | 169.128 | 0 | 19.0658 | 0 | 69.9564 | 26.8947 | 100.6046 | 0 | 19% | 0 | 0 | 10% | 0 | 43.9669
3561 | 859 | 649 | 81 | 6 | 20.8 | 213.5506 | 0 | 37.9352 | 0 | 44.6721 | 15.9267 | 170.0752 | 0 | 32% | 6.9804 | 0 | 19.49% | 0 | 44.5177
3562 | 899 | 810 | 88 | 6.2 | 21.5 | 236.9827 | 0 | 54.7784 | 0 | 45.347 | 16.1561 | 192.9717 | 0 | 46% | 23.5453 | 0 | 51.52% | 0 | 44.7931
3563 | 924 | 930 | 92 | 5.5 | 21.9 | 253.9184 | 0 | 56.3487 | 10.8819 | 42.599 | 15.0002 | 212.5055 | 0 | 62% | 25 | 0 | 85.52% | 0 | 43.5785
3564 | 931 | 992 | 96 | 6 | 22.8 | 261.1517 | 0 | 33.9536 | 39.6526 | 42.6034 | 14.9356 | 219.6562 | 0 | 79% | 3.2978 | 0 | 90% | 0 | 42.7266
3565 | 926 | 997 | 99 | 6.4 | 23.2 | 260.0268 | 0 | 30.0927 | 43.8472 | 42.6052 | 14.9059 | 218.315 | 0 | 95% | 0 | 0 | 90% | 0 | 42.5437
3566 | 916 | 946 | 99 | 6.3 | 23.8 | 112.9349 | 161.3871 | 27.1708 | 41.3537 | 42.6063 | 14.86 | 71.2853 | 0 | 100% | 0 | 0 | 90% | 0 | 42.605
3567 | 884 | 838 | 101 | 6.5 | 23.6 | 42.1522 | 224.2709 | 26.3624 | 30.865 | 42.6046 | 14.8748 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.948
3568 | 837 | 683 | 96 | 6.7 | 22.9 | 42.1577 | 198.3019 | 26.1153 | 15.0721 | 42.6019 | 14.9276 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.7538
3569 | 768 | 498 | 85 | 6.7 | 22 | 42.1578 | 158.7909 | 22.6197 | 0 | 42.5994 | 14.9935 | 0 | 0 | 100% | 0 | 3.6201 | 84.21% | 0 | 41.9444
3570 | 629 | 293 | 70 | 6.4 | 20.5 | 42.1579 | 91.7606 | 5.1443 | 0 | 42.5969 | 15.0941 | 0 | 0 | 100% | 0 | 21.3115 | 50.11% | 0 | 42.2615
3571 | 348 | 100 | 40 | 6.4 | 18.5 | 0 | 45.8277 | 0 | 0 | 48.1566 | 17.537 | 0 | 46.6271 | 97% | 0 | 25 | 10.11% | 0 | 40.4638
3572 | 3 | 4 | 4 | 5.5 | 17 | 0 | 0 | 0 | 0 | 100.0421 | 40.0696 | 0 | 102.83 | 89% | 0 | 0 | 10.11% | 0 | 37.1053
3573 | 0 | 0 | 0 | 4.3 | 16.2 | 0 | 0 | 0 | 0 | 93.8253 | 37.5273 | 0 | 93.2871 | 82% | 0 | 0 | 10.11% | 0 | 35.1361
3574 | 0 | 0 | 0 | 2.6 | 15.4 | 0 | 0 | 0 | 0 | 89.5791 | 35.7805 | 0 | 87.8601 | 76% | 0 | 0 | 10.11% | 0 | 33.448
3575 | 0 | 0 | 0 | 2.7 | 14.5 | 0 | 0 | 0 | 0 | 86.2862 | 34.4486 | 0 | 84.0304 | 69% | 0 | 0 | 10.11% | 0 | 32.0775
3576 | 0 | 0 | 0 | 2.2 | 13.9 | 0 | 0 | 0 | 0 | 84.876 | 33.8923 | 0 | 82.5444 | 63% | 0 | 0 | 10.11% | 0 | 31.4599
3577 | 0 | 0 | 0 | 2.7 | 13.8 | 0 | 0 | 0 | 0 | 84.8619 | 33.8925 | 0 | 82.6868 | 57% | 0 | 0 | 10.11% | 0 | 31.4055
3578 | 0 | 0 | 0 | 2.9 | 13.2 | 0 | 0 | 0 | 0 | 86.1694 | 34.4787 | 0 | 84.3547 | 51% | 0 | 0 | 10.11% | 0 | 31.9507
3579 | 0 | 0 | 0 | 1.2 | 13 | 0 | 0 | 0 | 0 | 91.8909 | 36.914 | 0 | 91.3785 | 44% | 0 | 0 | 10.11% | 0 | 34.3574
3580 | 0 | 0 | 0 | 0.8 | 12.9 | 0 | 0 | 0 | 0 | 99.7063 | 40.2143 | 0 | 100.7031 | 36% | 0 | 0 | 10.11% | 0 | 37.6698
3581 | 0 | 1 | 1 | 0.9 | 12.4 | 0 | 0 | 0 | 0 | 106.579 | 43.1378 | 0 | 108.7519 | 28% | 0 | 0 | 10.11% | 0 | 40.6449
3582 | 356 | 69 | 24 | 0.6 | 13.2 | 0 | 55.0051 | 0 | 0 | 110.0512 | 44.5348 | 0 | 112.497 | 20% | 0 | 0 | 10.11% | 0 | 42.119
3583 | 705 | 262 | 46 | 2.3 | 16.6 | 102.7864 | 25.7069 | 2.0793 | 0 | 105.7737 | 42.5078 | 12.6191 | 20.0951 | 19% | 0 | 0 | 10.11% | 0 | 42.8127
3584 | 846 | 472 | 57 | 3.9 | 19.3 | 190.8193 | 0 | 19.3468 | 0 | 68.799 | 26.4159 | 123.2149 | 0 | 28% | 0 | 0 | 10.11% | 0 | 43.5726
3585 | 922 | 671 | 62 | 6.2 | 21 | 230.5913 | 0 | 39.2709 | 0 | 45.1516 | 16.1117 | 186.545 | 0 | 42% | 8.3878 | 0 | 21.52% | 0 | 44.4653
3586 | 959 | 835 | 67 | 6.6 | 21.6 | 253.8797 | 0 | 56.7191 | 0 | 43.832 | 15.5251 | 211.1668 | 0 | 58% | 24.6025 | 0 | 54.98% | 0 | 44.8791
3587 | 962 | 948 | 78 | 6 | 22 | 264.6558 | 0 | 56.3976 | 12.3781 | 42.5946 | 14.9918 | 223.0939 | 0 | 75% | 25 | 0 | 88.98% | 0 | 43.5033
3588 | 980 | 1016 | 74 | 7.3 | 22.5 | 274.124 | 0 | 31.4998 | 43.6002 | 42.5992 | 14.9563 | 232.415 | 0 | 92% | 0.75277 | 0 | 90% | 0 | 42.7046
3589 | 986 | 1023 | 70 | 7.7 | 23.4 | 150.5375 | 145.4449 | 27.3586 | 47.7414 | 42.6021 | 14.8894 | 108.8064 | 0 | 100% | 0 | 0 | 90% | 0 | 42.6819
3590 | 978 | 970 | 69 | 8 | 23.9 | 42.1521 | 262.7914 | 27.0858 | 43.5492 | 42.6011 | 14.8505 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.647
3591 | 961 | 865 | 66 | 7.7 | 23.9 | 42.1576 | 248.2381 | 26.5167 | 32.7812 | 42.5986 | 14.8496 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.077
3592 | 916 | 707 | 66 | 7.7 | 23.5 | 42.1577 | 222.0066 | 26.2774 | 16.4213 | 42.5961 | 14.8796 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8678
3593 | 850 | 516 | 61 | 7.7 | 22.7 | 42.1577 | 181.6391 | 23.3857 | 0 | 42.5937 | 14.9396 | 0 | 0 | 100% | 0 | 2.7861 | 85.54% | 0 | 41.8224
3594 | 736 | 310 | 50 | 6.9 | 21.5 | 42.1578 | 117.87 | 5.2579 | 0 | 42.5914 | 15.0251 | 0 | 0 | 100% | 0 | 21.1861 | 51.64% | 0 | 42.1803
3595 | 474 | 111 | 30 | 6.3 | 19.7 | 0 | 67.4729 | 0 | 0 | 48.5524 | 17.6296 | 0 | 47.0217 | 97% | 0 | 25 | 11.64% | 0 | 40.5543
3596 | 6 | 3 | 3 | 5.6 | 17.6 | 0 | 0 | 0 | 0 | 100.9617 | 40.4097 | 0 | 103.9638 | 89% | 0 | 0 | 11.64% | 0 | 37.4443
3597 | 0 | 0 | 0 | 4.6 | 15.9 | 0 | 0 | 0 | 0 | 94.8821 | 37.9918 | 0 | 94.4726 | 82% | 0 | 0 | 11.64% | 0 | 35.6218
3598 | 0 | 0 | 0 | 3.9 | 15.1 | 0 | 0 | 0 | 0 | 90.418 | 36.1558 | 0 | 88.7794 | 75% | 0 | 0 | 11.64% | 0 | 33.8532
3599 | 0 | 0 | 0 | 1.6 | 14.2 | 0 | 0 | 0 | 0 | 87.1373 | 34.8264 | 0 | 84.9366 | 69% | 0 | 0 | 11.64% | 0 | 32.4887
3600 | 0 | 0 | 0 | 1.3 | 13.8 | 0 | 0 | 0 | 0 | 85.8155 | 34.2938 | 0 | 83.5457 | 63% | 0 | 0 | 11.64% | 0 | 31.8965
3601 | 0 | 0 | 0 | 1.6 | 13.8 | 0 | 0 | 0 | 0 | 85.3531 | 34.0994 | 0 | 83.1526 | 56% | 0 | 0 | 11.64% | 0 | 31.6496
3602 | 0 | 0 | 0 | 1.4 | 13.2 | 0 | 0 | 0 | 0 | 86.7052 | 34.705 | 0 | 84.8846 | 50% | 0 | 0 | 11.64% | 0 | 32.2118
3603 | 0 | 0 | 0 | 2 | 13.1 | 0 | 0 | 0 | 0 | 91.8341 | 36.884 | 0 | 91.1937 | 43% | 0 | 0 | 11.64% | 0 | 34.3616
3604 | 0 | 0 | 0 | 1.8 | 12.9 | 0 | 0 | 0 | 0 | 99.7607 | 40.2374 | 0 | 100.6624 | 36% | 0 | 0 | 11.64% | 0 | 37.7214
3605 | 0 | 1 | 1 | 2.2 | 12.3 | 0 | 0 | 0 | 0 | 105.8651 | 42.8469 | 0 | 107.8132 | 28% | 0 | 0 | 11.64% | 0 | 40.3794
3606 | 389 | 72 | 22 | 1.4 | 13.6 | 0 | 49.2192 | 0 | 0 | 109.8258 | 44.4141 | 0 | 112.101 | 19% | 0 | 0 | 11.64% | 0 | 42.0284
3607 | 732 | 266 | 41 | 1.9 | 17.5 | 131.8598 | 0 | 1.9422 | 0 | 107.5343 | 43.1667 | 18.6416 | 0 | 21% | 0 | 0 | 11.64% | 0 | 43.4064
3608 | 854 | 474 | 52 | 4.5 | 20.7 | 192.317 | 0 | 19.0208 | 0 | 71.9465 | 27.7015 | 121.7028 | 0 | 30% | 0 | 0 | 11.64% | 0 | 44.5108
3609 | 919 | 669 | 59 | 5.4 | 22.2 | 230.4803 | 0 | 38.6243 | 0 | 45.2948 | 16.0852 | 186.3374 | 0 | 44% | 7.1387 | 0 | 21.35% | 0 | 45.0382
3610 | 960 | 836 | 62 | 6.6 | 23.6 | 254.1637 | 0 | 55.8828 | 0 | 46.1537 | 16.3315 | 209.2197 | 0 | 59% | 24.1964 | 0 | 54.26% | 0 | 45.2461
3611 | 975 | 952 | 66 | 6.5 | 24.2 | 267.9314 | 0 | 57.2237 | 10.9021 | 42.5949 | 14.8246 | 226.3622 | 0 | 76% | 25 | 0 | 88.26% | 0 | 44.1285
3612 | 980 | 1014 | 70 | 7 | 24.7 | 274.4401 | 0 | 32.5391 | 42.1785 | 42.5995 | 14.7864 | 232.7208 | 0 | 94% | 1.2792 | 0 | 90% | 0 | 43.041
3613 | 984 | 1022 | 69 | 7.6 | 25.3 | 129.9863 | 168.6603 | 27.4952 | 47.6048 | 42.6022 | 14.7387 | 88.3091 | 0 | 100% | 0 | 0 | 90% | 0 | 42.674
3614 | 977 | 971 | 67 | 7.5 | 25.4 | 42.1519 | 262.5576 | 27.001 | 42.9847 | 42.6009 | 14.73 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4414
3615 | 952 | 863 | 68 | 6.8 | 25.7 | 42.1575 | 245.5916 | 26.6036 | 31.8853 | 42.5984 | 14.7045 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.0184
3616 | 914 | 708 | 65 | 7.2 | 25.6 | 42.1575 | 221.5742 | 26.2345 | 15.9675 | 42.5959 | 14.7119 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.6567
3617 | 849 | 518 | 61 | 7.5 | 24.7 | 42.1576 | 181.5689 | 23.2049 | 0 | 42.5935 | 14.7843 | 0 | 0 | 100% | 0 | 2.6293 | 85.79% | 0 | 41.329
3618 | 734 | 312 | 50 | 6.7 | 23.6 | 42.1577 | 117.7544 | 5.2135 | 0 | 42.5912 | 14.8702 | 0 | 0 | 100% | 0 | 20.4061 | 53.14% | 0 | 41.2005
3619 | 474 | 113 | 31 | 6.1 | 21.5 | 0 | 67.7733 | 0 | 0 | 47.7387 | 17.1636 | 0 | 46.2106 | 97% | 0 | 25 | 13.14% | 0 | 40.0859
3620 | 9 | 4 | 3 | 5 | 18.6 | 0 | 0 | 0 | 0 | 101.1689 | 40.4195 | 0 | 104.2145 | 89% | 0 | 0 | 13.14% | 0 | 37.4554
3621 | 0 | 0 | 0 | 4.6 | 16.9 | 0 | 0 | 0 | 0 | 96.2881 | 38.5079 | 0 | 96.0951 | 82% | 0 | 0 | 13.14% | 0 | 36.1448
3622 | 0 | 0 | 0 | 5.3 | 15.8 | 0 | 0 | 0 | 0 | 91.2042 | 36.4422 | 0 | 89.6523 | 75% | 0 | 0 | 13.14% | 0 | 34.1645
3623 | 0 | 0 | 0 | 3.4 | 15.7 | 0 | 0 | 0 | 0 | 87.4689 | 34.8706 | 0 | 85.2369 | 69% | 0 | 0 | 13.14% | 0 | 32.5625
3624 | 0 | 0 | 0 | 2.6 | 16 | 0 | 0 | 0 | 0 | 85.3672 | 33.9675 | 0 | 82.9308 | 62% | 0 | 0 | 13.14% | 0 | 31.5977
3625 | 0 | 0 | 0 | 2.2 | 15.6 | 0 | 0 | 0 | 0 | 84.2119 | 33.5084 | 0 | 81.7497 | 56% | 0 | 0 | 13.14% | 0 | 31.0781
3626 | 0 | 0 | 0 | 3 | 15 | 0 | 0 | 0 | 0 | 83.2485 | 33.1425 | 0 | 80.771 | 50% | 0 | 0 | 13.14% | 0 | 30.6603
3627 | 0 | 0 | 0 | 2.2 | 14.7 | 0 | 0 | 0 | 0 | 82.8713 | 32.9983 | 0 | 80.4786 | 44% | 0 | 0 | 13.14% | 0 | 30.4703
3628 | 0 | 0 | 0 | 1 | 13.9 | 0 | 0 | 0 | 0 | 84.7498 | 33.8405 | 0 | 82.7797 | 38% | 0 | 0 | 13.14% | 0 | 31.2723
3629 | 0 | 1 | 1 | 1.2 | 13.2 | 0 | 0 | 0 | 0 | 91.0009 | 36.5246 | 0 | 90.4054 | 31% | 0 | 0 | 13.14% | 0 | 33.926
3630 | 373 | 73 | 23 | 1.2 | 14 | 0 | 57.8262 | 0 | 0 | 98.9718 | 39.8369 | 0 | 99.984 | 24% | 0 | 0 | 13.14% | 0 | 37.2432
3631 | 718 | 266 | 43 | 3.2 | 18.1 | 104.851 | 26.1824 | 1.9248 | 0 | 97.5848 | 38.9636 | 22.0049 | 18.4677 | 24% | 0 | 0 | 13.14% | 0 | 39.0778
3632 | 855 | 476 | 52 | 6.2 | 21.2 | 191.1849 | 0 | 18.9512 | 0 | 61.5476 | 23.1097 | 130.3032 | 0 | 34% | 0 | 0 | 13.14% | 0 | 39.8875
3633 | 930 | 676 | 55 | 6.4 | 22.8 | 232.7008 | 0 | 38.6495 | 0 | 45.8013 | 16.2499 | 187.5992 | 0 | 48% | 12.2348 | 0 | 29.78% | 0 | 40.1244
3634 | 968 | 841 | 59 | 6.7 | 24.1 | 256.4093 | 0 | 53.5584 | 2.3869 | 42.579 | 14.8271 | 214.5223 | 0 | 64% | 25 | 0 | 63.78% | 0 | 40.6105
3635 | 989 | 961 | 61 | 7.3 | 25.3 | 271.1495 | 0 | 47.1641 | 21.2328 | 42.5895 | 14.7343 | 229.1869 | 0 | 81% | 19.2775 | 0 | 90% | 0 | 39.6796
3636 | 997 | 1026 | 63 | 7.7 | 25.7 | 278.649 | 0 | 22.4885 | 52.6115 | 42.5941 | 14.703 | 236.5671 | 0 | 98% | 0 | 0 | 90% | 0 | 38.2826
3637 | 996 | 1030 | 63 | 8.3 | 25.9 | 67.0177 | 245.1783 | 22.0643 | 53.0357 | 42.5977 | 14.6878 | 25.5868 | 0 | 100% | 0 | 0 | 90% | 0 | 37.2813
3638 | 988 | 979 | 63 | 8.7 | 26.2 | 42.1519 | 265.8715 | 21.554 | 48.6868 | 42.5956 | 14.662 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.9261
3639 | 968 | 871 | 62 | 8.5 | 25.9 | 42.1575 | 250.3313 | 21.4372 | 37.5232 | 42.5932 | 14.6863 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.8337
3640 | 936 | 718 | 58 | 8.2 | 25.6 | 42.1575 | 228.1006 | 21.6337 | 21.1017 | 42.5909 | 14.7102 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.0542
3641 | 878 | 528 | 53 | 8.4 | 24.8 | 42.1576 | 189.5931 | 22.0175 | 1.5003 | 42.5887 | 14.7746 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.5026
3642 | 773 | 320 | 44 | 7.8 | 23.5 | 42.1577 | 127.0888 | 5.2958 | 0 | 42.5865 | 14.8762 | 0 | 0 | 100% | 0 | 17.0827 | 62.67% | 0 | 37.9655
3643 | 531 | 119 | 27 | 6.3 | 22.1 | 42.1578 | 31.5118 | 0 | 0 | 42.5844 | 14.9808 | 0 | 0 | 100% | 0 | 21.9703 | 27.52% | 0 | 37.6622
3644 | 14 | 4 | 3 | 4.9 | 19.6 | 0 | 0 | 0 | 0 | 69.2725 | 26.6524 | 0 | 69.6007 | 95% | 0 | 10.947 | 10% | 0 | 35.5321
3645 | 0 | 0 | 0 | 4.8 | 17.8 | 0 | 0 | 0 | 0 | 90.6703 | 36.0786 | 0 | 90.0878 | 88% | 0 | 0 | 10% | 0 | 33.4862
3646 | 0 | 0 | 0 | 2.3 | 16.8 | 0 | 0 | 0 | 0 | 85.4372 | 33.9444 | 0 | 83.4289 | 82% | 0 | 0 | 10% | 0 | 31.4527
3647 | 0 | 0 | 0 | 2.1 | 16.7 | 0 | 0 | 0 | 0 | 82.0766 | 32.5073 | 0 | 79.8022 | 76% | 0 | 0 | 10% | 0 | 29.9558
3648 | 0 | 0 | 0 | 1.2 | 15.5 | 0 | 0 | 0 | 0 | 80.2111 | 31.7331 | 0 | 78.0927 | 70% | 0 | 0 | 10% | 0 | 29.1185
3649 | 0 | 0 | 0 | 1.3 | 15 | 0 | 0 | 0 | 0 | 79.4155 | 31.403 | 0 | 77.3976 | 65% | 0 | 0 | 10% | 0 | 28.7475
3650 | 0 | 0 | 0 | 2.2 | 14.9 | 0 | 0 | 0 | 0 | 78.7617 | 31.1133 | 0 | 76.8094 | 59% | 0 | 0 | 10% | 0 | 28.4293
3651 | 0 | 0 | 0 | 1.9 | 14.4 | 0 | 0 | 0 | 0 | 77.6846 | 30.6566 | 0 | 75.7707 | 53% | 0 | 0 | 10% | 0 | 27.9518
3652 | 0 | 0 | 0 | 1.4 | 13.4 | 0 | 0 | 0 | 0 | 77.527 | 30.6432 | 0 | 75.6515 | 48% | 0 | 0 | 10% | 0 | 27.921
3653 | 0 | 1 | 1 | 2.4 | 13.6 | 0 | 0 | 0 | 0 | 81.4342 | 32.4072 | 0 | 79.654 | 42% | 0 | 0 | 10% | 0 | 29.6664
3654 | 420 | 77 | 21 | 2 | 15.4 | 0 | 54.2431 | 0 | 0 | 87.6981 | 34.9888 | 0 | 86.9011 | 35% | 0 | 0 | 10% | 0 | 32.2327
3655 | 760 | 275 | 39 | 1.1 | 19.1 | 138.3582 | 0 | 1.9204 | 0 | 86.1659 | 34.0951 | 49.1859 | 0 | 39% | 0 | 0 | 10% | 0 | 34.3075
3656 | 883 | 487 | 48 | 1.8 | 21.5 | 201.4709 | 0 | 19.3259 | 0 | 50.168 | 18.1865 | 151.3895 | 0 | 50% | 0 | 0 | 10% | 0 | 35.2595
3657 | 946 | 686 | 54 | 3.4 | 23.8 | 239.8482 | 0 | 39.1204 | 0 | 46.5184 | 16.4689 | 193.596 | 0 | 64% | 17.2114 | 0 | 33.41% | 0 | 35.7648
3658 | 978 | 850 | 58 | 5.4 | 25.2 | 260.4861 | 0 | 49.5291 | 6.6753 | 42.5726 | 14.7367 | 218.1499 | 0 | 80% | 25 | 0 | 67.41% | 0 | 36.5198
3659 | 993 | 967 | 61 | 5.2 | 26.4 | 274.2308 | 0 | 38.8504 | 29.51 | 42.5827 | 14.6406 | 231.8038 | 0 | 97% | 16.6121 | 0 | 90% | 0 | 36.6535
3660 | 1001 | 1031 | 63 | 4.4 | 27.1 | 77.8314 | 234.5437 | 20.3026 | 54.7425 | 42.5876 | 14.5829 | 36.349 | 0 | 100% | 0 | 0 | 90% | 0 | 35.3729
3661 | 1001 | 1037 | 63 | 4.5 | 27.9 | 42.1517 | 276.195 | 19.4435 | 55.6565 | 42.5859 | 14.5129 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.6662
3662 | 991 | 985 | 64 | 4.8 | 28.6 | 42.1572 | 267.4499 | 19.245 | 50.7108 | 42.5839 | 14.4502 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.4048
3663 | 967 | 874 | 63 | 5.3 | 28.7 | 42.1572 | 250.5684 | 19.3937 | 39.0207 | 42.5819 | 14.4406 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.5439
3664 | 931 | 718 | 60 | 5.1 | 27.9 | 42.1573 | 227.2256 | 19.8885 | 22.4297 | 42.5799 | 14.5108 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.1091
3665 | 871 | 528 | 55 | 4.8 | 27.8 | 42.1573 | 188.5796 | 20.8159 | 2.4095 | 42.578 | 14.5189 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.0445
3666 | 760 | 320 | 46 | 4.9 | 26.6 | 42.1574 | 125.1552 | 5.2352 | 0 | 42.5762 | 14.6214 | 0 | 0 | 100% | 0 | 17.178 | 62.52% | 0 | 37.7447
3667 | 485 | 115 | 30 | 4.9 | 24.6 | 42.1576 | 23.445 | 0 | 0 | 42.5744 | 14.7856 | 0 | 0 | 100% | 0 | 22.8841 | 25.9% | 0 | 38.3803
3668 | 15 | 5 | 4 | 3.6 | 22 | 0 | 0 | 0 | 0 | 73.0873 | 28.1045 | 0 | 73.8053 | 95% | 0 | 9.9379 | 10% | 0 | 35.9667
3669 | 0 | 0 | 0 | 2 | 20 | 0 | 0 | 0 | 0 | 91.3037 | 36.1857 | 0 | 90.6658 | 88% | 0 | 0 | 10% | 0 | 33.6549
3670 | 0 | 0 | 0 | 1.5 | 19.3 | 0 | 0 | 0 | 0 | 86.4708 | 34.2062 | 0 | 84.5186 | 82% | 0 | 0 | 10% | 0 | 31.7598
3671 | 0 | 0 | 0 | 1.3 | 18.2 | 0 | 0 | 0 | 0 | 83.5907 | 33.0796 | 0 | 81.284 | 75% | 0 | 0 | 10% | 0 | 30.575
3672 | 0 | 0 | 0 | 1 | 16.1 | 0 | 0 | 0 | 0 | 81.9891 | 32.5071 | 0 | 79.7642 | 70% | 0 | 0 | 10% | 0 | 29.9349
3673 | 0 | 0 | 0 | 0.6 | 15.7 | 0 | 0 | 0 | 0 | 81.9381 | 32.5093 | 0 | 79.8494 | 64% | 0 | 0 | 10% | 0 | 29.8876
3674 | 0 | 0 | 0 | 1 | 15.1 | 0 | 0 | 0 | 0 | 83.8664 | 33.3957 | 0 | 82.0462 | 58% | 0 | 0 | 10% | 0 | 30.738
3675 | 0 | 0 | 0 | 1.7 | 15.4 | 0 | 0 | 0 | 0 | 91.267 | 36.4976 | 0 | 91.0669 | 51% | 0 | 0 | 10% | 0 | 33.813
3676 | 0 | 0 | 0 | 0.6 | 15 | 0 | 0 | 0 | 0 | 100.4184 | 40.3761 | 0 | 102.0008 | 43% | 0 | 0 | 10% | 0 | 37.7226
3677 | 0 | 2 | 2 | 1.7 | 14.4 | 0 | 0 | 0 | 0 | 107.1436 | 43.2415 | 0 | 109.7677 | 35% | 0 | 0 | 10% | 0 | 40.6704
3678 | 347 | 76 | 28 | 1.3 | 17.2 | 0 | 53.9403 | 0 | 0 | 111.5268 | 44.8473 | 0 | 114.5193 | 26% | 0 | 0 | 10% | 0 | 42.3763
3679 | 694 | 267 | 51 | 0.6 | 21.8 | 102.2095 | 24.9996 | 2.0762 | 0 | 109.0158 | 43.4142 | 8.5766 | 20.5758 | 26% | 0 | 0 | 10% | 0 | 43.7144
3680 | 813 | 476 | 71 | 0.9 | 23.7 | 184.3992 | 0 | 18.9595 | 0 | 73.2311 | 28.0232 | 112.3628 | 0 | 34% | 0 | 0 | 10% | 0 | 44.8374
3681 | 811 | 652 | 114 | 1.5 | 25.4 | 203.8512 | 2.98e-14 | 37.3146 | 0 | 45.2811 | 15.8247 | 159.7231 | 0 | 46% | 5.2079 | 0 | 17.08% | 0 | 45.6362
3682 | 874 | 819 | 115 | 1.7 | 26.8 | 233.0071 | 0 | 54.0353 | 0 | 46.2403 | 16.0966 | 187.8191 | 0 | 60% | 21.3505 | 0 | 46.12% | 0 | 46.2041
3683 | 933 | 942 | 96 | 1.6 | 28.8 | 259.2308 | 0 | 58.7233 | 7.5526 | 42.5839 | 14.4324 | 217.4905 | 0 | 76% | 25 | 0 | 80.12% | 0 | 45.32
3684 | 948 | 1012 | 99 | 2.1 | 30.2 | 269.2854 | 0 | 40.8275 | 32.1873 | 42.5917 | 14.3103 | 227.4171 | 0 | 93% | 7.2651 | 0 | 90% | 0 | 44.9165
3685 | 914 | 1013 | 125 | 3.9 | 30.1 | 137.1031 | 139.3457 | 30.2286 | 42.8255 | 42.5955 | 14.3206 | 95.3985 | 0 | 100% | 0 | 0 | 90% | 0 | 44.9439
3686 | 577 | 844 | 300 | 3.7 | 30.2 | 42.1516 | 133.4635 | 30.1096 | 27.2165 | 42.5946 | 14.3113 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.1301
3687 | 162 | 585 | 441 | 5 | 29 | 0 | 50.1 | 31.9053 | 3.3017 | 42.5916 | 14.4173 | 0 | 41.1002 | 97% | 0 | 0 | 90% | 0 | 44.2532
3688 | 249 | 522 | 339 | 4.3 | 29.1 | 0 | 63.0928 | 28.3997 | 0 | 51.462 | 18.0624 | 0 | 49.7887 | 93% | 0 | 0 | 90% | 0 | 43.549
3689 | 644 | 499 | 152 | 4.1 | 29 | 135.4663 | 12.7674 | 22.998 | 0 | 42.5857 | 14.4153 | 90.7217 | 0 | 100% | 0 | 4.6916 | 82.49% | 0 | 43.4485
3690 | 499 | 266 | 92 | 4.2 | 28.2 | 42.1526 | 61.5296 | 4.9959 | 0 | 42.5862 | 14.4865 | 0 | 0 | 100% | 0 | 23.3459 | 45.14% | 0 | 43.538
3691 | 376 | 110 | 43 | 3.8 | 26.8 | 0 | 51.7604 | 0 | 0 | 59.8683 | 21.8809 | 0 | 59.2367 | 96% | 0 | 21.9625 | 10% | 0 | 41.7523
3692 | 11 | 5 | 5 | 1.8 | 24.1 | 0 | 0 | 0 | 0 | 104.3086 | 41.246 | 0 | 107.3598 | 88% | 0 | 0 | 10% | 0 | 38.4687
3693 | 0 | 0 | 0 | 1.4 | 21.2 | 0 | 0 | 0 | 0 | 98.3839 | 39.0486 | 0 | 98.1146 | 80% | 0 | 0 | 10% | 0 | 36.8081
3694 | 0 | 0 | 0 | 0.6 | 20.5 | 0 | 0 | 0 | 0 | 93.4013 | 37.0321 | 0 | 92.0002 | 73% | 0 | 0 | 10% | 0 | 34.8554
3695 | 0 | 0 | 0 | 1 | 19 | 0 | 0 | 0 | 0 | 90.1362 | 35.7674 | 0 | 88.0926 | 67% | 0 | 0 | 10% | 0 | 33.5641
3696 | 0 | 0 | 0 | 0.5 | 17.5 | 0 | 0 | 0 | 0 | 88.4628 | 35.1693 | 0 | 86.2512 | 60% | 0 | 0 | 10% | 0 | 32.9105
3697 | 0 | 0 | 0 | 0.6 | 16.8 | 0 | 0 | 0 | 0 | 88.3043 | 35.1505 | 0 | 86.2264 | 54% | 0 | 0 | 10% | 0 | 32.8373
3698 | 0 | 0 | 0 | 0.2 | 16.4 | 0 | 0 | 0 | 0 | 89.7954 | 35.8068 | 0 | 88.1507 | 47% | 0 | 0 | 10% | 0 | 33.4508
3699 | 0 | 0 | 0 | 0.4 | 16.4 | 0 | 0 | 0 | 0 | 95.1893 | 38.0863 | 0 | 94.7866 | 40% | 0 | 0 | 10% | 0 | 35.7021
3700 | 0 | 0 | 0 | 0.2 | 15.7 | 0 | 0 | 0 | 0 | 103.3348 | 41.5516 | 0 | 104.4222 | 32% | 0 | 0 | 10% | 0 | 39.1745
3701 | 0 | 1 | 1 | 1 | 15.5 | 0 | 0 | 0 | 0 | 109.5902 | 44.1775 | 0 | 111.6141 | 24% | 0 | 0 | 10% | 0 | 41.8459
3702 | 369 | 75 | 26 | 0.6 | 17 | 0 | 57.4229 | 0 | 0 | 113.4591 | 45.6679 | 0 | 115.895 | 15% | 0 | 0 | 10% | 0 | 43.3996
3703 | 711 | 271 | 50 | 0.9 | 20.8 | 104.8539 | 25.724 | 2.1027 | 0 | 110.6316 | 44.1713 | 10.0935 | 20.731 | 14% | 0 | 0 | 10% | 0 | 44.498
3704 | 831 | 478 | 68 | 1.2 | 21.8 | 188.6344 | 0 | 19.2821 | 0 | 73.5861 | 28.3404 | 116.7136 | 0 | 23% | 0 | 0 | 10% | 0 | 45.4399
3705 | 905 | 675 | 76 | 1.7 | 24.8 | 229.1665 | 0 | 38.7284 | 0 | 45.7199 | 16.0549 | 184.8228 | 0 | 37% | 5.9604 | 0 | 18.11% | 0 | 46.3029
3706 | 941 | 839 | 83 | 2.3 | 25.8 | 251.9543 | 0 | 55.7206 | 0 | 46.417 | 16.2568 | 207.004 | 0 | 53% | 22.792 | 0 | 49.1% | 0 | 46.4346
3707 | 958 | 955 | 87 | 2.3 | 27.7 | 266.1452 | 0 | 58.786 | 8.7382 | 42.5988 | 14.5346 | 224.806 | 0 | 70% | 25 | 0 | 83.1% | 0 | 45.4183
3708 | 962 | 1017 | 90 | 4 | 29.7 | 272.0138 | 0 | 38.5761 | 34.8501 | 42.6033 | 14.359 | 230.5228 | 0 | 87% | 5.0712 | 0 | 90% | 0 | 44.8776
3709 | 954 | 1019 | 94 | 4.9 | 30.1 | 222.6283 | 54.1076 | 29.8449 | 43.8407 | 42.6051 | 14.3239 | 180.9379 | 0 | 100% | 0 | 0 | 90% | 0 | 44.8011
3710 | 933 | 961 | 96 | 5.6 | 30.8 | 42.1515 | 248.7553 | 29.8403 | 37.8417 | 42.6053 | 14.2606 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.8099
3711 | 897 | 856 | 104 | 5.1 | 30.9 | 42.157 | 228.7108 | 29.0243 | 27.7541 | 42.6027 | 14.2507 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.984
3712 | 823 | 701 | 118 | 5.2 | 30.2 | 42.1571 | 194.7886 | 28.2931 | 12.8685 | 42.6001 | 14.3131 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.3154
3713 | 722 | 506 | 112 | 4.2 | 29.6 | 42.1572 | 147.3555 | 22.568 | 0 | 42.5976 | 14.3659 | 0 | 0 | 100% | 0 | 5.5243 | 81.16% | 0 | 43.1676
3714 | 571 | 301 | 93 | 4.3 | 26.6 | 42.1574 | 79.6653 | 5.9008 | 0 | 42.5953 | 14.628 | 0 | 0 | 100% | 0 | 22.0111 | 45.94% | 0 | 43.2499
3715 | 255 | 103 | 52 | 3.6 | 23.9 | 0 | 44.0497 | 0 | 0 | 57.6021 | 21.1816 | 0 | 56.7909 | 96% | 0 | 22.4645 | 10% | 0 | 41.5726
3716 | 3 | 4 | 4 | 2.7 | 21.4 | 0 | 0 | 0 | 0 | 103.3303 | 41.0935 | 0 | 106.2804 | 88% | 0 | 0 | 10% | 0 | 38.2817
3717 | 0 | 0 | 0 | 1.9 | 19.7 | 0 | 0 | 0 | 0 | 98.0283 | 39.0226 | 0 | 97.8163 | 81% | 0 | 0 | 10% | 0 | 36.7481
3718 | 0 | 0 | 0 | 1.2 | 18.8 | 0 | 0 | 0 | 0 | 93.1857 | 37.0694 | 0 | 91.819 | 74% | 0 | 0 | 10% | 0 | 34.8669
3719 | 0 | 0 | 0 | 1.1 | 18.5 | 0 | 0 | 0 | 0 | 90.3855 | 35.9081 | 0 | 88.4652 | 67% | 0 | 0 | 10% | 0 | 33.6823
3720 | 0 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 0 | 89.2862 | 35.3358 | 0 | 87.2881 | 61% | 0 | 0 | 10% | 0 | 33.0613
3721 | 0 | 0 | 0 | 0.9 | 20.5 | 0 | 0 | 0 | 0 | 89.0277 | 35.1883 | 0 | 87.1105 | 54% | 0 | 0 | 10% | 0 | 32.8696
3722 | 0 | 0 | 0 | 1.7 | 19.6 | 0 | 0 | 0 | 0 | 90.3886 | 35.8298 | 0 | 88.8644 | 47% | 0 | 0 | 10% | 0 | 33.4747
3723 | 0 | 0 | 0 | 3.9 | 21.5 | 0 | 0 | 0 | 0 | 96.1643 | 38.1019 | 0 | 95.909 | 40% | 0 | 0 | 10% | 0 | 35.7223
3724 | 0 | 0 | 0 | 4.6 | 20.7 | 0 | 0 | 0 | 0 | 104.1667 | 41.5067 | 0 | 105.3916 | 32% | 0 | 0 | 10% | 0 | 39.1386
3725 | 0 | 1 | 1 | 4.6 | 20.9 | 0 | 0 | 0 | 0 | 110.1188 | 43.9493 | 0 | 112.1796 | 24% | 0 | 0 | 10% | 0 | 41.6307
3726 | 119 | 54 | 38 | 7.8 | 21.4 | 0 | 18.5357 | 0 | 0 | 112.894 | 45.0501 | 0 | 115.1536 | 15% | 0 | 0 | 10% | 0 | 42.7968
3727 | 509 | 237 | 75 | 8.5 | 22 | 66.6225 | 17.51 | 2.0499 | 0 | 108.4307 | 43.1552 | 0 | 45.0136 | 12% | 0 | 0 | 10% | 0 | 43.7699
3728 | 685 | 453 | 115 | 9.1 | 22.8 | 146.3322 | 0 | 18.5243 | 0 | 72.2117 | 27.6538 | 75.517 | 0 | 17% | 0 | 0 | 10% | 0 | 44.3831
3729 | 882 | 678 | 91 | 10.1 | 24 | 216.0417 | 0 | 38.8962 | 0 | 45.2962 | 15.9465 | 171.806 | 0 | 30% | 7.6028 | 0 | 20.34% | 0 | 44.8516
3730 | 858 | 855 | 165 | 10.7 | 25.3 | 220.9937 | 0 | 57.0202 | 0 | 43.8331 | 15.2387 | 178.6321 | 0 | 44% | 24.3579 | 0 | 53.47% | 0 | 45.4486
3731 | 481 | 811 | 369 | 10.3 | 26.1 | 118.4342 | 0 | 55.7036 | 0 | 43.1985 | 14.9138 | 77.1669 | 0 | 50% | 24.9282 | 0 | 87.37% | 0 | 44.161
3732 | 778 | 1045 | 288 | 6.9 | 27.6 | 213.9456 | 0 | 32.6633 | 42.4367 | 42.596 | 14.5423 | 172.5113 | 0 | 62% | 1.9346 | 0 | 90% | 0 | 42.865
3733 | 947 | 1051 | 129 | 3.5 | 28 | 268.956 | 0 | 31.1215 | 43.9785 | 42.5991 | 14.5087 | 227.1498 | 0 | 79% | 0 | 0 | 90% | 0 | 42.6987
3734 | 935 | 980 | 109 | 2.4 | 28.5 | 261.2165 | 0 | 29.875 | 39.5103 | 42.6024 | 14.4654 | 219.4668 | 0 | 96% | 0 | 0 | 90% | 0 | 42.5593
3735 | 740 | 841 | 213 | 4.8 | 28.5 | 102.2232 | 109.0066 | 26.7251 | 29.2328 | 42.6039 | 14.4659 | 60.589 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8606
3736 | 376 | 586 | 309 | 5.8 | 27.5 | 42.1522 | 55.8669 | 26.1749 | 6.9605 | 42.6023 | 14.5532 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.4378
3737 | 296 | 409 | 244 | 4.4 | 26.6 | 42.1574 | 20.9233 | 18.0082 | 0 | 42.5998 | 14.6296 | 0 | 0 | 100% | 0 | 8.4922 | 76.41% | 0 | 41.8399
3738 | 27 | 154 | 142 | 3.4 | 25.4 | 0 | 6.2863 | 2.4793 | 0 | 47.2619 | 16.6522 | 0 | 45.7354 | 97% | 0 | 25 | 36.41% | 0 | 42.064
3739 | 37 | 67 | 59 | 2.1 | 24.4 | 0 | 6.4102 | 0 | 0 | 71.4302 | 27.0493 | 0 | 72.0343 | 91% | 0 | 16.5078 | 10% | 0 | 40.6198
3740 | 2 | 6 | 6 | 1.6 | 23.1 | 0 | 0 | 0 | 0 | 101.3478 | 40.1099 | 0 | 103.0724 | 84% | 0 | 0 | 10% | 0 | 37.4963
3741 | 0 | 0 | 0 | 1.9 | 21.3 | 0 | 0 | 0 | 0 | 96.1851 | 38.1263 | 0 | 95.7973 | 77% | 0 | 0 | 10% | 0 | 35.8081
3742 | 0 | 0 | 0 | 1 | 20.2 | 0 | 0 | 0 | 0 | 91.6929 | 36.3333 | 0 | 90.1951 | 70% | 0 | 0 | 10% | 0 | 34.0675
3743 | 0 | 0 | 0 | 1.8 | 20 | 0 | 0 | 0 | 0 | 88.884 | 35.1665 | 0 | 86.8598 | 63% | 0 | 0 | 10% | 0 | 32.8763
3744 | 0 | 0 | 0 | 1.7 | 18.6 | 0 | 0 | 0 | 0 | 87.3689 | 34.6322 | 0 | 85.1841 | 57% | 0 | 0 | 10% | 0 | 32.2962
3745 | 0 | 0 | 0 | 1.6 | 18.1 | 0 | 0 | 0 | 0 | 87.3084 | 34.6424 | 0 | 85.2496 | 50% | 0 | 0 | 10% | 0 | 32.26
3746 | 0 | 0 | 0 | 2.1 | 17.7 | 0 | 0 | 0 | 0 | 88.1376 | 35.0188 | 0 | 86.348 | 44% | 0 | 0 | 10% | 0 | 32.6
3747 | 0 | 0 | 0 | 1.5 | 15.9 | 0 | 0 | 0 | 0 | 93.1202 | 37.25 | 0 | 92.5153 | 37% | 0 | 0 | 10% | 0 | 34.8017
3748 | 0 | 0 | 0 | 0.8 | 14.5 | 0 | 0 | 0 | 0 | 100.7165 | 40.5354 | 0 | 101.5209 | 30% | 0 | 0 | 10% | 0 | 38.0898
3749 | 0 | 1 | 1 | 0.7 | 13.7 | 0 | 0 | 0 | 0 | 106.957 | 43.2123 | 0 | 108.8253 | 21% | 0 | 0 | 10% | 0 | 40.8046
3750 | 303 | 73 | 30 | 0.7 | 15.6 | 0 | 47.2323 | 0 | 0 | 110.1146 | 44.3882 | 0 | 112.2593 | 13% | 0 | 0 | 10% | 0 | 42.0411
3751 | 642 | 260 | 61 | 0.2 | 20.3 | 93.678 | 23.0429 | 2.0374 | 0 | 106.5451 | 42.5294 | 3.0522 | 20.0649 | 12% | 0 | 0 | 10% | 0 | 42.8811
3752 | 791 | 469 | 78 | 1.1 | 22.5 | 178.771 | 0 | 18.7526 | 0 | 70.4321 | 26.8985 | 109.6532 | 0 | 20% | 0 | 0 | 10% | 0 | 43.5721
3753 | 872 | 665 | 87 | 3.3 | 23.7 | 219.3234 | 0 | 38.0386 | 0 | 45.3727 | 16.001 | 175.1877 | 0 | 33% | 7.5657 | 0 | 20.29% | 0 | 44.0566
3754 | 926 | 833 | 88 | 3.7 | 24.5 | 246.7344 | 0 | 55.2524 | 0 | 46.2064 | 16.2798 | 201.8499 | 0 | 48% | 24.5515 | 0 | 53.68% | 0 | 44.2938
3755 | 951 | 951 | 88 | 3 | 25.6 | 263.6573 | 0 | 56.3202 | 11.0661 | 42.6006 | 14.7135 | 222.2193 | 0 | 65% | 25 | 0 | 87.68% | 0 | 43.1711
3756 | 944 | 1013 | 102 | 3.6 | 26.4 | 267.0764 | 0 | 32.4594 | 41.1737 | 42.6046 | 14.6481 | 225.5591 | 0 | 82% | 1.7064 | 0 | 90% | 0 | 42.4789
3757 | 946 | 1019 | 99 | 4.3 | 26.7 | 268.0234 | 0 | 27.7614 | 46.4044 | 42.6063 | 14.6233 | 226.2328 | 0 | 98% | 0 | 0 | 90% | 0 | 42.5814
3758 | 950 | 974 | 93 | 5.2 | 26.4 | 65.5584 | 227.4462 | 27.1959 | 42.4396 | 42.6071 | 14.649 | 24.1247 | 0 | 100% | 0 | 0 | 90% | 0 | 42.3846
3759 | 937 | 872 | 87 | 4.9 | 26.9 | 42.1519 | 241.3264 | 26.6548 | 32.0909 | 42.6047 | 14.6059 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.9706
3760 | 915 | 724 | 77 | 5.7 | 26.7 | 42.1574 | 222.565 | 26.466 | 16.6517 | 42.6021 | 14.6219 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.7979
3761 | 850 | 533 | 69 | 6.4 | 26.1 | 42.1575 | 182.9729 | 23.8757 | 0 | 42.5996 | 14.6718 | 0 | 0 | 100% | 0 | 2.6634 | 85.74% | 0 | 41.9211
3762 | 732 | 323 | 57 | 5.7 | 25.4 | 42.1575 | 119.2072 | 5.7291 | 0 | 42.5971 | 14.7287 | 0 | 0 | 100% | 0 | 21.1761 | 51.86% | 0 | 42.3442
3763 | 479 | 121 | 34 | 4.2 | 24.5 | 43.2904 | 22.3896 | 0 | 0 | 43.7107 | 15.2538 | 0 | 0 | 100% | 0 | 25 | 11.86% | 0 | 40.9636
3764 | 17 | 5 | 4 | 2.4 | 22.4 | 0 | 0 | 0 | 0 | 99.9065 | 39.5766 | 0 | 102.0222 | 92% | 0 | 0 | 11.86% | 0 | 37.7027
3765 | 0 | 0 | 0 | 1.1 | 20.7 | 0 | 0 | 0 | 0 | 96.8654 | 38.4587 | 0 | 96.5481 | 85% | 0 | 0 | 11.86% | 0 | 36.1598
3766 | 0 | 0 | 0 | 1.3 | 18.6 | 0 | 0 | 0 | 0 | 92.0008 | 36.5825 | 0 | 90.4272 | 78% | 0 | 0 | 11.86% | 0 | 34.3645
3767 | 0 | 0 | 0 | 0.5 | 16.6 | 0 | 0 | 0 | 0 | 88.867 | 35.3999 | 0 | 86.7536 | 72% | 0 | 0 | 11.86% | 0 | 33.1409
3768 | 0 | 0 | 0 | 0.8 | 15.8 | 0 | 0 | 0 | 0 | 87.4906 | 34.873 | 0 | 85.3046 | 66% | 0 | 0 | 11.86% | 0 | 32.5493
3769 | 0 | 0 | 0 | 1 | 14.2 | 0 | 0 | 0 | 0 | 87.2786 | 34.8861 | 0 | 85.2203 | 59% | 0 | 0 | 11.86% | 0 | 32.5062
3770 | 0 | 0 | 0 | 0.7 | 13.9 | 0 | 0 | 0 | 0 | 88.48 | 35.4124 | 0 | 86.786 | 53% | 0 | 0 | 11.86% | 0 | 32.9899
3771 | 0 | 0 | 0 | 1.5 | 13.6 | 0 | 0 | 0 | 0 | 93.8115 | 37.6953 | 0 | 93.4015 | 46% | 0 | 0 | 11.86% | 0 | 35.2442
3772 | 0 | 0 | 0 | 1.3 | 12.7 | 0 | 0 | 0 | 0 | 100.9781 | 40.7616 | 0 | 101.8248 | 38% | 0 | 0 | 11.86% | 0 | 38.3242
3773 | 0 | 1 | 1 | 1.9 | 13.4 | 0 | 0 | 0 | 0 | 107.214 | 43.339 | 0 | 109.0825 | 30% | 0 | 0 | 11.86% | 0 | 40.9482
3774 | 185 | 66 | 38 | 1.7 | 16.2 | 0 | 28.8557 | 0 | 0 | 111.0374 | 44.7245 | 0 | 113.2726 | 21% | 0 | 0 | 11.86% | 0 | 42.4017
3775 | 455 | 220 | 77 | 0.8 | 18.6 | 61.9746 | 15.5687 | 1.8345 | 0 | 106.6043 | 42.6937 | 0 | 47.6356 | 18% | 0 | 0 | 11.86% | 0 | 43.1243
3776 | 731 | 457 | 93 | 0.9 | 21.6 | 163.9497 | 0 | 18.1977 | 0 | 72.0398 | 27.6755 | 92.7328 | 0 | 25% | 0 | 0 | 11.86% | 0 | 43.9222
3777 | 829 | 654 | 103 | 1.5 | 23.2 | 208.5172 | 0 | 37.2661 | 0 | 45.0694 | 15.9163 | 164.5862 | 0 | 37% | 6.4432 | 0 | 20.62% | 0 | 44.4108
3778 | 877 | 817 | 110 | 1.9 | 25.1 | 233.5468 | 0 | 53.7815 | 0 | 46.0469 | 16.1646 | 188.7825 | 0 | 51% | 22.8769 | 0 | 51.73% | 0 | 44.4942
3779 | 908 | 936 | 112 | 2.4 | 26.5 | 251.2811 | 0 | 56.2833 | 9.6334 | 42.5908 | 14.6349 | 209.8006 | 0 | 67% | 25 | 0 | 85.73% | 0 | 43.1632
3780 | 908 | 997 | 120 | 4.7 | 27 | 255.2967 | 0 | 33.4723 | 38.5363 | 42.597 | 14.5948 | 213.7292 | 0 | 83% | 3.1382 | 0 | 90% | 0 | 42.1119
3781 | 899 | 1000 | 124 | 3.6 | 27.5 | 254.4906 | 0 | 26.9671 | 45.1948 | 42.5998 | 14.5523 | 212.667 | 0 | 99% | 0 | 0 | 90% | 0 | 42.009
3782 | 890 | 949 | 119 | 2.3 | 28.1 | 61.3997 | 213.3951 | 26.7885 | 40.0098 | 42.6017 | 14.5007 | 19.9659 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8526
3783 | 864 | 845 | 117 | 3.1 | 28.4 | 42.1518 | 218.7347 | 26.2121 | 29.8605 | 42.5994 | 14.4732 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.395
3784 | 813 | 690 | 111 | 2.5 | 29 | 42.1572 | 192.4255 | 25.8598 | 14.4159 | 42.5969 | 14.4191 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.9883
3785 | 733 | 502 | 100 | 3.9 | 28.7 | 42.1572 | 150.8978 | 22.1954 | 0 | 42.5945 | 14.4449 | 0 | 0 | 100% | 0 | 3.3872 | 84.58% | 0 | 40.737
3786 | 596 | 298 | 79 | 4.6 | 27.9 | 42.1573 | 86.4351 | 5.3497 | 0 | 42.5922 | 14.515 | 0 | 0 | 100% | 0 | 20.1578 | 52.33% | 0 | 40.7323
3787 | 358 | 112 | 46 | 4.1 | 26.6 | 0 | 49.3711 | 0 | 0 | 47.3888 | 16.5995 | 0 | 45.862 | 97% | 0 | 25 | 12.33% | 0 | 39.5161
3788 | 15 | 7 | 6 | 4.1 | 23.9 | 0 | 0 | 0 | 0 | 100.3549 | 39.6182 | 0 | 103.2105 | 89% | 0 | 0 | 12.33% | 0 | 36.6563
3789 | 0 | 0 | 0 | 3.4 | 21.1 | 0 | 0 | 0 | 0 | 95.3623 | 37.8023 | 0 | 95.0753 | 82% | 0 | 0 | 12.33% | 0 | 35.4212
3790 | 0 | 0 | 0 | 3.7 | 19.4 | 0 | 0 | 0 | 0 | 90.6461 | 35.9521 | 0 | 89.0543 | 75% | 0 | 0 | 12.33% | 0 | 33.6504
3791 | 0 | 0 | 0 | 3.4 | 19 | 0 | 0 | 0 | 0 | 86.9443 | 34.4259 | 0 | 84.694 | 69% | 0 | 0 | 12.33% | 0 | 32.0927
3792 | 0 | 0 | 0 | 4.4 | 18.6 | 0 | 0 | 0 | 0 | 84.7785 | 33.5477 | 0 | 82.3167 | 63% | 0 | 0 | 12.33% | 0 | 31.1528
3793 | 0 | 0 | 0 | 4.8 | 17 | 0 | 0 | 0 | 0 | 83.4144 | 33.085 | 0 | 80.8937 | 57% | 0 | 0 | 12.33% | 0 | 30.6293
3794 | 0 | 0 | 0 | 3.8 | 16.5 | 0 | 0 | 0 | 0 | 83.351 | 33.0907 | 0 | 80.9758 | 51% | 0 | 0 | 12.33% | 0 | 30.5805
3795 | 0 | 0 | 0 | 3.8 | 16.4 | 0 | 0 | 0 | 0 | 83.2884 | 33.0713 | 0 | 81.0198 | 45% | 0 | 0 | 12.33% | 0 | 30.5195
3796 | 0 | 0 | 0 | 1.4 | 15.9 | 0 | 0 | 0 | 0 | 85.2295 | 33.9171 | 0 | 83.4084 | 38% | 0 | 0 | 12.33% | 0 | 31.3296
3797 | 0 | 1 | 1 | 1.3 | 15.9 | 0 | 0 | 0 | 0 | 91.3692 | 36.5076 | 0 | 90.9082 | 32% | 0 | 0 | 12.33% | 0 | 33.8947
3798 | 264 | 70 | 32 | 1.4 | 17 | 0 | 41.1964 | 0 | 0 | 98.2941 | 39.3409 | 0 | 99.2072 | 24% | 0 | 0 | 12.33% | 0 | 36.7389
3799 | 589 | 252 | 67 | 2 | 20.2 | 84.1111 | 20.8757 | 1.9957 | 0 | 96.5312 | 38.3639 | 2.8563 | 18.2069 | 23% | 0 | 0 | 12.33% | 0 | 38.7314
3800 | 740 | 457 | 88 | 5.6 | 23.1 | 163.1367 | 0 | 17.931 | 0 | 62.829 | 23.5124 | 100.8974 | 0 | 31% | 0 | 0 | 12.33% | 0 | 39.5223
3801 | 815 | 647 | 103 | 7.1 | 24.2 | 200.6315 | 0 | 36.4031 | 0 | 45.432 | 15.9867 | 155.8772 | 0 | 42% | 10.5593 | 0 | 26.69% | 0 | 39.587
3802 | 850 | 807 | 118 | 6.9 | 24.9 | 222.0175 | -2.98e-14 | 52.5307 | 0.14752 | 42.5733 | 14.7613 | 180.1279 | 0 | 56% | 25 | 0 | 60.69% | 0 | 39.8432
3803 | 870 | 924 | 130 | 7.1 | 25.1 | 236.226 | 0 | 48.1769 | 16.6029 | 42.5844 | 14.749 | 194.2847 | 0 | 70% | 21.5524 | 0 | 90% | 0 | 38.774
3804 | 875 | 989 | 140 | 7.2 | 25.6 | 243.2354 | 0 | 25.2397 | 45.9812 | 42.59 | 14.7098 | 201.2147 | 0 | 85% | 0 | 0 | 90% | 0 | 37.2682
3805 | 851 | 990 | 158 | 7.7 | 25.8 | 236.3664 | 0 | 19.5707 | 51.715 | 42.594 | 14.6948 | 194.1459 | 0 | 99% | 0 | 0 | 90% | 0 | 36.5269
3806 | 846 | 947 | 157 | 7.9 | 25.9 | 54.8979 | 205.3175 | 20.9207 | 45.9619 | 42.5964 | 14.6874 | 13.4755 | 0 | 100% | 0 | 0 | 90% | 0 | 36.212
3807 | 817 | 837 | 147 | 8.4 | 25.6 | 42.1521 | 202.9527 | 20.3173 | 35.4979 | 42.5942 | 14.7113 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.7389
3808 | 769 | 686 | 136 | 8.3 | 25.3 | 42.1575 | 178.0166 | 20.4427 | 19.9874 | 42.5919 | 14.7351 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.8882
3809 | 681 | 500 | 124 | 8 | 24.4 | 42.1576 | 135.1339 | 20.6064 | 2.0087 | 42.5896 | 14.8069 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.1238
3810 | 519 | 295 | 101 | 7.3 | 22.7 | 42.1578 | 65.8319 | 6.0083 | 0 | 42.5874 | 14.9373 | 0 | 0 | 100% | 0 | 15.6436 | 64.97% | 0 | 37.3002
3811 | 211 | 100 | 56 | 6.6 | 20.8 | 0 | 36.8581 | 0 | 0 | 42.5845 | 15.0701 | 0 | 41.0931 | 97% | 0 | 24.109 | 26.4% | 0 | 37.1219
3812 | 2 | 5 | 4 | 5.6 | 19.1 | 0 | 0 | 0 | 0 | 71.472 | 27.6475 | 0 | 71.6768 | 92% | 0 | 10.2474 | 10% | 0 | 34.9716
3813 | 0 | 0 | 0 | 5 | 18.4 | 0 | 0 | 0 | 0 | 88.9783 | 35.3225 | 0 | 88.1804 | 85% | 0 | 0 | 10% | 0 | 32.6783
3814 | 0 | 0 | 0 | 4.4 | 18.1 | 0 | 0 | 0 | 0 | 84.7194 | 33.5573 | 0 | 82.8341 | 79% | 0 | 0 | 10% | 0 | 30.9816
3815 | 0 | 0 | 0 | 3.2 | 17.8 | 0 | 0 | 0 | 0 | 81.7021 | 32.2657 | 0 | 79.6017 | 73% | 0 | 0 | 10% | 0 | 29.6526
3816 | 0 | 0 | 0 | 1.9 | 17.2 | 0 | 0 | 0 | 0 | 79.9841 | 31.5244 | 0 | 77.9784 | 67% | 0 | 0 | 10% | 0 | 28.8686
3817 | 0 | 0 | 0 | 1.4 | 17 | 0 | 0 | 0 | 0 | 79.0335 | 31.1077 | 0 | 77.0929 | 62% | 0 | 0 | 10% | 0 | 28.4223
3818 | 0 | 0 | 0 | 1.1 | 16.9 | 0 | 0 | 0 | 0 | 78.425 | 30.8398 | 0 | 76.5308 | 56% | 0 | 0 | 10% | 0 | 28.1326
3819 | 0 | 0 | 0 | 1.1 | 16.7 | 0 | 0 | 0 | 0 | 78.4435 | 30.8611 | 0 | 76.5905 | 50% | 0 | 0 | 10% | 0 | 28.1365
3820 | 0 | 0 | 0 | 1 | 15.7 | 0 | 0 | 0 | 0 | 78.3853 | 30.8967 | 0 | 76.5622 | 45% | 0 | 0 | 10% | 0 | 28.1582
3821 | 0 | 1 | 1 | 0.6 | 15.7 | 0 | 0 | 0 | 0 | 81.8078 | 32.4516 | 0 | 80.0682 | 39% | 0 | 0 | 10% | 0 | 29.6976
3822 | 3 | 34 | 33 | 0.4 | 15.4 | 0 | 0.46828 | 0 | 0 | 86.8442 | 34.629 | 0 | 85.9072 | 32% | 0 | 0 | 10% | 0 | 31.8597
3823 | 169 | 198 | 141 | 2 | 18 | 0 | 36.9773 | 2.8699 | 0 | 85.2137 | 33.7736 | 0 | 83.891 | 26% | 0 | 0 | 10% | 0 | 33.8909
3824 | 72 | 342 | 303 | 2.1 | 19.7 | 0 | 19.0448 | 13.8894 | 0 | 62.9691 | 23.833 | 0 | 60.8943 | 22% | 0 | 0 | 10% | 0 | 35.0033
3825 | 28 | 342 | 319 | 1.9 | 20.7 | 0 | 8.1509 | 15.0746 | 0 | 61.5133 | 23.1349 | 0 | 59.4467 | 17% | 0 | 0 | 10% | 0 | 35.4784
3826 | 165 | 454 | 311 | 1.7 | 22 | 0 | 50.473 | 24.968 | 0 | 46.4025 | 16.5662 | 0 | 44.4191 | 14% | 2.7233 | 0 | 13.7% | 0 | 36.0884
3827 | 441 | 731 | 315 | 1.2 | 24.4 | 93.0231 | 22.5202 | 47.5982 | 1.2127 | 42.4576 | 14.761 | 56.8159 | 7.3139 | 18% | 25 | 0 | 47.7% | 0 | 35.7038
3828 | 516 | 855 | 344 | 2.2 | 26.6 | 138.63 | -2.98e-14 | 46.118 | 13.8687 | 42.497 | 14.5942 | 96.2708 | 0 | 25% | 25 | 0 | 81.7% | 0 | 34.0541
3829 | 750 | 978 | 242 | 4 | 27.4 | 208.8716 | 0 | 26.9625 | 43.4099 | 42.5392 | 14.5403 | 166.5194 | 0 | 37% | 6.1003 | 0 | 90% | 0 | 33.1149
3830 | 768 | 916 | 195 | 4.4 | 28.3 | 210.0871 | 0 | 20.6996 | 42.5189 | 42.5608 | 14.469 | 167.8822 | 0 | 49% | 0 | 0 | 90% | 0 | 32.8556
3831 | 763 | 838 | 188 | 5.1 | 28.3 | 201.4919 | -2.98e-14 | 20.5683 | 34.9873 | 42.5749 | 14.4738 | 159.3109 | 0 | 61% | 0 | 0 | 90% | 0 | 32.7908
3832 | 715 | 677 | 164 | 5.2 | 28.1 | 179.2611 | 0 | 19.3826 | 20.3334 | 42.5824 | 14.4941 | 137.0912 | 0 | 71% | 0 | 0 | 90% | 0 | 33.2576
3833 | 647 | 495 | 134 | 5.4 | 27.4 | 146.5293 | 2.98e-14 | 19.6189 | 2.4166 | 42.5861 | 14.5563 | 104.4399 | 0 | 79% | 0 | 0 | 90% | 0 | 34.3656
3834 | 468 | 284 | 108 | 5.5 | 25.7 | 82.8554 | 0 | 5.5214 | 0 | 42.5876 | 14.7008 | 41.0781 | 0 | 82% | 0 | 15.5626 | 65.1% | 0 | 36.3103
3835 | 169 | 90 | 53 | 4.9 | 23.3 | 0 | 29.5971 | 0 | 0 | 43.1334 | 15.1141 | 0 | 41.6729 | 79% | 0 | 24.2178 | 26.35% | 0 | 37.242
3836 | 6 | 5 | 5 | 3 | 21.1 | 0 | 0 | 0 | 0 | 71.4199 | 27.4818 | 0 | 71.8063 | 73% | 0 | 10.2195 | 10% | 0 | 34.6986
3837 | 0 | 0 | 0 | 1.8 | 19.6 | 0 | 0 | 0 | 0 | 90.1929 | 35.7465 | 0 | 90.4292 | 67% | 0 | 0 | 10% | 0 | 32.8615
3838 | 0 | 0 | 0 | 0.7 | 18.9 | 0 | 0 | 0 | 0 | 85.3395 | 33.7613 | 0 | 84.1781 | 61% | 0 | 0 | 10% | 0 | 30.979
3839 | 0 | 0 | 0 | 0.5 | 18.5 | 0 | 0 | 0 | 0 | 82.6108 | 32.6337 | 0 | 80.9377 | 55% | 0 | 0 | 10% | 0 | 29.871
3840 | 0 | 0 | 0 | 1 | 18.6 | 0 | 0 | 0 | 0 | 81.6328 | 32.1816 | 0 | 79.9495 | 49% | 0 | 0 | 10% | 0 | 29.4135
3841 | 0 | 0 | 0 | 0.8 | 18.1 | 0 | 0 | 0 | 0 | 81.4335 | 32.1255 | 0 | 79.7553 | 43% | 0 | 0 | 10% | 0 | 29.3512
3842 | 0 | 0 | 0 | 1.2 | 18 | 0 | 0 | 0 | 0 | 83.1702 | 32.9183 | 0 | 81.5654 | 37% | 0 | 0 | 10% | 0 | 30.136
3843 | 0 | 0 | 0 | 1.2 | 17.8 | 0 | 0 | 0 | 0 | 89.4089 | 35.5484 | 0 | 89.1017 | 30% | 0 | 0 | 10% | 0 | 32.7533
3844 | 0 | 0 | 0 | 0.6 | 16.9 | 0 | 0 | 0 | 0 | 97.0438 | 38.8256 | 0 | 98.354 | 23% | 0 | 0 | 10% | 0 | 36.0485
3845 | 0 | 1 | 1 | 1.4 | 17.1 | 0 | 0 | 0 | 0 | 103.6801 | 41.5923 | 0 | 106.1644 | 15% | 0 | 0 | 10% | 0 | 38.8687
3846 | 44 | 51 | 45 | 1.3 | 17.7 | 0 | 6.869 | 0 | 0 | 107.5907 | 43.1745 | 0 | 110.5278 | 7% | 0 | 0 | 10% | 0 | 40.526
3847 | 514 | 240 | 70 | 0.7 | 21.3 | 72.2361 | 17.8289 | 1.6788 | 0 | 104.3901 | 41.5503 | 0 | 36.3843 | 4% | 0 | 0 | 10% | 0 | 41.6874
3848 | 809 | 472 | 71 | 0.6 | 24.6 | 183.3906 | 2.98e-14 | 18.3259 | 0 | 69.513 | 26.3133 | 113.9631 | 0 | 13% | 0 | 0 | 10% | 0 | 42.551
3849 | 873 | 662 | 83 | 3 | 25.6 | 219.6947 | 0 | 37.2032 | 0 | 45.8452 | 16.0376 | 174.8133 | 0 | 26% | 7.8435 | 0 | 20.67% | 0 | 43.0084
3850 | 916 | 827 | 88 | 4.8 | 26.9 | 242.8153 | 0 | 53.8667 | 0 | 46.592 | 16.2307 | 197.2717 | 0 | 40% | 24.0695 | 0 | 53.4% | 0 | 43.4115
3851 | 950 | 951 | 88 | 4 | 27.5 | 262.5477 | 0 | 55.6907 | 10.9058 | 42.6088 | 14.5554 | 220.8313 | 0 | 57% | 25 | 0 | 87.4% | 0 | 42.4317
3852 | 953 | 1013 | 92 | 2.5 | 28.2 | 270.3847 | 0 | 31.9231 | 40.9208 | 42.6108 | 14.4949 | 228.6395 | 0 | 74% | 1.9105 | 0 | 90% | 0 | 41.5899
3853 | 934 | 1016 | 106 | 3.9 | 28.7 | 264.787 | 0 | 29.2896 | 43.8153 | 42.6115 | 14.4507 | 222.8894 | 0 | 90% | 0 | 0 | 90% | 0 | 41.324
3854 | 911 | 965 | 116 | 5.1 | 28.7 | 180.3676 | 82.7898 | 25.2758 | 42.6622 | 42.6114 | 14.4506 | 138.4681 | 0 | 100% | 0 | 0 | 90% | 0 | 41.1603
3855 | 887 | 853 | 105 | 4.3 | 28.8 | 42.1517 | 225.8336 | 25.4513 | 31.0845 | 42.6102 | 14.4413 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.6021
3856 | 854 | 705 | 95 | 5.3 | 28.7 | 42.1572 | 204.5041 | 25.0496 | 16.1612 | 42.6074 | 14.4493 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.2084
3857 | 801 | 522 | 80 | 6 | 28.1 | 48.3547 | 162.5265 | 23.076 | 0 | 48.6938 | 16.9927 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.7557
3858 | 644 | 316 | 76 | 5.8 | 27.6 | 42.0343 | 98.6331 | 5.791 | 0 | 42.6023 | 14.5445 | 0 | 0 | 100% | 0 | 20.3408 | 57.45% | 0 | 41.386
3859 | 418 | 127 | 49 | 4.6 | 26.4 | 0 | 60.3923 | 0 | 0 | 48.8604 | 17.2319 | 0 | 47.329 | 97% | 0 | 25 | 17.46% | 0 | 40.1466
3860 | 25 | 9 | 7 | 2.8 | 24.5 | 0 | 0 | 0 | 0 | 89.8232 | 35.038 | 0 | 91.8908 | 90% | 0 | 4.6592 | 10% | 0 | 36.7471
3861 | 0 | 0 | 0 | 1.9 | 23.1 | 0 | 0 | 0 | 0 | 95.5432 | 37.7 | 0 | 95.5519 | 83% | 0 | 0 | 10% | 0 | 35.2445
3862 | 0 | 0 | 0 | 1.3 | 20.3 | 0 | 0 | 0 | 0 | 90.8592 | 35.9734 | 0 | 89.4415 | 76% | 0 | 0 | 10% | 0 | 33.6327
3863 | 0 | 0 | 0 | 0.9 | 19.8 | 0 | 0 | 0 | 0 | 87.7913 | 34.7221 | 0 | 85.7836 | 70% | 0 | 0 | 10% | 0 | 32.3631
3864 | 0 | 0 | 0 | 1 | 19.4 | 0 | 0 | 0 | 0 | 86.4754 | 34.2001 | 0 | 84.3592 | 63% | 0 | 0 | 10% | 0 | 31.7925
3865 | 0 | 0 | 0 | 1.8 | 19.3 | 0 | 0 | 0 | 0 | 86.2646 | 34.1194 | 0 | 84.2425 | 57% | 0 | 0 | 10% | 0 | 31.6661
3866 | 0 | 0 | 0 | 0.9 | 18.3 | 0 | 0 | 0 | 0 | 87.3223 | 34.6341 | 0 | 85.6082 | 51% | 0 | 0 | 10% | 0 | 32.1446
3867 | 0 | 0 | 0 | 1.8 | 18.3 | 0 | 0 | 0 | 0 | 93.0599 | 37.0542 | 0 | 92.6867 | 44% | 0 | 0 | 10% | 0 | 34.5382
3868 | 0 | 0 | 0 | 0.6 | 17.6 | 0 | 0 | 0 | 0 | 101.0776 | 40.4596 | 0 | 102.1827 | 36% | 0 | 0 | 10% | 0 | 37.9584
3869 | 0 | 1 | 1 | 0.8 | 17.4 | 0 | 0 | 0 | 0 | 107.9863 | 43.3606 | 0 | 110.2195 | 28% | 0 | 0 | 10% | 0 | 40.9123
3870 | 339 | 75 | 26 | 0.7 | 18.7 | 0 | 52.9222 | 0 | 0 | 111.2535 | 44.608 | 0 | 113.7273 | 19% | 0 | 0 | 10% | 0 | 42.2368
3871 | 689 | 265 | 49 | 1.1 | 22.2 | 101.2443 | 24.7332 | 1.6615 | 0 | 108.6135 | 43.2107 | 8.2378 | 20.3364 | 18% | 0 | 0 | 10% | 0 | 43.1176
3872 | 831 | 473 | 60 | 3.1 | 24.4 | 187.4899 | 0 | 18.0372 | 0 | 72.8055 | 27.7696 | 116.0737 | 0 | 27% | 0 | 0 | 10% | 0 | 43.6381
3873 | 905 | 666 | 66 | 3.4 | 26.4 | 228.0542 | 0 | 37.1151 | 0 | 46.1922 | 16.1123 | 183.0949 | 0 | 41% | 6.7183 | 0 | 19.14% | 0 | 43.9993
3874 | 948 | 831 | 68 | 2.7 | 27.2 | 253.4711 | 0 | 54.0366 | 0 | 46.9414 | 16.3491 | 207.8267 | 0 | 56% | 23.6871 | 0 | 51.35% | 0 | 43.9344
3875 | 956 | 943 | 75 | 3.1 | 28.5 | 264.9253 | 0 | 55.9765 | 9.6733 | 42.5967 | 14.4635 | 223.4383 | 0 | 73% | 25 | 0 | 85.35% | 0 | 42.5502
3876 | 955 | 1005 | 83 | 4.7 | 28.9 | 269.3073 | 8.15e-15 | 33.7463 | 38.287 | 42.6013 | 14.4294 | 227.6599 | 0 | 90% | 3.4181 | 0 | 90% | 0 | 41.8008
3877 | 950 | 1014 | 90 | 4.9 | 29.4 | 178.5098 | 103.3581 | 26.9653 | 45.9041 | 42.6035 | 14.3857 | 136.7631 | 0 | 100% | 0 | 0 | 90% | 0 | 41.7324
3878 | 935 | 962 | 90 | 3.1 | 29.7 | 42.1516 | 249.8377 | 26.5532 | 40.8316 | 42.603 | 14.3588 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.6213
3879 | 909 | 857 | 90 | 3.9 | 30.2 | 42.1571 | 232.8417 | 26.1857 | 30.3081 | 42.6004 | 14.3132 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.208
3880 | 768 | 691 | 140 | 4.7 | 30.5 | 42.1571 | 178.7174 | 26.2859 | 13.7377 | 42.5979 | 14.2853 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2803
3881 | 720 | 519 | 122 | 4.7 | 30 | 42.1571 | 147.5056 | 23.3826 | 0 | 42.5955 | 14.3297 | 0 | 0 | 100% | 0 | 3.2471 | 84.8% | 0 | 41.6685
3882 | 657 | 315 | 69 | 4.3 | 28.9 | 42.1572 | 102.4186 | 5.5107 | 0 | 42.5932 | 14.4267 | 0 | 0 | 100% | 0 | 21.1152 | 51.02% | 0 | 41.762
3883 | 310 | 108 | 52 | 4.1 | 24.9 | 0 | 54.5541 | 0 | 0 | 49.2361 | 17.5249 | 0 | 47.7037 | 97% | 0 | 25 | 11.02% | 0 | 40.4512
3884 | 9 | 7 | 6 | 5.8 | 20.4 | 0 | 0 | 0 | 0 | 101.3999 | 40.3724 | 0 | 104.5044 | 89% | 0 | 0 | 11.02% | 0 | 37.4063
3885 | 0 | 0 | 0 | 7.9 | 18.4 | 0 | 0 | 0 | 0 | 95.7733 | 38.1828 | 0 | 95.4851 | 82% | 0 | 0 | 11.02% | 0 | 35.821
3886 | 0 | 0 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 91.5582 | 36.4396 | 0 | 90.1102 | 75% | 0 | 0 | 11.02% | 0 | 34.154
3887 | 0 | 0 | 0 | 7.4 | 17.5 | 0 | 0 | 0 | 0 | 88.1654 | 35.0435 | 0 | 86.0698 | 68% | 0 | 0 | 11.02% | 0 | 32.7347
3888 | 0 | 0 | 0 | 6.9 | 16.9 | 0 | 0 | 0 | 0 | 87.3758 | 34.7523 | 0 | 85.2938 | 62% | 0 | 0 | 11.02% | 0 | 32.3879
3889 | 0 | 0 | 0 | 6.6 | 16.5 | 0 | 0 | 0 | 0 | 87.1626 | 34.6894 | 0 | 85.1731 | 56% | 0 | 0 | 11.02% | 0 | 32.2798
3890 | 0 | 0 | 0 | 5.1 | 16.1 | 0 | 0 | 0 | 0 | 88.7026 | 35.3651 | 0 | 87.1277 | 49% | 0 | 0 | 11.02% | 0 | 32.919
3891 | 0 | 0 | 0 | 4.7 | 16 | 0 | 0 | 0 | 0 | 93.9162 | 37.5819 | 0 | 93.5902 | 42% | 0 | 0 | 11.02% | 0 | 35.1132
3892 | 0 | 0 | 0 | 5.3 | 15.2 | 0 | 0 | 0 | 0 | 101.9613 | 41.01 | 0 | 103.069 | 35% | 0 | 0 | 11.02% | 0 | 38.555
3893 | 0 | 1 | 1 | 4.1 | 14.9 | 0 | 0 | 0 | 0 | 108.5796 | 43.8026 | 0 | 110.7351 | 26% | 0 | 0 | 11.02% | 0 | 41.3979
3894 | 9 | 42 | 41 | 3.5 | 15.5 | 0 | 1.4048 | 0 | 0 | 111.4562 | 44.9545 | 0 | 113.7981 | 18% | 0 | 0 | 11.02% | 0 | 42.6224
3895 | 495 | 258 | 100 | 4.7 | 17 | 66.5573 | 17.2095 | 2.9166 | 0 | 104.3006 | 41.8602 | 0 | 40.5123 | 15% | 0 | 0 | 11.02% | 0 | 43.3336
3896 | 495 | 443 | 203 | 5.2 | 18 | 102.4057 | 0 | 19.3536 | 0 | 67.5397 | 25.9426 | 36.6731 | 0 | 17% | 0 | 0 | 11.02% | 0 | 43.8988
3897 | 358 | 499 | 256 | 5.3 | 18.9 | 77.3561 | 0 | 26.869 | 0 | 51.4072 | 18.8938 | 28.0107 | 0 | 19% | 0 | 0 | 11.02% | 0 | 44.6096
3898 | 708 | 752 | 175 | 5.1 | 20.2 | 182.726 | 0 | 49.1748 | 0 | 43.9217 | 15.6586 | 138.7479 | 0 | 30% | 18.3534 | 0 | 35.98% | 0 | 44.4089
3899 | 924 | 938 | 106 | 5.1 | 21.2 | 253.6507 | 0 | 55.6554 | 11.7421 | 42.5753 | 15.04 | 211.7924 | 0 | 46% | 25 | 0 | 69.98% | 0 | 42.9639
3900 | 943 | 999 | 99 | 5.7 | 21.8 | 264.6847 | 0 | 44.8291 | 29.1944 | 42.5922 | 15.0047 | 223.1536 | 0 | 62% | 14.7199 | 0 | 90% | 0 | 42.2441
3901 | 942 | 1006 | 101 | 6.1 | 22.7 | 265.0254 | 0 | 29.9993 | 44.6887 | 42.5972 | 14.9408 | 223.4438 | 0 | 79% | 0 | 0 | 90% | 0 | 42.0463
3902 | 930 | 956 | 102 | 6.5 | 23.2 | 256.4945 | 0 | 29.0317 | 40.3864 | 42.6008 | 14.9044 | 214.7072 | 0 | 95% | 0 | 0 | 90% | 0 | 42.0202
3903 | 900 | 858 | 100 | 6 | 23.7 | 112.953 | 147.6413 | 26.1482 | 31.8097 | 42.6027 | 14.8665 | 71.2885 | 0 | 100% | 0 | 0 | 90% | 0 | 41.622
3904 | 850 | 705 | 97 | 6.4 | 23.2 | 42.1523 | 203.1721 | 25.8532 | 16.1192 | 42.6012 | 14.9045 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.4685
3905 | 784 | 518 | 84 | 6.3 | 22.5 | 42.1578 | 165.225 | 23.338 | 0 | 42.5987 | 14.9561 | 0 | 0 | 100% | 0 | 2.7198 | 85.65% | 0 | 41.7249
3906 | 653 | 312 | 68 | 6.7 | 21.5 | 42.1578 | 100.6922 | 5.6116 | 0 | 42.5962 | 15.0267 | 0 | 0 | 100% | 0 | 20.7186 | 52.5% | 0 | 42.0681
3907 | 373 | 115 | 42 | 6.8 | 19.8 | 0 | 52.6744 | 0 | 0 | 49.2977 | 17.939 | 0 | 47.7653 | 97% | 0 | 25 | 12.5% | 0 | 40.8626
3908 | 13 | 6 | 5 | 6.4 | 17.9 | 0 | 0 | 0 | 0 | 101.3711 | 40.5582 | 0 | 104.4683 | 89% | 0 | 0 | 12.5% | 0 | 37.5914
3909 | 0 | 0 | 0 | 5.3 | 17.3 | 0 | 0 | 0 | 0 | 96.1568 | 38.4238 | 0 | 95.9394 | 82% | 0 | 0 | 12.5% | 0 | 36.0603
3910 | 0 | 0 | 0 | 4 | 17.7 | 0 | 0 | 0 | 0 | 91.8308 | 36.576 | 0 | 90.427 | 75% | 0 | 0 | 12.5% | 0 | 34.2948
3911 | 0 | 0 | 0 | 3.5 | 17.5 | 0 | 0 | 0 | 0 | 88.8973 | 35.3515 | 0 | 86.9248 | 68% | 0 | 0 | 12.5% | 0 | 33.0493
3912 | 0 | 0 | 0 | 3.1 | 16.7 | 0 | 0 | 0 | 0 | 87.6089 | 34.8635 | 0 | 85.5272 | 62% | 0 | 0 | 12.5% | 0 | 32.5127
3913 | 0 | 0 | 0 | 3.6 | 16.5 | 0 | 0 | 0 | 0 | 87.3003 | 34.7472 | 0 | 85.294 | 56% | 0 | 0 | 12.5% | 0 | 32.3507
3914 | 0 | 0 | 0 | 1.5 | 16 | 0 | 0 | 0 | 0 | 88.7233 | 35.3804 | 0 | 87.1114 | 49% | 0 | 0 | 12.5% | 0 | 32.9464
3915 | 0 | 0 | 0 | 1.5 | 15.4 | 0 | 0 | 0 | 0 | 93.7791 | 37.5644 | 0 | 93.3798 | 42% | 0 | 0 | 12.5% | 0 | 35.1063
3916 | 0 | 0 | 0 | 2 | 15.4 | 0 | 0 | 0 | 0 | 102.082 | 41.0459 | 0 | 103.1836 | 34% | 0 | 0 | 12.5% | 0 | 38.5985
3917 | 0 | 1 | 1 | 1.7 | 15.2 | 0 | 0 | 0 | 0 | 108.4612 | 43.7306 | 0 | 110.5634 | 26% | 0 | 0 | 12.5% | 0 | 41.3332
3918 | 7 | 37 | 36 | 1.4 | 15.5 | 0 | 1.0923 | 0 | 0 | 111.0397 | 44.7809 | 0 | 113.2768 | 18% | 0 | 0 | 12.5% | 0 | 42.4549
3919 | 117 | 147 | 109 | 2.1 | 18.1 | 0 | 25.5733 | 1.1356 | 0 | 110.539 | 44.3631 | 0 | 112.3652 | 9% | 0 | 0 | 12.5% | 0 | 43.2422
3920 | 479 | 424 | 182 | 5.3 | 20.7 | 80.311 | 20.4033 | 17.2525 | 0 | 72.7225 | 28.0493 | 21.3992 | 12.8922 | 10% | 0 | 0 | 12.5% | 0 | 43.8053
3921 | 695 | 630 | 164 | 6.3 | 21.9 | 168.3718 | 2.98e-14 | 35.5835 | 0 | 43.8863 | 15.53 | 125.0859 | 0 | 19% | 4.6516 | 0 | 18.82% | 0 | 44.5195
3922 | 741 | 796 | 194 | 6.8 | 23.5 | 190.7909 | 0 | 52.1806 | 0 | 44.6423 | 15.7165 | 147.4437 | 0 | 30% | 21.0221 | 0 | 47.41% | 0 | 44.7164
3923 | 828 | 918 | 162 | 6.8 | 25 | 223.6247 | 0 | 56.2097 | 7.65 | 42.5857 | 14.7577 | 182.1666 | 0 | 44% | 25 | 0 | 81.42% | 0 | 43.5016
3924 | 845 | 982 | 162 | 6.8 | 25.9 | 234.1489 | 0 | 36.9906 | 33.1908 | 42.5962 | 14.6873 | 192.759 | 0 | 58% | 6.3127 | 0 | 90% | 0 | 42.779
3925 | 848 | 989 | 159 | 7.1 | 25.4 | 235.6976 | 0 | 30.5678 | 40.4592 | 42.5999 | 14.7297 | 194.2071 | 0 | 73% | 0 | 0 | 90% | 0 | 42.6813
3926 | 856 | 944 | 143 | 6.9 | 25.4 | 234.0543 | 0 | 30.588 | 35.9935 | 42.6024 | 14.7306 | 192.3757 | 0 | 87% | 0 | 0 | 90% | 0 | 42.7023
3927 | 810 | 839 | 152 | 6 | 25.2 | 214.1883 | 0 | 25.6366 | 30.1749 | 42.6037 | 14.7475 | 172.2534 | 0 | 100% | 0 | 0 | 90% | 0 | 42.3635
3928 | 715 | 685 | 170 | 5.7 | 25.1 | 41.3744 | 163.3642 | 26.6769 | 13.9783 | 42.604 | 14.7558 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.143
3929 | 545 | 475 | 167 | 5.8 | 24.1 | 42.1523 | 97.2545 | 21.2959 | 0 | 42.6014 | 14.8349 | 0 | 0 | 100% | 0 | 5.4873 | 81.22% | 0 | 42.3286
3930 | 306 | 245 | 121 | 5.2 | 22.7 | 0 | 58.9203 | 4.416 | 0 | 43.6056 | 15.3522 | 0 | 42.1066 | 97% | 0 | 24.393 | 42.19% | 0 | 42.0844
3931 | 1 | 41 | 41 | 5.4 | 20.6 | 0 | 0.17677 | 0 | 0 | 62.7624 | 23.6515 | 0 | 62.3863 | 92% | 0 | 20.1196 | 10% | 0 | 40.8406
3932 | 0 | 3 | 3 | 4.7 | 19.5 | 0 | 0 | 0 | 0 | 101.697 | 40.5695 | 0 | 104.0078 | 84% | 0 | 0 | 10% | 0 | 37.8228
3933 | 0 | 0 | 0 | 4.2 | 18.9 | 0 | 0 | 0 | 0 | 96.9069 | 38.6168 | 0 | 96.8488 | 77% | 0 | 0 | 10% | 0 | 36.2425
3934 | 0 | 0 | 0 | 3.1 | 18.5 | 0 | 0 | 0 | 0 | 92.5659 | 36.829 | 0 | 91.3617 | 70% | 0 | 0 | 10% | 0 | 34.5351
3935 | 0 | 0 | 0 | 2.2 | 18.1 | 0 | 0 | 0 | 0 | 89.4413 | 35.5389 | 0 | 87.562 | 64% | 0 | 0 | 10% | 0 | 33.239
3936 | 0 | 0 | 0 | 3.3 | 18.2 | 0 | 0 | 0 | 0 | 88.4366 | 35.1091 | 0 | 86.4709 | 57% | 0 | 0 | 10% | 0 | 32.7698
3937 | 0 | 0 | 0 | 3.1 | 17.9 | 0 | 0 | 0 | 0 | 88.2413 | 35.0483 | 0 | 86.3465 | 51% | 0 | 0 | 10% | 0 | 32.6717
3938 | 0 | 0 | 0 | 3.5 | 17.9 | 0 | 0 | 0 | 0 | 89.3683 | 35.5231 | 0 | 87.7945 | 44% | 0 | 0 | 10% | 0 | 33.1153
3939 | 0 | 0 | 0 | 3.2 | 19 | 0 | 0 | 0 | 0 | 94.6365 | 37.6662 | 0 | 94.2973 | 37% | 0 | 0 | 10% | 0 | 35.2351
3940 | 0 | 0 | 0 | 2.3 | 18.2 | 0 | 0 | 0 | 0 | 102.4197 | 40.9766 | 0 | 103.4763 | 29% | 0 | 0 | 10% | 0 | 38.5551
3941 | 0 | 1 | 1 | 2.4 | 18 | 0 | 0 | 0 | 0 | 108.438 | 43.5 | 0 | 110.4379 | 21% | 0 | 0 | 10% | 0 | 41.1223
3942 | 83 | 50 | 36 | 2.7 | 17.6 | 0 | 12.9453 | 0 | 0 | 111.9265 | 44.98 | 0 | 114.2674 | 12% | 0 | 0 | 10% | 0 | 42.6639
3943 | 455 | 233 | 88 | 2.2 | 18.9 | 61.3055 | 15.4996 | 1.9618 | 0 | 107.6552 | 43.1043 | 0 | 49.5124 | 9% | 0 | 0 | 10% | 0 | 43.6645
3944 | 672 | 443 | 108 | 2.6 | 20.7 | 148.2018 | 0 | 17.2682 | 0 | 74.2952 | 28.7402 | 74.9867 | 0 | 14% | 0 | 0 | 10% | 0 | 44.2007
3945 | 804 | 644 | 109 | 1.9 | 23.3 | 201.2761 | 0 | 36.0391 | 0 | 44.8817 | 15.8306 | 157.5216 | 0 | 26% | 4.763 | 0 | 16.48% | 0 | 44.8603
3946 | 876 | 814 | 108 | 4 | 24.9 | 231.641 | 0 | 53.0782 | 0 | 45.9139 | 16.1258 | 187.0782 | 0 | 40% | 21.9727 | 0 | 46.36% | 0 | 44.6923
3947 | 918 | 938 | 105 | 3 | 26.4 | 253.6388 | 0 | 56.603 | 9.0395 | 42.5998 | 14.6465 | 212.251 | 0 | 56% | 25 | 0 | 80.36% | 0 | 43.492
3948 | 935 | 1006 | 103 | 5.2 | 27.5 | 262.804 | 0 | 37.7663 | 34.5272 | 42.6049 | 14.5541 | 221.359 | 0 | 73% | 7.0878 | 0 | 90% | 0 | 42.3591
3949 | 934 | 1014 | 104 | 5.3 | 28.4 | 263.4391 | 0 | 30.614 | 42.2775 | 42.6066 | 14.4757 | 221.8453 | 0 | 89% | 0 | 0 | 90% | 0 | 42.192
3950 | 920 | 961 | 103 | 6 | 28.9 | 191.2445 | 72.6238 | 26.8514 | 40.6225 | 42.6077 | 14.4316 | 149.4636 | 0 | 100% | 0 | 0 | 90% | 0 | 42.1006
3951 | 913 | 867 | 94 | 4.3 | 29.2 | 42.1517 | 234.1234 | 26.4108 | 30.9068 | 42.607 | 14.4047 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.5249
3952 | 869 | 715 | 92 | 5.6 | 28.8 | 42.1572 | 209.1627 | 26.0362 | 15.8057 | 42.6043 | 14.4394 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.1851
3953 | 745 | 518 | 100 | 5.3 | 28 | 42.1573 | 154.7401 | 22.8798 | 0 | 42.6017 | 14.5096 | 0 | 0 | 100% | 0 | 2.6954 | 85.69% | 0 | 40.7945
3954 | 585 | 309 | 90 | 5.3 | 26.6 | 42.1574 | 84.6556 | 6.137 | 0 | 42.5992 | 14.6294 | 0 | 0 | 100% | 0 | 19.2328 | 54.92% | 0 | 40.7092
3955 | 288 | 102 | 45 | 4.2 | 25.5 | 0 | 51.0142 | 0 | 0 | 47.8275 | 16.8795 | 0 | 46.2989 | 97% | 0 | 25 | 14.92% | 0 | 39.8116
3956 | 19 | 9 | 8 | 3.7 | 23.4 | 0 | 0 | 0 | 0 | 94.4719 | 37.1267 | 0 | 97.0194 | 90% | 0 | 3.0718 | 10% | 0 | 37.2441
3957 | 0 | 0 | 0 | 1.7 | 21.4 | 0 | 0 | 0 | 0 | 96.5959 | 38.288 | 0 | 96.6069 | 82% | 0 | 0 | 10% | 0 | 35.8834
3958 | 0 | 0 | 0 | 0.9 | 19.4 | 0 | 0 | 0 | 0 | 90.8792 | 36.0501 | 0 | 89.3135 | 76% | 0 | 0 | 10% | 0 | 33.7548
3959 | 0 | 0 | 0 | 0.3 | 18.7 | 0 | 0 | 0 | 0 | 87.2715 | 34.5839 | 0 | 85.0574 | 69% | 0 | 0 | 10% | 0 | 32.258
3960 | 0 | 0 | 0 | 0.8 | 18.7 | 0 | 0 | 0 | 0 | 85.9844 | 34.0448 | 0 | 83.7136 | 63% | 0 | 0 | 10% | 0 | 31.6574
3961 | 0 | 0 | 0 | 1.9 | 18.8 | 0 | 0 | 0 | 0 | 84.8394 | 33.5592 | 0 | 82.5153 | 57% | 0 | 0 | 10% | 0 | 31.1193
3962 | 0 | 0 | 0 | 1.9 | 17.6 | 0 | 0 | 0 | 0 | 83.8383 | 33.2227 | 0 | 81.4713 | 51% | 0 | 0 | 10% | 0 | 30.7365
3963 | 0 | 0 | 0 | 1.8 | 16.7 | 0 | 0 | 0 | 0 | 83.5899 | 33.1778 | 0 | 81.2991 | 45% | 0 | 0 | 10% | 0 | 30.6496
3964 | 0 | 0 | 0 | 1.6 | 16 | 0 | 0 | 0 | 0 | 85.5972 | 34.0648 | 0 | 83.7736 | 38% | 0 | 0 | 10% | 0 | 31.4992
3965 | 0 | 1 | 1 | 1.8 | 15.6 | 0 | 0 | 0 | 0 | 91.6538 | 36.648 | 0 | 91.1835 | 32% | 0 | 0 | 10% | 0 | 34.0564
3966 | 384 | 78 | 25 | 1.3 | 16 | 0 | 48.9045 | 0 | 0 | 98.2463 | 39.393 | 0 | 99.0375 | 24% | 0 | 0 | 10% | 0 | 36.8197
3967 | 729 | 272 | 45 | 0.6 | 19.9 | 131.9935 | 0 | 1.5462 | 0 | 98.1839 | 39.0748 | 29.1667 | 0 | 26% | 0 | 0 | 10% | 0 | 38.9426
3968 | 860 | 482 | 56 | 1 | 22.4 | 195.5693 | 0 | 18.366 | 0 | 62.7473 | 23.5331 | 133.5446 | 0 | 36% | 0 | 0 | 10% | 0 | 39.6813
3969 | 926 | 678 | 62 | 1.4 | 24.3 | 234.6809 | 0 | 37.7333 | 0 | 46.1298 | 16.2661 | 189.3153 | 0 | 50% | 11.4606 | 0 | 25.59% | 0 | 39.9753
3970 | 962 | 842 | 66 | 2.4 | 26.6 | 257.499 | 0 | 53.3361 | 1.235 | 42.5831 | 14.6238 | 215.6337 | 0 | 66% | 25 | 0 | 59.59% | 0 | 40.1696
3971 | 970 | 957 | 75 | 5.1 | 27.7 | 267.3421 | 0 | 49.7362 | 16.8811 | 42.5917 | 14.5322 | 225.4018 | 0 | 83% | 22.3629 | 0 | 90% | 0 | 38.9968
3972 | 965 | 1025 | 90 | 5 | 27.9 | 271.8764 | 0 | 19.8929 | 53.5806 | 42.5959 | 14.5163 | 229.7726 | 0 | 100% | 0 | 0 | 90% | 0 | 37.3778
3973 | 963 | 1028 | 87 | 4.2 | 28.4 | 41.3307 | 264.8229 | 21.2382 | 52.5625 | 42.5987 | 14.473 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.4208
3974 | 950 | 975 | 86 | 3.1 | 28.8 | 42.1517 | 254.7278 | 20.92 | 47.4434 | 42.5962 | 14.4366 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.0661
3975 | 927 | 869 | 82 | 4.2 | 28.4 | 42.1573 | 238.5595 | 20.7547 | 36.66 | 42.5939 | 14.4714 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.9357
3976 | 889 | 718 | 78 | 3.4 | 28.6 | 42.1572 | 215.6495 | 20.8786 | 20.9177 | 42.5916 | 14.4528 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.041
3977 | 826 | 532 | 71 | 4.3 | 28.3 | 42.1573 | 177.9141 | 21.2273 | 2.1736 | 42.5893 | 14.4787 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.4157
3978 | 710 | 327 | 59 | 4.2 | 27.1 | 42.1574 | 116.2603 | 5.8948 | 0 | 42.5872 | 14.5827 | 0 | 0 | 100% | 0 | 15.8467 | 64.64% | 0 | 37.0341
3979 | 440 | 125 | 39 | 3.5 | 25.8 | 0 | 65.079 | 0 | 0 | 43.3865 | 15.0163 | 0 | 41.8869 | 97% | 0 | 24.2972 | 25.77% | 0 | 37.2338
3980 | 26 | 8 | 6 | 2.3 | 23.2 | 0 | 0 | 0 | 0 | 73.6355 | 28.2518 | 0 | 74.0905 | 91% | 0 | 9.8561 | 10% | 0 | 35.1812
3981 | 0 | 0 | 0 | 1.7 | 21.2 | 0 | 0 | 0 | 0 | 90.8184 | 35.8849 | 0 | 90.3469 | 85% | 0 | 0 | 10% | 0 | 33.2679
3982 | 0 | 0 | 0 | 3.2 | 19.7 | 0 | 0 | 0 | 0 | 85.8337 | 33.9102 | 0 | 83.9841 | 79% | 0 | 0 | 10% | 0 | 31.3898
3983 | 0 | 0 | 0 | 2.1 | 19.5 | 0 | 0 | 0 | 0 | 82.4074 | 32.4709 | 0 | 80.1511 | 73% | 0 | 0 | 10% | 0 | 29.9127
3984 | 0 | 0 | 0 | 1.8 | 18.6 | 0 | 0 | 0 | 0 | 80.5381 | 31.6837 | 0 | 78.4136 | 67% | 0 | 0 | 10% | 0 | 29.0708
3985 | 0 | 0 | 0 | 2.4 | 18.7 | 0 | 0 | 0 | 0 | 79.6841 | 31.2909 | 0 | 77.6504 | 61% | 0 | 0 | 10% | 0 | 28.6403
3986 | 0 | 0 | 0 | 2.7 | 18.8 | 0 | 0 | 0 | 0 | 78.9459 | 30.9514 | 0 | 76.9736 | 55% | 0 | 0 | 10% | 0 | 28.2736
3987 | 0 | 0 | 0 | 2.5 | 18.1 | 0 | 0 | 0 | 0 | 78.4738 | 30.786 | 0 | 76.5476 | 50% | 0 | 0 | 10% | 0 | 28.087
3988 | 0 | 0 | 0 | 3.4 | 17.6 | 0 | 0 | 0 | 0 | 78.1643 | 30.6794 | 0 | 76.2742 | 44% | 0 | 0 | 10% | 0 | 27.9635
3989 | 0 | 1 | 1 | 1.8 | 16.3 | 0 | 0 | 0 | 0 | 81.7641 | 32.3941 | 0 | 79.9652 | 38% | 0 | 0 | 10% | 0 | 29.6596
3990 | 255 | 87 | 56 | 2.1 | 17.5 | 0 | 39.7183 | 0 | 0 | 87.7228 | 34.8596 | 0 | 86.918 | 32% | 0 | 0 | 10% | 0 | 32.1063
3991 | 349 | 235 | 118 | 2.4 | 20.1 | 0 | 65.2849 | 2.9692 | 0 | 85.686 | 33.8217 | 0 | 84.3916 | 25% | 0 | 0 | 10% | 0 | 34.0583
3992 | 331 | 378 | 215 | 4 | 22.4 | 63.1702 | 0 | 15.0575 | 0 | 57.6599 | 21.3598 | 5.7456 | 0 | 26% | 0 | 0 | 10% | 0 | 35.4008
3993 | 572 | 653 | 266 | 5.1 | 24.4 | 136.0541 | 0 | 37.0183 | 0 | 44.256 | 15.4895 | 91.1925 | 0 | 33% | 15.0491 | 0 | 30.47% | 0 | 35.8198
3994 | 265 | 590 | 366 | 5.8 | 24.7 | 55.5876 | 0 | 35.4315 | 0 | 42.5375 | 14.7649 | 14.325 | 0 | 34% | 13.1437 | 0 | 48.34% | 0 | 36.1122
3995 | 126 | 568 | 445 | 4.6 | 25.3 | 0 | 39.8252 | 34.9139 | 0 | 45.432 | 15.9043 | 0 | 43.6603 | 30% | 12.9898 | 0 | 66.01% | 0 | 35.9119
3996 | 2 | 283 | 275 | 5.3 | 24.4 | 0 | 0.64582 | 11.2483 | 0 | 42.5288 | 14.7857 | 0 | 40.8003 | 27% | 0 | 11.1202 | 48.22% | 0 | 34.3196
3997 | 135 | 477 | 336 | 5.2 | 24.4 | 0 | 43.7466 | 28.3626 | 0 | 47.376 | 16.7801 | 0 | 45.5813 | 24% | 9.007 | 0 | 60.47% | 0 | 33.2937
3998 | 566 | 816 | 277 | 5.6 | 26.1 | 122.1482 | 29.7169 | 42.0962 | 13.2811 | 42.5065 | 14.6398 | 85.3491 | 7.3091 | 30% | 21.7165 | 0 | 90% | 0 | 33.0911
3999 | 250 | 587 | 372 | 6.2 | 25.6 | 0 | 64.3979 | 20.5114 | 15.8333 | 42.5255 | 14.6876 | 0 | 40.8586 | 27% | 0 | 0 | 90% | 0 | 33.2259
4000 | 785 | 718 | 151 | 6.3 | 25.5 | 197.6868 | 0 | 21.2026 | 21.6928 | 42.5171 | 14.6929 | 149.5417 | 0 | 38% | 0 | 0 | 90% | 0 | 33.7616
4001 | 468 | 406 | 146 | 6 | 24.7 | 100.3692 | 1.49e-14 | 17.2912 | 0 | 42.5474 | 14.7683 | 58.6805 | 0 | 42% | 0 | 4.1417 | 83.37% | 0 | 34.8661
4002 | 311 | 214 | 87 | 5.4 | 23.8 | 0 | 60.3841 | 2.8151 | 0 | 42.5516 | 14.8409 | 0 | 41.0347 | 39% | 0 | 20.8566 | 50% | 0 | 36.4445
4003 | 221 | 117 | 68 | 4.9 | 22.8 | 0 | 39.2969 | 0 | 0 | 43.6502 | 15.3653 | 0 | 42.1096 | 36% | 0 | 25 | 10% | 0 | 37.3977
4004 | 5 | 10 | 9 | 3.4 | 21.5 | 0 | 0 | 0 | 0 | 96.6459 | 38.3026 | 0 | 98.8112 | 29% | 0 | 0 | 10% | 0 | 35.2734
4005 | 0 | 0 | 0 | 2.4 | 20.3 | 0 | 0 | 0 | 0 | 90.6847 | 35.9035 | 0 | 91.0855 | 22% | 0 | 0 | 10% | 0 | 32.983
4006 | 0 | 0 | 0 | 1.3 | 19.4 | 0 | 0 | 0 | 0 | 86.4237 | 34.1818 | 0 | 85.6848 | 16% | 0 | 0 | 10% | 0 | 31.3151
4007 | 0 | 0 | 0 | 1.1 | 18.7 | 0 | 0 | 0 | 0 | 83.1633 | 32.87 | 0 | 81.7158 | 10% | 0 | 0 | 10% | 0 | 30.026
4008 | 0 | 0 | 0 | 1 | 17.8 | 0 | 0 | 0 | 0 | 81.2977 | 32.0934 | 0 | 79.7495 | 4% | 0 | 0 | 10% | 0 | 29.253
4009 | 0 | 0 | 0 | 1.1 | 17.1 | 0 | 0 | 0 | 0 | 52.7052 | 20.8314 | 0 | 51.6937 | 0% | 0 | 0 | 10% | 0 | 18.0248
4010 | 0 | 0 | 0 | 0.8 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.7314
4011 | 0 | 0 | 0 | 0.4 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.7009
4012 | 0 | 0 | 0 | 0.1 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.6709
4013 | 0 | 1 | 1 | 0.9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.6413
4014 | 308 | 74 | 30 | 0.3 | 16.1 | 0 | 47.9311 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.6122
4015 | 652 | 261 | 58 | 0.2 | 21.2 | 95.2163 | 23.3179 | 1.6874 | 0 | 0 | 0 | 91.0791 | 0 | 7% | 0 | 0 | 10% | 0 | 0.070025
4016 | 795 | 465 | 72 | 1.1 | 23 | 179.3371 | 0 | 17.6887 | 0 | 0 | 0 | 176.4578 | 0 | 20% | 0 | 0 | 10% | 0 | 15.7177
4017 | 882 | 662 | 77 | 1.9 | 24.3 | 222.3561 | -2.98e-14 | 36.7959 | 0 | 0 | 0 | 220.3046 | 0 | 36% | 0 | 0 | 10% | 0 | 34.4169
4018 | 928 | 827 | 80 | 1.4 | 26.9 | 248.2182 | 0 | 53.4684 | 0 | 0 | 0 | 246.5379 | 0 | 55% | 6.7734 | 0 | 19.21% | 0 | 44.0446
4019 | 942 | 942 | 86 | 2.3 | 28.6 | 261.0397 | 0 | 65.206 | 0 | 42.5574 | 0 | 219.0671 | 0 | 71% | 22.8613 | 0 | 50.31% | 0 | 39.0137
4020 | 943 | 1004 | 92 | 3.9 | 29.4 | 266.4189 | 0 | 71.2755 | 0.20296 | 0 | 0 | 265.066 | 0 | 90% | 25 | 0 | 84.31% | 0 | 43.3801
4021 | 945 | 1016 | 94 | 4.9 | 29.6 | 130.2486 | 150.3028 | 49.2814 | 23.3408 | 0 | 0 | 129.6382 | 0 | 100% | 4.1869 | 0 | 90% | 0 | 43.1701
4022 | 930 | 963 | 93 | 3.6 | 30.3 | 0 | 283.5312 | 45.5651 | 21.5441 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.1338
4023 | 924 | 867 | 84 | 4.9 | 30.7 | 0 | 273.1773 | 44.5718 | 12.4204 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.6551
4024 | 896 | 721 | 76 | 5.2 | 30.2 | 40.8552 | 218.9279 | 36.9387 | 4.909 | 42.5733 | 5.4311 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2459
4025 | 832 | 534 | 69 | 3.7 | 29.9 | 41.9118 | 180.2403 | 23.41 | 0 | 42.572 | 14.3306 | 0 | 0 | 100% | 0 | 4.3387 | 83.06% | 0 | 42.6153
4026 | 709 | 328 | 60 | 3 | 29.4 | 42.1614 | 116.707 | 5.9661 | 0 | 42.5703 | 14.3745 | 0 | 0 | 100% | 0 | 21.6331 | 48.45% | 0 | 42.6831
4027 | 470 | 131 | 39 | 1.6 | 27.6 | 45.5331 | 21.5631 | 0 | 0 | 47.6973 | 16.6612 | 0 | 2.0599 | 100% | 0 | 24.0282 | 10% | 0 | 41.3272
4028 | 36 | 9 | 6 | 1.6 | 24.7 | 0 | 0.018938 | 0 | 0 | 101.1051 | 39.8496 | 0 | 103.2483 | 92% | 0 | 0 | 10% | 0 | 38.0351
4029 | 0 | 0 | 0 | 2.4 | 22 | 0 | 0 | 0 | 0 | 97.5609 | 38.6381 | 0 | 97.1977 | 85% | 0 | 0 | 10% | 0 | 36.3883
4030 | 0 | 0 | 0 | 0.8 | 20.5 | 0 | 0 | 0 | 0 | 92.9936 | 36.8605 | 0 | 91.5281 | 78% | 0 | 0 | 10% | 0 | 34.6804
4031 | 0 | 0 | 0 | 1 | 19.4 | 0 | 0 | 0 | 0 | 89.4321 | 35.4421 | 0 | 87.2991 | 71% | 0 | 0 | 10% | 0 | 33.2271
4032 | 0 | 0 | 0 | 1.7 | 17.9 | 0 | 0 | 0 | 0 | 88.1813 | 35.024 | 0 | 86.0078 | 65% | 0 | 0 | 10% | 0 | 32.7412
4033 | 0 | 0 | 0 | 1 | 18.2 | 0 | 0 | 0 | 0 | 88.0354 | 34.9418 | 0 | 86.006 | 59% | 0 | 0 | 10% | 0 | 32.6021
4034 | 0 | 0 | 0 | 0.8 | 17.6 | 0 | 0 | 0 | 0 | 89.279 | 35.5074 | 0 | 87.6299 | 52% | 0 | 0 | 10% | 0 | 33.1249
4035 | 0 | 0 | 0 | 0.7 | 16.5 | 0 | 0 | 0 | 0 | 94.1407 | 37.6426 | 0 | 93.673 | 45% | 0 | 0 | 10% | 0 | 35.2324
4036 | 0 | 0 | 0 | 0.4 | 15.5 | 0 | 0 | 0 | 0 | 101.4126 | 40.758 | 0 | 102.2169 | 37% | 0 | 0 | 10% | 0 | 38.3575
4037 | 0 | 1 | 1 | 0.6 | 16.2 | 0 | 0 | 0 | 0 | 108.5841 | 43.7049 | 0 | 110.5669 | 29% | 0 | 0 | 10% | 0 | 41.3465
4038 | 341 | 75 | 27 | 0.4 | 17.8 | 0 | 53.0124 | 0 | 0 | 113.5764 | 45.6494 | 0 | 116.1633 | 20% | 0 | 0 | 10% | 0 | 43.3576
4039 | 681 | 262 | 50 | 0.9 | 22 | 99.5582 | 24.3653 | 1.4111 | 0 | 112.514 | 44.839 | 3.0433 | 21.121 | 19% | 0 | 0 | 10% | 0 | 44.5154
4040 | 825 | 469 | 62 | 2 | 23.9 | 186.0079 | 0 | 17.6141 | 0 | 76.7297 | 29.5568 | 110.859 | 0 | 27% | 0 | 0 | 10% | 0 | 45.0033
4041 | 880 | 657 | 75 | 3.2 | 23.7 | 220.9312 | -2.98e-14 | 36.542 | 0 | 45.4019 | 16.014 | 176.8441 | 0 | 41% | 4.2746 | 0 | 15.81% | 0 | 45.8302
4042 | 909 | 817 | 86 | 2.6 | 25.7 | 241.9521 | 0 | 52.9411 | 0 | 46.235 | 16.1908 | 197.1031 | 0 | 55% | 20.4428 | 0 | 43.62% | 0 | 46.0254
4043 | 922 | 932 | 95 | 3 | 27.4 | 254.6984 | 0 | 58.1737 | 6.5329 | 42.5908 | 14.5579 | 213.2936 | 0 | 71% | 25 | 0 | 77.62% | 0 | 44.9325
4044 | 916 | 992 | 105 | 3.4 | 28.9 | 258.6405 | 0 | 41.5696 | 28.9336 | 42.5971 | 14.428 | 217.0509 | 0 | 87% | 9.1061 | 0 | 90% | 0 | 44.0303
4045 | 916 | 1001 | 106 | 3 | 30.4 | 211.8826 | 54.898 | 29.0003 | 42.0922 | 42.5997 | 14.2949 | 170.1456 | 0 | 100% | 0 | 0 | 90% | 0 | 43.917
4046 | 899 | 949 | 109 | 6.4 | 31.1 | 42.1515 | 237.8453 | 28.866 | 37.0457 | 42.6003 | 14.2317 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.8067
4047 | 870 | 845 | 107 | 6.2 | 30 | 42.1571 | 220.3872 | 28.3389 | 27.1347 | 42.5978 | 14.3304 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.3786
4048 | 828 | 697 | 100 | 6 | 29.6 | 42.1572 | 196.8275 | 27.7332 | 12.6599 | 42.5954 | 14.3652 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.8077
4049 | 769 | 517 | 86 | 4.5 | 29.4 | 42.1572 | 162.1403 | 22.7061 | 0 | 42.5931 | 14.3822 | 0 | 0 | 100% | 0 | 5.0427 | 81.93% | 0 | 42.8404
4050 | 680 | 323 | 66 | 3.9 | 29 | 42.1572 | 109.4705 | 6.0279 | 0 | 42.5908 | 14.417 | 0 | 0 | 100% | 0 | 21.6265 | 47.33% | 0 | 42.7809
4051 | 455 | 130 | 39 | 4.5 | 27 | 46.0387 | 15.5508 | 0 | 0 | 49.8146 | 17.6117 | 0 | 3.8395 | 100% | 0 | 23.3308 | 10% | 0 | 41.5336
4052 | 26 | 8 | 6 | 3.3 | 21.7 | 0 | 0.045036 | 0 | 0 | 100.6264 | 39.9398 | 0 | 102.5491 | 92% | 0 | 0 | 10% | 0 | 38.1547
4053 | 0 | 0 | 0 | 1.9 | 19.1 | 0 | 0 | 0 | 0 | 97.7576 | 38.9562 | 0 | 97.4473 | 85% | 0 | 0 | 10% | 0 | 36.6988
4054 | 0 | 0 | 0 | 0.8 | 18.3 | 0 | 0 | 0 | 0 | 92.8054 | 36.9454 | 0 | 91.291 | 78% | 0 | 0 | 10% | 0 | 34.7637
4055 | 0 | 0 | 0 | 0.5 | 17.8 | 0 | 0 | 0 | 0 | 90.0643 | 35.8229 | 0 | 88.0707 | 71% | 0 | 0 | 10% | 0 | 33.6021
4056 | 0 | 0 | 0 | 0.3 | 17.2 | 0 | 0 | 0 | 0 | 88.8209 | 35.3404 | 0 | 86.7554 | 65% | 0 | 0 | 10% | 0 | 33.0606
4057 | 0 | 0 | 0 | 0.8 | 16.3 | 0 | 0 | 0 | 0 | 88.2306 | 35.1524 | 0 | 86.2023 | 58% | 0 | 0 | 10% | 0 | 32.8215
4058 | 0 | 0 | 0 | 0.5 | 15.6 | 0 | 0 | 0 | 0 | 89.5198 | 35.7434 | 0 | 87.8833 | 52% | 0 | 0 | 10% | 0 | 33.3693
4059 | 0 | 0 | 0 | 0.9 | 15.1 | 0 | 0 | 0 | 0 | 94.8562 | 38.0374 | 0 | 94.47 | 45% | 0 | 0 | 10% | 0 | 35.6352
4060 | 0 | 0 | 0 | 1.2 | 15.4 | 0 | 0 | 0 | 0 | 102.7859 | 41.3423 | 0 | 103.8237 | 37% | 0 | 0 | 10% | 0 | 38.9512
4061 | 0 | 1 | 1 | 1.2 | 15.4 | 0 | 0 | 0 | 0 | 109.3693 | 44.0929 | 0 | 111.4123 | 28% | 0 | 0 | 10% | 0 | 41.7506
4062 | 253 | 70 | 33 | 1.5 | 19.1 | 0 | 39.2863 | 0 | 0 | 114.927 | 46.0973 | 0 | 117.694 | 20% | 0 | 0 | 10% | 0 | 43.8213
4063 | 626 | 259 | 64 | 0.9 | 22.9 | 90.3352 | 22.0939 | 1.6226 | 0 | 112.6646 | 44.8127 | 0 | 27.0472 | 18% | 0 | 0 | 10% | 0 | 44.7852
4064 | 741 | 458 | 91 | 0.8 | 25.4 | 165.8192 | 0 | 17.38 | 0 | 78.1284 | 30.0347 | 89.4678 | 0 | 24% | 0 | 0 | 10% | 0 | 45.4275
4065 | 873 | 669 | 90 | 1.8 | 27.8 | 219.6857 | 0 | 36.8865 | 0 | 46.1158 | 15.9552 | 174.8296 | 0 | 38% | 4.1113 | 0 | 15.59% | 0 | 46.2943
4066 | 927 | 835 | 89 | 3.2 | 28.9 | 246.8655 | 0 | 53.7019 | 0 | 47.0665 | 16.2422 | 201.2379 | 0 | 53% | 20.8435 | 0 | 43.94% | 0 | 46.3947
4067 | 958 | 958 | 89 | 3.7 | 30.1 | 264.7769 | 0 | 58.7445 | 7.4689 | 42.5944 | 14.3202 | 223.404 | 0 | 69% | 25 | 0 | 77.94% | 0 | 45.1749
4068 | 917 | 1051 | 164 | 4.5 | 31.2 | 258.0025 | 0 | 41.8245 | 32.7406 | 42.6003 | 14.2225 | 216.4979 | 0 | 86% | 8.8687 | 0 | 90% | 0 | 44.3238
4069 | 962 | 1041 | 103 | 5.2 | 32.1 | 237.9102 | 38.8737 | 29.1732 | 44.9012 | 42.6023 | 14.1401 | 196.1631 | 0 | 100% | 0 | 0 | 90% | 0 | 44.2152
4070 | 942 | 983 | 101 | 6 | 32.5 | 42.1513 | 251.806 | 29.3209 | 38.8749 | 42.6031 | 14.103 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.1325
4071 | 862 | 899 | 161 | 5.9 | 33.2 | 42.1568 | 217.9725 | 28.8985 | 29.6649 | 42.6006 | 14.0363 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.6433
4072 | 272 | 527 | 318 | 5.8 | 32.4 | 0 | 68.0041 | 28.0547 | 0 | 50.5061 | 17.3279 | 0 | 48.9722 | 96% | 0 | 0 | 90% | 0 | 43.2877
4073 | 353 | 440 | 246 | 4.8 | 31.9 | 71.774 | 0 | 19.8115 | 0 | 42.5949 | 14.1562 | 28.2454 | 0 | 98% | 0 | 8.3422 | 76.65% | 0 | 43.0299
4074 | 627 | 355 | 117 | 3.9 | 31.7 | 62.5912 | 71.4207 | 8.3874 | 0 | 42.5931 | 14.1741 | 20.689 | 0 | 100% | 0 | 19.5275 | 45.41% | 0 | 42.7243
4075 | 416 | 143 | 64 | 2.8 | 30.5 | 0 | 61.4541 | 0 | 0 | 59.7226 | 21.429 | 0 | 59.0513 | 96% | 0 | 22.1304 | 10% | 0 | 41.4627
4076 | 41 | 15 | 12 | 2.8 | 25.2 | 0 | 0.11624 | 0 | 0 | 103.9572 | 40.9808 | 0 | 106.9515 | 88% | 0 | 0 | 10% | 0 | 38.1958
4077 | 0 | 0 | 0 | 1.8 | 22.2 | 0 | 0 | 0 | 0 | 99.1136 | 39.264 | 0 | 99.0219 | 80% | 0 | 0 | 10% | 0 | 37.0107
4078 | 0 | 0 | 0 | 0.5 | 21.4 | 0 | 0 | 0 | 0 | 93.9732 | 37.2001 | 0 | 92.6937 | 73% | 0 | 0 | 10% | 0 | 35.026
4079 | 0 | 0 | 0 | 0.5 | 20.7 | 0 | 0 | 0 | 0 | 90.7011 | 35.876 | 0 | 88.7385 | 67% | 0 | 0 | 10% | 0 | 33.6829
4080 | 0 | 0 | 0 | 0 | 19.9 | 0 | 0 | 0 | 0 | 89.4773 | 35.4236 | 0 | 87.4217 | 60% | 0 | 0 | 10% | 0 | 33.1783
4081 | 0 | 0 | 0 | 0.5 | 19.6 | 0 | 0 | 0 | 0 | 89.083 | 35.2801 | 0 | 87.092 | 54% | 0 | 0 | 10% | 0 | 32.9872
4082 | 0 | 0 | 0 | 1.2 | 19.5 | 0 | 0 | 0 | 0 | 90.154 | 35.7385 | 0 | 88.5042 | 47% | 0 | 0 | 10% | 0 | 33.406
4083 | 0 | 0 | 0 | 0.8 | 19.3 | 0 | 0 | 0 | 0 | 94.5136 | 37.5928 | 0 | 93.9118 | 40% | 0 | 0 | 10% | 0 | 35.2326
4084 | 0 | 0 | 0 | 0.8 | 19.3 | 0 | 0 | 0 | 0 | 102.0885 | 40.7515 | 0 | 102.8453 | 32% | 0 | 0 | 10% | 0 | 38.3925
4085 | 0 | 1 | 1 | 1.2 | 20.9 | 0 | 0 | 0 | 0 | 108.3551 | 43.2221 | 0 | 110.1241 | 24% | 0 | 0 | 10% | 0 | 40.8994
4086 | 241 | 83 | 48 | 1.5 | 22.4 | 0 | 37.3746 | 0 | 0 | 113.4499 | 45.1851 | 0 | 115.8794 | 15% | 0 | 0 | 10% | 0 | 42.9173
4087 | 610 | 255 | 65 | 1 | 24.5 | 87.663 | 21.286 | 1.5465 | 0 | 111.4962 | 44.1645 | 0 | 28.2843 | 13% | 0 | 0 | 10% | 0 | 44.0871
4088 | 779 | 459 | 74 | 0.8 | 26.5 | 175.1123 | 0 | 17.0339 | 0 | 78.1339 | 29.9221 | 98.5692 | 0 | 20% | 0 | 0 | 10% | 0 | 44.8912
4089 | 858 | 653 | 84 | 1.5 | 28.4 | 215.7165 | 0 | 35.5786 | 0 | 46.2055 | 15.9358 | 170.9058 | 0 | 33% | 3.5307 | 0 | 14.8% | 0 | 45.5899
4090 | 902 | 817 | 92 | 2.1 | 29.9 | 240.1197 | 0 | 52.1758 | 0 | 47.1781 | 16.1922 | 194.4393 | 0 | 48% | 19.9573 | 0 | 41.94% | 0 | 45.775
4091 | 925 | 934 | 93 | 2 | 31.3 | 256.0123 | 0 | 58.0965 | 5.7647 | 42.5989 | 14.2128 | 214.6891 | 0 | 64% | 25 | 0 | 75.94% | 0 | 44.5105
4092 | 939 | 1004 | 94 | 3.3 | 32.1 | 265.6159 | 0 | 42.6388 | 27.9936 | 42.6038 | 14.1406 | 224.1451 | 0 | 81% | 10.3356 | 0 | 90% | 0 | 43.5255
4093 | 970 | 1031 | 85 | 5.3 | 32.8 | 273.9676 | 0 | 29.9107 | 43.1702 | 42.6053 | 14.0756 | 232.2899 | 0 | 98% | 0 | 0 | 90% | 0 | 43.2291
4094 | 975 | 988 | 77 | 6.3 | 32.8 | 69.8812 | 230.5123 | 28.504 | 40.1324 | 42.6066 | 14.076 | 28.4345 | 0 | 100% | 0 | 0 | 90% | 0 | 43.0977
4095 | 967 | 890 | 70 | 6.1 | 32.9 | 42.1513 | 250.9854 | 27.7049 | 30.6174 | 42.6043 | 14.0659 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4794
4096 | 945 | 745 | 64 | 6.5 | 32.9 | 42.1569 | 232.2469 | 27.4471 | 15.6934 | 42.6017 | 14.0651 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.2207
4097 | 871 | 550 | 62 | 6 | 31.8 | 42.157 | 190.7653 | 24.1605 | 0 | 42.5992 | 14.1669 | 0 | 0 | 100% | 0 | 3.0542 | 85.11% | 0 | 42.0904
4098 | 734 | 336 | 56 | 4.2 | 31.5 | 42.157 | 123.0322 | 6.1007 | 0 | 42.5968 | 14.1937 | 0 | 0 | 100% | 0 | 21.048 | 51.44% | 0 | 42.0513
4099 | 455 | 130 | 39 | 3 | 30.6 | 44.6999 | 19.0969 | 0 | 0 | 45.0976 | 15.277 | 0 | 0 | 100% | 0 | 25 | 11.44% | 0 | 40.9823
4100 | 31 | 9 | 6 | 2.1 | 28.2 | 0 | 0.1188 | 0 | 0 | 101.9511 | 39.7878 | 0 | 104.4229 | 92% | 0 | 0 | 11.44% | 0 | 37.9282
4101 | 0 | 0 | 0 | 3 | 24.6 | 0 | 0 | 0 | 0 | 99.1246 | 39.0347 | 0 | 98.9978 | 85% | 0 | 0 | 11.44% | 0 | 36.7946
4102 | 0 | 0 | 0 | 2.3 | 21.9 | 0 | 0 | 0 | 0 | 93.7858 | 37.0782 | 0 | 92.379 | 78% | 0 | 0 | 11.44% | 0 | 34.9303
4103 | 0 | 0 | 0 | 3 | 20.9 | 0 | 0 | 0 | 0 | 90.2993 | 35.6908 | 0 | 88.2197 | 71% | 0 | 0 | 11.44% | 0 | 33.5099
4104 | 0 | 0 | 0 | 3.8 | 20.2 | 0 | 0 | 0 | 0 | 88.9824 | 35.1922 | 0 | 86.8405 | 65% | 0 | 0 | 11.44% | 0 | 32.9452
4105 | 0 | 0 | 0 | 3.1 | 20.4 | 0 | 0 | 0 | 0 | 88.742 | 35.0759 | 0 | 86.7259 | 58% | 0 | 0 | 11.44% | 0 | 32.7721
4106 | 0 | 0 | 0 | 2.2 | 18.9 | 0 | 0 | 0 | 0 | 89.8442 | 35.6517 | 0 | 88.1856 | 52% | 0 | 0 | 11.44% | 0 | 33.3044
4107 | 0 | 0 | 0 | 1.6 | 18 | 0 | 0 | 0 | 0 | 94.6411 | 37.7427 | 0 | 94.127 | 45% | 0 | 0 | 11.44% | 0 | 35.3661
4108 | 0 | 0 | 0 | 1.2 | 17.8 | 0 | 0 | 0 | 0 | 102.2968 | 40.9557 | 0 | 103.1498 | 37% | 0 | 0 | 11.44% | 0 | 38.5854
4109 | 0 | 1 | 1 | 1.1 | 18.3 | 0 | 0 | 0 | 0 | 108.4462 | 43.4785 | 0 | 110.2601 | 28% | 0 | 0 | 11.44% | 0 | 41.1518
4110 | 57 | 41 | 32 | 0.9 | 18.9 | 0 | 8.8271 | 0 | 0 | 113.2626 | 45.424 | 0 | 115.6596 | 20% | 0 | 0 | 11.44% | 0 | 43.1584
4111 | 524 | 234 | 63 | 2 | 21.3 | 72.8378 | 18.0682 | 1.0522 | 0 | 112.0816 | 44.7241 | 0 | 43.296 | 16% | 0 | 0 | 11.44% | 0 | 44.2796
4112 | 763 | 453 | 74 | 1.1 | 24.1 | 170.9527 | 2.98e-14 | 16.7157 | 0 | 78.5105 | 30.3342 | 93.7788 | 0 | 24% | 0 | 0 | 11.44% | 0 | 45.0208
4113 | 847 | 646 | 82 | 2.4 | 25.8 | 212.2332 | -2.98e-14 | 35.1677 | 0 | 45.624 | 15.931 | 167.9406 | 0 | 36% | 3.18 | 0 | 15.76% | 0 | 45.5519
4114 | 881 | 809 | 97 | 2.9 | 27.3 | 233.6298 | 0 | 51.6981 | 0 | 46.4025 | 16.1175 | 188.68 | 0 | 50% | 19.6387 | 0 | 42.47% | 0 | 45.5961
4115 | 769 | 865 | 158 | 3.5 | 27.8 | 208.9787 | 0 | 57.1036 | 1.2258 | 42.5941 | 14.5244 | 167.8287 | 0 | 63% | 25 | 0 | 76.47% | 0 | 44.2605
4116 | 586 | 788 | 210 | 5.2 | 28.3 | 157.3988 | 0 | 40.1081 | 13.5492 | 43.665 | 14.9125 | 115.0345 | 0 | 72% | 9.9487 | 0 | 90% | 0 | 43.1737
4117 | 878 | 995 | 131 | 4.9 | 29 | 246.9277 | 0 | 31.1021 | 39.2787 | 42.5982 | 14.4195 | 204.717 | 0 | 87% | 0 | 0 | 90% | 0 | 42.7874
4118 | 852 | 943 | 140 | 4.8 | 29.6 | 221.8553 | 15.1782 | 26.4427 | 38.7614 | 42.6007 | 14.367 | 179.9619 | 0 | 100% | 0 | 0 | 90% | 0 | 42.7084
4119 | 821 | 841 | 138 | 4.8 | 29.5 | 42.1518 | 205.3237 | 27.0366 | 27.8432 | 42.6016 | 14.3762 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.1221
4120 | 757 | 655 | 136 | 4.6 | 29.2 | 42.1572 | 175.7223 | 26.798 | 12.8167 | 42.5991 | 14.402 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.9094
4121 | 698 | 509 | 114 | 5.4 | 28.4 | 42.1573 | 142.0625 | 22.6076 | 0 | 42.5966 | 14.4723 | 0 | 0 | 100% | 0 | 3.6762 | 84.12% | 0 | 41.4657
4122 | 582 | 312 | 88 | 5.3 | 27.1 | 42.1574 | 84.8796 | 6.2143 | 0 | 42.5942 | 14.5851 | 0 | 0 | 100% | 0 | 19.4723 | 52.96% | 0 | 40.9815
4123 | 327 | 119 | 52 | 4.7 | 25.6 | 0 | 45.5781 | 0 | 0 | 48.2202 | 17.0354 | 0 | 46.6904 | 97% | 0 | 25 | 12.96% | 0 | 39.9517
4124 | 3 | 5 | 5 | 3.8 | 23.8 | 0 | 0.014163 | 0 | 0 | 102.1333 | 40.3683 | 0 | 105.4048 | 89% | 0 | 0 | 12.96% | 0 | 37.4036
4125 | 0 | 0 | 0 | 3.1 | 22.5 | 0 | 0 | 0 | 0 | 97.9733 | 38.7627 | 0 | 98.0012 | 82% | 0 | 0 | 12.96% | 0 | 36.4216
4126 | 0 | 0 | 0 | 2.7 | 20.9 | 0 | 0 | 0 | 0 | 93.0728 | 36.8608 | 0 | 91.8148 | 75% | 0 | 0 | 12.96% | 0 | 34.6205
4127 | 0 | 0 | 0 | 2.9 | 19.8 | 0 | 0 | 0 | 0 | 89.4297 | 35.4106 | 0 | 87.4074 | 68% | 0 | 0 | 12.96% | 0 | 33.1569
4128 | 0 | 0 | 0 | 3.6 | 18.9 | 0 | 0 | 0 | 0 | 87.2225 | 34.5497 | 0 | 84.9252 | 62% | 0 | 0 | 12.96% | 0 | 32.2433
4129 | 0 | 0 | 0 | 3.5 | 18.6 | 0 | 0 | 0 | 0 | 86.193 | 34.1396 | 0 | 83.8718 | 55% | 0 | 0 | 12.96% | 0 | 31.7769
4130 | 0 | 0 | 0 | 3.2 | 18.2 | 0 | 0 | 0 | 0 | 85.6035 | 33.9209 | 0 | 83.3172 | 49% | 0 | 0 | 12.96% | 0 | 31.5096
4131 | 0 | 0 | 0 | 3.1 | 17.7 | 0 | 0 | 0 | 0 | 85.352 | 33.8498 | 0 | 83.1384 | 43% | 0 | 0 | 12.96% | 0 | 31.3974
4132 | 0 | 0 | 0 | 1.8 | 17 | 0 | 0 | 0 | 0 | 87.0901 | 34.6267 | 0 | 85.309 | 37% | 0 | 0 | 12.96% | 0 | 32.1378
4133 | 0 | 1 | 1 | 1.6 | 16.7 | 0 | 0 | 0 | 0 | 92.9779 | 37.1352 | 0 | 92.5627 | 30% | 0 | 0 | 12.96% | 0 | 34.6195
4134 | 214 | 64 | 33 | 1.3 | 18 | 0 | 33.0887 | 0 | 0 | 100.2605 | 40.0885 | 0 | 101.1995 | 22% | 0 | 0 | 12.96% | 0 | 37.5804
4135 | 521 | 238 | 74 | 1.3 | 20.6 | 72.5646 | 17.9724 | 1.5776 | 0 | 100.2207 | 39.8674 | 0 | 30.6003 | 20% | 0 | 0 | 12.96% | 0 | 39.9257
4136 | 698 | 442 | 94 | 2.9 | 22.9 | 154.0016 | 0 | 16.3796 | 0 | 69.2717 | 26.3579 | 85.3757 | 0 | 26% | 0 | 0 | 12.96% | 0 | 40.8876
4137 | 788 | 632 | 105 | 4.5 | 24.8 | 194.965 | 0 | 34.352 | 0 | 45.3125 | 15.8881 | 150.4595 | 0 | 37% | 7.0207 | 0 | 22.51% | 0 | 41.0271
4138 | 842 | 794 | 111 | 5.8 | 25.8 | 220.1267 | 0 | 50.6316 | 0 | 46.1156 | 16.1333 | 174.9284 | 0 | 50% | 22.9 | 0 | 53.65% | 0 | 41.4296
4139 | 867 | 910 | 116 | 5.4 | 27 | 236.3603 | 0 | 53.621 | 8.7422 | 42.5858 | 14.5909 | 194.5744 | 0 | 65% | 25 | 0 | 87.66% | 0 | 40.6147
4140 | 881 | 978 | 119 | 5.2 | 27.7 | 246.5658 | 0 | 28.834 | 40.2524 | 42.5926 | 14.5325 | 204.7265 | 0 | 80% | 1.7246 | 0 | 90% | 0 | 38.9288
4141 | 890 | 991 | 115 | 5.7 | 28.5 | 249.9886 | 0 | 23.9049 | 46.2986 | 42.5963 | 14.4633 | 207.9254 | 0 | 95% | 0 | 0 | 90% | 0 | 37.9597
4142 | 891 | 948 | 108 | 6 | 29.2 | 106.2858 | 161.3013 | 22.9283 | 42.8053 | 42.5991 | 14.402 | 64.6436 | 0 | 100% | 0 | 0 | 90% | 0 | 37.8847
4143 | 874 | 850 | 102 | 6.5 | 29 | 42.1518 | 221.7442 | 22.4862 | 33.1836 | 42.5976 | 14.4193 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.615
4144 | 825 | 701 | 100 | 6.8 | 28.5 | 42.1573 | 195.9046 | 22.4938 | 18.0894 | 42.5952 | 14.4629 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.6663
4145 | 749 | 520 | 94 | 7.4 | 27.3 | 42.1574 | 156.1417 | 22.6114 | 0.39872 | 42.5928 | 14.5673 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.8886
4146 | 613 | 318 | 81 | 7 | 25.9 | 42.1575 | 92.1789 | 6.2217 | 0 | 42.5906 | 14.6854 | 0 | 0 | 100% | 0 | 16.956 | 62.87% | 0 | 38.5733
4147 | 345 | 123 | 52 | 5.8 | 24.1 | 0 | 48.8522 | 0 | 0 | 45.1853 | 15.8962 | 0 | 43.6699 | 97% | 0 | 24.7641 | 23.25% | 0 | 38.5824
4148 | 14 | 9 | 8 | 4.6 | 22 | 0 | 0.076984 | 0 | 0 | 79.3645 | 30.7986 | 0 | 80.4072 | 91% | 0 | 8.2798 | 10% | 0 | 36.1434
4149 | 0 | 0 | 0 | 3.8 | 20.5 | 0 | 0 | 0 | 0 | 92.3276 | 36.5776 | 0 | 91.9894 | 84% | 0 | 0 | 10% | 0 | 34.0258
4150 | 0 | 0 | 0 | 2.5 | 19.7 | 0 | 0 | 0 | 0 | 87.6649 | 34.6768 | 0 | 85.9531 | 78% | 0 | 0 | 10% | 0 | 32.2244
4151 | 0 | 0 | 0 | 1.3 | 19.6 | 0 | 0 | 0 | 0 | 83.939 | 33.1264 | 0 | 81.6185 | 72% | 0 | 0 | 10% | 0 | 30.6427
4152 | 0 | 0 | 0 | 1.3 | 19.6 | 0 | 0 | 0 | 0 | 82.0109 | 32.2831 | 0 | 79.7003 | 66% | 0 | 0 | 10% | 0 | 29.7378
4153 | 0 | 0 | 0 | 1.5 | 19.8 | 0 | 0 | 0 | 0 | 81.067 | 31.8401 | 0 | 78.8841 | 60% | 0 | 0 | 10% | 0 | 29.2452
4154 | 0 | 0 | 0 | 1.4 | 19.1 | 0 | 0 | 0 | 0 | 80.6149 | 31.6854 | 0 | 78.5235 | 54% | 0 | 0 | 10% | 0 | 29.0543
4155 | 0 | 0 | 0 | 1.5 | 18.6 | 0 | 0 | 0 | 0 | 80.0385 | 31.4589 | 0 | 78.0107 | 48% | 0 | 0 | 10% | 0 | 28.8005
4156 | 0 | 0 | 0 | 1.7 | 18.3 | 0 | 0 | 0 | 0 | 79.8002 | 31.3719 | 0 | 77.8238 | 42% | 0 | 0 | 10% | 0 | 28.6917
4157 | 0 | 1 | 1 | 1.5 | 18.3 | 0 | 0 | 0 | 0 | 83.8751 | 33.1924 | 0 | 82.161 | 36% | 0 | 0 | 10% | 0 | 30.4891
4158 | 249 | 68 | 33 | 0.8 | 17.8 | 0 | 38.4358 | 0 | 0 | 89.5025 | 35.5883 | 0 | 88.9751 | 30% | 0 | 0 | 10% | 0 | 32.8675
4159 | 569 | 247 | 69 | 0.6 | 20.6 | 80.6899 | 19.859 | 1.5105 | 0 | 88.8073 | 35.0911 | 6.8637 | 16.6578 | 29% | 0 | 0 | 10% | 0 | 34.9913
4160 | 732 | 451 | 86 | 1.3 | 23.2 | 163.2101 | 0 | 16.732 | 0 | 57.8767 | 21.3853 | 105.4658 | 0 | 37% | 0 | 0 | 10% | 0 | 36.2078
4161 | 822 | 646 | 95 | 4 | 26 | 204.5708 | 0 | 34.948 | 0 | 46.0707 | 16.0991 | 158.8387 | 0 | 49% | 11.9287 | 0 | 26.22% | 0 | 36.8429
4162 | 857 | 806 | 109 | 5.8 | 27.2 | 224.5279 | 0 | 50.592 | 0.54451 | 42.5683 | 14.5676 | 182.3472 | 0 | 62% | 25 | 0 | 60.22% | 0 | 37.6914
4163 | 890 | 927 | 111 | 6 | 28.6 | 242.8541 | 0 | 47.9547 | 15.3379 | 42.5796 | 14.4487 | 200.5929 | 0 | 77% | 21.8948 | 0 | 90% | 0 | 37.852
4164 | 905 | 995 | 112 | 6.4 | 29.6 | 252.8769 | 0 | 22.0629 | 47.9235 | 42.5857 | 14.3619 | 210.5341 | 0 | 92% | 0 | 0 | 90% | 0 | 36.5847
4165 | 901 | 1006 | 118 | 6.1 | 30.4 | 150.1158 | 118.7905 | 20.601 | 50.2915 | 42.5912 | 14.2921 | 108.2675 | 0 | 100% | 0 | 0 | 90% | 0 | 35.8171
4166 | 872 | 955 | 132 | 6 | 30.9 | 42.1516 | 229.2739 | 20.6803 | 45.1867 | 42.5909 | 14.2468 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.6362
4167 | 822 | 848 | 142 | 6.3 | 30.4 | 42.1571 | 205.4208 | 20.5268 | 34.6474 | 42.5887 | 14.2912 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.5271
4168 | 776 | 703 | 136 | 6.4 | 30.1 | 42.1571 | 181.1883 | 20.8518 | 19.7924 | 42.5866 | 14.3176 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.8786
4169 | 668 | 518 | 136 | 6.4 | 29.5 | 42.1572 | 133.3803 | 21.3434 | 1.9073 | 42.5845 | 14.3704 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.4232
4170 | 473 | 309 | 123 | 6.7 | 27.9 | 42.1573 | 56.2404 | 6.8153 | 0 | 42.5825 | 14.5117 | 0 | 0 | 100% | 0 | 15.2142 | 65.66% | 0 | 37.2509
4171 | 219 | 119 | 72 | 6.3 | 25.1 | 0 | 39.3322 | 0 | 0 | 44.4208 | 15.4985 | 0 | 42.911 | 97% | 0 | 24.5693 | 26.35% | 0 | 38.0009
4172 | 2 | 6 | 5 | 4.6 | 22.5 | 0 | 0.012327 | 0 | 0 | 74.7881 | 28.79 | 0 | 75.4926 | 91% | 0 | 10.2166 | 10% | 0 | 36.0767
4173 | 0 | 0 | 0 | 4 | 21 | 0 | 0 | 0 | 0 | 92.8715 | 36.7682 | 0 | 92.7953 | 84% | 0 | 0 | 10% | 0 | 34.1807
4174 | 0 | 0 | 0 | 2 | 19.5 | 0 | 0 | 0 | 0 | 87.9499 | 34.8113 | 0 | 86.3156 | 78% | 0 | 0 | 10% | 0 | 32.354
4175 | 0 | 0 | 0 | 1.1 | 19.3 | 0 | 0 | 0 | 0 | 84.9129 | 33.5547 | 0 | 82.7686 | 72% | 0 | 0 | 10% | 0 | 31.0709
4176 | 0 | 0 | 0 | 1.4 | 19.5 | 0 | 0 | 0 | 0 | 83.0898 | 32.7804 | 0 | 80.7732 | 66% | 0 | 0 | 10% | 0 | 30.2451
4177 | 0 | 0 | 0 | 1.3 | 18.8 | 0 | 0 | 0 | 0 | 82.3524 | 32.4967 | 0 | 80.1578 | 60% | 0 | 0 | 10% | 0 | 29.9104
4178 | 0 | 0 | 0 | 1 | 17.5 | 0 | 0 | 0 | 0 | 83.2369 | 32.9787 | 0 | 81.1984 | 54% | 0 | 0 | 10% | 0 | 30.3535
4179 | 0 | 0 | 0 | 0.2 | 17.1 | 0 | 0 | 0 | 0 | 87.1616 | 34.6501 | 0 | 85.9536 | 47% | 0 | 0 | 10% | 0 | 31.9936
4180 | 0 | 0 | 0 | 0.9 | 16.6 | 0 | 0 | 0 | 0 | 92.3715 | 36.8848 | 0 | 92.3273 | 41% | 0 | 0 | 10% | 0 | 34.2263
4181 | 0 | 1 | 1 | 1.1 | 16.8 | 0 | 0 | 0 | 0 | 97.4048 | 38.9835 | 0 | 98.2613 | 33% | 0 | 0 | 10% | 0 | 36.3572
4182 | 123 | 56 | 37 | 1.4 | 18.5 | 0 | 18.9521 | 0 | 0 | 103.7164 | 41.4986 | 0 | 105.6658 | 25% | 0 | 0 | 10% | 0 | 38.9207
4183 | 473 | 237 | 87 | 1.1 | 21.4 | 64.3409 | 16.0065 | 1.7045 | 0 | 100.9972 | 40.1235 | 0 | 39.6523 | 22% | 0 | 0 | 10% | 0 | 40.3744
4184 | 656 | 442 | 112 | 3.2 | 23.9 | 143.4639 | 0 | 16.4715 | 0 | 69.7461 | 26.4814 | 74.2034 | 0 | 28% | 0 | 0 | 10% | 0 | 41.1966
4185 | 766 | 633 | 125 | 3 | 25.3 | 190.0335 | 0 | 34.721 | 0 | 45.2269 | 15.8116 | 145.467 | 0 | 39% | 6.3755 | 0 | 18.67% | 0 | 42.0091
4186 | 828 | 800 | 133 | 2.5 | 26.8 | 218.6677 | -2.98e-14 | 51.2713 | 0 | 46.1887 | 16.0758 | 173.2862 | 0 | 52% | 22.339 | 0 | 49.05% | 0 | 42.586
4187 | 875 | 921 | 124 | 2.9 | 28.2 | 240.7433 | 0 | 55.2259 | 8.0741 | 42.5795 | 14.4843 | 198.8508 | 0 | 66% | 25 | 0 | 83.05% | 0 | 42.0728
4188 | 884 | 985 | 128 | 2.4 | 29.6 | 249.5502 | 0 | 34.3086 | 35.2815 | 42.5886 | 14.3629 | 207.6182 | 0 | 82% | 5.109 | 0 | 90% | 0 | 40.8191
4189 | 864 | 986 | 141 | 2.5 | 29.9 | 244.5351 | 0 | 25.6874 | 44.1701 | 42.5926 | 14.3376 | 202.4485 | 0 | 97% | 0 | 0 | 90% | 0 | 40.4302
4190 | 863 | 957 | 146 | 2.2 | 31 | 87.5094 | 175.0089 | 25.7823 | 40.4914 | 42.5958 | 14.2394 | 45.9418 | 0 | 100% | 0 | 0 | 90% | 0 | 40.5326
4191 | 789 | 832 | 156 | 2.3 | 31.1 | 42.1516 | 195.7626 | 25.418 | 28.5379 | 42.5941 | 14.2296 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.3566
4192 | 771 | 689 | 130 | 3.2 | 30.3 | 42.1571 | 180.3857 | 25.4387 | 14.5081 | 42.5918 | 14.3013 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.4491
4193 | 723 | 517 | 107 | 4.1 | 29.8 | 42.1571 | 149.7804 | 22.9611 | 0 | 42.5896 | 14.3455 | 0 | 0 | 100% | 0 | 2.5397 | 85.94% | 0 | 40.5555
4194 | 539 | 299 | 91 | 3.9 | 28.7 | 42.1572 | 74.8126 | 5.9516 | 0 | 42.5874 | 14.4425 | 0 | 0 | 100% | 0 | 19.6721 | 54.46% | 0 | 40.7757
4195 | 199 | 90 | 46 | 3.7 | 26.9 | 0 | 35.7748 | 0 | 0 | 49.9777 | 17.6581 | 0 | 48.4441 | 96% | 0 | 25 | 14.46% | 0 | 40.5842
4196 | 15 | 9 | 8 | 2.3 | 24.6 | 0 | 0.10069 | 0 | 0 | 96.753 | 37.9654 | 0 | 99.7199 | 89% | 0 | 2.7882 | 10% | 0 | 37.7947
4197 | 0 | 0 | 0 | 2.3 | 23 | 0 | 0 | 0 | 0 | 98.4045 | 38.8963 | 0 | 98.6166 | 82% | 0 | 0 | 10% | 0 | 36.5279
4198 | 0 | 0 | 0 | 1 | 22.4 | 0 | 0 | 0 | 0 | 93.0571 | 36.7265 | 0 | 91.8264 | 75% | 0 | 0 | 10% | 0 | 34.4786
4199 | 0 | 0 | 0 | 0.5 | 21.8 | 0 | 0 | 0 | 0 | 90.4287 | 35.6713 | 0 | 88.6398 | 68% | 0 | 0 | 10% | 0 | 33.4112
4200 | 0 | 0 | 0 | 0.3 | 21.2 | 0 | 0 | 0 | 0 | 88.8362 | 35.0523 | 0 | 86.8397 | 62% | 0 | 0 | 10% | 0 | 32.7515
4201 | 0 | 0 | 0 | 1.2 | 20.4 | 0 | 0 | 0 | 0 | 88.5356 | 34.9898 | 0 | 86.6101 | 55% | 0 | 0 | 10% | 0 | 32.6452
4202 | 0 | 0 | 0 | 1.4 | 19.8 | 0 | 0 | 0 | 0 | 90.046 | 35.6711 | 0 | 88.5417 | 49% | 0 | 0 | 10% | 0 | 33.29
4203 | 0 | 0 | 0 | 1.2 | 20 | 0 | 0 | 0 | 0 | 96.099 | 38.1987 | 0 | 95.9289 | 41% | 0 | 0 | 10% | 0 | 35.7941
4204 | 0 | 0 | 0 | 1 | 19.8 | 0 | 0 | 0 | 0 | 103.9171 | 41.4778 | 0 | 105.1782 | 33% | 0 | 0 | 10% | 0 | 39.0891
4205 | 0 | 1 | 1 | 0.6 | 18.9 | 0 | 0 | 0 | 0 | 110.4755 | 44.2693 | 0 | 112.688 | 25% | 0 | 0 | 10% | 0 | 41.9319
4206 | 188 | 62 | 35 | 0.6 | 20 | 0 | 28.9115 | 0 | 0 | 117.3997 | 47.0393 | 0 | 120.6242 | 16% | 0 | 0 | 10% | 0 | 44.7656
4207 | 506 | 233 | 76 | 1.8 | 22.5 | 69.5091 | 17.2231 | 1.5132 | 0 | 115.727 | 46.1165 | 0 | 50.8309 | 12% | 0 | 0 | 10% | 0 | 46.1573
4208 | 670 | 431 | 101 | 2.8 | 25.3 | 146.8568 | 0 | 15.9014 | 0 | 84.6578 | 32.934 | 63.603 | 0 | 17% | 0 | 0 | 10% | 0 | 47.0139
4209 | 767 | 623 | 115 | 2.1 | 27.1 | 190.5701 | 0 | 33.7599 | 0 | 47.1588 | 16.4501 | 144.8307 | 0 | 28% | 0 | 0 | 10% | 0 | 48.0458
4210 | 831 | 788 | 120 | 2.1 | 28.6 | 219.5669 | 0 | 50.0971 | 0 | 46.229 | 15.926 | 174.8155 | 0 | 41% | 15.3309 | 0 | 30.85% | 0 | 48.2528
4211 | 872 | 911 | 119 | 2 | 30.2 | 240.1386 | 0 | 60.8588 | 1.3908 | 42.5953 | 14.3115 | 198.8526 | 0 | 56% | 25 | 0 | 64.85% | 0 | 47.5286
4212 | 888 | 980 | 120 | 3.2 | 31.1 | 250.2626 | 0 | 53.9388 | 14.9957 | 42.6013 | 14.232 | 208.8769 | 0 | 72% | 18.4927 | 0 | 90% | 0 | 46.9169
4213 | 898 | 995 | 117 | 3.8 | 31 | 253.9635 | 0 | 35.5374 | 34.9237 | 42.6036 | 14.242 | 212.4577 | 0 | 87% | 0 | 0 | 90% | 0 | 46.9667
4214 | 889 | 949 | 115 | 4.8 | 31.5 | 214.1582 | 36.9758 | 31.7532 | 33.9832 | 42.6052 | 14.1965 | 172.3864 | 0 | 100% | 0 | 0 | 90% | 0 | 47.1084
4215 | 868 | 851 | 111 | 5.7 | 30.5 | 42.1516 | 220.1238 | 31.3931 | 24.4663 | 42.6053 | 14.2877 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 46.39
4216 | 835 | 706 | 102 | 5.1 | 30.5 | 42.1571 | 199.4102 | 30.9241 | 10.227 | 42.6027 | 14.2869 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.9201
4217 | 777 | 526 | 87 | 4.5 | 30.4 | 42.1571 | 165.0435 | 23.3421 | 0 | 42.6001 | 14.2951 | 0 | 0 | 100% | 0 | 7.0459 | 78.73% | 0 | 45.3922
4218 | 658 | 325 | 72 | 4.5 | 29.7 | 42.1572 | 104.685 | 6.2305 | 0 | 42.5976 | 14.3571 | 0 | 0 | 100% | 0 | 23.507 | 41.12% | 0 | 44.8039
4219 | 387 | 130 | 50 | 3.3 | 26.3 | 0 | 56.6264 | 0 | 0 | 70.2137 | 26.326 | 0 | 70.5871 | 95% | 0 | 19.4471 | 10% | 0 | 43.6753
4220 | 22 | 10 | 8 | 2.9 | 22.9 | 0 | 0.15718 | 0 | 0 | 109.003 | 43.301 | 0 | 112.2624 | 87% | 0 | 0 | 10% | 0 | 40.6992
4221 | 0 | 0 | 0 | 1.1 | 21.9 | 0 | 0 | 0 | 0 | 103.194 | 40.9923 | 0 | 103.2884 | 79% | 0 | 0 | 10% | 0 | 38.8934
4222 | 0 | 0 | 0 | 3 | 21.4 | 0 | 0 | 0 | 0 | 97.7671 | 38.7746 | 0 | 96.559 | 71% | 0 | 0 | 10% | 0 | 36.7518
4223 | 0 | 0 | 0 | 2.2 | 20.6 | 0 | 0 | 0 | 0 | 94.3622 | 37.4285 | 0 | 92.6821 | 64% | 0 | 0 | 10% | 0 | 35.3823
4224 | 0 | 0 | 0 | 1.9 | 21 | 0 | 0 | 0 | 0 | 92.6667 | 36.6816 | 0 | 90.7548 | 57% | 0 | 0 | 10% | 0 | 34.5926
4225 | 0 | 0 | 0 | 0.9 | 20 | 0 | 0 | 0 | 0 | 92.2026 | 36.5652 | 0 | 90.3333 | 51% | 0 | 0 | 10% | 0 | 34.4299
4226 | 0 | 0 | 0 | 1.3 | 19.4 | 0 | 0 | 0 | 0 | 93.1986 | 37.0314 | 0 | 91.6763 | 44% | 0 | 0 | 10% | 0 | 34.8564
4227 | 0 | 0 | 0 | 1.9 | 19 | 0 | 0 | 0 | 0 | 98.1756 | 39.1394 | 0 | 97.6181 | 36% | 0 | 0 | 10% | 0 | 36.935
4228 | 0 | 0 | 0 | 3.7 | 19.5 | 0 | 0 | 0 | 0 | 105.9946 | 42.3677 | 0 | 106.9161 | 28% | 0 | 0 | 10% | 0 | 40.1589
4229 | 0 | 0 | 0 | 2.9 | 19.8 | 0 | 0 | 0 | 0 | 113.5479 | 45.4637 | 0 | 115.6131 | 20% | 0 | 0 | 10% | 0 | 43.2856
4230 | 0 | 17 | 17 | 2.3 | 20.2 | 0 | 0 | 0 | 0 | 120.5692 | 48.3235 | 0 | 123.6961 | 10% | 0 | 0 | 10% | 0 | 46.195
4231 | 0 | 66 | 66 | 1.4 | 20.9 | 0 | 0 | 0 | 0 | 124.3187 | 49.7985 | 0 | 127.8369 | 0% | 0 | 0 | 10% | 0 | 47.7374
4232 | 0 | 154 | 152 | 2.8 | 22.1 | 0 | 0 | 3.1113 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 1.3071
4233 | 126 | 437 | 342 | 3.7 | 23.7 | 0 | 36.5329 | 21.2442 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 19.4532
4234 | 798 | 798 | 158 | 4.2 | 25.6 | 170.9898 | 41.0882 | 51.4672 | 0 | 0 | 0 | 164.6313 | 0 | 13% | 0 | 0 | 10% | 0 | 49.3168
4235 | 849 | 913 | 143 | 3.9 | 27.3 | 231.9303 | 0 | 63.0537 | 0 | 0 | 0 | 230.0922 | 0 | 31% | 12.1872 | 0 | 26.57% | 0 | 48.3502
4236 | 853 | 980 | 153 | 3.1 | 28.8 | 239.3595 | 0 | 69.2686 | 0 | 0 | 0 | 237.9624 | 0 | 49% | 19.2126 | 0 | 52.7% | 0 | 47.4273
4237 | 854 | 990 | 154 | 4 | 29.8 | 240.1198 | 0 | 70.1181 | 0 | 0 | 0 | 238.8609 | 0 | 67% | 20.0865 | 0 | 80.02% | 0 | 47.3509
4238 | 856 | 949 | 144 | 3.9 | 30.9 | 236.7144 | 0 | 58.0927 | 7.5977 | 0 | 0 | 235.5298 | 0 | 85% | 7.3372 | 0 | 90% | 0 | 48.0521
4239 | 500 | 667 | 239 | 4.4 | 30.7 | 125.9383 | 0 | 42.3525 | 0 | 0 | 0 | 125.3158 | 0 | 95% | 0 | 7.0809 | 78.67% | 0 | 47.7815
4240 | 772 | 718 | 156 | 5.8 | 30.5 | 111.2351 | 98.6519 | 42.2951 | 0.079066 | 42.5938 | 0.1312 | 70.4163 | 0 | 100% | 8.3304 | 0 | 90% | 0 | 32.0899
4241 | 627 | 516 | 161 | 6.8 | 28.9 | 42.0274 | 121.8549 | 23.8708 | 0 | 42.5929 | 14.4266 | 0 | 0 | 100% | 0 | 7.6375 | 77.78% | 0 | 46.5557
4242 | 455 | 309 | 132 | 6.7 | 27.6 | 42.1595 | 51.5177 | 7.2485 | 0 | 42.5906 | 14.5405 | 0 | 0 | 100% | 0 | 23.5218 | 40.14% | 0 | 46.0206
4243 | 142 | 100 | 65 | 5.4 | 26.7 | 0 | 25.5679 | 0 | 0 | 74.6328 | 28.1638 | 0 | 75.4263 | 94% | 0 | 18.8407 | 10% | 0 | 44.9241
4244 | 4 | 5 | 5 | 4.2 | 24.5 | 0 | 0.029832 | 0 | 0 | 111.7142 | 44.2506 | 0 | 115.2338 | 86% | 0 | 0 | 10% | 0 | 41.7135
4245 | 0 | 0 | 0 | 2.1 | 24.1 | 0 | 0 | 0 | 0 | 105.4611 | 41.7264 | 0 | 105.7373 | 78% | 0 | 0 | 10% | 0 | 39.6965
4246 | 0 | 0 | 0 | 1.5 | 23.7 | 0 | 0 | 0 | 0 | 99.5644 | 39.3097 | 0 | 98.3829 | 70% | 0 | 0 | 10% | 0 | 37.362
4247 | 0 | 0 | 0 | 1.8 | 23.4 | 0 | 0 | 0 | 0 | 95.2985 | 37.5709 | 0 | 93.4992 | 63% | 0 | 0 | 10% | 0 | 35.5983
4248 | 0 | 0 | 0 | 1.7 | 22.2 | 0 | 0 | 0 | 0 | 93.1047 | 36.7649 | 0 | 91.0642 | 56% | 0 | 0 | 10% | 0 | 34.7416
4249 | 0 | 0 | 0 | 1.8 | 22.4 | 0 | 0 | 0 | 0 | 92.5783 | 36.5251 | 0 | 90.5914 | 50% | 0 | 0 | 10% | 0 | 34.4485
4250 | 0 | 0 | 0 | 2.8 | 22.4 | 0 | 0 | 0 | 0 | 93.7538 | 37.0222 | 0 | 92.1771 | 43% | 0 | 0 | 10% | 0 | 34.9
4251 | 0 | 0 | 0 | 2.5 | 21.6 | 0 | 0 | 0 | 0 | 99.1826 | 39.3476 | 0 | 98.6211 | 35% | 0 | 0 | 10% | 0 | 37.1921
4252 | 0 | 0 | 0 | 1.1 | 20.2 | 0 | 0 | 0 | 0 | 106.391 | 42.473 | 0 | 107.1809 | 27% | 0 | 0 | 10% | 0 | 40.3118
4253 | 0 | 1 | 1 | 2.3 | 20.1 | 0 | 0 | 0 | 0 | 114.1592 | 45.6907 | 0 | 116.1542 | 18% | 0 | 0 | 10% | 0 | 43.5542
4254 | 19 | 49 | 46 | 4.7 | 20.9 | 0 | 2.9096 | 0 | 0 | 121.4578 | 48.6221 | 0 | 124.5832 | 9% | 0 | 0 | 10% | 0 | 46.5307
4255 | 88 | 161 | 133 | 6.1 | 23.1 | 0 | 19.0205 | 1.8577 | 0 | 111.2966 | 44.3559 | 0 | 113.8256 | 0% | 0 | 0 | 10% | 0 | 44.214
4256 | 252 | 359 | 226 | 6 | 24.8 | 0 | 55.3653 | 13.2841 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 11.5001
4257 | 391 | 549 | 277 | 6.7 | 27.2 | 84.884 | -1.49e-14 | 28.7168 | 0 | 0 | 0 | 81.8476 | 0 | 6% | 0 | 0 | 10% | 0 | 27.5576
4258 | 570 | 811 | 345 | 7.5 | 29.2 | 140.9556 | -2.98e-14 | 51.6347 | 0 | 0 | 0 | 138.7082 | 0 | 17% | 0 | 0 | 10% | 0 | 49.9598
4259 | 347 | 697 | 372 | 7.3 | 30.3 | 80.9559 | 0 | 45.1168 | 0 | 0 | 0 | 80.1898 | 0 | 23% | 0 | 0 | 10% | 0 | 43.9621
4260 | 570 | 939 | 374 | 7.2 | 31 | 150.5674 | 2.98e-14 | 65.2468 | 0 | 0 | 0 | 148.4191 | 0 | 34% | 13.7468 | 0 | 28.7% | 0 | 49.7142
4261 | 552 | 949 | 394 | 7.4 | 31.8 | 145.8039 | 0 | 65.8073 | 0 | 0 | 0 | 144.586 | 0 | 45% | 14.3073 | 0 | 48.15% | 0 | 49.7331
4262 | 439 | 831 | 409 | 8 | 31.1 | 108.9994 | 0 | 55.6143 | 0 | 0 | 0 | 108.098 | 0 | 54% | 4.1143 | 0 | 53.75% | 0 | 50.0603
4263 | 658 | 825 | 255 | 8.4 | 31.5 | 168.4412 | 0 | 53.3981 | 0 | 42.8297 | 1.252 | 127.1488 | 0 | 63% | 17.2261 | 0 | 77.18% | 0 | 34.9419
4264 | 624 | 677 | 217 | 8.3 | 32.2 | 151.5543 | 0 | 38.9792 | 0 | 45.5736 | 15.316 | 108.0697 | 0 | 72% | 3.5202 | 0 | 81.96% | 0 | 48.9029
4265 | 536 | 496 | 188 | 7.6 | 30.6 | 117.0944 | 0 | 22.5343 | 0 | 42.5831 | 14.2713 | 76.3455 | 0 | 77% | 0 | 12.6987 | 61.65% | 0 | 47.9639
4266 | 313 | 282 | 155 | 7 | 28.7 | 0 | 61.3287 | 6.5065 | 0 | 49.0906 | 17.1088 | 0 | 46.5073 | 74% | 0 | 25 | 21.65% | 0 | 47.1235
4267 | 77 | 102 | 84 | 5.8 | 27.1 | 0 | 13.8726 | 0 | 0 | 105.9943 | 41.3852 | 0 | 109.4794 | 66% | 0 | 7.2789 | 10% | 0 | 46.1389
4268 | 2 | 9 | 9 | 5.1 | 25.3 | 0 | 0.015303 | 0 | 0 | 114.1456 | 45.1625 | 0 | 116.9241 | 57% | 0 | 0 | 10% | 0 | 42.8801
4269 | 0 | 0 | 0 | 3.8 | 23.8 | 0 | 0 | 0 | 0 | 107.9157 | 42.7645 | 0 | 108.8601 | 49% | 0 | 0 | 10% | 0 | 40.6417
4270 | 0 | 0 | 0 | 3.4 | 24.2 | 0 | 0 | 0 | 0 | 101.703 | 40.1496 | 0 | 101.2322 | 41% | 0 | 0 | 10% | 0 | 38.0945
4271 | 0 | 0 | 0 | 3.5 | 26.7 | 0 | 0 | 0 | 0 | 97.774 | 38.2441 | 0 | 96.5495 | 34% | 0 | 0 | 10% | 0 | 36.2009
4272 | 0 | 0 | 0 | 2.8 | 26.2 | 0 | 0 | 0 | 0 | 95.4773 | 37.3545 | 0 | 93.916 | 27% | 0 | 0 | 10% | 0 | 35.2988
4273 | 0 | 0 | 0 | 2.3 | 23.9 | 0 | 0 | 0 | 0 | 94.3972 | 37.1523 | 0 | 92.7337 | 20% | 0 | 0 | 10% | 0 | 35.0751
4274 | 0 | 0 | 0 | 2.1 | 22.9 | 0 | 0 | 0 | 0 | 94.8718 | 37.4441 | 0 | 93.352 | 12% | 0 | 0 | 10% | 0 | 35.3427
4275 | 0 | 0 | 0 | 1.3 | 21.7 | 0 | 0 | 0 | 0 | 99.9732 | 39.6704 | 0 | 99.3861 | 5% | 0 | 0 | 10% | 0 | 37.5412
4276 | 0 | 0 | 0 | 1.7 | 21.9 | 0 | 0 | 0 | 0 | 63.7636 | 25.378 | 0 | 64.266 | 0% | 0 | 0 | 10% | 0 | 23.3028
4277 | 0 | 1 | 1 | 1.1 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9693
4278 | 79 | 55 | 43 | 1.7 | 22.4 | 0 | 12.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9532
4279 | 350 | 220 | 110 | 0.7 | 26 | 0 | 64.7684 | 2.2065 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.27181
4280 | 539 | 421 | 155 | 3.1 | 28.3 | 114.1972 | 0 | 15.9228 | 0 | 0 | 0 | 109.6642 | 0 | 8% | 0 | 0 | 10% | 0 | 14.5155
4281 | 656 | 616 | 181 | 5 | 31.4 | 158.2899 | 0 | 33.2805 | 0 | 0 | 0 | 156.0971 | 0 | 20% | 0 | 0 | 10% | 0 | 31.4523
4282 | 731 | 784 | 195 | 6 | 33.3 | 188.2756 | 0 | 49.4004 | 0 | 43.5131 | 3.8908 | 146.1984 | 0 | 31% | 12.9004 | 0 | 27.54% | 0 | 37.8592
4283 | 771 | 909 | 206 | 6.6 | 34.1 | 206.7971 | 0 | 61.6734 | 0 | 43.7985 | 14.4236 | 164.4993 | 0 | 44% | 23.7865 | 0 | 59.89% | 0 | 49.974
4284 | 789 | 979 | 211 | 7.1 | 34.6 | 216.8246 | 0 | 60.6561 | 6.498 | 42.5734 | 13.8931 | 175.6752 | 0 | 57% | 22.1366 | 0 | 90% | 0 | 49.9692
4285 | 798 | 992 | 206 | 7.3 | 34.6 | 220.5143 | 0 | 38.5639 | 29.8206 | 42.5825 | 13.8961 | 179.2894 | 0 | 71% | 0 | 0 | 90% | 0 | 49.9687
4286 | 800 | 951 | 196 | 7.8 | 34.5 | 216.9624 | 2.98e-14 | 38.5307 | 26.0737 | 42.5886 | 13.9078 | 175.5636 | 0 | 84% | 0 | 0 | 90% | 0 | 49.9691
4287 | 789 | 857 | 181 | 9 | 34.2 | 206.1922 | 0 | 37.6436 | 17.7718 | 42.5922 | 13.938 | 164.5105 | 0 | 96% | 0 | 0 | 90% | 0 | 49.9165
4288 | 733 | 704 | 168 | 8.2 | 33.8 | 98.2147 | 100.8563 | 35.0204 | 5.8865 | 42.5945 | 13.9771 | 56.4967 | 0 | 100% | 0 | 0 | 90% | 0 | 49.6771
4289 | 636 | 516 | 153 | 7.4 | 32.8 | 42.1518 | 124.2673 | 23.388 | 0 | 42.5933 | 14.0717 | 0 | 0 | 100% | 0 | 10.3689 | 73.41% | 0 | 48.5372
4290 | 478 | 312 | 126 | 6.8 | 31.6 | 42.88 | 57.009 | 7.1192 | 0 | 43.3035 | 14.4647 | 0 | 0 | 100% | 0 | 25 | 33.41% | 0 | 47.2926
4291 | 221 | 120 | 73 | 7.4 | 29.4 | 0 | 39.835 | 0 | 0 | 87.6672 | 33.3353 | 0 | 90.3982 | 93% | 0 | 14.6311 | 10% | 0 | 45.8759
4292 | 8 | 10 | 9 | 6.1 | 26.9 | 0 | 0.061784 | 0 | 0 | 114.8616 | 45.2635 | 0 | 117.7522 | 85% | 0 | 0 | 10% | 0 | 43.0133
4293 | 0 | 0 | 0 | 6.5 | 26 | 0 | 0 | 0 | 0 | 109.7724 | 43.2832 | 0 | 110.0542 | 76% | 0 | 0 | 10% | 0 | 41.4148
4294 | 0 | 0 | 0 | 5.1 | 25.5 | 0 | 0 | 0 | 0 | 103.336 | 40.6888 | 0 | 102.2664 | 68% | 0 | 0 | 10% | 0 | 38.8863
4295 | 0 | 0 | 0 | 4.4 | 24.6 | 0 | 0 | 0 | 0 | 98.0151 | 38.5755 | 0 | 96.1031 | 61% | 0 | 0 | 10% | 0 | 36.7482
4296 | 0 | 0 | 0 | 3 | 23.2 | 0 | 0 | 0 | 0 | 94.7763 | 37.3744 | 0 | 92.5699 | 54% | 0 | 0 | 10% | 0 | 35.488
4297 | 0 | 0 | 0 | 1.9 | 22.6 | 0 | 0 | 0 | 0 | 92.9057 | 36.6454 | 0 | 90.5392 | 47% | 0 | 0 | 10% | 0 | 34.6978
4298 | 0 | 0 | 0 | 1.1 | 22.5 | 0 | 0 | 0 | 0 | 91.8292 | 36.2006 | 0 | 89.4204 | 40% | 0 | 0 | 10% | 0 | 34.1946
4299 | 0 | 0 | 0 | 1.1 | 21.7 | 0 | 0 | 0 | 0 | 90.6345 | 35.7675 | 0 | 88.142 | 34% | 0 | 0 | 10% | 0 | 33.7097
4300 | 0 | 0 | 0 | 1.5 | 21.3 | 0 | 0 | 0 | 0 | 92.0711 | 36.407 | 0 | 90.0443 | 27% | 0 | 0 | 10% | 0 | 34.2971
4301 | 0 | 1 | 1 | 2.5 | 22.4 | 0 | 0 | 0 | 0 | 98.6516 | 39.0563 | 0 | 97.9527 | 19% | 0 | 0 | 10% | 0 | 36.9028
4302 | 102 | 60 | 44 | 3 | 23.3 | 0 | 15.5466 | 0 | 0 | 107.141 | 42.4989 | 0 | 108.0341 | 11% | 0 | 0 | 10% | 0 | 40.3308
4303 | 363 | 229 | 116 | 1.8 | 26 | 45.3877 | 11.4301 | 2.5807 | 0 | 105.9855 | 41.7361 | 0 | 62.5816 | 6% | 0 | 0 | 10% | 0 | 43.0782
4304 | 541 | 428 | 160 | 3.4 | 28.5 | 114.6004 | 0 | 16.2788 | 0 | 78.7212 | 29.96 | 37.2255 | 0 | 9% | 0 | 0 | 10% | 0 | 44.7213
4305 | 666 | 622 | 179 | 5.2 | 30.4 | 160.8351 | 0 | 33.5584 | 0.12025 | 42.5605 | 14.2818 | 119.4175 | 0 | 18% | 0 | 0 | 10% | 0 | 45.9609
4306 | 734 | 787 | 194 | 5.8 | 32.5 | 189.3393 | 0 | 49.6331 | 0 | 46.5398 | 15.6763 | 144.3063 | 0 | 29% | 16.2813 | 0 | 32.14% | 0 | 46.8776
4307 | 774 | 911 | 204 | 6.2 | 34 | 208.0792 | 0 | 60.0588 | 1.7056 | 42.596 | 13.9586 | 166.8435 | 0 | 42% | 25 | 0 | 66.14% | 0 | 46.69
4308 | 785 | 979 | 213 | 6.7 | 34.5 | 216.0258 | 1.2e-14 | 51.8345 | 15.1928 | 42.6021 | 13.9122 | 174.7367 | 0 | 55% | 17.5422 | 0 | 90% | 0 | 45.7853
4309 | 789 | 994 | 215 | 7.2 | 34.8 | 217.9621 | 0 | 33.3618 | 34.9215 | 42.6041 | 13.8838 | 176.5962 | 0 | 68% | 0 | 0 | 90% | 0 | 44.796
4310 | 779 | 949 | 211 | 7.3 | 35.2 | 211.2439 | 0 | 33.1185 | 32.0488 | 42.6055 | 13.8452 | 169.7294 | 0 | 80% | 0 | 0 | 90% | 0 | 44.5641
4311 | 744 | 847 | 206 | 6.8 | 35.5 | 195.2722 | 0 | 32.8274 | 22.0754 | 42.606 | 13.8159 | 153.5424 | 0 | 92% | 0 | 0 | 90% | 0 | 44.3868
4312 | 695 | 699 | 189 | 7.1 | 35 | 154.9849 | 21.5036 | 28.6353 | 11.7514 | 42.6058 | 13.865 | 112.9573 | 0 | 100% | 0 | 0 | 90% | 0 | 44.293
4313 | 614 | 513 | 162 | 6.9 | 34.1 | 42.1518 | 118.1392 | 23.2313 | 0 | 42.6049 | 13.9518 | 0 | 0 | 100% | 0 | 5.9807 | 80.43% | 0 | 43.8722
4314 | 462 | 308 | 128 | 6.7 | 32.6 | 42.1569 | 53.693 | 7.0455 | 0 | 42.6024 | 14.0934 | 0 | 0 | 100% | 0 | 21.7382 | 45.65% | 0 | 43.5858
4315 | 229 | 122 | 73 | 5.6 | 30.5 | 0 | 41.2914 | 0 | 0 | 63.3463 | 22.9548 | 0 | 62.7603 | 95% | 0 | 22.2811 | 10% | 0 | 43.1502
4316 | 10 | 11 | 10 | 5.8 | 28.1 | 0 | 0.076713 | 0 | 0 | 111.6255 | 43.7768 | 0 | 116.1693 | 87% | 0 | 0 | 10% | 0 | 40.9972
4317 | 0 | 0 | 0 | 3.1 | 26.6 | 0 | 0 | 0 | 0 | 103.1733 | 40.4929 | 0 | 103.2875 | 79% | 0 | 0 | 10% | 0 | 38.388
4318 | 0 | 0 | 0 | 1.1 | 25.2 | 0 | 0 | 0 | 0 | 96.763 | 37.9934 | 0 | 95.3983 | 72% | 0 | 0 | 10% | 0 | 35.9685
4319 | 0 | 0 | 0 | 1.1 | 23.5 | 0 | 0 | 0 | 0 | 91.8222 | 36.1039 | 0 | 89.6271 | 65% | 0 | 0 | 10% | 0 | 34.0479
4320 | 0 | 0 | 0 | 2.2 | 24.2 | 0 | 0 | 0 | 0 | 89.261 | 34.961 | 0 | 86.7534 | 58% | 0 | 0 | 10% | 0 | 32.838
4321 | 0 | 0 | 0 | 1.5 | 22.5 | 0 | 0 | 0 | 0 | 86.8885 | 34.1264 | 0 | 84.1428 | 52% | 0 | 0 | 10% | 0 | 31.9352
4322 | 0 | 0 | 0 | 2.1 | 22.7 | 0 | 0 | 0 | 0 | 86.3561 | 33.8869 | 0 | 83.7213 | 46% | 0 | 0 | 10% | 0 | 31.6273
4323 | 0 | 0 | 0 | 1.8 | 22.3 | 0 | 0 | 0 | 0 | 85.3632 | 33.5081 | 0 | 82.7146 | 40% | 0 | 0 | 10% | 0 | 31.1936
4324 | 0 | 0 | 0 | 1.5 | 21.4 | 0 | 0 | 0 | 0 | 85.0759 | 33.4636 | 0 | 82.522 | 33% | 0 | 0 | 10% | 0 | 31.0996
4325 | 0 | 1 | 0 | 1.1 | 20.2 | 0 | 0 | 0 | 0 | 88.9732 | 35.1901 | 0 | 87.3033 | 27% | 0 | 0 | 10% | 0 | 32.7781
4326 | 177 | 62 | 36 | 0.4 | 21.6 | 0 | 26.9101 | 0 | 0 | 95.1234 | 37.6628 | 0 | 94.8547 | 20% | 0 | 0 | 10% | 0 | 35.2251
4327 | 524 | 241 | 80 | 1.4 | 25.5 | 72.4374 | 17.6984 | 1.6564 | 0 | 95.6129 | 37.4895 | 0 | 25.1362 | 18% | 0 | 0 | 10% | 0 | 37.6444
4328 | 692 | 443 | 103 | 1.1 | 27.8 | 152.713 | 0 | 16.2731 | 0 | 67.565 | 25.1216 | 85.8593 | 0 | 24% | 0 | 0 | 10% | 0 | 39.5599
4329 | 781 | 637 | 120 | 2.8 | 30.4 | 193.9518 | 0 | 34.2367 | 0 | 46.5704 | 15.897 | 148.2565 | 0 | 35% | 7.3156 | 0 | 19.95% | 0 | 40.6354
4330 | 832 | 801 | 131 | 4.4 | 32.6 | 218.3924 | 0 | 50.2601 | 0 | 47.5274 | 16.0684 | 171.8583 | 0 | 48% | 22.1269 | 0 | 50.04% | 0 | 41.7832
4331 | 856 | 921 | 140 | 5.3 | 34.1 | 233.1741 | 0 | 56.1846 | 5.7447 | 42.5887 | 13.9465 | 191.4298 | 0 | 62% | 25 | 0 | 84.04% | 0 | 42.5665
4332 | 854 | 987 | 154 | 5.6 | 35 | 238.0117 | 0 | 35.0693 | 33.02 | 42.5953 | 13.8616 | 196.2019 | 0 | 77% | 4.381 | 0 | 90% | 0 | 41.9183
4333 | 842 | 1000 | 169 | 6.1 | 35.7 | 235.2321 | 0 | 29.4389 | 39.6167 | 42.5981 | 13.7937 | 193.2706 | 0 | 91% | 0 | 0 | 90% | 0 | 41.2632
4334 | 752 | 928 | 213 | 6.3 | 35.6 | 163.9502 | 47.4259 | 25.9355 | 37.3344 | 42.6002 | 13.8042 | 121.9966 | 0 | 100% | 0 | 0 | 90% | 0 | 41.3365
4335 | 713 | 834 | 219 | 5.6 | 35.4 | 42.1514 | 171.4003 | 26.81 | 27.0898 | 42.6 | 13.8238 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.3418
4336 | 723 | 696 | 166 | 5.5 | 34.6 | 42.1567 | 165.5224 | 27.0589 | 13.1875 | 42.5976 | 13.901 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.6681
4337 | 648 | 516 | 145 | 5.5 | 34.1 | 42.1568 | 128.3685 | 23.2211 | 0 | 42.5952 | 13.9486 | 0 | 0 | 100% | 0 | 4.2724 | 83.16% | 0 | 42.1504
4338 | 491 | 311 | 119 | 5.5 | 33.1 | 42.1569 | 62.1425 | 6.8856 | 0 | 42.5929 | 14.0433 | 0 | 0 | 100% | 0 | 21.2803 | 49.12% | 0 | 42.9178
4339 | 215 | 118 | 71 | 5.1 | 31.1 | 0 | 38.7754 | 0 | 0 | 60.1568 | 21.5449 | 0 | 58.8796 | 96% | 0 | 24.4474 | 10% | 0 | 43.9059
4340 | 10 | 10 | 9 | 4.2 | 28.8 | 0 | 0.074954 | 0 | 0 | 113.3467 | 44.3866 | 0 | 118.8992 | 87% | 0 | 0 | 10% | 0 | 41.4626
4341 | 0 | 0 | 0 | 2.1 | 26.7 | 0 | 0 | 0 | 0 | 103.3504 | 40.5553 | 0 | 103.5496 | 79% | 0 | 0 | 10% | 0 | 38.4391
4342 | 0 | 0 | 0 | 1.9 | 25.3 | 0 | 0 | 0 | 0 | 96.8426 | 38.0158 | 0 | 95.5073 | 72% | 0 | 0 | 10% | 0 | 35.9875
4343 | 0 | 0 | 0 | 0.6 | 24 | 0 | 0 | 0 | 0 | 92.2276 | 36.2278 | 0 | 90.1313 | 65% | 0 | 0 | 10% | 0 | 34.17
4344 | 0 | 0 | 0 | 0.6 | 23.2 | 0 | 0 | 0 | 0 | 90.4418 | 35.5524 | 0 | 88.1687 | 58% | 0 | 0 | 10% | 0 | 33.4314
4345 | 0 | 0 | 0 | 1.4 | 23.2 | 0 | 0 | 0 | 0 | 90.0238 | 35.3771 | 0 | 87.8552 | 52% | 0 | 0 | 10% | 0 | 33.1953
4346 | 0 | 0 | 0 | 1.2 | 22.3 | 0 | 0 | 0 | 0 | 91.2182 | 35.9608 | 0 | 89.4548 | 45% | 0 | 0 | 10% | 0 | 33.7293
4347 | 0 | 0 | 0 | 1.2 | 21.1 | 0 | 0 | 0 | 0 | 97.7658 | 38.8014 | 0 | 97.3822 | 38% | 0 | 0 | 10% | 0 | 36.5322
4348 | 0 | 0 | 0 | 1.8 | 22.4 | 0 | 0 | 0 | 0 | 106.2613 | 42.2235 | 0 | 107.4694 | 30% | 0 | 0 | 10% | 0 | 39.9564
4349 | 1 | 1 | 0 | 1.3 | 21.9 | 0 | 0 | 0 | 0 | 113.9721 | 45.4489 | 0 | 116.3384 | 21% | 0 | 0 | 10% | 0 | 43.2223
4350 | 154 | 53 | 31 | 1.9 | 22.2 | 0 | 23.3517 | 0 | 0 | 120.0498 | 47.9189 | 0 | 123.2683 | 11% | 0 | 0 | 10% | 0 | 45.753
4351 | 540 | 235 | 71 | 1.2 | 26 | 74.956 | 18.2627 | 1.2233 | 0 | 121.8538 | 48.2403 | 0 | 52.4311 | 7% | 0 | 0 | 10% | 0 | 47.9491
4352 | 715 | 439 | 91 | 1.6 | 29.2 | 157.8481 | 0 | 15.8631 | 0 | 90.6899 | 34.9907 | 67.8602 | 0 | 13% | 0 | 0 | 10% | 0 | 48.919
4353 | 817 | 635 | 100 | 1.7 | 30.5 | 203.903 | 0 | 34.287 | 0 | 51.4583 | 17.9181 | 154.3546 | 0 | 24% | 0 | 0 | 10% | 0 | 49.9106
4354 | 876 | 802 | 102 | 2 | 32.3 | 232.2989 | 0 | 50.6819 | 0 | 47.1977 | 15.9627 | 186.9186 | 0 | 39% | 14.1819 | 0 | 29.29% | 0 | 49.9009
4355 | 905 | 923 | 104 | 2.2 | 33.8 | 249.8185 | 0 | 62.6719 | 0 | 43.9558 | 14.5116 | 207.5002 | 0 | 54% | 24.5241 | 0 | 62.64% | 0 | 49.9197
4356 | 924 | 996 | 104 | 4.8 | 34.2 | 259.6488 | 0 | 58.9965 | 10.8644 | 42.609 | 13.9435 | 218.4893 | 0 | 71% | 20.1175 | 0 | 90% | 0 | 49.9656
4357 | 940 | 1015 | 97 | 5.7 | 34.7 | 265.1363 | 0 | 38.997 | 32.5219 | 42.61 | 13.8954 | 223.8307 | 0 | 87% | 0 | 0 | 90% | 0 | 49.9645
4358 | 921 | 965 | 100 | 6.9 | 34.7 | 213.8626 | 46.6421 | 35.6382 | 30.884 | 42.6104 | 13.8956 | 172.2542 | 0 | 100% | 0 | 0 | 90% | 0 | 50.0715
4359 | 881 | 861 | 108 | 7.2 | 34.4 | 42.1512 | 224.2238 | 34.8143 | 21.2913 | 42.6098 | 13.9244 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 49.447
4360 | 739 | 670 | 133 | 6.9 | 34 | 42.1568 | 170.1309 | 34.0009 | 4.4103 | 42.6071 | 13.9622 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 48.6715
4361 | 703 | 514 | 114 | 6.7 | 33.9 | 42.1568 | 143.85 | 22.8795 | 0 | 42.6045 | 13.9709 | 0 | 0 | 100% | 0 | 10.2056 | 73.67% | 0 | 47.7643
4362 | 537 | 304 | 95 | 5.8 | 33 | 44.5989 | 70.7676 | 6.3135 | 0 | 45.0065 | 15.0084 | 0 | 0 | 100% | 0 | 25 | 33.67% | 0 | 47.027
4363 | 245 | 110 | 56 | 3.7 | 31.5 | 0 | 44.1898 | 0 | 0 | 86.7876 | 32.6853 | 0 | 89.4029 | 93% | 0 | 14.7944 | 10% | 0 | 45.3868
4364 | 1 | 7 | 7 | 3.6 | 28.1 | 0 | 0.007194 | 0 | 0 | 113.0061 | 44.343 | 0 | 115.5865 | 85% | 0 | 0 | 10% | 0 | 42.0792
4365 | 0 | 0 | 0 | 4.9 | 25 | 0 | 0 | 0 | 0 | 105.9243 | 41.8195 | 0 | 105.7551 | 77% | 0 | 0 | 10% | 0 | 39.9152
4366 | 0 | 0 | 0 | 3.8 | 23.4 | 0 | 0 | 0 | 0 | 99.9032 | 39.4793 | 0 | 98.4631 | 69% | 0 | 0 | 10% | 0 | 37.6135
4367 | 0 | 0 | 0 | 2.5 | 23.6 | 0 | 0 | 0 | 0 | 96.1469 | 37.9021 | 0 | 94.2427 | 62% | 0 | 0 | 10% | 0 | 35.9926
4368 | 0 | 0 | 0 | 3.9 | 22.6 | 0 | 0 | 0 | 0 | 94.0683 | 37.1359 | 0 | 92.0384 | 55% | 0 | 0 | 10% | 0 | 35.169
4369 | 0 | 0 | 0 | 4 | 21.3 | 0 | 0 | 0 | 0 | 93.2711 | 36.9119 | 0 | 91.2345 | 48% | 0 | 0 | 10% | 0 | 34.8914
4370 | 0 | 0 | 0 | 3.2 | 20.6 | 0 | 0 | 0 | 0 | 94.1211 | 37.3291 | 0 | 92.4294 | 41% | 0 | 0 | 10% | 0 | 35.2604
4371 | 0 | 0 | 0 | 2.4 | 20.5 | 0 | 0 | 0 | 0 | 99.7813 | 39.69 | 0 | 99.1358 | 34% | 0 | 0 | 10% | 0 | 37.5827
4372 | 0 | 0 | 0 | 2.1 | 20.5 | 0 | 0 | 0 | 0 | 107.3972 | 42.8614 | 0 | 108.1589 | 25% | 0 | 0 | 10% | 0 | 40.7437
4373 | 0 | 1 | 1 | 2.6 | 19.1 | 0 | 0 | 0 | 0 | 114.8291 | 46.0563 | 0 | 116.7554 | 17% | 0 | 0 | 10% | 0 | 43.9605
4374 | 118 | 51 | 34 | 3.3 | 18.8 | 0 | 17.8439 | 0 | 0 | 121.8698 | 48.9895 | 0 | 124.8716 | 7% | 0 | 0 | 10% | 0 | 46.9353
4375 | 391 | 213 | 94 | 4.3 | 20.8 | 48.5099 | 12.6249 | 1.5399 | 0 | 120.833 | 48.376 | 0 | 76.2977 | 1% | 0 | 0 | 10% | 0 | 48.645
4376 | 621 | 421 | 119 | 6.2 | 23.4 | 131.2473 | 0 | 15.8375 | 0 | 90.4647 | 35.5458 | 41.4022 | 0 | 4% | 0 | 0 | 10% | 0 | 49.6902
4377 | 749 | 621 | 130 | 6.5 | 25.2 | 181.8342 | 0 | 34.2417 | 0 | 49.9261 | 17.7792 | 133.931 | 0 | 15% | 0 | 0 | 10% | 0 | 49.9345
4378 | 814 | 786 | 135 | 6.1 | 26.8 | 211.4355 | 0 | 50.4211 | 0 | 45.4691 | 15.777 | 167.904 | 0 | 27% | 13.9211 | 0 | 28.93% | 0 | 49.9177
4379 | 830 | 904 | 151 | 5.4 | 28.1 | 225.0118 | 0 | 62.1498 | 0 | 43.8586 | 15.0054 | 183.0025 | 0 | 41% | 24.5605 | 0 | 62.33% | 0 | 50.0967
4380 | 839 | 974 | 161 | 4.5 | 29.2 | 234.0319 | 0 | 58.5099 | 10.305 | 42.6129 | 14.4067 | 193.0859 | 0 | 56% | 20.3419 | 0 | 90% | 0 | 49.9733
4381 | 865 | 993 | 145 | 3.4 | 30.4 | 244.3025 | 0 | 38.3853 | 32.0248 | 42.613 | 14.2994 | 203.2178 | 0 | 71% | 0 | 0 | 90% | 0 | 49.9707
4382 | 845 | 948 | 152 | 4.4 | 31.3 | 233.3551 | 0 | 38.3807 | 27.3103 | 42.6128 | 14.2175 | 192.1197 | 0 | 85% | 0 | 0 | 90% | 0 | 49.9707
4383 | 808 | 845 | 154 | 5.3 | 31 | 214.8629 | 0 | 35.196 | 20.3409 | 42.6122 | 14.2449 | 173.2874 | 0 | 98% | 0 | 0 | 90% | 0 | 49.1417
4384 | 772 | 699 | 138 | 4.9 | 30.9 | 67.3355 | 151.1789 | 33.6403 | 7.3648 | 42.6112 | 14.2536 | 25.8176 | 0 | 100% | 0 | 0 | 90% | 0 | 48.4545
4385 | 613 | 479 | 127 | 5 | 30.3 | 42.1519 | 118.5258 | 21.1458 | 0 | 42.6088 | 14.307 | 0 | 0 | 100% | 0 | 11.452 | 71.68% | 0 | 47.614
4386 | 524 | 302 | 99 | 5.2 | 28.7 | 43.398 | 69.2064 | 6.5487 | 0 | 43.8288 | 14.9394 | 0 | 0 | 100% | 0 | 25 | 31.68% | 0 | 47.1968
4387 | 236 | 106 | 56 | 5.1 | 26.7 | 0 | 42.5645 | 0 | 0 | 89.6802 | 34.5219 | 0 | 92.7512 | 93% | 0 | 13.548 | 10% | 0 | 45.9805
4388 | 6 | 7 | 6 | 4.4 | 25 | 0 | 0.040603 | 0 | 0 | 113.3933 | 44.8864 | 0 | 115.7813 | 85% | 0 | 0 | 10% | 0 | 42.6826
4389 | 0 | 0 | 0 | 4.4 | 23.2 | 0 | 0 | 0 | 0 | 106.7549 | 42.3473 | 0 | 106.5837 | 76% | 0 | 0 | 10% | 0 | 40.4731
4390 | 0 | 0 | 0 | 4.5 | 21.9 | 0 | 0 | 0 | 0 | 100.6678 | 39.9378 | 0 | 99.2522 | 69% | 0 | 0 | 10% | 0 | 38.0992
4391 | 0 | 0 | 0 | 2.7 | 21.4 | 0 | 0 | 0 | 0 | 96.3036 | 38.1668 | 0 | 94.3186 | 62% | 0 | 0 | 10% | 0 | 36.2854
4392 | 0 | 0 | 0 | 1.6 | 21.3 | 0 | 0 | 0 | 0 | 94.3335 | 37.3591 | 0 | 92.2606 | 55% | 0 | 0 | 10% | 0 | 35.4157
4393 | 0 | 0 | 0 | 2.7 | 20.7 | 0 | 0 | 0 | 0 | 93.6987 | 37.1419 | 0 | 91.6811 | 48% | 0 | 0 | 10% | 0 | 35.1424
4394 | 0 | 0 | 0 | 2.8 | 21.3 | 0 | 0 | 0 | 0 | 94.7819 | 37.5453 | 0 | 93.112 | 41% | 0 | 0 | 10% | 0 | 35.4976
4395 | 0 | 0 | 0 | 3.1 | 21.2 | 0 | 0 | 0 | 0 | 100.4681 | 39.9173 | 0 | 99.8628 | 33% | 0 | 0 | 10% | 0 | 37.8311
4396 | 0 | 0 | 0 | 2.2 | 20.5 | 0 | 0 | 0 | 0 | 107.9073 | 43.0715 | 0 | 108.6577 | 25% | 0 | 0 | 10% | 0 | 40.9754
4397 | 0 | 1 | 1 | 1.3 | 20 | 0 | 0 | 0 | 0 | 115.7183 | 46.3454 | 0 | 117.7203 | 16% | 0 | 0 | 10% | 0 | 44.2693
4398 | 160 | 54 | 31 | 1.5 | 20.4 | 0 | 24.1262 | 0 | 0 | 122.1731 | 48.9639 | 0 | 125.1375 | 6% | 0 | 0 | 10% | 0 | 46.9309
4399 | 522 | 228 | 71 | 1.8 | 22.2 | 71.2997 | 17.6421 | 1.144 | 0 | 122.1734 | 48.791 | 0 | 55.7591 | 2% | 0 | 0 | 10% | 0 | 48.4671
4400 | 684 | 428 | 98 | 3.2 | 24 | 149.2201 | 0 | 15.8359 | 0 | 90.7663 | 35.6139 | 59.6599 | 0 | 7% | 0 | 0 | 10% | 0 | 49.5894
4401 | 758 | 616 | 120 | 4.6 | 25.5 | 185.8837 | 0 | 33.6872 | 0 | 51.3175 | 18.3451 | 136.8338 | 0 | 17% | 0 | 0 | 10% | 0 | 49.9015
4402 | 805 | 777 | 135 | 4.7 | 26.7 | 210.0842 | 0 | 49.8762 | 0 | 45.4359 | 15.7722 | 166.6468 | 0 | 30% | 13.3762 | 0 | 28.19% | 0 | 49.9193
4403 | 846 | 902 | 137 | 4.2 | 28.3 | 230.7937 | 0 | 62.2055 | 0 | 43.8581 | 14.9871 | 188.7675 | 0 | 44% | 24.5603 | 0 | 61.59% | 0 | 50.0757
4404 | 828 | 961 | 159 | 3.9 | 29.7 | 231.2072 | 0 | 59.0056 | 8.7131 | 42.6126 | 14.3621 | 190.3077 | 0 | 58% | 20.887 | 0 | 90% | 0 | 49.8995
4405 | 833 | 975 | 159 | 4.5 | 30.5 | 233.5734 | 0 | 37.9544 | 30.9848 | 42.6126 | 14.2902 | 192.527 | 0 | 73% | 0 | 0 | 90% | 0 | 49.626
4406 | 816 | 927 | 161 | 5.2 | 31.1 | 223.9938 | 0 | 37.728 | 26.5419 | 42.6123 | 14.2357 | 182.742 | 0 | 86% | 0 | 0 | 90% | 0 | 49.4224
4407 | 770 | 823 | 165 | 6.4 | 30.9 | 203.0255 | 0 | 34.2644 | 19.6328 | 42.6117 | 14.2537 | 161.4334 | 0 | 98% | 0 | 0 | 90% | 0 | 48.4856
4408 | 733 | 682 | 149 | 6.1 | 30.6 | 64.6577 | 141.9015 | 33.0972 | 7.101 | 42.6106 | 14.2805 | 23.1334 | 0 | 100% | 0 | 0 | 90% | 0 | 47.9514
4409 | 653 | 499 | 129 | 5.6 | 30 | 42.152 | 129.8641 | 22.721 | 0 | 42.6082 | 14.3339 | 0 | 0 | 100% | 0 | 9.5032 | 74.8% | 0 | 47.2673
4410 | 530 | 304 | 99 | 5.2 | 28.9 | 42.1572 | 72.3608 | 6.6549 | 0 | 42.6055 | 14.4309 | 0 | 0 | 100% | 0 | 25 | 34.8% | 0 | 46.7952
4411 | 289 | 117 | 56 | 4.5 | 27.5 | 0 | 52.114 | 0 | 0 | 84.3607 | 32.1816 | 0 | 86.5813 | 94% | 0 | 15.4968 | 10% | 0 | 45.593
4412 | 14 | 9 | 8 | 3.3 | 25.8 | 0 | 0.086991 | 0 | 0 | 112.754 | 44.5303 | 0 | 115.5276 | 85% | 0 | 0 | 10% | 0 | 42.2104
4413 | 0 | 0 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 106.3912 | 42.1178 | 0 | 106.403 | 77% | 0 | 0 | 10% | 0 | 40.1858
4414 | 0 | 0 | 0 | 4.8 | 22.1 | 0 | 0 | 0 | 0 | 99.9347 | 39.6145 | 0 | 98.545 | 69% | 0 | 0 | 10% | 0 | 37.7364
4415 | 0 | 0 | 0 | 3.5 | 21.5 | 0 | 0 | 0 | 0 | 96.1225 | 38.0831 | 0 | 94.2456 | 62% | 0 | 0 | 10% | 0 | 36.1646
4416 | 0 | 0 | 0 | 1.9 | 21.9 | 0 | 0 | 0 | 0 | 94.3113 | 37.299 | 0 | 92.3475 | 55% | 0 | 0 | 10% | 0 | 35.3243
4417 | 0 | 0 | 0 | 1 | 21.1 | 0 | 0 | 0 | 0 | 93.7913 | 37.1487 | 0 | 91.889 | 48% | 0 | 0 | 10% | 0 | 35.1227
4418 | 0 | 0 | 0 | 1.5 | 20.7 | 0 | 0 | 0 | 0 | 94.5381 | 37.4938 | 0 | 92.9095 | 41% | 0 | 0 | 10% | 0 | 35.4246
4419 | 0 | 0 | 0 | 0.5 | 20.4 | 0 | 0 | 0 | 0 | 99.6399 | 39.6391 | 0 | 98.9597 | 34% | 0 | 0 | 10% | 0 | 37.5341
4420 | 0 | 0 | 0 | 1.6 | 20.1 | 0 | 0 | 0 | 0 | 107.1777 | 42.8053 | 0 | 107.8979 | 26% | 0 | 0 | 10% | 0 | 40.6889
4421 | 0 | 0 | 0 | 1.8 | 18.7 | 0 | 0 | 0 | 0 | 114.6246 | 46.0061 | 0 | 116.5096 | 17% | 0 | 0 | 10% | 0 | 43.9108
4422 | 54 | 46 | 37 | 1.6 | 19.2 | 0 | 8.1185 | 0 | 0 | 121.7204 | 48.8907 | 0 | 124.697 | 7% | 0 | 0 | 10% | 0 | 46.836
4423 | 336 | 207 | 104 | 2.6 | 21.4 | 0 | 61.0931 | 1.7997 | 0 | 91.7299 | 36.6847 | 0 | 93.6352 | 0% | 0 | 0 | 10% | 0 | 36.5571
4424 | 502 | 397 | 152 | 1.5 | 24.3 | 105.1938 | 0 | 14.8901 | 0 | 0 | 0 | 101.6551 | 0 | 8% | 0 | 0 | 10% | 0 | 13.5547
4425 | 597 | 584 | 192 | 2.9 | 26.4 | 143.6424 | 0 | 31.8661 | 0 | 0 | 0 | 141.8643 | 0 | 19% | 0 | 0 | 10% | 0 | 30.1616
4426 | 631 | 739 | 231 | 4.4 | 27.4 | 160.812 | 0 | 46.8636 | 0 | 0 | 0 | 159.4196 | 0 | 31% | 0 | 0 | 10% | 0 | 44.9839
4427 | 700 | 867 | 229 | 4.8 | 28.4 | 187.2356 | 0 | 59.5009 | 0 | 0 | 0 | 185.8315 | 0 | 45% | 8.0009 | 0 | 20.88% | 0 | 49.3557
4428 | 726 | 939 | 233 | 5.8 | 29.5 | 198.7834 | 0 | 66.5354 | 0 | 0 | 0 | 197.5188 | 0 | 60% | 15.372 | 0 | 41.79% | 0 | 48.8822
4429 | 738 | 956 | 228 | 5.5 | 30.2 | 203.7925 | 0 | 67.9229 | 0 | 0 | 0 | 202.5936 | 0 | 76% | 16.814 | 0 | 64.65% | 0 | 48.7487
4430 | 744 | 916 | 213 | 5.2 | 30.5 | 202.3918 | 0 | 63.9812 | 0 | 0 | 0 | 201.2477 | 0 | 91% | 12.9182 | 0 | 82.22% | 0 | 48.684
4431 | 750 | 825 | 183 | 4.6 | 31 | 159.7933 | 45.4845 | 51.2043 | 3.4856 | 42.5971 | 0.97551 | 119.0682 | 0 | 100% | 5.7184 | 0 | 90% | 0 | 44.01
4432 | 757 | 691 | 140 | 5.6 | 30.7 | 41.7761 | 176.4467 | 33.7754 | 6.7488 | 42.597 | 14.2669 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 48.4904
4433 | 703 | 515 | 115 | 5.1 | 30.4 | 42.1634 | 144.3451 | 23.4186 | 0 | 42.5946 | 14.2932 | 0 | 0 | 100% | 0 | 9.2232 | 75.24% | 0 | 47.6441
4434 | 579 | 316 | 91 | 5.6 | 29.4 | 42.7154 | 84.1066 | 6.805 | 0 | 43.1424 | 14.6015 | 0 | 0 | 100% | 0 | 25 | 35.24% | 0 | 47.1158
4435 | 361 | 131 | 57 | 5.6 | 27.4 | 0 | 52.091 | 0 | 0 | 84.3804 | 32.2021 | 0 | 86.5637 | 94% | 0 | 15.7768 | 10% | 0 | 45.8797
4436 | 19 | 11 | 9 | 5.5 | 24.8 | 0 | 0.10513 | 0 | 0 | 113.9004 | 45.118 | 0 | 116.9377 | 85% | 0 | 0 | 10% | 0 | 42.7911
4437 | 0 | 0 | 0 | 4.4 | 23.2 | 0 | 0 | 0 | 0 | 107.6301 | 42.7072 | 0 | 107.7653 | 77% | 0 | 0 | 10% | 0 | 40.7927
4438 | 0 | 0 | 0 | 3.3 | 23.4 | 0 | 0 | 0 | 0 | 101.8131 | 40.2748 | 0 | 100.6683 | 69% | 0 | 0 | 10% | 0 | 38.4203
4439 | 0 | 0 | 0 | 1.4 | 22.9 | 0 | 0 | 0 | 0 | 97.2875 | 38.4421 | 0 | 95.4618 | 62% | 0 | 0 | 10% | 0 | 36.5603
4440 | 0 | 0 | 0 | 1.1 | 22.2 | 0 | 0 | 0 | 0 | 95.4343 | 37.7379 | 0 | 93.5056 | 55% | 0 | 0 | 10% | 0 | 35.801
4441 | 0 | 0 | 0 | 0.9 | 21.7 | 0 | 0 | 0 | 0 | 94.4182 | 37.361 | 0 | 92.5013 | 48% | 0 | 0 | 10% | 0 | 35.3737
4442 | 0 | 0 | 0 | 1 | 21.5 | 0 | 0 | 0 | 0 | 95.4867 | 37.8208 | 0 | 93.8747 | 40% | 0 | 0 | 10% | 0 | 35.7884
4443 | 0 | 0 | 0 | 1.3 | 21.4 | 0 | 0 | 0 | 0 | 100.9078 | 40.0838 | 0 | 100.3244 | 33% | 0 | 0 | 10% | 0 | 38.0144
4444 | 0 | 0 | 0 | 1.3 | 20.5 | 0 | 0 | 0 | 0 | 107.9396 | 43.0853 | 0 | 108.6287 | 25% | 0 | 0 | 10% | 0 | 41.0066
4445 | 0 | 0 | 0 | 1.1 | 20 | 0 | 0 | 0 | 0 | 115.4955 | 46.2535 | 0 | 117.3916 | 16% | 0 | 0 | 10% | 0 | 44.1932
4446 | 36 | 45 | 40 | 1.6 | 20 | 0 | 5.3958 | 0 | 0 | 122.7669 | 49.2477 | 0 | 125.7979 | 6% | 0 | 0 | 10% | 0 | 47.2262
4447 | 220 | 189 | 121 | 1.7 | 22.6 | 0 | 47.0462 | 1.8036 | 0 | 77.2039 | 30.8136 | 0 | 78.9473 | 0% | 0 | 0 | 10% | 0 | 30.7427
4448 | 387 | 380 | 190 | 2.8 | 24.6 | 62.5356 | 15.5834 | 14.3072 | 0 | 0 | 0 | 60.3715 | 0 | 5% | 0 | 0 | 10% | 0 | 13.1049
4449 | 537 | 576 | 222 | 2.7 | 26 | 127.3142 | 0 | 31.4984 | 0 | 0 | 0 | 125.1316 | 0 | 14% | 0 | 0 | 10% | 0 | 29.9463
4450 | 634 | 745 | 237 | 2 | 27.7 | 163.2084 | 0 | 47.4426 | 0 | 0 | 0 | 161.5464 | 0 | 27% | 0 | 0 | 10% | 0 | 45.5479
4451 | 668 | 866 | 258 | 2 | 29.4 | 179.6779 | 0 | 59.1216 | 0 | 0 | 0 | 178.2911 | 0 | 40% | 7.6216 | 0 | 20.36% | 0 | 49.4308
4452 | 691 | 936 | 264 | 3.6 | 30.5 | 190.1425 | 0 | 65.8723 | 0 | 0 | 0 | 188.8512 | 0 | 55% | 14.8825 | 0 | 40.61% | 0 | 48.7969
4453 | 698 | 948 | 261 | 3.4 | 31.2 | 193.6 | 0 | 66.9878 | 0 | 0 | 0 | 192.3855 | 0 | 69% | 16.325 | 0 | 62.81% | 0 | 48.4084
4454 | 683 | 910 | 262 | 3.2 | 32.7 | 185.9396 | 0 | 62.5736 | 0 | 0 | 0 | 184.8152 | 0 | 84% | 12.0572 | 0 | 79.2% | 0 | 48.3066
4455 | 647 | 811 | 254 | 4.7 | 32.9 | 168.714 | -1.31e-14 | 50.8416 | 1.9547 | 42.5931 | 0.81349 | 128.1678 | 0 | 93% | 7.9372 | 0 | 90% | 0 | 41.1789
4456 | 589 | 656 | 224 | 4.8 | 31.9 | 130.2725 | 18.0223 | 34.1286 | 4.2819 | 42.5939 | 14.1559 | 89.2633 | 0 | 100% | 0 | 0 | 90% | 0 | 47.5816
4457 | 535 | 491 | 183 | 4.6 | 32.4 | 42.1522 | 96.1025 | 22.4021 | 0 | 42.5937 | 14.1092 | 0 | 0 | 100% | 0 | 9.4281 | 74.91% | 0 | 46.6482
4458 | 58 | 154 | 127 | 4.6 | 30.2 | 0 | 13.8243 | 2.1949 | 0 | 57.3843 | 20.4722 | 0 | 55.8901 | 96% | 0 | 25 | 34.91% | 0 | 45.5817
4459 | 19 | 52 | 49 | 4.7 | 26.9 | 0 | 3.4235 | 0 | 0 | 83.2365 | 31.7896 | 0 | 84.9848 | 90% | 0 | 15.5719 | 10% | 0 | 44.4204
4460 | 4 | 9 | 9 | 5.1 | 25.2 | 0 | 0.018905 | 0 | 0 | 112.302 | 44.4146 | 0 | 115.8076 | 81% | 0 | 0 | 10% | 0 | 41.9036
4461 | 0 | 0 | 0 | 3.9 | 24.5 | 0 | 0 | 0 | 0 | 107.1284 | 42.367 | 0 | 107.9805 | 73% | 0 | 0 | 10% | 0 | 40.2557
4462 | 0 | 0 | 0 | 1.8 | 24 | 0 | 0 | 0 | 0 | 101.6156 | 40.1335 | 0 | 100.9922 | 65% | 0 | 0 | 10% | 0 | 38.1317
4463 | 0 | 0 | 0 | 2.4 | 22.7 | 0 | 0 | 0 | 0 | 97.0157 | 38.3477 | 0 | 95.5431 | 58% | 0 | 0 | 10% | 0 | 36.3549
4464 | 0 | 0 | 0 | 1.8 | 24.1 | 0 | 0 | 0 | 0 | 94.7097 | 37.2602 | 0 | 92.9724 | 51% | 0 | 0 | 10% | 0 | 35.2368
4465 | 0 | 0 | 0 | 1.1 | 23.8 | 0 | 0 | 0 | 0 | 92.9977 | 36.5726 | 0 | 91.032 | 44% | 0 | 0 | 10% | 0 | 34.5133
4466 | 0 | 0 | 0 | 1 | 24.1 | 0 | 0 | 0 | 0 | 92.1682 | 36.1941 | 0 | 90.1425 | 37% | 0 | 0 | 10% | 0 | 34.0956
4467 | 0 | 0 | 0 | 0.4 | 23.1 | 0 | 0 | 0 | 0 | 91.9979 | 36.2183 | 0 | 90.0503 | 30% | 0 | 0 | 10% | 0 | 34.0826
4468 | 0 | 0 | 0 | 1.5 | 22.6 | 0 | 0 | 0 | 0 | 93.1514 | 36.751 | 0 | 91.5635 | 23% | 0 | 0 | 10% | 0 | 34.5819
4469 | 0 | 0 | 0 | 0.9 | 21.5 | 0 | 0 | 0 | 0 | 98.0678 | 38.8938 | 0 | 97.4229 | 16% | 0 | 0 | 10% | 0 | 36.6965
4470 | 42 | 46 | 39 | 1.4 | 21.3 | 0 | 6.2753 | 0 | 0 | 105.0546 | 41.829 | 0 | 105.7701 | 8% | 0 | 0 | 10% | 0 | 39.6213
4471 | 246 | 197 | 121 | 0.7 | 24.4 | 0 | 52.5269 | 1.8831 | 0 | 107.4666 | 42.5205 | 0 | 108.4512 | 0% | 0 | 0 | 10% | 0 | 42.2199
4472 | 421 | 391 | 184 | 0.9 | 27.8 | 70.3738 | 17.0554 | 14.867 | 0 | 0 | 0 | 67.9611 | 0 | 5% | 0 | 0 | 10% | 0 | 13.5568
4473 | 511 | 576 | 237 | 3 | 34.1 | 120.3846 | 0 | 30.5553 | 0 | 0 | 0 | 118.5267 | 0 | 14% | 0 | 0 | 10% | 0 | 29.0743
4474 | 521 | 735 | 312 | 4.9 | 35.8 | 129.2116 | 0 | 45.2848 | 0 | 0 | 0 | 127.8495 | 0 | 24% | 0 | 0 | 10% | 0 | 43.7103
4475 | 212 | 625 | 426 | 5.9 | 35.9 | 0 | 53.8501 | 38.3657 | 0 | 0 | 0 | 0 | 0 | 24% | 0 | 0 | 10% | 0 | 37.2489
4476 | 332 | 752 | 421 | 2.7 | 36.6 | 82.2754 | 0 | 49.8363 | 0 | 43.7492 | 6.3586 | 39.2389 | 0 | 27% | 19.5843 | 0 | 36.63% | 0 | 35.1431
4477 | 273 | 703 | 424 | 4.4 | 37.5 | 64.0895 | 0 | 45.8251 | 0 | 45.2369 | 14.6435 | 20.922 | 0 | 28% | 16.2574 | 0 | 58.75% | 0 | 43.1806
4478 | 3 | 232 | 226 | 6.6 | 35.7 | 0 | 0.95811 | 7.6372 | 0 | 42.5528 | 13.779 | 0 | 39.8391 | 25% | 0 | 22.5787 | 22.62% | 0 | 42.7115
4479 | 17 | 336 | 318 | 8.9 | 36.5 | 0 | 5.2785 | 14.3776 | 0 | 62.8494 | 22.2314 | 0 | 59.9253 | 21% | 0 | 7.8868 | 10% | 0 | 42.2465
4480 | 165 | 433 | 310 | 7.4 | 37.7 | 0 | 49.2193 | 21.7091 | 0 | 65.2129 | 22.8487 | 0 | 62.154 | 16% | 0 | 0 | 10% | 0 | 42.2704
4481 | 63 | 204 | 172 | 4.6 | 37.7 | 0 | 17.4579 | 5.9327 | 0 | 102.9614 | 38.6554 | 0 | 103.9815 | 8% | 0 | 0 | 10% | 0 | 42.1942
4482 | 35 | 149 | 134 | 5.6 | 36.6 | 0 | 8.3416 | 2.1819 | 0 | 112.2052 | 42.6007 | 0 | 114.8187 | 0% | 0 | 0 | 10% | 0 | 42.4101
4483 | 1 | 43 | 43 | 6.4 | 29.3 | 0 | 0.18008 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.149
4484 | 0 | 6 | 6 | 4.2 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1296
4485 | 0 | 0 | 0 | 1.5 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1105
4486 | 0 | 0 | 0 | 3.7 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0918
4487 | 0 | 0 | 0 | 2.4 | 27.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0731
4488 | 0 | 0 | 0 | 0.8 | 25.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0552
4489 | 0 | 0 | 0 | 1.4 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0374
4490 | 0 | 0 | 0 | 1.1 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.02
4491 | 0 | 0 | 0 | 1.9 | 26.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0028
4492 | 0 | 0 | 0 | 3.9 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.986
4493 | 0 | 0 | 0 | 1.9 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9698
4494 | 0 | 18 | 18 | 1.4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9537
4495 | 34 | 97 | 85 | 1.1 | 26.1 | 0 | 7.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9377
4496 | 242 | 328 | 210 | 3.4 | 30.9 | 0 | 52.4637 | 11.6647 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.7451
4497 | 262 | 463 | 279 | 3.8 | 32 | 0 | 65.9071 | 22.6914 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 20.7849
4498 | 455 | 695 | 332 | 5.4 | 34.5 | 109.7769 | 0 | 42.4863 | 0.39984 | 0 | 0 | 102.9335 | 0 | 8% | 0 | 0 | 10% | 0 | 41.1164
4499 | 70 | 483 | 411 | 6.6 | 34.7 | 0 | 22.0967 | 26.5876 | 0 | 0 | 0 | 0 | 0 | 8% | 0 | 0 | 10% | 0 | 25.6051
4500 | 299 | 788 | 484 | 5.2 | 35.9 | 58.0699 | 14.2457 | 52.1493 | 0 | 0 | 0 | 55.6186 | 0 | 12% | 10.2583 | 0 | 23.95% | 0 | 40.7083
4501 | 121 | 593 | 462 | 5.1 | 35.8 | 0 | 39.2554 | 36.4659 | 0 | 42.195 | 0 | 0 | 39.0895 | 9% | 10.3524 | 0 | 38.03% | 0 | 24.596
4502 | 33 | 423 | 383 | 5.4 | 35.4 | 0 | 10.5403 | 22.1729 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 17.5191 | 10% | 0 | 37.7674
4503 | 88 | 464 | 384 | 4.1 | 35.3 | 0 | 27.3278 | 24.9408 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 10% | 0 | 23.0316
4504 | 411 | 657 | 353 | 4.2 | 36.6 | 79.1025 | 18.7637 | 37.8591 | 0 | 0 | 0 | 75.8548 | 0 | 15% | 0 | 0 | 10% | 0 | 36.4908
4505 | 239 | 432 | 291 | 5.4 | 36.5 | 0 | 53.055 | 19.147 | 0 | 48.4802 | 6.2797 | 0 | 45.2039 | 11% | 0 | 0 | 10% | 0 | 24.0077
4506 | 79 | 178 | 145 | 3.9 | 34.4 | 0 | 18.8251 | 3.2198 | 0 | 104.7259 | 40.0053 | 0 | 104.9775 | 3% | 0 | 0 | 10% | 0 | 41.1449
4507 | 37 | 78 | 69 | 5 | 32.1 | 0 | 6.658 | 0 | 0 | 42.9303 | 16.6348 | 0 | 43.6159 | 0% | 0 | 0 | 10% | 0 | 14.6646
4508 | 1 | 2 | 2 | 4.8 | 28.2 | 0 | 0.002733 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8926
4509 | 0 | 0 | 0 | 1.6 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8779
4510 | 0 | 0 | 0 | 0.7 | 27.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8635
4511 | 0 | 0 | 0 | 1 | 26.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8494
4512 | 0 | 0 | 0 | 0.9 | 25.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8355
4513 | 0 | 0 | 0 | 1.3 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.822
4514 | 0 | 0 | 0 | 1.8 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8087
4515 | 0 | 0 | 0 | 2.9 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7957
4516 | 0 | 0 | 0 | 1.8 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7829
4517 | 0 | 0 | 0 | 0.7 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7704
4518 | 0 | 23 | 23 | 0.7 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.758
4519 | 2 | 99 | 98 | 0.9 | 21.6 | 0 | 0.42572 | 0.27425 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4715
4520 | 140 | 262 | 190 | 1.7 | 24.2 | 0 | 36.5256 | 8.3618 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 6.6281
4521 | 257 | 392 | 215 | 2.6 | 27.6 | 0 | 63.5279 | 18.286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 16.5659
4522 | 389 | 617 | 297 | 2.7 | 30.3 | 92.8795 | 0 | 37.0339 | 0 | 0 | 0 | 86.7438 | 0 | 7% | 0 | 0 | 10% | 0 | 35.8033
4523 | 577 | 833 | 306 | 3 | 32.6 | 152.3423 | 0 | 56.4485 | 0 | 0 | 0 | 148.1272 | 0 | 18% | 6.2806 | 0 | 18.54% | 0 | 48.3857
4524 | 542 | 872 | 340 | 3 | 33.9 | 145.6352 | -2.98e-14 | 60.3537 | 0 | 42.2843 | 0 | 104.4822 | 0 | 26% | 15.0804 | 0 | 39.05% | 0 | 42.9969
4525 | 661 | 958 | 306 | 5.6 | 34.2 | 180.5912 | 0 | 62.8657 | 3.8272 | 42.4166 | 8.1678 | 139.3112 | 0 | 37% | 23.6716 | 0 | 71.24% | 0 | 45.0527
4526 | 833 | 961 | 177 | 5.7 | 34.2 | 228.6827 | 0 | 49.1593 | 17.2581 | 42.4772 | 13.9004 | 187.2538 | 0 | 51% | 13.7909 | 0 | 90% | 0 | 46.707
4527 | 887 | 880 | 124 | 7.2 | 34.2 | 236.311 | 0 | 34.5642 | 23.7732 | 42.5094 | 13.9109 | 195.0151 | 0 | 66% | 0 | 0 | 90% | 0 | 45.8269
4528 | 903 | 742 | 89 | 4.9 | 34.5 | 232.6333 | 0 | 34.1141 | 9.9176 | 42.5352 | 13.8903 | 191.2915 | 0 | 81% | 0 | 0 | 90% | 0 | 45.3753
4529 | 860 | 561 | 75 | 5.4 | 34.3 | 203.2657 | 2.98e-14 | 25.7594 | 0 | 42.5505 | 13.9147 | 161.8261 | 0 | 93% | 0 | 7.5675 | 77.89% | 0 | 44.8846
4530 | 713 | 342 | 67 | 4.3 | 33.2 | 140.4216 | 0 | 7.2538 | 0 | 42.5591 | 14.0226 | 98.7097 | 0 | 100% | 0 | 22.0571 | 42.6% | 0 | 44.7478
4531 | 426 | 129 | 42 | 4 | 31.8 | 0 | 63.6769 | 0 | 0 | 68.7917 | 25.096 | 0 | 68.919 | 95% | 0 | 20.3754 | 10% | 0 | 43.3687
4532 | 32 | 9 | 6 | 2.2 | 29.5 | 0 | 0.049507 | 0 | 0 | 109.3573 | 42.6564 | 0 | 112.895 | 87% | 0 | 0 | 10% | 0 | 40.0096
4533 | 0 | 0 | 0 | 1.7 | 27.9 | 0 | 0 | 0 | 0 | 103.1343 | 40.3186 | 0 | 103.2686 | 79% | 0 | 0 | 10% | 0 | 38.2112
4534 | 0 | 0 | 0 | 3.9 | 27.2 | 0 | 0 | 0 | 0 | 97.7623 | 38.18 | 0 | 96.5853 | 71% | 0 | 0 | 10% | 0 | 36.1525
4535 | 0 | 0 | 0 | 4.6 | 25.9 | 0 | 0 | 0 | 0 | 94.474 | 36.9749 | 0 | 92.8328 | 64% | 0 | 0 | 10% | 0 | 34.926
4536 | 0 | 0 | 0 | 3.7 | 24.7 | 0 | 0 | 0 | 0 | 92.4992 | 36.2736 | 0 | 90.5688 | 58% | 0 | 0 | 10% | 0 | 34.1843
4537 | 0 | 0 | 0 | 3 | 23.5 | 0 | 0 | 0 | 0 | 91.9615 | 36.1656 | 0 | 90.0599 | 51% | 0 | 0 | 10% | 0 | 34.0293
4538 | 0 | 0 | 0 | 3.5 | 22.7 | 0 | 0 | 0 | 0 | 93.0887 | 36.7158 | 0 | 91.5671 | 44% | 0 | 0 | 10% | 0 | 34.5386
4539 | 0 | 0 | 0 | 2.9 | 22 | 0 | 0 | 0 | 0 | 98.1418 | 38.8813 | 0 | 97.6017 | 36% | 0 | 0 | 10% | 0 | 36.6747
4540 | 0 | 0 | 0 | 1.3 | 20.5 | 0 | 0 | 0 | 0 | 104.7861 | 41.785 | 0 | 105.5137 | 28% | 0 | 0 | 10% | 0 | 39.5761
4541 | 0 | 0 | 0 | 1.3 | 19 | 0 | 0 | 0 | 0 | 110.6528 | 44.3353 | 0 | 112.2212 | 20% | 0 | 0 | 10% | 0 | 42.1551
4542 | 296 | 57 | 21 | 2.3 | 19.8 | 0 | 43.7814 | 0 | 0 | 117.2719 | 47.0057 | 0 | 119.8565 | 11% | 0 | 0 | 10% | 0 | 44.8653
4543 | 674 | 240 | 47 | 1.2 | 23 | 95.5773 | 23.3133 | 0.59877 | 0 | 119.3269 | 47.5443 | 0 | 29.4789 | 9% | 0 | 0 | 10% | 0 | 46.4525
4544 | 827 | 449 | 57 | 0.8 | 25.3 | 184.704 | 0 | 16.3188 | 0 | 85.2011 | 33.1591 | 101.2511 | 0 | 16% | 0 | 0 | 10% | 0 | 47.3095
4545 | 907 | 647 | 62 | 1.4 | 26.8 | 227.8262 | 0 | 35.5985 | 0 | 43.8304 | 15.1104 | 185.5729 | 0 | 30% | 0 | 0 | 10% | 0 | 48.2036
4546 | 940 | 813 | 70 | 2.1 | 28.4 | 250.5346 | 0 | 52.6504 | 0 | 46.8463 | 16.1976 | 205.4855 | 0 | 46% | 17.4438 | 0 | 33.72% | 0 | 48.665
4547 | 960 | 936 | 75 | 2.1 | 29.8 | 265.9496 | 0 | 61.265 | 4.0329 | 42.6056 | 14.3509 | 224.8847 | 0 | 63% | 25 | 0 | 67.72% | 0 | 47.7144
4548 | 966 | 1005 | 78 | 2.9 | 30.6 | 273.404 | 3.91e-14 | 51.5366 | 20.694 | 42.6087 | 14.2799 | 232.1565 | 0 | 80% | 16.3798 | 0 | 90% | 0 | 46.4337
4549 | 978 | 1025 | 77 | 5.3 | 30.8 | 276.4631 | 0 | 33.9197 | 40.4044 | 42.6096 | 14.2621 | 235.0334 | 0 | 98% | 0 | 0 | 90% | 0 | 46.2344
4550 | 968 | 979 | 76 | 6.1 | 30.3 | 72.8758 | 225.4579 | 31.3413 | 38.3153 | 42.6099 | 14.3074 | 31.4179 | 0 | 100% | 0 | 0 | 90% | 0 | 46.1567
4551 | 934 | 873 | 80 | 6 | 30.1 | 42.1516 | 241.4579 | 30.547 | 28.226 | 42.6076 | 14.3247 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.5809
4552 | 881 | 719 | 82 | 6.2 | 29.3 | 42.1572 | 213.7717 | 30.0469 | 13.0811 | 42.6049 | 14.3951 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.1513
4553 | 804 | 531 | 79 | 4.7 | 29.8 | 42.1571 | 173.2394 | 24.5849 | 0 | 42.6023 | 14.3497 | 0 | 0 | 100% | 0 | 5.1277 | 81.8% | 0 | 44.7716
4554 | 680 | 327 | 67 | 5.1 | 28.5 | 42.1573 | 110.2786 | 6.9947 | 0 | 42.5998 | 14.4645 | 0 | 0 | 100% | 0 | 22.3643 | 46.01% | 0 | 44.533
4555 | 428 | 129 | 43 | 4.3 | 27.2 | 0 | 63.8809 | 0 | 0 | 63.1935 | 23.2536 | 0 | 62.5398 | 95% | 0 | 22.508 | 10% | 0 | 43.6684
4556 | 30 | 8 | 6 | 2 | 25.4 | 0 | 0.007108 | 0 | 0 | 109.743 | 43.3394 | 0 | 113.9517 | 87% | 0 | 0 | 10% | 0 | 40.5468
4557 | 0 | 0 | 0 | 0.5 | 24 | 0 | 0 | 0 | 0 | 103.2961 | 40.8333 | 0 | 103.6049 | 79% | 0 | 0 | 10% | 0 | 38.6852
4558 | 0 | 0 | 0 | 1.4 | 23.3 | 0 | 0 | 0 | 0 | 97.917 | 38.6644 | 0 | 96.8354 | 72% | 0 | 0 | 10% | 0 | 36.6142
4559 | 0 | 0 | 0 | 1 | 23.4 | 0 | 0 | 0 | 0 | 94.4531 | 37.2211 | 0 | 92.8522 | 65% | 0 | 0 | 10% | 0 | 35.1567
4560 | 0 | 0 | 0 | 0.8 | 22.5 | 0 | 0 | 0 | 0 | 92.4645 | 36.4672 | 0 | 90.5552 | 58% | 0 | 0 | 10% | 0 | 34.3646
4561 | 0 | 0 | 0 | 1.4 | 21.8 | 0 | 0 | 0 | 0 | 91.5049 | 36.1243 | 0 | 89.5279 | 51% | 0 | 0 | 10% | 0 | 33.9764
4562 | 0 | 0 | 0 | 1 | 21.2 | 0 | 0 | 0 | 0 | 92.4567 | 36.5766 | 0 | 90.8232 | 44% | 0 | 0 | 10% | 0 | 34.3853
4563 | 0 | 0 | 0 | 1.7 | 20.9 | 0 | 0 | 0 | 0 | 98.0486 | 38.9355 | 0 | 97.5452 | 37% | 0 | 0 | 10% | 0 | 36.7109
4564 | 0 | 0 | 0 | 1.3 | 20.6 | 0 | 0 | 0 | 0 | 105.0548 | 41.8873 | 0 | 105.8885 | 29% | 0 | 0 | 10% | 0 | 39.6618
4565 | 0 | 0 | 0 | 1.7 | 21.7 | 0 | 0 | 0 | 0 | 111.9192 | 44.6192 | 0 | 113.7603 | 20% | 0 | 0 | 10% | 0 | 42.4245
4566 | 223 | 51 | 24 | 1.8 | 22.5 | 0 | 32.8515 | 0 | 0 | 117.8864 | 47.0026 | 0 | 120.6 | 11% | 0 | 0 | 10% | 0 | 44.8558
4567 | 597 | 228 | 57 | 2.7 | 24.4 | 82.2648 | 20.1858 | 0.59646 | 0 | 119.7075 | 47.5482 | 0 | 42.7337 | 8% | 0 | 0 | 10% | 0 | 46.5708
4568 | 728 | 428 | 83 | 5.3 | 25.9 | 157.5049 | 0 | 15.7161 | 0 | 87.1003 | 33.8856 | 71.9566 | 0 | 14% | 0 | 0 | 10% | 0 | 47.6752
4569 | 811 | 624 | 100 | 5.9 | 27.8 | 198.8092 | 0 | 34.2441 | 0 | 48.2893 | 16.8538 | 152.305 | 0 | 25% | 0 | 0 | 10% | 0 | 48.8538
4570 | 840 | 785 | 120 | 6.4 | 28.7 | 218.5489 | 0 | 50.6207 | 0 | 46.1165 | 15.8695 | 174.2219 | 0 | 38% | 14.2336 | 0 | 29.36% | 0 | 49.8217
4571 | 864 | 907 | 129 | 6.9 | 29.5 | 233.8985 | 0 | 62.3841 | 0.49511 | 42.6044 | 14.3771 | 192.855 | 0 | 53% | 25 | 0 | 63.36% | 0 | 49.1723
4572 | 862 | 974 | 143 | 6.9 | 30.1 | 239.0192 | 0 | 56.3541 | 13.1042 | 42.6074 | 14.3246 | 197.8565 | 0 | 68% | 19.59 | 0 | 90% | 0 | 48.4294
4573 | 863 | 990 | 147 | 7.3 | 30.6 | 240.5449 | 0 | 36.6321 | 34.2376 | 42.6084 | 14.2798 | 199.2484 | 0 | 82% | 0 | 0 | 90% | 0 | 48.2231
4574 | 858 | 948 | 143 | 7.3 | 31.2 | 235.099 | 0 | 35.3497 | 31.2398 | 42.6089 | 14.2253 | 193.4969 | 0 | 97% | 0 | 0 | 90% | 0 | 48.0589
4575 | 831 | 848 | 139 | 7.3 | 31.7 | 85.1217 | 158.3991 | 32.8383 | 23.5662 | 42.6087 | 14.1793 | 43.5517 | 0 | 100% | 0 | 0 | 90% | 0 | 47.5509
4576 | 784 | 701 | 131 | 7.3 | 31.2 | 42.1517 | 184.1302 | 32.0813 | 9.5682 | 42.6067 | 14.2246 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 47.0149
4577 | 711 | 516 | 114 | 7.3 | 30.6 | 42.1571 | 146.1469 | 23.9669 | 0 | 42.604 | 14.2783 | 0 | 0 | 100% | 0 | 7.2644 | 78.38% | 0 | 46.2187
4578 | 620 | 321 | 83 | 6.7 | 29.7 | 42.1572 | 94.6322 | 7.0523 | 0 | 42.6014 | 14.3583 | 0 | 0 | 100% | 0 | 23.6976 | 40.46% | 0 | 45.8176
4579 | 376 | 126 | 50 | 6.1 | 27.7 | 0 | 54.4709 | 0 | 0 | 74.0948 | 27.8247 | 0 | 74.8053 | 95% | 0 | 19.038 | 10% | 0 | 44.7647
4580 | 23 | 10 | 8 | 4.8 | 25.4 | 0 | 0 | 0 | 0 | 111.9778 | 44.2576 | 0 | 115.6045 | 86% | 0 | 0 | 10% | 0 | 41.7066
4581 | 0 | 0 | 0 | 2.9 | 23.9 | 0 | 0 | 0 | 0 | 105.5854 | 41.7976 | 0 | 105.8782 | 78% | 0 | 0 | 10% | 0 | 39.7672
4582 | 0 | 0 | 0 | 2 | 23.2 | 0 | 0 | 0 | 0 | 99.7982 | 39.4553 | 0 | 98.65 | 70% | 0 | 0 | 10% | 0 | 37.5082
4583 | 0 | 0 | 0 | 1.9 | 23 | 0 | 0 | 0 | 0 | 96.0922 | 37.9373 | 0 | 94.4037 | 63% | 0 | 0 | 10% | 0 | 35.9665
4584 | 0 | 0 | 0 | 2.1 | 22.9 | 0 | 0 | 0 | 0 | 94.3853 | 37.2405 | 0 | 92.5855 | 56% | 0 | 0 | 10% | 0 | 35.2236
4585 | 0 | 0 | 0 | 1.2 | 22 | 0 | 0 | 0 | 0 | 93.1659 | 36.8084 | 0 | 91.2452 | 49% | 0 | 0 | 10% | 0 | 34.7486
4586 | 0 | 0 | 0 | 2.4 | 22.8 | 0 | 0 | 0 | 0 | 94.2107 | 37.1778 | 0 | 92.6581 | 42% | 0 | 0 | 10% | 0 | 35.0745
4587 | 0 | 0 | 0 | 1.7 | 21.9 | 0 | 0 | 0 | 0 | 99.3178 | 39.3773 | 0 | 98.7018 | 35% | 0 | 0 | 10% | 0 | 37.2413
4588 | 0 | 0 | 0 | 1 | 20.6 | 0 | 0 | 0 | 0 | 106.0439 | 42.2956 | 0 | 106.7009 | 27% | 0 | 0 | 10% | 0 | 40.1524
4589 | 0 | 0 | 0 | 0.9 | 20.3 | 0 | 0 | 0 | 0 | 113.6715 | 45.4705 | 0 | 115.5062 | 18% | 0 | 0 | 10% | 0 | 43.3483
4590 | 66 | 44 | 35 | 1.2 | 21.2 | 0 | 9.5246 | 0 | 0 | 121.6884 | 48.6877 | 0 | 124.8103 | 8% | 0 | 0 | 10% | 0 | 46.6052
4591 | 340 | 202 | 102 | 1 | 24.3 | 0 | 61.1988 | 1.6258 | 0 | 108.1171 | 42.9935 | 0 | 110.8086 | 0% | 0 | 0 | 10% | 0 | 42.6437
4592 | 535 | 401 | 146 | 2.1 | 27.5 | 112.5438 | 0 | 15.0476 | 0 | 0 | 0 | 108.7668 | 0 | 8% | 0 | 0 | 10% | 0 | 13.6488
4593 | 643 | 594 | 176 | 3 | 29.4 | 155.7 | 0 | 32.4578 | 0 | 0 | 0 | 153.8907 | 0 | 20% | 0 | 0 | 10% | 0 | 30.6444
4594 | 719 | 762 | 191 | 4.6 | 31.4 | 185.7398 | 0 | 48.794 | 0 | 0 | 0 | 184.2564 | 0 | 34% | 0 | 0 | 10% | 0 | 46.6849
4595 | 734 | 880 | 217 | 5.3 | 32.3 | 196.9628 | 0 | 60.5596 | 0 | 0 | 0 | 195.6807 | 0 | 49% | 9.0596 | 0 | 22.32% | 0 | 49.2584
4596 | 734 | 952 | 241 | 6 | 32.7 | 201.0523 | 2.98e-14 | 67.4368 | 0 | 0 | 0 | 199.8509 | 0 | 64% | 15.9368 | 0 | 43.99% | 0 | 49.1892
4597 | 730 | 967 | 250 | 5.9 | 33.2 | 201.1995 | 2.98e-14 | 68.705 | 0 | 0 | 0 | 200.0439 | 0 | 80% | 17.205 | 0 | 67.39% | 0 | 49.1563
4598 | 689 | 917 | 266 | 6.1 | 33.5 | 185.4988 | 0 | 63.5763 | 0 | 0 | 0 | 184.4488 | 0 | 94% | 12.0763 | 0 | 83.82% | 0 | 49.2778
4599 | 641 | 816 | 264 | 6.8 | 33.8 | 123.3149 | 50.7057 | 51.2115 | 2.1442 | 42.5979 | 1.0912 | 82.6072 | 0 | 100% | 4.5459 | 0 | 90% | 0 | 45.6686
4600 | 555 | 662 | 255 | 7.2 | 33.6 | 41.8199 | 113.9533 | 35.1958 | 3.8592 | 42.5972 | 13.9971 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 49.6703
4601 | 445 | 478 | 222 | 7.1 | 32.9 | 42.1625 | 68.2545 | 22.2814 | 0 | 42.5949 | 14.0628 | 0 | 0 | 100% | 0 | 11.5161 | 71.57% | 0 | 48.5689
4602 | 274 | 279 | 170 | 6.6 | 32 | 0 | 52.298 | 7.0935 | 0 | 51.5295 | 17.8008 | 0 | 49.9957 | 96% | 0 | 25 | 31.57% | 0 | 47.7982
4603 | 75 | 100 | 83 | 6.2 | 29.8 | 0 | 13.4367 | 0 | 0 | 94.5945 | 36.2134 | 0 | 97.9609 | 89% | 0 | 13.4839 | 10% | 0 | 46.7508
4604 | 1 | 8 | 8 | 4.6 | 27.5 | 0 | 0 | 0 | 0 | 116.745 | 45.9597 | 0 | 120.3479 | 80% | 0 | 0 | 10% | 0 | 43.6324
4605 | 0 | 0 | 0 | 5 | 25.8 | 0 | 0 | 0 | 0 | 110.3411 | 43.5395 | 0 | 111.0422 | 72% | 0 | 0 | 10% | 0 | 41.5901
4606 | 0 | 0 | 0 | 4.5 | 24.9 | 0 | 0 | 0 | 0 | 103.781 | 40.941 | 0 | 103.0164 | 64% | 0 | 0 | 10% | 0 | 39.0787
4607 | 0 | 0 | 0 | 3.3 | 24 | 0 | 0 | 0 | 0 | 98.556 | 38.862 | 0 | 96.8643 | 56% | 0 | 0 | 10% | 0 | 36.9952
4608 | 0 | 0 | 0 | 2.1 | 23 | 0 | 0 | 0 | 0 | 96.3521 | 38.0457 | 0 | 94.4568 | 49% | 0 | 0 | 10% | 0 | 36.1345
4609 | 0 | 0 | 0 | 1.9 | 22.8 | 0 | 0 | 0 | 0 | 95.4645 | 37.6966 | 0 | 93.5831 | 42% | 0 | 0 | 10% | 0 | 35.7394
4610 | 0 | 0 | 0 | 1.6 | 22.3 | 0 | 0 | 0 | 0 | 95.8495 | 37.9015 | 0 | 94.1573 | 35% | 0 | 0 | 10% | 0 | 35.9033
4611 | 0 | 0 | 0 | 1.7 | 21.9 | 0 | 0 | 0 | 0 | 101.4384 | 40.2615 | 0 | 100.8146 | 27% | 0 | 0 | 10% | 0 | 38.2242
4612 | 0 | 0 | 0 | 2.2 | 23.4 | 0 | 0 | 0 | 0 | 109.0748 | 43.2826 | 0 | 109.8123 | 19% | 0 | 0 | 10% | 0 | 41.2321
4613 | 0 | 0 | 0 | 2.2 | 24.1 | 0 | 0 | 0 | 0 | 117.0295 | 46.4869 | 0 | 119.0781 | 10% | 0 | 0 | 10% | 0 | 44.4512
4614 | 7 | 41 | 39 | 1.2 | 23.5 | 0 | 0.98866 | 0 | 0 | 124.754 | 49.7139 | 0 | 128.0888 | 0% | 0 | 0 | 10% | 0 | 47.7139
4615 | 104 | 156 | 122 | 1.2 | 26.9 | 0 | 21.9916 | 1.3049 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.44164
4616 | 314 | 373 | 221 | 1.8 | 30 | 48.2516 | 11.92 | 14.2257 | 0 | 0 | 0 | 46.5196 | 0 | 4% | 0 | 0 | 10% | 0 | 13.1501
4617 | 432 | 564 | 280 | 2.7 | 32.1 | 98.7377 | 0 | 30.252 | 0 | 0 | 0 | 96.5435 | 0 | 11% | 0 | 0 | 10% | 0 | 28.9576
4618 | 531 | 731 | 305 | 3.9 | 34.8 | 132.7435 | 0 | 45.6981 | 0 | 0 | 0 | 130.9666 | 0 | 21% | 0 | 0 | 10% | 0 | 44.0855
4619 | 491 | 849 | 397 | 4.6 | 35.6 | 125.8098 | 0 | 56.2729 | 0 | 0 | 0 | 124.5791 | 0 | 31% | 4.7729 | 0 | 16.49% | 0 | 49.9336
4620 | 505 | 895 | 400 | 4.4 | 36.6 | 133.3965 | 0 | 61.375 | 0 | 0 | 0 | 132.0953 | 0 | 41% | 9.875 | 0 | 29.92% | 0 | 49.8521
4621 | 357 | 862 | 500 | 5.7 | 36.5 | 88.4495 | 0 | 58.6996 | 0 | 43.0172 | 2.6144 | 47.8986 | 0 | 44% | 22.1996 | 0 | 60.11% | 0 | 37.4368
4622 | 226 | 698 | 474 | 6.5 | 36.2 | 0 | 59.1019 | 44.6018 | 0 | 44.5898 | 14.5272 | 0 | 41.3594 | 41% | 8.1018 | 0 | 71.13% | 0 | 50.0101
4623 | 19 | 416 | 393 | 6 | 35.2 | 0 | 5.9044 | 19.9522 | 0 | 42.5612 | 13.8308 | 0 | 39.5184 | 38% | 0 | 17.3206 | 43.42% | 0 | 49.144
4624 | 16 | 356 | 341 | 5.9 | 34.4 | 0 | 4.7776 | 15.6394 | 0 | 43.1075 | 14.1396 | 0 | 40.1784 | 35% | 0 | 20.8862 | 10% | 0 | 48.6374
4625 | 3 | 177 | 174 | 6 | 32.8 | 0 | 0.83134 | 4.2879 | 0 | 118.0145 | 45.6625 | 0 | 121.0164 | 26% | 0 | 0 | 10% | 0 | 47.7606
4626 | 5 | 146 | 143 | 5.6 | 31.3 | 0 | 1.1893 | 2.4059 | 0 | 119.157 | 46.3806 | 0 | 121.9294 | 17% | 0 | 0 | 10% | 0 | 46.6857
4627 | 3 | 73 | 72 | 6.1 | 29.7 | 0 | 0.53668 | 0 | 0 | 120.9719 | 47.3688 | 0 | 123.7329 | 7% | 0 | 0 | 10% | 0 | 45.3373
4628 | 0 | 5 | 5 | 3.3 | 28.2 | 0 | 0 | 0 | 0 | 95.5274 | 37.4779 | 0 | 96.3123 | 0% | 0 | 0 | 10% | 0 | 35.5525
4629 | 0 | 0 | 0 | 1.8 | 27.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7697
4630 | 0 | 0 | 0 | 1.4 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7574
4631 | 0 | 0 | 0 | 0.7 | 26.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7453
4632 | 0 | 0 | 0 | 2.3 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7333
4633 | 0 | 0 | 0 | 2.5 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7217
4634 | 0 | 0 | 0 | 2 | 27.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7101
4635 | 0 | 0 | 0 | 1.5 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.699
4636 | 0 | 0 | 0 | 1.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6881
4637 | 0 | 0 | 0 | 1.5 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6773
4638 | 1 | 30 | 30 | 1.4 | 23.3 | 0 | 0.13809 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6667
4639 | 103 | 158 | 126 | 1 | 26.6 | 0 | 21.7427 | 1.4575 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.19858
4640 | 285 | 351 | 210 | 1.5 | 28.9 | 0 | 63.382 | 12.9107 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 11.2664
4641 | 432 | 544 | 260 | 2.4 | 32.1 | 98.6748 | 0 | 28.9423 | 0 | 0 | 0 | 93.2003 | 0 | 7% | 0 | 0 | 10% | 0 | 27.6589
4642 | 529 | 707 | 290 | 2.2 | 33.9 | 133.1074 | 0 | 44.671 | 0 | 0 | 0 | 130.1724 | 0 | 17% | 0 | 0 | 10% | 0 | 43.0557
4643 | 593 | 828 | 303 | 2.4 | 35.4 | 157.3829 | -2.98e-14 | 57.0602 | 0 | 0 | 0 | 155.1409 | 0 | 29% | 10.3265 | 0 | 24.04% | 0 | 44.8802
4644 | 635 | 920 | 307 | 2.6 | 36.4 | 173.8534 | 0 | 63.6287 | 0 | 0 | 0 | 171.9548 | 0 | 43% | 17.8503 | 0 | 48.32% | 0 | 43.7516
4645 | 621 | 939 | 328 | 3.5 | 37 | 170.2763 | 2.98e-14 | 64.7045 | 0 | 0 | 0 | 168.7154 | 0 | 56% | 19.9002 | 0 | 75.39% | 0 | 42.7865
4646 | 666 | 897 | 273 | 3.2 | 36.9 | 181.0538 | -1.15e-14 | 55.3174 | 6.4409 | 0 | 0 | 179.5323 | 0 | 69% | 10.7466 | 0 | 90% | 0 | 42.4215
4647 | 524 | 701 | 249 | 4.8 | 36.5 | 132.9857 | 0 | 44.312 | 0.50292 | 0 | 0 | 131.9406 | 0 | 80% | 0 | 0 | 90% | 0 | 42.607
4648 | 515 | 612 | 235 | 6 | 36.1 | 123.4948 | 0 | 35.2934 | 0 | 42.5412 | 0 | 83.2201 | 0 | 86% | 0 | 9.0494 | 75.52% | 0 | 42.2127
4649 | 406 | 437 | 201 | 5.8 | 35.5 | 85.3137 | 0 | 19.4274 | 0 | 42.5471 | 7.3729 | 44.5246 | 0 | 89% | 0 | 16.4852 | 49.15% | 0 | 41.8077
4650 | 331 | 282 | 154 | 3.9 | 34.9 | 54.9421 | 0 | 6.9195 | 0 | 42.5485 | 13.856 | 14.0392 | 0 | 90% | 0 | 21.7106 | 14.41% | 0 | 41.538
4651 | 132 | 105 | 77 | 2.5 | 32.1 | 0 | 23.5754 | 0 | 0 | 104.6745 | 40.2465 | 0 | 108.0134 | 82% | 0 | 2.7548 | 10% | 0 | 41.2391
4652 | 2 | 8 | 8 | 2 | 29.5 | 0 | 0 | 0 | 0 | 105.9483 | 41.2679 | 0 | 107.4301 | 74% | 0 | 0 | 10% | 0 | 38.96
4653 | 0 | 0 | 0 | 2 | 27 | 0 | 0 | 0 | 0 | 99.7089 | 39.0104 | 0 | 99.2782 | 67% | 0 | 0 | 10% | 0 | 36.8717
4654 | 0 | 0 | 0 | 2.6 | 25.6 | 0 | 0 | 0 | 0 | 93.7102 | 36.69 | 0 | 92.1367 | 60% | 0 | 0 | 10% | 0 | 34.5798
4655 | 0 | 0 | 0 | 2.6 | 24.6 | 0 | 0 | 0 | 0 | 89.9971 | 35.2325 | 0 | 87.6991 | 53% | 0 | 0 | 10% | 0 | 33.0937
4656 | 0 | 0 | 0 | 1.7 | 23.8 | 0 | 0 | 0 | 0 | 87.3374 | 34.1982 | 0 | 84.6825 | 47% | 0 | 0 | 10% | 0 | 32.007
4657 | 0 | 0 | 0 | 0.7 | 22.5 | 0 | 0 | 0 | 0 | 85.6182 | 33.5992 | 0 | 82.8277 | 41% | 0 | 0 | 10% | 0 | 31.35
4658 | 0 | 0 | 0 | 1.6 | 22.8 | 0 | 0 | 0 | 0 | 84.6204 | 33.1579 | 0 | 81.8217 | 34% | 0 | 0 | 10% | 0 | 30.8531
4659 | 0 | 0 | 0 | 1.1 | 22.2 | 0 | 0 | 0 | 0 | 84.0877 | 32.9887 | 0 | 81.3451 | 28% | 0 | 0 | 10% | 0 | 30.6337
4660 | 0 | 0 | 0 | 1.2 | 22.4 | 0 | 0 | 0 | 0 | 83.3196 | 32.6527 | 0 | 80.5735 | 22% | 0 | 0 | 10% | 0 | 30.2546
4661 | 0 | 0 | 0 | 1.3 | 22.1 | 0 | 0 | 0 | 0 | 87.0513 | 34.2346 | 0 | 85.11 | 16% | 0 | 0 | 10% | 0 | 31.7898
4662 | 230 | 48 | 20 | 1.4 | 22.2 | 0 | 31.0238 | 0 | 0 | 93.2518 | 36.834 | 0 | 92.7575 | 9% | 0 | 0 | 10% | 0 | 34.3588
4663 | 645 | 230 | 47 | 1.6 | 25.9 | 89.9949 | 21.8246 | 0.3938 | 0 | 96.5897 | 37.8536 | 8.1593 | 17.7917 | 8% | 0 | 0 | 10% | 0 | 36.5858
4664 | 780 | 435 | 66 | 2.2 | 28.3 | 172.2282 | 0 | 15.6126 | 0 | 65.6144 | 24.2129 | 107.2742 | 0 | 16% | 0 | 0 | 10% | 0 | 37.8301
4665 | 851 | 627 | 79 | 2 | 30.5 | 212.3686 | 0 | 34.0989 | 0 | 47.1067 | 16.1061 | 166.172 | 0 | 29% | 9.0211 | 0 | 22.27% | 0 | 38.8498
4666 | 884 | 779 | 91 | 5.1 | 31.5 | 232.4845 | 0 | 50.6043 | 0 | 47.7284 | 16.2609 | 185.813 | 0 | 42% | 24.5683 | 0 | 55.68% | 0 | 39.7637
4667 | 894 | 888 | 105 | 3.4 | 31.8 | 246.1341 | 0 | 53.6583 | 9.171 | 42.5993 | 14.1669 | 204.4308 | 0 | 58% | 25 | 0 | 89.68% | 0 | 40.1536
4668 | 892 | 964 | 115 | 2.9 | 33.2 | 251.6228 | 0 | 28.0485 | 41.1302 | 42.6036 | 14.0373 | 209.8793 | 0 | 73% | 0.23414 | 0 | 90% | 0 | 39.1056
4669 | 885 | 981 | 122 | 3.1 | 34.1 | 251.0094 | 0 | 27.1396 | 43.0511 | 42.6056 | 13.952 | 209.0845 | 0 | 88% | 0 | 0 | 90% | 0 | 38.3311
4670 | 865 | 930 | 126 | 3.2 | 34.8 | 199.6946 | 47.3872 | 22.4222 | 42.9155 | 42.6067 | 13.8846 | 157.6591 | 0 | 100% | 0 | 0 | 90% | 0 | 38.2901
4671 | 824 | 835 | 131 | 4.2 | 35.3 | 42.1512 | 207.2567 | 23.8962 | 31.0798 | 42.6063 | 13.8356 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.4399
4672 | 767 | 684 | 127 | 4.7 | 35 | 42.1567 | 179.6802 | 24.1024 | 16.1036 | 42.6037 | 13.8643 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.6747
4673 | 693 | 508 | 112 | 4.1 | 34.5 | 45.6169 | 137.6553 | 23.115 | 0 | 46.0061 | 15.2571 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.0732
4674 | 576 | 304 | 86 | 2 | 34 | 42.084 | 84.8694 | 6.6725 | 0 | 42.5987 | 13.9595 | 0 | 0 | 100% | 0 | 18.7846 | 59.95% | 0 | 40.1249
4675 | 335 | 116 | 50 | 2.9 | 30.9 | 0 | 46.805 | 0 | 0 | 53.1152 | 18.5904 | 0 | 51.5836 | 96% | 0 | 25 | 19.95% | 0 | 41.491
4676 | 22 | 8 | 7 | 1.6 | 27.6 | 0 | 0 | 0 | 0 | 93.3837 | 36.1179 | 0 | 96.4129 | 89% | 0 | 6.2154 | 10% | 0 | 39.3771
4677 | 0 | 0 | 0 | 0.6 | 26.5 | 0 | 0 | 0 | 0 | 100.1284 | 39.2401 | 0 | 100.6377 | 82% | 0 | 0 | 10% | 0 | 36.879
4678 | 0 | 0 | 0 | 1.3 | 26.9 | 0 | 0 | 0 | 0 | 94.8346 | 37.0074 | 0 | 93.8576 | 75% | 0 | 0 | 10% | 0 | 34.7905
4679 | 0 | 0 | 0 | 0.8 | 26 | 0 | 0 | 0 | 0 | 90.6701 | 35.3647 | 0 | 88.7703 | 68% | 0 | 0 | 10% | 0 | 33.1516
4680 | 0 | 0 | 0 | 1.1 | 25.5 | 0 | 0 | 0 | 0 | 88.6874 | 34.5881 | 0 | 86.5285 | 61% | 0 | 0 | 10% | 0 | 32.3267
4681 | 0 | 0 | 0 | 1.2 | 25.5 | 0 | 0 | 0 | 0 | 88.0692 | 34.3301 | 0 | 85.9471 | 55% | 0 | 0 | 10% | 0 | 32.0164
4682 | 0 | 0 | 0 | 0.7 | 24.9 | 0 | 0 | 0 | 0 | 89.9498 | 35.1803 | 0 | 88.3489 | 48% | 0 | 0 | 10% | 0 | 32.8209
4683 | 0 | 0 | 0 | 0.9 | 24.2 | 0 | 0 | 0 | 0 | 97.1918 | 38.2766 | 0 | 97.1518 | 41% | 0 | 0 | 10% | 0 | 35.8879
4684 | 0 | 0 | 0 | 1.3 | 24.5 | 0 | 0 | 0 | 0 | 105.1858 | 41.5718 | 0 | 106.6412 | 33% | 0 | 0 | 10% | 0 | 39.202
4685 | 0 | 0 | 0 | 1.4 | 24.2 | 0 | 0 | 0 | 0 | 113.6667 | 45.0898 | 0 | 116.3842 | 24% | 0 | 0 | 10% | 0 | 42.7724
4686 | 141 | 41 | 25 | 1.3 | 24.7 | 0 | 18.5575 | 0 | 0 | 121.1317 | 48.0959 | 0 | 124.959 | 15% | 0 | 0 | 10% | 0 | 45.8515
4687 | 479 | 204 | 69 | 0.8 | 28.2 | 63.2165 | 15.3921 | 0.68051 | 0 | 123.549 | 48.6385 | 0 | 66.0923 | 10% | 0 | 0 | 10% | 0 | 47.8977
4688 | 661 | 405 | 96 | 1.6 | 31 | 143.3486 | 0 | 14.6088 | 0 | 94.1567 | 36.1941 | 48.8832 | 0 | 14% | 0 | 0 | 10% | 0 | 48.9938
4689 | 764 | 601 | 111 | 2.4 | 33.2 | 188.6232 | 0 | 32.4407 | 0 | 56.1323 | 19.6248 | 134.4579 | 0 | 24% | 0 | 0 | 10% | 0 | 49.9032
4690 | 807 | 772 | 136 | 2.9 | 34.6 | 212.1264 | 0 | 49.047 | 0 | 47.4017 | 15.8088 | 166.4913 | 0 | 36% | 12.547 | 0 | 27.06% | 0 | 49.9343
4691 | 841 | 915 | 159 | 3.1 | 35.5 | 230.4112 | 0 | 62.5589 | 0 | 43.9492 | 14.3404 | 188.0252 | 0 | 50% | 24.4253 | 0 | 60.28% | 0 | 49.9204
4692 | 847 | 1020 | 204 | 3.5 | 36.4 | 237.4689 | 0 | 60.729 | 10.9168 | 42.605 | 13.7265 | 196.2852 | 0 | 65% | 21.8512 | 0 | 90% | 0 | 49.9656
4693 | 831 | 1041 | 231 | 7.5 | 36.7 | 230.7321 | 0 | 38.8602 | 33.7189 | 42.6067 | 13.6972 | 189.4628 | 0 | 79% | 0 | 0 | 90% | 0 | 49.9658
4694 | 822 | 948 | 178 | 7.5 | 36.6 | 224.3705 | 0 | 38.6988 | 27.0219 | 42.6075 | 13.7074 | 182.808 | 0 | 93% | 0 | 0 | 90% | 0 | 49.8649
4695 | 808 | 847 | 156 | 7.1 | 36.2 | 138.7661 | 88.3099 | 34.6331 | 21.1002 | 42.6075 | 13.7472 | 96.9922 | 0 | 100% | 0 | 0 | 90% | 0 | 49.0278
4696 | 759 | 690 | 139 | 7.4 | 35.8 | 42.1513 | 176.7055 | 33.8628 | 6.7829 | 42.6063 | 13.7864 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 48.3571
4697 | 633 | 488 | 128 | 6.5 | 35.8 | 42.1566 | 123.9041 | 22.1764 | 0 | 42.6037 | 13.7856 | 0 | 0 | 100% | 0 | 10.7953 | 72.73% | 0 | 47.4651
4698 | 503 | 288 | 98 | 5.7 | 35 | 44.2696 | 61.9647 | 6.4597 | 0 | 44.682 | 14.6795 | 0 | 0 | 100% | 0 | 25 | 32.73% | 0 | 46.8447
4699 | 256 | 108 | 59 | 4.5 | 33.5 | 0 | 45.5525 | 0 | 0 | 89.9554 | 33.7132 | 0 | 93.0388 | 93% | 0 | 14.2047 | 10% | 0 | 45.822
4700 | 16 | 8 | 7 | 2.4 | 30.9 | 0 | 0 | 0 | 0 | 114.5978 | 44.5879 | 0 | 117.2152 | 84% | 0 | 0 | 10% | 0 | 42.3862
4701 | 0 | 0 | 0 | 1.7 | 27.5 | 0 | 0 | 0 | 0 | 107.6445 | 42.2259 | 0 | 107.5206 | 76% | 0 | 0 | 10% | 0 | 40.3736
4702 | 0 | 0 | 0 | 0.7 | 25.9 | 0 | 0 | 0 | 0 | 101.5328 | 39.8931 | 0 | 100.1817 | 68% | 0 | 0 | 10% | 0 | 38.0778
4703 | 0 | 0 | 0 | 0.5 | 25.8 | 0 | 0 | 0 | 0 | 97.1356 | 38.0821 | 0 | 95.1866 | 61% | 0 | 0 | 10% | 0 | 36.2265
4704 | 0 | 0 | 0 | 1.1 | 25.9 | 0 | 0 | 0 | 0 | 95.2251 | 37.2829 | 0 | 93.1899 | 54% | 0 | 0 | 10% | 0 | 35.3661
4705 | 0 | 0 | 0 | 2.8 | 25.2 | 0 | 0 | 0 | 0 | 94.1412 | 36.9122 | 0 | 92.1253 | 47% | 0 | 0 | 10% | 0 | 34.9406
4706 | 0 | 0 | 0 | 5.3 | 23.6 | 0 | 0 | 0 | 0 | 94.6408 | 37.2803 | 0 | 92.8517 | 40% | 0 | 0 | 10% | 0 | 35.2606
4707 | 0 | 0 | 0 | 5.1 | 21.9 | 0 | 0 | 0 | 0 | 100.0599 | 39.6863 | 0 | 99.2915 | 33% | 0 | 0 | 10% | 0 | 37.6241
4708 | 0 | 0 | 0 | 5.5 | 21.4 | 0 | 0 | 0 | 0 | 106.2106 | 42.2941 | 0 | 106.6105 | 24% | 0 | 0 | 10% | 0 | 40.2188
4709 | 0 | 0 | 0 | 4.3 | 21.3 | 0 | 0 | 0 | 0 | 113.9243 | 45.4848 | 0 | 115.5405 | 16% | 0 | 0 | 10% | 0 | 43.4209
4710 | 75 | 37 | 27 | 3.2 | 21.5 | 0 | 9.621 | 0 | 0 | 120.9931 | 48.3737 | 0 | 123.727 | 6% | 0 | 0 | 10% | 0 | 46.3431
4711 | 432 | 199 | 76 | 4.6 | 23.9 | 53.5314 | 13.7388 | 0.65877 | 0 | 122.8655 | 48.8968 | 0 | 73.8268 | 1% | 0 | 0 | 10% | 0 | 48.241
4712 | 629 | 399 | 105 | 6.6 | 26.6 | 131.6183 | 0 | 14.7198 | 0 | 93.1678 | 36.3494 | 38.8271 | 0 | 4% | 0 | 0 | 10% | 0 | 49.3648
4713 | 737 | 595 | 123 | 7 | 28 | 177.563 | 0 | 32.8898 | 0 | 53.5681 | 19.0739 | 126.3016 | 0 | 13% | 0 | 0 | 10% | 0 | 49.9088
4714 | 803 | 763 | 131 | 6.8 | 29.9 | 207.675 | 0 | 49.24 | 0 | 46.1176 | 15.7562 | 163.5744 | 0 | 26% | 12.74 | 0 | 27.33% | 0 | 49.9303
4715 | 833 | 887 | 141 | 7.3 | 30.7 | 224.389 | 0 | 61.6649 | 0 | 43.8595 | 14.7686 | 182.4106 | 0 | 39% | 23.911 | 0 | 59.85% | 0 | 50.031
4716 | 855 | 963 | 142 | 7.2 | 30.7 | 236.5805 | 0 | 60.4948 | 8.6455 | 42.6135 | 14.2724 | 195.6732 | 0 | 54% | 22.1725 | 0 | 90% | 0 | 49.9714
4717 | 874 | 985 | 132 | 6.3 | 31.5 | 244.7514 | 0 | 38.4161 | 32.4846 | 42.6136 | 14.1993 | 203.7246 | 0 | 70% | 0 | 0 | 90% | 0 | 49.8974
4718 | 867 | 941 | 129 | 5.8 | 32 | 239.1953 | 0 | 38.0933 | 28.4504 | 42.6133 | 14.1532 | 197.989 | 0 | 84% | 0 | 0 | 90% | 0 | 49.5636
4719 | 832 | 837 | 127 | 6 | 32.2 | 221.6867 | 0 | 35.1914 | 20.7646 | 42.6128 | 14.1342 | 180.1675 | 0 | 98% | 0 | 0 | 90% | 0 | 48.417
4720 | 756 | 681 | 133 | 6.4 | 31.7 | 73.6368 | 138.8243 | 32.9691 | 7.7089 | 42.6117 | 14.1802 | 32.0891 | 0 | 100% | 0 | 0 | 90% | 0 | 47.7081
4721 | 656 | 493 | 124 | 6.7 | 30.7 | 42.1519 | 130.3749 | 23.1376 | 0 | 42.6094 | 14.2711 | 0 | 0 | 100% | 0 | 8.7277 | 76.04% | 0 | 46.8454
4722 | 523 | 296 | 96 | 6.6 | 29 | 42.1572 | 69.2292 | 6.7982 | 0 | 42.6067 | 14.4224 | 0 | 0 | 100% | 0 | 24.2462 | 37.24% | 0 | 46.1763
4723 | 305 | 114 | 53 | 6.1 | 27.1 | 0 | 54.1582 | 0 | 0 | 78.9458 | 29.946 | 0 | 80.4088 | 94% | 0 | 17.0261 | 10% | 0 | 44.8878
4724 | 12 | 8 | 7 | 5.6 | 24.7 | 0 | 0 | 0 | 0 | 112.2362 | 44.4429 | 0 | 115.3889 | 86% | 0 | 0 | 10% | 0 | 42.0124
4725 | 0 | 0 | 0 | 4.9 | 23.1 | 0 | 0 | 0 | 0 | 105.4296 | 41.8135 | 0 | 105.4998 | 77% | 0 | 0 | 10% | 0 | 39.8316
4726 | 0 | 0 | 0 | 3.7 | 22.2 | 0 | 0 | 0 | 0 | 99.6471 | 39.4855 | 0 | 98.3654 | 70% | 0 | 0 | 10% | 0 | 37.566
4727 | 0 | 0 | 0 | 2.9 | 21.7 | 0 | 0 | 0 | 0 | 95.4307 | 37.7792 | 0 | 93.5688 | 63% | 0 | 0 | 10% | 0 | 35.8276
4728 | 0 | 0 | 0 | 2.8 | 21 | 0 | 0 | 0 | 0 | 93.7429 | 37.1363 | 0 | 91.777 | 56% | 0 | 0 | 10% | 0 | 35.1299
4729 | 0 | 0 | 0 | 2.1 | 20.7 | 0 | 0 | 0 | 0 | 92.7392 | 36.7359 | 0 | 90.7086 | 49% | 0 | 0 | 10% | 0 | 34.6795
4730 | 0 | 0 | 0 | 0.8 | 20.4 | 0 | 0 | 0 | 0 | 93.7345 | 37.1813 | 0 | 92.0788 | 42% | 0 | 0 | 10% | 0 | 35.0775
4731 | 0 | 0 | 0 | 1.3 | 20 | 0 | 0 | 0 | 0 | 99.5979 | 39.6545 | 0 | 99.0459 | 35% | 0 | 0 | 10% | 0 | 37.5139
4732 | 0 | 0 | 0 | 1.4 | 20.2 | 0 | 0 | 0 | 0 | 106.7423 | 42.6172 | 0 | 107.5194 | 26% | 0 | 0 | 10% | 0 | 40.4707
4733 | 0 | 0 | 0 | 2.2 | 19.6 | 0 | 0 | 0 | 0 | 114.1368 | 45.7249 | 0 | 116.0544 | 18% | 0 | 0 | 10% | 0 | 43.6025
4734 | 168 | 45 | 26 | 1.4 | 21.6 | 0 | 20.9809 | 0 | 0 | 121.2317 | 48.4617 | 0 | 124.2479 | 8% | 0 | 0 | 10% | 0 | 46.3824
4735 | 245 | 172 | 112 | 0.7 | 24.1 | 0 | 51.3501 | 1.4154 | 0 | 104.7803 | 41.6721 | 0 | 107.2215 | 0% | 0 | 0 | 10% | 0 | 41.1088
4736 | 171 | 281 | 192 | 1.3 | 25.1 | 0 | 44.3633 | 9.2066 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 7.428
4737 | 641 | 675 | 259 | 1.5 | 28.1 | 127.6682 | 30.4161 | 38.838 | 0 | 0 | 0 | 123.1025 | 0 | 9% | 0 | 0 | 10% | 0 | 37.0677
4738 | 557 | 676 | 234 | 1.2 | 29.8 | 141.6858 | 0 | 43.0012 | 0 | 0 | 0 | 140.3223 | 0 | 20% | 0 | 0 | 10% | 0 | 41.3078
4739 | 842 | 958 | 206 | 3.8 | 30.6 | 230.0076 | 0 | 67.2489 | 0 | 0 | 0 | 227.9468 | 0 | 38% | 15.7489 | 0 | 31.42% | 0 | 48.9875
4740 | 812 | 995 | 216 | 3.9 | 31.3 | 226.255 | 0 | 71.1275 | 0 | 0 | 0 | 224.9979 | 0 | 55% | 20.4403 | 0 | 59.22% | 0 | 48.1628
4741 | 913 | 994 | 111 | 3.9 | 31.9 | 258.4289 | 0 | 72.3532 | 0 | 0 | 0 | 257.051 | 0 | 74% | 22.0117 | 0 | 89.15% | 0 | 47.4712
4742 | 905 | 950 | 108 | 4.4 | 32.5 | 251.6612 | 0 | 52.0585 | 15.6839 | 0 | 0 | 250.4898 | 0 | 94% | 0.62256 | 0 | 90% | 0 | 48.5768
4743 | 852 | 840 | 119 | 5.8 | 32.1 | 84.5511 | 158.1398 | 48.8985 | 7.875 | 0 | 0 | 84.1654 | 0 | 100% | 0 | 0 | 90% | 0 | 47.6025
4744 | 801 | 690 | 115 | 6.1 | 30.9 | 40.5955 | 191.4921 | 41.8922 | 0 | 42.596 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.7065
4745 | 712 | 508 | 111 | 6.1 | 28.8 | 42.1573 | 146.5385 | 24.3385 | 0 | 42.5936 | 14.412 | 0 | 0 | 100% | 0 | 6.3453 | 79.85% | 0 | 45.8045
4746 | 443 | 282 | 111 | 4.9 | 27.4 | 42.1574 | 48.8689 | 6.4796 | 0 | 42.5913 | 14.5581 | 0 | 0 | 100% | 0 | 23.5443 | 42.18% | 0 | 45.2918
4747 | 137 | 77 | 44 | 2.7 | 26.1 | 0 | 24.2721 | 0 | 0 | 69.4844 | 26.0376 | 0 | 69.6818 | 95% | 0 | 20.1104 | 10% | 0 | 44.0694
4748 | 1 | 6 | 6 | 4.4 | 24.8 | 0 | 0 | 0 | 0 | 110.2244 | 43.6052 | 0 | 113.8657 | 86% | 0 | 0 | 10% | 0 | 40.9703
4749 | 0 | 0 | 0 | 3.7 | 23.4 | 0 | 0 | 0 | 0 | 104.187 | 41.2654 | 0 | 104.4449 | 79% | 0 | 0 | 10% | 0 | 39.1767
4750 | 0 | 0 | 0 | 2.3 | 22.8 | 0 | 0 | 0 | 0 | 98.7589 | 39.0618 | 0 | 97.642 | 71% | 0 | 0 | 10% | 0 | 37.0602
4751 | 0 | 0 | 0 | 1.2 | 22.1 | 0 | 0 | 0 | 0 | 94.8624 | 37.51 | 0 | 93.1681 | 64% | 0 | 0 | 10% | 0 | 35.4896
4752 | 0 | 0 | 0 | 0.7 | 21.8 | 0 | 0 | 0 | 0 | 93.0808 | 36.7896 | 0 | 91.1803 | 57% | 0 | 0 | 10% | 0 | 34.7247
4753 | 0 | 0 | 0 | 0.7 | 21.4 | 0 | 0 | 0 | 0 | 92.29 | 36.4895 | 0 | 90.3594 | 50% | 0 | 0 | 10% | 0 | 34.3785
4754 | 0 | 0 | 0 | 1.3 | 20.7 | 0 | 0 | 0 | 0 | 93.3788 | 37.0077 | 0 | 91.8268 | 43% | 0 | 0 | 10% | 0 | 34.8538
4755 | 0 | 0 | 0 | 0.9 | 20.6 | 0 | 0 | 0 | 0 | 98.977 | 39.347 | 0 | 98.4932 | 36% | 0 | 0 | 10% | 0 | 37.1614
4756 | 0 | 0 | 0 | 1 | 20.1 | 0 | 0 | 0 | 0 | 105.7288 | 42.2088 | 0 | 106.5225 | 28% | 0 | 0 | 10% | 0 | 40.0216
4757 | 0 | 0 | 0 | 2.3 | 20.9 | 0 | 0 | 0 | 0 | 113.2492 | 45.2427 | 0 | 115.1841 | 19% | 0 | 0 | 10% | 0 | 43.0821
4758 | 150 | 39 | 23 | 1.6 | 21.7 | 0 | 18.2154 | 0 | 0 | 120.3885 | 48.1067 | 0 | 123.4245 | 10% | 0 | 0 | 10% | 0 | 45.9919
4759 | 515 | 204 | 62 | 1.4 | 23.6 | 68.2127 | 16.8147 | 0.48667 | 0 | 122.6228 | 48.8295 | 0 | 59.6738 | 5% | 0 | 0 | 10% | 0 | 47.8642
4760 | 704 | 408 | 83 | 2 | 26.3 | 153.1289 | 0 | 15.0891 | 0 | 91.6714 | 35.7543 | 61.9985 | 0 | 10% | 0 | 0 | 10% | 0 | 48.9489
4761 | 789 | 601 | 100 | 3.5 | 26.8 | 194.6026 | 0 | 33.5101 | 0 | 52.2559 | 18.6279 | 144.4309 | 0 | 21% | 0 | 0 | 10% | 0 | 49.9269
4762 | 831 | 762 | 115 | 4.1 | 28 | 217.9596 | 0 | 50.1037 | 0 | 45.9416 | 15.8629 | 173.9056 | 0 | 34% | 13.6037 | 0 | 28.5% | 0 | 49.9358
4763 | 874 | 893 | 116 | 5.6 | 29.4 | 238.1097 | 0 | 63.0749 | 0 | 43.0801 | 14.5757 | 196.7052 | 0 | 49% | 24.9514 | 0 | 62.43% | 0 | 50.0732
4764 | 905 | 974 | 110 | 5.7 | 30.9 | 253.0895 | 0 | 58.7744 | 11.9114 | 42.6101 | 14.2532 | 212.0099 | 0 | 65% | 20.2685 | 0 | 90% | 0 | 49.9694
4765 | 919 | 994 | 104 | 5.8 | 31.8 | 258.8077 | 0 | 38.6156 | 33.7777 | 42.611 | 14.1708 | 217.6158 | 0 | 81% | 0 | 0 | 90% | 0 | 49.9236
4766 | 928 | 960 | 95 | 6 | 32.3 | 257.418 | 0 | 37.2797 | 31.3023 | 42.6113 | 14.1244 | 215.9206 | 0 | 97% | 0 | 0 | 90% | 0 | 49.5438
4767 | 919 | 864 | 87 | 5.7 | 32.7 | 78.8704 | 194.7948 | 34.1761 | 24.4834 | 42.611 | 14.0869 | 37.3655 | 0 | 100% | 0 | 0 | 90% | 0 | 48.7686
4768 | 887 | 716 | 81 | 6 | 32.7 | 42.1514 | 216.03 | 33.4062 | 10.1855 | 42.6088 | 14.0861 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 48.201
4769 | 821 | 529 | 73 | 5.7 | 32.4 | 42.1569 | 177.5736 | 25.0408 | 0 | 42.6061 | 14.1133 | 0 | 0 | 100% | 0 | 7.4155 | 78.14% | 0 | 47.2783
4770 | 695 | 321 | 61 | 5.6 | 30.8 | 42.1571 | 112.8326 | 7.0684 | 0 | 42.6034 | 14.26 | 0 | 0 | 100% | 0 | 24.7685 | 38.51% | 0 | 46.806
4771 | 442 | 121 | 38 | 4 | 29.3 | 0 | 65.1667 | 0 | 0 | 79.7628 | 30.021 | 0 | 81.1758 | 94% | 0 | 17.8159 | 10% | 0 | 45.7387
4772 | 23 | 6 | 4 | 3.5 | 27 | 0 | 0 | 0 | 0 | 114.6239 | 45.1527 | 0 | 118.3159 | 85% | 0 | 0 | 10% | 0 | 42.7101
4773 | 0 | 0 | 0 | 3.3 | 24.8 | 0 | 0 | 0 | 0 | 107.5536 | 42.5085 | 0 | 107.7995 | 77% | 0 | 0 | 10% | 0 | 40.5635
4774 | 0 | 0 | 0 | 2.8 | 23.4 | 0 | 0 | 0 | 0 | 101.0586 | 39.96 | 0 | 99.8484 | 69% | 0 | 0 | 10% | 0 | 38.0865
4775 | 0 | 0 | 0 | 1.8 | 22.2 | 0 | 0 | 0 | 0 | 96.7571 | 38.2854 | 0 | 94.9258 | 62% | 0 | 0 | 10% | 0 | 36.3815
4776 | 0 | 0 | 0 | 2.3 | 22 | 0 | 0 | 0 | 0 | 94.7547 | 37.4741 | 0 | 92.7991 | 55% | 0 | 0 | 10% | 0 | 35.5157
4777 | 0 | 0 | 0 | 2 | 23.1 | 0 | 0 | 0 | 0 | 93.9774 | 37.0523 | 0 | 92.0618 | 48% | 0 | 0 | 10% | 0 | 35.0427
4778 | 0 | 0 | 0 | 1.7 | 22.2 | 0 | 0 | 0 | 0 | 94.6922 | 37.4308 | 0 | 93.0332 | 41% | 0 | 0 | 10% | 0 | 35.377
4779 | 0 | 0 | 0 | 2.9 | 21.2 | 0 | 0 | 0 | 0 | 100.323 | 39.8569 | 0 | 99.716 | 34% | 0 | 0 | 10% | 0 | 37.765
4780 | 0 | 0 | 0 | 3.2 | 20.7 | 0 | 0 | 0 | 0 | 106.8609 | 42.6233 | 0 | 107.4653 | 25% | 0 | 0 | 10% | 0 | 40.5231
4781 | 0 | 0 | 0 | 3.5 | 20.4 | 0 | 0 | 0 | 0 | 114.4611 | 45.7885 | 0 | 116.2607 | 17% | 0 | 0 | 10% | 0 | 43.7058
4782 | 152 | 41 | 25 | 2.7 | 20.5 | 0 | 17.9254 | 0 | 0 | 121.9751 | 48.8729 | 0 | 124.9639 | 7% | 0 | 0 | 10% | 0 | 46.8279
4783 | 501 | 204 | 67 | 2.1 | 22.4 | 65.4085 | 16.3059 | 0.69174 | 0 | 124.031 | 49.5332 | 0 | 63.7485 | 2% | 0 | 0 | 10% | 0 | 48.8032
4784 | 658 | 404 | 100 | 3.1 | 26.3 | 141.4121 | 0 | 15.1111 | 0 | 94.0067 | 36.7369 | 47.8356 | 0 | 6% | 0 | 0 | 10% | 0 | 50.0516
4785 | 758 | 603 | 119 | 4.4 | 29.8 | 185.3857 | 0 | 33.2816 | 0 | 53.2648 | 18.7593 | 134.4197 | 0 | 16% | 0 | 0 | 10% | 0 | 49.9125
4786 | 830 | 774 | 125 | 6 | 31.9 | 216.0876 | 0 | 50.2553 | 0 | 46.7515 | 15.8204 | 171.3713 | 0 | 29% | 13.7553 | 0 | 28.71% | 0 | 49.9123
4787 | 843 | 894 | 143 | 6.7 | 32.8 | 227.999 | 0 | 62.3352 | 0 | 43.8586 | 14.5699 | 186.0342 | 0 | 43% | 24.4106 | 0 | 61.91% | 0 | 49.9636
4788 | 837 | 961 | 159 | 8.3 | 32.7 | 230.2353 | 0 | 59.1116 | 9.7167 | 42.6129 | 14.0875 | 189.3444 | 0 | 57% | 20.6576 | 0 | 90% | 0 | 49.9699
4789 | 828 | 975 | 168 | 8.7 | 32.7 | 228.6128 | 0 | 38.4539 | 31.5123 | 42.6129 | 14.0875 | 187.6026 | 0 | 72% | 0 | 0 | 90% | 0 | 49.9699
4790 | 784 | 921 | 186 | 7.9 | 33 | 212.5963 | 0 | 38.3445 | 26.2398 | 42.6125 | 14.0593 | 171.4012 | 0 | 84% | 0 | 0 | 90% | 0 | 49.9712
4791 | 660 | 806 | 240 | 7.4 | 33.1 | 170.8185 | 0 | 37.1998 | 16.5099 | 42.6117 | 14.0495 | 129.3997 | 0 | 94% | 0 | 0 | 90% | 0 | 49.2101
4792 | 493 | 634 | 274 | 7.4 | 32.7 | 116.844 | 0 | 33.0316 | 4.7113 | 42.6104 | 14.0866 | 74.9883 | 0 | 99% | 0 | 0 | 90% | 0 | 48.533
4793 | 349 | 446 | 246 | 7.7 | 31.9 | 50.043 | 26.3806 | 20.8251 | 0 | 42.608 | 14.1606 | 8.2714 | 0 | 100% | 0 | 11.935 | 70.9% | 0 | 47.6073
4794 | 174 | 248 | 178 | 7.1 | 30.8 | 0 | 41.1467 | 6.3093 | 0 | 50.1514 | 17.3462 | 0 | 48.6177 | 96% | 0 | 25 | 30.9% | 0 | 46.5769
4795 | 28 | 81 | 74 | 7.3 | 29.6 | 0 | 4.9361 | 0 | 0 | 92.1708 | 35.2173 | 0 | 95.2235 | 89% | 0 | 13.065 | 10% | 0 | 45.3348
4796 | 0 | 5 | 5 | 6 | 28.2 | 0 | 0 | 0 | 0 | 114.511 | 44.947 | 0 | 117.7659 | 81% | 0 | 0 | 10% | 0 | 42.5932
4797 | 0 | 0 | 0 | 5.7 | 25.9 | 0 | 0 | 0 | 0 | 109.1133 | 43.0237 | 0 | 109.7975 | 72% | 0 | 0 | 10% | 0 | 41.029
4798 | 0 | 0 | 0 | 4.9 | 24.1 | 0 | 0 | 0 | 0 | 102.4567 | 40.4726 | 0 | 101.6009 | 65% | 0 | 0 | 10% | 0 | 38.5688
4799 | 0 | 0 | 0 | 4.3 | 23.7 | 0 | 0 | 0 | 0 | 97.3681 | 38.398 | 0 | 95.6447 | 57% | 0 | 0 | 10% | 0 | 36.4872
4800 | 0 | 0 | 0 | 3.7 | 23.2 | 0 | 0 | 0 | 0 | 94.1928 | 37.1328 | 0 | 92.1272 | 50% | 0 | 0 | 10% | 0 | 35.1788
4801 | 0 | 0 | 0 | 1.4 | 23 | 0 | 0 | 0 | 0 | 92.9837 | 36.6418 | 0 | 90.816 | 43% | 0 | 0 | 10% | 0 | 34.6374
4802 | 0 | 0 | 0 | 0.7 | 23.2 | 0 | 0 | 0 | 0 | 91.9669 | 36.1943 | 0 | 89.7279 | 37% | 0 | 0 | 10% | 0 | 34.143
4803 | 0 | 0 | 0 | 1 | 22.9 | 0 | 0 | 0 | 0 | 92.3096 | 36.3672 | 0 | 90.287 | 30% | 0 | 0 | 10% | 0 | 34.2706
4804 | 0 | 0 | 0 | 1.2 | 23 | 0 | 0 | 0 | 0 | 92.9048 | 36.6101 | 0 | 91.1236 | 23% | 0 | 0 | 10% | 0 | 34.4782
4805 | 0 | 0 | 0 | 1.1 | 23.2 | 0 | 0 | 0 | 0 | 98.3132 | 38.8409 | 0 | 97.5887 | 15% | 0 | 0 | 10% | 0 | 36.6747
4806 | 9 | 29 | 28 | 1 | 22.8 | 0 | 1.0293 | 0 | 0 | 106.0539 | 42.1014 | 0 | 106.8099 | 7% | 0 | 0 | 10% | 0 | 39.9208
4807 | 103 | 148 | 117 | 0.9 | 26.7 | 0 | 21.4675 | 1.0887 | 0 | 95.6114 | 37.6538 | 0 | 96.9574 | 0% | 0 | 0 | 10% | 0 | 36.6075
4808 | 141 | 290 | 221 | 0.6 | 29.6 | 0 | 36.5124 | 10.1566 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 8.19
4809 | 294 | 509 | 311 | 1.8 | 31.6 | 50.9474 | 12.3819 | 26.6064 | 0 | 0 | 0 | 49.1266 | 0 | 4% | 0 | 0 | 10% | 0 | 25.4747
4810 | 511 | 719 | 311 | 4.8 | 33.3 | 126.3199 | 0 | 45.5063 | 0 | 0 | 0 | 123.6344 | 0 | 13% | 0 | 0 | 10% | 0 | 43.9774
4811 | 612 | 840 | 288 | 5.4 | 34 | 161.0638 | 0 | 57.0356 | 0 | 0 | 0 | 159.3265 | 0 | 25% | 9.8055 | 0 | 23.34% | 0 | 45.3694
4812 | 656 | 915 | 280 | 4.7 | 33.9 | 178.79 | 0 | 64.5424 | 0 | 0 | 0 | 177.3445 | 0 | 39% | 18.239 | 0 | 48.14% | 0 | 44.2594
4813 | 673 | 933 | 271 | 5.7 | 33.7 | 184.2137 | 0 | 66.3384 | 0 | 0 | 0 | 182.923 | 0 | 53% | 20.7723 | 0 | 76.39% | 0 | 43.4466
4814 | 662 | 888 | 263 | 6 | 33.4 | 177.7651 | -1.23e-14 | 55.4493 | 6.66 | 0 | 0 | 176.5857 | 0 | 66% | 10.0067 | 0 | 90% | 0 | 43.3516
4815 | 614 | 783 | 257 | 6.3 | 32.7 | 158.0765 | 0 | 45.2548 | 6.6856 | 0 | 0 | 157.0254 | 0 | 78% | 0 | 0 | 90% | 0 | 43.3328
4816 | 536 | 633 | 243 | 6.8 | 31.4 | 128.829 | 0 | 38.0535 | 0 | 42.5869 | 0 | 88.2938 | 0 | 85% | 0 | 0 | 90% | 0 | 35.8876
4817 | 418 | 450 | 212 | 7 | 30.7 | 87.235 | 1.49e-14 | 21.2323 | 0 | 42.5877 | 14.238 | 46.122 | 0 | 88% | 0 | 8.8238 | 75.88% | 0 | 43.0372
4818 | 268 | 258 | 153 | 6.6 | 30.2 | 0 | 50.1979 | 6.3179 | 0 | 42.96 | 14.4573 | 0 | 40.8951 | 85% | 0 | 24.1896 | 37.18% | 0 | 43.2529
4819 | 71 | 84 | 68 | 6.2 | 28.1 | 0 | 12.4822 | 0 | 0 | 75.7106 | 28.488 | 0 | 75.9324 | 79% | 0 | 16.9866 | 10% | 0 | 42.7826
4820 | 1 | 5 | 5 | 5.5 | 25.5 | 0 | 0 | 0 | 0 | 108.7299 | 42.9129 | 0 | 111.791 | 71% | 0 | 0 | 10% | 0 | 40.3341
4821 | 0 | 0 | 0 | 4.9 | 24.8 | 0 | 0 | 0 | 0 | 102.3563 | 40.3578 | 0 | 103.0918 | 63% | 0 | 0 | 10% | 0 | 38.0408
4822 | 0 | 0 | 0 | 2.1 | 24.1 | 0 | 0 | 0 | 0 | 96.316 | 37.9239 | 0 | 95.5735 | 56% | 0 | 0 | 10% | 0 | 35.6973
4823 | 0 | 0 | 0 | 1.2 | 24.5 | 0 | 0 | 0 | 0 | 92.3869 | 36.2451 | 0 | 90.8317 | 49% | 0 | 0 | 10% | 0 | 34.0306
4824 | 0 | 0 | 0 | 0.9 | 25 | 0 | 0 | 0 | 0 | 89.571 | 35.0121 | 0 | 87.4672 | 43% | 0 | 0 | 10% | 0 | 32.7781
4825 | 0 | 0 | 0 | 0.9 | 24.9 | 0 | 0 | 0 | 0 | 87.7229 | 34.2496 | 0 | 85.3604 | 36% | 0 | 0 | 10% | 0 | 31.9804
4826 | 0 | 0 | 0 | 1 | 23.3 | 0 | 0 | 0 | 0 | 86.6161 | 33.9426 | 0 | 84.1629 | 30% | 0 | 0 | 10% | 0 | 31.6338
4827 | 0 | 0 | 0 | 1 | 22.8 | 0 | 0 | 0 | 0 | 86.1444 | 33.7917 | 0 | 83.7182 | 24% | 0 | 0 | 10% | 0 | 31.4444
4828 | 0 | 0 | 0 | 2 | 22.2 | 0 | 0 | 0 | 0 | 85.0607 | 33.3928 | 0 | 82.5375 | 18% | 0 | 0 | 10% | 0 | 31.0124
4829 | 0 | 0 | 0 | 2.6 | 23 | 0 | 0 | 0 | 0 | 88.4668 | 34.7465 | 0 | 86.7056 | 11% | 0 | 0 | 10% | 0 | 32.3262
4830 | 35 | 33 | 28 | 3.6 | 23.7 | 0 | 3.8767 | 0 | 0 | 94.8562 | 37.3635 | 0 | 94.5582 | 4% | 0 | 0 | 10% | 0 | 34.9159
4831 | 274 | 177 | 99 | 3.4 | 24.6 | 0 | 56.9615 | 0.96783 | 0 | 52.1816 | 20.5398 | 0 | 52.2953 | 0% | 0 | 0 | 10% | 0 | 19.1351
4832 | 476 | 374 | 151 | 3.6 | 27.4 | 79.4535 | 19.4214 | 14.0689 | 0 | 0 | 0 | 76.6939 | 0 | 6% | 0 | 0 | 10% | 0 | 12.6376
4833 | 593 | 567 | 184 | 6.1 | 29.2 | 139.6435 | 0 | 31.082 | 0 | 0 | 0 | 137.6502 | 0 | 16% | 0 | 0 | 10% | 0 | 29.4431
4834 | 679 | 735 | 199 | 7.4 | 31 | 172.2149 | 0 | 47.4993 | 0 | 0 | 0 | 170.6023 | 0 | 29% | 4.7262 | 0 | 16.43% | 0 | 40.8273
4835 | 704 | 853 | 220 | 7.4 | 31.4 | 186.6662 | 0 | 59.4633 | 0 | 0 | 0 | 185.2978 | 0 | 43% | 15.7491 | 0 | 37.85% | 0 | 41.6141
4836 | 695 | 926 | 254 | 8.1 | 32.3 | 187.8347 | 0 | 66.2244 | 0 | 0 | 0 | 186.6072 | 0 | 57% | 23.1572 | 0 | 69.34% | 0 | 40.9297
4837 | 617 | 909 | 300 | 8.5 | 32.1 | 165.0635 | 0 | 57.7977 | 6.4846 | 0 | 0 | 163.9876 | 0 | 69% | 15.1911 | 0 | 90% | 0 | 40.6503
4838 | 534 | 892 | 385 | 9.3 | 31.5 | 136.9246 | 0 | 42.5555 | 20.1878 | 0 | 0 | 135.9706 | 0 | 79% | 0 | 0 | 90% | 0 | 40.8482
4839 | 619 | 788 | 258 | 9 | 31 | 157.3565 | 0 | 42.4794 | 10.2547 | 0 | 0 | 156.0728 | 0 | 91% | 0 | 0 | 90% | 0 | 40.5664
4840 | 554 | 636 | 233 | 8.2 | 30.6 | 132.83 | 0 | 38.4595 | 0 | 42.5899 | 0 | 91.7579 | 0 | 98% | 0 | 4.3701 | 83.01% | 0 | 40.7248
4841 | 454 | 459 | 201 | 8.4 | 29.9 | 72.2459 | 30.4594 | 21.8391 | 0 | 42.59 | 13.9691 | 30.3025 | 0 | 100% | 0 | 4.5529 | 75.72% | 0 | 41.1212
4842 | 128 | 173 | 118 | 8.1 | 28.2 | 0 | 30.1966 | 2.7033 | 0 | 47.6488 | 16.5602 | 0 | 46.1208 | 97% | 0 | 25 | 35.72% | 0 | 42.1909
4843 | 27 | 71 | 65 | 7.4 | 25.9 | 0 | 4.733 | 0 | 0 | 79.5186 | 30.3335 | 0 | 80.8504 | 91% | 0 | 16.077 | 10% | 0 | 43.4687
4844 | 0 | 6 | 6 | 5.4 | 24.3 | 0 | 0 | 0 | 0 | 110.7533 | 43.8773 | 0 | 114.0673 | 82% | 0 | 0 | 10% | 0 | 41.3406
4845 | 0 | 0 | 0 | 5.5 | 23.8 | 0 | 0 | 0 | 0 | 103.4586 | 40.9216 | 0 | 103.715 | 74% | 0 | 0 | 10% | 0 | 38.793
4846 | 0 | 0 | 0 | 4.6 | 23.5 | 0 | 0 | 0 | 0 | 97.5459 | 38.4917 | 0 | 96.3949 | 67% | 0 | 0 | 10% | 0 | 36.4414
4847 | 0 | 0 | 0 | 2.3 | 23.7 | 0 | 0 | 0 | 0 | 93.4589 | 36.7763 | 0 | 91.6552 | 60% | 0 | 0 | 10% | 0 | 34.7105
4848 | 0 | 0 | 0 | 1.5 | 23.5 | 0 | 0 | 0 | 0 | 91.2538 | 35.8659 | 0 | 89.0997 | 53% | 0 | 0 | 10% | 0 | 33.7573
4849 | 0 | 0 | 0 | 2.4 | 23.8 | 0 | 0 | 0 | 0 | 90.4776 | 35.5115 | 0 | 88.3197 | 47% | 0 | 0 | 10% | 0 | 33.3522
4850 | 0 | 0 | 0 | 2.7 | 23.1 | 0 | 0 | 0 | 0 | 91.5134 | 36.0138 | 0 | 89.7186 | 40% | 0 | 0 | 10% | 0 | 33.8081
4851 | 0 | 0 | 0 | 2.4 | 22.6 | 0 | 0 | 0 | 0 | 99.0549 | 39.2048 | 0 | 98.8015 | 32% | 0 | 0 | 10% | 0 | 36.9596
4852 | 0 | 0 | 0 | 2.3 | 22.4 | 0 | 0 | 0 | 0 | 106.3787 | 42.2721 | 0 | 107.4847 | 24% | 0 | 0 | 10% | 0 | 40.0313
4853 | 0 | 0 | 0 | 1.3 | 22.7 | 0 | 0 | 0 | 0 | 115.6786 | 46.0768 | 0 | 118.2879 | 15% | 0 | 0 | 10% | 0 | 43.8661
4854 | 51 | 31 | 24 | 1 | 22.4 | 0 | 5.4624 | 0 | 0 | 124.4919 | 49.7218 | 0 | 128.5486 | 6% | 0 | 0 | 10% | 0 | 47.566
4855 | 369 | 187 | 86 | 2.1 | 25.6 | 0 | 65.6963 | 0.91318 | 0 | 72.0974 | 28.6107 | 0 | 74.4444 | 0% | 0 | 0 | 10% | 0 | 27.5614
4856 | 535 | 381 | 135 | 4.7 | 27.7 | 109.9028 | 0 | 14.3953 | 0 | 0 | 0 | 106.1483 | 0 | 8% | 0 | 0 | 10% | 0 | 13.0215
4857 | 631 | 573 | 172 | 7 | 30.5 | 148.8409 | 0 | 31.8101 | 0 | 0 | 0 | 147.0363 | 0 | 19% | 0 | 0 | 10% | 0 | 30.0617
4858 | 680 | 734 | 204 | 7.7 | 31.5 | 172.0888 | 0 | 47.9123 | 0 | 0 | 0 | 170.6309 | 0 | 32% | 0 | 0 | 10% | 0 | 45.9327
4859 | 691 | 849 | 233 | 7.6 | 32.5 | 182.508 | 0 | 59.3422 | 0 | 0 | 0 | 181.2128 | 0 | 46% | 7.8422 | 0 | 20.66% | 0 | 49.4002
4860 | 723 | 927 | 233 | 7.7 | 33.6 | 196.4424 | 0 | 66.6972 | 0 | 0 | 0 | 195.1618 | 0 | 61% | 15.1972 | 0 | 41.33% | 0 | 49.2436
4861 | 734 | 944 | 227 | 8.3 | 34.2 | 200.4265 | -2.98e-14 | 68.1071 | 0 | 0 | 0 | 199.2306 | 0 | 76% | 16.6071 | 0 | 63.92% | 0 | 49.1752
4862 | 717 | 900 | 227 | 9.2 | 34.2 | 191.6089 | 0 | 63.7208 | 0 | 0 | 0 | 190.5055 | 0 | 91% | 12.2208 | 0 | 80.54% | 0 | 49.2294
4863 | 668 | 793 | 225 | 8 | 33.7 | 163.2225 | 11.1193 | 52.0321 | 1.2694 | 42.5957 | 0.73973 | 122.4279 | 0 | 100% | 6.9563 | 0 | 90% | 0 | 43.3288
4864 | 586 | 640 | 217 | 8.2 | 32.4 | 41.7905 | 123.5621 | 35.5144 | 3.3039 | 42.596 | 14.11 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 50.0824
4865 | 490 | 462 | 187 | 7.6 | 32.1 | 42.163 | 81.2185 | 21.9932 | 0 | 42.5937 | 14.1373 | 0 | 0 | 100% | 0 | 13.1917 | 68.89% | 0 | 50.031
4866 | 321 | 266 | 144 | 7.8 | 30.3 | 0 | 62.6915 | 6.56 | 0 | 56.5115 | 20.0921 | 0 | 55.0063 | 96% | 0 | 25 | 28.89% | 0 | 49.554
4867 | 93 | 90 | 70 | 6.9 | 27.9 | 0 | 16.2526 | 0 | 0 | 100.0872 | 38.7949 | 0 | 104.2554 | 88% | 0 | 11.8083 | 10% | 0 | 47.6587
4868 | 0 | 5 | 5 | 5.5 | 26.1 | 0 | 0 | 0 | 0 | 118.8459 | 46.9956 | 0 | 122.5708 | 79% | 0 | 0 | 10% | 0 | 44.7334
4869 | 0 | 0 | 0 | 4.3 | 25.6 | 0 | 0 | 0 | 0 | 111.728 | 44.1324 | 0 | 112.4254 | 71% | 0 | 0 | 10% | 0 | 42.2378
4870 | 0 | 0 | 0 | 3.4 | 25.5 | 0 | 0 | 0 | 0 | 105.3736 | 41.5384 | 0 | 104.7186 | 63% | 0 | 0 | 10% | 0 | 39.7242
4871 | 0 | 0 | 0 | 1.2 | 24.9 | 0 | 0 | 0 | 0 | 100.8934 | 39.7388 | 0 | 99.4023 | 55% | 0 | 0 | 10% | 0 | 37.9219
4872 | 0 | 0 | 0 | 1.2 | 24.2 | 0 | 0 | 0 | 0 | 98.3547 | 38.7581 | 0 | 96.5605 | 48% | 0 | 0 | 10% | 0 | 36.9042
4873 | 0 | 0 | 0 | 2 | 23.8 | 0 | 0 | 0 | 0 | 97.0045 | 38.239 | 0 | 95.1371 | 40% | 0 | 0 | 10% | 0 | 36.342
4874 | 0 | 0 | 0 | 3 | 23.3 | 0 | 0 | 0 | 0 | 97.9593 | 38.6836 | 0 | 96.3817 | 33% | 0 | 0 | 10% | 0 | 36.744
4875 | 0 | 0 | 0 | 2.4 | 23.2 | 0 | 0 | 0 | 0 | 103.621 | 41.051 | 0 | 103.1684 | 25% | 0 | 0 | 10% | 0 | 39.0738
4876 | 0 | 0 | 0 | 2.7 | 23.3 | 0 | 0 | 0 | 0 | 110.4879 | 43.8744 | 0 | 111.1827 | 17% | 0 | 0 | 10% | 0 | 41.8871
4877 | 0 | 0 | 0 | 2.5 | 22.8 | 0 | 0 | 0 | 0 | 118.0602 | 47.0442 | 0 | 120.0096 | 7% | 0 | 0 | 10% | 0 | 45.0684
4878 | 58 | 34 | 27 | 2.3 | 22.7 | 0 | 5.9974 | 0 | 0 | 94.4494 | 37.7176 | 0 | 97.0005 | 0% | 0 | 0 | 10% | 0 | 35.8316
4879 | 324 | 181 | 92 | 2.6 | 25.2 | 0 | 56.1697 | 1.0657 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.63648
4880 | 536 | 381 | 135 | 2.7 | 29 | 111.5096 | 0 | 14.3761 | 0 | 0 | 0 | 107.5019 | 0 | 8% | 0 | 0 | 10% | 0 | 12.9832
4881 | 661 | 579 | 162 | 4.1 | 31.7 | 159.33 | 0 | 32.3289 | 0 | 0 | 0 | 157.3229 | 0 | 20% | 0 | 0 | 10% | 0 | 30.4786
4882 | 731 | 749 | 179 | 5.3 | 33.3 | 188.6648 | -2.98e-14 | 48.928 | 0 | 0 | 0 | 187.1011 | 0 | 35% | 0 | 0 | 10% | 0 | 46.7858
4883 | 772 | 875 | 188 | 5.5 | 34.6 | 208.1203 | 0 | 60.5231 | 0 | 0 | 0 | 206.7255 | 0 | 51% | 9.0231 | 0 | 22.27% | 0 | 49.1473
4884 | 783 | 947 | 199 | 6.9 | 35.3 | 215.0463 | 0 | 67.2992 | 0 | 0 | 0 | 213.7825 | 0 | 67% | 15.7992 | 0 | 43.76% | 0 | 49.0469
4885 | 799 | 968 | 192 | 8 | 35.6 | 220.2634 | 0 | 69.1331 | 0 | 0 | 0 | 219.0448 | 0 | 84% | 17.6331 | 0 | 67.74% | 0 | 48.9601
4886 | 790 | 936 | 198 | 7.8 | 35.9 | 214.4056 | 4.93e-16 | 64.2636 | 1.4097 | 42.5935 | 0.93028 | 173.9742 | 0 | 97% | 16.3681 | 0 | 90% | 0 | 45.8375
4887 | 699 | 819 | 223 | 7.5 | 35.9 | 81.569 | 120.0984 | 36.7487 | 18.1987 | 42.5957 | 13.7732 | 40.468 | 0 | 100% | 0 | 0 | 90% | 0 | 50.0149
4888 | 160 | 417 | 298 | 7.1 | 35 | 0 | 47.8136 | 21.3689 | 0 | 42.5934 | 13.861 | 0 | 41.1021 | 97% | 0 | 16.8136 | 63.1% | 0 | 49.9652
4889 | 149 | 280 | 203 | 6.3 | 34.1 | 0 | 41.1678 | 10.9748 | 0 | 49.8037 | 16.8439 | 0 | 48.1433 | 93% | 0 | 25 | 23.1% | 0 | 49.904
4890 | 461 | 288 | 116 | 6.6 | 34 | 66.8165 | 16.3881 | 6.9856 | 0 | 95.4384 | 36.0167 | 3.9418 | 37.155 | 91% | 0 | 8.1864 | 10% | 0 | 49.6741
4891 | 183 | 99 | 62 | 6.1 | 32.1 | 0 | 31.8774 | 0 | 0 | 126.4732 | 49.2115 | 0 | 131.7224 | 81% | 0 | 0 | 10% | 0 | 47.88
4892 | 2 | 5 | 5 | 4.6 | 28.6 | 0 | 0 | 0 | 0 | 118.1355 | 46.3741 | 0 | 119.6544 | 72% | 0 | 0 | 10% | 0 | 44.5532
4893 | 0 | 0 | 0 | 4 | 26.5 | 0 | 0 | 0 | 0 | 112.109 | 44.1814 | 0 | 111.9757 | 63% | 0 | 0 | 10% | 0 | 42.4875
4894 | 0 | 0 | 0 | 2.6 | 25.6 | 0 | 0 | 0 | 0 | 105.4115 | 41.5428 | 0 | 104.1825 | 55% | 0 | 0 | 10% | 0 | 39.8665
4895 | 0 | 0 | 0 | 1.4 | 24.9 | 0 | 0 | 0 | 0 | 101.2865 | 39.9024 | 0 | 99.423 | 48% | 0 | 0 | 10% | 0 | 38.1949
4896 | 0 | 0 | 0 | 1 | 24.2 | 0 | 0 | 0 | 0 | 98.6882 | 38.8967 | 0 | 96.5674 | 40% | 0 | 0 | 10% | 0 | 37.1397
4897 | 0 | 0 | 0 | 1.6 | 23.7 | 0 | 0 | 0 | 0 | 97.5319 | 38.4675 | 0 | 95.4055 | 33% | 0 | 0 | 10% | 0 | 36.6585
4898 | 0 | 0 | 0 | 1.9 | 24.1 | 0 | 0 | 0 | 0 | 98.0422 | 38.64 | 0 | 96.1553 | 26% | 0 | 0 | 10% | 0 | 36.7829
4899 | 0 | 0 | 0 | 2.4 | 23.8 | 0 | 0 | 0 | 0 | 103.8325 | 41.0803 | 0 | 103.1086 | 18% | 0 | 0 | 10% | 0 | 39.1771
4900 | 0 | 0 | 0 | 2.4 | 23.5 | 0 | 0 | 0 | 0 | 110.0326 | 43.6671 | 0 | 110.3515 | 9% | 0 | 0 | 10% | 0 | 41.7456
4901 | 0 | 0 | 0 | 2.5 | 24.1 | 0 | 0 | 0 | 0 | 117.9062 | 46.8458 | 0 | 119.5651 | 0% | 0 | 0 | 10% | 0 | 44.9228
4902 | 55 | 30 | 23 | 2.3 | 23.8 | 0 | 5.4811 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7155
4903 | 412 | 188 | 77 | 2.6 | 26.5 | 50.482 | 12.6055 | 0.63298 | 0 | 0 | 0 | 48.666 | 0 | 4% | 0 | 0 | 10% | 0 | -0.45925
4904 | 618 | 391 | 110 | 3.5 | 29.6 | 130.8922 | 0 | 14.7782 | 0 | 0 | 0 | 128.0891 | 0 | 14% | 0 | 0 | 10% | 0 | 13.1976
4905 | 738 | 592 | 128 | 4.7 | 32.3 | 179.5648 | 0 | 33.1728 | 0 | 0 | 0 | 177.6802 | 0 | 27% | 0 | 0 | 10% | 0 | 31.1289
4906 | 790 | 759 | 144 | 5 | 33.3 | 205.6519 | -2.98e-14 | 49.3851 | 0 | 0 | 0 | 204.1401 | 0 | 43% | 0 | 0 | 10% | 0 | 47.0722
4907 | 814 | 882 | 159 | 6 | 34 | 220.0771 | 0 | 61.6423 | 0 | 0 | 0 | 218.7255 | 0 | 60% | 10.1423 | 0 | 23.79% | 0 | 49.0171
4908 | 830 | 955 | 163 | 6.3 | 34.6 | 229.7661 | 0 | 68.6394 | 0 | 0 | 0 | 228.4923 | 0 | 77% | 17.1394 | 0 | 47.1% | 0 | 48.8858
4909 | 849 | 976 | 155 | 6.8 | 35 | 236.5455 | 0 | 70.6568 | 0 | 0 | 0 | 235.3209 | 0 | 95% | 19.1568 | 0 | 73.16% | 0 | 48.7781
4910 | 849 | 934 | 145 | 6.6 | 35.1 | 62.3494 | 189.3786 | 63.1357 | 3.3907 | 0 | 0 | 62.0418 | 0 | 100% | 12.385 | 0 | 90% | 0 | 49.6475
4911 | 822 | 833 | 139 | 5.8 | 35.2 | 40.5062 | 208.3622 | 51.2524 | 5.1187 | 42.592 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 50.0045
4912 | 780 | 686 | 129 | 6.4 | 34.8 | 42.1591 | 183.3567 | 36.4747 | 5.3384 | 42.5895 | 13.0145 | 0 | 0 | 100% | 0.58455 | 0.49686 | 90% | 0 | 50.0785
4913 | 712 | 504 | 111 | 6 | 34.5 | 42.1567 | 146.0773 | 24.2262 | 0 | 42.5877 | 13.9075 | 0 | 0 | 100% | 0 | 11.2444 | 72.01% | 0 | 50.0862
4914 | 568 | 298 | 88 | 6.1 | 33.3 | 49.9897 | 69.719 | 6.9728 | 0 | 50.2707 | 17.1241 | 0 | 0 | 100% | 0 | 25 | 32.01% | 0 | 49.7691
4915 | 262 | 100 | 50 | 4.5 | 31.5 | 0 | 45.4833 | 0 | 0 | 94.4689 | 35.9245 | 0 | 97.9442 | 93% | 0 | 13.7556 | 10% | 0 | 47.5939
4916 | 4 | 4 | 4 | 3.7 | 28.8 | 0 | 0 | 0 | 0 | 119.8619 | 47.0477 | 0 | 123.3479 | 84% | 0 | 0 | 10% | 0 | 44.886
4917 | 0 | 0 | 0 | 2.9 | 27 | 0 | 0 | 0 | 0 | 112.7657 | 44.3896 | 0 | 113.0339 | 75% | 0 | 0 | 10% | 0 | 42.6393
4918 | 0 | 0 | 0 | 1.5 | 26.1 | 0 | 0 | 0 | 0 | 105.6807 | 41.5958 | 0 | 104.6078 | 67% | 0 | 0 | 10% | 0 | 39.8999
4919 | 0 | 0 | 0 | 2.2 | 25.9 | 0 | 0 | 0 | 0 | 100.7782 | 39.5808 | 0 | 98.9366 | 59% | 0 | 0 | 10% | 0 | 37.8544
4920 | 0 | 0 | 0 | 3.1 | 25.9 | 0 | 0 | 0 | 0 | 98.5472 | 38.656 | 0 | 96.546 | 52% | 0 | 0 | 10% | 0 | 36.8698
4921 | 0 | 0 | 0 | 2 | 24.8 | 0 | 0 | 0 | 0 | 96.7228 | 38.0208 | 0 | 94.6253 | 45% | 0 | 0 | 10% | 0 | 36.1786
4922 | 0 | 0 | 0 | 2.5 | 25.2 | 0 | 0 | 0 | 0 | 97.0508 | 38.1143 | 0 | 95.181 | 37% | 0 | 0 | 10% | 0 | 36.2187
4923 | 0 | 0 | 0 | 2.3 | 24.6 | 0 | 0 | 0 | 0 | 101.862 | 40.1749 | 0 | 100.9603 | 30% | 0 | 0 | 10% | 0 | 38.2322
4924 | 0 | 0 | 0 | 2.1 | 24.4 | 0 | 0 | 0 | 0 | 107.1538 | 42.3901 | 0 | 107.2314 | 21% | 0 | 0 | 10% | 0 | 40.4283
4925 | 0 | 0 | 0 | 2.7 | 24 | 0 | 0 | 0 | 0 | 113.8999 | 45.2091 | 0 | 115.0549 | 13% | 0 | 0 | 10% | 0 | 43.2482
4926 | 57 | 29 | 23 | 2.9 | 24.4 | 0 | 5.4645 | 0 | 0 | 121.9703 | 48.4739 | 0 | 124.4941 | 3% | 0 | 0 | 10% | 0 | 46.5302
4927 | 409 | 186 | 76 | 1.4 | 27.2 | 50.3158 | 12.4275 | 0.57851 | 0 | 90.7122 | 34.9127 | 0 | 40.4659 | 0% | 0 | 0 | 10% | 0 | 34.2733
4928 | 634 | 391 | 105 | 2 | 30.1 | 135.4758 | 2.98e-14 | 14.8097 | 0 | 95.8766 | 37.0287 | 39.3028 | 0 | 3% | 0 | 0 | 10% | 0 | 50.0953
4929 | 766 | 594 | 114 | 3.8 | 31.8 | 187.8721 | 2.98e-14 | 33.3028 | 0 | 53.8269 | 18.7838 | 136.4176 | 0 | 13% | 0 | 0 | 10% | 0 | 49.9386
4930 | 844 | 770 | 117 | 4.8 | 32.6 | 221.2092 | 0 | 50.7791 | 0 | 47.0156 | 15.857 | 176.2902 | 0 | 27% | 14.2791 | 0 | 29.42% | 0 | 49.9054
4931 | 890 | 902 | 116 | 5.1 | 33.5 | 243.6031 | 0 | 63.6252 | 0.37126 | 42.6159 | 14.0127 | 202.8234 | 0 | 42% | 25 | 0 | 63.42% | 0 | 49.9681
4932 | 903 | 973 | 117 | 4.9 | 34.3 | 253.286 | 0 | 58.3624 | 12.6349 | 42.6158 | 13.936 | 212.4128 | 0 | 58% | 19.5444 | 0 | 90% | 0 | 49.9662
4933 | 902 | 985 | 116 | 5.1 | 34.8 | 254.3152 | 0 | 38.8952 | 33.1243 | 42.6155 | 13.8875 | 213.3387 | 0 | 74% | 0 | 0 | 90% | 0 | 49.9655
4934 | 898 | 943 | 112 | 5.5 | 34.9 | 249.1466 | 0 | 38.8733 | 28.935 | 42.6149 | 13.8777 | 207.9157 | 0 | 90% | 0 | 0 | 90% | 0 | 49.9657
4935 | 865 | 838 | 112 | 6 | 35 | 179.8124 | 60.2288 | 35.9468 | 21.3189 | 42.6139 | 13.8676 | 138.2212 | 0 | 100% | 0 | 0 | 90% | 0 | 50.0454
4936 | 780 | 677 | 122 | 5.2 | 34.1 | 42.1513 | 183.5808 | 35.0219 | 6.418 | 42.6125 | 13.9543 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 49.6845
4937 | 685 | 488 | 111 | 4.2 | 33.6 | 42.1568 | 138.735 | 23.3962 | 0 | 42.6098 | 14.0012 | 0 | 0 | 100% | 0 | 10.2799 | 73.55% | 0 | 48.3857
4938 | 517 | 283 | 93 | 3.8 | 32.8 | 45.6029 | 63.2122 | 6.6292 | 0 | 45.9986 | 15.426 | 0 | 0 | 100% | 0 | 25 | 33.55% | 0 | 47.7569
4939 | 248 | 98 | 52 | 4 | 30.8 | 0 | 42.8989 | 0 | 0 | 89.6007 | 33.9577 | 0 | 92.556 | 93% | 0 | 14.7201 | 10% | 0 | 46.5877
4940 | 5 | 5 | 5 | 3.1 | 28.4 | 0 | 0 | 0 | 0 | 116.5933 | 45.7751 | 0 | 119.6975 | 84% | 0 | 0 | 10% | 0 | 43.5535
4941 | 0 | 0 | 0 | 2.3 | 27 | 0 | 0 | 0 | 0 | 109.9835 | 43.2471 | 0 | 110.1159 | 76% | 0 | 0 | 10% | 0 | 41.4203
4942 | 0 | 0 | 0 | 1.3 | 25.9 | 0 | 0 | 0 | 0 | 103.3044 | 40.6299 | 0 | 102.1104 | 68% | 0 | 0 | 10% | 0 | 38.8555
4943 | 0 | 0 | 0 | 1.6 | 24.4 | 0 | 0 | 0 | 0 | 98.8104 | 38.9251 | 0 | 96.9477 | 61% | 0 | 0 | 10% | 0 | 37.1169
4944 | 0 | 0 | 0 | 1.6 | 23 | 0 | 0 | 0 | 0 | 96.3649 | 38.0502 | 0 | 94.3153 | 53% | 0 | 0 | 10% | 0 | 36.1836
4945 | 0 | 0 | 0 | 1 | 22 | 0 | 0 | 0 | 0 | 94.9943 | 37.5734 | 0 | 92.9261 | 46% | 0 | 0 | 10% | 0 | 35.6504
4946 | 0 | 0 | 0 | 0.7 | 21.3 | 0 | 0 | 0 | 0 | 95.1475 | 37.6967 | 0 | 93.2655 | 39% | 0 | 0 | 10% | 0 | 35.7231
4947 | 0 | 0 | 0 | 0.3 | 20.8 | 0 | 0 | 0 | 0 | 101.282 | 40.291 | 0 | 100.5717 | 32% | 0 | 0 | 10% | 0 | 38.2698
4948 | 0 | 0 | 0 | 1.4 | 20.6 | 0 | 0 | 0 | 0 | 107.4479 | 42.8736 | 0 | 107.8649 | 23% | 0 | 0 | 10% | 0 | 40.8394
4949 | 0 | 0 | 0 | 0.8 | 19.4 | 0 | 0 | 0 | 0 | 114.115 | 45.7336 | 0 | 115.5756 | 15% | 0 | 0 | 10% | 0 | 43.711
4950 | 144 | 35 | 18 | 0.5 | 20.4 | 0 | 13.2541 | 0 | 0 | 122.0932 | 48.9312 | 0 | 124.8598 | 5% | 0 | 0 | 10% | 0 | 46.9351
4951 | 561 | 200 | 55 | 0.7 | 24.3 | 74.132 | 18.139 | 0.31729 | 0 | 125.7152 | 50.0206 | 0 | 57.1754 | 1% | 0 | 0 | 10% | 0 | 48.843
4952 | 731 | 407 | 81 | 1.3 | 27.4 | 159.1207 | 0 | 15.699 | 0 | 93.1066 | 36.2267 | 66.9214 | 0 | 6% | 0 | 0 | 10% | 0 | 49.9706
4953 | 778 | 616 | 134 | 3.7 | 29.6 | 191.1432 | 0 | 35.8857 | 0 | 47.1521 | 16.2086 | 146.227 | 0 | 17% | 0 | 0 | 10% | 0 | 49.9194
4954 | 446 | 663 | 313 | 4 | 30.8 | 108.5231 | 0 | 42.3845 | 0 | 44.1109 | 14.8601 | 67.0538 | 0 | 22% | 5.8845 | 0 | 18% | 0 | 49.9233
4955 | 353 | 704 | 391 | 4.1 | 31.8 | 85.7093 | 0 | 48.0037 | 0 | 43.8533 | 14.6636 | 44.1446 | 0 | 25% | 11.5037 | 0 | 33.65% | 0 | 49.9362
4956 | 326 | 678 | 362 | 3.2 | 32.9 | 80.3033 | 0 | 46.5523 | 0 | 43.965 | 14.6033 | 38.3573 | 0 | 28% | 10.617 | 0 | 48.09% | 0 | 49.3625
4957 | 779 | 927 | 176 | 2.9 | 34.4 | 218.4366 | 0 | 62.4457 | 4.5017 | 42.5972 | 13.9203 | 175.7925 | 0 | 42% | 25 | 0 | 82.09% | 0 | 48.9497
4958 | 875 | 937 | 128 | 4.1 | 35.5 | 243.3475 | 0 | 43.1878 | 24.113 | 42.6036 | 13.8151 | 202.2449 | 0 | 57% | 5.8183 | 0 | 90% | 0 | 48.5015
4959 | 850 | 839 | 127 | 4.4 | 36.1 | 228.4809 | 0 | 36.2343 | 21.0955 | 42.6061 | 13.7567 | 187.3564 | 0 | 71% | 0 | 0 | 90% | 0 | 47.4292
4960 | 805 | 691 | 120 | 4.9 | 35.8 | 205.6956 | 0 | 35.0637 | 7.3977 | 42.6072 | 13.7868 | 164.3956 | 0 | 83% | 0 | 0 | 90% | 0 | 46.4902
4961 | 719 | 516 | 121 | 5.6 | 35.7 | 165.9664 | 0 | 25.2146 | 0 | 42.6073 | 13.7966 | 124.4541 | 0 | 92% | 0 | 8.4038 | 76.55% | 0 | 45.4267
4962 | 240 | 199 | 101 | 3.7 | 35.1 | 0 | 56.1981 | 3.1642 | 0 | 54.466 | 18.6927 | 0 | 52.9043 | 88% | 0 | 25 | 36.55% | 0 | 44.7839
4963 | 340 | 135 | 75 | 6 | 33.7 | 0 | 47.9354 | 0 | 0 | 80.239 | 29.6431 | 0 | 81.6747 | 82% | 0 | 16.5962 | 10% | 0 | 43.2778
4964 | 8 | 6 | 5 | 4.7 | 32 | 0 | 0 | 0 | 0 | 111.8863 | 43.301 | 0 | 116.1407 | 74% | 0 | 0 | 10% | 0 | 40.5892
4965 | 0 | 0 | 0 | 2.8 | 30.7 | 0 | 0 | 0 | 0 | 107.5743 | 41.7516 | 0 | 109.4353 | 66% | 0 | 0 | 10% | 0 | 39.4055
4966 | 0 | 0 | 0 | 4.1 | 29.6 | 0 | 0 | 0 | 0 | 101.7452 | 39.5122 | 0 | 101.8577 | 58% | 0 | 0 | 10% | 0 | 37.3185
4967 | 0 | 0 | 0 | 3.2 | 27.9 | 0 | 0 | 0 | 0 | 96.2956 | 37.4877 | 0 | 95.2373 | 51% | 0 | 0 | 10% | 0 | 35.342
4968 | 0 | 0 | 0 | 2.2 | 27 | 0 | 0 | 0 | 0 | 93.7873 | 36.562 | 0 | 92.3119 | 44% | 0 | 0 | 10% | 0 | 34.4108
4969 | 0 | 0 | 0 | 1.9 | 26 | 0 | 0 | 0 | 0 | 91.7498 | 35.8186 | 0 | 89.8677 | 37% | 0 | 0 | 10% | 0 | 33.6488
4970 | 0 | 0 | 0 | 1.3 | 24.1 | 0 | 0 | 0 | 0 | 90.2229 | 35.3753 | 0 | 88.1035 | 30% | 0 | 0 | 10% | 0 | 33.1768
4971 | 0 | 0 | 0 | 2.1 | 23.6 | 0 | 0 | 0 | 0 | 91.0154 | 35.7568 | 0 | 89.1695 | 24% | 0 | 0 | 10% | 0 | 33.5229
4972 | 0 | 0 | 0 | 2.1 | 23.1 | 0 | 0 | 0 | 0 | 91.5249 | 36.0192 | 0 | 89.8639 | 17% | 0 | 0 | 10% | 0 | 33.7602
4973 | 0 | 0 | 0 | 1.3 | 21.8 | 0 | 0 | 0 | 0 | 95.8196 | 37.9346 | 0 | 95.0959 | 10% | 0 | 0 | 10% | 0 | 35.6498
4974 | 161 | 32 | 15 | 2.1 | 21.8 | 0 | 14.1969 | 0 | 0 | 102.9051 | 40.8851 | 0 | 103.5084 | 2% | 0 | 0 | 10% | 0 | 38.5892
4975 | 613 | 199 | 41 | 1.1 | 25 | 81.8608 | 19.9344 | 0 | 0 | 99.2508 | 39.0524 | 0 | 19.8633 | 0% | 0 | 0 | 10% | 0 | 37.4866
4976 | 786 | 406 | 55 | 1 | 27.9 | 172.6561 | 0 | 15.1525 | 0 | 75.1917 | 28.4481 | 98.9216 | 0 | 8% | 0 | 0 | 10% | 0 | 41.5833
4977 | 864 | 602 | 65 | 1.5 | 29.9 | 215.4649 | 0 | 34.1111 | 0 | 46.7962 | 16.0339 | 170.0961 | 0 | 21% | 6.074 | 0 | 18.26% | 0 | 41.7085
4978 | 905 | 770 | 73 | 2.6 | 31.5 | 240.4991 | 0 | 51.2161 | 0 | 47.677 | 16.238 | 194.3229 | 0 | 35% | 22.5952 | 0 | 48.99% | 0 | 42.2516
4979 | 927 | 895 | 79 | 4.6 | 32.6 | 255.1619 | 0 | 55.45 | 8.5459 | 42.6147 | 14.0975 | 213.8326 | 0 | 51% | 25 | 0 | 82.99% | 0 | 41.79
4980 | 931 | 963 | 84 | 4 | 32.7 | 262.5926 | 0 | 34.6424 | 36.4468 | 42.615 | 14.0882 | 221.1785 | 0 | 68% | 5.1544 | 0 | 90% | 0 | 40.7189
4981 | 925 | 978 | 90 | 2.5 | 32.5 | 263.2434 | 0 | 28.5913 | 43.927 | 42.6147 | 14.1068 | 221.6787 | 0 | 84% | 0 | 0 | 90% | 0 | 39.8142
4982 | 920 | 934 | 84 | 3.8 | 33.9 | 257.2929 | 0 | 23.1818 | 44.4285 | 42.6141 | 13.974 | 215.4399 | 0 | 100% | 0 | 0 | 90% | 0 | 39.4365
4983 | 882 | 828 | 87 | 8.9 | 34.7 | 41.3415 | 226.064 | 24.4743 | 32.1122 | 42.6134 | 13.8965 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.0789
4984 | 817 | 679 | 97 | 6.3 | 35.5 | 42.1511 | 194.5328 | 24.7733 | 16.6198 | 42.6105 | 13.8173 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.2986
4985 | 770 | 504 | 83 | 4.3 | 34.2 | 43.1926 | 161.3508 | 24.3033 | 0 | 43.6287 | 14.3433 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.3541
4986 | 663 | 309 | 69 | 6.1 | 32.5 | 42.1339 | 102.6714 | 7.1362 | 0 | 42.6052 | 14.1037 | 0 | 0 | 100% | 0 | 18.0571 | 61.11% | 0 | 40.0056
4987 | 430 | 116 | 41 | 5 | 30.4 | 0 | 60.8789 | 0 | 0 | 48.0913 | 16.5298 | 0 | 46.5636 | 96% | 0 | 25 | 21.11% | 0 | 39.4374
4988 | 7 | 4 | 4 | 3.7 | 29 | 0 | 0 | 0 | 0 | 86.5436 | 33.1056 | 0 | 88.5613 | 90% | 0 | 6.9429 | 10% | 0 | 37.1017
4989 | 0 | 0 | 0 | 4.1 | 28.2 | 0 | 0 | 0 | 0 | 96.7509 | 37.6366 | 0 | 96.9853 | 83% | 0 | 0 | 10% | 0 | 35.1784
4990 | 0 | 0 | 0 | 4.2 | 27.3 | 0 | 0 | 0 | 0 | 91.3593 | 35.5039 | 0 | 89.9907 | 76% | 0 | 0 | 10% | 0 | 33.1818
4991 | 0 | 0 | 0 | 2.8 | 26.5 | 0 | 0 | 0 | 0 | 87.2858 | 33.8939 | 0 | 85.1114 | 70% | 0 | 0 | 10% | 0 | 31.5567
4992 | 0 | 0 | 0 | 1.9 | 25.5 | 0 | 0 | 0 | 0 | 84.8283 | 32.9807 | 0 | 82.3744 | 63% | 0 | 0 | 10% | 0 | 30.5856
4993 | 0 | 0 | 0 | 1.3 | 24.2 | 0 | 0 | 0 | 0 | 83.3587 | 32.5019 | 0 | 80.8287 | 57% | 0 | 0 | 10% | 0 | 30.0458
4994 | 0 | 0 | 0 | 1.5 | 23.7 | 0 | 0 | 0 | 0 | 82.3485 | 32.102 | 0 | 79.9137 | 51% | 0 | 0 | 10% | 0 | 29.5915
4995 | 0 | 0 | 0 | 1.7 | 23.4 | 0 | 0 | 0 | 0 | 82.4737 | 32.1872 | 0 | 80.1621 | 45% | 0 | 0 | 10% | 0 | 29.6324
4996 | 0 | 0 | 0 | 1.6 | 22.1 | 0 | 0 | 0 | 0 | 81.4623 | 31.8419 | 0 | 79.2308 | 40% | 0 | 0 | 10% | 0 | 29.2536
4997 | 0 | 0 | 0 | 2.1 | 21.8 | 0 | 0 | 0 | 0 | 84.367 | 33.1359 | 0 | 82.4793 | 33% | 0 | 0 | 10% | 0 | 30.5156
4998 | 136 | 30 | 16 | 1.9 | 22.7 | 0 | 11.4624 | 0 | 0 | 89.9778 | 35.4046 | 0 | 89.2947 | 27% | 0 | 0 | 10% | 0 | 32.7597
4999 | 563 | 194 | 48 | 2 | 25.1 | 73.7291 | 18.0016 | 0.015038 | 0 | 92.7512 | 36.3378 | 0 | 21.1359 | 25% | 0 | 0 | 10% | 0 | 34.8121
5000 | 747 | 398 | 65 | 2 | 26.5 | 162.7559 | 0 | 15.0574 | 0 | 62.0664 | 22.8664 | 100.8674 | 0 | 33% | 0 | 0 | 10% | 0 | 36.0129
5001 | 843 | 597 | 71 | 3.8 | 28 | 208.6631 | 0 | 33.953 | 0 | 46.5614 | 16.1207 | 162.5949 | 0 | 45% | 10.8763 | 0 | 24.79% | 0 | 36.8846
5002 | 842 | 733 | 85 | 3.9 | 28.7 | 221.732 | 0 | 48.883 | 0 | 47.0718 | 16.2639 | 175.3434 | 0 | 58% | 24.9628 | 0 | 58.74% | 0 | 37.7357
5003 | 850 | 874 | 121 | 4.1 | 29.5 | 232.8333 | 0 | 49.2072 | 13.412 | 42.5858 | 14.3709 | 190.7694 | 0 | 72% | 22.9843 | 0 | 90% | 0 | 38.0307
5004 | 902 | 959 | 106 | 4.5 | 29.8 | 253.5998 | 0 | 24.5634 | 46.8585 | 42.591 | 14.3459 | 211.369 | 0 | 87% | 0 | 0 | 90% | 0 | 37.1736
5005 | 922 | 980 | 93 | 5.6 | 30.3 | 216.4134 | 50.2905 | 20.0924 | 53.0864 | 42.5954 | 14.3025 | 174.2686 | 0 | 100% | 0 | 0 | 90% | 0 | 36.5658
5006 | 907 | 933 | 93 | 5.2 | 30.2 | 42.1516 | 241.8077 | 21.2523 | 47.0644 | 42.5966 | 14.312 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.2734
5007 | 886 | 831 | 89 | 5.1 | 30.3 | 42.1571 | 227.0036 | 21.0964 | 36.8704 | 42.5943 | 14.3021 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.1077
5008 | 851 | 684 | 81 | 4.9 | 30.1 | 42.1571 | 205.0542 | 21.3633 | 21.3901 | 42.592 | 14.3194 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.3919
5009 | 788 | 501 | 72 | 4.6 | 29.8 | 42.1571 | 167.4244 | 21.9978 | 2.5026 | 42.5897 | 14.3455 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.0525
5010 | 664 | 298 | 59 | 3.6 | 29.4 | 42.1572 | 103.4278 | 6.7579 | 0 | 42.5876 | 14.3803 | 0 | 0 | 100% | 0 | 16.8665 | 63.01% | 0 | 38.7141
5011 | 379 | 103 | 35 | 3.4 | 28.2 | 0 | 51.8183 | 0 | 0 | 48.7894 | 17.0353 | 0 | 47.2581 | 97% | 0 | 25 | 23.01% | 0 | 39.948
5012 | 3 | 3 | 3 | 1.8 | 26.6 | 0 | 0 | 0 | 0 | 84.9479 | 32.687 | 0 | 86.9099 | 90% | 0 | 8.1335 | 10% | 0 | 37.875
5013 | 0 | 0 | 0 | 1.6 | 25.4 | 0 | 0 | 0 | 0 | 96.7769 | 37.9778 | 0 | 97.0189 | 83% | 0 | 0 | 10% | 0 | 35.5208
5014 | 0 | 0 | 0 | 2.9 | 23.6 | 0 | 0 | 0 | 0 | 90.9742 | 35.7381 | 0 | 89.5164 | 76% | 0 | 0 | 10% | 0 | 33.4194
5015 | 0 | 0 | 0 | 1.9 | 22.5 | 0 | 0 | 0 | 0 | 87.2439 | 34.2751 | 0 | 85.079 | 70% | 0 | 0 | 10% | 0 | 31.9344
5016 | 0 | 0 | 0 | 0.8 | 22.4 | 0 | 0 | 0 | 0 | 85.6129 | 33.6033 | 0 | 83.3178 | 64% | 0 | 0 | 10% | 0 | 31.204
5017 | 0 | 0 | 0 | 0.7 | 21.5 | 0 | 0 | 0 | 0 | 85.2224 | 33.5162 | 0 | 83.0168 | 57% | 0 | 0 | 10% | 0 | 31.0622
5018 | 0 | 0 | 0 | 0.6 | 20.7 | 0 | 0 | 0 | 0 | 86.8767 | 34.2715 | 0 | 85.112 | 51% | 0 | 0 | 10% | 0 | 31.773
5019 | 0 | 0 | 0 | 0.4 | 20.5 | 0 | 0 | 0 | 0 | 93.7443 | 37.1788 | 0 | 93.5929 | 44% | 0 | 0 | 10% | 0 | 34.6507
5020 | 0 | 0 | 0 | 0.7 | 19.8 | 0 | 0 | 0 | 0 | 100.4925 | 40.0446 | 0 | 101.4988 | 37% | 0 | 0 | 10% | 0 | 37.5409
5021 | 0 | 0 | 0 | 0.8 | 19.5 | 0 | 0 | 0 | 0 | 107.867 | 43.1406 | 0 | 110.1111 | 28% | 0 | 0 | 10% | 0 | 40.6868
5022 | 135 | 30 | 16 | 1.1 | 19.3 | 0 | 10.8478 | 0 | 0 | 115.6024 | 46.3602 | 0 | 118.9852 | 19% | 0 | 0 | 10% | 0 | 43.977
5023 | 550 | 190 | 51 | 0.7 | 23.2 | 71.6075 | 17.601 | 0.12863 | 0 | 119.1685 | 47.457 | 0 | 53.3649 | 15% | 0 | 0 | 10% | 0 | 46.0734
5024 | 729 | 393 | 72 | 0.6 | 26.5 | 158.7898 | 0 | 15.1606 | 0 | 87.4258 | 33.9559 | 71.9306 | 0 | 21% | 0 | 0 | 10% | 0 | 47.1856
5025 | 812 | 589 | 87 | 1.7 | 28 | 201.3846 | 0 | 33.9317 | 0 | 48.1323 | 16.7712 | 154.6072 | 0 | 32% | 0 | 0 | 10% | 0 | 48.4379
5026 | 869 | 759 | 95 | 2.4 | 29.3 | 230.2474 | -2.98e-14 | 51.4191 | 0 | 46.5334 | 15.9851 | 185.0831 | 0 | 46% | 15.6517 | 0 | 31.29% | 0 | 49.2122
5027 | 902 | 887 | 98 | 2.6 | 30.6 | 249.2724 | 0 | 61.9286 | 2.4878 | 42.5935 | 14.2748 | 207.8784 | 0 | 62% | 25 | 0 | 65.29% | 0 | 48.4725
5028 | 918 | 963 | 100 | 4.8 | 31.2 | 258.0212 | 0 | 54.0288 | 17.9565 | 42.5998 | 14.2223 | 216.5043 | 0 | 78% | 18.1719 | 0 | 90% | 0 | 47.24
5029 | 908 | 973 | 106 | 5.2 | 32 | 256.1412 | 0 | 35.7975 | 37.0217 | 42.6022 | 14.1495 | 214.5022 | 0 | 94% | 0 | 0 | 90% | 0 | 47.1092
5030 | 899 | 929 | 104 | 5 | 32.7 | 125.5258 | 143.3924 | 32.4992 | 35.65 | 42.604 | 14.0845 | 83.8322 | 0 | 100% | 0 | 0 | 90% | 0 | 47.085
5031 | 873 | 825 | 100 | 5.1 | 32.8 | 42.1514 | 222.9209 | 31.5063 | 26.096 | 42.6026 | 14.0747 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 46.2897
5032 | 830 | 677 | 94 | 5.6 | 32.7 | 42.1569 | 198.5022 | 30.7708 | 11.6078 | 42.6001 | 14.0832 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.5626
5033 | 752 | 491 | 85 | 5.7 | 32 | 42.1569 | 156.871 | 24.0778 | 0 | 42.5976 | 14.1479 | 0 | 0 | 100% | 0 | 5.8698 | 80.61% | 0 | 44.8044
5034 | 617 | 288 | 69 | 4.7 | 31.1 | 42.157 | 91.2675 | 6.5746 | 0 | 42.5952 | 14.23 | 0 | 0 | 100% | 0 | 23.3036 | 43.32% | 0 | 44.8171
5035 | 328 | 96 | 39 | 3.5 | 29.5 | 0 | 55.832 | 0 | 0 | 67.2064 | 24.7011 | 0 | 67.1306 | 95% | 0 | 20.8266 | 10% | 0 | 43.4438
5036 | 2 | 3 | 3 | 2 | 26.4 | 0 | 0 | 0 | 0 | 109.0904 | 42.9545 | 0 | 112.7053 | 87% | 0 | 0 | 10% | 0 | 40.2726
5037 | 0 | 0 | 0 | 0.5 | 25.2 | 0 | 0 | 0 | 0 | 102.971 | 40.5698 | 0 | 103.1234 | 79% | 0 | 0 | 10% | 0 | 38.4454
5038 | 0 | 0 | 0 | 0.8 | 24.8 | 0 | 0 | 0 | 0 | 97.1658 | 38.2028 | 0 | 95.9261 | 72% | 0 | 0 | 10% | 0 | 36.1621
5039 | 0 | 0 | 0 | 1.1 | 24 | 0 | 0 | 0 | 0 | 93.4613 | 36.7481 | 0 | 91.6604 | 65% | 0 | 0 | 10% | 0 | 34.6836
5040 | 0 | 0 | 0 | 1.5 | 24.4 | 0 | 0 | 0 | 0 | 91.984 | 36.0849 | 0 | 90.0069 | 58% | 0 | 0 | 10% | 0 | 33.9721
5041 | 0 | 0 | 0 | 1.6 | 23.7 | 0 | 0 | 0 | 0 | 90.9867 | 35.7344 | 0 | 88.944 | 51% | 0 | 0 | 10% | 0 | 33.574
5042 | 0 | 0 | 0 | 1 | 21.5 | 0 | 0 | 0 | 0 | 91.6779 | 36.223 | 0 | 89.9226 | 44% | 0 | 0 | 10% | 0 | 34.0176
5043 | 0 | 0 | 0 | 0.8 | 20.3 | 0 | 0 | 0 | 0 | 97.5673 | 38.7846 | 0 | 97.0483 | 37% | 0 | 0 | 10% | 0 | 36.5419
5044 | 0 | 0 | 0 | 1.4 | 20.1 | 0 | 0 | 0 | 0 | 103.5891 | 41.3155 | 0 | 104.1844 | 29% | 0 | 0 | 10% | 0 | 39.0737
5045 | 0 | 0 | 0 | 1.9 | 20.9 | 0 | 0 | 0 | 0 | 110.217 | 43.9899 | 0 | 111.8502 | 21% | 0 | 0 | 10% | 0 | 41.7739
5046 | 104 | 28 | 17 | 1.3 | 22.1 | 0 | 7.9453 | 0 | 0 | 117.3086 | 46.8061 | 0 | 120.0415 | 12% | 0 | 0 | 10% | 0 | 44.6324
5047 | 503 | 183 | 56 | 1.4 | 23.9 | 63.6318 | 15.7272 | 0.21639 | 0 | 119.9922 | 47.7201 | 0 | 61.2424 | 7% | 0 | 0 | 10% | 0 | 46.52
5048 | 705 | 388 | 78 | 1.2 | 28 | 152.5693 | 0 | 14.962 | 0 | 88.8726 | 34.3849 | 64.4134 | 0 | 12% | 0 | 0 | 10% | 0 | 47.4667
5049 | 790 | 583 | 96 | 1.5 | 30.9 | 195.5383 | 0 | 33.3949 | 0 | 49.9567 | 17.2457 | 147.3739 | 0 | 23% | 0 | 0 | 10% | 0 | 48.4273
5050 | 824 | 749 | 117 | 3.2 | 32.7 | 217.0311 | 0 | 49.961 | 0 | 47.0389 | 15.8578 | 171.7834 | 0 | 36% | 14.4574 | 0 | 29.66% | 0 | 48.9434
5051 | 841 | 875 | 136 | 4.5 | 33.7 | 229.7031 | 0 | 61.6191 | 0.88129 | 42.6042 | 13.9898 | 188.6574 | 0 | 50% | 25 | 0 | 63.66% | 0 | 48.0635
5052 | 866 | 953 | 135 | 4.9 | 34.5 | 242.2487 | 0 | 55.1567 | 14.8686 | 42.6074 | 13.9139 | 201.053 | 0 | 65% | 19.3661 | 0 | 90% | 0 | 47.0201
5053 | 859 | 964 | 140 | 5.7 | 34.7 | 240.8025 | 0 | 35.6109 | 35.4464 | 42.6086 | 13.895 | 199.5241 | 0 | 80% | 0 | 0 | 90% | 0 | 46.8187
5054 | 847 | 919 | 139 | 6.3 | 34.6 | 233.239 | 0 | 35.2888 | 31.3569 | 42.6091 | 13.9048 | 191.6816 | 0 | 95% | 0 | 0 | 90% | 0 | 46.5665
5055 | 826 | 821 | 133 | 6.2 | 34.2 | 116.6289 | 120.9524 | 31.2696 | 25.627 | 42.6089 | 13.9434 | 74.9286 | 0 | 100% | 0 | 0 | 90% | 0 | 45.7898
5056 | 761 | 669 | 133 | 6.7 | 33 | 42.1515 | 177.2533 | 30.3311 | 11.4167 | 42.6073 | 14.0576 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.0973
5057 | 667 | 489 | 128 | 6.7 | 31.5 | 42.157 | 132.2857 | 24.4181 | 0 | 42.6047 | 14.1963 | 0 | 0 | 100% | 0 | 5.0171 | 81.97% | 0 | 44.3405
5058 | 502 | 279 | 100 | 6.6 | 30.3 | 42.1571 | 61.2139 | 6.7941 | 0 | 42.6021 | 14.3048 | 0 | 0 | 100% | 0 | 22.7521 | 45.57% | 0 | 44.5601
5059 | 217 | 90 | 51 | 6.4 | 28.3 | 0 | 36.773 | 0 | 0 | 63.1057 | 23.099 | 0 | 62.5208 | 95% | 0 | 22.2308 | 10% | 0 | 43.2476
5060 | 1 | 3 | 3 | 4.9 | 26.4 | 0 | 0 | 0 | 0 | 108.9744 | 42.9067 | 0 | 112.9627 | 87% | 0 | 0 | 10% | 0 | 40.1295
5061 | 0 | 0 | 0 | 5.4 | 24.8 | 0 | 0 | 0 | 0 | 102.6481 | 40.4783 | 0 | 102.8585 | 79% | 0 | 0 | 10% | 0 | 38.322
5062 | 0 | 0 | 0 | 5.4 | 23.5 | 0 | 0 | 0 | 0 | 96.4537 | 38.0385 | 0 | 95.181 | 72% | 0 | 0 | 10% | 0 | 35.9746
5063 | 0 | 0 | 0 | 4.8 | 22.4 | 0 | 0 | 0 | 0 | 92.3372 | 36.422 | 0 | 90.3643 | 65% | 0 | 0 | 10% | 0 | 34.3338
5064 | 0 | 0 | 0 | 3.3 | 21.8 | 0 | 0 | 0 | 0 | 90.6942 | 35.7824 | 0 | 88.5467 | 59% | 0 | 0 | 10% | 0 | 33.6382
5065 | 0 | 0 | 0 | 2.3 | 21.7 | 0 | 0 | 0 | 0 | 89.731 | 35.3861 | 0 | 87.553 | 52% | 0 | 0 | 10% | 0 | 33.1879
5066 | 0 | 0 | 0 | 1.7 | 21.7 | 0 | 0 | 0 | 0 | 90.7859 | 35.83 | 0 | 88.9796 | 45% | 0 | 0 | 10% | 0 | 33.5825
5067 | 0 | 0 | 0 | 3.2 | 22.3 | 0 | 0 | 0 | 0 | 96.4974 | 38.1697 | 0 | 95.9493 | 38% | 0 | 0 | 10% | 0 | 35.8849
5068 | 0 | 0 | 0 | 6 | 23.6 | 0 | 0 | 0 | 0 | 102.5113 | 40.5476 | 0 | 103.0497 | 30% | 0 | 0 | 10% | 0 | 38.2647
5069 | 0 | 0 | 0 | 4.3 | 23 | 0 | 0 | 0 | 0 | 107.945 | 42.8583 | 0 | 109.3535 | 22% | 0 | 0 | 10% | 0 | 40.6036
5070 | 0 | 15 | 15 | 4.9 | 22.8 | 0 | 0 | 0 | 0 | 114.5144 | 45.5853 | 0 | 116.9002 | 13% | 0 | 0 | 10% | 0 | 43.3709
5071 | 0 | 32 | 32 | 4.5 | 23.3 | 0 | 0 | 0 | 0 | 118.7949 | 47.2933 | 0 | 121.7065 | 4% | 0 | 0 | 10% | 0 | 45.1357
5072 | 0 | 55 | 55 | 4.7 | 23.9 | 0 | 0 | 0 | 0 | 51.4114 | 20.4525 | 0 | 52.7182 | 0% | 0 | 0 | 10% | 0 | 18.4751
5073 | 56 | 221 | 180 | 6.3 | 24.4 | 0 | 16.1195 | 7.4571 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 5.5759
5074 | 461 | 628 | 268 | 5.8 | 26.6 | 91.2413 | 22.5763 | 41.0063 | 0 | 0 | 0 | 87.9229 | 0 | 7% | 0 | 0 | 10% | 0 | 39.5365
5075 | 320 | 684 | 394 | 7.5 | 27.5 | 72.767 | 0 | 46.8841 | 0 | 0 | 0 | 71.8062 | 0 | 12% | 0 | 0 | 10% | 0 | 45.8146
5076 | 114 | 510 | 392 | 7.7 | 28 | 0 | 36.8085 | 31.9109 | 0 | 44.057 | 7.6651 | 0 | 40.8687 | 9% | 0 | 0 | 10% | 0 | 38.3124
5077 | 253 | 696 | 442 | 6.9 | 29.2 | 45.5433 | 11.976 | 48.58 | 0 | 43.5443 | 14.7888 | 11.1083 | 7.478 | 9% | 16.0487 | 0 | 31.83% | 0 | 46.198
5078 | 291 | 682 | 401 | 7.9 | 30 | 65.0745 | 0 | 46.6573 | 0 | 43.608 | 14.7401 | 23.085 | 0 | 11% | 14.2852 | 0 | 51.25% | 0 | 46.0805
5079 | 462 | 723 | 337 | 8 | 30.4 | 112.5854 | 0 | 49.4256 | 0 | 44.3766 | 15.0104 | 69.1197 | 0 | 16% | 17.646 | 0 | 75.25% | 0 | 45.339
5080 | 662 | 649 | 180 | 6.6 | 31.2 | 164.0297 | 0 | 40.6529 | 0 | 45.7923 | 15.5042 | 119.3277 | 0 | 25% | 9.579 | 0 | 88.28% | 0 | 44.6602
5081 | 564 | 462 | 156 | 7.2 | 30 | 123.7209 | 0 | 22.9227 | 0 | 42.5714 | 14.3215 | 82.8697 | 0 | 32% | 0 | 8.1848 | 75.18% | 0 | 43.8668
5082 | 420 | 266 | 114 | 7.4 | 28.3 | 69.4861 | 0 | 6.6069 | 0 | 42.578 | 14.4748 | 28.8071 | 0 | 34% | 0 | 24.0869 | 36.65% | 0 | 44.0941
5083 | 152 | 83 | 55 | 6.9 | 26.4 | 0 | 25.6386 | 0 | 0 | 73.6694 | 27.79 | 0 | 73.1206 | 28% | 0 | 16.6534 | 10% | 0 | 42.9358
5084 | 1 | 3 | 3 | 6.9 | 24 | 0 | 0 | 0 | 0 | 106.7845 | 42.2802 | 0 | 108.7452 | 20% | 0 | 0 | 10% | 0 | 39.8393
5085 | 0 | 0 | 0 | 6.6 | 23 | 0 | 0 | 0 | 0 | 102.6986 | 40.6851 | 0 | 103.542 | 12% | 0 | 0 | 10% | 0 | 38.3191
5086 | 0 | 0 | 0 | 5.4 | 22.6 | 0 | 0 | 0 | 0 | 97.6115 | 38.6059 | 0 | 97.3057 | 5% | 0 | 0 | 10% | 0 | 36.2857
5087 | 0 | 0 | 0 | 3.4 | 22.4 | 0 | 0 | 0 | 0 | 67.9228 | 26.8221 | 0 | 67.1574 | 0% | 0 | 0 | 10% | 0 | 24.5532
5088 | 0 | 0 | 0 | 2.8 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1755
5089 | 0 | 0 | 0 | 2.4 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1555
5090 | 0 | 0 | 0 | 2.1 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1359
5091 | 0 | 0 | 0 | 1.8 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1166
5092 | 0 | 0 | 0 | 1.3 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0976
5093 | 0 | 0 | 0 | 1.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0791
5094 | 3 | 17 | 17 | 1.2 | 19.7 | 0 | 0.20522 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0608
5095 | 56 | 105 | 90 | 1.1 | 21.3 | 0 | 11.2632 | 0.0025565 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0402
5096 | 55 | 198 | 170 | 1 | 23.6 | 0 | 14.1427 | 5.4446 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.4196
5097 | 153 | 385 | 283 | 2.1 | 25.1 | 0 | 44.0353 | 19.1186 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 17.111
5098 | 377 | 572 | 274 | 4.4 | 27.3 | 72.7135 | 17.9519 | 36.1548 | 0 | 0 | 0 | 68.9657 | 0 | 5% | 0 | 0 | 10% | 0 | 34.8263
5099 | 695 | 847 | 234 | 2.6 | 29.2 | 187.883 | 0 | 61.3692 | 0 | 0 | 0 | 183.4638 | 0 | 19% | 10.4067 | 0 | 24.15% | 0 | 48.8856
5100 | 680 | 908 | 263 | 1.8 | 30.7 | 188.0312 | 0 | 67.2007 | 0 | 0 | 0 | 186.0199 | 0 | 34% | 17.2121 | 0 | 47.56% | 0 | 47.873
5101 | 709 | 930 | 248 | 2.8 | 32 | 197.4295 | 0 | 69.2651 | 0 | 0 | 0 | 195.6894 | 0 | 48% | 19.6021 | 0 | 74.22% | 0 | 47.4341
5102 | 671 | 882 | 262 | 3.5 | 32.6 | 182.7967 | 0 | 61.3167 | 2.7685 | 0 | 0 | 181.3919 | 0 | 62% | 11.6026 | 0 | 90% | 0 | 47.5875
5103 | 643 | 782 | 244 | 3.4 | 33.6 | 169.2083 | 0 | 49.5164 | 4.309 | 0 | 0 | 167.9162 | 0 | 75% | 0 | 0 | 90% | 0 | 47.4975
5104 | 583 | 634 | 224 | 5.8 | 31.6 | 142.625 | -2.98e-14 | 39.9549 | 0 | 42.5492 | 0 | 101.895 | 0 | 83% | 0 | 8.8777 | 75.8% | 0 | 46.5389
5105 | 535 | 456 | 167 | 5.2 | 30.3 | 117.981 | 0 | 22.7015 | 0 | 42.5559 | 8.6573 | 76.7327 | 0 | 88% | 0 | 15.9942 | 50.2% | 0 | 45.6078
5106 | 386 | 258 | 120 | 4.4 | 29.1 | 64.8296 | 0 | 6.499 | 0 | 44.2509 | 15.0765 | 22.0814 | 0 | 90% | 0 | 25 | 10.21% | 0 | 45.5352
5107 | 134 | 78 | 53 | 3.6 | 26.7 | 0 | 22.4935 | 0 | 0 | 116.4797 | 45.9531 | 0 | 121.8633 | 81% | 0 | 0 | 10.21% | 0 | 44.1302
5108 | 1 | 3 | 3 | 3.9 | 24.2 | 0 | 0 | 0 | 0 | 109.8126 | 43.5025 | 0 | 111.8136 | 73% | 0 | 0 | 10.21% | 0 | 41.2281
5109 | 0 | 0 | 0 | 2.9 | 22.8 | 0 | 0 | 0 | 0 | 102.8698 | 40.7754 | 0 | 102.8181 | 65% | 0 | 0 | 10.21% | 0 | 38.6908
5110 | 0 | 0 | 0 | 1.7 | 22.5 | 0 | 0 | 0 | 0 | 97.2733 | 38.474 | 0 | 96.0318 | 57% | 0 | 0 | 10.21% | 0 | 36.4318
5111 | 0 | 0 | 0 | 0.6 | 22.1 | 0 | 0 | 0 | 0 | 93.3411 | 36.8756 | 0 | 91.4771 | 51% | 0 | 0 | 10.21% | 0 | 34.8168
5112 | 0 | 0 | 0 | 1.2 | 22 | 0 | 0 | 0 | 0 | 91.5059 | 36.1103 | 0 | 89.3585 | 44% | 0 | 0 | 10.21% | 0 | 34.0129
5113 | 0 | 0 | 0 | 1 | 21.9 | 0 | 0 | 0 | 0 | 90.537 | 35.711 | 0 | 88.3207 | 37% | 0 | 0 | 10.21% | 0 | 33.5703
5114 | 0 | 0 | 0 | 1.3 | 21.6 | 0 | 0 | 0 | 0 | 91.6044 | 36.1862 | 0 | 89.7482 | 30% | 0 | 0 | 10.21% | 0 | 34.0023
5115 | 0 | 0 | 0 | 1.1 | 21.4 | 0 | 0 | 0 | 0 | 96.9694 | 38.4467 | 0 | 96.2463 | 23% | 0 | 0 | 10.21% | 0 | 36.2265
5116 | 0 | 0 | 0 | 0.6 | 20.9 | 0 | 0 | 0 | 0 | 102.3598 | 40.7363 | 0 | 102.6332 | 15% | 0 | 0 | 10.21% | 0 | 38.5088
5117 | 0 | 0 | 0 | 1.7 | 21.3 | 0 | 0 | 0 | 0 | 110.3492 | 44.0105 | 0 | 111.9947 | 7% | 0 | 0 | 10.21% | 0 | 41.7909
5118 | 33 | 22 | 18 | 1.8 | 21.1 | 0 | 2.1245 | 0 | 0 | 87.5592 | 35.0099 | 0 | 89.6505 | 0% | 0 | 0 | 10.21% | 0 | 32.8778
5119 | 331 | 162 | 78 | 0.8 | 23 | 0 | 55.5224 | 0.54021 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.21% | 0 | -1.4227
5120 | 559 | 363 | 117 | 1.3 | 26.2 | 117.1109 | 0 | 14.3417 | 0 | 0 | 0 | 112.8348 | 0 | 9% | 0 | 0 | 10.21% | 0 | 12.9105
5121 | 666 | 555 | 146 | 2.5 | 28.9 | 161.5405 | 0 | 32.2808 | 0 | 0 | 0 | 159.5403 | 0 | 21% | 0 | 0 | 10.21% | 0 | 30.4247
5122 | 723 | 720 | 170 | 3 | 30.1 | 188.4621 | 0 | 49.1242 | 0 | 0 | 0 | 186.8944 | 0 | 35% | 0 | 0 | 10.21% | 0 | 47.001
5123 | 764 | 850 | 181 | 5 | 30.6 | 206.4738 | 0 | 61.2618 | 0 | 0 | 0 | 205.071 | 0 | 51% | 10.2719 | 0 | 24.18% | 0 | 48.6721
5124 | 758 | 921 | 205 | 5.5 | 31.2 | 208.9087 | 0 | 69.1188 | 0 | 0 | 0 | 207.658 | 0 | 66% | 19.3784 | 0 | 50.53% | 0 | 47.3663
5125 | 713 | 928 | 243 | 5.6 | 31.3 | 196.4272 | 0 | 69.4988 | 0 | 0 | 0 | 195.3001 | 0 | 81% | 20.2432 | 0 | 78.06% | 0 | 46.967
5126 | 686 | 883 | 249 | 4.5 | 32 | 186.4472 | 0 | 58.0428 | 6.5047 | 0 | 0 | 185.3192 | 0 | 95% | 8.7793 | 0 | 90% | 0 | 47.0366
5127 | 626 | 775 | 253 | 3 | 33 | 64.8633 | 110.0376 | 48.0614 | 5.4158 | 0 | 0 | 64.4636 | 0 | 100% | 0 | 0 | 90% | 0 | 46.9405
5128 | 616 | 633 | 202 | 3.6 | 33.9 | 40.8187 | 134.8011 | 39.4963 | 0 | 42.5899 | 0 | 0 | 0 | 100% | 0 | 7.5656 | 77.9% | 0 | 46.0292
5129 | 528 | 448 | 165 | 4.6 | 33.3 | 42.1595 | 92.5979 | 22.1026 | 0 | 42.5876 | 12.9093 | 0 | 0 | 100% | 0 | 9.3691 | 62.91% | 0 | 45.0498
5130 | 364 | 250 | 122 | 3.7 | 32.4 | 42.1569 | 25.5772 | 6.2437 | 0 | 42.5857 | 14.1066 | 0 | 0 | 100% | 0 | 23.8078 | 24.81% | 0 | 44.8668
5131 | 134 | 78 | 53 | 3.3 | 29.7 | 0 | 22.3809 | 0 | 0 | 95.2469 | 36.5297 | 0 | 99.3207 | 93% | 0 | 8.9532 | 10.49% | 0 | 43.3706
5132 | 1 | 2 | 2 | 3.3 | 25.9 | 0 | 0 | 0 | 0 | 108.19 | 42.6459 | 0 | 109.1126 | 84% | 0 | 0 | 10.49% | 0 | 40.5701
5133 | 0 | 0 | 0 | 2.3 | 24.7 | 0 | 0 | 0 | 0 | 102.1239 | 40.2715 | 0 | 101.2397 | 77% | 0 | 0 | 10.49% | 0 | 38.371
5134 | 0 | 0 | 0 | 1.2 | 24.1 | 0 | 0 | 0 | 0 | 96.5751 | 38.031 | 0 | 94.7721 | 70% | 0 | 0 | 10.49% | 0 | 36.1185
5135 | 0 | 0 | 0 | 0.7 | 24 | 0 | 0 | 0 | 0 | 92.3342 | 36.2732 | 0 | 89.9678 | 63% | 0 | 0 | 10.49% | 0 | 34.3002
5136 | 0 | 0 | 0 | 1 | 23.3 | 0 | 0 | 0 | 0 | 89.6334 | 35.204 | 0 | 86.9546 | 56% | 0 | 0 | 10.49% | 0 | 33.1555
5137 | 0 | 0 | 0 | 0.7 | 22.8 | 0 | 0 | 0 | 0 | 88.0246 | 34.576 | 0 | 85.2751 | 50% | 0 | 0 | 10.49% | 0 | 32.4515
5138 | 0 | 0 | 0 | 1.3 | 22.6 | 0 | 0 | 0 | 0 | 87.3028 | 34.292 | 0 | 84.6281 | 43% | 0 | 0 | 10.49% | 0 | 32.0994
5139 | 0 | 0 | 0 | 0.7 | 22.5 | 0 | 0 | 0 | 0 | 88.2557 | 34.6999 | 0 | 85.9409 | 37% | 0 | 0 | 10.49% | 0 | 32.4483
5140 | 0 | 0 | 0 | 1.4 | 21.5 | 0 | 0 | 0 | 0 | 88.7222 | 34.9813 | 0 | 86.6231 | 30% | 0 | 0 | 10.49% | 0 | 32.6883
5141 | 0 | 0 | 0 | 0.9 | 21.2 | 0 | 0 | 0 | 0 | 93.4204 | 36.9865 | 0 | 92.464 | 23% | 0 | 0 | 10.49% | 0 | 34.6552
5142 | 23 | 22 | 19 | 0.8 | 20.9 | 0 | 1.3876 | 0 | 0 | 100.6467 | 40.02 | 0 | 101.0268 | 16% | 0 | 0 | 10.49% | 0 | 37.6761
5143 | 287 | 160 | 86 | 0.9 | 23.4 | 0 | 57.3541 | 0.79491 | 0 | 105.2153 | 41.6993 | 0 | 106.4301 | 8% | 0 | 0 | 10.49% | 0 | 40.1701
5144 | 509 | 361 | 136 | 3.2 | 25.3 | 85.3233 | 20.8666 | 14.3984 | 0 | 75.2785 | 28.783 | 23.7613 | 13.1945 | 9% | 0 | 0 | 10.49% | 0 | 41.6289
5145 | 591 | 557 | 192 | 4.2 | 26.4 | 140.3253 | 0 | 32.8136 | 0 | 44.3262 | 15.3504 | 96.9259 | 0 | 16% | 3.8326 | 0 | 15.7% | 0 | 42.6403
5146 | 262 | 565 | 362 | 3.3 | 27.5 | 56.6053 | 0 | 35.8014 | 0 | 43.0633 | 14.7408 | 15.5934 | 0 | 17% | 6.0644 | 0 | 23.95% | 0 | 43.5205
5147 | 611 | 809 | 267 | 2 | 29.3 | 163.4122 | 0 | 56.014 | 1.6661 | 42.5609 | 14.3802 | 120.2154 | 0 | 26% | 25 | 0 | 57.95% | 0 | 43.5103
5148 | 727 | 913 | 227 | 1.5 | 31.6 | 202.5298 | 1.71e-15 | 54.2351 | 14.1195 | 42.5794 | 14.1787 | 160.7976 | 0 | 38% | 23.5684 | 0 | 90% | 0 | 42.5878
5149 | 688 | 918 | 258 | 2.9 | 33.2 | 191.1824 | 0 | 29.9156 | 38.32 | 42.5902 | 14.0329 | 149.7235 | 0 | 49% | 0 | 0 | 90% | 0 | 41.7778
5150 | 665 | 869 | 256 | 3.7 | 33.4 | 181.079 | 0 | 29.3783 | 33.8358 | 42.5952 | 14.0155 | 139.5172 | 0 | 59% | 0 | 0 | 90% | 0 | 41.3047
5151 | 664 | 776 | 225 | 4.6 | 32.8 | 174.4936 | 0 | 28.9078 | 25.2906 | 42.5975 | 14.0731 | 132.7872 | 0 | 69% | 0 | 0 | 90% | 0 | 40.9447
5152 | 653 | 637 | 182 | 4.7 | 32 | 163.2254 | 0 | 28.5871 | 11.78 | 42.5987 | 14.1483 | 121.3905 | 0 | 78% | 0 | 0 | 90% | 0 | 40.7979
5153 | 528 | 447 | 165 | 2.3 | 31.7 | 118.2582 | 0 | 22.2609 | 0 | 42.5991 | 14.1761 | 76.458 | 0 | 84% | 0 | 4.9332 | 82.11% | 0 | 40.5787
5154 | 361 | 246 | 119 | 2.7 | 30.5 | 60.3723 | 0 | 6.0842 | 0 | 42.5982 | 14.2854 | 18.6745 | 0 | 85% | 0 | 20.583 | 49.17% | 0 | 41.5924
5155 | 105 | 72 | 52 | 2.7 | 28.5 | 0 | 17.4463 | 0 | 0 | 51.9631 | 18.3466 | 0 | 50.6149 | 81% | 0 | 24.4838 | 10% | 0 | 40.7281
5156 | 0 | 2 | 2 | 3 | 25.9 | 0 | 0 | 0 | 0 | 104.8842 | 41.2888 | 0 | 108.9948 | 74% | 0 | 0 | 10% | 0 | 38.2674
5157 | 0 | 0 | 0 | 2.5 | 24.6 | 0 | 0 | 0 | 0 | 98.3967 | 38.7329 | 0 | 99.5828 | 66% | 0 | 0 | 10% | 0 | 36.0883
5158 | 0 | 0 | 0 | 2.1 | 23.8 | 0 | 0 | 0 | 0 | 93.0076 | 36.5753 | 0 | 92.6246 | 59% | 0 | 0 | 10% | 0 | 34.0672
5159 | 0 | 0 | 0 | 2.3 | 23.2 | 0 | 0 | 0 | 0 | 88.6856 | 34.8153 | 0 | 87.1756 | 53% | 0 | 0 | 10% | 0 | 32.349
5160 | 0 | 0 | 0 | 2.3 | 23.2 | 0 | 0 | 0 | 0 | 86.2057 | 33.7792 | 0 | 84.2248 | 46% | 0 | 0 | 10% | 0 | 31.3037
5161 | 0 | 0 | 0 | 2.5 | 23.4 | 0 | 0 | 0 | 0 | 84.3859 | 33.0035 | 0 | 82.1404 | 40% | 0 | 0 | 10% | 0 | 30.5035
5162 | 0 | 0 | 0 | 1.5 | 23.1 | 0 | 0 | 0 | 0 | 83.8636 | 32.8145 | 0 | 81.6141 | 34% | 0 | 0 | 10% | 0 | 30.2831
5163 | 0 | 0 | 0 | 1.1 | 22.9 | 0 | 0 | 0 | 0 | 84.1117 | 32.9358 | 0 | 81.9869 | 28% | 0 | 0 | 10% | 0 | 30.3753
5164 | 0 | 0 | 0 | 1.3 | 22.7 | 0 | 0 | 0 | 0 | 82.8317 | 32.4167 | 0 | 80.5635 | 22% | 0 | 0 | 10% | 0 | 29.8352
5165 | 0 | 0 | 0 | 1.2 | 23 | 0 | 0 | 0 | 0 | 85.9555 | 33.6959 | 0 | 84.3121 | 16% | 0 | 0 | 10% | 0 | 31.085
5166 | 12 | 19 | 17 | 1.2 | 23 | 0 | 0.67524 | 0 | 0 | 91.3851 | 35.972 | 0 | 90.9502 | 9% | 0 | 0 | 10% | 0 | 33.3427
5167 | 218 | 147 | 90 | 1.2 | 24.1 | 0 | 43.4235 | 0.51235 | 0 | 95.7583 | 37.6974 | 0 | 96.2327 | 2% | 0 | 0 | 10% | 0 | 35.5885
5168 | 439 | 343 | 148 | 1.3 | 25.6 | 72.4438 | 17.5891 | 13.5352 | 0 | 67.241 | 25.2223 | 17.2959 | 12.0212 | 2% | 0 | 0 | 10% | 0 | 37.2793
5169 | 559 | 537 | 191 | 1.2 | 27.3 | 133.4691 | 0 | 31.2406 | 0 | 44.6174 | 15.3893 | 89.2321 | 0 | 9% | 6.6132 | 0 | 18.99% | 0 | 38.4069
5170 | 629 | 701 | 220 | 1.2 | 29.7 | 162.7192 | 0 | 47.2943 | 0 | 45.6961 | 15.6053 | 117.7891 | 0 | 18% | 21.4606 | 0 | 48.18% | 0 | 39.5655
5171 | 678 | 828 | 233 | 2.2 | 32.2 | 183.3474 | 0 | 53.2886 | 6.4678 | 42.5957 | 14.1286 | 141.5029 | 0 | 28% | 25 | 0 | 82.18% | 0 | 40.3575
5172 | 691 | 899 | 248 | 2.7 | 33.9 | 191.2957 | 0 | 33.5855 | 33.0415 | 42.6022 | 13.9701 | 149.5001 | 0 | 39% | 5.7497 | 0 | 90% | 0 | 39.6608
5173 | 672 | 908 | 265 | 3 | 34.6 | 186.3726 | 0 | 27.1025 | 40.1251 | 42.6042 | 13.9032 | 144.5512 | 0 | 50% | 0 | 0 | 90% | 0 | 38.8944
5174 | 645 | 862 | 268 | 4.6 | 34.1 | 174.4769 | -2.98e-14 | 26.6648 | 35.7979 | 42.6052 | 13.9519 | 132.6011 | 0 | 60% | 0 | 0 | 90% | 0 | 38.6025
5175 | 601 | 760 | 260 | 5.1 | 33.1 | 155.795 | 0 | 26.0905 | 26.2814 | 42.6052 | 14.0474 | 113.8548 | 0 | 68% | 0 | 0 | 90% | 0 | 38.2862
5176 | 543 | 613 | 233 | 4.2 | 33.3 | 132.9812 | 0 | 24.789 | 13.5958 | 42.6046 | 14.0281 | 90.9565 | 0 | 75% | 0 | 0 | 90% | 0 | 38.444
5177 | 439 | 431 | 195 | 4 | 32.9 | 94.2753 | 0 | 21.1668 | 0 | 42.6034 | 14.0656 | 52.3655 | 0 | 78% | 0 | 3.2651 | 84.78% | 0 | 38.9417
5178 | 304 | 240 | 133 | 4 | 32.5 | 0 | 56.9968 | 5.8387 | 0 | 42.6005 | 14.1021 | 0 | 41.1467 | 75% | 0 | 22.5928 | 48.63% | 0 | 40.4174
5179 | 108 | 72 | 52 | 3.7 | 31 | 0 | 17.8483 | 0 | 0 | 55.9213 | 19.7609 | 0 | 54.6414 | 71% | 0 | 24.1421 | 10% | 0 | 40.9067
5180 | 1 | 2 | 2 | 2.4 | 28.5 | 0 | 0 | 0 | 0 | 106.495 | 41.6256 | 0 | 110.8817 | 63% | 0 | 0 | 10% | 0 | 38.6119
5181 | 0 | 0 | 0 | 2 | 26.3 | 0 | 0 | 0 | 0 | 99.1497 | 38.8581 | 0 | 100.7206 | 56% | 0 | 0 | 10% | 0 | 36.1429
5182 | 0 | 0 | 0 | 2.4 | 25.6 | 0 | 0 | 0 | 0 | 93.255 | 36.4946 | 0 | 93.1851 | 49% | 0 | 0 | 10% | 0 | 33.9069
5183 | 0 | 0 | 0 | 1.2 | 24.8 | 0 | 0 | 0 | 0 | 89.273 | 34.9062 | 0 | 88.1064 | 42% | 0 | 0 | 10% | 0 | 32.3666
5184 | 0 | 0 | 0 | 1.2 | 24.4 | 0 | 0 | 0 | 0 | 87.4862 | 34.1995 | 0 | 85.9246 | 36% | 0 | 0 | 10% | 0 | 31.6643
5185 | 0 | 0 | 0 | 0.7 | 24 | 0 | 0 | 0 | 0 | 86.6223 | 33.8792 | 0 | 84.9089 | 30% | 0 | 0 | 10% | 0 | 31.3353
5186 | 0 | 0 | 0 | 1.1 | 23.4 | 0 | 0 | 0 | 0 | 87.5309 | 34.3149 | 0 | 86.035 | 23% | 0 | 0 | 10% | 0 | 31.7563
5187 | 0 | 0 | 0 | 1.1 | 23.2 | 0 | 0 | 0 | 0 | 93.6654 | 36.9133 | 0 | 93.6012 | 16% | 0 | 0 | 10% | 0 | 34.3371
5188 | 0 | 0 | 0 | 1.3 | 22.5 | 0 | 0 | 0 | 0 | 99.2388 | 39.2916 | 0 | 100.1447 | 9% | 0 | 0 | 10% | 0 | 36.7302
5189 | 0 | 0 | 0 | 0.9 | 22.7 | 0 | 0 | 0 | 0 | 107.3281 | 42.6352 | 0 | 109.7346 | 1% | 0 | 0 | 10% | 0 | 40.0995
5190 | 14 | 18 | 16 | 1.2 | 21.6 | 0 | 0.73075 | 0 | 0 | 7.5801 | 3.0261 | 0 | 7.824 | 0% | 0 | 0 | 10% | 0 | 0.69961
5191 | 255 | 150 | 86 | 0.7 | 23.6 | 0 | 50.6269 | 0.49116 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8024
5192 | 472 | 345 | 139 | 1.3 | 26.5 | 78.6812 | 19.0723 | 13.7312 | 0 | 0 | 0 | 75.7858 | 0 | 6% | 0 | 0 | 10% | 0 | 12.3077
5193 | 606 | 543 | 172 | 2.8 | 29.3 | 145.3697 | 0 | 31.6728 | 0 | 0 | 0 | 143.1366 | 0 | 16% | 0 | 0 | 10% | 0 | 29.9835
5194 | 668 | 707 | 199 | 2.8 | 31.5 | 173.1008 | 0 | 47.9992 | 0 | 0 | 0 | 171.4505 | 0 | 29% | 0 | 0 | 10% | 0 | 46.0435
5195 | 694 | 831 | 224 | 2.8 | 32.9 | 187.7133 | 0 | 60.2469 | 0 | 0 | 0 | 186.2905 | 0 | 43% | 8.8826 | 0 | 22.08% | 0 | 49.2527
5196 | 684 | 897 | 253 | 3.5 | 33.9 | 188.598 | 0 | 66.551 | 0 | 0 | 0 | 187.3335 | 0 | 57% | 16.1823 | 0 | 44.09% | 0 | 48.222
5197 | 658 | 905 | 275 | 4.4 | 34.8 | 180.9083 | 2.98e-14 | 66.8671 | 0 | 0 | 0 | 179.7421 | 0 | 71% | 16.7924 | 0 | 66.93% | 0 | 47.973
5198 | 650 | 862 | 265 | 4.1 | 35 | 176.2086 | 0 | 62.5477 | 0 | 0 | 0 | 175.0565 | 0 | 84% | 12.6839 | 0 | 84.18% | 0 | 47.7825
5199 | 622 | 758 | 241 | 5.7 | 34.7 | 161.2584 | 2.27e-14 | 50.7163 | 1.5594 | 42.5866 | 0 | 119.9742 | 0 | 93% | 4.2823 | 0 | 90% | 0 | 43.9702
5200 | 567 | 617 | 221 | 4.6 | 34.7 | 139.2925 | 0 | 33.4508 | 5.2204 | 43.0293 | 13.2544 | 97.0173 | 0 | 100% | 0.7072 | 0.60112 | 90% | 0 | 46.8083
5201 | 496 | 441 | 178 | 4.9 | 34.8 | 41.4799 | 83.5873 | 21.8712 | 0 | 42.5885 | 13.8787 | 0 | 0 | 100% | 0 | 9.5342 | 74.74% | 0 | 45.9923
5202 | 336 | 242 | 126 | 3.8 | 34 | 0 | 64.1776 | 5.8382 | 0 | 51.6049 | 17.6153 | 0 | 50.0704 | 96% | 0 | 25 | 34.74% | 0 | 46.3545
5203 | 108 | 71 | 52 | 3.8 | 30.9 | 0 | 17.7491 | 0 | 0 | 85.9128 | 32.4111 | 0 | 87.9965 | 90% | 0 | 15.4658 | 10% | 0 | 44.9326
5204 | 0 | 2 | 2 | 2.4 | 28.3 | 0 | 0 | 0 | 0 | 112.5539 | 44.1308 | 0 | 115.8937 | 81% | 0 | 0 | 10% | 0 | 41.671
5205 | 0 | 0 | 0 | 2.4 | 26.4 | 0 | 0 | 0 | 0 | 104.3122 | 40.9922 | 0 | 104.5131 | 73% | 0 | 0 | 10% | 0 | 38.9212
5206 | 0 | 0 | 0 | 2.1 | 23.8 | 0 | 0 | 0 | 0 | 97.3078 | 38.364 | 0 | 95.9364 | 66% | 0 | 0 | 10% | 0 | 36.3626
5207 | 0 | 0 | 0 | 0.3 | 23.1 | 0 | 0 | 0 | 0 | 93.3582 | 36.791 | 0 | 91.407 | 59% | 0 | 0 | 10% | 0 | 34.7605
5208 | 0 | 0 | 0 | 0.8 | 23.2 | 0 | 0 | 0 | 0 | 91.2366 | 35.8872 | 0 | 88.9823 | 52% | 0 | 0 | 10% | 0 | 33.8066
5209 | 0 | 0 | 0 | 1.3 | 22.9 | 0 | 0 | 0 | 0 | 90.3387 | 35.5377 | 0 | 88.0698 | 46% | 0 | 0 | 10% | 0 | 33.4025
5210 | 0 | 0 | 0 | 0.9 | 22.7 | 0 | 0 | 0 | 0 | 91.4599 | 36.0276 | 0 | 89.5838 | 39% | 0 | 0 | 10% | 0 | 33.8421
5211 | 0 | 0 | 0 | 0.7 | 22 | 0 | 0 | 0 | 0 | 96.5402 | 38.2156 | 0 | 95.7709 | 32% | 0 | 0 | 10% | 0 | 35.9913
5212 | 0 | 0 | 0 | 0.5 | 21.6 | 0 | 0 | 0 | 0 | 101.9593 | 40.506 | 0 | 102.1782 | 24% | 0 | 0 | 10% | 0 | 38.2748
5213 | 0 | 0 | 0 | 1.1 | 22.3 | 0 | 0 | 0 | 0 | 109.8492 | 43.7098 | 0 | 111.4238 | 16% | 0 | 0 | 10% | 0 | 41.4899
5214 | 16 | 19 | 17 | 1.2 | 21.9 | 0 | 0.76982 | 0 | 0 | 117.2344 | 46.7957 | 0 | 119.9862 | 7% | 0 | 0 | 10% | 0 | 44.6121
5215 | 264 | 150 | 84 | 1 | 23.1 | 0 | 52.2403 | 0.45862 | 0 | 84.0872 | 33.5125 | 0 | 86.3528 | 0% | 0 | 0 | 10% | 0 | 31.915
5216 | 514 | 351 | 128 | 0.8 | 26.5 | 86.8003 | 20.9855 | 14.0589 | 0 | 0 | 0 | 83.8011 | 0 | 6% | 0 | 0 | 10% | 0 | 12.6227
5217 | 658 | 550 | 151 | 0.8 | 31 | 160.0751 | -2.98e-14 | 32.389 | 0 | 0 | 0 | 157.9987 | 0 | 18% | 0 | 0 | 10% | 0 | 30.5474
5218 | 716 | 715 | 174 | 2.4 | 32.6 | 186.852 | 0 | 49.0118 | 0 | 0 | 0 | 185.337 | 0 | 33% | 0 | 0 | 10% | 0 | 46.9036
5219 | 743 | 844 | 199 | 4.8 | 34.7 | 200.5975 | 0 | 61.7125 | 0 | 0 | 0 | 199.2668 | 0 | 48% | 10.2125 | 0 | 23.89% | 0 | 49.2369
5220 | 758 | 920 | 210 | 4.4 | 36.1 | 209.97 | 2.98e-14 | 68.874 | 0 | 0 | 0 | 208.7143 | 0 | 64% | 17.7393 | 0 | 48.01% | 0 | 48.7523
5221 | 736 | 928 | 227 | 3.3 | 37.6 | 205.3353 | -2.98e-14 | 69.1727 | 0 | 0 | 0 | 204.1882 | 0 | 79% | 18.322 | 0 | 72.93% | 0 | 48.4781
5222 | 721 | 887 | 229 | 3.3 | 38.5 | 198.0802 | 0 | 63.0382 | 1.7355 | 0 | 0 | 196.9677 | 0 | 94% | 12.5497 | 0 | 90% | 0 | 48.1508
5223 | 673 | 782 | 226 | 3.5 | 39.2 | 119.2988 | 68.9957 | 49.1699 | 4.779 | 42.5964 | 0.8482 | 78.5369 | 0 | 100% | 0 | 0 | 90% | 0 | 47.9632
5224 | 600 | 632 | 216 | 3.8 | 39.4 | 42.1138 | 128.2388 | 33.0923 | 6.4096 | 42.5957 | 13.4193 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 47.189
5225 | 491 | 443 | 185 | 4.2 | 38.7 | 42.1571 | 81.3719 | 21.8996 | 0 | 42.5934 | 13.4905 | 0 | 0 | 100% | 0 | 10.248 | 73.6% | 0 | 46.3454
5226 | 293 | 236 | 133 | 5.2 | 34 | 0 | 54.0925 | 5.6734 | 0 | 53.2592 | 18.3107 | 0 | 51.728 | 96% | 0 | 25 | 33.6% | 0 | 46.8773
5227 | 66 | 67 | 55 | 4.5 | 30.3 | 0 | 10.7843 | 0 | 0 | 88.2494 | 33.4739 | 0 | 90.6772 | 90% | 0 | 14.752 | 10% | 0 | 45.2796
5228 | 0 | 1 | 1 | 4.4 | 28.4 | 0 | 0 | 0 | 0 | 112.7513 | 44.1978 | 0 | 115.9957 | 81% | 0 | 0 | 10% | 0 | 41.7679
5229 | 0 | 0 | 0 | 2.9 | 24.8 | 0 | 0 | 0 | 0 | 104.1032 | 41.0859 | 0 | 104.205 | 73% | 0 | 0 | 10% | 0 | 39.0279
5230 | 0 | 0 | 0 | 2.7 | 24.3 | 0 | 0 | 0 | 0 | 98.0378 | 38.6158 | 0 | 96.7672 | 66% | 0 | 0 | 10% | 0 | 36.6189
5231 | 0 | 0 | 0 | 1 | 23.8 | 0 | 0 | 0 | 0 | 94.0415 | 37.0128 | 0 | 92.2086 | 59% | 0 | 0 | 10% | 0 | 34.9918
5232 | 0 | 0 | 0 | 0.9 | 23.7 | 0 | 0 | 0 | 0 | 92.0598 | 36.1861 | 0 | 89.9276 | 52% | 0 | 0 | 10% | 0 | 34.1201
5233 | 0 | 0 | 0 | 0.6 | 24.3 | 0 | 0 | 0 | 0 | 91.6625 | 35.9605 | 0 | 89.6055 | 45% | 0 | 0 | 10% | 0 | 33.8436
5234 | 0 | 0 | 0 | 1 | 25.8 | 0 | 0 | 0 | 0 | 92.8649 | 36.3107 | 0 | 91.2094 | 38% | 0 | 0 | 10% | 0 | 34.1502
5235 | 0 | 0 | 0 | 1.5 | 24.5 | 0 | 0 | 0 | 0 | 97.9493 | 38.56 | 0 | 97.3023 | 31% | 0 | 0 | 10% | 0 | 36.3668
5236 | 0 | 0 | 0 | 1.7 | 23.1 | 0 | 0 | 0 | 0 | 103.481 | 41.0028 | 0 | 103.8691 | 23% | 0 | 0 | 10% | 0 | 38.8044
5237 | 0 | 0 | 0 | 1 | 22.8 | 0 | 0 | 0 | 0 | 110.5442 | 43.9478 | 0 | 112.0782 | 14% | 0 | 0 | 10% | 0 | 41.7643
5238 | 6 | 16 | 16 | 0.9 | 22.8 | 0 | 0.26415 | 0 | 0 | 117.9289 | 46.9908 | 0 | 120.6492 | 5% | 0 | 0 | 10% | 0 | 44.841
5239 | 148 | 137 | 99 | 1.7 | 25 | 0 | 29.1884 | 0.6422 | 0 | 68.3591 | 27.1227 | 0 | 70.0542 | 0% | 0 | 0 | 10% | 0 | 25.7659
5240 | 399 | 356 | 183 | 1.5 | 30.2 | 63.8746 | 15.558 | 14.5474 | 0 | 0 | 0 | 61.6651 | 0 | 5% | 0 | 0 | 10% | 0 | 13.3143
5241 | 468 | 510 | 225 | 2.1 | 34.2 | 108.3221 | 0 | 29.0786 | 0 | 0 | 0 | 106.4894 | 0 | 13% | 0 | 0 | 10% | 0 | 27.6999
5242 | 573 | 705 | 270 | 3.1 | 36.3 | 145.7968 | 0 | 47.3717 | 0 | 0 | 0 | 144.0859 | 0 | 24% | 0 | 0 | 10% | 0 | 45.6453
5243 | 608 | 823 | 292 | 3.4 | 38.5 | 161.9011 | 0 | 59.018 | 0 | 0 | 0 | 160.5028 | 0 | 36% | 8.3825 | 0 | 21.4% | 0 | 48.7435
5244 | 721 | 970 | 293 | 4 | 40.1 | 199.3137 | 0 | 71.1083 | 0 | 0 | 0 | 197.8077 | 0 | 51% | 21.761 | 0 | 51% | 0 | 47.0889
5245 | 301 | 817 | 521 | 4 | 40.1 | 72.7041 | 0 | 57.2527 | 0 | 0 | 0 | 72.2604 | 0 | 57% | 8.5807 | 0 | 62.67% | 0 | 47.5675
5246 | 126 | 569 | 447 | 3.6 | 39 | 0 | 40.3609 | 35.9578 | 0.050496 | 42.5803 | 1.8539 | 0 | 39.5009 | 54% | 0 | 10.8082 | 45.37% | 0 | 47.148
5247 | 282 | 630 | 396 | 5.8 | 37.4 | 51.3629 | 12.6163 | 41.2297 | 0 | 45.366 | 14.7048 | 15.1865 | 7.6304 | 54% | 8.4589 | 0 | 56.88% | 0 | 46.2948
5248 | 266 | 547 | 355 | 5.6 | 37.4 | 53.9499 | 0 | 31.7185 | 0 | 45.6604 | 14.8195 | 10.2733 | 0 | 55% | 0 | 0 | 56.88% | 0 | 45.5975
5249 | 36 | 257 | 235 | 5.9 | 36 | 0 | 9.8288 | 9.4173 | 0 | 42.5707 | 13.7553 | 0 | 39.9665 | 52% | 0 | 23.2342 | 19.7% | 0 | 45.0558
5250 | 1 | 105 | 105 | 4 | 34.8 | 0 | 0.22792 | 0.61562 | 0 | 109.4319 | 41.6362 | 0 | 112.7728 | 43% | 0 | 6.0633 | 10% | 0 | 45.9311
5251 | 0 | 28 | 28 | 2.9 | 33.5 | 0 | 0 | 0 | 0 | 120.7151 | 46.6252 | 0 | 124.5606 | 34% | 0 | 0 | 10% | 0 | 44.376
5252 | 0 | 0 | 0 | 1.2 | 31.6 | 0 | 0 | 0 | 0 | 112.2023 | 43.4978 | 0 | 113.7403 | 25% | 0 | 0 | 10% | 0 | 41.3893
5253 | 0 | 0 | 0 | 1 | 29.8 | 0 | 0 | 0 | 0 | 105.0327 | 40.8523 | 0 | 105.1026 | 17% | 0 | 0 | 10% | 0 | 38.8085
5254 | 0 | 0 | 0 | 1 | 28.5 | 0 | 0 | 0 | 0 | 98.9544 | 38.5105 | 0 | 97.7838 | 10% | 0 | 0 | 10% | 0 | 36.4913
5255 | 0 | 0 | 0 | 1.4 | 28.8 | 0 | 0 | 0 | 0 | 94.7063 | 36.7245 | 0 | 92.8741 | 3% | 0 | 0 | 10% | 0 | 34.6997
5256 | 0 | 0 | 0 | 1.7 | 27.8 | 0 | 0 | 0 | 0 | 39.6674 | 15.4072 | 0 | 38.7145 | 0% | 0 | 0 | 10% | 0 | 13.4238
5257 | 0 | 0 | 0 | 2 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.928
5258 | 0 | 0 | 0 | 1.2 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9127
5259 | 0 | 0 | 0 | 1.9 | 25.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8976
5260 | 0 | 0 | 0 | 2.9 | 26.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8827
5261 | 0 | 0 | 0 | 0.7 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8684
5262 | 5 | 16 | 15 | 1.4 | 23.6 | 0 | 0.19966 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8541
5263 | 164 | 141 | 100 | 1.5 | 26.5 | 0 | 32.2351 | 0.73763 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.1023
5264 | 371 | 337 | 177 | 0.6 | 29.7 | 58.666 | 14.2308 | 13.5428 | 0 | 0 | 0 | 55.8843 | 0 | 4% | 0 | 0 | 10% | 0 | 12.3623
5265 | 499 | 535 | 231 | 0.9 | 32.1 | 117.2953 | 0 | 31.217 | 0 | 0 | 0 | 114.346 | 0 | 13% | 0 | 0 | 10% | 0 | 29.759
5266 | 593 | 712 | 261 | 1.1 | 34.2 | 152.3286 | 2.98e-14 | 48.41 | 0 | 0 | 0 | 150.1023 | 0 | 25% | 0 | 0 | 10% | 0 | 46.6213
5267 | 670 | 850 | 267 | 1.7 | 35.4 | 180.9767 | -2.98e-14 | 61.4242 | 0 | 0 | 0 | 179.0781 | 0 | 38% | 9.9242 | 0 | 23.5% | 0 | 49.4295
5268 | 713 | 925 | 259 | 2.5 | 36.3 | 197.7997 | 0 | 69.1384 | 0 | 0 | 0 | 196.1523 | 0 | 53% | 17.6384 | 0 | 47.48% | 0 | 49.2464
5269 | 734 | 943 | 248 | 3.4 | 36.6 | 204.6106 | 0 | 71.0485 | 0 | 0 | 0 | 203.1349 | 0 | 69% | 19.7746 | 0 | 74.38% | 0 | 48.9248
5270 | 718 | 894 | 243 | 5.6 | 36.4 | 195.2411 | -1.5e-14 | 62.6719 | 3.5724 | 0 | 0 | 193.9404 | 0 | 84% | 11.4864 | 0 | 90% | 0 | 48.8885
5271 | 665 | 785 | 240 | 6.7 | 35.9 | 172.7792 | 0 | 51.291 | 3.881 | 42.5634 | 0 | 132.2408 | 0 | 94% | 0 | 0 | 90% | 0 | 48.6847
5272 | 556 | 622 | 238 | 6.3 | 35.3 | 127.3629 | 8.8319 | 39.4104 | 0 | 43.1285 | 9.3544 | 85.2931 | 0 | 100% | 3.6442 | 3.5207 | 89.32% | 0 | 47.3639
5273 | 445 | 433 | 200 | 4.7 | 35 | 42.1521 | 67.3059 | 21.6518 | 0 | 42.5706 | 13.8535 | 0 | 0 | 100% | 0 | 10.5067 | 72.51% | 0 | 46.7202
5274 | 299 | 234 | 133 | 4 | 34 | 0 | 55.082 | 5.7608 | 0 | 53.6231 | 18.4671 | 0 | 52.0928 | 96% | 0 | 25 | 32.51% | 0 | 47.1271
5275 | 99 | 67 | 50 | 2.9 | 31.5 | 0 | 15.9815 | 0 | 0 | 91.5145 | 34.6807 | 0 | 94.4309 | 89% | 0 | 14.0702 | 10% | 0 | 45.8043
5276 | 1 | 1 | 1 | 2 | 28.6 | 0 | 0 | 0 | 0 | 114.7441 | 44.9893 | 0 | 118.1833 | 80% | 0 | 0 | 10% | 0 | 42.6096
5277 | 0 | 0 | 0 | 0.8 | 26.7 | 0 | 0 | 0 | 0 | 106.1074 | 41.6989 | 0 | 106.3681 | 72% | 0 | 0 | 10% | 0 | 39.6951
5278 | 0 | 0 | 0 | 0.3 | 25.7 | 0 | 0 | 0 | 0 | 99.726 | 39.167 | 0 | 98.5289 | 65% | 0 | 0 | 10% | 0 | 37.2293
5279 | 0 | 0 | 0 | 0.5 | 25 | 0 | 0 | 0 | 0 | 95.1192 | 37.3381 | 0 | 93.2424 | 58% | 0 | 0 | 10% | 0 | 35.378
5280 | 0 | 0 | 0 | 0.3 | 24.3 | 0 | 0 | 0 | 0 | 92.8105 | 36.4453 | 0 | 90.6535 | 51% | 0 | 0 | 10% | 0 | 34.4366
5281 | 0 | 0 | 0 | 1 | 23.9 | 0 | 0 | 0 | 0 | 91.7666 | 36.0455 | 0 | 89.5501 | 44% | 0 | 0 | 10% | 0 | 33.9845
5282 | 0 | 0 | 0 | 0.3 | 23.8 | 0 | 0 | 0 | 0 | 92.2545 | 36.261 | 0 | 90.2987 | 37% | 0 | 0 | 10% | 0 | 34.1508
5283 | 0 | 0 | 0 | 0.5 | 23.7 | 0 | 0 | 0 | 0 | 97.293 | 38.37 | 0 | 96.3926 | 30% | 0 | 0 | 10% | 0 | 36.2171
5284 | 0 | 0 | 0 | 0.3 | 22.4 | 0 | 0 | 0 | 0 | 102.2349 | 40.5496 | 0 | 102.2545 | 22% | 0 | 0 | 10% | 0 | 38.3847
5285 | 0 | 0 | 0 | 1.3 | 23.1 | 0 | 0 | 0 | 0 | 109.5044 | 43.4912 | 0 | 110.7698 | 14% | 0 | 0 | 10% | 0 | 41.3311
5286 | 13 | 16 | 15 | 1.4 | 23.5 | 0 | 0.46591 | 0 | 0 | 118.3812 | 47.104 | 0 | 121.1342 | 5% | 0 | 0 | 10% | 0 | 44.9682
5287 | 282 | 155 | 87 | 0.6 | 25.9 | 0 | 55.2404 | 0.68168 | 0 | 58.223 | 23.0653 | 0 | 59.8565 | 0% | 0 | 0 | 10% | 0 | 21.7791
5288 | 535 | 363 | 137 | 0.9 | 30.2 | 90.6314 | 21.6436 | 15.181 | 0 | 0 | 0 | 87.4346 | 0 | 7% | 0 | 0 | 10% | 0 | 13.7195
5289 | 651 | 566 | 175 | 2.3 | 34.2 | 157.474 | 0 | 33.7452 | 0 | 0 | 0 | 155.4572 | 0 | 19% | 0 | 0 | 10% | 0 | 31.9235
5290 | 739 | 747 | 191 | 3 | 36.4 | 193.3243 | -2.98e-14 | 51.4589 | 0 | 0 | 0 | 191.7115 | 0 | 33% | 0 | 0 | 10% | 0 | 49.2895
5291 | 772 | 875 | 207 | 4 | 37.9 | 209.8367 | -2.98e-14 | 64.1663 | 0 | 0 | 0 | 208.4692 | 0 | 49% | 12.6663 | 0 | 27.23% | 0 | 49.1474
5292 | 764 | 941 | 230 | 5.1 | 38.9 | 211.2587 | 0 | 70.5929 | 0 | 0 | 0 | 210.037 | 0 | 65% | 19.0929 | 0 | 53.19% | 0 | 49.0992
5293 | 750 | 956 | 247 | 5.9 | 39.8 | 207.4049 | 0 | 71.4128 | 0 | 0 | 0 | 206.2478 | 0 | 81% | 20.3225 | 0 | 80.83% | 0 | 48.6919
5294 | 705 | 901 | 260 | 6.8 | 40.3 | 190.4626 | -1.65e-14 | 57.8024 | 7.8836 | 0 | 0 | 189.3585 | 0 | 95% | 6.7418 | 0 | 90% | 0 | 48.7877
5295 | 654 | 792 | 254 | 7.3 | 40.4 | 104.7654 | 77.5903 | 49.5393 | 5.0875 | 42.5955 | 0.604 | 64.1095 | 0 | 100% | 0 | 0 | 90% | 0 | 48.22
5296 | 556 | 632 | 247 | 6.3 | 40.6 | 42.082 | 113.7209 | 33.2283 | 6.1585 | 42.5946 | 13.2952 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 47.1792
5297 | 415 | 436 | 217 | 5.7 | 40.2 | 42.1574 | 57.8098 | 21.2427 | 0 | 42.5923 | 13.3357 | 0 | 0 | 100% | 0 | 10.8786 | 72.59% | 0 | 46.164
5298 | 244 | 233 | 150 | 3.9 | 38.1 | 0 | 55.2918 | 5.882 | 0 | 52.0618 | 17.3414 | 0 | 50.5287 | 96% | 0 | 25 | 32.59% | 0 | 46.1298
5299 | 51 | 65 | 56 | 1.9 | 35 | 0 | 8.1798 | 0 | 0 | 89.9533 | 33.4907 | 0 | 92.6886 | 90% | 0 | 14.1214 | 10% | 0 | 44.6661
5300 | 1 | 1 | 1 | 1.1 | 30.4 | 0 | 0 | 0 | 0 | 113.4682 | 44.2026 | 0 | 116.6927 | 81% | 0 | 0 | 10% | 0 | 41.8105
5301 | 0 | 0 | 0 | 1.2 | 29.4 | 0 | 0 | 0 | 0 | 106.5615 | 41.5299 | 0 | 106.9865 | 73% | 0 | 0 | 10% | 0 | 39.5013
5302 | 0 | 0 | 0 | 0.6 | 28.4 | 0 | 0 | 0 | 0 | 100.081 | 38.9861 | 0 | 98.9848 | 65% | 0 | 0 | 10% | 0 | 37.036
5303 | 0 | 0 | 0 | 0.9 | 29.6 | 0 | 0 | 0 | 0 | 95.8027 | 37.064 | 0 | 94.0495 | 58% | 0 | 0 | 10% | 0 | 35.0967
5304 | 0 | 0 | 0 | 0.7 | 29.1 | 0 | 0 | 0 | 0 | 92.586 | 35.7966 | 0 | 90.374 | 51% | 0 | 0 | 10% | 0 | 33.7872
5305 | 0 | 0 | 0 | 0.7 | 28.3 | 0 | 0 | 0 | 0 | 90.4741 | 35.0138 | 0 | 87.9864 | 44% | 0 | 0 | 10% | 0 | 32.9513
5306 | 0 | 0 | 0 | 0.7 | 28 | 0 | 0 | 0 | 0 | 89.6559 | 34.7101 | 0 | 87.1795 | 38% | 0 | 0 | 10% | 0 | 32.5915
5307 | 0 | 0 | 0 | 0.9 | 27.1 | 0 | 0 | 0 | 0 | 90.4647 | 35.1561 | 0 | 88.3115 | 31% | 0 | 0 | 10% | 0 | 32.9861
5308 | 0 | 0 | 0 | 1.2 | 26.7 | 0 | 0 | 0 | 0 | 90.9578 | 35.4092 | 0 | 89.0207 | 24% | 0 | 0 | 10% | 0 | 33.2025
5309 | 0 | 0 | 0 | 0.7 | 26 | 0 | 0 | 0 | 0 | 95.2534 | 37.2864 | 0 | 94.3051 | 17% | 0 | 0 | 10% | 0 | 35.045
5310 | 5 | 14 | 14 | 1.3 | 26.3 | 0 | 0.15875 | 0 | 0 | 103.5985 | 40.7109 | 0 | 104.2221 | 9% | 0 | 0 | 10% | 0 | 38.4518
5311 | 166 | 138 | 96 | 2.2 | 28.3 | 0 | 32.4061 | 0.59912 | 0 | 109.0762 | 42.7116 | 0 | 110.5706 | 1% | 0 | 0 | 10% | 0 | 41.0698
5312 | 383 | 334 | 170 | 2.1 | 31.5 | 60.3427 | 14.6472 | 13.3957 | 0 | 75.8105 | 28.2999 | 0 | 13.9577 | 0% | 0 | 0 | 10% | 0 | 40.3761
5313 | 467 | 528 | 244 | 4.1 | 33.7 | 106.9004 | 0 | 30.6456 | 0 | 43.7979 | 14.4625 | 64.2362 | 0 | 5% | 0 | 0 | 10% | 0 | 43.7165
5314 | 527 | 669 | 271 | 3.2 | 34.6 | 132.7015 | 0 | 45.1495 | 0 | 45.9154 | 15.2117 | 88.2035 | 0 | 12% | 14.2162 | 0 | 29.33% | 0 | 44.5194
5315 | 653 | 832 | 261 | 2.2 | 36.1 | 175.9207 | 0 | 57.6774 | 2.1641 | 42.5957 | 13.7534 | 134.4401 | 0 | 22% | 25 | 0 | 63.33% | 0 | 44.4235
5316 | 715 | 910 | 240 | 2.7 | 37.4 | 198.521 | 0 | 51.5942 | 16.3173 | 42.6035 | 13.6258 | 157.1697 | 0 | 33% | 19.6073 | 0 | 90% | 0 | 43.3883
5317 | 561 | 897 | 360 | 4.5 | 38.4 | 151.4919 | 0 | 30.9477 | 35.4193 | 42.6063 | 13.5253 | 110.4393 | 0 | 42% | 0 | 0 | 90% | 0 | 42.6606
5318 | 737 | 892 | 223 | 6 | 38.9 | 200.8059 | 0 | 30.7917 | 35.0846 | 42.6057 | 13.474 | 159.0491 | 0 | 53% | 0 | 0 | 90% | 0 | 42.0035
5319 | 699 | 791 | 218 | 6.4 | 39.2 | 183.2426 | 2.98e-14 | 30.2286 | 25.2119 | 42.6068 | 13.4435 | 141.7742 | 0 | 64% | 0 | 0 | 90% | 0 | 41.5558
5320 | 605 | 625 | 209 | 5.9 | 39.1 | 148.5025 | 0 | 29.5568 | 9.9395 | 42.6068 | 13.4538 | 106.997 | 0 | 72% | 0 | 0 | 90% | 0 | 41.2077
5321 | 488 | 434 | 179 | 4.6 | 38.9 | 105.4329 | 0 | 21.4585 | 0 | 42.6057 | 13.474 | 63.8649 | 0 | 77% | 0 | 7.361 | 78.22% | 0 | 40.8881
5322 | 318 | 232 | 125 | 5 | 36.5 | 0 | 59.0006 | 5.5112 | 0 | 43.6215 | 14.1121 | 0 | 42.005 | 74% | 0 | 24.3556 | 39.25% | 0 | 41.9512
5323 | 72 | 59 | 46 | 5.6 | 32.8 | 0 | 11.4712 | 0 | 0 | 69.8399 | 25.4249 | 0 | 70.1078 | 68% | 0 | 18.2834 | 10% | 0 | 40.7828
5324 | 0 | 1 | 1 | 4.4 | 30.3 | 0 | 0 | 0 | 0 | 106.1212 | 41.2207 | 0 | 109.7746 | 60% | 0 | 0 | 10% | 0 | 38.367
5325 | 0 | 0 | 0 | 3 | 27 | 0 | 0 | 0 | 0 | 99.4187 | 38.8874 | 0 | 100.661 | 53% | 0 | 0 | 10% | 0 | 36.2719
5326 | 0 | 0 | 0 | 1.1 | 23.4 | 0 | 0 | 0 | 0 | 92.9846 | 36.6035 | 0 | 92.5734 | 46% | 0 | 0 | 10% | 0 | 34.0924
5327 | 0 | 0 | 0 | 0.9 | 23.5 | 0 | 0 | 0 | 0 | 88.7864 | 34.8293 | 0 | 87.3109 | 39% | 0 | 0 | 10% | 0 | 32.3503
5328 | 0 | 0 | 0 | 0.9 | 24.4 | 0 | 0 | 0 | 0 | 86.6142 | 33.8357 | 0 | 84.7168 | 33% | 0 | 0 | 10% | 0 | 31.3503
5329 | 0 | 0 | 0 | 1.7 | 23.7 | 0 | 0 | 0 | 0 | 84.6597 | 33.0899 | 0 | 82.4479 | 27% | 0 | 0 | 10% | 0 | 30.5871
5330 | 0 | 0 | 0 | 1.2 | 24.5 | 0 | 0 | 0 | 0 | 84.2508 | 32.844 | 0 | 82.0389 | 21% | 0 | 0 | 10% | 0 | 30.3156
5331 | 0 | 0 | 0 | 1.1 | 24 | 0 | 0 | 0 | 0 | 84.6032 | 33.04 | 0 | 82.5232 | 15% | 0 | 0 | 10% | 0 | 30.4868
5332 | 0 | 0 | 0 | 0.9 | 23.9 | 0 | 0 | 0 | 0 | 83.2226 | 32.4771 | 0 | 80.949 | 9% | 0 | 0 | 10% | 0 | 29.9068
5333 | 0 | 0 | 0 | 1.1 | 24 | 0 | 0 | 0 | 0 | 85.4028 | 33.3748 | 0 | 83.5958 | 2% | 0 | 0 | 10% | 0 | 30.7787
5334 | 1 | 9 | 9 | 1.2 | 24.6 | 0 | 0.027667 | 0 | 0 | 32.6761 | 12.8044 | 0 | 32.4758 | 0% | 0 | 0 | 10% | 0 | 10.2648
5335 | 148 | 141 | 103 | 1.9 | 25.9 | 0 | 28.7925 | 0.83909 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6393
5336 | 320 | 292 | 150 | 5 | 27.3 | 46.2632 | 11.8979 | 10.7994 | 0 | 0 | 0 | 44.5879 | 0 | 3% | 0 | 0 | 10% | 0 | 9.623
5337 | 549 | 522 | 189 | 5.2 | 29.2 | 128.0395 | 0 | 31.0292 | 0 | 0 | 0 | 125.0246 | 0 | 13% | 0 | 0 | 10% | 0 | 29.5099
5338 | 658 | 703 | 206 | 3 | 31.7 | 170.4415 | 1.42e-14 | 48.5148 | 0 | 44.3955 | 7.5087 | 126.6813 | 0 | 22% | 23.1903 | 0 | 41.54% | 0 | 30.6189
5339 | 692 | 832 | 231 | 2.1 | 33.5 | 187.5923 | 0 | 52.6849 | 8.5455 | 42.5497 | 13.991 | 145.759 | 0 | 33% | 25 | 0 | 75.54% | 0 | 39.5655
5340 | 654 | 859 | 247 | 2.1 | 34.9 | 180.413 | 0 | 37.4566 | 26.7221 | 42.5746 | 13.8645 | 138.684 | 0 | 43% | 10.6332 | 0 | 90% | 0 | 38.6268
5341 | 709 | 901 | 230 | 4.4 | 35.4 | 196.5762 | 0 | 26.2405 | 42.0535 | 42.5817 | 13.8178 | 154.6754 | 0 | 55% | 0 | 0 | 90% | 0 | 37.8439
5342 | 143 | 536 | 396 | 5.3 | 33.4 | 0 | 45.8123 | 25.1675 | 8.9016 | 42.5869 | 14.0127 | 0 | 40.7303 | 52% | 0 | 0 | 90% | 0 | 37.3368
5343 | 164 | 473 | 335 | 4.2 | 32.8 | 0 | 51.0444 | 25.7539 | 2.7702 | 42.5823 | 14.068 | 0 | 40.7363 | 49% | 0 | 0 | 90% | 0 | 37.0704
5344 | 82 | 377 | 314 | 3.7 | 33 | 0 | 24.3754 | 18.7939 | 0 | 42.5759 | 14.0472 | 0 | 40.7419 | 46% | 0 | 6.9587 | 78.87% | 0 | 37.0397
5345 | 43 | 260 | 233 | 3.4 | 31.2 | 0 | 11.6832 | 9.7738 | 0 | 42.569 | 14.212 | 0 | 40.7456 | 43% | 0 | 16.0302 | 53.22% | 0 | 37.2481
5346 | 207 | 237 | 172 | 3 | 30.5 | 0 | 46.6191 | 6.6918 | 0 | 42.5617 | 14.2731 | 0 | 40.7474 | 40% | 0 | 21.1906 | 19.31% | 0 | 39.381
5347 | 55 | 63 | 53 | 2 | 29.6 | 0 | 8.7027 | 0 | 0 | 94.857 | 36.4861 | 0 | 97.5685 | 32% | 0 | 5.8206 | 10% | 0 | 39.4561
5348 | 0 | 0 | 0 | 1.3 | 27.7 | 0 | 0 | 0 | 0 | 102.2444 | 39.9746 | 0 | 104.5071 | 25% | 0 | 0 | 10% | 0 | 37.2311
5349 | 0 | 0 | 0 | 0.8 | 26.5 | 0 | 0 | 0 | 0 | 95.9766 | 37.5265 | 0 | 96.5969 | 18% | 0 | 0 | 10% | 0 | 34.8815
5350 | 0 | 0 | 0 | 0.6 | 24.7 | 0 | 0 | 0 | 0 | 90.6371 | 35.4919 | 0 | 89.9102 | 11% | 0 | 0 | 10% | 0 | 32.8979
5351 | 0 | 0 | 0 | 0.7 | 24.2 | 0 | 0 | 0 | 0 | 87.0767 | 34.0525 | 0 | 85.5368 | 5% | 0 | 0 | 10% | 0 | 31.4748
5352 | 0 | 0 | 0 | 0.4 | 23.7 | 0 | 0 | 0 | 0 | 61.8197 | 24.1704 | 0 | 60.4014 | 0% | 0 | 0 | 10% | 0 | 21.6159
5353 | 0 | 0 | 0 | 0.6 | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4772
5354 | 0 | 0 | 0 | 0.5 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4514
5355 | 0 | 0 | 0 | 0.7 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.426
5356 | 0 | 0 | 0 | 0.9 | 22.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4012
5357 | 0 | 0 | 0 | 1.4 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3768
5358 | 23 | 14 | 11 | 1.5 | 22 | 0 | 0.54265 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3529
5359 | 374 | 151 | 65 | 1.1 | 24.6 | 0 | 61.693 | 0.28033 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0454
5360 | 605 | 356 | 104 | 0.5 | 28.2 | 126.6146 | 0 | 15.0308 | 0 | 0 | 0 | 120.7589 | 0 | 9% | 0 | 0 | 10% | 0 | 13.533
5361 | 708 | 571 | 150 | 1.4 | 29.8 | 173.369 | 2.98e-14 | 35.35 | 0 | 0 | 0 | 170.7353 | 0 | 22% | 0 | 0 | 10% | 0 | 33.4089
5362 | 734 | 756 | 207 | 2.6 | 31.5 | 192.2894 | 0 | 53.5799 | 0 | 0 | 0 | 190.4317 | 0 | 36% | 7.2019 | 0 | 19.79% | 0 | 44.242
5363 | 815 | 938 | 237 | 4.5 | 32.5 | 222.217 | 0 | 71.2373 | 0 | 42.5194 | 0 | 180.4197 | 0 | 50% | 24.0079 | 0 | 52.45% | 0 | 44.269
5364 | 447 | 806 | 390 | 5.2 | 32.5 | 115.7533 | 0 | 56.4492 | 3.2958 | 42.5484 | 12.0595 | 74.3747 | 0 | 55% | 24.1616 | 0 | 85.3% | 0 | 42.7771
5365 | 234 | 642 | 415 | 5.7 | 32.4 | 0 | 62.9142 | 33.9374 | 11.413 | 42.6566 | 14.1366 | 0 | 40.4805 | 52% | 3.4521 | 0 | 90% | 0 | 42.9796
5366 | 30 | 398 | 364 | 5.9 | 31 | 0 | 9.6112 | 21.8646 | 0 | 42.5479 | 14.2234 | 0 | 40.4058 | 49% | 0 | 8.8934 | 75.77% | 0 | 42.426
5367 | 93 | 440 | 363 | 5.7 | 30.6 | 0 | 28.9446 | 25.3217 | 0 | 42.5415 | 14.2573 | 0 | 40.4384 | 46% | 0 | 5.0329 | 67.72% | 0 | 42.0301
5368 | 264 | 508 | 321 | 5.1 | 30.2 | 0 | 67.7239 | 30.3725 | 0 | 47.4508 | 16.2796 | 0 | 45.2786 | 43% | 2.5836 | 0 | 71.23% | 0 | 41.4549
5369 | 512 | 434 | 175 | 5 | 29.6 | 110.5207 | 0 | 22.7839 | 0 | 42.5275 | 14.3423 | 66.6938 | 0 | 48% | 0 | 5.2334 | 62.86% | 0 | 40.9417
5370 | 566 | 258 | 77 | 4.8 | 28.8 | 99.6883 | 0 | 6.4679 | 0 | 42.5368 | 14.4165 | 57.9291 | 0 | 52% | 0 | 22.8751 | 26.26% | 0 | 42.42
5371 | 201 | 61 | 31 | 4.6 | 27.1 | 0 | 31.5801 | 0 | 0 | 85.8473 | 32.9316 | 0 | 87.9128 | 46% | 0 | 9.9804 | 10.29% | 0 | 40.9963
5372 | 0 | 0 | 0 | 4.8 | 25 | 0 | 0 | 0 | 0 | 103.1267 | 40.66 | 0 | 105.5611 | 38% | 0 | 0 | 10.29% | 0 | 37.9347
5373 | 0 | 0 | 0 | 4 | 23.6 | 0 | 0 | 0 | 0 | 96.6993 | 38.1334 | 0 | 97.3413 | 31% | 0 | 0 | 10.29% | 0 | 35.5292
5374 | 0 | 0 | 0 | 2.9 | 23.1 | 0 | 0 | 0 | 0 | 91.3256 | 35.9368 | 0 | 90.6235 | 24% | 0 | 0 | 10.29% | 0 | 33.3908
5375 | 0 | 0 | 0 | 2.6 | 22.9 | 0 | 0 | 0 | 0 | 87.9178 | 34.5253 | 0 | 86.411 | 18% | 0 | 0 | 10.29% | 0 | 31.9966
5376 | 0 | 0 | 0 | 1.7 | 22.6 | 0 | 0 | 0 | 0 | 86.1512 | 33.8142 | 0 | 84.3064 | 11% | 0 | 0 | 10.29% | 0 | 31.2805
5377 | 0 | 0 | 0 | 1.2 | 21.7 | 0 | 0 | 0 | 0 | 85.0487 | 33.4321 | 0 | 83.0345 | 5% | 0 | 0 | 10.29% | 0 | 30.8857
5378 | 0 | 0 | 0 | 1.1 | 21.9 | 0 | 0 | 0 | 0 | 68.7754 | 27.0413 | 0 | 67.3488 | 0% | 0 | 0 | 10.29% | 0 | 24.4962
5379 | 0 | 0 | 0 | 1 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.29% | 0 | -2.4601
5380 | 0 | 0 | 0 | 1.5 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.29% | 0 | -2.4346
5381 | 0 | 0 | 0 | 1.5 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.29% | 0 | -2.4096
5382 | 0 | 7 | 7 | 0.7 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.29% | 0 | -2.3851
5383 | 20 | 78 | 72 | 0.7 | 22.1 | 0 | 3.8637 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.29% | 0 | -2.3609
5384 | 362 | 337 | 181 | 3.2 | 24.9 | 55.3969 | 13.8792 | 14.1106 | 0 | 0 | 0 | 52.978 | 0 | 4% | 0 | 0 | 10.29% | 0 | 12.8726
5385 | 523 | 492 | 181 | 3.9 | 26.4 | 122.1069 | 0 | 29.6681 | 0 | 0 | 0 | 119.1271 | 0 | 13% | 0 | 0 | 10.29% | 0 | 28.1909
5386 | 800 | 734 | 140 | 5.1 | 27.6 | 209.1195 | -2.03e-15 | 52.7547 | 0 | 42.6594 | 1.0835 | 166.174 | 0 | 25% | 21.5044 | 0 | 39.53% | 0 | 29.572
5387 | 828 | 863 | 156 | 5.8 | 28.8 | 224.9315 | 0 | 57.3415 | 8.5707 | 42.5181 | 14.4101 | 183.0752 | 0 | 39% | 25 | 0 | 73.53% | 0 | 44.2929
5388 | 762 | 900 | 196 | 6.8 | 29.1 | 209.2991 | 1.54e-14 | 43.3308 | 25.989 | 42.5587 | 14.3972 | 167.6293 | 0 | 52% | 12.1064 | 0 | 90% | 0 | 43.2814
5389 | 689 | 970 | 323 | 7.3 | 29.5 | 187.8881 | 0 | 30.7206 | 44.167 | 42.5695 | 14.3654 | 146.273 | 0 | 62% | 0 | 0 | 90% | 0 | 42.9309
5390 | 323 | 701 | 405 | 7.1 | 29 | 75.6219 | 0 | 29.3159 | 21.4596 | 42.5772 | 14.4124 | 34.5079 | 0 | 65% | 0 | 0 | 90% | 0 | 42.597
5391 | 607 | 788 | 296 | 6.8 | 29.1 | 155.8846 | 0 | 29.6186 | 28.2326 | 42.5766 | 14.4033 | 112.9179 | 0 | 73% | 0 | 0 | 90% | 0 | 42.1673
5392 | 520 | 625 | 271 | 6.2 | 28.5 | 124.2266 | 0 | 28.4711 | 12.4878 | 42.58 | 14.4578 | 82.3331 | 0 | 79% | 0 | 0 | 90% | 0 | 41.484
5393 | 371 | 373 | 193 | 6 | 27.4 | 73.8606 | 0 | 19.0075 | 0 | 42.5812 | 14.5546 | 32.056 | 0 | 82% | 0 | 7.153 | 78.55% | 0 | 41.2808
5394 | 318 | 212 | 110 | 5.4 | 26.5 | 0 | 58.1997 | 4.9011 | 0 | 44.469 | 15.3991 | 0 | 42.9977 | 79% | 0 | 24.576 | 39.23% | 0 | 42.7689
5395 | 55 | 43 | 34 | 4.6 | 25 | 0 | 8.5786 | 0 | 0 | 68.6122 | 25.7861 | 0 | 68.9812 | 74% | 0 | 18.271 | 10% | 0 | 41.0541
5396 | 0 | 0 | 0 | 4.2 | 23.8 | 0 | 0 | 0 | 0 | 103.6284 | 40.9929 | 0 | 106.9359 | 66% | 0 | 0 | 10% | 0 | 38.0928
5397 | 0 | 0 | 0 | 3.9 | 22.9 | 0 | 0 | 0 | 0 | 97.3225 | 38.457 | 0 | 98.2872 | 58% | 0 | 0 | 10% | 0 | 35.8124
5398 | 0 | 0 | 0 | 3.4 | 22.2 | 0 | 0 | 0 | 0 | 91.842 | 36.2324 | 0 | 91.2796 | 52% | 0 | 0 | 10% | 0 | 33.693
5399 | 0 | 0 | 0 | 3.4 | 21.8 | 0 | 0 | 0 | 0 | 88.0522 | 34.6746 | 0 | 86.5452 | 45% | 0 | 0 | 10% | 0 | 32.1654
5400 | 0 | 0 | 0 | 2.9 | 21.8 | 0 | 0 | 0 | 0 | 86.0393 | 33.8332 | 0 | 84.1497 | 39% | 0 | 0 | 10% | 0 | 31.3169
5401 | 0 | 0 | 0 | 2.8 | 21.6 | 0 | 0 | 0 | 0 | 84.941 | 33.3918 | 0 | 82.898 | 33% | 0 | 0 | 10% | 0 | 30.8566
5402 | 0 | 0 | 0 | 2.7 | 21.4 | 0 | 0 | 0 | 0 | 85.9502 | 33.8295 | 0 | 84.1618 | 26% | 0 | 0 | 10% | 0 | 31.2701
5403 | 0 | 0 | 0 | 2.1 | 21 | 0 | 0 | 0 | 0 | 90.2355 | 35.6595 | 0 | 89.3916 | 20% | 0 | 0 | 10% | 0 | 33.0787
5404 | 0 | 0 | 0 | 1.8 | 20.7 | 0 | 0 | 0 | 0 | 94.5978 | 37.5212 | 0 | 94.7387 | 13% | 0 | 0 | 10% | 0 | 34.941
5405 | 0 | 0 | 0 | 0.7 | 20.4 | 0 | 0 | 0 | 0 | 100.2986 | 39.9176 | 0 | 101.425 | 5% | 0 | 0 | 10% | 0 | 37.3548
5406 | 19 | 13 | 11 | 1.4 | 20 | 0 | 0.29432 | 0 | 0 | 67.0426 | 26.7809 | 0 | 68.4949 | 0% | 0 | 0 | 10% | 0 | 24.3192
5407 | 344 | 142 | 64 | 1 | 22.1 | 0 | 55.3677 | 0.19287 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1378
5408 | 597 | 345 | 99 | 1.1 | 23.8 | 124.0117 | 0 | 14.8449 | 0 | 0 | 0 | 119.5525 | 0 | 9% | 0 | 0 | 10% | 0 | 13.3695
5409 | 744 | 550 | 110 | 1.7 | 25.7 | 182.8078 | 0 | 34.3467 | 0 | 0 | 0 | 180.6664 | 0 | 23% | 0 | 0 | 10% | 0 | 32.3239
5410 | 820 | 726 | 116 | 1.7 | 27.8 | 217.1838 | 0 | 52.1586 | 0 | 0 | 0 | 215.5797 | 0 | 39% | 4.841 | 0 | 16.58% | 0 | 44.9578
5411 | 842 | 854 | 134 | 1.8 | 29.3 | 231.9565 | 0 | 65.2152 | 0 | 0 | 0 | 230.5925 | 0 | 56% | 18.2634 | 0 | 41.42% | 0 | 44.4203
5412 | 778 | 903 | 185 | 2 | 30.6 | 217.7009 | 0 | 69.5915 | 0 | 0 | 0 | 216.554 | 0 | 72% | 23.5491 | 0 | 73.45% | 0 | 43.6028
5413 | 362 | 593 | 251 | 2.8 | 31.1 | 92.2826 | -1.49e-14 | 43.0371 | 0 | 0 | 0 | 91.7834 | 0 | 79% | 0 | 0 | 73.45% | 0 | 41.7452
5414 | 851 | 940 | 181 | 4.1 | 32.2 | 236.329 | 0 | 58.7381 | 13.6211 | 0 | 0 | 234.3887 | 0 | 97% | 12.1699 | 0 | 90% | 0 | 43.8979
5415 | 809 | 795 | 147 | 4.6 | 32.3 | 46.3454 | 187.5905 | 44.8425 | 13.5454 | 0 | 0 | 46.1166 | 0 | 100% | 0 | 0 | 90% | 0 | 43.41
5416 | 767 | 634 | 121 | 5.8 | 32.5 | 41.1292 | 179.0647 | 41.9456 | 0 | 42.59 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.1292
5417 | 680 | 443 | 102 | 6.3 | 31.9 | 42.1594 | 132.9078 | 23.1979 | 0 | 42.5876 | 12.9232 | 0 | 0 | 100% | 0 | 5.3627 | 81.42% | 0 | 42.1492
5418 | 522 | 237 | 74 | 5.6 | 30.6 | 42.1571 | 61.444 | 5.6287 | 0 | 42.5857 | 14.2722 | 0 | 0 | 100% | 0 | 22.6981 | 45.1% | 0 | 43.3081
5419 | 191 | 57 | 30 | 2.7 | 29.1 | 0 | 29.5689 | 0 | 0 | 59.9572 | 21.681 | 0 | 59.3379 | 96% | 0 | 21.9392 | 10% | 0 | 41.5402
5420 | 0 | 0 | 0 | 3.6 | 25.8 | 0 | 0 | 0 | 0 | 105.3339 | 41.4883 | 0 | 108.6227 | 88% | 0 | 0 | 10% | 0 | 38.713
5421 | 0 | 0 | 0 | 2.8 | 24.4 | 0 | 0 | 0 | 0 | 98.4174 | 38.7628 | 0 | 98.0564 | 80% | 0 | 0 | 10% | 0 | 36.549
5422 | 0 | 0 | 0 | 0.8 | 23.6 | 0 | 0 | 0 | 0 | 92.8406 | 36.5245 | 0 | 91.2507 | 73% | 0 | 0 | 10% | 0 | 34.3653
5423 | 0 | 0 | 0 | 0.7 | 23 | 0 | 0 | 0 | 0 | 88.735 | 34.8552 | 0 | 86.3913 | 67% | 0 | 0 | 10% | 0 | 32.6577
5424 | 0 | 0 | 0 | 0.3 | 22.7 | 0 | 0 | 0 | 0 | 86.4309 | 33.9184 | 0 | 83.8668 | 61% | 0 | 0 | 10% | 0 | 31.6504
5425 | 0 | 0 | 0 | 0.8 | 22.7 | 0 | 0 | 0 | 0 | 84.94 | 33.2972 | 0 | 82.3134 | 54% | 0 | 0 | 10% | 0 | 30.9613
5426 | 0 | 0 | 0 | 1 | 21.4 | 0 | 0 | 0 | 0 | 84.229 | 33.1108 | 0 | 81.6569 | 48% | 0 | 0 | 10% | 0 | 30.7144
5427 | 0 | 0 | 0 | 0.9 | 21.4 | 0 | 0 | 0 | 0 | 84.9708 | 33.4201 | 0 | 82.6796 | 42% | 0 | 0 | 10% | 0 | 30.9717
5428 | 0 | 0 | 0 | 1.4 | 20.6 | 0 | 0 | 0 | 0 | 84.5743 | 33.3182 | 0 | 82.3134 | 36% | 0 | 0 | 10% | 0 | 30.8342
5429 | 0 | 0 | 0 | 1.2 | 20.8 | 0 | 0 | 0 | 0 | 86.9289 | 34.2868 | 0 | 85.2065 | 30% | 0 | 0 | 10% | 0 | 31.7681
5430 | 39 | 14 | 10 | 0.8 | 20.5 | 0 | 0.44724 | 0 | 0 | 92.1914 | 36.5237 | 0 | 91.6717 | 23% | 0 | 0 | 10% | 0 | 33.9822
5431 | 461 | 150 | 49 | 1.3 | 22.5 | 53.7159 | 13.3711 | 0.092413 | 0 | 94.6625 | 37.3946 | 0 | 42.5745 | 20% | 0 | 0 | 10% | 0 | 36.1301
5432 | 690 | 356 | 73 | 1.8 | 26.3 | 145.668 | 0 | 15.2851 | 0 | 65.3963 | 24.3319 | 80.2319 | 0 | 26% | 0 | 0 | 10% | 0 | 37.8564
5433 | 795 | 558 | 89 | 2.1 | 29.1 | 196.4816 | 0 | 34.755 | 0 | 46.3481 | 15.9308 | 150.6752 | 0 | 37% | 9.5667 | 0 | 23.01% | 0 | 38.92
5434 | 846 | 728 | 100 | 1.4 | 31.4 | 224.9096 | 0 | 51.9716 | 0 | 44.1806 | 14.8345 | 181.403 | 0 | 50% | 24.2869 | 0 | 56.04% | 0 | 40.0514
5435 | 876 | 854 | 107 | 1.6 | 32.9 | 242.3585 | 0 | 53.8202 | 11.0501 | 42.5817 | 14.0585 | 200.4251 | 0 | 65% | 24.9699 | 0 | 90% | 0 | 40.264
5436 | 892 | 928 | 110 | 2.9 | 34 | 252.1361 | 0 | 28.2772 | 43.9258 | 42.5895 | 13.9564 | 210.1394 | 0 | 81% | 0 | 0 | 90% | 0 | 39.477
5437 | 891 | 940 | 112 | 5.3 | 34.1 | 251.1088 | 0 | 24.6174 | 48.8087 | 42.5943 | 13.9483 | 208.9443 | 0 | 96% | 0 | 0 | 90% | 0 | 38.9934
5438 | 873 | 890 | 113 | 5.7 | 33.8 | 98.5803 | 165.7472 | 24.0105 | 44.3299 | 42.5975 | 13.9781 | 56.9729 | 0 | 100% | 0 | 0 | 90% | 0 | 38.5191
5439 | 840 | 784 | 111 | 5.4 | 34.3 | 42.1513 | 212.3795 | 23.5988 | 33.6667 | 42.5959 | 13.9295 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.2367
5440 | 788 | 629 | 103 | 5.4 | 33.6 | 42.1568 | 184.2916 | 23.1816 | 18.3261 | 42.5936 | 13.9959 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.886
5441 | 705 | 441 | 90 | 5.1 | 33.4 | 43.1079 | 138.8264 | 23.0263 | 0 | 43.5284 | 14.3827 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.117
5442 | 549 | 236 | 66 | 4 | 32 | 42.1358 | 68.3097 | 5.4312 | 0 | 42.5892 | 14.1451 | 0 | 0 | 100% | 0 | 19.6614 | 58.54% | 0 | 39.9466
5443 | 206 | 56 | 27 | 1.6 | 30.1 | 0 | 31.6465 | 0 | 0 | 48.5688 | 16.7585 | 0 | 47.0379 | 97% | 0 | 25 | 18.54% | 0 | 39.6813
5444 | 0 | 0 | 0 | 0.9 | 27.7 | 0 | 0 | 0 | 0 | 90.7654 | 35.058 | 0 | 93.1924 | 90% | 0 | 5.3386 | 10% | 0 | 37.4465
5445 | 0 | 0 | 0 | 2.9 | 25.6 | 0 | 0 | 0 | 0 | 96.4479 | 37.8199 | 0 | 96.4628 | 83% | 0 | 0 | 10% | 0 | 35.4089
5446 | 0 | 0 | 0 | 1.9 | 23.8 | 0 | 0 | 0 | 0 | 90.9647 | 35.7151 | 0 | 89.4398 | 76% | 0 | 0 | 10% | 0 | 33.4154
5447 | 0 | 0 | 0 | 0.9 | 23.3 | 0 | 0 | 0 | 0 | 87.37 | 34.2558 | 0 | 85.1857 | 69% | 0 | 0 | 10% | 0 | 31.9284
5448 | 0 | 0 | 0 | 1.6 | 22.9 | 0 | 0 | 0 | 0 | 85.3188 | 33.4371 | 0 | 82.9304 | 63% | 0 | 0 | 10% | 0 | 31.0504
5449 | 0 | 0 | 0 | 1.1 | 23.1 | 0 | 0 | 0 | 0 | 84.4211 | 33.0459 | 0 | 82.0451 | 57% | 0 | 0 | 10% | 0 | 30.6006
5450 | 0 | 0 | 0 | 1.1 | 22.5 | 0 | 0 | 0 | 0 | 85.1089 | 33.385 | 0 | 83.0017 | 51% | 0 | 0 | 10% | 0 | 30.8894
5451 | 0 | 0 | 0 | 2.1 | 23.3 | 0 | 0 | 0 | 0 | 88.9715 | 34.9271 | 0 | 87.7349 | 44% | 0 | 0 | 10% | 0 | 32.3939
5452 | 0 | 0 | 0 | 1.9 | 21.1 | 0 | 0 | 0 | 0 | 92.3103 | 36.5245 | 0 | 91.8319 | 38% | 0 | 0 | 10% | 0 | 33.9858
5453 | 0 | 0 | 0 | 2.1 | 22.2 | 0 | 0 | 0 | 0 | 97.6742 | 38.6682 | 0 | 98.2034 | 30% | 0 | 0 | 10% | 0 | 36.1427
5454 | 35 | 12 | 9 | 1.8 | 21.5 | 0 | 0.26142 | 0 | 0 | 104.3676 | 41.5222 | 0 | 106.1106 | 22% | 0 | 0 | 10% | 0 | 39.0298
5455 | 423 | 144 | 51 | 1.9 | 23.2 | 47.4485 | 11.9681 | 0.072147 | 0 | 106.7725 | 42.358 | 0 | 62.6639 | 18% | 0 | 0 | 10% | 0 | 41.127
5456 | 657 | 347 | 79 | 3.5 | 26.1 | 136.6041 | 0 | 14.9403 | 0 | 76.6474 | 29.3032 | 60.2193 | 0 | 22% | 0 | 0 | 10% | 0 | 42.5422
5457 | 782 | 550 | 93 | 4 | 28.3 | 191.7122 | 0 | 34.6749 | 0 | 45.807 | 15.7836 | 146.6506 | 0 | 33% | 4.6138 | 0 | 16.28% | 0 | 43.684
5458 | 846 | 725 | 102 | 3.8 | 30.2 | 223.5798 | 0 | 52.4787 | 0 | 46.8996 | 16.0503 | 177.6657 | 0 | 46% | 20.9903 | 0 | 44.82% | 0 | 45.074
5459 | 877 | 853 | 109 | 2.8 | 31.8 | 242.0689 | 0 | 58.6949 | 6.7931 | 42.5853 | 14.1623 | 200.3675 | 0 | 61% | 25 | 0 | 78.82% | 0 | 45.2097
5460 | 889 | 927 | 115 | 2.5 | 33.1 | 251.3799 | 0 | 41.6113 | 31.1142 | 42.594 | 14.0436 | 209.6129 | 0 | 77% | 8.2195 | 0 | 90% | 0 | 44.675
5461 | 887 | 937 | 116 | 3.3 | 34.1 | 251.5191 | 0 | 32.81 | 40.7331 | 42.5971 | 13.9493 | 209.6198 | 0 | 92% | 0 | 0 | 90% | 0 | 44.3274
5462 | 871 | 887 | 116 | 4.5 | 34.7 | 149.1453 | 107.3506 | 29.235 | 39.0803 | 42.6 | 13.8921 | 107.3065 | 0 | 100% | 0 | 0 | 90% | 0 | 44.1012
5463 | 845 | 782 | 110 | 4.6 | 34.6 | 42.1513 | 214.0898 | 28.9343 | 28.5913 | 42.5992 | 13.9016 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.5442
5464 | 798 | 629 | 101 | 4.3 | 34.5 | 42.1567 | 187.4085 | 28.3702 | 13.4175 | 42.5968 | 13.9105 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.9889
5465 | 701 | 435 | 90 | 3.6 | 33.8 | 42.1568 | 138.9605 | 22.8497 | 0 | 42.5945 | 13.9771 | 0 | 0 | 100% | 0 | 4.9293 | 82.11% | 0 | 42.4645
5466 | 538 | 231 | 67 | 4.1 | 33.4 | 42.1568 | 65.1556 | 5.3039 | 0 | 42.5922 | 14.0145 | 0 | 0 | 100% | 0 | 23.6365 | 44.3% | 0 | 43.6633
5467 | 176 | 51 | 27 | 3.1 | 31.1 | 0 | 26.8245 | 0 | 0 | 62.5438 | 22.5571 | 0 | 62.1313 | 95% | 0 | 21.4342 | 10% | 0 | 41.9051
5468 | 1 | 0 | 0 | 3.4 | 27.4 | 0 | 0 | 0 | 0 | 107.1609 | 42.0413 | 0 | 110.6397 | 87% | 0 | 0 | 10% | 0 | 39.3031
5469 | 0 | 0 | 0 | 3.2 | 25.2 | 0 | 0 | 0 | 0 | 99.6811 | 39.2021 | 0 | 99.3859 | 80% | 0 | 0 | 10% | 0 | 37.0311
5470 | 0 | 0 | 0 | 1.9 | 23.9 | 0 | 0 | 0 | 0 | 93.7902 | 36.8965 | 0 | 92.263 | 73% | 0 | 0 | 10% | 0 | 34.7809
5471 | 0 | 0 | 0 | 1.7 | 23.1 | 0 | 0 | 0 | 0 | 89.26 | 35.0655 | 0 | 86.8658 | 66% | 0 | 0 | 10% | 0 | 32.9137
5472 | 0 | 0 | 0 | 1.2 | 22.7 | 0 | 0 | 0 | 0 | 86.4013 | 33.9057 | 0 | 83.6942 | 60% | 0 | 0 | 10% | 0 | 31.6801
5473 | 0 | 0 | 0 | 0.3 | 22.5 | 0 | 0 | 0 | 0 | 84.669 | 33.2015 | 0 | 81.8833 | 54% | 0 | 0 | 10% | 0 | 30.9009
5474 | 0 | 0 | 0 | 0.3 | 21.9 | 0 | 0 | 0 | 0 | 84.6187 | 33.2323 | 0 | 82.0253 | 48% | 0 | 0 | 10% | 0 | 30.8635
5475 | 0 | 0 | 0 | 0.7 | 21.5 | 0 | 0 | 0 | 0 | 86.0293 | 33.8533 | 0 | 83.8473 | 41% | 0 | 0 | 10% | 0 | 31.4302
5476 | 0 | 0 | 0 | 0.7 | 21.4 | 0 | 0 | 0 | 0 | 86.1101 | 33.8956 | 0 | 84.0387 | 35% | 0 | 0 | 10% | 0 | 31.4392
5477 | 0 | 0 | 0 | 1 | 20.8 | 0 | 0 | 0 | 0 | 89.6987 | 35.4485 | 0 | 88.4412 | 29% | 0 | 0 | 10% | 0 | 32.96
5478 | 33 | 12 | 8 | 1.1 | 21.2 | 0 | 0.11544 | 0 | 0 | 97.4004 | 38.6422 | 0 | 97.7796 | 21% | 0 | 0 | 10% | 0 | 36.138
5479 | 438 | 143 | 49 | 1.3 | 24.8 | 49.8421 | 12.414 | 0.052464 | 0 | 101.5103 | 40.0097 | 0 | 54.2316 | 17% | 0 | 0 | 10% | 0 | 38.7385
5480 | 674 | 347 | 75 | 1.3 | 27.7 | 141.5442 | 0 | 15.07 | 0 | 72.2309 | 27.1792 | 69.3807 | 0 | 22% | 0 | 0 | 10% | 0 | 40.5138
5481 | 787 | 550 | 91 | 1.1 | 30.9 | 194.7222 | 0 | 34.554 | 0 | 46.5819 | 15.8542 | 148.8268 | 0 | 33% | 6.4094 | 0 | 18.72% | 0 | 41.8142
5482 | 857 | 727 | 97 | 1.3 | 33.1 | 228.1829 | 0 | 52.3754 | 0 | 47.8474 | 16.1483 | 181.2291 | 0 | 47% | 22.9928 | 0 | 49.99% | 0 | 43.028
5483 | 889 | 853 | 100 | 1.7 | 34.8 | 246.2325 | 0 | 56.9715 | 8.1261 | 42.5863 | 13.878 | 204.4411 | 0 | 62% | 25 | 0 | 83.99% | 0 | 43.1682
5484 | 903 | 925 | 101 | 1.8 | 36.2 | 255.9476 | 0 | 35.9181 | 36.132 | 42.5944 | 13.743 | 214.1114 | 0 | 78% | 4.4214 | 0 | 90% | 0 | 42.4419
5485 | 907 | 939 | 101 | 2.6 | 37 | 257.9 | 0 | 29.3552 | 43.111 | 42.5978 | 13.6644 | 215.8926 | 0 | 94% | 0 | 0 | 90% | 0 | 41.7869
5486 | 906 | 896 | 96 | 4.8 | 37.3 | 126.9625 | 144.4543 | 27.1266 | 41.7114 | 42.6006 | 13.635 | 85.2445 | 0 | 100% | 0 | 0 | 90% | 0 | 41.4305
5487 | 884 | 792 | 91 | 5.4 | 37.4 | 42.151 | 226.2739 | 26.681 | 31.4233 | 42.5994 | 13.6245 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.0131
5488 | 832 | 634 | 86 | 5.6 | 36.8 | 42.1565 | 197.2658 | 26.0896 | 15.9879 | 42.597 | 13.6841 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.4814
5489 | 744 | 441 | 77 | 5.6 | 36.1 | 42.1566 | 150.1246 | 23.1093 | 0 | 42.5947 | 13.7531 | 0 | 0 | 100% | 0 | 2.8209 | 85.49% | 0 | 40.3911
5490 | 576 | 233 | 59 | 4.7 | 34.6 | 42.1567 | 73.4442 | 5.2416 | 0 | 42.5924 | 13.8994 | 0 | 0 | 100% | 0 | 22.0413 | 50.22% | 0 | 41.8904
5491 | 215 | 53 | 24 | 3.2 | 33 | 0 | 31.5416 | 0 | 0 | 50.9717 | 17.4608 | 0 | 49.4378 | 96% | 0 | 25 | 10.22% | 0 | 40.3771
5492 | 0 | 0 | 0 | 2.1 | 29.7 | 0 | 0 | 0 | 0 | 104.7227 | 40.734 | 0 | 108.6367 | 88% | 0 | 0 | 10.22% | 0 | 37.7658
5493 | 0 | 0 | 0 | 0.9 | 27.8 | 0 | 0 | 0 | 0 | 97.3152 | 37.9201 | 0 | 97.0068 | 81% | 0 | 0 | 10.22% | 0 | 35.639
5494 | 0 | 0 | 0 | 1.7 | 26.2 | 0 | 0 | 0 | 0 | 91.4742 | 35.6796 | 0 | 89.7666 | 74% | 0 | 0 | 10.22% | 0 | 33.4657
5495 | 0 | 0 | 0 | 0.6 | 25 | 0 | 0 | 0 | 0 | 87.3253 | 34.0723 | 0 | 84.9044 | 68% | 0 | 0 | 10.22% | 0 | 31.8149
5496 | 0 | 0 | 0 | 0.2 | 24.3 | 0 | 0 | 0 | 0 | 84.8339 | 33.1046 | 0 | 82.1821 | 62% | 0 | 0 | 10.22% | 0 | 30.7741
5497 | 0 | 0 | 0 | 0.5 | 23.6 | 0 | 0 | 0 | 0 | 83.5731 | 32.6476 | 0 | 80.9151 | 56% | 0 | 0 | 10.22% | 0 | 30.246
5498 | 0 | 0 | 0 | 1.2 | 23.8 | 0 | 0 | 0 | 0 | 83.2417 | 32.4921 | 0 | 80.704 | 50% | 0 | 0 | 10.22% | 0 | 30.0296
5499 | 0 | 0 | 0 | 1.1 | 23.4 | 0 | 0 | 0 | 0 | 83.0515 | 32.4501 | 0 | 80.6191 | 44% | 0 | 0 | 10.22% | 0 | 29.9394
5500 | 0 | 0 | 0 | 1.1 | 23.5 | 0 | 0 | 0 | 0 | 81.8719 | 31.9068 | 0 | 79.5235 | 38% | 0 | 0 | 10.22% | 0 | 29.3584
5501 | 0 | 0 | 0 | 1.2 | 23.4 | 0 | 0 | 0 | 0 | 84.0757 | 32.8759 | 0 | 82.0254 | 32% | 0 | 0 | 10.22% | 0 | 30.2923
5502 | 44 | 12 | 8 | 1.7 | 23 | 0 | 0 | 0 | 0 | 89.4245 | 35.1466 | 0 | 88.517 | 25% | 0 | 0 | 10.22% | 0 | 32.5334
5503 | 504 | 148 | 42 | 1 | 26.5 | 59.3314 | 14.546 | 0 | 0 | 92.9881 | 36.2838 | 0 | 35.3308 | 23% | 0 | 0 | 10.22% | 0 | 34.8716
5504 | 707 | 354 | 71 | 1.3 | 30.4 | 149.0699 | -2.98e-14 | 15.5872 | 0 | 63.2461 | 22.9455 | 85.7831 | 0 | 29% | 0 | 0 | 10.22% | 0 | 36.7455
5505 | 800 | 556 | 90 | 3.1 | 29.7 | 197.2827 | 0 | 35.3503 | 0 | 46.5535 | 15.9579 | 151.1852 | 0 | 40% | 10.8635 | 0 | 25% | 0 | 38.2388
5506 | 848 | 726 | 104 | 3.4 | 30.7 | 224.6969 | 0 | 52.657 | 0.30234 | 42.5694 | 14.2577 | 182.6494 | 0 | 54% | 25 | 0 | 58.99% | 0 | 39.4511
5507 | 887 | 856 | 106 | 3.1 | 33.2 | 245.0811 | 0 | 51.6736 | 14.2791 | 42.5821 | 14.0302 | 203.0078 | 0 | 69% | 22.798 | 0 | 90% | 0 | 40.2349
5508 | 913 | 931 | 100 | 3.8 | 34.8 | 257.9341 | 0 | 28.389 | 44.8568 | 42.589 | 13.8789 | 215.7963 | 0 | 84% | 0 | 0 | 90% | 0 | 39.4575
5509 | 924 | 946 | 96 | 5.3 | 35.9 | 261.1091 | 0 | 21.2853 | 51.5948 | 42.5937 | 13.7725 | 218.7714 | 0 | 100% | 0 | 0 | 90% | 0 | 38.984
5510 | 924 | 906 | 92 | 7 | 36.6 | 41.3349 | 248.3006 | 24.0323 | 46.1147 | 42.5966 | 13.7039 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.4439
5511 | 896 | 799 | 90 | 6.4 | 36.6 | 42.151 | 229.8742 | 23.7252 | 35.3355 | 42.5943 | 13.7031 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.1361
5512 | 799 | 626 | 101 | 6.9 | 36.2 | 42.1566 | 186.9052 | 23.5119 | 18.1352 | 42.5921 | 13.7423 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.9619
5513 | 701 | 430 | 89 | 6.6 | 35.3 | 44.6884 | 134.5087 | 22.6443 | 0 | 45.0819 | 14.808 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 38.1566
5514 | 525 | 222 | 64 | 5.4 | 33.9 | 42.1024 | 60.555 | 4.9132 | 0 | 42.5878 | 13.9654 | 0 | 0 | 100% | 0 | 20.6842 | 56.9% | 0 | 40.2712
5515 | 177 | 48 | 25 | 4.8 | 31.4 | 0 | 24.7292 | 0 | 0 | 49.4808 | 17.0069 | 0 | 47.9441 | 97% | 0 | 25 | 16.91% | 0 | 39.9277
5516 | 0 | 0 | 0 | 3 | 29.2 | 0 | 0 | 0 | 0 | 94.4179 | 36.4142 | 0 | 97.3095 | 90% | 0 | 4.3158 | 10% | 0 | 37.7793
5517 | 0 | 0 | 0 | 1.1 | 26.8 | 0 | 0 | 0 | 0 | 97.1416 | 37.9701 | 0 | 97.0496 | 83% | 0 | 0 | 10% | 0 | 35.6226
5518 | 0 | 0 | 0 | 0.8 | 25.4 | 0 | 0 | 0 | 0 | 91.1345 | 35.6241 | 0 | 89.4831 | 76% | 0 | 0 | 10% | 0 | 33.3732
5519 | 0 | 0 | 0 | 0.5 | 24.8 | 0 | 0 | 0 | 0 | 87.5293 | 34.1776 | 0 | 85.2581 | 69% | 0 | 0 | 10% | 0 | 31.887
5520 | 0 | 0 | 0 | 0.7 | 23.4 | 0 | 0 | 0 | 0 | 85.2918 | 33.3802 | 0 | 82.805 | 63% | 0 | 0 | 10% | 0 | 31.0236
5521 | 0 | 0 | 0 | 0.1 | 22.7 | 0 | 0 | 0 | 0 | 84.6167 | 33.1625 | 0 | 82.2019 | 57% | 0 | 0 | 10% | 0 | 30.741
5522 | 0 | 0 | 0 | 1 | 22 | 0 | 0 | 0 | 0 | 85.8311 | 33.7296 | 0 | 83.7929 | 51% | 0 | 0 | 10% | 0 | 31.2546
5523 | 0 | 0 | 0 | 1.3 | 22.6 | 0 | 0 | 0 | 0 | 91.8695 | 36.2091 | 0 | 91.2152 | 44% | 0 | 0 | 10% | 0 | 33.695
5524 | 0 | 0 | 0 | 1.1 | 22.6 | 0 | 0 | 0 | 0 | 97.7631 | 38.6683 | 0 | 98.2484 | 37% | 0 | 0 | 10% | 0 | 36.1633
5525 | 0 | 0 | 0 | 1.4 | 22.6 | 0 | 0 | 0 | 0 | 104.7284 | 41.572 | 0 | 106.4742 | 29% | 0 | 0 | 10% | 0 | 39.1031
5526 | 39 | 10 | 7 | 2.1 | 23.7 | 0 | 0 | 0 | 0 | 112.3107 | 44.5845 | 0 | 115.1609 | 20% | 0 | 0 | 10% | 0 | 42.1753
5527 | 474 | 142 | 43 | 2 | 26 | 54.3584 | 13.4568 | 0 | 0 | 115.5549 | 45.6639 | 0 | 65.9244 | 15% | 0 | 0 | 10% | 0 | 44.3054
5528 | 720 | 350 | 64 | 0.9 | 29.2 | 151.8239 | 0 | 15.5502 | 0 | 83.7051 | 32.0918 | 68.6932 | 0 | 20% | 0 | 0 | 10% | 0 | 45.7875
5529 | 834 | 556 | 74 | 0.7 | 32.8 | 207.1456 | 0 | 35.2294 | 0.11189 | 42.558 | 14.06 | 165.4881 | 0 | 33% | 0 | 0 | 10% | 0 | 46.9865
5530 | 885 | 729 | 83 | 1.9 | 34.6 | 236.0118 | 0 | 52.9399 | 0 | 48.0713 | 16.0814 | 189.2465 | 0 | 47% | 18.297 | 0 | 34.88% | 0 | 48.1337
5531 | 905 | 851 | 90 | 2.3 | 35.6 | 250.738 | 0 | 61.9018 | 3.6169 | 42.592 | 13.8015 | 209.2735 | 0 | 63% | 25 | 0 | 68.88% | 0 | 47.9629
5532 | 906 | 917 | 95 | 3.7 | 36.1 | 255.843 | 0 | 51.581 | 20.4684 | 42.5989 | 13.7544 | 214.2527 | 0 | 78% | 15.5265 | 0 | 90% | 0 | 46.9932
5533 | 944 | 952 | 87 | 5.1 | 36.5 | 267.1823 | 0 | 35.056 | 37.5983 | 42.6013 | 13.7153 | 225.4068 | 0 | 95% | 0 | 0 | 90% | 0 | 46.4039
5534 | 955 | 912 | 77 | 5.4 | 37.1 | 108.8905 | 181.1146 | 31.8177 | 39.3884 | 42.6035 | 13.6561 | 67.2695 | 0 | 100% | 0 | 0 | 90% | 0 | 45.9925
5535 | 940 | 809 | 72 | 5.3 | 37.4 | 42.1509 | 243.9142 | 30.6438 | 29.7434 | 42.6018 | 13.6253 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.9766
5536 | 908 | 656 | 66 | 5.4 | 35.9 | 42.1566 | 219.8719 | 29.6632 | 14.9967 | 42.5994 | 13.7744 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.1455
5537 | 768 | 439 | 70 | 5.4 | 33.8 | 42.1568 | 156.1202 | 23.5612 | 0 | 42.597 | 13.9779 | 0 | 0 | 100% | 0 | 5.5701 | 81.09% | 0 | 43.8177
5538 | 578 | 224 | 55 | 5.2 | 32.2 | 43.3413 | 71.1063 | 5.0281 | 0 | 43.7615 | 14.5899 | 0 | 0 | 100% | 0 | 25 | 41.09% | 0 | 45.3259
5539 | 189 | 46 | 22 | 5 | 29.1 | 0 | 25.0649 | 0 | 0 | 69.2864 | 25.6302 | 0 | 69.6143 | 95% | 0 | 19.4299 | 10% | 0 | 42.9725
5540 | 0 | 0 | 0 | 4.2 | 26.9 | 0 | 0 | 0 | 0 | 108.1615 | 42.5135 | 0 | 111.285 | 87% | 0 | 0 | 10% | 0 | 39.9067
5541 | 0 | 0 | 0 | 5 | 24.3 | 0 | 0 | 0 | 0 | 100.2815 | 39.5466 | 0 | 99.8708 | 79% | 0 | 0 | 10% | 0 | 37.4345
5542 | 0 | 0 | 0 | 4.3 | 23.1 | 0 | 0 | 0 | 0 | 94.4048 | 37.2299 | 0 | 92.8409 | 72% | 0 | 0 | 10% | 0 | 35.1582
5543 | 0 | 0 | 0 | 4.1 | 22.5 | 0 | 0 | 0 | 0 | 90.812 | 35.771 | 0 | 88.6014 | 65% | 0 | 0 | 10% | 0 | 33.6579
5544 | 0 | 0 | 0 | 2.2 | 21.8 | 0 | 0 | 0 | 0 | 89.1385 | 35.1291 | 0 | 86.7965 | 59% | 0 | 0 | 10% | 0 | 32.9495
5545 | 0 | 0 | 0 | 2.4 | 21.6 | 0 | 0 | 0 | 0 | 88.2267 | 34.7635 | 0 | 85.8934 | 52% | 0 | 0 | 10% | 0 | 32.523
5546 | 0 | 0 | 0 | 2.3 | 21.2 | 0 | 0 | 0 | 0 | 88.9209 | 35.0881 | 0 | 86.8863 | 46% | 0 | 0 | 10% | 0 | 32.7944
5547 | 0 | 0 | 0 | 1.8 | 20.2 | 0 | 0 | 0 | 0 | 93.9306 | 37.2814 | 0 | 93.137 | 39% | 0 | 0 | 10% | 0 | 34.9452
5548 | 0 | 0 | 0 | 1.6 | 19.9 | 0 | 0 | 0 | 0 | 99.3562 | 39.5624 | 0 | 99.5019 | 31% | 0 | 0 | 10% | 0 | 37.2238
5549 | 0 | 0 | 0 | 1.8 | 19.1 | 0 | 0 | 0 | 0 | 104.8968 | 41.9461 | 0 | 106.0574 | 23% | 0 | 0 | 10% | 0 | 39.6275
5550 | 40 | 10 | 7 | 2 | 20 | 0 | 0 | 0 | 0 | 111.7384 | 44.698 | 0 | 113.9054 | 15% | 0 | 0 | 10% | 0 | 42.4167
5551 | 450 | 140 | 48 | 1.7 | 22 | 50.6457 | 12.7234 | 0.16361 | 0 | 113.9086 | 45.4149 | 0 | 67.0938 | 10% | 0 | 0 | 10% | 0 | 44.2663
5552 | 658 | 345 | 85 | 3.4 | 24.1 | 135.702 | 0 | 15.8686 | 0 | 80.8016 | 31.3695 | 55.9908 | 0 | 14% | 0 | 0 | 10% | 0 | 45.5306
5553 | 785 | 551 | 99 | 4 | 25.6 | 192.0457 | 0 | 36.1176 | 0 | 44.9737 | 15.6811 | 148.1927 | 0 | 25% | 3.0183 | 0 | 14.11% | 0 | 46.6146
5554 | 864 | 727 | 100 | 3.7 | 27.4 | 228.9114 | 0 | 54.5096 | 0 | 46.1346 | 15.998 | 184.1421 | 0 | 39% | 20.6858 | 0 | 42.24% | 0 | 47.3059
5555 | 898 | 857 | 103 | 3.6 | 29.2 | 247.8586 | 0 | 59.8179 | 7.8726 | 42.5971 | 14.4014 | 206.5386 | 0 | 54% | 25 | 0 | 76.24% | 0 | 46.5135
5556 | 905 | 932 | 114 | 3.2 | 30.8 | 255.827 | 0 | 43.9714 | 30.8276 | 42.6033 | 14.26 | 214.4297 | 0 | 70% | 10.1194 | 0 | 90% | 0 | 45.3024
5557 | 862 | 946 | 156 | 4 | 31.8 | 243.153 | 0 | 33.1779 | 41.2449 | 42.6052 | 14.1689 | 201.6894 | 0 | 85% | 0 | 0 | 90% | 0 | 44.6398
5558 | 752 | 903 | 242 | 4.9 | 32.2 | 206.1554 | 0 | 30.1603 | 40.787 | 42.6062 | 14.1321 | 164.46 | 0 | 98% | 0 | 0 | 90% | 0 | 44.3169
5559 | 469 | 636 | 259 | 6.7 | 31 | 75.0544 | 51.5239 | 28.4907 | 16.881 | 42.6057 | 14.2427 | 33.4106 | 0 | 100% | 0 | 0 | 90% | 0 | 43.4605
5560 | 514 | 618 | 282 | 6.1 | 30.6 | 42.1529 | 99.5404 | 27.6387 | 13.6537 | 42.604 | 14.2783 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.6261
5561 | 281 | 302 | 154 | 6.3 | 29.5 | 0 | 62.3917 | 13.133 | 0 | 42.6007 | 14.3759 | 0 | 41.1095 | 97% | 0 | 17.0584 | 62.71% | 0 | 42.4838
5562 | 161 | 143 | 99 | 6.1 | 28 | 0 | 35.1046 | 2.2692 | 0 | 54.5841 | 19.5161 | 0 | 52.9146 | 93% | 0 | 25 | 22.71% | 0 | 43.8665
5563 | 88 | 39 | 27 | 6.3 | 26.5 | 0 | 11.0374 | 0 | 0 | 94.5027 | 36.6648 | 0 | 97.7747 | 86% | 0 | 7.9416 | 10% | 0 | 41.6758
5564 | 0 | 0 | 0 | 5.5 | 25.1 | 0 | 0 | 0 | 0 | 104.5412 | 41.2356 | 0 | 106.1736 | 78% | 0 | 0 | 10% | 0 | 38.8187
5565 | 0 | 0 | 0 | 5.2 | 24.6 | 0 | 0 | 0 | 0 | 98.1538 | 38.6323 | 0 | 97.6808 | 71% | 0 | 0 | 10% | 0 | 36.4275
5566 | 0 | 0 | 0 | 4.4 | 24.5 | 0 | 0 | 0 | 0 | 92.988 | 36.4973 | 0 | 91.4496 | 64% | 0 | 0 | 10% | 0 | 34.3249
5567 | 0 | 0 | 0 | 4.4 | 24.1 | 0 | 0 | 0 | 0 | 89.5311 | 35.0843 | 0 | 87.3271 | 57% | 0 | 0 | 10% | 0 | 32.8851
5568 | 0 | 0 | 0 | 3.8 | 23.8 | 0 | 0 | 0 | 0 | 88.0687 | 34.5012 | 0 | 85.7338 | 51% | 0 | 0 | 10% | 0 | 32.2502
5569 | 0 | 0 | 0 | 3.1 | 23.5 | 0 | 0 | 0 | 0 | 87.5334 | 34.3058 | 0 | 85.2455 | 44% | 0 | 0 | 10% | 0 | 32.0051
5570 | 0 | 0 | 0 | 3.1 | 23.5 | 0 | 0 | 0 | 0 | 88.5775 | 34.7429 | 0 | 86.6246 | 38% | 0 | 0 | 10% | 0 | 32.3984
5571 | 0 | 0 | 0 | 3 | 22.9 | 0 | 0 | 0 | 0 | 93.656 | 36.9364 | 0 | 92.9319 | 31% | 0 | 0 | 10% | 0 | 34.5565
5572 | 0 | 0 | 0 | 3.3 | 23.3 | 0 | 0 | 0 | 0 | 99.1258 | 39.1684 | 0 | 99.3678 | 23% | 0 | 0 | 10% | 0 | 36.7875
5573 | 0 | 0 | 0 | 3.2 | 22.5 | 0 | 0 | 0 | 0 | 104.3414 | 41.4197 | 0 | 105.5311 | 15% | 0 | 0 | 10% | 0 | 39.0588
5574 | 1 | 7 | 7 | 2.7 | 22.2 | 0 | 0 | 0 | 0 | 110.6356 | 44.0439 | 0 | 112.7734 | 7% | 0 | 0 | 10% | 0 | 41.7171
5575 | 132 | 96 | 63 | 3.8 | 23.2 | 0 | 24.7678 | 0 | 0 | 90.2384 | 35.8979 | 0 | 92.3793 | 0% | 0 | 0 | 10% | 0 | 33.6673
5576 | 418 | 306 | 144 | 5 | 25.4 | 63.7694 | 16.1342 | 13.7298 | 0 | 0 | 0 | 61.5962 | 0 | 5% | 0 | 0 | 10% | 0 | 12.4661
5577 | 479 | 499 | 222 | 6.6 | 26.2 | 107.5373 | 0 | 31.4236 | 0 | 0 | 0 | 105.7364 | 0 | 13% | 0 | 0 | 10% | 0 | 30.0591
5578 | 727 | 724 | 194 | 6.9 | 27.2 | 187.0614 | 0 | 54.0689 | 0 | 0 | 0 | 184.8681 | 0 | 27% | 5.8548 | 0 | 17.96% | 0 | 46.1314
5579 | 664 | 821 | 260 | 8.5 | 27.2 | 174.1901 | 0 | 63.7846 | 0 | 0 | 0 | 172.9893 | 0 | 40% | 15.8258 | 0 | 39.49% | 0 | 45.9597
5580 | 638 | 856 | 273 | 8.4 | 27.4 | 170.5271 | 0 | 67.5961 | 0 | 0 | 0 | 169.3447 | 0 | 53% | 20.5568 | 0 | 67.44% | 0 | 45.0515
5581 | 760 | 913 | 212 | 8.7 | 27.7 | 207.765 | 0 | 64.3637 | 9.7455 | 0 | 0 | 206.4141 | 0 | 68% | 16.5862 | 0 | 90% | 0 | 45.4124
5582 | 753 | 869 | 207 | 8.5 | 28.2 | 202.9516 | 0 | 47.2654 | 22.0774 | 0 | 0 | 201.8011 | 0 | 83% | 0 | 0 | 90% | 0 | 44.9193
5583 | 689 | 747 | 204 | 8.7 | 28 | 177.7368 | 2.98e-14 | 46.4522 | 10.0286 | 0 | 0 | 176.7246 | 0 | 97% | 0 | 0 | 90% | 0 | 44.3188
5584 | 639 | 599 | 184 | 8.7 | 27.2 | 84.6872 | 85.0292 | 41.0807 | 0 | 42.5937 | 0 | 43.5262 | 0 | 100% | 2.1973 | 3.3678 | 87.6% | 0 | 40.5845
5585 | 558 | 410 | 142 | 8.6 | 26.2 | 42.1575 | 95.71 | 22.3434 | 0 | 42.5926 | 14.5573 | 0 | 0 | 100% | 0 | 5.5602 | 78.7% | 0 | 43.1676
5586 | 210 | 174 | 107 | 7.7 | 24.8 | 0 | 45.6031 | 3.4246 | 0 | 50.4604 | 18.0525 | 0 | 48.9263 | 96% | 0 | 25 | 38.7% | 0 | 44.4066
5587 | 0 | 18 | 18 | 6.8 | 23.5 | 0 | 0 | 0 | 0 | 71.1007 | 26.9888 | 0 | 71.5246 | 91% | 0 | 17.9397 | 10% | 0 | 41.9871
5588 | 0 | 0 | 0 | 6.3 | 23.1 | 0 | 0 | 0 | 0 | 105.6724 | 41.9136 | 0 | 108.5075 | 83% | 0 | 0 | 10% | 0 | 39.2617
5589 | 0 | 0 | 0 | 4.4 | 22.6 | 0 | 0 | 0 | 0 | 98.8139 | 39.1029 | 0 | 98.6768 | 76% | 0 | 0 | 10% | 0 | 36.8442
5590 | 0 | 0 | 0 | 3.5 | 22.1 | 0 | 0 | 0 | 0 | 93.7076 | 37.0283 | 0 | 92.4293 | 69% | 0 | 0 | 10% | 0 | 34.8336
5591 | 0 | 0 | 0 | 2.8 | 21.7 | 0 | 0 | 0 | 0 | 89.9157 | 35.4639 | 0 | 87.8373 | 62% | 0 | 0 | 10% | 0 | 33.2544
5592 | 0 | 0 | 0 | 3.3 | 20.9 | 0 | 0 | 0 | 0 | 87.9609 | 34.7095 | 0 | 85.6471 | 56% | 0 | 0 | 10% | 0 | 32.4494
5593 | 0 | 0 | 0 | 3.7 | 20.9 | 0 | 0 | 0 | 0 | 87.0741 | 34.3383 | 0 | 84.75 | 49% | 0 | 0 | 10% | 0 | 32.0256
5594 | 0 | 0 | 0 | 3.8 | 20.4 | 0 | 0 | 0 | 0 | 88.0361 | 34.7806 | 0 | 86.0403 | 43% | 0 | 0 | 10% | 0 | 32.4199
5595 | 0 | 0 | 0 | 1.5 | 20 | 0 | 0 | 0 | 0 | 92.8855 | 36.8553 | 0 | 92.0538 | 36% | 0 | 0 | 10% | 0 | 34.4572
5596 | 0 | 0 | 0 | 0.8 | 19.9 | 0 | 0 | 0 | 0 | 97.9337 | 38.97 | 0 | 98.0408 | 29% | 0 | 0 | 10% | 0 | 36.5704
5597 | 0 | 0 | 0 | 1 | 19.4 | 0 | 0 | 0 | 0 | 103.6311 | 41.3909 | 0 | 104.7642 | 21% | 0 | 0 | 10% | 0 | 39.0105
5598 | 26 | 9 | 7 | 1.6 | 19.3 | 0 | 0 | 0 | 0 | 111.0453 | 44.4718 | 0 | 113.3546 | 12% | 0 | 0 | 10% | 0 | 42.1267
5599 | 382 | 129 | 50 | 1.8 | 21 | 0 | 60.5351 | 0.060193 | 0 | 115.531 | 46.1798 | 0 | 118.3658 | 3% | 0 | 0 | 10% | 0 | 43.9636
5600 | 645 | 332 | 80 | 3.1 | 23.6 | 132.1331 | 0 | 15.3519 | 0 | 81.7625 | 31.8598 | 49.6411 | 0 | 7% | 0 | 0 | 10% | 0 | 45.5531
5601 | 775 | 535 | 94 | 5.6 | 25.5 | 187.6959 | 0 | 34.1361 | 1.3238 | 42.5725 | 14.712 | 146.1138 | 0 | 18% | 0 | 0 | 10% | 0 | 46.7373
5602 | 839 | 708 | 103 | 5.6 | 26.6 | 220.1773 | 0 | 53.5444 | 0 | 45.7328 | 15.9038 | 175.8503 | 0 | 31% | 19.253 | 0 | 36.18% | 0 | 47.7732
5603 | 860 | 835 | 117 | 5.5 | 27.7 | 234.8339 | 0 | 60.2983 | 6.2871 | 42.6046 | 14.5366 | 193.5616 | 0 | 46% | 25 | 0 | 70.18% | 0 | 47.2647
5604 | 873 | 911 | 126 | 6.5 | 28 | 243.3548 | 0 | 48.8516 | 25.4906 | 42.6083 | 14.5118 | 201.9896 | 0 | 61% | 14.5706 | 0 | 90% | 0 | 46.1174
5605 | 892 | 925 | 112 | 7.1 | 28.7 | 249.5682 | 0 | 33.9595 | 41.1405 | 42.6093 | 14.4499 | 208.0947 | 0 | 76% | 0 | 0 | 90% | 0 | 45.6598
5606 | 884 | 877 | 109 | 7.2 | 29.1 | 243.6254 | 0 | 33.4784 | 37.0581 | 42.6099 | 14.4146 | 201.9619 | 0 | 91% | 0 | 0 | 90% | 0 | 45.1818
5607 | 850 | 769 | 108 | 7.8 | 29.1 | 161.2075 | 75.3548 | 29.2676 | 29.8176 | 42.6098 | 14.4145 | 119.3888 | 0 | 100% | 0 | 0 | 90% | 0 | 44.6774
5608 | 798 | 612 | 102 | 7.7 | 28.5 | 42.1519 | 185.774 | 28.6657 | 14.1718 | 42.6086 | 14.4675 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.8428
5609 | 708 | 420 | 88 | 7.7 | 27.5 | 42.1573 | 137.8503 | 23.3998 | 0 | 42.6059 | 14.5544 | 0 | 0 | 100% | 0 | 4.7936 | 82.33% | 0 | 43.4576
5610 | 529 | 212 | 63 | 7.2 | 26.4 | 42.1574 | 58.3574 | 4.9783 | 0 | 42.6033 | 14.6477 | 0 | 0 | 100% | 0 | 24.5349 | 43.07% | 0 | 44.871
5611 | 134 | 38 | 22 | 6.3 | 24.9 | 0 | 14.8416 | 0 | 0 | 64.2693 | 23.9426 | 0 | 64.0776 | 95% | 0 | 20.6714 | 10% | 0 | 42.5385
5612 | 0 | 0 | 0 | 5.1 | 23.2 | 0 | 0 | 0 | 0 | 106.5464 | 42.2617 | 0 | 109.7314 | 87% | 0 | 0 | 10% | 0 | 39.5651
5613 | 0 | 0 | 0 | 4.5 | 21.9 | 0 | 0 | 0 | 0 | 99.3205 | 39.3767 | 0 | 98.9484 | 80% | 0 | 0 | 10% | 0 | 37.207
5614 | 0 | 0 | 0 | 3.7 | 21.2 | 0 | 0 | 0 | 0 | 93.6777 | 37.0914 | 0 | 92.1357 | 73% | 0 | 0 | 10% | 0 | 34.9706
5615 | 0 | 0 | 0 | 3.2 | 21 | 0 | 0 | 0 | 0 | 90.0171 | 35.564 | 0 | 87.7918 | 66% | 0 | 0 | 10% | 0 | 33.4055
5616 | 0 | 0 | 0 | 2.8 | 19.8 | 0 | 0 | 0 | 0 | 87.9124 | 34.7731 | 0 | 85.475 | 60% | 0 | 0 | 10% | 0 | 32.549
5617 | 0 | 0 | 0 | 1.7 | 19.2 | 0 | 0 | 0 | 0 | 86.7238 | 34.3189 | 0 | 84.2569 | 53% | 0 | 0 | 10% | 0 | 32.031
5618 | 0 | 0 | 0 | 1 | 19.2 | 0 | 0 | 0 | 0 | 87.7696 | 34.7576 | 0 | 85.6743 | 47% | 0 | 0 | 10% | 0 | 32.4121
5619 | 0 | 0 | 0 | 1.3 | 18.9 | 0 | 0 | 0 | 0 | 92.5957 | 36.8134 | 0 | 91.6629 | 40% | 0 | 0 | 10% | 0 | 34.4251
5620 | 0 | 0 | 0 | 1.1 | 18.6 | 0 | 0 | 0 | 0 | 97.408 | 38.8498 | 0 | 97.3956 | 33% | 0 | 0 | 10% | 0 | 36.4579
5621 | 0 | 0 | 0 | 1.9 | 17.8 | 0 | 0 | 0 | 0 | 102.6393 | 41.0997 | 0 | 103.5399 | 25% | 0 | 0 | 10% | 0 | 38.7267
5622 | 43 | 9 | 6 | 1.6 | 18.3 | 0 | 0 | 0 | 0 | 110.4716 | 44.3177 | 0 | 112.6641 | 17% | 0 | 0 | 10% | 0 | 41.9769
5623 | 493 | 137 | 39 | 1.9 | 20.7 | 55.7873 | 14.0632 | 0.024461 | 0 | 113.6396 | 45.4228 | 0 | 62.0243 | 12% | 0 | 0 | 10% | 0 | 44.0811
5624 | 727 | 343 | 62 | 3.6 | 24.1 | 150.7706 | 0 | 16.2363 | 0 | 80.4298 | 31.2 | 71.242 | 0 | 17% | 0 | 0 | 10% | 0 | 45.5964
5625 | 833 | 547 | 75 | 5.8 | 26.1 | 202.8646 | 0 | 36.6946 | 0 | 45.3485 | 15.7919 | 158.6407 | 0 | 29% | 3.3083 | 0 | 14.5% | 0 | 46.9127
5626 | 892 | 722 | 81 | 6 | 27.3 | 235.1767 | 0 | 55.0792 | 0 | 46.2966 | 16.0737 | 190.1972 | 0 | 43% | 20.653 | 0 | 42.59% | 0 | 47.9237
5627 | 917 | 851 | 88 | 5.7 | 28.3 | 251.7276 | 0 | 60.6414 | 7.7867 | 42.597 | 14.4813 | 210.332 | 0 | 59% | 25 | 0 | 76.59% | 0 | 47.3773
5628 | 924 | 923 | 95 | 6.4 | 28.9 | 258.8744 | 0 | 44.3583 | 30.7417 | 42.6028 | 14.4299 | 217.3762 | 0 | 75% | 9.8622 | 0 | 90% | 0 | 46.0843
5629 | 927 | 936 | 95 | 6.7 | 29.5 | 260.5012 | 0 | 34.0563 | 41.0437 | 42.6045 | 14.3772 | 218.8548 | 0 | 92% | 0 | 0 | 90% | 0 | 45.5604
5630 | 915 | 885 | 94 | 6.7 | 29.8 | 156.5718 | 111.9186 | 30.4295 | 41.1762 | 42.606 | 14.351 | 114.8208 | 0 | 100% | 0 | 0 | 90% | 0 | 45.3143
5631 | 882 | 774 | 92 | 6.7 | 30 | 42.1516 | 225.1757 | 29.5274 | 30.2704 | 42.6049 | 14.3328 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.5695
5632 | 811 | 609 | 92 | 7.3 | 29.1 | 42.1572 | 189.6045 | 28.6426 | 13.9813 | 42.6023 | 14.412 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.7641
5633 | 697 | 412 | 87 | 7.4 | 28.2 | 42.1573 | 134.5524 | 22.8527 | 0 | 42.5998 | 14.4912 | 0 | 0 | 100% | 0 | 5.225 | 81.64% | 0 | 43.2785
5634 | 501 | 203 | 64 | 7.7 | 26.8 | 42.1574 | 50.5126 | 4.6618 | 0 | 42.5973 | 14.6118 | 0 | 0 | 100% | 0 | 24.5016 | 42.44% | 0 | 44.4852
5635 | 132 | 37 | 21 | 5.6 | 25.4 | 0 | 13.6351 | 0 | 0 | 63.8078 | 23.6946 | 0 | 63.6757 | 95% | 0 | 20.2734 | 10% | 0 | 41.8924
5636 | 0 | 0 | 0 | 3.9 | 23.7 | 0 | 0 | 0 | 0 | 105.3217 | 41.7095 | 0 | 108.2254 | 87% | 0 | 0 | 10% | 0 | 39.0276
5637 | 0 | 0 | 0 | 3.7 | 22.4 | 0 | 0 | 0 | 0 | 99.1106 | 39.2442 | 0 | 98.7608 | 80% | 0 | 0 | 10% | 0 | 37.0592
5638 | 0 | 0 | 0 | 3.8 | 21.5 | 0 | 0 | 0 | 0 | 94.2193 | 37.2948 | 0 | 92.8455 | 73% | 0 | 0 | 10% | 0 | 35.1613
5639 | 0 | 0 | 0 | 3 | 20.9 | 0 | 0 | 0 | 0 | 89.9305 | 35.5357 | 0 | 87.6939 | 66% | 0 | 0 | 10% | 0 | 33.3762
5640 | 0 | 0 | 0 | 1.4 | 20.5 | 0 | 0 | 0 | 0 | 87.3127 | 34.4685 | 0 | 84.7687 | 60% | 0 | 0 | 10% | 0 | 32.2433
5641 | 0 | 0 | 0 | 1 | 20.2 | 0 | 0 | 0 | 0 | 85.4992 | 33.7334 | 0 | 82.8309 | 54% | 0 | 0 | 10% | 0 | 31.4405
5642 | 0 | 0 | 0 | 1.2 | 19.4 | 0 | 0 | 0 | 0 | 84.4268 | 33.3447 | 0 | 81.7572 | 48% | 0 | 0 | 10% | 0 | 30.9891
5643 | 0 | 0 | 0 | 1.1 | 19.2 | 0 | 0 | 0 | 0 | 85.6852 | 33.8851 | 0 | 83.4048 | 41% | 0 | 0 | 10% | 0 | 31.4725
5644 | 0 | 0 | 0 | 2.4 | 19.9 | 0 | 0 | 0 | 0 | 86.627 | 34.2287 | 0 | 84.6316 | 35% | 0 | 0 | 10% | 0 | 31.7782
5645 | 0 | 0 | 0 | 1.7 | 19.2 | 0 | 0 | 0 | 0 | 89.8275 | 35.6241 | 0 | 88.5668 | 28% | 0 | 0 | 10% | 0 | 33.144
5646 | 36 | 9 | 6 | 1.7 | 18.8 | 0 | 0 | 0 | 0 | 97.1908 | 38.7452 | 0 | 97.4972 | 21% | 0 | 0 | 10% | 0 | 36.2495
5647 | 443 | 132 | 45 | 1.9 | 20.3 | 48.4543 | 12.3049 | 0.14334 | 0 | 100.5982 | 40.0499 | 0 | 54.447 | 17% | 0 | 0 | 10% | 0 | 38.8809
5648 | 680 | 336 | 73 | 4.3 | 23 | 139.0527 | 0 | 15.9745 | 0 | 68.9146 | 26.1916 | 70.2021 | 0 | 22% | 0 | 0 | 10% | 0 | 40.4578
5649 | 794 | 538 | 88 | 5 | 25 | 193.1691 | 0 | 36.1884 | 0 | 45.2545 | 15.8482 | 148.5604 | 0 | 33% | 8.3249 | 0 | 21.32% | 0 | 41.543
5650 | 861 | 715 | 96 | 6.7 | 26.8 | 225.7564 | 0 | 54.6221 | 0 | 43.8188 | 15.1064 | 182.7413 | 0 | 47% | 24.649 | 0 | 54.84% | 0 | 42.6036
5651 | 894 | 845 | 101 | 6.5 | 27.9 | 244.3356 | 0 | 55.5669 | 12.4785 | 42.5862 | 14.513 | 202.5504 | 0 | 62% | 25 | 0 | 88.84% | 0 | 42.4156
5652 | 906 | 917 | 105 | 6.1 | 28.4 | 253.8212 | 0 | 30.6524 | 44.4476 | 42.5936 | 14.4713 | 212.0151 | 0 | 78% | 0.84965 | 0 | 90% | 0 | 41.4985
5653 | 910 | 929 | 103 | 6.1 | 29.4 | 255.9797 | 0 | 27.5458 | 47.5542 | 42.5976 | 14.3837 | 213.9653 | 0 | 93% | 0 | 0 | 90% | 0 | 40.5893
5654 | 891 | 874 | 103 | 5.6 | 29.7 | 132.7679 | 131.9973 | 25.1365 | 45.4437 | 42.6004 | 14.358 | 91.0178 | 0 | 100% | 0 | 0 | 90% | 0 | 40.2431
5655 | 850 | 762 | 106 | 5.7 | 29.8 | 42.1517 | 215.1883 | 24.8382 | 34.0157 | 42.5993 | 14.3487 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.8962
5656 | 780 | 600 | 104 | 6.2 | 29.3 | 42.1572 | 180.3562 | 24.5803 | 17.3251 | 42.5968 | 14.3924 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.6821
5657 | 672 | 404 | 92 | 5.8 | 28.3 | 47.9868 | 120.6972 | 22.34 | 0 | 48.3219 | 16.819 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 39.8487
5658 | 482 | 196 | 64 | 5.5 | 27.3 | 42.0407 | 46.6522 | 4.397 | 0 | 42.5923 | 14.5671 | 0 | 0 | 100% | 0 | 21.7576 | 55.19% | 0 | 41.4316
5659 | 112 | 33 | 19 | 4.9 | 25.7 | 0 | 10.7248 | 0 | 0 | 46.7615 | 16.4187 | 0 | 45.2372 | 97% | 0 | 25 | 15.19% | 0 | 39.3514
5660 | 0 | 0 | 0 | 3.8 | 23.8 | 0 | 0 | 0 | 0 | 94.0131 | 36.8926 | 0 | 96.5107 | 90% | 0 | 3.2424 | 10% | 0 | 37.1831
5661 | 0 | 0 | 0 | 4 | 22.7 | 0 | 0 | 0 | 0 | 95.0434 | 37.5304 | 0 | 94.7852 | 83% | 0 | 0 | 10% | 0 | 35.1266
5662 | 0 | 0 | 0 | 2.6 | 21.9 | 0 | 0 | 0 | 0 | 89.7932 | 35.3953 | 0 | 88.0733 | 76% | 0 | 0 | 10% | 0 | 33.0781
5663 | 0 | 0 | 0 | 1.8 | 21.6 | 0 | 0 | 0 | 0 | 86.061 | 33.8573 | 0 | 83.7233 | 70% | 0 | 0 | 10% | 0 | 31.5004
5664 | 0 | 0 | 0 | 1.4 | 20.8 | 0 | 0 | 0 | 0 | 83.889 | 33.0159 | 0 | 81.3622 | 64% | 0 | 0 | 10% | 0 | 30.5927
5665 | 0 | 0 | 0 | 1.9 | 20.6 | 0 | 0 | 0 | 0 | 82.066 | 32.2346 | 0 | 79.5666 | 58% | 0 | 0 | 10% | 0 | 29.7485
5666 | 0 | 0 | 0 | 2.2 | 20 | 0 | 0 | 0 | 0 | 81.7005 | 32.1143 | 0 | 79.345 | 52% | 0 | 0 | 10% | 0 | 29.5754
5667 | 0 | 0 | 0 | 2.2 | 19.8 | 0 | 0 | 0 | 0 | 81.988 | 32.2602 | 0 | 79.7457 | 46% | 0 | 0 | 10% | 0 | 29.6807
5668 | 0 | 0 | 0 | 1.7 | 19.6 | 0 | 0 | 0 | 0 | 81.5722 | 32.086 | 0 | 79.4078 | 40% | 0 | 0 | 10% | 0 | 29.4755
5669 | 0 | 0 | 0 | 1.7 | 19.3 | 0 | 0 | 0 | 0 | 82.72 | 32.6316 | 0 | 80.6389 | 34% | 0 | 0 | 10% | 0 | 29.994
5670 | 33 | 8 | 5 | 2.3 | 19.1 | 0 | 0 | 0 | 0 | 88.4148 | 35.0378 | 0 | 87.469 | 27% | 0 | 0 | 10% | 0 | 32.3708
5671 | 456 | 129 | 41 | 1.3 | 20.9 | 50.5095 | 12.6693 | 0.039549 | 0 | 90.9195 | 35.9563 | 0 | 41.521 | 24% | 0 | 0 | 10% | 0 | 34.6501
5672 | 695 | 334 | 67 | 2.4 | 23 | 143.6665 | 0 | 16.0207 | 0 | 59.935 | 22.2776 | 83.3366 | 0 | 31% | 0 | 0 | 10% | 0 | 36.5678
5673 | 809 | 538 | 81 | 4.7 | 25.2 | 197.3659 | 2.98e-14 | 36.4179 | 0 | 45.694 | 16.0126 | 151.9395 | 0 | 42% | 12.7158 | 0 | 27.29% | 0 | 37.5116
5674 | 865 | 711 | 91 | 5.7 | 26.8 | 227.9316 | 0 | 51.6121 | 2.9636 | 42.5659 | 14.601 | 185.76 | 0 | 56% | 25 | 0 | 61.29% | 0 | 38.7224
5675 | 886 | 838 | 101 | 6.4 | 27.9 | 242.136 | 0 | 48.5016 | 19.0596 | 42.5798 | 14.5108 | 199.9917 | 0 | 70% | 21.1078 | 0 | 90% | 0 | 39.261
5676 | 883 | 906 | 114 | 6.2 | 28.7 | 246.9717 | 0 | 25.7996 | 48.5486 | 42.5864 | 14.4422 | 204.7776 | 0 | 85% | 0 | 0 | 90% | 0 | 38.4236
5677 | 876 | 915 | 120 | 5.8 | 28.9 | 246.0549 | 0 | 19.9715 | 55.1285 | 42.5912 | 14.426 | 203.7272 | 0 | 100% | 0 | 0 | 90% | 0 | 37.802
5678 | 849 | 860 | 126 | 6.2 | 29.3 | 41.3453 | 223.6479 | 22.1933 | 47.1799 | 42.5942 | 14.3915 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.2942
5679 | 771 | 745 | 149 | 7.2 | 28.8 | 42.1518 | 189.8453 | 21.7239 | 35.4111 | 42.5919 | 14.4351 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.8686
5680 | 668 | 582 | 158 | 6.5 | 28.5 | 42.1573 | 146.2102 | 21.5334 | 19.0466 | 42.5896 | 14.461 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.7041
5681 | 548 | 383 | 128 | 6.7 | 27.8 | 45.8697 | 87.8685 | 20.7801 | 0 | 46.2388 | 16.0043 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 37.486
5682 | 387 | 192 | 86 | 6.8 | 26.2 | 42.0797 | 20.6361 | 4.4676 | 0 | 42.5855 | 14.6585 | 0 | 0 | 100% | 0 | 20.1964 | 57.69% | 0 | 40.0326
5683 | 78 | 41 | 31 | 5.9 | 24.5 | 0 | 6.8756 | 0 | 0 | 46.2178 | 16.2955 | 0 | 44.6953 | 97% | 0 | 25 | 17.69% | 0 | 39.2309
5684 | 0 | 0 | 0 | 4.6 | 23.1 | 0 | 0 | 0 | 0 | 89.95 | 35.2231 | 0 | 92.0816 | 90% | 0 | 4.8036 | 10% | 0 | 37.0812
5685 | 0 | 0 | 0 | 3.4 | 22.4 | 0 | 0 | 0 | 0 | 94.2793 | 37.2417 | 0 | 93.9987 | 83% | 0 | 0 | 10% | 0 | 34.8087
5686 | 0 | 0 | 0 | 2.7 | 22 | 0 | 0 | 0 | 0 | 89.9191 | 35.4403 | 0 | 88.3202 | 76% | 0 | 0 | 10% | 0 | 33.0959
5687 | 0 | 0 | 0 | 2.8 | 21.6 | 0 | 0 | 0 | 0 | 86.9567 | 34.2318 | 0 | 84.8482 | 70% | 0 | 0 | 10% | 0 | 31.8567
5688 | 0 | 0 | 0 | 3.1 | 21.8 | 0 | 0 | 0 | 0 | 85.8589 | 33.7572 | 0 | 83.7048 | 64% | 0 | 0 | 10% | 0 | 31.3278
5689 | 0 | 0 | 0 | 3 | 21.4 | 0 | 0 | 0 | 0 | 85.0849 | 33.4671 | 0 | 82.9232 | 58% | 0 | 0 | 10% | 0 | 30.9915
5690 | 0 | 0 | 0 | 3.4 | 21 | 0 | 0 | 0 | 0 | 86.8402 | 34.233 | 0 | 85.1309 | 51% | 0 | 0 | 10% | 0 | 31.7154
5691 | 0 | 0 | 0 | 2.5 | 20.6 | 0 | 0 | 0 | 0 | 93.6016 | 37.1106 | 0 | 93.4735 | 44% | 0 | 0 | 10% | 0 | 34.5662
5692 | 0 | 0 | 0 | 2.6 | 19.8 | 0 | 0 | 0 | 0 | 101.3381 | 40.3981 | 0 | 102.5801 | 37% | 0 | 0 | 10% | 0 | 37.8781
5693 | 0 | 0 | 0 | 3.2 | 20.3 | 0 | 0 | 0 | 0 | 108.3658 | 43.2787 | 0 | 110.7351 | 28% | 0 | 0 | 10% | 0 | 40.8167
5694 | 1 | 5 | 5 | 3.9 | 20.6 | 0 | 0 | 0 | 0 | 115.326 | 46.1296 | 0 | 118.6705 | 19% | 0 | 0 | 10% | 0 | 43.743
5695 | 44 | 87 | 78 | 3.2 | 21.5 | 0 | 8.0987 | 0 | 0 | 120.4226 | 48.14 | 0 | 124.3396 | 10% | 0 | 0 | 10% | 0 | 45.8408
5696 | 123 | 232 | 188 | 4.6 | 23.5 | 0 | 30.4331 | 9.09 | 0 | 101.9603 | 40.3315 | 0 | 101.897 | 2% | 0 | 0 | 10% | 0 | 47.2519
5697 | 115 | 344 | 275 | 5.3 | 24.5 | 0 | 32.8727 | 17.6306 | 0 | 32.5074 | 12.6751 | 0 | 31.1742 | 0% | 0 | 0 | 10% | 0 | 28.2342
5698 | 49 | 371 | 331 | 5.8 | 25.2 | 0 | 15.0209 | 20.3089 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 18.2813
5699 | 344 | 731 | 438 | 6 | 26.7 | 66.7841 | 16.8834 | 55.0399 | 0 | 0 | 0 | 64.3099 | 0 | 5% | 5.832 | 0 | 17.93% | 0 | 47.9272
5700 | 301 | 699 | 422 | 6.4 | 27.5 | 70.1544 | 0 | 53.2196 | 0 | 0 | 0 | 68.9192 | 0 | 10% | 5.4606 | 0 | 25.36% | 0 | 46.7196
5701 | 434 | 813 | 415 | 6.3 | 28.6 | 111.1272 | 0 | 64.4066 | 0 | 0 | 0 | 109.1371 | 0 | 18% | 16.7993 | 0 | 48.2% | 0 | 46.2044
5702 | 364 | 710 | 390 | 7.7 | 28.6 | 87.2476 | 5.21e-15 | 54.0052 | 0 | 42.9569 | 5.2235 | 46.1108 | 0 | 22% | 21.593 | 0 | 77.57% | 0 | 36.076
5703 | 249 | 552 | 356 | 7.4 | 28.2 | 0 | 64.1799 | 38.2364 | 0 | 43.9218 | 15.0307 | 0 | 41.0691 | 19% | 7.052 | 0 | 87.16% | 0 | 44.9847
5704 | 29 | 279 | 259 | 7.6 | 27.1 | 0 | 8.5429 | 11.4872 | 0 | 42.5187 | 14.5593 | 0 | 39.7716 | 16% | 0 | 20.1544 | 54.92% | 0 | 44.0405
5705 | 160 | 306 | 226 | 7.2 | 26.4 | 0 | 42.4475 | 14.085 | 0 | 42.5016 | 14.6127 | 0 | 39.8126 | 13% | 0 | 17.6907 | 26.61% | 0 | 44.1889
5706 | 20 | 104 | 98 | 6.9 | 25.1 | 0 | 4.2268 | 0.57626 | 0 | 94.9843 | 36.9762 | 0 | 96.1175 | 6% | 0 | 10.3812 | 10% | 0 | 45.6023
5707 | 4 | 30 | 30 | 5.9 | 24.1 | 0 | 0.32192 | 0 | 0 | 72.1355 | 28.6234 | 0 | 73.7947 | 0% | 0 | 0 | 10% | 0 | 26.3841
5708 | 0 | 0 | 0 | 4.7 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1035
5709 | 0 | 0 | 0 | 4.6 | 23.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0848
5710 | 0 | 0 | 0 | 4.3 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0665
5711 | 0 | 0 | 0 | 1.7 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0485
5712 | 0 | 0 | 0 | 1 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0309
5713 | 0 | 0 | 0 | 1.3 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0136
5714 | 0 | 0 | 0 | 1.1 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9966
5715 | 0 | 0 | 0 | 1.4 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.98
5716 | 0 | 0 | 0 | 1.4 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9636
5717 | 0 | 0 | 0 | 0.7 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9476
5718 | 0 | 6 | 6 | 0.5 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9319
5719 | 48 | 85 | 78 | 0.7 | 20.8 | 0 | 8.8002 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9163
5720 | 159 | 241 | 177 | 0.9 | 22.9 | 0 | 39.2659 | 9.3399 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 7.4388
5721 | 574 | 500 | 177 | 1.2 | 25.4 | 111.545 | 26.8559 | 33.4036 | 0 | 0 | 0 | 105.0613 | 0 | 8% | 0 | 0 | 10% | 0 | 31.7547
5722 | 699 | 687 | 187 | 1.7 | 27 | 183.0001 | 0 | 52.4929 | 0 | 0 | 0 | 179.4302 | 0 | 22% | 3.1255 | 0 | 14.25% | 0 | 47.3149
5723 | 803 | 846 | 183 | 2.6 | 28.8 | 220.1026 | 0 | 68.0622 | 0 | 0 | 0 | 217.5741 | 0 | 39% | 19.97 | 0 | 41.41% | 0 | 45.6727
5724 | 796 | 919 | 211 | 5.3 | 29.4 | 220.8635 | 0 | 72.9216 | 2.1784 | 0 | 0 | 219.0201 | 0 | 55% | 25 | 0 | 75.41% | 0 | 45.4558
5725 | 638 | 859 | 283 | 4.7 | 29.5 | 174.3589 | 0 | 58.0448 | 11.2228 | 42.5176 | 0 | 133.5165 | 0 | 66% | 10.7281 | 0 | 90% | 0 | 44.7364
5726 | 248 | 587 | 370 | 3.8 | 29.6 | 55.4883 | 0 | 42.7928 | 0 | 0 | 0 | 55.036 | 0 | 70% | 0 | 0 | 90% | 0 | 41.845
5727 | 707 | 759 | 220 | 3.9 | 30.2 | 186.8965 | 0 | 38.4178 | 20.3859 | 42.534 | 7.7312 | 144.6765 | 0 | 81% | 0 | 0 | 90% | 0 | 43.7215
5728 | 501 | 501 | 185 | 5.2 | 29.7 | 118.4384 | 0 | 30.2911 | 3.3518 | 42.5428 | 14.3386 | 77.571 | 0 | 86% | 0 | 0 | 90% | 0 | 43.0736
5729 | 157 | 225 | 154 | 3.1 | 28.7 | 0 | 41.5729 | 8.7941 | 0 | 42.5464 | 14.4286 | 0 | 40.4418 | 83% | 0 | 21.8054 | 55.11% | 0 | 43.3638
5730 | 4 | 70 | 69 | 1.9 | 27.6 | 0 | 0.83965 | 0 | 0 | 61.1833 | 22.3736 | 0 | 58.9542 | 79% | 0 | 25 | 15.11% | 0 | 44.7384
5731 | 19 | 16 | 14 | 4.4 | 26.5 | 0 | 1.3824 | 0 | 0 | 106.0586 | 41.5857 | 0 | 109.9676 | 71% | 0 | 3.1946 | 10% | 0 | 42.0395
5732 | 0 | 0 | 0 | 5.9 | 22.9 | 0 | 0 | 0 | 0 | 104.4878 | 41.4431 | 0 | 106.1092 | 63% | 0 | 0 | 10% | 0 | 39.0212
5733 | 0 | 0 | 0 | 3.4 | 21.6 | 0 | 0 | 0 | 0 | 97.7942 | 38.7711 | 0 | 97.534 | 56% | 0 | 0 | 10% | 0 | 36.4861
5734 | 0 | 0 | 0 | 1.4 | 21.2 | 0 | 0 | 0 | 0 | 92.8061 | 36.7268 | 0 | 91.4877 | 49% | 0 | 0 | 10% | 0 | 34.4766
5735 | 0 | 0 | 0 | 1.3 | 21 | 0 | 0 | 0 | 0 | 89.279 | 35.2574 | 0 | 87.2137 | 42% | 0 | 0 | 10% | 0 | 32.9985
5736 | 0 | 0 | 0 | 0.6 | 20.7 | 0 | 0 | 0 | 0 | 87.8452 | 34.6794 | 0 | 85.5951 | 36% | 0 | 0 | 10% | 0 | 32.3869
5737 | 0 | 0 | 0 | 2.4 | 20.5 | 0 | 0 | 0 | 0 | 87.284 | 34.4603 | 0 | 85.0329 | 29% | 0 | 0 | 10% | 0 | 32.1316
5738 | 0 | 0 | 0 | 1.5 | 19.9 | 0 | 0 | 0 | 0 | 88.3886 | 34.9702 | 0 | 86.4567 | 23% | 0 | 0 | 10% | 0 | 32.6066
5739 | 0 | 0 | 0 | 0.6 | 18.9 | 0 | 0 | 0 | 0 | 94.2754 | 37.5268 | 0 | 93.73 | 16% | 0 | 0 | 10% | 0 | 35.1303
5740 | 0 | 0 | 0 | 0.3 | 18.2 | 0 | 0 | 0 | 0 | 101.1535 | 40.4501 | 0 | 101.8457 | 8% | 0 | 0 | 10% | 0 | 38.0509
5741 | 0 | 0 | 0 | 1 | 17.9 | 0 | 0 | 0 | 0 | 107.4696 | 43.1107 | 0 | 109.2777 | 0% | 0 | 0 | 10% | 0 | 40.732
5742 | 13 | 5 | 5 | 0.7 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1779
5743 | 340 | 114 | 48 | 0.4 | 20.5 | 0 | 51.2067 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1546
5744 | 617 | 315 | 82 | 0.6 | 23.6 | 125.2635 | 0 | 15.3084 | 0 | 0 | 0 | 120.4469 | 0 | 9% | 0 | 0 | 10% | 0 | 13.8152
5745 | 752 | 520 | 100 | 0.8 | 27.1 | 183.9143 | -2.98e-14 | 35.3999 | 0 | 0 | 0 | 181.6318 | 0 | 23% | 0 | 0 | 10% | 0 | 33.3557
5746 | 822 | 697 | 114 | 1.5 | 29.4 | 218.2953 | 0 | 53.7088 | 0 | 0 | 0 | 216.6062 | 0 | 39% | 3.343 | 0 | 14.55% | 0 | 47.9817
5747 | 852 | 826 | 126 | 1.7 | 30.7 | 235.2329 | 0 | 66.8877 | 0 | 0 | 0 | 233.7988 | 0 | 57% | 17.0656 | 0 | 37.76% | 0 | 47.2444
5748 | 768 | 842 | 163 | 2.6 | 31.6 | 214.6212 | 0 | 68.4979 | 0 | 0 | 0 | 213.4681 | 0 | 73% | 19.9366 | 0 | 64.87% | 0 | 46.1343
5749 | 857 | 940 | 175 | 5.8 | 31.5 | 239.9177 | 0 | 68.0129 | 6.5227 | 0 | 0 | 238.609 | 0 | 91% | 18.4784 | 0 | 90% | 0 | 46.824
5750 | 854 | 865 | 140 | 5.3 | 31.8 | 122.9445 | 124.3579 | 47.8047 | 22.7715 | 0 | 0 | 122.335 | 0 | 100% | 0 | 0 | 90% | 0 | 46.1616
5751 | 819 | 748 | 129 | 6.2 | 31.5 | 0 | 241.3198 | 47.4634 | 10.981 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.5667
5752 | 758 | 583 | 114 | 6.2 | 31.2 | 40.6028 | 174.728 | 41.2562 | 0 | 42.5859 | 0 | 0 | 0 | 100% | 0 | 4.5204 | 82.77% | 0 | 44.6018
5753 | 660 | 387 | 92 | 5.4 | 30.6 | 42.1617 | 123.2376 | 21.6451 | 0 | 42.5836 | 12.4743 | 0 | 0 | 100% | 0 | 9.8119 | 67.07% | 0 | 44.5776
5754 | 463 | 180 | 61 | 5.2 | 29.3 | 47.5552 | 31.6411 | 3.851 | 0 | 47.8851 | 16.5423 | 0 | 0 | 100% | 0 | 25 | 27.07% | 0 | 46.0856
5755 | 99 | 25 | 15 | 3.9 | 27.7 | 0 | 6.4347 | 0 | 0 | 93.6635 | 36.1276 | 0 | 97.4929 | 93% | 0 | 9.0064 | 12.66% | 0 | 43.0279
5756 | 0 | 0 | 0 | 1.6 | 26.4 | 0 | 0 | 0 | 0 | 106.9321 | 42.0714 | 0 | 107.7691 | 85% | 0 | 0 | 12.66% | 0 | 39.967
5757 | 0 | 0 | 0 | 1.6 | 24.8 | 0 | 0 | 0 | 0 | 100.5019 | 39.5865 | 0 | 99.4474 | 77% | 0 | 0 | 12.66% | 0 | 37.6546
5758 | 0 | 0 | 0 | 0.9 | 23.4 | 0 | 0 | 0 | 0 | 95.0057 | 37.45 | 0 | 93.114 | 70% | 0 | 0 | 12.66% | 0 | 35.4963
5759 | 0 | 0 | 0 | 1.2 | 22.5 | 0 | 0 | 0 | 0 | 91.3945 | 36.0169 | 0 | 88.9869 | 63% | 0 | 0 | 12.66% | 0 | 33.9986
5760 | 0 | 0 | 0 | 0.8 | 22.4 | 0 | 0 | 0 | 0 | 89.765 | 35.3408 | 0 | 87.2719 | 57% | 0 | 0 | 12.66% | 0 | 33.245
5761 | 0 | 0 | 0 | 1.6 | 21.2 | 0 | 0 | 0 | 0 | 88.9436 | 35.098 | 0 | 86.5016 | 50% | 0 | 0 | 12.66% | 0 | 32.9338
5762 | 0 | 0 | 0 | 1.9 | 20.4 | 0 | 0 | 0 | 0 | 89.7057 | 35.4822 | 0 | 87.596 | 44% | 0 | 0 | 12.66% | 0 | 33.2597
5763 | 0 | 0 | 0 | 1.6 | 20.3 | 0 | 0 | 0 | 0 | 95.7753 | 38.0404 | 0 | 95.0573 | 36% | 0 | 0 | 12.66% | 0 | 35.7701
5764 | 0 | 0 | 0 | 1.5 | 19.9 | 0 | 0 | 0 | 0 | 102.8095 | 41.0061 | 0 | 103.3853 | 29% | 0 | 0 | 12.66% | 0 | 38.7303
5765 | 0 | 0 | 0 | 1.1 | 19.3 | 0 | 0 | 0 | 0 | 108.9827 | 43.6186 | 0 | 110.5473 | 20% | 0 | 0 | 12.66% | 0 | 41.3692
5766 | 19 | 8 | 7 | 1.7 | 20 | 0 | 0 | 0 | 0 | 116.4698 | 46.6577 | 0 | 119.2132 | 11% | 0 | 0 | 12.66% | 0 | 44.449
5767 | 329 | 115 | 50 | 0.9 | 22.5 | 0 | 48.9896 | 0 | 0 | 121.4603 | 48.4682 | 0 | 124.7867 | 2% | 0 | 0 | 12.66% | 0 | 46.3321
5768 | 602 | 317 | 90 | 1.4 | 24.9 | 121.1111 | 0 | 15.5217 | 0 | 87.4427 | 34.1391 | 32.9343 | 0 | 4% | 0 | 0 | 12.66% | 0 | 48.0805
5769 | 704 | 552 | 160 | 4.2 | 27.6 | 169.0266 | 0 | 36.816 | 1.3627 | 42.5926 | 14.5412 | 127.8126 | 0 | 14% | 0 | 0 | 12.66% | 0 | 49.4056
5770 | 719 | 687 | 177 | 5.4 | 28.6 | 186.1949 | 0 | 53.015 | 0 | 45.3026 | 15.5459 | 142.6727 | 0 | 25% | 16.515 | 0 | 35.12% | 0 | 49.9244
5771 | 643 | 782 | 244 | 5.6 | 29.7 | 170.7277 | 0 | 61.4465 | 0 | 43.5916 | 14.7535 | 128.9442 | 0 | 34% | 24.6714 | 0 | 68.67% | 0 | 49.5375
5772 | 768 | 871 | 190 | 4.7 | 31 | 213.1288 | 0 | 51.9343 | 18.9824 | 42.608 | 14.2435 | 171.8845 | 0 | 47% | 15.6826 | 0 | 90% | 0 | 48.1079
5773 | 230 | 625 | 409 | 4.9 | 31.2 | 0 | 61.5489 | 34.7436 | 10.4049 | 42.6072 | 14.2248 | 0 | 40.1047 | 44% | 0 | 0 | 90% | 0 | 47.5449
5774 | 431 | 718 | 350 | 5.1 | 30.6 | 109.2541 | 0 | 34.2927 | 21.215 | 42.602 | 14.2776 | 65.1967 | 0 | 49% | 0 | 0 | 90% | 0 | 47.1594
5775 | 415 | 601 | 283 | 5.4 | 30.8 | 100.8218 | 0 | 33.483 | 10.315 | 42.6001 | 14.2589 | 59.5138 | 0 | 54% | 0 | 0 | 90% | 0 | 46.3823
5776 | 119 | 357 | 286 | 4.5 | 29.1 | 0 | 34.9758 | 19.4445 | 0 | 42.5968 | 14.4101 | 0 | 40.4284 | 51% | 0 | 13.5457 | 68.33% | 0 | 45.7711
5777 | 422 | 352 | 170 | 2.8 | 29.6 | 71.0505 | 17.1214 | 19.2132 | 0 | 42.5912 | 14.3638 | 35.7136 | 7.1636 | 53% | 0 | 13.3855 | 46.91% | 0 | 45.5136
5778 | 334 | 159 | 70 | 2 | 28.7 | 0 | 56.0049 | 2.8344 | 0 | 62.0023 | 22.5915 | 0 | 60.4012 | 48% | 0 | 23.0688 | 10% | 0 | 46.7368
5779 | 1 | 11 | 11 | 2.6 | 27 | 0 | 0.057207 | 0 | 0 | 118.216 | 46.6286 | 0 | 123.7833 | 39% | 0 | 0 | 10% | 0 | 43.8979
5780 | 0 | 0 | 0 | 2.6 | 26.2 | 0 | 0 | 0 | 0 | 110.6118 | 43.6035 | 0 | 113.6043 | 31% | 0 | 0 | 10% | 0 | 41.0895
5781 | 0 | 0 | 0 | 1.1 | 24.5 | 0 | 0 | 0 | 0 | 103.6026 | 40.9096 | 0 | 104.7772 | 23% | 0 | 0 | 10% | 0 | 38.5142
5782 | 0 | 0 | 0 | 1.2 | 23.8 | 0 | 0 | 0 | 0 | 97.9143 | 38.6163 | 0 | 97.7376 | 15% | 0 | 0 | 10% | 0 | 36.2813
5783 | 0 | 0 | 0 | 0.9 | 22.9 | 0 | 0 | 0 | 0 | 93.6175 | 36.9211 | 0 | 92.5988 | 9% | 0 | 0 | 10% | 0 | 34.6092
5784 | 0 | 0 | 0 | 1.2 | 21.9 | 0 | 0 | 0 | 0 | 91.6547 | 36.1828 | 0 | 90.181 | 2% | 0 | 0 | 10% | 0 | 33.8715
5785 | 0 | 0 | 0 | 0.9 | 21.3 | 0 | 0 | 0 | 0 | 23.501 | 9.2829 | 0 | 23.0595 | 0% | 0 | 0 | 10% | 0 | 7.0463
5786 | 0 | 0 | 0 | 1.2 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1917
5787 | 0 | 0 | 0 | 1.3 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1714
5788 | 0 | 0 | 0 | 0.9 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1514
5789 | 0 | 0 | 0 | 0.9 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1318
5790 | 19 | 5 | 5 | 1.8 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1125
5791 | 368 | 113 | 45 | 0.8 | 22.4 | 0 | 55.8102 | 0.018736 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0719
5792 | 627 | 312 | 79 | 1 | 25.3 | 126.7864 | 0 | 15.4514 | 0 | 0 | 0 | 121.0794 | 0 | 9% | 0 | 0 | 10% | 0 | 13.9424
5793 | 750 | 513 | 99 | 1.3 | 27.7 | 182.8392 | 0 | 35.393 | 0 | 0 | 0 | 180.164 | 0 | 23% | 0 | 0 | 10% | 0 | 33.3536
5794 | 813 | 685 | 114 | 1.3 | 29.6 | 215.7134 | 0 | 53.342 | 0 | 42.4887 | 0 | 174.1072 | 0 | 36% | 16.842 | 0 | 32.91% | 0 | 33.6047
5795 | 854 | 815 | 119 | 2.7 | 30.4 | 235.4202 | 0 | 66.7587 | 0 | 0 | 0 | 233.8041 | 0 | 54% | 15.2587 | 0 | 53.66% | 0 | 48.9296
5796 | 873 | 889 | 122 | 3.4 | 31.5 | 246.1943 | 0 | 74.0924 | 0 | 0 | 0 | 244.76 | 0 | 72% | 23.5717 | 0 | 85.71% | 0 | 47.8069
5797 | 861 | 895 | 131 | 4.4 | 32 | 242.3578 | 0 | 54.3631 | 19.9844 | 0 | 0 | 241.0688 | 0 | 90% | 3.1512 | 0 | 90% | 0 | 48.4837
5798 | 684 | 755 | 174 | 3 | 32 | 129.2108 | 63.2643 | 49.8142 | 11.0467 | 0 | 0 | 128.5446 | 0 | 100% | 0 | 0 | 90% | 0 | 48.1236
5799 | 556 | 671 | 244 | 4.8 | 31.4 | 41.4727 | 122.3066 | 42.2983 | 8.4356 | 42.5802 | 5.7217 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 47.0509
5800 | 470 | 477 | 197 | 5.7 | 30.5 | 42.1631 | 84.7994 | 30.8261 | 1.9716 | 42.5788 | 14.2789 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.8142
5801 | 272 | 278 | 155 | 4.8 | 29.6 | 0 | 58.6546 | 12.9686 | 0 | 42.5762 | 14.3587 | 0 | 41.085 | 97% | 0 | 20.2085 | 57.67% | 0 | 45.4523
5802 | 48 | 71 | 55 | 3.5 | 28.4 | 0 | 9.8639 | 0 | 0 | 65.3394 | 24.0753 | 0 | 63.8488 | 92% | 0 | 25 | 17.67% | 0 | 46.15
5803 | 11 | 12 | 11 | 4.4 | 26.8 | 0 | 0.54342 | 0 | 0 | 105.571 | 41.3048 | 0 | 110.3773 | 84% | 0 | 4.7915 | 10% | 0 | 43.1818
5804 | 0 | 0 | 0 | 3.3 | 25.5 | 0 | 0 | 0 | 0 | 108.1685 | 42.6833 | 0 | 109.9706 | 76% | 0 | 0 | 10% | 0 | 40.3885
5805 | 0 | 0 | 0 | 2.8 | 24 | 0 | 0 | 0 | 0 | 101.8387 | 40.2272 | 0 | 101.6349 | 68% | 0 | 0 | 10% | 0 | 38.1318
5806 | 0 | 0 | 0 | 1.9 | 22.9 | 0 | 0 | 0 | 0 | 96.0548 | 37.9321 | 0 | 94.6737 | 61% | 0 | 0 | 10% | 0 | 35.8755
5807 | 0 | 0 | 0 | 1.8 | 22.5 | 0 | 0 | 0 | 0 | 92.2409 | 36.3744 | 0 | 90.209 | 54% | 0 | 0 | 10% | 0 | 34.2943
5808 | 0 | 0 | 0 | 1.3 | 22.4 | 0 | 0 | 0 | 0 | 90.1166 | 35.4893 | 0 | 87.7815 | 48% | 0 | 0 | 10% | 0 | 33.3628
5809 | 0 | 0 | 0 | 1.3 | 22.3 | 0 | 0 | 0 | 0 | 88.4397 | 34.7948 | 0 | 85.928 | 41% | 0 | 0 | 10% | 0 | 32.618
5810 | 0 | 0 | 0 | 1 | 21.6 | 0 | 0 | 0 | 0 | 86.9143 | 34.216 | 0 | 84.2656 | 35% | 0 | 0 | 10% | 0 | 31.9898
5811 | 0 | 0 | 0 | 1.4 | 21.2 | 0 | 0 | 0 | 0 | 87.3591 | 34.4353 | 0 | 84.9438 | 28% | 0 | 0 | 10% | 0 | 32.159
5812 | 0 | 0 | 0 | 1.8 | 21.9 | 0 | 0 | 0 | 0 | 89.49 | 35.2717 | 0 | 87.6211 | 22% | 0 | 0 | 10% | 0 | 32.9534
5813 | 0 | 0 | 0 | 1.1 | 20.9 | 0 | 0 | 0 | 0 | 92.2056 | 36.4992 | 0 | 91.007 | 15% | 0 | 0 | 10% | 0 | 34.1541
5814 | 15 | 5 | 5 | 0.8 | 20.3 | 0 | 0 | 0 | 0 | 99.8408 | 39.735 | 0 | 100.1353 | 7% | 0 | 0 | 10% | 0 | 37.3703
5815 | 246 | 104 | 57 | 0.4 | 22.2 | 0 | 44.3784 | 0 | 0 | 96.7628 | 38.4726 | 0 | 98.1583 | 0% | 0 | 0 | 10% | 0 | 36.1364
5816 | 522 | 292 | 98 | 0.8 | 24.3 | 84.0421 | 20.424 | 14.1184 | 0 | 0 | 0 | 81.1317 | 0 | 6% | 0 | 0 | 10% | 0 | 12.6643
5817 | 627 | 491 | 143 | 1 | 26.4 | 150.0954 | 0 | 33.4291 | 0 | 0 | 0 | 148.0707 | 0 | 17% | 0 | 0 | 10% | 0 | 31.6913
5818 | 723 | 667 | 158 | 1.1 | 28.7 | 190.1456 | 0 | 51.9762 | 0 | 0 | 0 | 188.492 | 0 | 32% | 6.8591 | 0 | 19.33% | 0 | 43.0008
5819 | 792 | 791 | 145 | 1.5 | 30.2 | 217.5555 | 0 | 64.3257 | 0 | 0 | 0 | 216.1138 | 0 | 48% | 19.3564 | 0 | 45.65% | 0 | 42.5741
5820 | 823 | 876 | 154 | 3 | 31.6 | 231.1571 | 0 | 70.3538 | 2.3543 | 0 | 0 | 229.8623 | 0 | 65% | 25 | 0 | 79.65% | 0 | 42.7954
5821 | 812 | 924 | 205 | 5.3 | 31.7 | 226.5818 | 0 | 51.9394 | 22.521 | 0 | 0 | 225.4138 | 0 | 82% | 7.6081 | 0 | 90% | 0 | 41.7673
5822 | 715 | 862 | 257 | 6.2 | 31.7 | 193.3518 | 0 | 43.4601 | 26.5141 | 0 | 0 | 192.3659 | 0 | 96% | 0 | 0 | 90% | 0 | 41.1853
5823 | 590 | 649 | 212 | 5.8 | 30.8 | 46.9193 | 117.3105 | 41.8714 | 8.0225 | 0 | 0 | 46.6457 | 0 | 100% | 0 | 0 | 90% | 0 | 40.6892
5824 | 691 | 585 | 165 | 6.1 | 31.3 | 41.0239 | 153.5695 | 41.2088 | 0.78886 | 42.5936 | 0.028024 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.343
5825 | 575 | 395 | 147 | 4.5 | 31 | 42.157 | 98.9492 | 22.7729 | 0 | 42.5913 | 14.2379 | 0 | 0 | 100% | 0 | 3.1455 | 84.97% | 0 | 40.8654
5826 | 184 | 119 | 64 | 4.5 | 29 | 0 | 37.5335 | 0.84063 | 0 | 53.3608 | 18.895 | 0 | 51.8294 | 96% | 0 | 25 | 44.97% | 0 | 42.6552
5827 | 41 | 15 | 12 | 3.4 | 27.3 | 0 | 1.7054 | 0 | 0 | 58.3676 | 21.1874 | 0 | 57.5496 | 92% | 0 | 21.8545 | 10% | 0 | 40.107
5828 | 0 | 0 | 0 | 2.1 | 26.2 | 0 | 0 | 0 | 0 | 103.0091 | 40.4727 | 0 | 105.9141 | 84% | 0 | 0 | 10% | 0 | 37.6521
5829 | 0 | 0 | 0 | 1.9 | 24.9 | 0 | 0 | 0 | 0 | 96.797 | 38.0401 | 0 | 96.7643 | 77% | 0 | 0 | 10% | 0 | 35.6552
5830 | 0 | 0 | 0 | 0.5 | 23.8 | 0 | 0 | 0 | 0 | 90.9094 | 35.692 | 0 | 89.3626 | 70% | 0 | 0 | 10% | 0 | 33.3916
5831 | 0 | 0 | 0 | 0.8 | 23.1 | 0 | 0 | 0 | 0 | 86.9539 | 34.1008 | 0 | 84.6705 | 64% | 0 | 0 | 10% | 0 | 31.7763
5832 | 0 | 0 | 0 | 0.7 | 22.6 | 0 | 0 | 0 | 0 | 84.6124 | 33.1692 | 0 | 82.0709 | 58% | 0 | 0 | 10% | 0 | 30.7887
5833 | 0 | 0 | 0 | 1.1 | 22.6 | 0 | 0 | 0 | 0 | 83.1326 | 32.5546 | 0 | 80.5082 | 52% | 0 | 0 | 10% | 0 | 30.116
5834 | 0 | 0 | 0 | 0.8 | 21.8 | 0 | 0 | 0 | 0 | 82.2363 | 32.2194 | 0 | 79.7357 | 46% | 0 | 0 | 10% | 0 | 29.7274
5835 | 0 | 0 | 0 | 0.6 | 20.2 | 0 | 0 | 0 | 0 | 82.7924 | 32.5986 | 0 | 80.4169 | 40% | 0 | 0 | 10% | 0 | 30.0627
5836 | 0 | 0 | 0 | 0.8 | 20.4 | 0 | 0 | 0 | 0 | 82.7542 | 32.567 | 0 | 80.4714 | 34% | 0 | 0 | 10% | 0 | 29.9966
5837 | 0 | 0 | 0 | 1.2 | 19.4 | 0 | 0 | 0 | 0 | 83.5964 | 32.9999 | 0 | 81.5062 | 28% | 0 | 0 | 10% | 0 | 30.3999
5838 | 19 | 5 | 4 | 1.3 | 19.7 | 0 | 0 | 0 | 0 | 89.3698 | 35.3959 | 0 | 88.501 | 21% | 0 | 0 | 10% | 0 | 32.7658
5839 | 382 | 110 | 41 | 1.1 | 21.2 | 0 | 57.7612 | 0 | 0 | 95.0007 | 37.6473 | 0 | 95.372 | 14% | 0 | 0 | 10% | 0 | 35.0225
5840 | 638 | 308 | 73 | 0.9 | 25.2 | 128.9269 | 0 | 15.4968 | 0 | 61.967 | 22.9564 | 65.4101 | 0 | 19% | 0 | 0 | 10% | 0 | 36.8649
5841 | 764 | 510 | 90 | 0.8 | 28.3 | 186.6741 | 0 | 35.4973 | 0 | 46.0194 | 15.8719 | 140.9161 | 0 | 29% | 11.1884 | 0 | 25.22% | 0 | 38.0842
5842 | 834 | 683 | 100 | 1.8 | 30.1 | 221.5854 | 0 | 52.7084 | 0.97433 | 42.5628 | 14.3096 | 179.5167 | 0 | 43% | 25 | 0 | 59.22% | 0 | 39.5994
5843 | 869 | 816 | 112 | 2.9 | 31.4 | 240.025 | 0 | 51.3158 | 16.025 | 42.5808 | 14.1976 | 198.0318 | 0 | 57% | 22.6351 | 0 | 90% | 0 | 40.2706
5844 | 775 | 857 | 181 | 3.7 | 32.7 | 216.3462 | 0 | 27.6452 | 43.0753 | 42.5894 | 14.0797 | 174.4945 | 0 | 70% | 0 | 0 | 90% | 0 | 39.3134
5845 | 794 | 893 | 192 | 6.1 | 33.1 | 220.7255 | 2.98e-14 | 26.5577 | 47.2491 | 42.5936 | 14.0435 | 178.6019 | 0 | 83% | 0 | 0 | 90% | 0 | 38.4555
5846 | 467 | 657 | 255 | 6 | 32.7 | 119.6976 | 0 | 23.5591 | 27.3481 | 42.5963 | 14.082 | 77.9236 | 0 | 89% | 0 | 0 | 90% | 0 | 38.1639
5847 | 119 | 459 | 368 | 5.9 | 31.3 | 0 | 36.9369 | 25.8412 | 2.5687 | 42.5949 | 14.2115 | 0 | 41.1349 | 86% | 0 | 0 | 90% | 0 | 37.9574
5848 | 273 | 451 | 291 | 5.5 | 30.5 | 0 | 69.3353 | 26.4685 | 2.7735 | 42.5914 | 14.2831 | 0 | 41.0745 | 83% | 0 | 0 | 90% | 0 | 37.7875
5849 | 577 | 386 | 138 | 4.7 | 30.6 | 122.0241 | 0 | 22.1925 | 0 | 42.5881 | 14.273 | 77.5356 | 0 | 89% | 0 | 2.9342 | 85.3% | 0 | 39.2345
5850 | 311 | 153 | 76 | 3.7 | 29.3 | 0 | 49.9528 | 2.8576 | 0 | 46.351 | 15.9216 | 0 | 44.865 | 85% | 0 | 25 | 45.3% | 0 | 41.6764
5851 | 4 | 10 | 9 | 2.5 | 26.6 | 0 | 0.13523 | 0 | 0 | 58.5934 | 21.3516 | 0 | 57.8311 | 81% | 0 | 22.0658 | 10% | 0 | 40.4341
5852 | 0 | 0 | 0 | 1.2 | 24.6 | 0 | 0 | 0 | 0 | 103.8304 | 40.9932 | 0 | 107.345 | 73% | 0 | 0 | 10% | 0 | 38.058
5853 | 0 | 0 | 0 | 1 | 23.9 | 0 | 0 | 0 | 0 | 97.0286 | 38.2385 | 0 | 97.8043 | 66% | 0 | 0 | 10% | 0 | 35.6351
5854 | 0 | 0 | 0 | 1.1 | 23.7 | 0 | 0 | 0 | 0 | 91.6941 | 36.0318 | 0 | 90.9423 | 59% | 0 | 0 | 10% | 0 | 33.5417
5855 | 0 | 0 | 0 | 1 | 23.1 | 0 | 0 | 0 | 0 | 88.3004 | 34.664 | 0 | 86.7154 | 53% | 0 | 0 | 10% | 0 | 32.198
5856 | 0 | 0 | 0 | 1.2 | 22.5 | 0 | 0 | 0 | 0 | 86.3087 | 33.885 | 0 | 84.362 | 46% | 0 | 0 | 10% | 0 | 31.4062
5857 | 0 | 0 | 0 | 1.1 | 21.7 | 0 | 0 | 0 | 0 | 85.6961 | 33.6979 | 0 | 83.7034 | 40% | 0 | 0 | 10% | 0 | 31.1941
5858 | 0 | 0 | 0 | 1.2 | 21.4 | 0 | 0 | 0 | 0 | 87.7746 | 34.5918 | 0 | 86.2626 | 34% | 0 | 0 | 10% | 0 | 32.0606
5859 | 0 | 0 | 0 | 0.3 | 21 | 0 | 0 | 0 | 0 | 95.1542 | 37.7265 | 0 | 95.3128 | 27% | 0 | 0 | 10% | 0 | 35.175
5860 | 0 | 0 | 0 | 1.1 | 20.6 | 0 | 0 | 0 | 0 | 103.9475 | 41.4245 | 0 | 105.7455 | 19% | 0 | 0 | 10% | 0 | 38.8919
5861 | 0 | 0 | 0 | 1.8 | 21.3 | 0 | 0 | 0 | 0 | 110.2023 | 43.9486 | 0 | 112.9164 | 10% | 0 | 0 | 10% | 0 | 41.4708
5862 | 2 | 2 | 2 | 2.4 | 21.2 | 0 | 0 | 0 | 0 | 116.5247 | 46.5714 | 0 | 120.175 | 1% | 0 | 0 | 10% | 0 | 44.1574
5863 | 57 | 54 | 40 | 5.3 | 21 | 0 | 10.1978 | 0 | 0 | 16.615 | 6.6486 | 0 | 17.1689 | 0% | 0 | 0 | 10% | 0 | 4.474
5864 | 527 | 292 | 96 | 6.1 | 23.6 | 81.5337 | 20.6107 | 14.3204 | 0 | 0 | 0 | 78.6592 | 0 | 6% | 0 | 0 | 10% | 0 | 12.8915
5865 | 695 | 499 | 116 | 6.5 | 25.9 | 164.0876 | 0 | 34.9424 | 0 | 0 | 0 | 161.7714 | 0 | 18% | 0 | 0 | 10% | 0 | 33.0808
5866 | 802 | 675 | 115 | 6.1 | 27.5 | 209.0639 | 0 | 53.4682 | 0 | 0 | 0 | 207.3527 | 0 | 34% | 2.9445 | 0 | 14.01% | 0 | 48.233
5867 | 839 | 804 | 125 | 7.1 | 28.4 | 227.3312 | 0 | 66.9311 | 0 | 0 | 0 | 225.9403 | 0 | 51% | 16.7345 | 0 | 36.76% | 0 | 47.7034
5868 | 867 | 880 | 123 | 7.7 | 28.7 | 240.5319 | 0 | 74.6901 | 0 | 0 | 0 | 239.2387 | 0 | 69% | 23.7826 | 0 | 69.11% | 0 | 48.2513
5869 | 873 | 888 | 119 | 7.6 | 29 | 243.2214 | 0 | 66.3394 | 8.7606 | 0 | 0 | 242.0347 | 0 | 87% | 15.3619 | 0 | 90% | 0 | 48.2412
5870 | 863 | 838 | 115 | 8.1 | 29.2 | 172.1894 | 70.6154 | 49.8073 | 20.2173 | 0 | 0 | 171.3702 | 0 | 100% | 0 | 0 | 90% | 0 | 47.706
5871 | 847 | 732 | 105 | 7.9 | 29.4 | 41.2461 | 214.3313 | 47.1395 | 11.7046 | 42.5958 | 0.27654 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 46.6453
5872 | 780 | 570 | 100 | 6.5 | 29.6 | 42.1572 | 178.6729 | 30.6322 | 10.8179 | 42.5934 | 14.3645 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.7061
5873 | 660 | 369 | 86 | 6 | 29.3 | 42.1572 | 120.3518 | 21.106 | 0 | 42.5912 | 14.3904 | 0 | 0 | 100% | 0 | 9.5859 | 74.66% | 0 | 45.7918
5874 | 395 | 146 | 53 | 6.1 | 27.9 | 0 | 66.3823 | 2.5293 | 0 | 60.0148 | 21.8481 | 0 | 58.5604 | 96% | 0 | 25 | 34.66% | 0 | 47.2823
5875 | 22 | 10 | 8 | 4.6 | 26.1 | 0 | 0.57311 | 0 | 0 | 81.8002 | 31.2761 | 0 | 83.4019 | 90% | 0 | 15.4141 | 10% | 0 | 43.7551
5876 | 0 | 0 | 0 | 2.6 | 24.7 | 0 | 0 | 0 | 0 | 109.0048 | 43.1153 | 0 | 111.9265 | 81% | 0 | 0 | 10% | 0 | 40.591
5877 | 0 | 0 | 0 | 3.3 | 23.5 | 0 | 0 | 0 | 0 | 102.8295 | 40.6888 | 0 | 103.1069 | 73% | 0 | 0 | 10% | 0 | 38.5217
5878 | 0 | 0 | 0 | 3.5 | 22.1 | 0 | 0 | 0 | 0 | 97.5839 | 38.6381 | 0 | 96.5741 | 66% | 0 | 0 | 10% | 0 | 36.5502
5879 | 0 | 0 | 0 | 2.7 | 21.6 | 0 | 0 | 0 | 0 | 94.0654 | 37.223 | 0 | 92.4992 | 59% | 0 | 0 | 10% | 0 | 35.1284
5880 | 0 | 0 | 0 | 3.2 | 21.2 | 0 | 0 | 0 | 0 | 92.4378 | 36.5687 | 0 | 90.5954 | 52% | 0 | 0 | 10% | 0 | 34.4428
5881 | 0 | 0 | 0 | 3.7 | 21.1 | 0 | 0 | 0 | 0 | 91.6263 | 36.2349 | 0 | 89.7218 | 46% | 0 | 0 | 10% | 0 | 34.0715
5882 | 0 | 0 | 0 | 1.8 | 20.8 | 0 | 0 | 0 | 0 | 92.2825 | 36.5366 | 0 | 90.6342 | 39% | 0 | 0 | 10% | 0 | 34.3365
5883 | 0 | 0 | 0 | 1.4 | 20.5 | 0 | 0 | 0 | 0 | 98.461 | 39.1406 | 0 | 98.0523 | 31% | 0 | 0 | 10% | 0 | 36.9075
5884 | 0 | 0 | 0 | 1.6 | 19.7 | 0 | 0 | 0 | 0 | 105.9278 | 42.3243 | 0 | 106.9289 | 23% | 0 | 0 | 10% | 0 | 40.0904
5885 | 0 | 0 | 0 | 1.1 | 19.6 | 0 | 0 | 0 | 0 | 111.03 | 44.4395 | 0 | 112.7217 | 15% | 0 | 0 | 10% | 0 | 42.2395
5886 | 8 | 4 | 3 | 1.2 | 19.6 | 0 | 0 | 0 | 0 | 117.7955 | 47.2386 | 0 | 120.5409 | 6% | 0 | 0 | 10% | 0 | 45.0773
5887 | 303 | 100 | 45 | 1.2 | 21.7 | 0 | 53.9813 | 0 | 0 | 71.2524 | 28.4869 | 0 | 73.2243 | 0% | 0 | 0 | 10% | 0 | 26.4739
5888 | 585 | 295 | 82 | 1.5 | 23.9 | 94.9782 | 23.0833 | 14.9754 | 0 | 0 | 0 | 91.6874 | 0 | 7% | 0 | 0 | 10% | 0 | 13.4699
5889 | 725 | 498 | 104 | 3.4 | 26.3 | 174.4822 | 0 | 35.4998 | 0 | 0 | 0 | 172.3849 | 0 | 20% | 0 | 0 | 10% | 0 | 33.527
5890 | 798 | 671 | 118 | 3.8 | 28.2 | 209.7971 | 0 | 52.3463 | 1.1192 | 0 | 0 | 208.2315 | 0 | 36% | 0 | 0 | 10% | 0 | 50.0246
5891 | 832 | 797 | 128 | 3.6 | 29.6 | 228.2128 | 0 | 66.4975 | 0 | 0 | 0 | 226.863 | 0 | 53% | 14.9975 | 0 | 30.4% | 0 | 48.972
5892 | 853 | 870 | 131 | 3 | 30.7 | 240.0764 | 0 | 73.8142 | 0 | 0 | 0 | 238.8187 | 0 | 71% | 22.3142 | 0 | 60.74% | 0 | 48.8189
5893 | 855 | 880 | 131 | 3.3 | 31.5 | 241.3019 | 0 | 73.0979 | 1.4168 | 0 | 0 | 240.1335 | 0 | 90% | 21.5119 | 0 | 90% | 0 | 48.8456
5894 | 839 | 826 | 130 | 4.8 | 31.5 | 136.4638 | 104.2782 | 51.4631 | 17.4511 | 0 | 0 | 135.8188 | 0 | 100% | 0 | 0 | 90% | 0 | 49.6806
5895 | 797 | 712 | 127 | 4.7 | 31.2 | 40.8978 | 199.497 | 48.75 | 8.147 | 42.5976 | 0.76889 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 48.4152
5896 | 718 | 549 | 122 | 6 | 30.1 | 42.1571 | 159.9751 | 31.9715 | 8.1884 | 42.5953 | 14.3206 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 47.0013
5897 | 391 | 267 | 90 | 5.4 | 28.6 | 42.1572 | 44.4361 | 12.4105 | 0 | 42.593 | 14.4533 | 0 | 0 | 100% | 0 | 19.3517 | 59.04% | 0 | 46.9252
5898 | 0 | 34 | 33 | 4 | 27 | 0 | 0 | 0 | 0 | 67.2452 | 25.0697 | 0 | 65.9572 | 95% | 0 | 25 | 19.04% | 0 | 47.9956
5899 | 0 | 6 | 6 | 2.6 | 25.6 | 0 | 0 | 0 | 0 | 106.2213 | 41.6852 | 0 | 111.2862 | 87% | 0 | 5.6483 | 10% | 0 | 44.4093
5900 | 0 | 0 | 0 | 3.1 | 24.1 | 0 | 0 | 0 | 0 | 109.3849 | 43.3364 | 0 | 110.9152 | 79% | 0 | 0 | 10% | 0 | 41.1579
5901 | 0 | 0 | 0 | 3.8 | 22.8 | 0 | 0 | 0 | 0 | 103.9478 | 41.2241 | 0 | 103.7392 | 71% | 0 | 0 | 10% | 0 | 39.2348
5902 | 0 | 0 | 0 | 3.6 | 22 | 0 | 0 | 0 | 0 | 99.0448 | 39.2542 | 0 | 97.7834 | 63% | 0 | 0 | 10% | 0 | 37.2987
5903 | 0 | 0 | 0 | 2.3 | 21.5 | 0 | 0 | 0 | 0 | 95.3852 | 37.7782 | 0 | 93.6083 | 56% | 0 | 0 | 10% | 0 | 35.7979
5904 | 0 | 0 | 0 | 2.8 | 21.4 | 0 | 0 | 0 | 0 | 93.5635 | 37.0277 | 0 | 91.6092 | 49% | 0 | 0 | 10% | 0 | 35.0045
5905 | 0 | 0 | 0 | 2.8 | 20.9 | 0 | 0 | 0 | 0 | 92.6004 | 36.6625 | 0 | 90.5688 | 42% | 0 | 0 | 10% | 0 | 34.5958
5906 | 0 | 0 | 0 | 2 | 20.6 | 0 | 0 | 0 | 0 | 93.4587 | 37.0498 | 0 | 91.7539 | 35% | 0 | 0 | 10% | 0 | 34.9405
5907 | 0 | 0 | 0 | 2.2 | 20.6 | 0 | 0 | 0 | 0 | 99.8648 | 39.7173 | 0 | 99.3735 | 28% | 0 | 0 | 10% | 0 | 37.5708
5908 | 0 | 0 | 0 | 1.4 | 20.5 | 0 | 0 | 0 | 0 | 107.4127 | 42.8685 | 0 | 108.3103 | 20% | 0 | 0 | 10% | 0 | 40.7154
5909 | 0 | 0 | 0 | 1.6 | 20.3 | 0 | 0 | 0 | 0 | 112.5067 | 44.9894 | 0 | 114.1307 | 11% | 0 | 0 | 10% | 0 | 42.8632
5910 | 3 | 3 | 3 | 1.6 | 20.1 | 0 | 0 | 0 | 0 | 118.9764 | 47.6788 | 0 | 121.6123 | 2% | 0 | 0 | 10% | 0 | 45.5857
5911 | 235 | 95 | 53 | 1.1 | 21.2 | 0 | 41.689 | 0 | 0 | 22.9657 | 9.1917 | 0 | 23.5547 | 0% | 0 | 0 | 10% | 0 | 7.3068
5912 | 497 | 287 | 107 | 2.5 | 23 | 77.8227 | 19.2061 | 14.5158 | 0 | 0 | 0 | 75.0702 | 0 | 6% | 0 | 0 | 10% | 0 | 13.1639
5913 | 641 | 483 | 137 | 2.6 | 24.5 | 152.3656 | 0 | 34.3309 | 0 | 0 | 0 | 150.1406 | 0 | 17% | 0 | 0 | 10% | 0 | 32.5571
5914 | 716 | 659 | 163 | 1.3 | 27 | 187.7463 | 0 | 52.1357 | 0.59306 | 0 | 0 | 186.1066 | 0 | 31% | 0 | 0 | 10% | 0 | 50.0185
5915 | 755 | 782 | 175 | 1.7 | 28.6 | 206.4423 | 0 | 65.7344 | 0 | 0 | 0 | 205.0435 | 0 | 47% | 14.2344 | 0 | 29.36% | 0 | 49.1812
5916 | 770 | 863 | 196 | 2.5 | 30.1 | 215.0627 | 0 | 73.7157 | 0 | 0 | 0 | 213.7863 | 0 | 63% | 22.2157 | 0 | 59.57% | 0 | 49.0664
5917 | 719 | 873 | 244 | 5.1 | 30.4 | 198.4555 | 0 | 73.7658 | 0 | 0 | 0 | 197.3564 | 0 | 78% | 22.3155 | 0 | 89.92% | 0 | 49.1392
5918 | 461 | 653 | 268 | 5.6 | 29.5 | 117.6328 | 0 | 51.0314 | 1.1514 | 0 | 0 | 116.946 | 0 | 87% | 0 | 0 | 89.92% | 0 | 49.4725
5919 | 643 | 732 | 258 | 6.2 | 29.1 | 166.0562 | 0 | 50.5885 | 7.9555 | 42.5921 | 0.33152 | 125.4463 | 0 | 97% | 0.057875 | 0 | 90% | 0 | 48.3316
5920 | 629 | 564 | 192 | 5.7 | 28.6 | 84.6007 | 81.7202 | 33.0036 | 8.4439 | 42.5932 | 14.4534 | 43.1446 | 0 | 100% | 0 | 0 | 90% | 0 | 47.0608
5921 | 122 | 165 | 108 | 4.9 | 26.6 | 0 | 31.4921 | 4.8048 | 0 | 54.1401 | 19.4711 | 0 | 52.6108 | 96% | 0 | 25 | 50% | 0 | 47.1982
5922 | 0 | 16 | 16 | 4.7 | 25.2 | 0 | 0 | 0 | 0 | 69.0503 | 26.0437 | 0 | 67.7081 | 91% | 0 | 25 | 10% | 0 | 48.1
5923 | 0 | 4 | 4 | 2.1 | 23.9 | 0 | 0 | 0 | 0 | 119.6112 | 47.5611 | 0 | 126.5747 | 82% | 0 | 0 | 10% | 0 | 44.6393
5924 | 0 | 0 | 0 | 0.4 | 23.8 | 0 | 0 | 0 | 0 | 109.7245 | 43.5073 | 0 | 111.2621 | 74% | 0 | 0 | 10% | 0 | 41.3367
5925 | 0 | 0 | 0 | 1.4 | 23.8 | 0 | 0 | 0 | 0 | 104.7347 | 41.4549 | 0 | 104.7626 | 66% | 0 | 0 | 10% | 0 | 39.4419
5926 | 0 | 0 | 0 | 1 | 22.9 | 0 | 0 | 0 | 0 | 99.2433 | 39.2542 | 0 | 98.0558 | 58% | 0 | 0 | 10% | 0 | 37.2842
5927 | 0 | 0 | 0 | 1.5 | 22.2 | 0 | 0 | 0 | 0 | 95.3269 | 37.6935 | 0 | 93.5561 | 51% | 0 | 0 | 10% | 0 | 35.7055
5928 | 0 | 0 | 0 | 1.1 | 21.4 | 0 | 0 | 0 | 0 | 93.545 | 37.0201 | 0 | 91.5871 | 44% | 0 | 0 | 10% | 0 | 34.9935
5929 | 0 | 0 | 0 | 0.8 | 21.2 | 0 | 0 | 0 | 0 | 92.7351 | 36.6949 | 0 | 90.7233 | 37% | 0 | 0 | 10% | 0 | 34.6281
5930 | 0 | 0 | 0 | 1.4 | 21.5 | 0 | 0 | 0 | 0 | 93.5494 | 37.0145 | 0 | 91.8441 | 30% | 0 | 0 | 10% | 0 | 34.9084
5931 | 0 | 0 | 0 | 1 | 21.6 | 0 | 0 | 0 | 0 | 99.6813 | 39.5558 | 0 | 99.1271 | 23% | 0 | 0 | 10% | 0 | 37.414
5932 | 0 | 0 | 0 | 1.4 | 21.8 | 0 | 0 | 0 | 0 | 107.1412 | 42.6419 | 0 | 107.9727 | 15% | 0 | 0 | 10% | 0 | 40.4907
5933 | 0 | 0 | 0 | 1.7 | 22.2 | 0 | 0 | 0 | 0 | 111.7797 | 44.516 | 0 | 113.267 | 6% | 0 | 0 | 10% | 0 | 42.3883
5934 | 0 | 2 | 1 | 1.5 | 22.4 | 0 | 0 | 0 | 0 | 76.0283 | 30.3188 | 0 | 77.582 | 0% | 0 | 0 | 10% | 0 | 28.2925
5935 | 0 | 31 | 31 | 1.4 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.888
5936 | 256 | 271 | 173 | 2 | 23.8 | 0 | 51.2827 | 12.3395 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 10.4683
5937 | 399 | 473 | 253 | 2.5 | 25.3 | 88.0298 | 0 | 31.5034 | 0 | 0 | 0 | 84.699 | 0 | 7% | 0 | 0 | 10% | 0 | 30.3196
5938 | 450 | 555 | 241 | 2.7 | 26.5 | 110.8892 | 0 | 41.8413 | 0 | 0 | 0 | 109.0704 | 0 | 15% | 0 | 0 | 10% | 0 | 40.4362
5939 | 591 | 762 | 284 | 2.8 | 27.9 | 157.3427 | 0 | 61.9248 | 0.91489 | 42.5167 | 5.5613 | 116.2348 | 0 | 24% | 19.9518 | 0 | 37.13% | 0 | 45.3569
5940 | 230 | 603 | 399 | 4.6 | 28.3 | 0 | 61.1551 | 44.9744 | 0 | 43.5345 | 14.8632 | 0 | 40.4787 | 21% | 11.2312 | 0 | 52.41% | 0 | 47.5198
5941 | 196 | 570 | 391 | 5.2 | 28.3 | 0 | 50.3205 | 41.5361 | 0 | 45.2306 | 15.5492 | 0 | 42.16 | 17% | 7.9017 | 0 | 63.15% | 0 | 47.1547
5942 | 46 | 324 | 280 | 5.1 | 27.9 | 0 | 14.6784 | 17.2741 | 0 | 42.5168 | 14.4893 | 0 | 39.6416 | 14% | 0 | 17.0312 | 35.91% | 0 | 46.7191
5943 | 1 | 122 | 120 | 5.2 | 26.6 | 0 | 0.31013 | 1.5776 | 0 | 79.7719 | 30.3671 | 0 | 78.8 | 8% | 0 | 16.1908 | 10% | 0 | 45.946
5944 | 7 | 192 | 187 | 5 | 26 | 0 | 2.0454 | 5.7216 | 0 | 105.6489 | 41.5988 | 0 | 106.5132 | 0% | 0 | 0 | 10% | 0 | 45.0964
5945 | 149 | 203 | 136 | 5 | 25.8 | 0 | 38.295 | 7.5004 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 5.4527
5946 | 77 | 105 | 90 | 4.8 | 24.9 | 0 | 15.1031 | 1.0142 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.0159
5947 | 0 | 11 | 11 | 4.8 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0128
5948 | 0 | 0 | 0 | 4.6 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9958
5949 | 0 | 0 | 0 | 3.5 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9792
5950 | 0 | 0 | 0 | 2.4 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9628
5951 | 0 | 0 | 0 | 1.2 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9467
5952 | 0 | 0 | 0 | 1 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9309
5953 | 0 | 0 | 0 | 1.7 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9155
5954 | 0 | 0 | 0 | 1.6 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9003
5955 | 0 | 0 | 0 | 1.3 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8855
5956 | 0 | 0 | 0 | 0.7 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8709
5957 | 0 | 0 | 0 | 0.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8566
5958 | 4 | 3 | 3 | 1.6 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8425
5959 | 261 | 92 | 46 | 1.7 | 20 | 0 | 45.9031 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8287
5960 | 563 | 290 | 89 | 2.4 | 22.2 | 89.6334 | 22.0706 | 15.2454 | 0 | 0 | 0 | 84.3306 | 0 | 7% | 0 | 0 | 10% | 0 | 13.7937
5961 | 546 | 423 | 133 | 4 | 24.1 | 125.9304 | 0 | 29.4597 | 0 | 0 | 0 | 122.9187 | 0 | 17% | 0 | 0 | 10% | 0 | 27.9162
5962 | 658 | 612 | 155 | 4.5 | 25.1 | 169.0735 | 0 | 48.6757 | 0 | 0 | 0 | 166.3063 | 0 | 29% | 0 | 0 | 10% | 0 | 46.7292
5963 | 800 | 818 | 179 | 4.3 | 26.6 | 218.0297 | 0 | 70.3253 | 0 | 42.4119 | 0 | 176.344 | 0 | 43% | 21.2959 | 0 | 38.96% | 0 | 46.0812
5964 | 678 | 876 | 290 | 3.2 | 27.7 | 186.9868 | 0 | 72.5825 | 1.1968 | 0 | 0 | 185.4409 | 0 | 57% | 25 | 0 | 72.96% | 0 | 45.4257
5965 | 733 | 917 | 278 | 4.7 | 28.2 | 202.8391 | 1.49e-14 | 59.972 | 15.128 | 0 | 0 | 201.2369 | 0 | 72% | 12.5276 | 0 | 90% | 0 | 45.1042
5966 | 336 | 606 | 323 | 5.2 | 28.3 | 80.4677 | 0 | 45.9384 | 0.87908 | 0 | 0 | 79.879 | 0 | 78% | 0 | 0 | 90% | 0 | 44.7455
5967 | 271 | 426 | 237 | 4.7 | 27.7 | 59.3634 | 0 | 30.38 | 0.044739 | 42.5327 | 4.0856 | 18.8592 | 0 | 80% | 0 | 10.7193 | 72.85% | 0 | 43.83
5968 | 299 | 345 | 170 | 4.4 | 28.1 | 62.7178 | 0 | 21.3555 | 0 | 42.5334 | 14.4775 | 21.6814 | 0 | 81% | 0 | 8.2323 | 59.68% | 0 | 43.0438
5969 | 293 | 215 | 103 | 5.5 | 27.2 | 0 | 61.7754 | 10.2634 | 0 | 42.5336 | 14.5557 | 0 | 40.2304 | 78% | 0 | 20.3994 | 27.04% | 0 | 43.6737
5970 | 267 | 122 | 62 | 5.6 | 25.9 | 0 | 51.9371 | 1.6218 | 0 | 90.0853 | 34.8478 | 0 | 91.6095 | 72% | 0 | 10.649 | 10% | 0 | 44.5554
5971 | 0 | 6 | 6 | 4.7 | 23.9 | 0 | 0 | 0 | 0 | 110.0835 | 43.647 | 0 | 112.6376 | 63% | 0 | 0 | 10% | 0 | 41.2484
5972 | 0 | 0 | 0 | 5.2 | 22 | 0 | 0 | 0 | 0 | 102.3674 | 40.6417 | 0 | 102.7214 | 55% | 0 | 0 | 10% | 0 | 38.4237
5973 | 0 | 0 | 0 | 4.8 | 21.5 | 0 | 0 | 0 | 0 | 98.4992 | 39.0736 | 0 | 97.8999 | 48% | 0 | 0 | 10% | 0 | 36.9098
5974 | 0 | 0 | 0 | 3.3 | 21.4 | 0 | 0 | 0 | 0 | 94.1019 | 37.2578 | 0 | 92.7148 | 41% | 0 | 0 | 10% | 0 | 35.1075
5975 | 0 | 0 | 0 | 3.6 | 21.2 | 0 | 0 | 0 | 0 | 90.4102 | 35.7175 | 0 | 88.2475 | 34% | 0 | 0 | 10% | 0 | 33.5545
5976 | 0 | 0 | 0 | 3.9 | 21.1 | 0 | 0 | 0 | 0 | 88.2153 | 34.804 | 0 | 85.719 | 28% | 0 | 0 | 10% | 0 | 32.6066
5977 | 0 | 0 | 0 | 3.1 | 21.3 | 0 | 0 | 0 | 0 | 87.3701 | 34.4339 | 0 | 84.838 | 21% | 0 | 0 | 10% | 0 | 32.1954
5978 | 0 | 0 | 0 | 4 | 21.2 | 0 | 0 | 0 | 0 | 86.5941 | 34.1181 | 0 | 84.0329 | 15% | 0 | 0 | 10% | 0 | 31.8414
5979 | 0 | 0 | 0 | 3.1 | 20.7 | 0 | 0 | 0 | 0 | 87.0798 | 34.3618 | 0 | 84.7223 | 9% | 0 | 0 | 10% | 0 | 32.0476
5980 | 0 | 0 | 0 | 3.9 | 20.3 | 0 | 0 | 0 | 0 | 89.201 | 35.2845 | 0 | 87.367 | 2% | 0 | 0 | 10% | 0 | 32.9366
5981 | 0 | 0 | 0 | 3.7 | 21 | 0 | 0 | 0 | 0 | 27.8694 | 11.0279 | 0 | 27.5025 | 0% | 0 | 0 | 10% | 0 | 8.7403
5982 | 2 | 3 | 3 | 4.1 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2364
5983 | 266 | 96 | 48 | 4.2 | 21.3 | 0 | 46.5777 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2151
5984 | 494 | 280 | 107 | 4.2 | 22.8 | 75.8703 | 18.9415 | 14.7046 | 0 | 0 | 0 | 72.8295 | 0 | 6% | 0 | 0 | 10% | 0 | 13.3142
5985 | 287 | 403 | 247 | 5.2 | 23.5 | 56.1683 | 0 | 25.7633 | 0 | 0 | 0 | 55.1929 | 0 | 10% | 0 | 0 | 10% | 0 | 24.8491
5986 | 468 | 599 | 267 | 5.9 | 24.6 | 113.6256 | 0 | 45.5458 | 0 | 0 | 0 | 111.0754 | 0 | 18% | 3.2977 | 0 | 14.49% | 0 | 40.8346
5987 | 308 | 592 | 344 | 6.6 | 25.3 | 70.2905 | 0 | 45.9385 | 0 | 0 | 0 | 69.4172 | 0 | 23% | 4.3714 | 0 | 20.43% | 0 | 40.5196
5988 | 128 | 595 | 475 | 6.6 | 25.8 | 0 | 41.3798 | 41.7641 | 0.45948 | 0 | 0 | 0 | 0 | 23% | 1.4524 | 0 | 22.41% | 0 | 39.0348
5989 | 299 | 711 | 442 | 7.3 | 26.2 | 56.5064 | 14.7063 | 56.1922 | 0.1985 | 42.4873 | 0.43144 | 22.0415 | 7.1171 | 24% | 22.105 | 0 | 52.47% | 0 | 32.7724
5990 | 240 | 609 | 405 | 7.4 | 26.1 | 0 | 63.3467 | 45.5152 | 0 | 44.223 | 15.3405 | 0 | 41.5896 | 21% | 21.5032 | 0 | 81.71% | 0 | 37.9778
5991 | 251 | 522 | 339 | 8 | 25.5 | 0 | 64.5944 | 30.7127 | 6.4584 | 44.0698 | 15.3292 | 0 | 41.4962 | 18% | 6.0938 | 0 | 90% | 0 | 37.6346
5992 | 312 | 411 | 230 | 8 | 25.2 | 62.7135 | 0 | 23.8662 | 3.3586 | 42.4696 | 14.701 | 20.2755 | 0 | 20% | 0 | 0 | 90% | 0 | 37.5727
5993 | 420 | 325 | 157 | 7.5 | 25.2 | 78.3324 | 0 | 18.3117 | 0 | 42.4858 | 14.7066 | 36.7002 | 0 | 22% | 0 | 6.7109 | 79.26% | 0 | 38.5883
5994 | 270 | 125 | 66 | 7.7 | 23.6 | 0 | 52.079 | 1.8695 | 0 | 44.0651 | 15.4789 | 0 | 41.7241 | 19% | 0 | 24.7047 | 39.73% | 0 | 40.5102
5995 | 10 | 11 | 10 | 7.8 | 22 | 0 | 0 | 0 | 0 | 59.1114 | 22.0611 | 0 | 57.8371 | 15% | 0 | 18.5843 | 10% | 0 | 38.1377
5996 | 0 | 0 | 0 | 8.6 | 21.2 | 0 | 0 | 0 | 0 | 96.7632 | 38.3798 | 0 | 97.2187 | 8% | 0 | 0 | 10% | 0 | 35.8191
5997 | 0 | 0 | 0 | 6.9 | 20.7 | 0 | 0 | 0 | 0 | 92.5051 | 36.645 | 0 | 91.9787 | 1% | 0 | 0 | 10% | 0 | 34.1239
5998 | 0 | 0 | 0 | 4.8 | 20.6 | 0 | 0 | 0 | 0 | 12.1678 | 4.8057 | 0 | 11.9463 | 0% | 0 | 0 | 10% | 0 | 2.4001
5999 | 0 | 0 | 0 | 3.8 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3692
6000 | 0 | 0 | 0 | 4 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3454
6001 | 0 | 0 | 0 | 2.2 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3222
6002 | 0 | 0 | 0 | 1.9 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2994
6003 | 0 | 0 | 0 | 0.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.277
6004 | 0 | 0 | 0 | 2.3 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.255
6005 | 0 | 0 | 0 | 2.3 | 18.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2334
6006 | 0 | 2 | 2 | 3.3 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2122
6007 | 37 | 68 | 61 | 3.6 | 19.7 | 0 | 6.4502 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1913
6008 | 208 | 234 | 168 | 5.1 | 21.9 | 0 | 50.1474 | 10.7275 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 8.5568
6009 | 4 | 236 | 231 | 5.5 | 22.5 | 0 | 1.1321 | 8.6955 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 6.5448
6010 | 89 | 434 | 363 | 5.9 | 23.5 | 0 | 27.2061 | 26.6262 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 24.4953
6011 | 473 | 741 | 352 | 6.2 | 25.1 | 98.0258 | 24.3223 | 59.3074 | 0 | 0 | 0 | 92.3814 | 0 | 7% | 20.8061 | 0 | 38.3% | 0 | 36.9363
6012 | 115 | 659 | 547 | 6.2 | 26 | 0 | 37.1714 | 47.9377 | 0 | 0 | 0 | 0 | 0 | 7% | 11.0821 | 0 | 53.37% | 0 | 35.6755
6013 | 266 | 728 | 486 | 6.4 | 26.5 | 49.2246 | 12.7812 | 56.9108 | 0 | 0 | 0 | 47.1726 | 0 | 11% | 20.483 | 0 | 81.23% | 0 | 35.2813
6014 | 158 | 500 | 363 | 6.5 | 26.2 | 0 | 50.3745 | 34.9988 | 0 | 19.4681 | 0 | 0 | 18.1737 | 9% | 6.4523 | 0 | 90% | 0 | 27.1259
6015 | 340 | 524 | 287 | 6 | 26.2 | 63.8699 | 16.1985 | 36.1237 | 3.7143 | 0 | 0 | 61.3306 | 0 | 14% | 0 | 0 | 90% | 0 | 34.8489
6016 | 692 | 544 | 145 | 5.6 | 26.9 | 167.9445 | -3.27e-15 | 36.0037 | 4.9277 | 42.2786 | 1.5941 | 124.9245 | 0 | 24% | 0 | 0 | 90% | 0 | 35.2104
6017 | 479 | 319 | 122 | 4.1 | 26.5 | 94.9071 | 0 | 17.7387 | 0 | 42.4127 | 14.5737 | 54.116 | 0 | 28% | 0 | 5.868 | 80.61% | 0 | 36.8768
6018 | 254 | 131 | 72 | 4 | 25.6 | 0 | 48.5744 | 1.8871 | 0 | 42.7924 | 14.8001 | 0 | 40.2053 | 25% | 0 | 24.193 | 41.9% | 0 | 39.5218
6019 | 1 | 6 | 6 | 4.1 | 23.5 | 0 | 0 | 0 | 0 | 55.5622 | 20.4269 | 0 | 53.7194 | 21% | 0 | 19.939 | 10% | 0 | 38.0396
6020 | 0 | 0 | 0 | 3.4 | 22 | 0 | 0 | 0 | 0 | 96.5731 | 38.2346 | 0 | 96.4401 | 13% | 0 | 0 | 10% | 0 | 35.8362
6021 | 0 | 0 | 0 | 2 | 21.1 | 0 | 0 | 0 | 0 | 91.0829 | 36.0148 | 0 | 89.7479 | 7% | 0 | 0 | 10% | 0 | 33.644
6022 | 0 | 0 | 0 | 2.4 | 20.5 | 0 | 0 | 0 | 0 | 87.7042 | 34.643 | 0 | 85.6677 | 0% | 0 | 0 | 10% | 0 | 32.2706
6023 | 0 | 0 | 0 | 1.7 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2802
6024 | 0 | 0 | 0 | 1.5 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2581
6025 | 0 | 0 | 0 | 1.4 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2365
6026 | 0 | 0 | 0 | 1.1 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2152
6027 | 0 | 0 | 0 | 0.2 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1944
6028 | 0 | 0 | 0 | 0.2 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1739
6029 | 0 | 0 | 0 | 0.5 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1539
6030 | 2 | 2 | 2 | 0.5 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1343
6031 | 232 | 93 | 53 | 0.7 | 18.7 | 0 | 40.2635 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1149
6032 | 504 | 275 | 94 | 0.6 | 22 | 78.8925 | 19.3862 | 14.1956 | 0 | 0 | 0 | 74.7769 | 0 | 6% | 0 | 0 | 10% | 0 | 12.793
6033 | 688 | 476 | 111 | 1.1 | 23.8 | 164.9424 | 0 | 35.2621 | 0 | 0 | 0 | 161.2122 | 0 | 18% | 0 | 0 | 10% | 0 | 33.3915
6034 | 799 | 661 | 118 | 1.6 | 25.5 | 211.0147 | 0 | 54.7823 | 0 | 0 | 0 | 208.4806 | 0 | 34% | 7.5293 | 0 | 20.24% | 0 | 44.9421
6035 | 836 | 802 | 142 | 1.8 | 26.9 | 230.4354 | 0 | 69.3403 | 0 | 0 | 0 | 228.5089 | 0 | 51% | 22.9967 | 0 | 51.52% | 0 | 43.8184
6036 | 562 | 833 | 351 | 3.6 | 28.3 | 151.6031 | 0 | 70.3617 | 0 | 42.522 | 0 | 110.8213 | 0 | 60% | 24.2068 | 0 | 84.44% | 0 | 43.8057
6037 | 57 | 413 | 357 | 3.7 | 27.5 | 0 | 18.4567 | 25.3724 | 0 | 42.5343 | 10.4723 | 0 | 39.967 | 57% | 0 | 9.6239 | 69.04% | 0 | 43.9693
6038 | 1 | 122 | 120 | 3.4 | 25.5 | 0 | 0.31873 | 1.609 | 0 | 53.5433 | 19.3118 | 0 | 50.7169 | 53% | 0 | 25 | 29.04% | 0 | 43.5963
6039 | 4 | 182 | 178 | 5 | 24.4 | 0 | 1.2374 | 5.1117 | 0 | 75.046 | 28.6883 | 0 | 74.6331 | 47% | 0 | 11.899 | 10% | 0 | 43.2724
6040 | 270 | 430 | 268 | 3.8 | 25.6 | 0 | 67.4382 | 27.9539 | 0 | 48.3301 | 17.0771 | 0 | 45.7099 | 44% | 0 | 0 | 10% | 0 | 42.6668
6041 | 56 | 186 | 163 | 2.1 | 26.5 | 0 | 14.1369 | 6.2596 | 0 | 102.8895 | 40.3917 | 0 | 104.2889 | 36% | 0 | 0 | 10% | 0 | 44.1791
6042 | 6 | 56 | 55 | 2.3 | 26.2 | 0 | 1.1375 | 0 | 0 | 119.6363 | 47.3098 | 0 | 124.0971 | 27% | 0 | 0 | 10% | 0 | 44.8823
6043 | 16 | 9 | 8 | 2.1 | 25.7 | 0 | 0 | 0 | 0 | 109.8921 | 43.3707 | 0 | 111.7391 | 18% | 0 | 0 | 10% | 0 | 41.0942
6044 | 0 | 0 | 0 | 3.4 | 24.1 | 0 | 0 | 0 | 0 | 100.9113 | 39.8353 | 0 | 100.8022 | 11% | 0 | 0 | 10% | 0 | 37.6336
6045 | 0 | 0 | 0 | 2.8 | 22.4 | 0 | 0 | 0 | 0 | 97.1578 | 38.4395 | 0 | 96.2968 | 3% | 0 | 0 | 10% | 0 | 36.2571
6046 | 0 | 0 | 0 | 3 | 22.1 | 0 | 0 | 0 | 0 | 45.1496 | 17.8381 | 0 | 44.3919 | 0% | 0 | 0 | 10% | 0 | 15.7196
6047 | 0 | 0 | 0 | 2.2 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0533
6048 | 0 | 0 | 0 | 1 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0356
6049 | 0 | 0 | 0 | 0.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0182
6050 | 0 | 0 | 0 | 3.8 | 22.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0009
6051 | 0 | 0 | 0 | 2.3 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9841
6052 | 0 | 0 | 0 | 2.5 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9677
6053 | 0 | 0 | 0 | 3.8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9515
6054 | 5 | 2 | 2 | 2.2 | 21.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9358
6055 | 231 | 99 | 69 | 2.8 | 21.4 | 0 | 39.9088 | 0.61904 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3012
6056 | 71 | 164 | 137 | 4.6 | 23.1 | 0 | 17.0446 | 4.7507 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 2.8458
6057 | 216 | 384 | 266 | 7.9 | 26.4 | 0 | 50.2444 | 23.362 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 21.4744
6058 | 115 | 428 | 342 | 9.6 | 27 | 0 | 35.133 | 26.3386 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 24.4635
6059 | 436 | 680 | 326 | 9.8 | 28 | 86.6598 | 22.0083 | 54.0978 | 0 | 0 | 0 | 81.6881 | 0 | 6% | 9.1485 | 0 | 22.44% | 0 | 43.5214
6060 | 878 | 883 | 138 | 8.3 | 28.4 | 242.9059 | 0 | 70.4334 | 4.6666 | 0 | 0 | 237.2734 | 0 | 25% | 25 | 0 | 56.44% | 0 | 42.8517
6061 | 833 | 884 | 172 | 8.6 | 27.1 | 229.3159 | 0 | 70.2433 | 4.8567 | 42.4186 | 0 | 187.8858 | 0 | 39% | 24.675 | 0 | 90% | 0 | 42.5245
6062 | 849 | 838 | 154 | 9.4 | 26.7 | 229.4742 | 0 | 44.8784 | 28.2793 | 0 | 0 | 227.7249 | 0 | 56% | 0 | 0 | 90% | 0 | 42.3371
6063 | 735 | 672 | 146 | 6.1 | 26.4 | 192.0083 | -1.18e-14 | 35.1609 | 20.5959 | 42.5325 | 8.8118 | 151.0392 | 0 | 68% | 0 | 0 | 90% | 0 | 41.5295
6064 | 313 | 346 | 170 | 4.7 | 25.7 | 65.4204 | 0 | 22.3157 | 0 | 42.5438 | 14.6857 | 25.1683 | 0 | 70% | 0 | 5.4145 | 81.34% | 0 | 41.3634
6065 | 572 | 314 | 101 | 4.7 | 25.9 | 115.3009 | 0 | 19.1178 | 0 | 42.5449 | 14.6696 | 73.3351 | 0 | 75% | 0 | 10.9756 | 63.78% | 0 | 43.2562
6066 | 485 | 141 | 45 | 4.9 | 25.1 | 65.9182 | 0 | 2.7707 | 0 | 49.1361 | 17.4581 | 18.5194 | 0 | 77% | 0 | 25 | 23.78% | 0 | 44.175
6067 | 36 | 9 | 6 | 2.7 | 23.4 | 0 | 0 | 0 | 0 | 85.7578 | 33.3274 | 0 | 87.2078 | 70% | 0 | 8.6099 | 10% | 0 | 40.1762
6068 | 0 | 0 | 0 | 2.5 | 22.5 | 0 | 0 | 0 | 0 | 99.2847 | 39.3095 | 0 | 100.2241 | 63% | 0 | 0 | 10% | 0 | 36.7806
6069 | 0 | 0 | 0 | 2.5 | 21.7 | 0 | 0 | 0 | 0 | 95.2009 | 37.6861 | 0 | 94.981 | 56% | 0 | 0 | 10% | 0 | 35.2639
6070 | 0 | 0 | 0 | 2.5 | 20.6 | 0 | 0 | 0 | 0 | 90.5972 | 35.8425 | 0 | 89.2199 | 49% | 0 | 0 | 10% | 0 | 33.4622
6071 | 0 | 0 | 0 | 6.4 | 19.6 | 0 | 0 | 0 | 0 | 88.1898 | 34.9068 | 0 | 86.3219 | 42% | 0 | 0 | 10% | 0 | 32.519
6072 | 0 | 0 | 0 | 7.4 | 19.1 | 0 | 0 | 0 | 0 | 86.3053 | 34.1536 | 0 | 84.1354 | 36% | 0 | 0 | 10% | 0 | 31.7432
6073 | 0 | 0 | 0 | 3.9 | 18.7 | 0 | 0 | 0 | 0 | 86.0238 | 34.0643 | 0 | 83.8892 | 30% | 0 | 0 | 10% | 0 | 31.6232
6074 | 0 | 0 | 0 | 4.9 | 17.5 | 0 | 0 | 0 | 0 | 86.2413 | 34.2385 | 0 | 84.2255 | 24% | 0 | 0 | 10% | 0 | 31.7699
6075 | 0 | 0 | 0 | 3.8 | 17.1 | 0 | 0 | 0 | 0 | 90.9344 | 36.2441 | 0 | 89.977 | 17% | 0 | 0 | 10% | 0 | 33.7457
6076 | 0 | 0 | 0 | 4 | 16.6 | 0 | 0 | 0 | 0 | 98.6214 | 39.5092 | 0 | 99.2335 | 9% | 0 | 0 | 10% | 0 | 37.0003
6077 | 0 | 0 | 0 | 2.4 | 16.1 | 0 | 0 | 0 | 0 | 101.9457 | 40.9418 | 0 | 103.0996 | 2% | 0 | 0 | 10% | 0 | 38.4607
6078 | 0 | 1 | 1 | 1.7 | 16.2 | 0 | 0 | 0 | 0 | 21.4151 | 8.6126 | 0 | 21.7718 | 0% | 0 | 0 | 10% | 0 | 6.2908
6079 | 24 | 52 | 47 | 2.5 | 16.8 | 0 | 4.1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2719
6080 | 47 | 125 | 111 | 2.5 | 17.8 | 0 | 11.2586 | 2.6691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.41913
6081 | 0 | 129 | 128 | 2.7 | 18.8 | 0 | 0 | 2.0621 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.16622
6082 | 0 | 92 | 91 | 1.7 | 18.9 | 0 | 0 | 0.17666 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0306
6083 | 0 | 123 | 121 | 3.2 | 18.9 | 0 | 0 | 1.678 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.5085
6084 | 0 | 133 | 132 | 3.1 | 18.8 | 0 | 0 | 2.287 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.12072
6085 | 0 | 177 | 175 | 1.7 | 19.6 | 0 | 0 | 4.8262 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 2.68
6086 | 0 | 195 | 193 | 2.9 | 20.8 | 0 | 0 | 5.9415 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.8149
6087 | 16 | 183 | 169 | 5.2 | 21.3 | 0 | 4.9402 | 5.2922 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.1847
6088 | 109 | 240 | 176 | 6.4 | 20.9 | 0 | 31.4458 | 11.7298 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.6411
6089 | 430 | 281 | 102 | 6.7 | 20.4 | 64.8063 | 16.8658 | 14.8718 | 0 | 0 | 0 | 61.3084 | 0 | 5% | 0 | 0 | 10% | 0 | 13.5942
6090 | 0 | 23 | 23 | 3.4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.1313
6091 | 0 | 1 | 1 | 2.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -2.0508
6092 | 0 | 0 | 0 | 3.5 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -2.0323
6093 | 0 | 0 | 0 | 5.3 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -2.0141
6094 | 0 | 0 | 0 | 5 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.9963
6095 | 0 | 0 | 0 | 5.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.9789
6096 | 0 | 0 | 0 | 4.4 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.9617
6097 | 0 | 0 | 0 | 4.2 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.945
6098 | 0 | 0 | 0 | 3.6 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.9286
6099 | 0 | 0 | 0 | 5 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.9127
6100 | 0 | 0 | 0 | 3.6 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.8969
6101 | 0 | 0 | 0 | 1.9 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.8815
6102 | 0 | 1 | 1 | 2.5 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.8664
6103 | 1 | 40 | 40 | 2.3 | 15.7 | 0 | 0.17117 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.8515
6104 | 1 | 49 | 48 | 2.3 | 16.1 | 0 | 0.23902 | 0 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | -1.837
6105 | 15 | 137 | 123 | 2.2 | 15.5 | 0 | 4.2306 | 2.3799 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | 0.55712
6106 | 343 | 565 | 307 | 1.6 | 18.3 | 65.4882 | 16.5388 | 41.8266 | 0 | 0 | 0 | 61.7241 | 0 | 10% | 0 | 0 | 10% | 0 | 40.5788
6107 | 85 | 374 | 302 | 4.7 | 20.4 | 0 | 26.9488 | 22.7825 | 0 | 0 | 0 | 0 | 0 | 10% | 0 | 0 | 10% | 0 | 21.9143
6108 | 529 | 798 | 348 | 5.3 | 22.4 | 114.4166 | 28.3163 | 68.8359 | 0 | 0 | 0 | 108.7994 | 0 | 18% | 24.8348 | 0 | 43.77% | 0 | 42.3274
6109 | 335 | 650 | 361 | 6 | 22.9 | 80.7339 | 0 | 53.6024 | 0 | 42.0968 | 0 | 40.1999 | 0 | 21% | 24.9284 | 0 | 77.68% | 0 | 26.9899
6110 | 186 | 492 | 335 | 6.4 | 22.7 | 0 | 45.8781 | 35.3668 | 0 | 42.9007 | 6.0009 | 0 | 39.7541 | 18% | 6.8057 | 0 | 86.93% | 0 | 33.245
6111 | 2 | 159 | 156 | 5.4 | 21.8 | 0 | 0.61692 | 3.7172 | 0 | 42.8456 | 15.1299 | 0 | 39.7632 | 15% | 0 | 25 | 46.93% | 0 | 41.8867
6112 | 1 | 156 | 154 | 5.4 | 21 | 0 | 0.28786 | 3.5709 | 0 | 47.5334 | 17.196 | 0 | 44.7453 | 12% | 0 | 23.0836 | 10% | 0 | 41.8284
6113 | 1 | 83 | 82 | 4 | 20.3 | 0 | 0.24893 | 0 | 0 | 114.076 | 45.654 | 0 | 116.3516 | 3% | 0 | 0 | 10% | 0 | 43.4832
6114 | 0 | 22 | 22 | 2.8 | 19.8 | 0 | 0 | 0 | 0 | 35.141 | 14.0793 | 0 | 35.782 | 0% | 0 | 0 | 10% | 0 | 12.0877
6115 | 0 | 0 | 0 | 2.1 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.925
6116 | 0 | 0 | 0 | 2.9 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9097
6117 | 0 | 0 | 0 | 1.4 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8947
6118 | 0 | 0 | 0 | 2.8 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8801
6119 | 0 | 0 | 0 | 2.5 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8657
6120 | 0 | 0 | 0 | 3.7 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8516
6121 | 0 | 0 | 0 | 3.3 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8377
6122 | 0 | 0 | 0 | 2.1 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8241
6123 | 0 | 0 | 0 | 3.2 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8107
6124 | 0 | 0 | 0 | 3.4 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7976
6125 | 0 | 0 | 0 | 3.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7848
6126 | 0 | 0 | 0 | 1.9 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7722
6127 | 16 | 37 | 33 | 1.9 | 15 | 0 | 2.7259 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7598
6128 | 118 | 166 | 112 | 1.3 | 16.4 | 0 | 28.1417 | 4.8438 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.0962
6129 | 341 | 379 | 188 | 1.4 | 19 | 58.9955 | 14.9198 | 24.6757 | 0 | 0 | 0 | 54.9311 | 0 | 4% | 0 | 0 | 10% | 0 | 23.4996
6130 | 693 | 664 | 201 | 3 | 21.5 | 179.665 | -2.98e-14 | 56.2013 | 0 | 0 | 0 | 173.1026 | 0 | 18% | 10.8088 | 0 | 24.7% | 0 | 43.3774
6131 | 638 | 717 | 223 | 6.6 | 23.2 | 168.1295 | 0 | 62.3158 | 0 | 42.2534 | 0 | 126.6595 | 0 | 28% | 22.4502 | 0 | 55.23% | 0 | 37.3856
6132 | 62 | 441 | 383 | 6.4 | 23 | 0 | 20.0245 | 28.079 | 0.64123 | 42.3884 | 8.692 | 0 | 39.2174 | 25% | 0 | 5.5883 | 46.29% | 0 | 41.195
6133 | 14 | 114 | 102 | 7.1 | 21 | 0 | 4.5276 | 2.2709 | 0 | 49.0308 | 17.8173 | 0 | 46.1176 | 21% | 0 | 22.6818 | 10% | 0 | 40.8362
6134 | 85 | 360 | 287 | 5.9 | 21.1 | 0 | 27.0608 | 21.6248 | 0 | 56.8837 | 21.1408 | 0 | 53.2794 | 17% | 0 | 0 | 10% | 0 | 40.7749
6135 | 122 | 385 | 296 | 5.6 | 22 | 0 | 37.5952 | 24.8638 | 0 | 48.6037 | 17.4995 | 0 | 45.4001 | 14% | 0 | 0 | 10% | 0 | 40.3202
6136 | 72 | 319 | 276 | 6.1 | 22.8 | 0 | 20.6797 | 17.1966 | 0 | 66.9478 | 25.3561 | 0 | 63.4742 | 9% | 0 | 0 | 10% | 0 | 40.4317
6137 | 6 | 122 | 118 | 5.3 | 22.6 | 0 | 1.4865 | 1.6751 | 0 | 107.2232 | 42.6087 | 0 | 108.5041 | 1% | 0 | 0 | 10% | 0 | 42.0382
6138 | 10 | 51 | 50 | 5.2 | 22.1 | 0 | 1.8285 | 0 | 0 | 7.2128 | 2.8744 | 0 | 7.3466 | 0% | 0 | 0 | 10% | 0 | 0.81001
6139 | 0 | 4 | 4 | 5.5 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0372
6140 | 0 | 0 | 0 | 3.3 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0197
6141 | 0 | 0 | 0 | 4.4 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0026
6142 | 0 | 0 | 0 | 4.2 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9859
6143 | 0 | 0 | 0 | 2.9 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9695
6144 | 0 | 0 | 0 | 4.1 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9535
6145 | 0 | 0 | 0 | 3.2 | 17.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9376
6146 | 0 | 0 | 0 | 3.4 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9221
6147 | 0 | 0 | 0 | 3.1 | 17.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9068
6148 | 0 | 0 | 0 | 3.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8919
6149 | 0 | 0 | 0 | 3.4 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8772
6150 | 0 | 1 | 1 | 3.5 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8628
6151 | 0 | 31 | 31 | 4 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8486
6152 | 0 | 57 | 57 | 5.2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8347
6153 | 0 | 116 | 116 | 3.7 | 19.5 | 0 | 0 | 1.4125 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.40862
6154 | 0 | 187 | 186 | 4.2 | 21.5 | 0 | 0 | 5.4943 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.6866
6155 | 8 | 322 | 312 | 5.8 | 22.6 | 0 | 2.5363 | 15.105 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 13.3105
6156 | 26 | 382 | 355 | 4.9 | 23 | 0 | 8.396 | 20.0433 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 18.2616
6157 | 310 | 693 | 423 | 5.8 | 24.3 | 59.8476 | 15.411 | 56.6004 | 0 | 0 | 0 | 55.51 | 0 | 4% | 20.0213 | 0 | 37.23% | 0 | 35.3944
6158 | 342 | 673 | 395 | 6.6 | 24.9 | 80.668 | 0 | 54.3851 | 0 | 0 | 0 | 77.5875 | 0 | 11% | 18.2435 | 0 | 62.04% | 0 | 35.0045
6159 | 351 | 580 | 336 | 6.3 | 24.6 | 80.1651 | 0 | 45.118 | 0 | 0 | 0 | 77.9504 | 0 | 17% | 9.1414 | 0 | 74.47% | 0 | 34.8379
6160 | 456 | 468 | 215 | 6 | 24.7 | 101.5776 | 0 | 33.8642 | 0 | 42.1876 | 0 | 60.2956 | 0 | 21% | 11.4173 | 0.2852 | 89.54% | 0 | 20.8643
6161 | 343 | 276 | 150 | 5.1 | 24.7 | 59.4836 | 0 | 15.0932 | 0 | 42.3081 | 6.963 | 19.0592 | 0 | 23% | 0 | 16.6669 | 62.88% | 0 | 37.4716
6162 | 125 | 97 | 71 | 5.9 | 23.5 | 0 | 22.6431 | 0.56226 | 0 | 42.8578 | 15.0013 | 0 | 39.805 | 20% | 0 | 24.5033 | 23.67% | 0 | 39.0118
6163 | 1 | 4 | 4 | 4.8 | 22.2 | 0 | 0 | 0 | 0 | 77.5794 | 30.0397 | 0 | 75.8953 | 14% | 0 | 8.5445 | 10% | 0 | 36.5059
6164 | 0 | 0 | 0 | 4.7 | 21.1 | 0 | 0 | 0 | 0 | 91.8345 | 36.338 | 0 | 89.8214 | 7% | 0 | 0 | 10% | 0 | 34.2292
6165 | 0 | 0 | 0 | 4.2 | 21.9 | 0 | 0 | 0 | 0 | 87.3934 | 34.4055 | 0 | 84.5466 | 1% | 0 | 0 | 10% | 0 | 32.278
6166 | 0 | 0 | 0 | 3.2 | 22.3 | 0 | 0 | 0 | 0 | 7.3042 | 2.8635 | 0 | 6.996 | 0% | 0 | 0 | 10% | 0 | 0.79462
6167 | 0 | 0 | 0 | 2.9 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0438
6168 | 0 | 0 | 0 | 2.2 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0264
6169 | 0 | 0 | 0 | 0.8 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0091
6170 | 0 | 0 | 0 | 0.6 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9922
6171 | 0 | 0 | 0 | 0.9 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9757
6172 | 0 | 0 | 0 | 0.5 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9594
6173 | 0 | 0 | 0 | 0.5 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9434
6174 | 0 | 1 | 1 | 1.7 | 19.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9278
6175 | 76 | 65 | 52 | 1.7 | 20.4 | 0 | 12.8247 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9124
6176 | 348 | 244 | 126 | 1.1 | 22.3 | 49.074 | 12.324 | 12.4007 | 0 | 0 | 0 | 46.2788 | 0 | 4% | 0 | 0 | 10% | 0 | 11.2866
6177 | 520 | 444 | 172 | 2.9 | 24.5 | 118.829 | 0 | 32.4566 | 0 | 0 | 0 | 114.7561 | 0 | 12% | 0 | 0 | 10% | 0 | 30.9918
6178 | 634 | 618 | 192 | 4.3 | 26 | 161.8696 | 0 | 50.832 | 0 | 42.2685 | 0 | 119.846 | 0 | 22% | 18.0392 | 0 | 34.53% | 0 | 30.3903
6179 | 702 | 744 | 199 | 4.2 | 26.8 | 189.3109 | 0 | 52.5127 | 12.5314 | 42.4399 | 11.1095 | 147.891 | 0 | 33% | 25 | 0 | 68.53% | 0 | 36.3394
6180 | 734 | 816 | 200 | 4.5 | 27.6 | 202.5262 | 0 | 38.3418 | 34.1894 | 42.5018 | 14.5102 | 161.1665 | 0 | 45% | 15.7843 | 0 | 90% | 0 | 34.7695
6181 | 718 | 821 | 215 | 4.5 | 27.9 | 198.0132 | 0 | 21.674 | 50.9849 | 42.5279 | 14.4931 | 156.7393 | 0 | 57% | 0 | 0 | 90% | 0 | 33.9002
6182 | 661 | 748 | 222 | 5.7 | 27.7 | 176.6797 | 0 | 20.9874 | 43.3597 | 42.5474 | 14.5171 | 135.4359 | 0 | 67% | 0 | 0 | 90% | 0 | 33.4261
6183 | 653 | 644 | 193 | 5.7 | 27.5 | 167.9351 | 0 | 20.8359 | 32.6746 | 42.5579 | 14.538 | 126.4808 | 0 | 77% | 0 | 0 | 90% | 0 | 33.3735
6184 | 560 | 477 | 170 | 6 | 27.1 | 129.5597 | 0 | 20.9975 | 14.8377 | 42.5647 | 14.575 | 88.1139 | 0 | 83% | 0 | 0 | 90% | 0 | 33.9304
6185 | 394 | 274 | 131 | 5.6 | 26.2 | 70.5058 | 0 | 15.3234 | 0 | 42.5678 | 14.6524 | 29.0903 | 0 | 85% | 0 | 7.8195 | 77.49% | 0 | 36.7094
6186 | 104 | 83 | 59 | 4.9 | 24.9 | 0 | 18.6614 | 0 | 0 | 45.3693 | 15.9091 | 0 | 43.8203 | 82% | 0 | 24.7996 | 37.81% | 0 | 38.662
6187 | 0 | 3 | 3 | 3.8 | 23.5 | 0 | 0 | 0 | 0 | 60.2794 | 22.4653 | 0 | 60.1177 | 78% | 0 | 17.3809 | 10% | 0 | 36.8914
6188 | 0 | 0 | 0 | 3.1 | 22.7 | 0 | 0 | 0 | 0 | 94.7601 | 37.4143 | 0 | 96.0807 | 71% | 0 | 0 | 10% | 0 | 34.5456
6189 | 0 | 0 | 0 | 2.1 | 22.1 | 0 | 0 | 0 | 0 | 88.9378 | 35.0205 | 0 | 88.2575 | 64% | 0 | 0 | 10% | 0 | 32.3277
6190 | 0 | 0 | 0 | 1.9 | 21.2 | 0 | 0 | 0 | 0 | 84.7441 | 33.3417 | 0 | 83.0677 | 58% | 0 | 0 | 10% | 0 | 30.6904
6191 | 0 | 0 | 0 | 1 | 21.2 | 0 | 0 | 0 | 0 | 82.1466 | 32.2277 | 0 | 80.1577 | 52% | 0 | 0 | 10% | 0 | 29.5676
6192 | 0 | 0 | 0 | 1.3 | 20.9 | 0 | 0 | 0 | 0 | 81.3472 | 31.8883 | 0 | 79.4007 | 46% | 0 | 0 | 10% | 0 | 29.2069
6193 | 0 | 0 | 0 | 1.6 | 20.9 | 0 | 0 | 0 | 0 | 81.7516 | 32.073 | 0 | 79.8555 | 40% | 0 | 0 | 10% | 0 | 29.3731
6194 | 0 | 0 | 0 | 0.7 | 21 | 0 | 0 | 0 | 0 | 83.6626 | 32.9086 | 0 | 81.9549 | 34% | 0 | 0 | 10% | 0 | 30.1916
6195 | 0 | 0 | 0 | 0.8 | 20.5 | 0 | 0 | 0 | 0 | 91.6496 | 36.2953 | 0 | 91.6844 | 27% | 0 | 0 | 10% | 0 | 33.5575
6196 | 0 | 0 | 0 | 1.1 | 20 | 0 | 0 | 0 | 0 | 102.9309 | 41.0504 | 0 | 105.2582 | 19% | 0 | 0 | 10% | 0 | 38.33
6197 | 0 | 0 | 0 | 0.9 | 19.4 | 0 | 0 | 0 | 0 | 108.5246 | 43.4221 | 0 | 111.6514 | 11% | 0 | 0 | 10% | 0 | 40.7749
6198 | 0 | 1 | 1 | 1.1 | 18.7 | 0 | 0 | 0 | 0 | 112.851 | 45.273 | 0 | 116.4477 | 2% | 0 | 0 | 10% | 0 | 42.707
6199 | 155 | 71 | 43 | 1.3 | 19.1 | 0 | 26.0287 | 0 | 0 | 31.2814 | 12.5532 | 0 | 32.3398 | 0% | 0 | 0 | 10% | 0 | 10.2092
6200 | 532 | 266 | 88 | 2 | 21.8 | 81.9871 | 20.2437 | 15.1599 | 0 | 0 | 0 | 79.0888 | 0 | 6% | 0 | 0 | 10% | 0 | 13.7033
6201 | 728 | 475 | 103 | 1.7 | 23.6 | 174.0935 | -2.98e-14 | 37.5025 | 0 | 0 | 0 | 171.6304 | 0 | 19% | 0 | 0 | 10% | 0 | 35.5618
6202 | 815 | 651 | 113 | 1.9 | 25.6 | 214.9759 | 0 | 56.2357 | 0 | 0 | 0 | 213.2961 | 0 | 35% | 8.8952 | 0 | 22.1% | 0 | 45.006
6203 | 540 | 607 | 195 | 1.8 | 26.4 | 142.9533 | -2.98e-14 | 51.7486 | 0 | 0 | 0 | 142.1008 | 0 | 46% | 5.5571 | 0 | 29.65% | 0 | 44.4741
6204 | 825 | 873 | 189 | 4.3 | 26.8 | 230.0765 | -2.98e-14 | 71.7155 | 3.3845 | 0 | 0 | 228.2043 | 0 | 63% | 25 | 0 | 63.65% | 0 | 44.1873
6205 | 833 | 850 | 156 | 5.2 | 26.5 | 231.9646 | 0 | 66.0181 | 9.0819 | 0 | 0 | 230.7514 | 0 | 80% | 19.3713 | 0 | 90% | 0 | 44.0488
6206 | 806 | 788 | 157 | 4.6 | 26.9 | 220.5201 | -2.98e-14 | 46.6212 | 23.3464 | 0 | 0 | 219.4034 | 0 | 96% | 0 | 0 | 90% | 0 | 44.0994
6207 | 753 | 709 | 194 | 4.1 | 27 | 49.2572 | 163.8709 | 44.7067 | 16.0483 | 0 | 0 | 49.0002 | 0 | 100% | 0 | 0 | 90% | 0 | 43.3385
6208 | 612 | 602 | 270 | 3 | 27.2 | 41.1103 | 125.1546 | 43.6944 | 1.9302 | 42.5917 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.8655
6209 | 401 | 359 | 211 | 3.5 | 26.2 | 42.1587 | 41.6901 | 21.2168 | 0 | 42.5894 | 14.0141 | 0 | 0 | 100% | 0 | 8.9982 | 75.6% | 0 | 44.9172
6210 | 134 | 111 | 85 | 3.3 | 24.5 | 0 | 23.8148 | 1.3629 | 0 | 56.1141 | 20.5058 | 0 | 54.604 | 96% | 0 | 25 | 35.6% | 0 | 44.7938
6211 | 0 | 2 | 2 | 2.5 | 22.8 | 0 | 0 | 0 | 0 | 71.6548 | 27.2962 | 0 | 72.3146 | 91% | 0 | 16.0018 | 10% | 0 | 40.3591
6212 | 0 | 0 | 0 | 1.4 | 22.1 | 0 | 0 | 0 | 0 | 100.2362 | 39.7406 | 0 | 101.7663 | 83% | 0 | 0 | 10% | 0 | 37.1176
6213 | 0 | 0 | 0 | 0.5 | 21.5 | 0 | 0 | 0 | 0 | 95.3918 | 37.7807 | 0 | 94.9938 | 76% | 0 | 0 | 10% | 0 | 35.4285
6214 | 0 | 0 | 0 | 0.3 | 21.1 | 0 | 0 | 0 | 0 | 91.347 | 36.1163 | 0 | 89.8906 | 69% | 0 | 0 | 10% | 0 | 33.8171
6215 | 0 | 0 | 0 | 0.8 | 20.8 | 0 | 0 | 0 | 0 | 88.5229 | 34.9529 | 0 | 86.5248 | 63% | 0 | 0 | 10% | 0 | 32.6338
6216 | 0 | 0 | 0 | 1.4 | 20.1 | 0 | 0 | 0 | 0 | 87.1333 | 34.425 | 0 | 84.9903 | 56% | 0 | 0 | 10% | 0 | 32.0631
6217 | 0 | 0 | 0 | 1.1 | 20.1 | 0 | 0 | 0 | 0 | 87.0877 | 34.4062 | 0 | 85.0632 | 50% | 0 | 0 | 10% | 0 | 32.0012
6218 | 0 | 0 | 0 | 1.1 | 19.9 | 0 | 0 | 0 | 0 | 88.5894 | 35.0515 | 0 | 86.965 | 44% | 0 | 0 | 10% | 0 | 32.6116
6219 | 0 | 0 | 0 | 0.5 | 19.6 | 0 | 0 | 0 | 0 | 95.462 | 37.9645 | 0 | 95.3909 | 36% | 0 | 0 | 10% | 0 | 35.4986
6220 | 0 | 0 | 0 | 1.2 | 19.8 | 0 | 0 | 0 | 0 | 105.9926 | 42.3427 | 0 | 107.9063 | 28% | 0 | 0 | 10% | 0 | 39.8904
6221 | 0 | 0 | 0 | 1.4 | 20 | 0 | 0 | 0 | 0 | 110.4933 | 44.1833 | 0 | 112.8931 | 20% | 0 | 0 | 10% | 0 | 41.799
6222 | 0 | 0 | 0 | 1.8 | 19.6 | 0 | 0 | 0 | 0 | 113.4169 | 45.428 | 0 | 116.0319 | 11% | 0 | 0 | 10% | 0 | 43.1142
6223 | 123 | 79 | 55 | 1.2 | 19.9 | 0 | 20.5538 | 0 | 0 | 115.6341 | 46.3216 | 0 | 118.3611 | 2% | 0 | 0 | 10% | 0 | 44.074
6224 | 152 | 171 | 126 | 1.4 | 21.8 | 0 | 35.921 | 6.704 | 0 | 28.8275 | 11.4511 | 0 | 28.8169 | 0% | 0 | 0 | 10% | 0 | 16.1012
6225 | 57 | 185 | 152 | 2.3 | 22.2 | 0 | 16.0014 | 6.7155 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.7145
6226 | 0 | 109 | 108 | 2 | 23.3 | 0 | 0 | 0.95811 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.026
6227 | 54 | 280 | 236 | 3.8 | 24 | 0 | 17.1197 | 14.7011 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 12.7335
6228 | 231 | 407 | 212 | 4 | 24 | 0 | 63.73 | 30.6759 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 28.7267
6229 | 819 | 908 | 231 | 4.1 | 25.8 | 228.2137 | 0 | 72.4104 | 2.6896 | 0 | 0 | 218.6089 | 0 | 17% | 25 | 0 | 44% | 0 | 45.0194
6230 | 438 | 597 | 256 | 3.5 | 26.7 | 112.0412 | 0 | 50.2205 | 0 | 0 | 0 | 111.1391 | 0 | 25% | 4.1839 | 0 | 49.69% | 0 | 44.6056
6231 | 721 | 658 | 170 | 3.1 | 27.5 | 188.9719 | -2.65e-14 | 56.4569 | 0.0040241 | 42.5243 | 1.6153 | 147.3706 | 0 | 36% | 16.1899 | 0 | 71.71% | 0 | 39.2749
6232 | 598 | 460 | 139 | 2.4 | 27.9 | 141.6391 | -2.98e-14 | 34.8017 | 0 | 44.6452 | 15.3461 | 98.963 | 0 | 44% | 4.9701 | 0 | 78.47% | 0 | 43.4313
6233 | 272 | 213 | 112 | 2.4 | 27.4 | 0 | 52.8841 | 9.9227 | 0 | 42.5605 | 14.5476 | 0 | 39.8361 | 41% | 0 | 22.1923 | 42.96% | 0 | 45.3909
6234 | 92 | 68 | 53 | 4 | 25.1 | 0 | 16.1923 | 0 | 0 | 71.3295 | 26.9288 | 0 | 69.4907 | 36% | 0 | 20.6 | 10% | 0 | 45.2722
6235 | 1 | 2 | 2 | 3.9 | 23.3 | 0 | 0 | 0 | 0 | 109.1794 | 43.3353 | 0 | 111.1132 | 27% | 0 | 0 | 10% | 0 | 41.01
6236 | 0 | 0 | 0 | 3.3 | 22.1 | 0 | 0 | 0 | 0 | 100.5185 | 39.8605 | 0 | 100.4824 | 20% | 0 | 0 | 10% | 0 | 37.6201
6237 | 0 | 0 | 0 | 1.6 | 21.3 | 0 | 0 | 0 | 0 | 95.7175 | 37.9352 | 0 | 94.7354 | 13% | 0 | 0 | 10% | 0 | 35.7203
6238 | 0 | 0 | 0 | 1.7 | 20.4 | 0 | 0 | 0 | 0 | 91.2316 | 36.1276 | 0 | 89.3395 | 6% | 0 | 0 | 10% | 0 | 33.9163
6239 | 0 | 0 | 0 | 1.6 | 20.3 | 0 | 0 | 0 | 0 | 79.9291 | 31.5929 | 0 | 77.7119 | 0% | 0 | 0 | 10% | 0 | 29.3729
6240 | 0 | 0 | 0 | 1.5 | 20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1409
6241 | 0 | 0 | 0 | 1.1 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1215
6242 | 0 | 0 | 0 | 1 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1025
6243 | 0 | 0 | 0 | 0.7 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0839
6244 | 0 | 0 | 0 | 0.7 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0655
6245 | 0 | 0 | 0 | 1 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0475
6246 | 0 | 0 | 0 | 1.8 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0299
6247 | 165 | 64 | 37 | 2.6 | 19.6 | 0 | 27.4357 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0125
6248 | 573 | 264 | 77 | 0.8 | 22.6 | 89.3922 | 21.855 | 15.7005 | 0 | 0 | 0 | 85.0319 | 0 | 7% | 0 | 0 | 10% | 0 | 14.2239
6249 | 741 | 469 | 97 | 0.5 | 25.1 | 177.6059 | 0 | 37.6889 | 0 | 0 | 0 | 174.2428 | 0 | 20% | 0 | 0 | 10% | 0 | 35.6974
6250 | 721 | 612 | 143 | 1.2 | 26 | 188.4062 | 0 | 53.1524 | 0 | 42.4433 | 0 | 146.9636 | 0 | 31% | 19.8049 | 0 | 36.94% | 0 | 30.698
6251 | 713 | 746 | 201 | 1.3 | 26.8 | 194.3596 | 0 | 59.5462 | 6.7938 | 42.5138 | 12.6095 | 153.0978 | 0 | 43% | 24.6751 | 0 | 70.49% | 0 | 45.1956
6252 | 840 | 837 | 150 | 1.9 | 27.7 | 236.047 | 0 | 47.6195 | 27.4805 | 42.5455 | 14.5164 | 194.552 | 0 | 57% | 14.3435 | 0 | 90% | 0 | 45.1753
6253 | 802 | 818 | 158 | 1.9 | 28.5 | 224.7543 | 0 | 32.9882 | 40.8733 | 42.5603 | 14.4511 | 183.4132 | 0 | 71% | 0 | 0 | 90% | 0 | 44.9116
6254 | 756 | 769 | 184 | 2.1 | 29.3 | 207.3699 | 0 | 33.0004 | 35.6798 | 42.5714 | 14.3838 | 165.8992 | 0 | 83% | 0 | 0 | 90% | 0 | 45.0081
6255 | 625 | 618 | 200 | 2.3 | 29.3 | 161.9068 | 0 | 31.6378 | 20.0125 | 42.5776 | 14.3859 | 120.3298 | 0 | 92% | 0 | 0 | 90% | 0 | 44.0734
6256 | 532 | 449 | 167 | 4.2 | 28.6 | 122.8448 | 0 | 28.1001 | 5.6934 | 42.5803 | 14.449 | 80.8653 | 0 | 98% | 0 | 0 | 90% | 0 | 43.6944
6257 | 360 | 249 | 126 | 4.1 | 27.1 | 63.1829 | 0 | 13.7322 | 0 | 42.5811 | 14.5806 | 21.4715 | 0 | 100% | 0 | 16.4352 | 63.7% | 0 | 45.7099
6258 | 242 | 93 | 52 | 2.6 | 26 | 0 | 42.1761 | 0.67562 | 0 | 59.3012 | 21.7355 | 0 | 57.8369 | 96% | 0 | 25 | 23.7% | 0 | 45.3333
6259 | 1 | 2 | 2 | 1.8 | 24.4 | 0 | 0 | 0 | 0 | 90.6666 | 35.2753 | 0 | 93.4776 | 89% | 0 | 8.5648 | 10% | 0 | 40.8928
6260 | 0 | 0 | 0 | 0.3 | 23 | 0 | 0 | 0 | 0 | 101.1796 | 40.0506 | 0 | 102.0523 | 81% | 0 | 0 | 10% | 0 | 37.6504
6261 | 0 | 0 | 0 | 0.9 | 22 | 0 | 0 | 0 | 0 | 95.9486 | 37.9691 | 0 | 95.1915 | 74% | 0 | 0 | 10% | 0 | 35.7425
6262 | 0 | 0 | 0 | 0.4 | 21.4 | 0 | 0 | 0 | 0 | 91.3714 | 36.1019 | 0 | 89.61 | 67% | 0 | 0 | 10% | 0 | 33.8939
6263 | 0 | 0 | 0 | 0.5 | 20.9 | 0 | 0 | 0 | 0 | 88.3902 | 34.8898 | 0 | 86.1315 | 61% | 0 | 0 | 10% | 0 | 32.6424
6264 | 0 | 0 | 0 | 0.2 | 20.2 | 0 | 0 | 0 | 0 | 87.8103 | 34.7014 | 0 | 85.611 | 54% | 0 | 0 | 10% | 0 | 32.3972
6265 | 0 | 0 | 0 | 0.6 | 19.8 | 0 | 0 | 0 | 0 | 87.274 | 34.507 | 0 | 85.1067 | 48% | 0 | 0 | 10% | 0 | 32.1573
6266 | 0 | 0 | 0 | 0.3 | 19.4 | 0 | 0 | 0 | 0 | 88.3538 | 34.9896 | 0 | 86.5174 | 41% | 0 | 0 | 10% | 0 | 32.5997
6267 | 0 | 0 | 0 | 0.7 | 18.9 | 0 | 0 | 0 | 0 | 95.3562 | 37.9737 | 0 | 95.1149 | 34% | 0 | 0 | 10% | 0 | 35.5495
6268 | 0 | 0 | 0 | 0.3 | 18.6 | 0 | 0 | 0 | 0 | 105.9068 | 42.4053 | 0 | 107.6626 | 26% | 0 | 0 | 10% | 0 | 39.9873
6269 | 0 | 0 | 0 | 1.7 | 18.3 | 0 | 0 | 0 | 0 | 110.9123 | 44.5011 | 0 | 113.2729 | 18% | 0 | 0 | 10% | 0 | 42.1429
6270 | 0 | 1 | 1 | 1.6 | 18.7 | 0 | 0 | 0 | 0 | 114.4999 | 45.9561 | 0 | 117.2269 | 9% | 0 | 0 | 10% | 0 | 43.6636
6271 | 184 | 66 | 38 | 1.4 | 19.8 | 0 | 30.4417 | 0 | 0 | 116.7742 | 46.8017 | 0 | 119.6219 | 0% | 0 | 0 | 10% | 0 | 44.5748
6272 | 493 | 248 | 89 | 0.8 | 22.2 | 74.858 | 18.3861 | 14.2697 | 0 | 0 | 0 | 72.2739 | 0 | 5% | 0 | 0 | 10% | 0 | 12.9185
6273 | 653 | 449 | 121 | 0.9 | 24.5 | 154.1197 | 0 | 35.3021 | 0 | 0 | 0 | 151.8572 | 0 | 17% | 0 | 0 | 10% | 0 | 33.5227
6274 | 760 | 622 | 129 | 1.6 | 25.6 | 199.2627 | 0 | 54.7972 | 0 | 0 | 0 | 197.5763 | 0 | 32% | 6.1456 | 0 | 18.36% | 0 | 46.4424
6275 | 798 | 746 | 143 | 1.8 | 26.6 | 219.0959 | 0 | 67.4138 | 0 | 0 | 0 | 217.7167 | 0 | 48% | 19.8882 | 0 | 45.41% | 0 | 45.1015
6276 | 752 | 810 | 197 | 2.3 | 27 | 209.1769 | 0 | 72.8553 | 1.3545 | 0 | 0 | 208.0251 | 0 | 64% | 25 | 0 | 79.41% | 0 | 45.4863
6277 | 716 | 785 | 199 | 3.8 | 27.4 | 197.6866 | 0 | 54.9422 | 16.4738 | 0 | 0 | 196.5488 | 0 | 79% | 7.7897 | 0 | 90% | 0 | 44.8536
6278 | 697 | 738 | 202 | 4.4 | 27.6 | 188.1658 | 0 | 47.3158 | 18.4167 | 0 | 0 | 187.0769 | 0 | 93% | 0 | 0 | 90% | 0 | 45.0856
6279 | 598 | 600 | 196 | 4.4 | 27.6 | 133.0397 | 23.198 | 44.7973 | 4.9135 | 42.5962 | 1.291 | 92.2316 | 0 | 100% | 0 | 0 | 90% | 0 | 44.1797
6280 | 337 | 328 | 153 | 4.6 | 26.8 | 42.1574 | 38.1822 | 22.4522 | 0 | 42.5959 | 14.6113 | 0 | 0 | 100% | 0 | 6.0476 | 80.32% | 0 | 43.8211
6281 | 304 | 220 | 114 | 4.8 | 26 | 0 | 60.1146 | 11.0709 | 0 | 42.5928 | 14.6779 | 0 | 41.1016 | 97% | 0 | 22.0554 | 45.03% | 0 | 45.7262
6282 | 129 | 72 | 50 | 4.7 | 24.5 | 0 | 22.2598 | 0 | 0 | 69.975 | 26.4132 | 0 | 69.5489 | 92% | 0 | 21.897 | 10% | 0 | 45.3838
6283 | 0 | 1 | 1 | 3.9 | 22.9 | 0 | 0 | 0 | 0 | 110.8483 | 44.0608 | 0 | 115.1163 | 83% | 0 | 0 | 10% | 0 | 41.305
6284 | 0 | 0 | 0 | 3 | 21.6 | 0 | 0 | 0 | 0 | 101.1419 | 40.1622 | 0 | 101.275 | 76% | 0 | 0 | 10% | 0 | 37.9475
6285 | 0 | 0 | 0 | 2.5 | 20.9 | 0 | 0 | 0 | 0 | 95.7863 | 37.9949 | 0 | 94.6569 | 69% | 0 | 0 | 10% | 0 | 35.8595
6286 | 0 | 0 | 0 | 3.1 | 20.3 | 0 | 0 | 0 | 0 | 91.6162 | 36.2935 | 0 | 89.6778 | 62% | 0 | 0 | 10% | 0 | 34.1482
6287 | 0 | 0 | 0 | 3.5 | 19.7 | 0 | 0 | 0 | 0 | 88.7051 | 35.1138 | 0 | 86.3091 | 55% | 0 | 0 | 10% | 0 | 32.9226
6288 | 0 | 0 | 0 | 2 | 19.7 | 0 | 0 | 0 | 0 | 87.684 | 34.6855 | 0 | 85.2698 | 49% | 0 | 0 | 10% | 0 | 32.4359
6289 | 0 | 0 | 0 | 2.4 | 19.9 | 0 | 0 | 0 | 0 | 87.3414 | 34.5276 | 0 | 85.0167 | 43% | 0 | 0 | 10% | 0 | 32.2267
6290 | 0 | 0 | 0 | 3.1 | 20.1 | 0 | 0 | 0 | 0 | 88.6735 | 35.0717 | 0 | 86.7414 | 36% | 0 | 0 | 10% | 0 | 32.7265
6291 | 0 | 0 | 0 | 3 | 19.8 | 0 | 0 | 0 | 0 | 95.5592 | 37.9899 | 0 | 95.1865 | 29% | 0 | 0 | 10% | 0 | 35.6076
6292 | 0 | 0 | 0 | 2.5 | 20 | 0 | 0 | 0 | 0 | 106.5772 | 42.5672 | 0 | 108.2878 | 21% | 0 | 0 | 10% | 0 | 40.1832
6293 | 0 | 0 | 0 | 2.2 | 19.6 | 0 | 0 | 0 | 0 | 111.0386 | 44.4432 | 0 | 113.2829 | 12% | 0 | 0 | 10% | 0 | 42.1126
6294 | 0 | 0 | 0 | 2.4 | 18.8 | 0 | 0 | 0 | 0 | 114.704 | 46.0323 | 0 | 117.3639 | 3% | 0 | 0 | 10% | 0 | 43.7589
6295 | 13 | 46 | 44 | 2.5 | 18.9 | 0 | 2.1399 | 0 | 0 | 43.289 | 17.3833 | 0 | 44.3746 | 0% | 0 | 0 | 10% | 0 | 15.2918
6296 | 89 | 168 | 135 | 3.5 | 20 | 0 | 20.8833 | 5.5031 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.4947
6297 | 163 | 339 | 261 | 5.3 | 22.4 | 0 | 45.622 | 21.4067 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 19.4154
6298 | 102 | 352 | 279 | 5.5 | 22.6 | 0 | 31.0603 | 20.9385 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 18.9638
6299 | 51 | 349 | 307 | 4.3 | 23.2 | 0 | 16.1678 | 20.7636 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 18.8051
6300 | 19 | 406 | 384 | 4.8 | 23.5 | 0 | 6.1273 | 22.0691 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 20.1266
6301 | 165 | 655 | 511 | 5.5 | 24.5 | 0 | 53.243 | 51.783 | 0 | 0 | 0 | 0 | 0 | 0% | 6.8897 | 0 | 19.37% | 0 | 42.9666
6302 | 257 | 661 | 455 | 6 | 25 | 45.6062 | 12.0271 | 52.6419 | 0 | 0 | 0 | 43.5243 | 0 | 3% | 8.555 | 0 | 31% | 0 | 43.0029
6303 | 336 | 546 | 326 | 6 | 25 | 75.4537 | 0 | 43.2498 | 0 | 0 | 0 | 73.2477 | 0 | 9% | 0 | 0 | 31% | 0 | 42.1662
6304 | 239 | 376 | 245 | 6.2 | 24.7 | 0 | 54.2347 | 24.1891 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 11.5562 | 12.52% | 0 | 34.741
6305 | 51 | 166 | 146 | 6.1 | 23.7 | 0 | 12.2057 | 5.2951 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | 3.3983
6306 | 2 | 61 | 60 | 7.1 | 22.5 | 0 | 0.34166 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.8808
6307 | 0 | 1 | 1 | 5.1 | 21.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.8651
6308 | 0 | 0 | 0 | 4.7 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.8496
6309 | 0 | 0 | 0 | 4.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.8345
6310 | 0 | 0 | 0 | 2.4 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.8197
6311 | 0 | 0 | 0 | 1.8 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.8052
6312 | 0 | 0 | 0 | 1.8 | 20.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.7911
6313 | 0 | 0 | 0 | 1.3 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.7772
6314 | 0 | 0 | 0 | 1.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.7636
6315 | 0 | 0 | 0 | 1.4 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.7503
6316 | 0 | 0 | 0 | 1 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.7373
6317 | 0 | 0 | 0 | 0.7 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.7245
6318 | 0 | 0 | 0 | 1 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.712
6319 | 1 | 32 | 32 | 0.8 | 19.1 | 0 | 0.16376 | 0 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -1.6997
6320 | 2 | 112 | 110 | 1.1 | 20.1 | 0 | 0.46815 | 1.2552 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | -0.43248
6321 | 29 | 283 | 266 | 0.5 | 22.3 | 0 | 8.1085 | 12.9362 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | 11.2604
6322 | 235 | 469 | 306 | 1 | 23.9 | 0 | 60.712 | 33.5269 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 12.52% | 0 | 31.8644
6323 | 278 | 636 | 416 | 2.1 | 24.9 | 64.6789 | 0 | 50.532 | 0 | 0 | 0 | 61.5575 | 0 | 14% | 9.8504 | 0 | 25.91% | 0 | 39.6886
6324 | 401 | 786 | 454 | 3.4 | 25.8 | 102.4783 | 0 | 64.1158 | 2.9763 | 0 | 0 | 99.3258 | 0 | 22% | 25 | 0 | 59.91% | 0 | 37.7733
6325 | 210 | 602 | 424 | 3.8 | 26 | 0 | 54.38 | 47.325 | 0 | 0 | 0 | 0 | 0 | 22% | 10.1948 | 0 | 73.78% | 0 | 36.3769
6326 | 35 | 398 | 366 | 3.9 | 25.6 | 0 | 11.1161 | 24.7701 | 0 | 42.1805 | 0 | 0 | 38.7038 | 19% | 0 | 13.6317 | 51.97% | 0 | 36.2257
6327 | 71 | 348 | 295 | 4.9 | 25.1 | 0 | 21.7056 | 20.2834 | 0 | 44.7534 | 6.7429 | 0 | 41.2675 | 15% | 0 | 0 | 51.97% | 0 | 24.9574
6328 | 14 | 224 | 216 | 4.7 | 24.3 | 0 | 3.9478 | 8.3069 | 0 | 42.1486 | 14.6614 | 0 | 38.8711 | 12% | 0 | 14.9569 | 28.04% | 0 | 36.1158
6329 | 2 | 92 | 91 | 4 | 23.8 | 0 | 0.47623 | 0.24155 | 0 | 76.0851 | 29.2194 | 0 | 74.355 | 7% | 0 | 11.2717 | 10% | 0 | 38.7981
6330 | 10 | 52 | 50 | 3.2 | 23.5 | 0 | 1.691 | 0 | 0 | 85.6963 | 33.9628 | 0 | 85.6534 | 0% | 0 | 0 | 10% | 0 | 31.9976
6331 | 0 | 1 | 1 | 3.3 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.837
6332 | 0 | 0 | 0 | 1.7 | 22.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8233
6333 | 0 | 0 | 0 | 1.8 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.81
6334 | 0 | 0 | 0 | 1.7 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7969
6335 | 0 | 0 | 0 | 1.4 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7841
6336 | 0 | 0 | 0 | 0.6 | 20.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7715
6337 | 0 | 0 | 0 | 1 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7591
6338 | 0 | 0 | 0 | 1.2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.747
6339 | 0 | 0 | 0 | 1 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7351
6340 | 0 | 0 | 0 | 0.9 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7234
6341 | 0 | 0 | 0 | 1.6 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7119
6342 | 0 | 0 | 0 | 0.7 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7007
6343 | 0 | 27 | 27 | 0.5 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6897
6344 | 415 | 240 | 91 | 1 | 19.6 | 59.8153 | 15.0042 | 12.6131 | 0 | 0 | 0 | 55.7928 | 0 | 4% | 0 | 0 | 10% | 0 | 11.4401
6345 | 749 | 456 | 87 | 1.3 | 22.8 | 178.35 | 0 | 37.6061 | 0 | 0 | 0 | 172.0575 | 0 | 18% | 0 | 0 | 10% | 0 | 35.5984
6346 | 859 | 635 | 84 | 2 | 25.2 | 226.7285 | 0 | 57.2298 | 0 | 42.2693 | 0 | 184.5158 | 0 | 32% | 24.1101 | 0 | 42.79% | 0 | 30.1009
6347 | 869 | 754 | 105 | 1.6 | 26.9 | 240.2453 | 0 | 54.8204 | 14.9928 | 42.4484 | 9.198 | 198.9339 | 0 | 47% | 25 | 0 | 76.79% | 0 | 36.1625
6348 | 852 | 812 | 126 | 1.6 | 28.1 | 239.4938 | 0 | 32.4252 | 42.6748 | 42.5022 | 14.4668 | 198.3213 | 0 | 63% | 9.7135 | 0 | 90% | 0 | 34.4927
6349 | 792 | 790 | 150 | 1.2 | 29.3 | 221.6727 | 0 | 21.567 | 50.6448 | 42.525 | 14.3681 | 180.575 | 0 | 76% | 0 | 0 | 90% | 0 | 33.4049
6350 | 755 | 740 | 167 | 2 | 30.1 | 206.788 | 0 | 21.2975 | 45.6602 | 42.5424 | 14.3028 | 165.48 | 0 | 89% | 0 | 0 | 90% | 0 | 33.2053
6351 | 614 | 584 | 181 | 3 | 30.3 | 157.6884 | 0 | 19.9011 | 29.2399 | 42.5531 | 14.2883 | 116.1967 | 0 | 97% | 0 | 0 | 90% | 0 | 33.2063
6352 | 597 | 425 | 112 | 2.8 | 30.3 | 79.4487 | 72.4272 | 19.0754 | 12.9925 | 42.559 | 14.2903 | 37.6806 | 0 | 100% | 0 | 0 | 90% | 0 | 34.0422
6353 | 119 | 188 | 149 | 2.8 | 29.3 | 0 | 28.1909 | 7.6907 | 0 | 42.558 | 14.3792 | 0 | 41.0666 | 97% | 0 | 17.1598 | 62.54% | 0 | 37.1603
6354 | 255 | 94 | 54 | 2.4 | 28.2 | 0 | 42.6809 | 0.69276 | 0 | 45.6107 | 15.7121 | 0 | 43.9814 | 94% | 0 | 25 | 22.54% | 0 | 38.4913
6355 | 0 | 1 | 1 | 1.5 | 25.8 | 0 | 0 | 0 | 0 | 82.1173 | 31.6108 | 0 | 83.4749 | 88% | 0 | 7.8402 | 10% | 0 | 36.5409
6356 | 0 | 0 | 0 | 1.9 | 23.8 | 0 | 0 | 0 | 0 | 93.6836 | 36.8631 | 0 | 93.7466 | 81% | 0 | 0 | 10% | 0 | 34.2963
6357 | 0 | 0 | 0 | 1.5 | 22.6 | 0 | 0 | 0 | 0 | 87.9911 | 34.5803 | 0 | 86.3338 | 74% | 0 | 0 | 10% | 0 | 32.134
6358 | 0 | 0 | 0 | 0.7 | 22.2 | 0 | 0 | 0 | 0 | 84.2964 | 33.0737 | 0 | 82.0063 | 68% | 0 | 0 | 10% | 0 | 30.6026
6359 | 0 | 0 | 0 | 1.1 | 21.7 | 0 | 0 | 0 | 0 | 81.7309 | 31.9996 | 0 | 79.3543 | 62% | 0 | 0 | 10% | 0 | 29.4742
6360 | 0 | 0 | 0 | 1.5 | 20.9 | 0 | 0 | 0 | 0 | 80.5313 | 31.5191 | 0 | 78.2806 | 56% | 0 | 0 | 10% | 0 | 28.9441
6361 | 0 | 0 | 0 | 1.2 | 20.3 | 0 | 0 | 0 | 0 | 80.81 | 31.6914 | 0 | 78.6638 | 51% | 0 | 0 | 10% | 0 | 29.0782
6362 | 0 | 0 | 0 | 1.1 | 19.8 | 0 | 0 | 0 | 0 | 82.1905 | 32.3569 | 0 | 80.1403 | 45% | 0 | 0 | 10% | 0 | 29.7132
6363 | 0 | 0 | 0 | 1.3 | 19.5 | 0 | 0 | 0 | 0 | 90.4452 | 35.8638 | 0 | 90.0175 | 38% | 0 | 0 | 10% | 0 | 33.1862
6364 | 0 | 0 | 0 | 1.7 | 18.5 | 0 | 0 | 0 | 0 | 101.695 | 40.6516 | 0 | 103.5799 | 30% | 0 | 0 | 10% | 0 | 37.984
6365 | 0 | 0 | 0 | 2 | 18.9 | 0 | 0 | 0 | 0 | 106.4024 | 42.587 | 0 | 108.9524 | 22% | 0 | 0 | 10% | 0 | 39.9949
6366 | 0 | 0 | 0 | 1.3 | 18 | 0 | 0 | 0 | 0 | 109.9459 | 44.1268 | 0 | 112.7785 | 14% | 0 | 0 | 10% | 0 | 41.6161
6367 | 239 | 61 | 27 | 1.1 | 19.3 | 0 | 38.7335 | 0 | 0 | 113.1759 | 45.3562 | 0 | 116.2746 | 5% | 0 | 0 | 10% | 0 | 42.922
6368 | 611 | 267 | 79 | 1.7 | 22 | 94.709 | 23.192 | 17.4712 | 0 | 72.2565 | 27.7507 | 35.2326 | 12.8287 | 7% | 0 | 0 | 10% | 0 | 43.5825
6369 | 617 | 433 | 130 | 2.9 | 23 | 143.2403 | 0 | 34.6626 | 0 | 43.7679 | 15.3997 | 100.4076 | 0 | 14% | 4.0592 | 0 | 15.52% | 0 | 44.2907
6370 | 734 | 611 | 141 | 3.4 | 24.2 | 190.7477 | 0 | 54.6787 | 0 | 44.8426 | 15.7431 | 146.8193 | 0 | 25% | 23.8975 | 0 | 48.02% | 0 | 44.384
6371 | 706 | 734 | 210 | 2.3 | 25.4 | 191.8651 | 0 | 55.6019 | 11.5279 | 42.5886 | 14.7258 | 150.4439 | 0 | 36% | 25 | 0 | 82.02% | 0 | 43.1654
6372 | 792 | 877 | 241 | 2.2 | 26.2 | 221.1689 | -2.28e-14 | 36.0423 | 39.0577 | 42.5972 | 14.6625 | 179.6182 | 0 | 50% | 5.8668 | 0 | 90% | 0 | 42.3942
6373 | 681 | 777 | 229 | 3.5 | 26.5 | 187.2822 | 0 | 29.5864 | 41.4791 | 42.6009 | 14.6384 | 145.8597 | 0 | 61% | 0 | 0 | 90% | 0 | 42.0764
6374 | 662 | 694 | 197 | 3.9 | 26.8 | 178.1754 | 0 | 29.3785 | 33.2245 | 42.6022 | 14.6134 | 136.5092 | 0 | 71% | 0 | 0 | 90% | 0 | 41.9197
6375 | 803 | 635 | 116 | 3.8 | 27 | 210.7899 | 0 | 29.3141 | 27.4573 | 42.6026 | 14.5967 | 168.6986 | 0 | 83% | 0 | 0 | 90% | 0 | 41.5312
6376 | 570 | 425 | 134 | 4.6 | 26.1 | 130.7509 | 0 | 27.0992 | 5.7041 | 42.6034 | 14.6731 | 89.014 | 0 | 90% | 0 | 0 | 90% | 0 | 41.6217
6377 | 125 | 191 | 143 | 4.3 | 24.6 | 0 | 29.4602 | 7.599 | 0 | 42.6014 | 14.795 | 0 | 41.1408 | 87% | 0 | 24.1297 | 51.39% | 0 | 44.4384
6378 | 16 | 50 | 48 | 3.3 | 23.4 | 0 | 2.6504 | 0 | 0 | 59.0258 | 21.8505 | 0 | 57.5129 | 82% | 0 | 25 | 11.39% | 0 | 43.8703
6379 | 0 | 1 | 1 | 2.7 | 22.1 | 0 | 0 | 0 | 0 | 107.3044 | 42.6788 | 0 | 111.8123 | 74% | 0 | 0 | 11.39% | 0 | 39.6835
6380 | 0 | 0 | 0 | 1.9 | 21.1 | 0 | 0 | 0 | 0 | 98.2763 | 39.0119 | 0 | 99.2147 | 67% | 0 | 0 | 11.39% | 0 | 36.4277
6381 | 0 | 0 | 0 | 0.7 | 20.5 | 0 | 0 | 0 | 0 | 93.6675 | 37.1441 | 0 | 93.2863 | 60% | 0 | 0 | 11.39% | 0 | 34.6817
6382 | 0 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 0 | 89.4117 | 35.3881 | 0 | 87.9074 | 53% | 0 | 0 | 11.39% | 0 | 32.9661
6383 | 0 | 0 | 0 | 0.8 | 19.2 | 0 | 0 | 0 | 0 | 86.6951 | 34.307 | 0 | 84.6709 | 47% | 0 | 0 | 11.39% | 0 | 31.8741
6384 | 0 | 0 | 0 | 0.6 | 18.7 | 0 | 0 | 0 | 0 | 85.5954 | 33.8825 | 0 | 83.4471 | 41% | 0 | 0 | 11.39% | 0 | 31.4207
6385 | 0 | 0 | 0 | 0.7 | 18.3 | 0 | 0 | 0 | 0 | 85.7386 | 33.9706 | 0 | 83.7038 | 34% | 0 | 0 | 11.39% | 0 | 31.478
6386 | 0 | 0 | 0 | 1.1 | 18.5 | 0 | 0 | 0 | 0 | 87.1006 | 34.5278 | 0 | 85.3999 | 28% | 0 | 0 | 11.39% | 0 | 32.0089
6387 | 0 | 0 | 0 | 0.3 | 17.2 | 0 | 0 | 0 | 0 | 92.9612 | 37.093 | 0 | 92.6125 | 21% | 0 | 0 | 11.39% | 0 | 34.5509
6388 | 0 | 0 | 0 | 0.5 | 17.4 | 0 | 0 | 0 | 0 | 103.3668 | 41.437 | 0 | 105.0515 | 13% | 0 | 0 | 11.39% | 0 | 38.8959
6389 | 0 | 0 | 0 | 0.6 | 16.8 | 0 | 0 | 0 | 0 | 106.8806 | 42.9513 | 0 | 109.0235 | 5% | 0 | 0 | 11.39% | 0 | 40.4628
6390 | 0 | 0 | 0 | 0.3 | 16.4 | 0 | 0 | 0 | 0 | 67.4805 | 27.1657 | 0 | 69.0141 | 0% | 0 | 0 | 11.39% | 0 | 24.8074
6391 | 323 | 67 | 23 | 1 | 17.3 | 0 | 52.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 11.39% | 0 | -2.2304
6392 | 691 | 259 | 48 | 0.6 | 21.5 | 108.8955 | 26.605 | 17.4496 | 0 | 0 | 0 | 104.9819 | 0 | 8% | 0 | 0 | 11.39% | 0 | 15.7731
6393 | 829 | 460 | 60 | 0.8 | 24.3 | 199.2952 | 0 | 39.274 | 0 | 0 | 0 | 197.0448 | 0 | 23% | 0 | 0 | 11.39% | 0 | 37.1
6394 | 905 | 635 | 65 | 1.5 | 25.9 | 240.1605 | 0 | 58.579 | 0 | 0 | 0 | 238.5206 | 0 | 41% | 11.6201 | 0 | 27.2% | 0 | 44.3825
6395 | 939 | 760 | 69 | 2 | 27.8 | 260.9836 | 0 | 71.8306 | 0 | 0 | 0 | 259.6004 | 0 | 60% | 24.6472 | 0 | 60.72% | 0 | 44.3698
6396 | 934 | 816 | 76 | 2.8 | 28.6 | 263.6475 | 0 | 68.2019 | 6.8981 | 0 | 0 | 262.4319 | 0 | 80% | 21.5323 | 0 | 90% | 0 | 43.7726
6397 | 937 | 819 | 76 | 2.7 | 29.5 | 264.6919 | 0 | 46.7398 | 28.3602 | 0 | 0 | 263.5199 | 0 | 100% | 0 | 0 | 90% | 0 | 43.7868
6398 | 918 | 755 | 74 | 3.5 | 30.1 | 0 | 278.2027 | 44.9069 | 25.5724 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.6469
6399 | 883 | 634 | 71 | 4.6 | 29.5 | 40.9348 | 221.6751 | 44.2032 | 13.3309 | 42.5942 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.0854
6400 | 815 | 465 | 64 | 4.4 | 29.6 | 42.1578 | 178.8022 | 28.0596 | 10.8597 | 42.5918 | 14.0783 | 0 | 0 | 100% | 0.085107 | 0.072341 | 90% | 0 | 42.8246
6401 | 687 | 267 | 51 | 4.2 | 28.2 | 42.1573 | 109.6558 | 17.8137 | 0 | 42.5896 | 14.4877 | 0 | 0 | 100% | 0 | 12.3035 | 70.31% | 0 | 45.3146
6402 | 314 | 68 | 25 | 3.4 | 24.6 | 0 | 51.4732 | 0 | 0 | 59.2515 | 21.8448 | 0 | 57.7869 | 95% | 0 | 25 | 30.31% | 0 | 44.7636
6403 | 0 | 0 | 0 | 1.8 | 22.1 | 0 | 0 | 0 | 0 | 79.6901 | 30.7992 | 0 | 81.2281 | 90% | 0 | 12.6965 | 10% | 0 | 40.5556
6404 | 0 | 0 | 0 | 0.4 | 20.7 | 0 | 0 | 0 | 0 | 99.7913 | 39.6766 | 0 | 100.8828 | 82% | 0 | 0 | 10% | 0 | 37.1444
6405 | 0 | 0 | 0 | 0.3 | 20.3 | 0 | 0 | 0 | 0 | 95.3342 | 37.8558 | 0 | 94.8116 | 75% | 0 | 0 | 10% | 0 | 35.5348
6406 | 0 | 0 | 0 | 0.7 | 20.3 | 0 | 0 | 0 | 0 | 91.104 | 36.0776 | 0 | 89.5267 | 68% | 0 | 0 | 10% | 0 | 33.7974
6407 | 0 | 0 | 0 | 0.9 | 19.4 | 0 | 0 | 0 | 0 | 88.1867 | 34.9182 | 0 | 86.0797 | 62% | 0 | 0 | 10% | 0 | 32.6112
6408 | 0 | 0 | 0 | 0.6 | 19.2 | 0 | 0 | 0 | 0 | 86.973 | 34.424 | 0 | 84.7734 | 55% | 0 | 0 | 10% | 0 | 32.0695
6409 | 0 | 0 | 0 | 1.6 | 20.2 | 0 | 0 | 0 | 0 | 87.5304 | 34.584 | 0 | 85.5734 | 49% | 0 | 0 | 10% | 0 | 32.1839
6410 | 0 | 0 | 0 | 2.2 | 20.7 | 0 | 0 | 0 | 0 | 88.8203 | 35.0865 | 0 | 87.215 | 42% | 0 | 0 | 10% | 0 | 32.6546
6411 | 0 | 0 | 0 | 2.4 | 20.5 | 0 | 0 | 0 | 0 | 95.4666 | 37.896 | 0 | 95.3623 | 35% | 0 | 0 | 10% | 0 | 35.4389
6412 | 0 | 0 | 0 | 2.4 | 20.6 | 0 | 0 | 0 | 0 | 106.8102 | 42.6116 | 0 | 108.8371 | 27% | 0 | 0 | 10% | 0 | 40.165
6413 | 0 | 0 | 0 | 1.5 | 19.6 | 0 | 0 | 0 | 0 | 110.4593 | 44.2034 | 0 | 112.8137 | 19% | 0 | 0 | 10% | 0 | 41.8272
6414 | 0 | 0 | 0 | 2.7 | 19.2 | 0 | 0 | 0 | 0 | 114.0487 | 45.7249 | 0 | 116.761 | 10% | 0 | 0 | 10% | 0 | 43.4157
6415 | 346 | 66 | 22 | 2.5 | 20.4 | 0 | 55.4791 | 0 | 0 | 116.4911 | 46.6309 | 0 | 119.3582 | 1% | 0 | 0 | 10% | 0 | 44.3882
6416 | 706 | 260 | 47 | 1.2 | 22.6 | 106.8832 | 31.6375 | 17.8525 | 0 | 11.8446 | 4.5816 | 103.2633 | 11.2756 | 8% | 0 | 0 | 10% | 0 | 20.7419
6417 | 836 | 461 | 60 | 1 | 26.7 | 200.7011 | 0 | 39.431 | 0 | 0 | 0 | 198.64 | 0 | 23% | 0 | 0 | 10% | 0 | 37.2309
6418 | 896 | 631 | 69 | 2.2 | 28.3 | 237.0928 | 0 | 57.9783 | 0 | 0 | 0 | 235.5843 | 0 | 41% | 10.4872 | 0 | 24.26% | 0 | 44.9253
6419 | 925 | 753 | 75 | 2.8 | 29.4 | 256.4233 | 0 | 70.9887 | 0 | 0 | 0 | 255.1152 | 0 | 60% | 24.6695 | 0 | 57.81% | 0 | 43.5293
6420 | 937 | 817 | 78 | 2.9 | 30 | 264.3762 | 0 | 70.8155 | 4.2845 | 0 | 0 | 263.1804 | 0 | 80% | 23.6669 | 0 | 90% | 0 | 44.2296
6421 | 930 | 815 | 81 | 3.9 | 30.1 | 261.6443 | 0 | 46.9121 | 28.1503 | 0 | 0 | 260.5246 | 0 | 100% | 0 | 0 | 90% | 0 | 43.9688
6422 | 901 | 748 | 84 | 4 | 30 | 0 | 272.6675 | 44.8968 | 25.1915 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.8047
6423 | 850 | 622 | 83 | 3.5 | 30.1 | 40.8837 | 211.4563 | 42.8872 | 13.3594 | 42.5986 | 1.4636 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.0881
6424 | 761 | 447 | 77 | 3 | 30.1 | 42.0648 | 163.2071 | 28.1429 | 9.0117 | 42.5964 | 14.3209 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.0971
6425 | 618 | 252 | 61 | 2 | 29.9 | 42.1587 | 92.5285 | 16.4267 | 0 | 42.594 | 14.3381 | 0 | 0 | 100% | 0 | 14.1519 | 67.36% | 0 | 45.6259
6426 | 270 | 64 | 28 | 2.5 | 27 | 0 | 43.7961 | 0 | 0 | 60.0255 | 21.9465 | 0 | 58.5744 | 95% | 0 | 25 | 27.36% | 0 | 44.8627
6427 | 0 | 0 | 0 | 2.1 | 24.2 | 0 | 0 | 0 | 0 | 84.2926 | 32.5776 | 0 | 86.3402 | 89% | 0 | 10.8481 | 10% | 0 | 40.4841
6428 | 0 | 0 | 0 | 3.7 | 21.9 | 0 | 0 | 0 | 0 | 100.0817 | 39.694 | 0 | 101.0359 | 81% | 0 | 0 | 10% | 0 | 37.2128
6429 | 0 | 0 | 0 | 3.2 | 20.8 | 0 | 0 | 0 | 0 | 95.0577 | 37.7007 | 0 | 94.3772 | 74% | 0 | 0 | 10% | 0 | 35.4103
6430 | 0 | 0 | 0 | 2.2 | 20.8 | 0 | 0 | 0 | 0 | 91.1519 | 36.058 | 0 | 89.5232 | 68% | 0 | 0 | 10% | 0 | 33.7952
6431 | 0 | 0 | 0 | 2.3 | 20.7 | 0 | 0 | 0 | 0 | 88.527 | 34.9622 | 0 | 86.4399 | 61% | 0 | 0 | 10% | 0 | 32.6691
6432 | 0 | 0 | 0 | 2.5 | 20.3 | 0 | 0 | 0 | 0 | 87.6103 | 34.6092 | 0 | 85.4846 | 55% | 0 | 0 | 10% | 0 | 32.2689
6433 | 0 | 0 | 0 | 2.6 | 19.8 | 0 | 0 | 0 | 0 | 87.0805 | 34.4253 | 0 | 84.9752 | 48% | 0 | 0 | 10% | 0 | 32.0435
6434 | 0 | 0 | 0 | 2.4 | 19.2 | 0 | 0 | 0 | 0 | 88.2142 | 34.945 | 0 | 86.4405 | 42% | 0 | 0 | 10% | 0 | 32.5259
6435 | 0 | 0 | 0 | 2.8 | 18.9 | 0 | 0 | 0 | 0 | 94.9427 | 37.8012 | 0 | 94.7205 | 35% | 0 | 0 | 10% | 0 | 35.3511
6436 | 0 | 0 | 0 | 2.2 | 18.2 | 0 | 0 | 0 | 0 | 105.6255 | 42.3205 | 0 | 107.4296 | 27% | 0 | 0 | 10% | 0 | 39.8782
6437 | 0 | 0 | 0 | 1.8 | 18.4 | 0 | 0 | 0 | 0 | 109.9165 | 44.0796 | 0 | 112.1797 | 18% | 0 | 0 | 10% | 0 | 41.7009
6438 | 0 | 0 | 0 | 2.3 | 18.3 | 0 | 0 | 0 | 0 | 112.837 | 45.2996 | 0 | 115.3301 | 10% | 0 | 0 | 10% | 0 | 42.9868
6439 | 304 | 63 | 24 | 1.8 | 19.4 | 0 | 48.4808 | 0 | 0 | 115.2188 | 46.1936 | 0 | 117.8717 | 1% | 0 | 0 | 10% | 0 | 43.943
6440 | 679 | 255 | 52 | 1.1 | 22.2 | 101.3256 | 30.9633 | 17.5729 | 0 | 10.8454 | 4.1933 | 97.9001 | 10.3259 | 7% | 0 | 0 | 10% | 0 | 20.1121
6441 | 824 | 458 | 65 | 2 | 24.5 | 196.8944 | 0 | 39.6742 | 0 | 0 | 0 | 194.7894 | 0 | 22% | 0 | 0 | 10% | 0 | 37.5103
6442 | 894 | 630 | 72 | 4.2 | 25.7 | 235.079 | 0 | 58.7186 | 0 | 0 | 0 | 233.5514 | 0 | 40% | 11.2145 | 0 | 25.25% | 0 | 44.9597
6443 | 929 | 754 | 77 | 5.3 | 26.1 | 255.5674 | 0 | 72.3336 | 0 | 0 | 0 | 254.2489 | 0 | 59% | 24.4227 | 0 | 58.47% | 0 | 45.1326
6444 | 941 | 818 | 79 | 4.5 | 26.8 | 264.2304 | 0 | 70.7087 | 4.3913 | 0 | 0 | 263.0297 | 0 | 79% | 23.1863 | 0 | 90% | 0 | 44.608
6445 | 933 | 816 | 82 | 3.4 | 27.2 | 262.8491 | 0 | 47.5099 | 27.5901 | 0 | 0 | 261.7212 | 0 | 99% | 0 | 0 | 90% | 0 | 44.559
6446 | 903 | 747 | 85 | 3 | 27.9 | 16.6732 | 254.9694 | 45.527 | 25.2691 | 0 | 0 | 16.6025 | 0 | 100% | 0 | 0 | 90% | 0 | 44.3675
6447 | 859 | 623 | 83 | 3.7 | 28.1 | 40.9038 | 213.909 | 43.3427 | 13.8466 | 42.5987 | 1.4651 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.6045
6448 | 770 | 447 | 76 | 3.8 | 27.9 | 42.1583 | 164.9902 | 28.1797 | 9.5693 | 42.5965 | 14.5165 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.406
6449 | 600 | 244 | 61 | 3.8 | 26.9 | 42.1574 | 86.8191 | 15.9811 | 0 | 42.5941 | 14.6022 | 0 | 0 | 100% | 0 | 14.7689 | 66.37% | 0 | 46.0621
6450 | 225 | 58 | 27 | 3.7 | 24.6 | 0 | 36.1108 | 0 | 0 | 60.673 | 22.4551 | 0 | 59.2304 | 96% | 0 | 25 | 26.37% | 0 | 45.3783
6451 | 0 | 0 | 0 | 3.1 | 22.4 | 0 | 0 | 0 | 0 | 86.5919 | 33.7217 | 0 | 88.8912 | 89% | 0 | 10.2311 | 10% | 0 | 41.0146
6452 | 0 | 0 | 0 | 2.3 | 21.1 | 0 | 0 | 0 | 0 | 100.838 | 40.0792 | 0 | 101.7936 | 82% | 0 | 0 | 10% | 0 | 37.6378
6453 | 0 | 0 | 0 | 2 | 20.3 | 0 | 0 | 0 | 0 | 96.0895 | 38.1691 | 0 | 95.4499 | 74% | 0 | 0 | 10% | 0 | 35.9154
6454 | 0 | 0 | 0 | 1.4 | 20 | 0 | 0 | 0 | 0 | 92.2364 | 36.579 | 0 | 90.7235 | 68% | 0 | 0 | 10% | 0 | 34.3527
6455 | 0 | 0 | 0 | 1.3 | 19.6 | 0 | 0 | 0 | 0 | 89.1511 | 35.3084 | 0 | 87.0536 | 61% | 0 | 0 | 10% | 0 | 33.0564
6456 | 0 | 0 | 0 | 0.9 | 19.5 | 0 | 0 | 0 | 0 | 88.013 | 34.838 | 0 | 85.8385 | 55% | 0 | 0 | 10% | 0 | 32.5369
6457 | 0 | 0 | 0 | 0.1 | 18.8 | 0 | 0 | 0 | 0 | 87.037 | 34.4795 | 0 | 84.8069 | 48% | 0 | 0 | 10% | 0 | 32.134
6458 | 0 | 0 | 0 | 0.2 | 17.8 | 0 | 0 | 0 | 0 | 88.3117 | 35.0855 | 0 | 86.4574 | 42% | 0 | 0 | 10% | 0 | 32.6969
6459 | 0 | 0 | 0 | 0.8 | 17.8 | 0 | 0 | 0 | 0 | 94.9102 | 37.8697 | 0 | 94.5848 | 35% | 0 | 0 | 10% | 0 | 35.4468
6460 | 0 | 0 | 0 | 0.5 | 17.5 | 0 | 0 | 0 | 0 | 105.2116 | 42.2043 | 0 | 106.8493 | 27% | 0 | 0 | 10% | 0 | 39.786
6461 | 0 | 0 | 0 | 0.4 | 17 | 0 | 0 | 0 | 0 | 109.1172 | 43.8626 | 0 | 111.1539 | 18% | 0 | 0 | 10% | 0 | 41.5035
6462 | 0 | 0 | 0 | 0.5 | 16.6 | 0 | 0 | 0 | 0 | 113.016 | 45.5165 | 0 | 115.4883 | 10% | 0 | 0 | 10% | 0 | 43.2161
6463 | 254 | 59 | 26 | 1.5 | 17.7 | 0 | 40.2815 | 0 | 0 | 115.9102 | 46.6301 | 0 | 118.651 | 1% | 0 | 0 | 10% | 0 | 44.3899
6464 | 633 | 247 | 59 | 0.6 | 22 | 93.4223 | 28.6857 | 16.9252 | 0 | 8.1517 | 3.1694 | 90.2547 | 7.767 | 7% | 0 | 0 | 10% | 0 | 18.5123
6465 | 799 | 450 | 71 | 0.9 | 24.7 | 190.6427 | 0 | 38.9913 | 0 | 0 | 0 | 188.4491 | 0 | 21% | 0 | 0 | 10% | 0 | 36.884
6466 | 881 | 623 | 75 | 1.4 | 26.1 | 232.9705 | 0 | 58.1095 | 0 | 0 | 0 | 231.3961 | 0 | 39% | 10.0617 | 0 | 23.68% | 0 | 45.5239
6467 | 922 | 747 | 78 | 1.5 | 27.1 | 256.1172 | 0 | 71.6818 | 0 | 0 | 0 | 254.774 | 0 | 58% | 23.5504 | 0 | 55.71% | 0 | 45.3498
6468 | 939 | 812 | 79 | 1.9 | 28.2 | 265.2896 | 0 | 72.3092 | 2.7908 | 0 | 0 | 264.0749 | 0 | 78% | 25 | 0 | 89.71% | 0 | 44.3897
6469 | 928 | 809 | 84 | 2.7 | 28.9 | 261.6491 | 0 | 47.0977 | 28.0023 | 0 | 0 | 260.512 | 0 | 98% | 0.2114 | 0 | 90% | 0 | 43.9477
6470 | 906 | 743 | 84 | 3.5 | 29.5 | 31.6984 | 239.396 | 44.8319 | 25.6905 | 0 | 0 | 31.5629 | 0 | 100% | 0 | 0 | 90% | 0 | 43.6231
6471 | 865 | 619 | 80 | 3.9 | 29.7 | 40.9078 | 215.4611 | 42.5443 | 14.3997 | 42.5986 | 1.4036 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.7537
6472 | 774 | 443 | 74 | 3.9 | 29 | 42.158 | 165.5873 | 27.3442 | 10.2144 | 42.5964 | 14.4189 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4726
6473 | 605 | 241 | 59 | 3.2 | 28 | 42.1573 | 87.5004 | 15.8507 | 0 | 42.594 | 14.507 | 0 | 0 | 100% | 0 | 13.2742 | 68.76% | 0 | 44.3416
6474 | 235 | 56 | 26 | 3.5 | 24.7 | 0 | 37.3134 | 0 | 0 | 56.1962 | 20.5228 | 0 | 54.6872 | 96% | 0 | 25 | 28.76% | 0 | 43.4451
6475 | 0 | 0 | 0 | 1.8 | 22.1 | 0 | 0 | 0 | 0 | 79.4366 | 30.7183 | 0 | 80.9605 | 90% | 0 | 11.7258 | 10% | 0 | 39.5011
6476 | 0 | 0 | 0 | 0.7 | 21.3 | 0 | 0 | 0 | 0 | 98.5579 | 39.112 | 0 | 99.3634 | 83% | 0 | 0 | 10% | 0 | 36.5913
6477 | 0 | 0 | 0 | 0.8 | 21 | 0 | 0 | 0 | 0 | 94.4447 | 37.4306 | 0 | 93.8071 | 76% | 0 | 0 | 10% | 0 | 35.1006
6478 | 0 | 0 | 0 | 1.2 | 20.6 | 0 | 0 | 0 | 0 | 90.4128 | 35.7624 | 0 | 88.737 | 69% | 0 | 0 | 10% | 0 | 33.467
6479 | 0 | 0 | 0 | 0.9 | 19.7 | 0 | 0 | 0 | 0 | 86.8324 | 34.3282 | 0 | 84.5282 | 63% | 0 | 0 | 10% | 0 | 32.0017
6480 | 0 | 0 | 0 | 0.2 | 19.2 | 0 | 0 | 0 | 0 | 85.015 | 33.6046 | 0 | 82.5457 | 56% | 0 | 0 | 10% | 0 | 31.2221
6481 | 0 | 0 | 0 | 1.4 | 18.7 | 0 | 0 | 0 | 0 | 83.7344 | 33.1053 | 0 | 81.1997 | 50% | 0 | 0 | 10% | 0 | 30.6689
6482 | 0 | 0 | 0 | 1.1 | 18.9 | 0 | 0 | 0 | 0 | 83.1427 | 32.8452 | 0 | 80.649 | 44% | 0 | 0 | 10% | 0 | 30.3597
6483 | 0 | 0 | 0 | 1.3 | 18.7 | 0 | 0 | 0 | 0 | 84.6752 | 33.4986 | 0 | 82.5744 | 38% | 0 | 0 | 10% | 0 | 30.9685
6484 | 0 | 0 | 0 | 2 | 18.8 | 0 | 0 | 0 | 0 | 88.179 | 34.9598 | 0 | 86.8442 | 32% | 0 | 0 | 10% | 0 | 32.3986
6485 | 0 | 0 | 0 | 1 | 18.9 | 0 | 0 | 0 | 0 | 91.1925 | 36.2221 | 0 | 90.5319 | 25% | 0 | 0 | 10% | 0 | 33.6531
6486 | 0 | 0 | 0 | 1.2 | 18.4 | 0 | 0 | 0 | 0 | 97.9377 | 39.0876 | 0 | 98.6399 | 18% | 0 | 0 | 10% | 0 | 36.5206
6487 | 281 | 58 | 23 | 1.1 | 19.2 | 0 | 43.1239 | 0 | 0 | 103.1954 | 41.2255 | 0 | 104.8207 | 10% | 0 | 0 | 10% | 0 | 38.6909
6488 | 655 | 245 | 53 | 1.1 | 22.8 | 101.271 | 24.6779 | 17.0426 | 0 | 64.5349 | 24.2839 | 47.7641 | 11.4815 | 13% | 0 | 0 | 10% | 0 | 39.6199
6489 | 803 | 446 | 68 | 1.5 | 24.8 | 191.2993 | -2.98e-14 | 38.9855 | 0 | 45.2652 | 15.8706 | 146.3605 | 0 | 23% | 12.7716 | 0 | 27.37% | 0 | 39.949
6490 | 875 | 617 | 76 | 1.1 | 27 | 231.473 | 0 | 53.3065 | 4.3819 | 42.5687 | 14.585 | 189.5931 | 0 | 38% | 25 | 0 | 61.37% | 0 | 40.3843
6491 | 909 | 738 | 81 | 1.6 | 28.3 | 252.4401 | 0 | 48.8189 | 21.8809 | 42.5884 | 14.4784 | 210.6695 | 0 | 53% | 21.052 | 0 | 90% | 0 | 39.5217
6492 | 918 | 800 | 86 | 3.7 | 28.9 | 258.16 | 0 | 26.2526 | 48.8474 | 42.5959 | 14.4276 | 216.3925 | 0 | 69% | 0 | 0 | 90% | 0 | 37.8811
6493 | 906 | 796 | 91 | 3.8 | 28.9 | 254.5395 | 0 | 25.1792 | 49.9208 | 42.6003 | 14.4291 | 212.658 | 0 | 85% | 0 | 0 | 90% | 0 | 36.8193
6494 | 875 | 730 | 96 | 3.6 | 29.2 | 241.3733 | 0 | 19.6278 | 49.6114 | 42.6026 | 14.4032 | 199.2635 | 0 | 99% | 0 | 0 | 90% | 0 | 36.5255
6495 | 818 | 604 | 97 | 4.6 | 29 | 48.5584 | 191.8063 | 21.2196 | 34.18 | 42.6036 | 14.4213 | 7.1543 | 0 | 100% | 0 | 0 | 90% | 0 | 36.2893
6496 | 733 | 432 | 85 | 4.3 | 28.4 | 42.152 | 153.3336 | 21.2817 | 15.1494 | 42.6011 | 14.4738 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.4652
6497 | 561 | 232 | 65 | 4.7 | 27.2 | 42.1574 | 75.2572 | 14.9591 | 0 | 42.5986 | 14.5779 | 0 | 0 | 100% | 0 | 8.7424 | 76.01% | 0 | 38.9894
6498 | 185 | 51 | 27 | 4.1 | 25 | 0 | 27.7607 | 0 | 0 | 46.1867 | 16.2403 | 0 | 44.6653 | 97% | 0 | 25 | 36.01% | 0 | 39.1734
6499 | 0 | 0 | 0 | 3.8 | 22.8 | 0 | 0 | 0 | 0 | 61.4793 | 23.0421 | 0 | 61.2713 | 92% | 0 | 16.2576 | 10% | 0 | 36.374
6500 | 0 | 0 | 0 | 3.4 | 21.3 | 0 | 0 | 0 | 0 | 93.2369 | 36.8965 | 0 | 93.6605 | 85% | 0 | 0 | 10% | 0 | 34.1895
6501 | 0 | 0 | 0 | 2.8 | 20.5 | 0 | 0 | 0 | 0 | 87.4266 | 34.5157 | 0 | 85.8433 | 79% | 0 | 0 | 10% | 0 | 32.0084
6502 | 0 | 0 | 0 | 1.1 | 19.9 | 0 | 0 | 0 | 0 | 83.0584 | 32.7378 | 0 | 80.7133 | 73% | 0 | 0 | 10% | 0 | 30.2122
6503 | 0 | 0 | 0 | 1.5 | 19.3 | 0 | 0 | 0 | 0 | 80.1421 | 31.4548 | 0 | 77.941 | 67% | 0 | 0 | 10% | 0 | 28.8672
6504 | 0 | 0 | 0 | 0.9 | 19.1 | 0 | 0 | 0 | 0 | 78.1006 | 30.5486 | 0 | 75.9934 | 62% | 0 | 0 | 10% | 0 | 27.9186
6505 | 0 | 0 | 0 | 1.3 | 18.2 | 0 | 0 | 0 | 0 | 76.9326 | 30.0851 | 0 | 74.8948 | 56% | 0 | 0 | 10% | 0 | 27.4238
6506 | 0 | 0 | 0 | 0.8 | 18.2 | 0 | 0 | 0 | 0 | 76.918 | 30.0791 | 0 | 74.9413 | 50% | 0 | 0 | 10% | 0 | 27.393
6507 | 0 | 0 | 0 | 1.4 | 18.1 | 0 | 0 | 0 | 0 | 78.0699 | 30.6036 | 0 | 76.1548 | 45% | 0 | 0 | 10% | 0 | 27.8966
6508 | 0 | 0 | 0 | 0.5 | 17.1 | 0 | 0 | 0 | 0 | 79.1306 | 31.1466 | 0 | 77.2664 | 39% | 0 | 0 | 10% | 0 | 28.4227
6509 | 0 | 0 | 0 | 0.9 | 17.2 | 0 | 0 | 0 | 0 | 80.0114 | 31.5397 | 0 | 78.1886 | 33% | 0 | 0 | 10% | 0 | 28.8023
6510 | 0 | 0 | 0 | 1.3 | 17.1 | 0 | 0 | 0 | 0 | 85.3401 | 33.886 | 0 | 84.0471 | 27% | 0 | 0 | 10% | 0 | 31.1308
6511 | 189 | 54 | 29 | 1.8 | 17.6 | 0 | 28.0322 | 0 | 0 | 90.8065 | 36.1533 | 0 | 90.6968 | 20% | 0 | 0 | 10% | 0 | 33.3926
6512 | 530 | 237 | 81 | 1.2 | 20.4 | 78.9537 | 19.5089 | 15.6022 | 0 | 55.4719 | 20.5655 | 33.3893 | 10.15 | 22% | 0 | 0 | 10% | 0 | 34.6168
6513 | 688 | 435 | 111 | 1.2 | 24 | 161.4527 | 0 | 37.2841 | 0 | 44.7854 | 15.7389 | 116.5032 | 0 | 31% | 15.7007 | 0 | 31.35% | 0 | 35.4568
6514 | 775 | 608 | 129 | 2.7 | 24.6 | 202.4009 | 0 | 48.814 | 8.074 | 42.5488 | 14.7767 | 160.0445 | 0 | 43% | 25 | 0 | 65.35% | 0 | 36.352
6515 | 831 | 732 | 132 | 2.6 | 25.5 | 228.7218 | 0 | 42.2823 | 27.6993 | 42.5706 | 14.7114 | 186.4806 | 0 | 56% | 18.1228 | 0 | 90% | 0 | 36.3747
6516 | 873 | 800 | 122 | 2 | 27.3 | 245.592 | 0 | 23.1631 | 51.9369 | 42.5799 | 14.5629 | 203.3271 | 0 | 71% | 0 | 0 | 90% | 0 | 35.0594
6517 | 885 | 799 | 113 | 2.2 | 28.2 | 249.1912 | 0 | 20.3053 | 54.7947 | 42.5874 | 14.4869 | 206.8708 | 0 | 86% | 0 | 0 | 90% | 0 | 34.3267
6518 | 860 | 730 | 110 | 2.2 | 29.6 | 237.6083 | 0 | 16.0066 | 53.2401 | 42.592 | 14.364 | 195.3429 | 0 | 100% | 0 | 0 | 90% | 0 | 34.0614
6519 | 794 | 600 | 110 | 2.5 | 30 | 41.3516 | 192.8981 | 19.144 | 35.5782 | 42.5946 | 14.3293 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.1827
6520 | 705 | 428 | 97 | 3.2 | 29.6 | 42.1517 | 145.1428 | 19.7578 | 16.3883 | 42.5923 | 14.3641 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.8313
6521 | 554 | 233 | 70 | 3.8 | 27.5 | 42.1573 | 73.2173 | 15.0445 | 0 | 42.5901 | 14.549 | 0 | 0 | 100% | 0 | 8.0992 | 77.04% | 0 | 38.4025
6522 | 175 | 48 | 27 | 3.6 | 25.8 | 0 | 24.6446 | 0 | 0 | 45.9355 | 16.067 | 0 | 44.4104 | 97% | 0 | 24.9343 | 37.15% | 0 | 38.9379
6523 | 0 | 0 | 0 | 2.9 | 22.9 | 0 | 0 | 0 | 0 | 60.4164 | 22.5758 | 0 | 60.1488 | 93% | 0 | 16.9665 | 10% | 0 | 36.6224
6524 | 0 | 0 | 0 | 1 | 21.6 | 0 | 0 | 0 | 0 | 93.3608 | 36.924 | 0 | 93.7982 | 86% | 0 | 0 | 10% | 0 | 34.2241
6525 | 0 | 0 | 0 | 0.8 | 20.9 | 0 | 0 | 0 | 0 | 87.6304 | 34.5704 | 0 | 86.049 | 79% | 0 | 0 | 10% | 0 | 32.0767
6526 | 0 | 0 | 0 | 0.4 | 20.3 | 0 | 0 | 0 | 0 | 83.6047 | 32.9355 | 0 | 81.3208 | 73% | 0 | 0 | 10% | 0 | 30.4219
6527 | 0 | 0 | 0 | 0.7 | 19.2 | 0 | 0 | 0 | 0 | 81.1908 | 31.9385 | 0 | 78.9608 | 68% | 0 | 0 | 10% | 0 | 29.3644
6528 | 0 | 0 | 0 | 0.7 | 18.5 | 0 | 0 | 0 | 0 | 80.1528 | 31.516 | 0 | 78.0374 | 62% | 0 | 0 | 10% | 0 | 28.8958
6529 | 0 | 0 | 0 | 0.6 | 18.5 | 0 | 0 | 0 | 0 | 80.3911 | 31.6246 | 0 | 78.3676 | 56% | 0 | 0 | 10% | 0 | 28.9705
6530 | 0 | 0 | 0 | 0.8 | 18 | 0 | 0 | 0 | 0 | 82.0792 | 32.4267 | 0 | 80.1464 | 50% | 0 | 0 | 10% | 0 | 29.7456
6531 | 0 | 0 | 0 | 0.5 | 17.2 | 0 | 0 | 0 | 0 | 90.6686 | 36.1216 | 0 | 90.3977 | 43% | 0 | 0 | 10% | 0 | 33.4105
6532 | 0 | 0 | 0 | 1.7 | 18.2 | 0 | 0 | 0 | 0 | 102.6732 | 41.0833 | 0 | 104.863 | 36% | 0 | 0 | 10% | 0 | 38.3912
6533 | 0 | 0 | 0 | 1.4 | 17.4 | 0 | 0 | 0 | 0 | 107.24 | 43.052 | 0 | 109.972 | 27% | 0 | 0 | 10% | 0 | 40.4521
6534 | 0 | 0 | 0 | 0.8 | 15.8 | 0 | 0 | 0 | 0 | 110.6552 | 44.5977 | 0 | 113.6038 | 19% | 0 | 0 | 10% | 0 | 42.0908
6535 | 286 | 57 | 22 | 0.9 | 17.5 | 0 | 40.9399 | 0 | 0 | 113.6584 | 45.7091 | 0 | 116.793 | 10% | 0 | 0 | 10% | 0 | 43.2873
6536 | 692 | 250 | 52 | 0.6 | 22.4 | 107.1708 | 26.151 | 18.3181 | 0 | 72.0445 | 27.6186 | 47.6147 | 12.7672 | 13% | 0 | 0 | 10% | 0 | 44.1901
6537 | 839 | 455 | 67 | 0.9 | 25.1 | 200.3664 | 2.98e-14 | 40.955 | 0 | 45.1065 | 15.7801 | 155.8339 | 0 | 24% | 9.2686 | 0 | 22.61% | 0 | 45.2396
6538 | 906 | 627 | 76 | 2.3 | 25 | 239.4857 | 0 | 58.5847 | 1.7932 | 42.5728 | 14.7532 | 197.8442 | 0 | 39% | 25 | 0 | 56.61% | 0 | 45.7442
6539 | 928 | 746 | 85 | 2 | 26 | 257.6841 | 0 | 57.335 | 15.9052 | 42.59 | 14.677 | 216.1351 | 0 | 55% | 24.5549 | 0 | 90% | 0 | 44.672
6540 | 937 | 808 | 89 | 1.8 | 28.5 | 264.7064 | 0 | 32.4083 | 42.6917 | 42.5978 | 14.4638 | 223.1246 | 0 | 72% | 0 | 0 | 90% | 0 | 43.9957
6541 | 927 | 804 | 92 | 2.3 | 29.4 | 261.502 | 0 | 32.457 | 42.643 | 42.6018 | 14.3851 | 219.7732 | 0 | 88% | 0 | 0 | 90% | 0 | 43.9722
6542 | 910 | 746 | 96 | 2.9 | 30.3 | 202.7921 | 56.2153 | 28.3051 | 43.3794 | 42.6039 | 14.3054 | 160.9 | 0 | 100% | 0 | 0 | 90% | 0 | 43.9831
6543 | 784 | 591 | 112 | 3.3 | 30.2 | 42.1516 | 188.5335 | 28.082 | 26.0385 | 42.6039 | 14.3144 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.1056
6544 | 766 | 442 | 88 | 4.1 | 29.3 | 42.1572 | 161.7126 | 27.896 | 10.3055 | 42.6013 | 14.3939 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.9993
6545 | 429 | 206 | 76 | 3.9 | 26.5 | 42.1574 | 40.9308 | 11.9079 | 0 | 42.5988 | 14.6377 | 0 | 0 | 100% | 0 | 18.3592 | 60.62% | 0 | 45.6149
6546 | 48 | 39 | 33 | 2.5 | 23.1 | 0 | 6.319 | 0 | 0 | 57.9985 | 21.4325 | 0 | 56.5122 | 96% | 0 | 25 | 20.62% | 0 | 44.3564
6547 | 0 | 0 | 0 | 1.5 | 21.3 | 0 | 0 | 0 | 0 | 92.2176 | 36.2632 | 0 | 95.079 | 89% | 0 | 6.6408 | 10% | 0 | 39.9541
6548 | 0 | 0 | 0 | 0.7 | 20.3 | 0 | 0 | 0 | 0 | 98.016 | 38.9697 | 0 | 98.2103 | 82% | 0 | 0 | 10% | 0 | 36.5849
6549 | 0 | 0 | 0 | 1.4 | 20.3 | 0 | 0 | 0 | 0 | 93.5976 | 37.1304 | 0 | 92.5517 | 75% | 0 | 0 | 10% | 0 | 34.864
6550 | 0 | 0 | 0 | 2 | 20.7 | 0 | 0 | 0 | 0 | 89.4884 | 35.3654 | 0 | 87.5093 | 68% | 0 | 0 | 10% | 0 | 33.1018
6551 | 0 | 0 | 0 | 1.6 | 20.4 | 0 | 0 | 0 | 0 | 86.9249 | 34.3138 | 0 | 84.5914 | 62% | 0 | 0 | 10% | 0 | 32.0009
6552 | 0 | 0 | 0 | 1.2 | 19.4 | 0 | 0 | 0 | 0 | 85.6991 | 33.8758 | 0 | 83.3108 | 55% | 0 | 0 | 10% | 0 | 31.5053
6553 | 0 | 0 | 0 | 0.6 | 18.3 | 0 | 0 | 0 | 0 | 85.4835 | 33.8635 | 0 | 83.2071 | 49% | 0 | 0 | 10% | 0 | 31.4415
6554 | 0 | 0 | 0 | 0.2 | 17.4 | 0 | 0 | 0 | 0 | 87.1603 | 34.6284 | 0 | 85.3243 | 43% | 0 | 0 | 10% | 0 | 32.1635
6555 | 0 | 0 | 0 | 0.9 | 17.7 | 0 | 0 | 0 | 0 | 94.5723 | 37.7361 | 0 | 94.4549 | 36% | 0 | 0 | 10% | 0 | 35.2387
6556 | 0 | 0 | 0 | 1.1 | 17.4 | 0 | 0 | 0 | 0 | 105.8543 | 42.4779 | 0 | 107.8719 | 28% | 0 | 0 | 10% | 0 | 39.9923
6557 | 0 | 0 | 0 | 0.4 | 16.3 | 0 | 0 | 0 | 0 | 110.748 | 44.5961 | 0 | 113.319 | 19% | 0 | 0 | 10% | 0 | 42.1806
6558 | 0 | 0 | 0 | 0.3 | 16.3 | 0 | 0 | 0 | 0 | 113.9107 | 45.9139 | 0 | 116.7336 | 10% | 0 | 0 | 10% | 0 | 43.5725
6559 | 36 | 37 | 34 | 1.6 | 18.7 | 0 | 4.9662 | 0 | 0 | 117.0716 | 47.0217 | 0 | 120.1755 | 1% | 0 | 0 | 10% | 0 | 44.7491
6560 | 58 | 134 | 116 | 0.7 | 19.7 | 0 | 13.2272 | 3.786 | 0 | 17.8237 | 7.1301 | 0 | 18.044 | 0% | 0 | 0 | 10% | 0 | 8.8643
6561 | 229 | 365 | 256 | 0.9 | 23 | 0 | 52.4748 | 25.2674 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 23.2592
6562 | 375 | 604 | 361 | 1 | 26.1 | 89.2921 | 0 | 47.674 | 1.1837 | 0 | 0 | 86.0144 | 0 | 7% | 0 | 0 | 10% | 0 | 46.4834
6563 | 859 | 860 | 246 | 2.2 | 27.5 | 236.6965 | 0 | 73.0031 | 2.0969 | 0 | 0 | 232.9646 | 0 | 24% | 25 | 0 | 44% | 0 | 45.4919
6564 | 914 | 804 | 106 | 2.1 | 26.8 | 257.4222 | 0 | 72.406 | 2.694 | 0 | 0 | 255.8536 | 0 | 44% | 25 | 0 | 78% | 0 | 44.6478
6565 | 919 | 797 | 96 | 2.3 | 28.1 | 258.7795 | 0 | 56.3414 | 18.7586 | 0 | 0 | 257.5109 | 0 | 63% | 8.8235 | 0 | 90% | 0 | 44.6835
6566 | 896 | 730 | 95 | 2.2 | 29.5 | 247.514 | 0 | 47.5273 | 23.0802 | 0 | 0 | 246.3533 | 0 | 82% | 0 | 0 | 90% | 0 | 44.7608
6567 | 838 | 600 | 93 | 2.8 | 30.1 | 219.3066 | 0 | 45.3902 | 10.6148 | 42.5939 | 1.4709 | 178.5087 | 0 | 95% | 0 | 0 | 90% | 0 | 43.8702
6568 | 372 | 309 | 126 | 2.5 | 29 | 78.1913 | 0 | 21.6816 | 0 | 42.5959 | 14.4187 | 37.3162 | 0 | 98% | 0 | 7.8645 | 77.42% | 0 | 43.6401
6569 | 73 | 146 | 125 | 1.6 | 28.6 | 0 | 16.4979 | 4.631 | 0 | 52.7656 | 18.6796 | 0 | 51.2464 | 94% | 0 | 25 | 37.42% | 0 | 46.2267
6570 | 10 | 22 | 22 | 3.6 | 28.7 | 0 | 1.2252 | 0 | 0 | 81.6726 | 30.9091 | 0 | 83.1215 | 88% | 0 | 17.1355 | 10% | 0 | 45.0851
6571 | 0 | 0 | 0 | 3.1 | 27.9 | 0 | 0 | 0 | 0 | 110.7547 | 43.4472 | 0 | 114.3447 | 80% | 0 | 0 | 10% | 0 | 40.8432
6572 | 0 | 0 | 0 | 2.3 | 26.1 | 0 | 0 | 0 | 0 | 101.2205 | 39.7407 | 0 | 101.328 | 72% | 0 | 0 | 10% | 0 | 37.5339
6573 | 0 | 0 | 0 | 1.9 | 24.6 | 0 | 0 | 0 | 0 | 96.0055 | 37.7437 | 0 | 94.9136 | 65% | 0 | 0 | 10% | 0 | 35.6052
6574 | 0 | 0 | 0 | 3.5 | 24.5 | 0 | 0 | 0 | 0 | 91.9501 | 36.0604 | 0 | 90.077 | 58% | 0 | 0 | 10% | 0 | 33.915
6575 | 0 | 0 | 0 | 3.1 | 23.2 | 0 | 0 | 0 | 0 | 88.9649 | 34.9327 | 0 | 86.5919 | 52% | 0 | 0 | 10% | 0 | 32.7478
6576 | 0 | 0 | 0 | 2.9 | 22.2 | 0 | 0 | 0 | 0 | 86.9699 | 34.1873 | 0 | 84.3771 | 45% | 0 | 0 | 10% | 0 | 31.9498
6577 | 0 | 0 | 0 | 1.5 | 20.7 | 0 | 0 | 0 | 0 | 86.4123 | 34.0772 | 0 | 83.8803 | 39% | 0 | 0 | 10% | 0 | 31.7851
6578 | 0 | 0 | 0 | 2.1 | 18.7 | 0 | 0 | 0 | 0 | 87.563 | 34.7078 | 0 | 85.3906 | 33% | 0 | 0 | 10% | 0 | 32.3672
6579 | 0 | 0 | 0 | 2.7 | 19.2 | 0 | 0 | 0 | 0 | 94.6962 | 37.6767 | 0 | 94.177 | 25% | 0 | 0 | 10% | 0 | 35.2927
6580 | 0 | 0 | 0 | 2.6 | 18.6 | 0 | 0 | 0 | 0 | 105.3242 | 42.1647 | 0 | 106.8399 | 17% | 0 | 0 | 10% | 0 | 39.7747
6581 | 0 | 0 | 0 | 1.9 | 17.8 | 0 | 0 | 0 | 0 | 109.9773 | 44.155 | 0 | 112.0747 | 9% | 0 | 0 | 10% | 0 | 41.8112
6582 | 0 | 0 | 0 | 2.2 | 17 | 0 | 0 | 0 | 0 | 112.9876 | 45.4729 | 0 | 115.3863 | 0% | 0 | 0 | 10% | 0 | 43.1825
6583 | 217 | 64 | 41 | 2.6 | 18.6 | 0 | 28.8019 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0706
6584 | 305 | 191 | 98 | 1.5 | 19.6 | 0 | 58.4701 | 10.3112 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 8.2615
6585 | 614 | 426 | 143 | 0.8 | 23.7 | 141.5395 | 0 | 36.6545 | 0 | 0 | 0 | 136.3053 | 0 | 11% | 0 | 0 | 10% | 0 | 35.0167
6586 | 794 | 598 | 117 | 1.2 | 25.1 | 207.9339 | 0 | 56.5852 | 0 | 0 | 0 | 205.6946 | 0 | 26% | 9.4097 | 0 | 22.8% | 0 | 44.906
6587 | 949 | 744 | 76 | 1.1 | 27.7 | 263.796 | 0 | 72.4242 | 1.2508 | 0 | 0 | 262.0377 | 0 | 46% | 25 | 0 | 56.8% | 0 | 44.6078
6588 | 955 | 805 | 81 | 1.5 | 29.1 | 269.9368 | 0 | 71.2323 | 3.8677 | 0 | 0 | 268.6124 | 0 | 66% | 24.4139 | 0 | 90% | 0 | 43.8877
6589 | 943 | 798 | 83 | 1.6 | 29.8 | 266.2269 | 0 | 46.4972 | 28.6028 | 0 | 0 | 265.0245 | 0 | 86% | 0 | 0 | 90% | 0 | 43.5473
6590 | 888 | 717 | 93 | 3 | 29.9 | 180.1932 | 70.3106 | 45.463 | 24.1634 | 0 | 0 | 179.3972 | 0 | 100% | 0 | 0 | 90% | 0 | 43.2781
6591 | 854 | 596 | 86 | 4 | 29.4 | 41.1157 | 210.5181 | 43.1784 | 13.3042 | 42.5945 | 0.12527 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.4583
6592 | 703 | 409 | 86 | 4.3 | 28.4 | 42.1573 | 142.8558 | 27.1002 | 7.8997 | 42.5922 | 14.4708 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.2806
6593 | 146 | 129 | 82 | 3.5 | 26.1 | 0 | 32.8212 | 4.3264 | 0 | 50.323 | 17.878 | 0 | 48.789 | 96% | 0 | 25 | 50% | 0 | 45.1309
6594 | 11 | 19 | 17 | 1.8 | 23.9 | 0 | 1.248 | 0 | 0 | 59.2486 | 21.9038 | 0 | 57.6552 | 92% | 0 | 25 | 10% | 0 | 43.9669
6595 | 0 | 0 | 0 | 4.1 | 21.7 | 0 | 0 | 0 | 0 | 107.6894 | 42.8743 | 0 | 112.1061 | 84% | 0 | 0 | 10% | 0 | 39.93
6596 | 0 | 0 | 0 | 4.1 | 21.1 | 0 | 0 | 0 | 0 | 98.3135 | 39.0279 | 0 | 98.4454 | 77% | 0 | 0 | 10% | 0 | 36.6724
6597 | 0 | 0 | 0 | 1.8 | 20.1 | 0 | 0 | 0 | 0 | 93.7799 | 37.2242 | 0 | 92.7637 | 70% | 0 | 0 | 10% | 0 | 34.9599
6598 | 0 | 0 | 0 | 1.3 | 19.4 | 0 | 0 | 0 | 0 | 89.9662 | 35.6662 | 0 | 88.0698 | 63% | 0 | 0 | 10% | 0 | 33.4054
6599 | 0 | 0 | 0 | 2 | 19 | 0 | 0 | 0 | 0 | 87.4777 | 34.65 | 0 | 85.2034 | 57% | 0 | 0 | 10% | 0 | 32.3493
6600 | 0 | 0 | 0 | 1.9 | 18.4 | 0 | 0 | 0 | 0 | 86.02 | 34.0815 | 0 | 83.621 | 50% | 0 | 0 | 10% | 0 | 31.7311
6601 | 0 | 0 | 0 | 2.2 | 18.3 | 0 | 0 | 0 | 0 | 85.7211 | 33.9636 | 0 | 83.409 | 44% | 0 | 0 | 10% | 0 | 31.5651
6602 | 0 | 0 | 0 | 1.7 | 18.1 | 0 | 0 | 0 | 0 | 87.0162 | 34.5208 | 0 | 85.0675 | 38% | 0 | 0 | 10% | 0 | 32.0809
6603 | 0 | 0 | 0 | 1.7 | 17.2 | 0 | 0 | 0 | 0 | 93.4662 | 37.3076 | 0 | 93.0292 | 31% | 0 | 0 | 10% | 0 | 34.8333
6604 | 0 | 0 | 0 | 1.3 | 16 | 0 | 0 | 0 | 0 | 103.8361 | 41.7409 | 0 | 105.3839 | 23% | 0 | 0 | 10% | 0 | 39.2679
6605 | 0 | 0 | 0 | 0.7 | 15.2 | 0 | 0 | 0 | 0 | 108.2228 | 43.6323 | 0 | 110.342 | 15% | 0 | 0 | 10% | 0 | 41.2135
6606 | 0 | 0 | 0 | 1.1 | 14.8 | 0 | 0 | 0 | 0 | 110.9107 | 44.782 | 0 | 113.2317 | 6% | 0 | 0 | 10% | 0 | 42.4241
6607 | 153 | 39 | 18 | 1.2 | 15.5 | 0 | 19.5046 | 0 | 0 | 79.2958 | 31.9936 | 0 | 80.9363 | 0% | 0 | 0 | 10% | 0 | 29.7538
6608 | 662 | 237 | 54 | 0.8 | 19.5 | 100.7247 | 24.8374 | 17.9541 | 0 | 0 | 0 | 97.2508 | 0 | 7% | 0 | 0 | 10% | 0 | 16.3629
6609 | 818 | 438 | 68 | 1.3 | 23.2 | 193.918 | 0 | 40.4055 | 0 | 0 | 0 | 191.7038 | 0 | 22% | 0 | 0 | 10% | 0 | 38.2729
6610 | 884 | 608 | 80 | 3.6 | 25 | 232.0417 | 0 | 59.4011 | 0 | 0 | 0 | 230.4744 | 0 | 39% | 13.5065 | 0 | 28.37% | 0 | 43.3837
6611 | 914 | 735 | 94 | 3.4 | 26.3 | 252.2074 | 0 | 71.3086 | 1.7102 | 0 | 0 | 250.8638 | 0 | 58% | 25 | 0 | 62.37% | 0 | 43.5689
6612 | 826 | 772 | 147 | 3.4 | 27.2 | 230.0839 | 0 | 65.801 | 9.299 | 0 | 0 | 228.9896 | 0 | 75% | 20.317 | 0 | 90% | 0 | 42.8978
6613 | 909 | 790 | 105 | 5.1 | 27.3 | 253.6108 | 0 | 45.5545 | 29.5455 | 0 | 0 | 252.3453 | 0 | 94% | 0 | 0 | 90% | 0 | 42.7093
6614 | 760 | 692 | 158 | 6.4 | 26.9 | 73.3253 | 144.9926 | 43.6658 | 23.282 | 0 | 0 | 72.9974 | 0 | 100% | 0 | 0 | 90% | 0 | 42.3504
6615 | 616 | 570 | 200 | 5.7 | 26.7 | 41.0407 | 136.3873 | 41.9521 | 9.8591 | 42.5972 | 0.93459 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8768
6616 | 666 | 430 | 131 | 5.1 | 26.4 | 42.1574 | 131.6728 | 26.5787 | 10.3442 | 42.5949 | 14.6448 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.9336
6617 | 358 | 189 | 87 | 4.6 | 25.5 | 0 | 66.9 | 10.5392 | 0 | 42.5919 | 14.7187 | 0 | 41.1006 | 97% | 0 | 21.4975 | 55.6% | 0 | 44.6782
6618 | 52 | 26 | 21 | 4.4 | 23.3 | 0 | 5.4322 | 0 | 0 | 58.1727 | 21.4978 | 0 | 56.5322 | 93% | 0 | 25 | 15.6% | 0 | 43.5759
6619 | 0 | 0 | 0 | 2.3 | 21.5 | 0 | 0 | 0 | 0 | 98.2766 | 38.8697 | 0 | 101.5978 | 85% | 0 | 3.5025 | 10% | 0 | 39.4421
6620 | 0 | 0 | 0 | 0.9 | 20.1 | 0 | 0 | 0 | 0 | 97.4775 | 38.7623 | 0 | 97.6867 | 78% | 0 | 0 | 10% | 0 | 36.3447
6621 | 0 | 0 | 0 | 1 | 18.8 | 0 | 0 | 0 | 0 | 93.1814 | 37.0678 | 0 | 92.1872 | 71% | 0 | 0 | 10% | 0 | 34.7567
6622 | 0 | 0 | 0 | 1.6 | 18.4 | 0 | 0 | 0 | 0 | 89.2536 | 35.4386 | 0 | 87.3517 | 65% | 0 | 0 | 10% | 0 | 33.1355
6623 | 0 | 0 | 0 | 1.5 | 17.5 | 0 | 0 | 0 | 0 | 86.4979 | 34.3431 | 0 | 84.1737 | 58% | 0 | 0 | 10% | 0 | 32.0007
6624 | 0 | 0 | 0 | 2.6 | 18.5 | 0 | 0 | 0 | 0 | 85.6037 | 33.9 | 0 | 83.2697 | 52% | 0 | 0 | 10% | 0 | 31.5056
6625 | 0 | 0 | 0 | 1.1 | 16.5 | 0 | 0 | 0 | 0 | 85.3699 | 33.9366 | 0 | 83.1258 | 46% | 0 | 0 | 10% | 0 | 31.4965
6626 | 0 | 0 | 0 | 1.6 | 17.4 | 0 | 0 | 0 | 0 | 86.446 | 34.3289 | 0 | 84.5125 | 40% | 0 | 0 | 10% | 0 | 31.8505
6627 | 0 | 0 | 0 | 1 | 16.3 | 0 | 0 | 0 | 0 | 93.2828 | 37.2922 | 0 | 92.9345 | 33% | 0 | 0 | 10% | 0 | 34.7803
6628 | 0 | 0 | 0 | 0.8 | 15.3 | 0 | 0 | 0 | 0 | 104.1229 | 41.914 | 0 | 105.8722 | 25% | 0 | 0 | 10% | 0 | 39.4068
6629 | 0 | 0 | 0 | 1 | 15.3 | 0 | 0 | 0 | 0 | 108.1163 | 43.5802 | 0 | 110.3288 | 16% | 0 | 0 | 10% | 0 | 41.1354
6630 | 0 | 0 | 0 | 1.1 | 15.6 | 0 | 0 | 0 | 0 | 111.4382 | 44.94 | 0 | 113.9578 | 8% | 0 | 0 | 10% | 0 | 42.5594
6631 | 256 | 55 | 26 | 0.5 | 16.4 | 0 | 31.2861 | 0 | 0 | 102.0877 | 41.144 | 0 | 104.5226 | 0% | 0 | 0 | 10% | 0 | 38.8492
6632 | 654 | 230 | 50 | 0.3 | 20.6 | 99.3057 | 24.36 | 17.3364 | 0 | 0 | 0 | 95.9093 | 0 | 7% | 0 | 0 | 10% | 0 | 15.7579
6633 | 835 | 436 | 61 | 0.7 | 24 | 198.3374 | -2.98e-14 | 40.5817 | 0 | 0 | 0 | 196.0671 | 0 | 22% | 0 | 0 | 10% | 0 | 38.4106
6634 | 907 | 607 | 68 | 0.5 | 27.2 | 240.1382 | 0 | 59.4103 | 0 | 0 | 0 | 238.561 | 0 | 40% | 12.7684 | 0 | 27.37% | 0 | 44.0572
6635 | 946 | 731 | 72 | 2.1 | 28.1 | 262.087 | 0 | 71.8922 | 1.0771 | 0 | 0 | 260.7469 | 0 | 60% | 25 | 0 | 61.37% | 0 | 44.0587
6636 | 955 | 790 | 75 | 3.3 | 28.7 | 268.9672 | 0 | 66.9926 | 8.1074 | 0 | 0 | 267.771 | 0 | 80% | 21.0551 | 0 | 90% | 0 | 42.9785
6637 | 947 | 784 | 76 | 5.3 | 29 | 264.7272 | 0 | 45.5547 | 29.5453 | 0 | 0 | 263.6061 | 0 | 100% | 0 | 0 | 90% | 0 | 42.5891
6638 | 925 | 717 | 75 | 6 | 28.9 | 0 | 278.4512 | 43.372 | 27.5159 | 0 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.2175
6639 | 877 | 590 | 73 | 5.9 | 28.7 | 40.9184 | 216.9367 | 41.5624 | 15.1864 | 42.5977 | 1.1537 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.4775
6640 | 800 | 418 | 64 | 6.1 | 28.3 | 42.1581 | 168.7095 | 26.2313 | 11.2658 | 42.5955 | 14.4808 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.4217
6641 | 629 | 216 | 48 | 5.3 | 27.6 | 42.1573 | 86.3015 | 15.16 | 0 | 42.5931 | 14.5414 | 0 | 0 | 100% | 0 | 13.368 | 68.61% | 0 | 43.7792
6642 | 152 | 35 | 16 | 3.9 | 25.4 | 0 | 14.5242 | 0 | 0 | 54.1727 | 19.5992 | 0 | 52.6452 | 96% | 0 | 25 | 28.61% | 0 | 42.5221
6643 | 0 | 0 | 0 | 3.2 | 23 | 0 | 0 | 0 | 0 | 78.0732 | 30.0783 | 0 | 79.4545 | 90% | 0 | 11.632 | 10% | 0 | 38.7647
6644 | 0 | 0 | 0 | 1.9 | 20.8 | 0 | 0 | 0 | 0 | 97.4371 | 38.6883 | 0 | 98.0987 | 83% | 0 | 0 | 10% | 0 | 36.1486
6645 | 0 | 0 | 0 | 0.5 | 19.5 | 0 | 0 | 0 | 0 | 93.5708 | 37.1806 | 0 | 92.8461 | 76% | 0 | 0 | 10% | 0 | 34.822
6646 | 0 | 0 | 0 | 0.3 | 18.5 | 0 | 0 | 0 | 0 | 88.7954 | 35.2385 | 0 | 86.8871 | 69% | 0 | 0 | 10% | 0 | 32.9117
6647 | 0 | 0 | 0 | 1.1 | 17.5 | 0 | 0 | 0 | 0 | 85.3325 | 33.8543 | 0 | 82.8895 | 63% | 0 | 0 | 10% | 0 | 31.4848
6648 | 0 | 0 | 0 | 0.8 | 16.9 | 0 | 0 | 0 | 0 | 83.4174 | 33.0926 | 0 | 80.8211 | 57% | 0 | 0 | 10% | 0 | 30.6621
6649 | 0 | 0 | 0 | 0.3 | 16.7 | 0 | 0 | 0 | 0 | 82.6049 | 32.75 | 0 | 80.1047 | 51% | 0 | 0 | 10% | 0 | 30.2612
6650 | 0 | 0 | 0 | 0.8 | 16.8 | 0 | 0 | 0 | 0 | 82.2141 | 32.5658 | 0 | 79.8409 | 45% | 0 | 0 | 10% | 0 | 30.0301
6651 | 0 | 0 | 0 | 1.7 | 17.4 | 0 | 0 | 0 | 0 | 84.1224 | 33.3555 | 0 | 82.0627 | 39% | 0 | 0 | 10% | 0 | 30.7803
6652 | 0 | 0 | 0 | 1.6 | 17.1 | 0 | 0 | 0 | 0 | 88.0088 | 35.0068 | 0 | 86.7801 | 33% | 0 | 0 | 10% | 0 | 32.4022
6653 | 0 | 0 | 0 | 1.7 | 17.5 | 0 | 0 | 0 | 0 | 91.1176 | 36.2913 | 0 | 90.5736 | 26% | 0 | 0 | 10% | 0 | 33.683
6654 | 0 | 0 | 0 | 1.4 | 16.8 | 0 | 0 | 0 | 0 | 97.6017 | 39.0663 | 0 | 98.3693 | 19% | 0 | 0 | 10% | 0 | 36.4647
6655 | 226 | 45 | 20 | 1.7 | 16.6 | 0 | 26.4236 | 0 | 0 | 102.3983 | 41.0919 | 0 | 103.9751 | 11% | 0 | 0 | 10% | 0 | 38.5264
6656 | 646 | 227 | 51 | 0.8 | 21.7 | 97.5501 | 23.9133 | 17.1747 | 0 | 63.4061 | 23.8805 | 45.1187 | 11.3688 | 13% | 0 | 0 | 10% | 0 | 39.3749
6657 | 804 | 426 | 66 | 0.9 | 25 | 190.083 | 0 | 39.3435 | 0 | 45.2942 | 15.8664 | 145.0089 | 0 | 24% | 13.3893 | 0 | 28.21% | 0 | 39.697
6658 | 881 | 597 | 73 | 0.8 | 27.6 | 232.6131 | 0 | 53.038 | 5.0354 | 42.5654 | 14.5319 | 190.6564 | 0 | 38% | 25 | 0 | 62.21% | 0 | 40.0537
6659 | 916 | 717 | 79 | 1.6 | 28.8 | 253.5197 | 0 | 47.7005 | 23.4284 | 42.5864 | 14.4333 | 211.6949 | 0 | 54% | 20.4343 | 0 | 90% | 0 | 38.9664
6660 | 930 | 779 | 82 | 2.4 | 29.5 | 262.0514 | 0 | 25.707 | 49.393 | 42.5942 | 14.3737 | 220.2185 | 0 | 70% | 0 | 0 | 90% | 0 | 37.2465
6661 | 927 | 780 | 86 | 3.6 | 29.7 | 260.3968 | 0 | 24.7843 | 50.3157 | 42.5991 | 14.3576 | 218.4541 | 0 | 86% | 0 | 0 | 90% | 0 | 36.2985
6662 | 855 | 698 | 104 | 2.3 | 30.3 | 234.5048 | 0 | 18.0324 | 49.7903 | 42.6017 | 14.3046 | 192.3819 | 0 | 100% | 0 | 0 | 90% | 0 | 35.8611
6663 | 684 | 536 | 129 | 2.9 | 30 | 41.3546 | 157.6267 | 20.4154 | 28.7166 | 42.6027 | 14.3321 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 35.4567
6664 | 432 | 320 | 128 | 2.5 | 29.2 | 42.1518 | 64.3401 | 20.9102 | 3.7999 | 42.6002 | 14.4024 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.022
6665 | 271 | 169 | 88 | 2.9 | 27.7 | 0 | 46.5516 | 7.9867 | 0 | 42.597 | 14.534 | 0 | 41.1015 | 97% | 0 | 18.3218 | 60.69% | 0 | 38.7631
6666 | 3 | 21 | 21 | 2.4 | 24.8 | 0 | 0.26019 | 0 | 0 | 46.5574 | 16.4004 | 0 | 44.9104 | 94% | 0 | 25 | 20.69% | 0 | 38.4916
6667 | 0 | 0 | 0 | 1.6 | 21.2 | 0 | 0 | 0 | 0 | 82.3756 | 32.1653 | 0 | 83.4695 | 88% | 0 | 6.6782 | 10% | 0 | 35.935
6668 | 0 | 0 | 0 | 0.2 | 20.1 | 0 | 0 | 0 | 0 | 90.8914 | 36.0029 | 0 | 90.3148 | 81% | 0 | 0 | 10% | 0 | 33.4183
6669 | 0 | 0 | 0 | 1.5 | 20.5 | 0 | 0 | 0 | 0 | 86.761 | 34.2372 | 0 | 85.0599 | 75% | 0 | 0 | 10% | 0 | 31.7231
6670 | 0 | 0 | 0 | 1.7 | 19.8 | 0 | 0 | 0 | 0 | 82.6389 | 32.5539 | 0 | 80.3166 | 69% | 0 | 0 | 10% | 0 | 30.0166
6671 | 0 | 0 | 0 | 1.6 | 20 | 0 | 0 | 0 | 0 | 79.6636 | 31.1892 | 0 | 77.4609 | 63% | 0 | 0 | 10% | 0 | 28.5984
6672 | 0 | 0 | 0 | 1.2 | 18.7 | 0 | 0 | 0 | 0 | 78.2014 | 30.6212 | 0 | 76.0884 | 58% | 0 | 0 | 10% | 0 | 27.9915
6673 | 0 | 0 | 0 | 0.5 | 16.8 | 0 | 0 | 0 | 0 | 77.0553 | 30.2289 | 0 | 75.0063 | 52% | 0 | 0 | 10% | 0 | 27.5698
6674 | 0 | 0 | 0 | 0.6 | 16.7 | 0 | 0 | 0 | 0 | 77.0979 | 30.2548 | 0 | 75.1079 | 47% | 0 | 0 | 10% | 0 | 27.5718
6675 | 0 | 0 | 0 | 0.9 | 16 | 0 | 0 | 0 | 0 | 77.6835 | 30.5616 | 0 | 75.7461 | 41% | 0 | 0 | 10% | 0 | 27.8587
6676 | 0 | 0 | 0 | 2.3 | 17.4 | 0 | 0 | 0 | 0 | 79.4552 | 31.2747 | 0 | 77.5792 | 35% | 0 | 0 | 10% | 0 | 28.5543
6677 | 0 | 0 | 0 | 1 | 16.8 | 0 | 0 | 0 | 0 | 80.4682 | 31.773 | 0 | 78.6359 | 29% | 0 | 0 | 10% | 0 | 29.0387
6678 | 0 | 0 | 0 | 0.9 | 15.3 | 0 | 0 | 0 | 0 | 85.8253 | 34.2068 | 0 | 84.614 | 23% | 0 | 0 | 10% | 0 | 31.4541
6679 | 169 | 46 | 25 | 1.2 | 16.9 | 0 | 18.861 | 0 | 0 | 91.5798 | 36.53 | 0 | 91.6386 | 16% | 0 | 0 | 10% | 0 | 33.7727
6680 | 628 | 222 | 52 | 0.7 | 19.6 | 94.1452 | 23.1298 | 16.8781 | 0 | 53.75 | 19.8707 | 49.4535 | 9.7895 | 19% | 0 | 0 | 10% | 0 | 35.0724
6681 | 799 | 422 | 66 | 0.6 | 24.5 | 188.7523 | 0 | 39.2009 | 0 | 45.3705 | 15.939 | 143.1909 | 0 | 30% | 17.4497 | 0 | 33.73% | 0 | 35.5855
6682 | 882 | 594 | 73 | 0.7 | 27.6 | 232.9181 | 0 | 49.4103 | 8.7709 | 42.5559 | 14.5287 | 190.5744 | 0 | 44% | 25 | 0 | 67.73% | 0 | 36.428
6683 | 910 | 713 | 82 | 1.2 | 29.1 | 251.8521 | 0 | 40.7414 | 30.1508 | 42.5788 | 14.404 | 209.6809 | 0 | 59% | 16.3739 | 0 | 90% | 0 | 36.0601
6684 | 909 | 769 | 91 | 2 | 29.4 | 255.9832 | 0 | 22.8819 | 52.2181 | 42.5868 | 14.3801 | 213.8147 | 0 | 75% | 0 | 0 | 90% | 0 | 34.4925
6685 | 890 | 758 | 96 | 2.3 | 29.8 | 250.0939 | 0 | 19.2377 | 55.8623 | 42.5927 | 14.3465 | 207.828 | 0 | 90% | 0 | 0 | 90% | 0 | 33.6219
6686 | 871 | 692 | 93 | 2.3 | 29.9 | 176.1068 | 72.1022 | 17.43 | 50.6153 | 42.5965 | 14.3389 | 134.1456 | 0 | 100% | 0 | 0 | 90% | 0 | 33.2481
6687 | 831 | 569 | 84 | 3.8 | 29.4 | 42.1517 | 201.0954 | 18.042 | 36.3717 | 42.5966 | 14.3834 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 33.1348
6688 | 692 | 396 | 92 | 4.4 | 28.3 | 42.1573 | 137.6725 | 19.2035 | 15.4885 | 42.5943 | 14.4804 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.3935
6689 | 561 | 209 | 66 | 3.6 | 27.7 | 42.1573 | 68.7054 | 14.4844 | 0 | 42.5919 | 14.5323 | 0 | 0 | 100% | 0 | 8.4698 | 76.45% | 0 | 38.1963
6690 | 123 | 33 | 17 | 2.9 | 25.4 | 0 | 9.5947 | 0 | 0 | 44.8112 | 15.6337 | 0 | 43.2984 | 97% | 0 | 24.6641 | 36.99% | 0 | 38.2308
6691 | 0 | 0 | 0 | 1.7 | 22.5 | 0 | 0 | 0 | 0 | 59.3362 | 22.1492 | 0 | 58.9356 | 93% | 0 | 16.8662 | 10% | 0 | 36.0929
6692 | 0 | 0 | 0 | 0.3 | 20.9 | 0 | 0 | 0 | 0 | 92.3146 | 36.5403 | 0 | 92.5868 | 86% | 0 | 0 | 10% | 0 | 33.8106
6693 | 0 | 0 | 0 | 0.5 | 19.6 | 0 | 0 | 0 | 0 | 87.1893 | 34.4846 | 0 | 85.6666 | 79% | 0 | 0 | 10% | 0 | 31.9444
6694 | 0 | 0 | 0 | 1.6 | 19.6 | 0 | 0 | 0 | 0 | 83.1087 | 32.7805 | 0 | 80.8535 | 73% | 0 | 0 | 10% | 0 | 30.2288
6695 | 0 | 0 | 0 | 2.3 | 20 | 0 | 0 | 0 | 0 | 81.1329 | 31.8551 | 0 | 79.0017 | 67% | 0 | 0 | 10% | 0 | 29.2472
6696 | 0 | 0 | 0 | 2.3 | 19.3 | 0 | 0 | 0 | 0 | 80.5201 | 31.6273 | 0 | 78.4872 | 62% | 0 | 0 | 10% | 0 | 28.9802
6697 | 0 | 0 | 0 | 1.4 | 19.9 | 0 | 0 | 0 | 0 | 80.9557 | 31.7829 | 0 | 79.0036 | 56% | 0 | 0 | 10% | 0 | 29.1069
6698 | 0 | 0 | 0 | 1.3 | 19.2 | 0 | 0 | 0 | 0 | 82.5234 | 32.5471 | 0 | 80.6511 | 50% | 0 | 0 | 10% | 0 | 29.848
6699 | 0 | 0 | 0 | 2 | 19.4 | 0 | 0 | 0 | 0 | 91.0954 | 36.1433 | 0 | 90.9761 | 43% | 0 | 0 | 10% | 0 | 33.417
6700 | 0 | 0 | 0 | 1.3 | 18.9 | 0 | 0 | 0 | 0 | 103.1541 | 41.2301 | 0 | 105.49 | 35% | 0 | 0 | 10% | 0 | 38.5276
6701 | 0 | 0 | 0 | 1.7 | 18 | 0 | 0 | 0 | 0 | 107.8881 | 43.2724 | 0 | 110.7641 | 27% | 0 | 0 | 10% | 0 | 40.6658
6702 | 0 | 0 | 0 | 2.5 | 19 | 0 | 0 | 0 | 0 | 110.9565 | 44.4604 | 0 | 113.9732 | 18% | 0 | 0 | 10% | 0 | 41.9507
6703 | 166 | 45 | 25 | 0.8 | 18.3 | 0 | 17.6404 | 0 | 0 | 112.7678 | 45.2711 | 0 | 115.7252 | 10% | 0 | 0 | 10% | 0 | 42.8495
6704 | 546 | 205 | 58 | 1.7 | 22.4 | 79.1276 | 19.5462 | 14.7509 | 0 | 78.4936 | 30.4848 | 15.2914 | 14.0156 | 10% | 0 | 0 | 10% | 0 | 43.7205
6705 | 700 | 397 | 93 | 0.5 | 26.6 | 162.9663 | 0 | 36.5604 | 0 | 44.7138 | 15.4913 | 118.7163 | 0 | 19% | 5.6716 | 0 | 17.71% | 0 | 44.4918
6706 | 847 | 582 | 88 | 0.9 | 28.3 | 222.6362 | 0 | 57.1423 | 0 | 43.8099 | 14.9707 | 179.6006 | 0 | 32% | 24.7799 | 0 | 51.41% | 0 | 44.9017
6707 | 887 | 703 | 94 | 1 | 30.2 | 244.7627 | 0 | 57.0957 | 12.9011 | 42.5869 | 14.3087 | 203.1896 | 0 | 47% | 25 | 0 | 85.41% | 0 | 43.7521
6708 | 872 | 751 | 107 | 1.5 | 31.4 | 244.8879 | 0 | 34.8244 | 39.7489 | 42.5973 | 14.2031 | 203.3491 | 0 | 63% | 3.372 | 0 | 90% | 0 | 42.9748
6709 | 900 | 753 | 91 | 3.4 | 31.3 | 252.3115 | 0 | 31.2804 | 43.3305 | 42.601 | 14.2135 | 210.6148 | 0 | 78% | 0 | 0 | 90% | 0 | 42.7257
6710 | 902 | 689 | 77 | 5.7 | 30.5 | 245.3581 | 0 | 30.2775 | 38.411 | 42.6035 | 14.2871 | 203.4999 | 0 | 93% | 0 | 0 | 90% | 0 | 42.6108
6711 | 785 | 549 | 94 | 5.8 | 30.3 | 136.0261 | 75.8417 | 26.5959 | 25.422 | 42.6046 | 14.3056 | 94.2318 | 0 | 100% | 0 | 0 | 90% | 0 | 41.9667
6712 | 600 | 389 | 132 | 4.4 | 29.6 | 42.152 | 110.947 | 27.3278 | 6.1342 | 42.6035 | 14.3679 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.405
6713 | 181 | 154 | 111 | 3.7 | 28.2 | 0 | 39.1228 | 6.9276 | 0 | 44.8284 | 15.3941 | 0 | 43.3155 | 97% | 0 | 24.6548 | 50.55% | 0 | 44.9075
6714 | 38 | 26 | 22 | 2.9 | 26.3 | 0 | 2.6369 | 0 | 0 | 59.7503 | 21.8919 | 0 | 58.1482 | 93% | 0 | 25 | 10.55% | 0 | 43.9633
6715 | 0 | 0 | 0 | 4 | 23 | 0 | 0 | 0 | 0 | 107.1209 | 42.5178 | 0 | 111.389 | 84% | 0 | 0 | 10.55% | 0 | 39.581
6716 | 0 | 0 | 0 | 4.2 | 20.5 | 0 | 0 | 0 | 0 | 97.3265 | 38.6665 | 0 | 97.2584 | 77% | 0 | 0 | 10.55% | 0 | 36.3155
6717 | 0 | 0 | 0 | 4.2 | 19.7 | 0 | 0 | 0 | 0 | 92.6396 | 36.7712 | 0 | 91.3782 | 70% | 0 | 0 | 10.55% | 0 | 34.4988
6718 | 0 | 0 | 0 | 3.3 | 19.5 | 0 | 0 | 0 | 0 | 88.5703 | 35.0712 | 0 | 86.456 | 64% | 0 | 0 | 10.55% | 0 | 32.7893
6719 | 0 | 0 | 0 | 2.5 | 18.4 | 0 | 0 | 0 | 0 | 85.934 | 34.0446 | 0 | 83.4684 | 58% | 0 | 0 | 10.55% | 0 | 31.713
6720 | 0 | 0 | 0 | 1.9 | 17.9 | 0 | 0 | 0 | 0 | 85.1574 | 33.7543 | 0 | 82.7232 | 51% | 0 | 0 | 10.55% | 0 | 31.3648
6721 | 0 | 0 | 0 | 1.8 | 18.3 | 0 | 0 | 0 | 0 | 84.729 | 33.548 | 0 | 82.3599 | 45% | 0 | 0 | 10.55% | 0 | 31.1101
6722 | 0 | 0 | 0 | 2.2 | 17.2 | 0 | 0 | 0 | 0 | 86.303 | 34.282 | 0 | 84.3453 | 39% | 0 | 0 | 10.55% | 0 | 31.8012
6723 | 0 | 0 | 0 | 3 | 17.8 | 0 | 0 | 0 | 0 | 93.561 | 37.304 | 0 | 93.2875 | 32% | 0 | 0 | 10.55% | 0 | 34.7887
6724 | 0 | 0 | 0 | 1.6 | 17.8 | 0 | 0 | 0 | 0 | 104.9485 | 42.0704 | 0 | 106.8847 | 24% | 0 | 0 | 10.55% | 0 | 39.5608
6725 | 0 | 0 | 0 | 1.7 | 17.4 | 0 | 0 | 0 | 0 | 109.1399 | 43.8396 | 0 | 111.525 | 16% | 0 | 0 | 10.55% | 0 | 41.3958
6726 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 0 | 0 | 112.0158 | 45.0676 | 0 | 114.6177 | 7% | 0 | 0 | 10.55% | 0 | 42.6916
6727 | 0 | 18 | 18 | 0.8 | 17.2 | 0 | 0 | 0 | 0 | 90.0295 | 36.2287 | 0 | 92.1152 | 0% | 0 | 0 | 10.55% | 0 | 33.9619
6728 | 0 | 96 | 96 | 1.2 | 18.6 | 0 | 0 | 0.66857 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.55% | 0 | -1.4256
6729 | 4 | 202 | 199 | 2.7 | 20.5 | 0 | 1.0962 | 7.2178 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.55% | 0 | 5.1424
6730 | 124 | 352 | 273 | 3.4 | 21.9 | 0 | 37.4797 | 24.1899 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.55% | 0 | 22.1328
6731 | 440 | 534 | 225 | 3.7 | 23 | 90.9757 | 22.404 | 46.4804 | 2.289 | 0 | 0 | 87.3834 | 0 | 7% | 0 | 0 | 10.55% | 0 | 44.985
6732 | 748 | 715 | 164 | 3.8 | 24.2 | 205.9666 | 0 | 71.3309 | 0.72466 | 0 | 0 | 202.9468 | 0 | 22% | 25 | 0 | 44.55% | 0 | 44.091
6733 | 761 | 692 | 135 | 3.1 | 24.6 | 210.2578 | 0 | 69.1086 | 0 | 0 | 0 | 208.7071 | 0 | 38% | 23.8266 | 0 | 76.96% | 0 | 42.963
6734 | 742 | 661 | 159 | 3.3 | 25.1 | 199.7875 | 0 | 55.3693 | 10.3411 | 0 | 0 | 198.4968 | 0 | 53% | 9.5908 | 0 | 90% | 0 | 43.5146
6735 | 606 | 500 | 152 | 3.1 | 25.2 | 151.7684 | 0 | 44.4901 | 1.7707 | 42.5727 | 1.042 | 111.075 | 0 | 61% | 0 | 0 | 90% | 0 | 43.2127
6736 | 574 | 346 | 108 | 2.6 | 25.1 | 126.8708 | 0 | 30.1133 | 0 | 43.1843 | 14.9922 | 85.3936 | 0 | 68% | 0 | 0 | 90% | 0 | 43.4832
6737 | 508 | 182 | 56 | 1.7 | 24.6 | 84.6029 | 1.49e-14 | 12.2627 | 0 | 42.5795 | 14.7874 | 43.7107 | 0 | 71% | 0 | 20.1725 | 57.72% | 0 | 45.9983
6738 | 72 | 24 | 15 | 2 | 22.1 | 0 | 4.3848 | 0 | 0 | 57.1297 | 21.1434 | 0 | 54.6569 | 67% | 0 | 25 | 17.72% | 0 | 44.5388
6739 | 0 | 0 | 0 | 1.6 | 20.2 | 0 | 0 | 0 | 0 | 95.7479 | 37.8835 | 0 | 97.6561 | 60% | 0 | 4.8275 | 10% | 0 | 40.0947
6740 | 0 | 0 | 0 | 1.7 | 18.9 | 0 | 0 | 0 | 0 | 98.3987 | 39.2395 | 0 | 98.9054 | 52% | 0 | 0 | 10% | 0 | 36.7694
6741 | 0 | 0 | 0 | 0.7 | 18.1 | 0 | 0 | 0 | 0 | 93.8355 | 37.398 | 0 | 93.2604 | 45% | 0 | 0 | 10% | 0 | 34.9959
6742 | 0 | 0 | 0 | 1.5 | 17.8 | 0 | 0 | 0 | 0 | 89.5243 | 35.5962 | 0 | 87.8812 | 39% | 0 | 0 | 10% | 0 | 33.2167
6743 | 0 | 0 | 0 | 1.1 | 17.9 | 0 | 0 | 0 | 0 | 86.3078 | 34.2373 | 0 | 84.0636 | 32% | 0 | 0 | 10% | 0 | 31.8449
6744 | 0 | 0 | 0 | 1.6 | 17 | 0 | 0 | 0 | 0 | 85.5236 | 33.9693 | 0 | 83.2252 | 26% | 0 | 0 | 10% | 0 | 31.5457
6745 | 0 | 0 | 0 | 1.1 | 17.1 | 0 | 0 | 0 | 0 | 85.256 | 33.8509 | 0 | 82.9958 | 20% | 0 | 0 | 10% | 0 | 31.3971
6746 | 0 | 0 | 0 | 0.6 | 16.5 | 0 | 0 | 0 | 0 | 86.1955 | 34.2853 | 0 | 84.1911 | 14% | 0 | 0 | 10% | 0 | 31.8027
6747 | 0 | 0 | 0 | 0.2 | 15.5 | 0 | 0 | 0 | 0 | 92.2968 | 36.9307 | 0 | 91.6788 | 7% | 0 | 0 | 10% | 0 | 34.4175
6748 | 0 | 0 | 0 | 0.5 | 15.3 | 0 | 0 | 0 | 0 | 90.2654 | 36.3075 | 0 | 91.4676 | 0% | 0 | 0 | 10% | 0 | 33.8059
6749 | 0 | 0 | 0 | 1.1 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3397
6750 | 0 | 0 | 0 | 1 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3165
6751 | 165 | 36 | 18 | 0.8 | 15.1 | 0 | 15.7638 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2937
6752 | 572 | 204 | 56 | 0.7 | 18.3 | 82.837 | 20.5877 | 15.7411 | 0 | 0 | 0 | 79.5533 | 0 | 6% | 0 | 0 | 10% | 0 | 14.2744
6753 | 756 | 398 | 71 | 0.7 | 20.9 | 176.7745 | 0 | 37.9766 | 0 | 0 | 0 | 173.9494 | 0 | 19% | 0 | 0 | 10% | 0 | 36.0119
6754 | 841 | 564 | 79 | 0.8 | 22.6 | 220.4539 | 0 | 56.9301 | 0 | 0 | 0 | 218.5556 | 0 | 36% | 11.1459 | 0 | 25.16% | 0 | 43.3995
6755 | 884 | 682 | 83 | 1 | 24.1 | 243.3996 | 0 | 70.0445 | 0 | 0 | 0 | 241.8517 | 0 | 54% | 24.0008 | 0 | 57.8% | 0 | 43.4112
6756 | 902 | 741 | 84 | 1 | 25.5 | 253.9397 | 0 | 68.9622 | 6.1378 | 0 | 0 | 252.5748 | 0 | 73% | 23.6768 | 0 | 90% | 0 | 42.507
6757 | 900 | 738 | 84 | 1.5 | 26.8 | 252.9189 | 0 | 45.0377 | 30.0623 | 0 | 0 | 251.6718 | 0 | 91% | 0 | 0 | 90% | 0 | 42.2228
6758 | 872 | 669 | 84 | 1.9 | 28.1 | 114.3954 | 135.4393 | 43.6236 | 23.7965 | 0 | 0 | 113.8483 | 0 | 100% | 0 | 0 | 90% | 0 | 42.0168
6759 | 824 | 545 | 79 | 3.7 | 28 | 41.2345 | 198.2464 | 42.103 | 11.341 | 42.5867 | 0 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.3577
6760 | 718 | 372 | 72 | 3.4 | 27.3 | 42.1609 | 142.4364 | 28.6322 | 5.1358 | 42.5841 | 12.63 | 0 | 0 | 100% | 1.2006 | 1.0205 | 90% | 0 | 41.7257
6761 | 523 | 178 | 51 | 3.9 | 25.7 | 42.1575 | 56.5176 | 12.2165 | 0 | 42.5826 | 14.6991 | 0 | 0 | 100% | 0 | 16.8321 | 63.07% | 0 | 44.4579
6762 | 81 | 23 | 13 | 2.9 | 23.7 | 0 | 4.2559 | 0 | 0 | 55.4081 | 20.2748 | 0 | 53.8903 | 96% | 0 | 25 | 23.07% | 0 | 43.201
6763 | 0 | 0 | 0 | 1.1 | 21.1 | 0 | 0 | 0 | 0 | 87.0713 | 34.093 | 0 | 89.3597 | 90% | 0 | 8.1679 | 10% | 0 | 39.3108
6764 | 0 | 0 | 0 | 0.5 | 19.8 | 0 | 0 | 0 | 0 | 96.9893 | 38.583 | 0 | 97.2028 | 82% | 0 | 0 | 10% | 0 | 36.1439
6765 | 0 | 0 | 0 | 1.4 | 19 | 0 | 0 | 0 | 0 | 92.632 | 36.821 | 0 | 91.5211 | 75% | 0 | 0 | 10% | 0 | 34.5105
6766 | 0 | 0 | 0 | 1.6 | 18.6 | 0 | 0 | 0 | 0 | 88.7976 | 35.2328 | 0 | 86.8358 | 69% | 0 | 0 | 10% | 0 | 32.9235
6767 | 0 | 0 | 0 | 2.1 | 18.2 | 0 | 0 | 0 | 0 | 86.4338 | 34.2688 | 0 | 84.1535 | 63% | 0 | 0 | 10% | 0 | 31.9125
6768 | 0 | 0 | 0 | 1.5 | 17.5 | 0 | 0 | 0 | 0 | 85.2755 | 33.8311 | 0 | 82.9426 | 56% | 0 | 0 | 10% | 0 | 31.4207
6769 | 0 | 0 | 0 | 4 | 17.4 | 0 | 0 | 0 | 0 | 84.995 | 33.7205 | 0 | 82.7521 | 50% | 0 | 0 | 10% | 0 | 31.2618
6770 | 0 | 0 | 0 | 3.7 | 16.7 | 0 | 0 | 0 | 0 | 86.2753 | 34.3042 | 0 | 84.3856 | 44% | 0 | 0 | 10% | 0 | 31.8051
6771 | 0 | 0 | 0 | 3.4 | 16.7 | 0 | 0 | 0 | 0 | 93.6682 | 37.4287 | 0 | 93.5 | 37% | 0 | 0 | 10% | 0 | 34.8965
6772 | 0 | 0 | 0 | 2.6 | 17 | 0 | 0 | 0 | 0 | 104.2474 | 41.8381 | 0 | 106.0878 | 29% | 0 | 0 | 10% | 0 | 39.3193
6773 | 0 | 0 | 0 | 2.4 | 17.1 | 0 | 0 | 0 | 0 | 109.1878 | 43.8842 | 0 | 111.6347 | 21% | 0 | 0 | 10% | 0 | 41.4335
6774 | 0 | 0 | 0 | 2.4 | 16.6 | 0 | 0 | 0 | 0 | 111.9556 | 45.0754 | 0 | 114.5702 | 12% | 0 | 0 | 10% | 0 | 42.6993
6775 | 91 | 27 | 16 | 1.9 | 16.5 | 0 | 8.2035 | 0 | 0 | 113.9552 | 45.9173 | 0 | 116.6256 | 3% | 0 | 0 | 10% | 0 | 43.6101
6776 | 558 | 200 | 56 | 2.3 | 19.1 | 79.3787 | 19.8436 | 15.2941 | 0 | 77.4838 | 30.2872 | 16.5614 | 13.8353 | 3% | 0 | 0 | 10% | 0 | 44.0808
6777 | 693 | 379 | 78 | 5.3 | 21.3 | 157.1893 | 0 | 35.2274 | 0 | 43.7834 | 15.5288 | 114.153 | 0 | 12% | 4.0589 | 0 | 15.52% | 0 | 44.8626
6778 | 839 | 562 | 81 | 5.9 | 22.6 | 215.9562 | 0 | 57.0188 | 0 | 43.5526 | 15.338 | 173.4474 | 0 | 25% | 24.8165 | 0 | 49.27% | 0 | 45.1728
6779 | 882 | 677 | 83 | 6.3 | 23.6 | 238.8132 | 0 | 56.6946 | 13.2945 | 42.6012 | 14.8737 | 197.4706 | 0 | 40% | 25 | 0 | 83.27% | 0 | 43.9751
6780 | 904 | 738 | 83 | 5.9 | 24.5 | 251.1014 | 0 | 36.0831 | 39.0169 | 42.6072 | 14.805 | 209.7653 | 0 | 56% | 4.9482 | 0 | 90% | 0 | 43.2062
6781 | 907 | 735 | 81 | 6.3 | 24.9 | 251.4731 | 0 | 31.0098 | 44.0902 | 42.6091 | 14.7737 | 210.0334 | 0 | 71% | 0 | 0 | 90% | 0 | 43.0261
6782 | 885 | 667 | 78 | 5.8 | 25.3 | 239.2275 | 0 | 30.8116 | 37.5774 | 42.6099 | 14.7414 | 197.642 | 0 | 86% | 0 | 0 | 90% | 0 | 42.8903
6783 | 833 | 540 | 75 | 6.1 | 25.2 | 211.9303 | 0 | 26.5548 | 27.5097 | 42.6099 | 14.7496 | 170.0865 | 0 | 98% | 0 | 0 | 90% | 0 | 42.2049
6784 | 747 | 372 | 65 | 6.1 | 24.5 | 65.5305 | 120.8259 | 27.3137 | 7.5061 | 42.6091 | 14.8056 | 23.9907 | 0 | 100% | 0 | 0 | 90% | 0 | 42.7058
6785 | 556 | 178 | 46 | 5.9 | 23.2 | 42.1528 | 62.1497 | 12.833 | 0 | 42.6068 | 14.9065 | 0 | 0 | 100% | 0 | 16.8198 | 63.09% | 0 | 45.2702
6786 | 89 | 22 | 12 | 6.1 | 21 | 0 | 3.9455 | 0 | 0 | 56.4278 | 20.9207 | 0 | 54.9209 | 96% | 0 | 25 | 23.09% | 0 | 43.8506
6787 | 0 | 0 | 0 | 4.4 | 19.5 | 0 | 0 | 0 | 0 | 87.8838 | 34.5558 | 0 | 90.2662 | 89% | 0 | 8.1802 | 10% | 0 | 39.7863
6788 | 0 | 0 | 0 | 4 | 18.9 | 0 | 0 | 0 | 0 | 98.3148 | 39.2032 | 0 | 98.7347 | 82% | 0 | 0 | 10% | 0 | 36.7717
6789 | 0 | 0 | 0 | 3.9 | 18.3 | 0 | 0 | 0 | 0 | 93.8383 | 37.3825 | 0 | 92.9193 | 75% | 0 | 0 | 10% | 0 | 35.0952
6790 | 0 | 0 | 0 | 3.3 | 17.8 | 0 | 0 | 0 | 0 | 90.1056 | 35.8396 | 0 | 88.2893 | 68% | 0 | 0 | 10% | 0 | 33.5644
6791 | 0 | 0 | 0 | 2.7 | 17.7 | 0 | 0 | 0 | 0 | 87.7157 | 34.8402 | 0 | 85.5384 | 62% | 0 | 0 | 10% | 0 | 32.5244
6792 | 0 | 0 | 0 | 1.8 | 17.7 | 0 | 0 | 0 | 0 | 85.8414 | 34.0538 | 0 | 83.4609 | 56% | 0 | 0 | 10% | 0 | 31.6882
6793 | 0 | 0 | 0 | 1.8 | 17 | 0 | 0 | 0 | 0 | 84.8409 | 33.6816 | 0 | 82.4297 | 50% | 0 | 0 | 10% | 0 | 31.2652
6794 | 0 | 0 | 0 | 1.8 | 16.2 | 0 | 0 | 0 | 0 | 86.1354 | 34.2772 | 0 | 84.0979 | 43% | 0 | 0 | 10% | 0 | 31.8132
6795 | 0 | 0 | 0 | 2 | 15.8 | 0 | 0 | 0 | 0 | 92.3771 | 36.9407 | 0 | 91.7723 | 36% | 0 | 0 | 10% | 0 | 34.4396
6796 | 0 | 0 | 0 | 1.5 | 15.6 | 0 | 0 | 0 | 0 | 103.4402 | 41.6028 | 0 | 105.0232 | 29% | 0 | 0 | 10% | 0 | 39.1007
6797 | 0 | 0 | 0 | 1.1 | 14.8 | 0 | 0 | 0 | 0 | 108.042 | 43.586 | 0 | 110.2307 | 20% | 0 | 0 | 10% | 0 | 41.145
6798 | 0 | 0 | 0 | 2 | 14.8 | 0 | 0 | 0 | 0 | 110.393 | 44.5652 | 0 | 112.6877 | 12% | 0 | 0 | 10% | 0 | 42.1932
6799 | 116 | 25 | 15 | 2.3 | 15.6 | 0 | 9.8304 | 0 | 0 | 112.5148 | 45.3887 | 0 | 114.9108 | 3% | 0 | 0 | 10% | 0 | 43.0788
6800 | 500 | 183 | 64 | 1.8 | 17.9 | 69.3616 | 17.4531 | 14.1202 | 0 | 79.0627 | 31.0759 | 5.6931 | 14.2119 | 3% | 0 | 0 | 10% | 0 | 43.7764
6801 | 782 | 439 | 106 | 3.2 | 20.8 | 181.1491 | 0 | 43.1236 | 0 | 43.9194 | 15.6188 | 137.394 | 0 | 13% | 12.2907 | 0 | 26.71% | 0 | 44.4113
6802 | 851 | 561 | 77 | 4.6 | 23.2 | 220.1531 | -2.98e-14 | 57.0272 | 0.33725 | 42.593 | 14.9017 | 178.7415 | 0 | 26% | 25 | 0 | 60.71% | 0 | 44.5231
6803 | 863 | 688 | 110 | 5.3 | 24.2 | 233.858 | 0 | 52.5996 | 18.4238 | 42.605 | 14.8281 | 192.5648 | 0 | 41% | 21.5328 | 0 | 90% | 0 | 43.3419
6804 | 598 | 725 | 287 | 5.9 | 25.1 | 159.2369 | 0 | 29.2748 | 41.007 | 42.6083 | 14.7573 | 118.2759 | 0 | 50% | 0 | 0 | 90% | 0 | 42.14
6805 | 359 | 673 | 408 | 6 | 25.5 | 87.5649 | -1.49e-14 | 28.2347 | 31.9756 | 42.6073 | 14.724 | 46.6265 | 0 | 53% | 0 | 0 | 90% | 0 | 41.7182
6806 | 279 | 481 | 296 | 5.2 | 25.3 | 62.2915 | 0 | 27.8334 | 13.3237 | 42.6041 | 14.7394 | 21.0789 | 0 | 55% | 0 | 0 | 90% | 0 | 41.5665
6807 | 493 | 498 | 221 | 4.7 | 25.6 | 118.1211 | 0 | 27.6834 | 16.901 | 42.6004 | 14.7134 | 75.5874 | 0 | 60% | 0 | 0 | 90% | 0 | 40.8916
6808 | 429 | 313 | 129 | 5 | 24.9 | 87.4452 | 0 | 24.7619 | 0 | 42.5992 | 14.7703 | 45.9014 | 0 | 64% | 0 | 3.3655 | 84.61% | 0 | 41.6637
6809 | 2 | 70 | 70 | 4.9 | 22.8 | 0 | 0.41843 | 0 | 0 | 56.3758 | 20.7606 | 0 | 54.5603 | 60% | 0 | 25 | 44.62% | 0 | 43.8304
6810 | 1 | 10 | 10 | 4.9 | 21 | 0 | 0.03628 | 0 | 0 | 62.5852 | 23.5535 | 0 | 61.7414 | 55% | 0 | 21.6345 | 10% | 0 | 42.3255
6811 | 0 | 0 | 0 | 4.2 | 19.6 | 0 | 0 | 0 | 0 | 104.4952 | 41.7341 | 0 | 107.8461 | 47% | 0 | 0 | 10% | 0 | 38.8569
6812 | 0 | 0 | 0 | 3.3 | 19.1 | 0 | 0 | 0 | 0 | 97.3014 | 38.7663 | 0 | 98.4074 | 40% | 0 | 0 | 10% | 0 | 36.0658
6813 | 0 | 0 | 0 | 3.4 | 18.7 | 0 | 0 | 0 | 0 | 93.2096 | 37.0876 | 0 | 93.2041 | 33% | 0 | 0 | 10% | 0 | 34.4676
6814 | 0 | 0 | 0 | 2.7 | 18.4 | 0 | 0 | 0 | 0 | 88.4852 | 35.1159 | 0 | 87.2471 | 26% | 0 | 0 | 10% | 0 | 32.538
6815 | 0 | 0 | 0 | 2.8 | 18.3 | 0 | 0 | 0 | 0 | 84.9082 | 33.6235 | 0 | 82.9458 | 20% | 0 | 0 | 10% | 0 | 31.0511
6816 | 0 | 0 | 0 | 2.4 | 18.2 | 0 | 0 | 0 | 0 | 82.5744 | 32.6412 | 0 | 80.3019 | 14% | 0 | 0 | 10% | 0 | 30.0553
6817 | 0 | 0 | 0 | 1.7 | 17.9 | 0 | 0 | 0 | 0 | 81.6767 | 32.2539 | 0 | 79.4498 | 8% | 0 | 0 | 10% | 0 | 29.6467
6818 | 0 | 0 | 0 | 1.3 | 17.1 | 0 | 0 | 0 | 0 | 80.4626 | 31.7565 | 0 | 78.2698 | 3% | 0 | 0 | 10% | 0 | 29.131
6819 | 0 | 0 | 0 | 2.5 | 17.3 | 0 | 0 | 0 | 0 | 35.0164 | 13.8379 | 0 | 34.0952 | 0% | 0 | 0 | 10% | 0 | 11.2464
6820 | 0 | 0 | 0 | 1.8 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5357
6821 | 0 | 0 | 0 | 1.2 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5089
6822 | 0 | 0 | 0 | 1.5 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4824
6823 | 27 | 23 | 20 | 1.8 | 17.5 | 0 | 2.1419 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4564
6824 | 23 | 105 | 99 | 2.5 | 18.7 | 0 | 5.0197 | 2.1154 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.31543
6825 | 270 | 340 | 221 | 3.2 | 20.4 | 0 | 62.4607 | 25.2636 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 22.8616
6826 | 42 | 315 | 287 | 4.2 | 21.2 | 0 | 12.6202 | 19.1171 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 16.7359
6827 | 20 | 396 | 376 | 4.6 | 22 | 0 | 6.2819 | 22.7752 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 20.4181
6828 | 114 | 498 | 407 | 3.7 | 23.6 | 0 | 36.561 | 37.5947 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 35.2614
6829 | 485 | 651 | 299 | 2.9 | 25.1 | 104.3591 | 25.2769 | 60.8283 | 0.21362 | 0 | 0 | 99.0854 | 0 | 8% | 24.8974 | 0 | 43.86% | 0 | 34.283
6830 | 763 | 642 | 141 | 2 | 26.5 | 205.7115 | 0 | 61.1979 | 4.0498 | 0 | 0 | 202.0711 | 0 | 23% | 25 | 0 | 77.86% | 0 | 33.9761
6831 | 742 | 542 | 135 | 2 | 27.3 | 188.6925 | 0 | 42.7438 | 10.8349 | 42.4632 | 0 | 146.9405 | 0 | 34% | 8.9261 | 0 | 90% | 0 | 31.1791
6832 | 662 | 355 | 89 | 3.6 | 27 | 145.5777 | 0 | 25.3014 | 7.2892 | 42.7702 | 11.5382 | 103.7896 | 0 | 42% | 1.1507 | 0.97814 | 90% | 0 | 34.8013
6833 | 397 | 153 | 61 | 4.9 | 25.1 | 57.6877 | 0 | 9.2567 | 0 | 42.5264 | 14.7289 | 16.8793 | 0 | 43% | 0 | 14.7943 | 66.33% | 0 | 37.8131
6834 | 36 | 16 | 12 | 4.1 | 22.8 | 0 | 1.0225 | 0 | 0 | 43.1479 | 15.1618 | 0 | 40.9954 | 40% | 0 | 24.2858 | 27.47% | 0 | 37.8035
6835 | 0 | 0 | 0 | 3.4 | 21 | 0 | 0 | 0 | 0 | 70.538 | 27.1062 | 0 | 69.911 | 35% | 0 | 10.9199 | 10% | 0 | 35.4057
6836 | 0 | 0 | 0 | 2.7 | 19.6 | 0 | 0 | 0 | 0 | 91.3535 | 36.2395 | 0 | 90.9227 | 28% | 0 | 0 | 10% | 0 | 33.6187
6837 | 0 | 0 | 0 | 2.2 | 19 | 0 | 0 | 0 | 0 | 86.4052 | 34.2036 | 0 | 84.8073 | 22% | 0 | 0 | 10% | 0 | 31.6121
6838 | 0 | 0 | 0 | 1.2 | 18.3 | 0 | 0 | 0 | 0 | 82.4814 | 32.5979 | 0 | 80.2347 | 16% | 0 | 0 | 10% | 0 | 30.0042
6839 | 0 | 0 | 0 | 1 | 18.1 | 0 | 0 | 0 | 0 | 79.549 | 31.2803 | 0 | 77.3213 | 10% | 0 | 0 | 10% | 0 | 28.6687
6840 | 0 | 0 | 0 | 1.5 | 18.2 | 0 | 0 | 0 | 0 | 77.2174 | 30.2256 | 0 | 75.0138 | 4% | 0 | 0 | 10% | 0 | 27.5977
6841 | 0 | 0 | 0 | 0.9 | 16.8 | 0 | 0 | 0 | 0 | 58.6069 | 22.9745 | 0 | 56.9422 | 0% | 0 | 0 | 10% | 0 | 20.3484
6842 | 0 | 0 | 0 | 1.1 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5581
6843 | 0 | 0 | 0 | 1.4 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5307
6844 | 0 | 0 | 0 | 1.6 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5039
6845 | 0 | 0 | 0 | 1.1 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4777
6846 | 0 | 0 | 0 | 2 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4519
6847 | 102 | 28 | 18 | 1.4 | 16.2 | 0 | 7.5384 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4265
6848 | 509 | 191 | 63 | 0.7 | 18.4 | 70.6072 | 17.5814 | 14.3881 | 0 | 0 | 0 | 67.3548 | 0 | 5% | 0 | 0 | 10% | 0 | 13.005
6849 | 705 | 385 | 88 | 1.1 | 21.4 | 161.6263 | 0 | 36.9109 | 0.37343 | 0 | 0 | 158.1557 | 0 | 17% | 0 | 0 | 10% | 0 | 35.0897
6850 | 796 | 550 | 101 | 0.7 | 24.3 | 206.5953 | 0 | 55.7289 | 0 | 42.4364 | 0 | 164.2262 | 0 | 29% | 23.5861 | 0 | 42.08% | 0 | 29.3653
6851 | 840 | 666 | 109 | 1.5 | 25.5 | 229.3733 | 0 | 48.6841 | 20.0631 | 42.5157 | 14.5134 | 187.4756 | 0 | 43% | 25 | 0 | 76.08% | 0 | 35.6898
6852 | 858 | 726 | 113 | 1.2 | 27 | 240.1571 | 0 | 32.2968 | 42.6298 | 42.5548 | 14.5803 | 198.2723 | 0 | 58% | 10.2375 | 0 | 90% | 0 | 34.0143
6853 | 850 | 719 | 115 | 1.5 | 28.1 | 237.2005 | 0 | 21.1691 | 52.6328 | 42.5673 | 14.489 | 195.3186 | 0 | 72% | 0 | 0 | 90% | 0 | 33.0437
6854 | 808 | 646 | 118 | 2.7 | 28.5 | 218.4299 | 0 | 20.5628 | 44.7789 | 42.5772 | 14.4568 | 176.4936 | 0 | 85% | 0 | 0 | 90% | 0 | 32.563
6855 | 736 | 517 | 114 | 2.6 | 27.5 | 186.5271 | 0 | 17.3961 | 33.8186 | 42.5826 | 14.5465 | 144.426 | 0 | 96% | 0 | 0 | 90% | 0 | 32.7331
6856 | 606 | 342 | 100 | 3.8 | 27.3 | 96.4966 | 42.0509 | 19.2148 | 11.3354 | 42.5855 | 14.5648 | 54.7162 | 0 | 100% | 0 | 0 | 90% | 0 | 34.7197
6857 | 379 | 152 | 65 | 4.3 | 25.8 | 0 | 65.0451 | 9.2379 | 0 | 42.5841 | 14.6914 | 0 | 41.0929 | 97% | 0 | 16.1954 | 64.09% | 0 | 38.0457
6858 | 24 | 16 | 12 | 3.5 | 23.6 | 0 | 0.49704 | 0 | 0 | 44.932 | 15.8269 | 0 | 43.3103 | 94% | 0 | 25 | 24.09% | 0 | 37.9129
6859 | 0 | 0 | 0 | 3.5 | 21.3 | 0 | 0 | 0 | 0 | 77.4973 | 30.0581 | 0 | 78.269 | 88% | 0 | 8.8046 | 10% | 0 | 35.9566
6860 | 0 | 0 | 0 | 3.3 | 19.8 | 0 | 0 | 0 | 0 | 91.739 | 36.3839 | 0 | 91.5026 | 81% | 0 | 0 | 10% | 0 | 33.7599
6861 | 0 | 0 | 0 | 2.5 | 18.8 | 0 | 0 | 0 | 0 | 86.2843 | 34.1637 | 0 | 84.5165 | 75% | 0 | 0 | 10% | 0 | 31.6429
6862 | 0 | 0 | 0 | 1.3 | 18.2 | 0 | 0 | 0 | 0 | 82.5033 | 32.6052 | 0 | 80.2124 | 69% | 0 | 0 | 10% | 0 | 30.0567
6863 | 0 | 0 | 0 | 1.7 | 17.3 | 0 | 0 | 0 | 0 | 80.5185 | 31.7609 | 0 | 78.3512 | 63% | 0 | 0 | 10% | 0 | 29.1604
6864 | 0 | 0 | 0 | 1.9 | 17.6 | 0 | 0 | 0 | 0 | 79.6915 | 31.3673 | 0 | 77.6151 | 57% | 0 | 0 | 10% | 0 | 28.7295
6865 | 0 | 0 | 0 | 2.4 | 17.6 | 0 | 0 | 0 | 0 | 79.5662 | 31.3113 | 0 | 77.5615 | 52% | 0 | 0 | 10% | 0 | 28.645
6866 | 0 | 0 | 0 | 2.7 | 18 | 0 | 0 | 0 | 0 | 81.8131 | 32.3064 | 0 | 79.8985 | 46% | 0 | 0 | 10% | 0 | 29.6156
6867 | 0 | 0 | 0 | 2.3 | 17.3 | 0 | 0 | 0 | 0 | 90.7389 | 36.1448 | 0 | 90.5083 | 39% | 0 | 0 | 10% | 0 | 33.4251
6868 | 0 | 0 | 0 | 2.2 | 17.1 | 0 | 0 | 0 | 0 | 103.8297 | 41.6546 | 0 | 106.3181 | 31% | 0 | 0 | 10% | 0 | 38.9502
6869 | 0 | 0 | 0 | 2.7 | 18.3 | 0 | 0 | 0 | 0 | 110.1148 | 44.1703 | 0 | 113.4269 | 23% | 0 | 0 | 10% | 0 | 41.5573
6870 | 0 | 0 | 0 | 1.6 | 18 | 0 | 0 | 0 | 0 | 112.9635 | 45.378 | 0 | 116.3685 | 14% | 0 | 0 | 10% | 0 | 42.8665
6871 | 22 | 27 | 25 | 1.1 | 16.9 | 0 | 1.5065 | 0 | 0 | 114.4613 | 46.0948 | 0 | 117.7348 | 5% | 0 | 0 | 10% | 0 | 43.6751
6872 | 43 | 76 | 69 | 1.8 | 18.2 | 0 | 9.2888 | 0.66308 | 0 | 67.5251 | 27.1292 | 0 | 69.2444 | 0% | 0 | 0 | 10% | 0 | 25.5375
6873 | 32 | 163 | 148 | 1.3 | 19.9 | 0 | 8.6406 | 6.1259 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.0004
6874 | 114 | 279 | 211 | 1.5 | 22 | 0 | 34.1468 | 17.9957 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 15.8895
6875 | 316 | 469 | 255 | 1.1 | 24.3 | 61.726 | 15.2328 | 41.0749 | 0 | 0 | 0 | 59.3621 | 0 | 5% | 0 | 0 | 10% | 0 | 39.8229
6876 | 655 | 722 | 254 | 2.9 | 26.7 | 178.1515 | 0 | 69.2756 | 2.8881 | 0 | 0 | 174.6823 | 0 | 18% | 25 | 0 | 44% | 0 | 42.2952
6877 | 860 | 723 | 118 | 6.1 | 28 | 236.4331 | 0 | 69.7854 | 5.1186 | 0 | 0 | 234.4338 | 0 | 35% | 25 | 0 | 78% | 0 | 42.2452
6878 | 825 | 646 | 112 | 6.4 | 27.6 | 219.9064 | -2.98e-14 | 52.8267 | 13.4078 | 0 | 0 | 218.6024 | 0 | 52% | 8.8235 | 0 | 90% | 0 | 41.5609
6879 | 262 | 298 | 147 | 9.1 | 26.3 | 0 | 64.2449 | 22.3419 | 0 | 42.5737 | 2.0491 | 0 | 39.8044 | 49% | 0 | 18.8211 | 59.89% | 0 | 41.5423
6880 | 590 | 336 | 99 | 10.7 | 26.6 | 120.0232 | 0 | 29.316 | 0.35331 | 42.5691 | 14.619 | 75.7329 | 0 | 55% | 0 | 0 | 59.89% | 0 | 42.4183
6881 | 455 | 144 | 47 | 8.8 | 25.3 | 64.0849 | 0 | 9.8028 | 0 | 42.5725 | 14.7285 | 23.4041 | 0 | 56% | 0 | 21.3113 | 25.79% | 0 | 44.8116
6882 | 37 | 16 | 9 | 7.1 | 23.6 | 0 | 0.48903 | 0 | 0 | 89.8291 | 34.9609 | 0 | 91.051 | 50% | 0 | 9.8677 | 10% | 0 | 43.286
6883 | 0 | 0 | 0 | 6.4 | 22.4 | 0 | 0 | 0 | 0 | 104.1616 | 41.3519 | 0 | 105.4759 | 42% | 0 | 0 | 10% | 0 | 38.9669
6884 | 0 | 0 | 0 | 6.5 | 21 | 0 | 0 | 0 | 0 | 95.6365 | 37.9256 | 0 | 94.992 | 35% | 0 | 0 | 10% | 0 | 35.6252
6885 | 0 | 0 | 0 | 7.9 | 20.5 | 0 | 0 | 0 | 0 | 91.5336 | 36.2443 | 0 | 89.9884 | 28% | 0 | 0 | 10% | 0 | 33.9582
6886 | 0 | 0 | 0 | 6.6 | 19.5 | 0 | 0 | 0 | 0 | 87.7491 | 34.7287 | 0 | 85.4508 | 21% | 0 | 0 | 10% | 0 | 32.4325
6887 | 0 | 0 | 0 | 4.3 | 18.1 | 0 | 0 | 0 | 0 | 85.004 | 33.6786 | 0 | 82.2888 | 15% | 0 | 0 | 10% | 0 | 31.3544
6888 | 0 | 0 | 0 | 3.9 | 17.7 | 0 | 0 | 0 | 0 | 83.953 | 33.2666 | 0 | 81.1689 | 9% | 0 | 0 | 10% | 0 | 30.9054
6889 | 0 | 0 | 0 | 4.6 | 17.8 | 0 | 0 | 0 | 0 | 83.6379 | 33.1296 | 0 | 80.9109 | 3% | 0 | 0 | 10% | 0 | 30.7317
6890 | 0 | 0 | 0 | 4.6 | 17.1 | 0 | 0 | 0 | 0 | 41.7719 | 16.589 | 0 | 40.643 | 0% | 0 | 0 | 10% | 0 | 14.2035
6891 | 0 | 0 | 0 | 4.1 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3266
6892 | 0 | 0 | 0 | 2.4 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3037
6893 | 0 | 0 | 0 | 2.1 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2813
6894 | 0 | 0 | 0 | 2.3 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2594
6895 | 170 | 27 | 12 | 2.2 | 12.5 | 0 | 10.7174 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2378
6896 | 688 | 206 | 43 | 1.6 | 14.7 | 98.454 | 24.6761 | 18.8046 | 0 | 0 | 0 | 94.1277 | 0 | 7% | 0 | 0 | 10% | 0 | 17.2106
6897 | 852 | 406 | 58 | 1.5 | 17.3 | 197.3515 | 0 | 42.6384 | 0 | 0 | 0 | 194.2648 | 0 | 22% | 0 | 0 | 10% | 0 | 40.4849
6898 | 918 | 572 | 68 | 1.7 | 19 | 239.3964 | 0 | 61.7512 | 0.27481 | 42.4935 | 0.67725 | 197.5022 | 0 | 37% | 20.9612 | 0 | 38.51% | 0 | 38.3922
6899 | 940 | 686 | 76 | 1.9 | 20.5 | 258.1059 | 0 | 54.6051 | 20.0035 | 42.5442 | 15.0754 | 216.4661 | 0 | 53% | 25 | 0 | 72.51% | 0 | 41.8881
6900 | 953 | 744 | 77 | 1.6 | 21 | 267.7564 | 0 | 41.7079 | 33.3921 | 42.5712 | 15.0523 | 226.1294 | 0 | 70% | 12.8623 | 0 | 90% | 0 | 40.9821
6901 | 942 | 735 | 79 | 2.1 | 21.6 | 263.7638 | 0 | 28.598 | 46.502 | 42.5798 | 15.0141 | 222.0941 | 0 | 86% | 0 | 0 | 90% | 0 | 40.7143
6902 | 909 | 662 | 81 | 1.8 | 22.2 | 227.8361 | 23.0197 | 24.0671 | 46.847 | 42.587 | 14.9743 | 185.9525 | 0 | 100% | 0 | 0 | 90% | 0 | 40.6967
6903 | 853 | 534 | 80 | 2.3 | 22.3 | 42.1523 | 202.8968 | 24.6085 | 31.4546 | 42.5898 | 14.9679 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.2874
6904 | 743 | 357 | 71 | 2.8 | 22 | 42.1578 | 143.8991 | 26.0456 | 9.0995 | 42.5876 | 14.9893 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 41.746
6905 | 503 | 156 | 47 | 3.2 | 20.7 | 42.1579 | 46.2632 | 11.2672 | 0 | 42.5855 | 15.077 | 0 | 0 | 100% | 0 | 17.4575 | 62.07% | 0 | 44.5131
6906 | 25 | 12 | 8 | 2.1 | 17.8 | 0 | 0.14839 | 0 | 0 | 53.8465 | 20.0234 | 0 | 52.3165 | 96% | 0 | 25 | 22.07% | 0 | 42.9586
6907 | 0 | 0 | 0 | 2.1 | 16.1 | 0 | 0 | 0 | 0 | 87.2969 | 34.5789 | 0 | 89.5463 | 90% | 0 | 7.5425 | 10% | 0 | 39.1687
6908 | 0 | 0 | 0 | 0.9 | 15.3 | 0 | 0 | 0 | 0 | 95.205 | 38.1684 | 0 | 95.1081 | 83% | 0 | 0 | 10% | 0 | 35.7269
6909 | 0 | 0 | 0 | 0.8 | 14.5 | 0 | 0 | 0 | 0 | 90.5877 | 36.2668 | 0 | 89.1078 | 76% | 0 | 0 | 10% | 0 | 33.9287
6910 | 0 | 0 | 0 | 2 | 14 | 0 | 0 | 0 | 0 | 86.6017 | 34.6133 | 0 | 84.3734 | 70% | 0 | 0 | 10% | 0 | 32.2535
6911 | 0 | 0 | 0 | 1.2 | 12.8 | 0 | 0 | 0 | 0 | 83.8991 | 33.5459 | 0 | 81.3612 | 63% | 0 | 0 | 10% | 0 | 31.1265
6912 | 0 | 0 | 0 | 1.1 | 12.5 | 0 | 0 | 0 | 0 | 82.7382 | 33.0643 | 0 | 80.2328 | 57% | 0 | 0 | 10% | 0 | 30.5807
6913 | 0 | 0 | 0 | 1.8 | 12.7 | 0 | 0 | 0 | 0 | 82.6668 | 33.0213 | 0 | 80.3108 | 51% | 0 | 0 | 10% | 0 | 30.4843
6914 | 0 | 0 | 0 | 1.5 | 12.6 | 0 | 0 | 0 | 0 | 84.1207 | 33.6506 | 0 | 82.083 | 45% | 0 | 0 | 10% | 0 | 31.0714
6915 | 0 | 0 | 0 | 0.7 | 10.7 | 0 | 0 | 0 | 0 | 91.3879 | 36.8233 | 0 | 90.9498 | 39% | 0 | 0 | 10% | 0 | 34.2088
6916 | 0 | 0 | 0 | 0.7 | 10.6 | 0 | 0 | 0 | 0 | 103.5671 | 41.9716 | 0 | 105.6094 | 31% | 0 | 0 | 10% | 0 | 39.3639
6917 | 0 | 0 | 0 | 1.5 | 10.9 | 0 | 0 | 0 | 0 | 109.1019 | 44.2749 | 0 | 111.8699 | 22% | 0 | 0 | 10% | 0 | 41.7444
6918 | 0 | 0 | 0 | 1.1 | 10.5 | 0 | 0 | 0 | 0 | 110.6833 | 44.9557 | 0 | 113.3455 | 14% | 0 | 0 | 10% | 0 | 42.5135
6919 | 177 | 27 | 13 | 1.4 | 11.5 | 0 | 10.1973 | 0 | 0 | 112.1589 | 45.5197 | 0 | 114.7539 | 5% | 0 | 0 | 10% | 0 | 43.1521
6920 | 659 | 197 | 42 | 1.1 | 15.1 | 93.335 | 23.4089 | 17.7485 | 0 | 70.243 | 27.3128 | 35.9305 | 12.6673 | 7% | 0 | 0 | 10% | 0 | 43.4382
6921 | 823 | 392 | 59 | 0.9 | 17.9 | 189.6816 | 0 | 41.0678 | 0 | 43.7751 | 15.7394 | 146.398 | 0 | 18% | 10.856 | 0 | 24.76% | 0 | 43.8283
6922 | 918 | 563 | 63 | 1.3 | 19.1 | 239.1967 | 0 | 56.2472 | 5.2054 | 42.5805 | 15.1767 | 197.5907 | 0 | 33% | 25 | 0 | 58.76% | 0 | 43.8423
6923 | 957 | 684 | 66 | 1.9 | 20.6 | 262.8469 | 0 | 53.2503 | 21.6143 | 42.5976 | 15.0878 | 221.3864 | 0 | 49% | 22.9675 | 0 | 90% | 0 | 42.5462
6924 | 966 | 741 | 69 | 1.8 | 21.6 | 271.1575 | 0 | 29.7127 | 45.3873 | 42.6038 | 15.0225 | 229.6908 | 0 | 66% | 0 | 0 | 90% | 0 | 41.8067
6925 | 957 | 732 | 70 | 2.1 | 22.6 | 267.9315 | 0 | 29.3888 | 45.7112 | 42.6068 | 14.9516 | 226.3409 | 0 | 83% | 0 | 0 | 90% | 0 | 41.4147
6926 | 935 | 660 | 68 | 2.8 | 23.1 | 254.7947 | 0 | 25.0839 | 46.2298 | 42.608 | 14.9146 | 212.9526 | 0 | 99% | 0 | 0 | 90% | 0 | 41.2747
6927 | 890 | 532 | 64 | 2 | 23.7 | 56.0577 | 197.4823 | 25.4803 | 31.0799 | 42.6082 | 14.8684 | 14.6365 | 0 | 100% | 0 | 0 | 90% | 0 | 40.9463
6928 | 789 | 355 | 56 | 3.4 | 23.4 | 42.1523 | 155.2006 | 26.9865 | 8.7414 | 42.6057 | 14.8907 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.5879
6929 | 567 | 158 | 40 | 3.9 | 21.2 | 42.1579 | 59.4781 | 12.3761 | 0 | 42.6031 | 15.0498 | 0 | 0 | 100% | 0 | 17.1071 | 62.63% | 0 | 45.2443
6930 | 45 | 14 | 8 | 2.7 | 18.9 | 0 | 0 | 0 | 0 | 55.7758 | 20.7838 | 0 | 54.2615 | 96% | 0 | 25 | 22.63% | 0 | 43.7171
6931 | 0 | 0 | 0 | 1.7 | 16.9 | 0 | 0 | 0 | 0 | 87.5628 | 34.6228 | 0 | 89.8834 | 89% | 0 | 7.8929 | 10% | 0 | 39.5648
6932 | 0 | 0 | 0 | 1.1 | 15.3 | 0 | 0 | 0 | 0 | 96.1665 | 38.5696 | 0 | 96.2129 | 82% | 0 | 0 | 10% | 0 | 36.133
6933 | 0 | 0 | 0 | 0.5 | 14.5 | 0 | 0 | 0 | 0 | 91.7754 | 36.77 | 0 | 90.4976 | 75% | 0 | 0 | 10% | 0 | 34.4473
6934 | 0 | 0 | 0 | 0.8 | 14.3 | 0 | 0 | 0 | 0 | 87.3659 | 34.9161 | 0 | 85.184 | 69% | 0 | 0 | 10% | 0 | 32.5848
6935 | 0 | 0 | 0 | 1.9 | 13.8 | 0 | 0 | 0 | 0 | 85.0417 | 33.9676 | 0 | 82.6043 | 63% | 0 | 0 | 10% | 0 | 31.5781
6936 | 0 | 0 | 0 | 0.7 | 12.3 | 0 | 0 | 0 | 0 | 83.8526 | 33.5531 | 0 | 81.3835 | 57% | 0 | 0 | 10% | 0 | 31.1032
6937 | 0 | 0 | 0 | 1.2 | 12.5 | 0 | 0 | 0 | 0 | 83.5139 | 33.4001 | 0 | 81.1378 | 51% | 0 | 0 | 10% | 0 | 30.8977
6938 | 0 | 0 | 0 | 0.6 | 11.2 | 0 | 0 | 0 | 0 | 84.4787 | 33.8734 | 0 | 82.3949 | 45% | 0 | 0 | 10% | 0 | 31.3275
6939 | 0 | 0 | 0 | 1.2 | 12 | 0 | 0 | 0 | 0 | 91.4156 | 36.7682 | 0 | 90.8671 | 38% | 0 | 0 | 10% | 0 | 34.1853
6940 | 0 | 0 | 0 | 0.7 | 10.5 | 0 | 0 | 0 | 0 | 103.042 | 41.7536 | 0 | 104.8486 | 30% | 0 | 0 | 10% | 0 | 39.1736
6941 | 0 | 0 | 0 | 1.4 | 11.6 | 0 | 0 | 0 | 0 | 108.7986 | 44.1095 | 0 | 111.4184 | 22% | 0 | 0 | 10% | 0 | 41.5985
6942 | 0 | 0 | 0 | 2.1 | 12 | 0 | 0 | 0 | 0 | 111.2614 | 45.1155 | 0 | 113.9637 | 13% | 0 | 0 | 10% | 0 | 42.6867
6943 | 173 | 25 | 12 | 0.6 | 10.6 | 0 | 9.028 | 0 | 0 | 112.3567 | 45.6503 | 0 | 114.9177 | 5% | 0 | 0 | 10% | 0 | 43.2964
6944 | 578 | 178 | 45 | 0.5 | 15.4 | 79.7942 | 20.0969 | 15.3742 | 0 | 76.0769 | 29.8852 | 18.2557 | 13.81 | 5% | 0 | 0 | 10% | 0 | 43.7451
6945 | 822 | 388 | 58 | 0.7 | 19.3 | 188.881 | 0 | 40.738 | 0 | 43.9009 | 15.708 | 145.2477 | 0 | 16% | 10.1748 | 0 | 23.84% | 0 | 44.1598
6946 | 898 | 552 | 65 | 1.2 | 21.2 | 233.21 | 0 | 56.6888 | 3.1337 | 42.5868 | 15.0441 | 191.6835 | 0 | 30% | 25 | 0 | 57.84% | 0 | 44.2079
6947 | 937 | 671 | 70 | 2.5 | 22.4 | 256.5119 | 0 | 54.2858 | 18.9148 | 42.6013 | 14.9645 | 215.0956 | 0 | 46% | 23.6487 | 0 | 90% | 0 | 42.8399
6948 | 947 | 728 | 73 | 2.2 | 23.8 | 265.1011 | 0 | 29.8019 | 45.2981 | 42.6064 | 14.8601 | 223.6747 | 0 | 63% | 0 | 0 | 90% | 0 | 41.7946
6949 | 925 | 715 | 78 | 1.6 | 25.1 | 258.3963 | 0 | 29.797 | 45.303 | 42.6088 | 14.7574 | 216.8721 | 0 | 79% | 0 | 0 | 90% | 0 | 41.7232
6950 | 829 | 621 | 97 | 1.2 | 26.4 | 224.3123 | 0 | 29.3724 | 35.7278 | 42.6096 | 14.6498 | 182.6545 | 0 | 93% | 0 | 0 | 90% | 0 | 41.6459
6951 | 652 | 479 | 143 | 3 | 26 | 144.3296 | 20.4082 | 24.8545 | 23.0504 | 42.6091 | 14.6835 | 102.4536 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2341
6952 | 398 | 294 | 142 | 3 | 25.8 | 42.1526 | 47.5885 | 23.7574 | 0 | 42.6078 | 14.6995 | 0 | 0 | 100% | 0 | 3.5891 | 84.26% | 0 | 42.7563
6953 | 391 | 172 | 97 | 3.7 | 24.4 | 0 | 64.8606 | 10.8471 | 0 | 42.6043 | 14.812 | 0 | 41.1131 | 97% | 0 | 21.4517 | 49.94% | 0 | 45.0343
6954 | 29 | 15 | 10 | 2.7 | 21.2 | 0 | 0 | 0 | 0 | 57.4213 | 21.3447 | 0 | 55.7814 | 93% | 0 | 24.9593 | 10% | 0 | 43.3821
6955 | 0 | 0 | 0 | 1.3 | 17.6 | 0 | 0 | 0 | 0 | 105.7298 | 42.4089 | 0 | 109.7204 | 85% | 0 | 0 | 10% | 0 | 39.4721
6956 | 0 | 0 | 0 | 0.5 | 16.2 | 0 | 0 | 0 | 0 | 96.6701 | 38.7167 | 0 | 96.5355 | 78% | 0 | 0 | 10% | 0 | 36.3513
6957 | 0 | 0 | 0 | 1.2 | 15.2 | 0 | 0 | 0 | 0 | 91.9797 | 36.8109 | 0 | 90.6225 | 71% | 0 | 0 | 10% | 0 | 34.5219
6958 | 0 | 0 | 0 | 1.2 | 15.6 | 0 | 0 | 0 | 0 | 87.8561 | 35.0397 | 0 | 85.6691 | 64% | 0 | 0 | 10% | 0 | 32.7365
6959 | 0 | 0 | 0 | 2.1 | 16.2 | 0 | 0 | 0 | 0 | 85.2632 | 33.9103 | 0 | 82.7532 | 58% | 0 | 0 | 10% | 0 | 31.5542
6960 | 0 | 0 | 0 | 1.8 | 16.8 | 0 | 0 | 0 | 0 | 84.3625 | 33.4941 | 0 | 81.8684 | 52% | 0 | 0 | 10% | 0 | 31.0788
6961 | 0 | 0 | 0 | 0.8 | 13.3 | 0 | 0 | 0 | 0 | 83.4805 | 33.3413 | 0 | 80.9785 | 46% | 0 | 0 | 10% | 0 | 30.876
6962 | 0 | 0 | 0 | 0.7 | 14.4 | 0 | 0 | 0 | 0 | 84.9304 | 33.8851 | 0 | 82.8154 | 40% | 0 | 0 | 10% | 0 | 31.3733
6963 | 0 | 0 | 0 | 0.6 | 12.8 | 0 | 0 | 0 | 0 | 91.8033 | 36.8882 | 0 | 91.223 | 33% | 0 | 0 | 10% | 0 | 34.3384
6964 | 0 | 0 | 0 | 1 | 13.7 | 0 | 0 | 0 | 0 | 102.4454 | 41.3178 | 0 | 103.9918 | 25% | 0 | 0 | 10% | 0 | 38.7684
6965 | 0 | 0 | 0 | 0.9 | 13.9 | 0 | 0 | 0 | 0 | 107.8042 | 43.5517 | 0 | 110.1539 | 17% | 0 | 0 | 10% | 0 | 41.0593
6966 | 0 | 0 | 0 | 1.9 | 14.2 | 0 | 0 | 0 | 0 | 109.9062 | 44.4064 | 0 | 112.3122 | 9% | 0 | 0 | 10% | 0 | 41.9853
6967 | 83 | 26 | 20 | 2.2 | 14.7 | 0 | 3.8816 | 0 | 0 | 111.7514 | 45.14 | 0 | 114.2063 | 0% | 0 | 0 | 10% | 0 | 42.7824
6968 | 212 | 140 | 88 | 1.7 | 16.4 | 0 | 44.8262 | 7.4931 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 5.3555
6969 | 515 | 328 | 115 | 1 | 20.2 | 90.9391 | 22.4458 | 29.9549 | 0 | 0 | 0 | 87.7048 | 0 | 7% | 0 | 0 | 10% | 0 | 28.4441
6970 | 634 | 504 | 157 | 1.3 | 23.6 | 159.3167 | 0 | 49.9041 | 0 | 0 | 0 | 157.248 | 0 | 19% | 5.2719 | 0 | 17.17% | 0 | 42.8091
6971 | 685 | 632 | 190 | 1 | 26 | 183.2898 | 0 | 63.9916 | 0 | 0 | 0 | 181.75 | 0 | 32% | 20.8742 | 0 | 45.56% | 0 | 41.0563
6972 | 505 | 578 | 225 | 1.2 | 26.7 | 133.4774 | 0 | 56.6975 | 0 | 0 | 0 | 132.5528 | 0 | 42% | 14.752 | 0 | 65.62% | 0 | 40.3105
6973 | 714 | 673 | 182 | 3.3 | 26.7 | 194.4194 | 0 | 60.29 | 9.0473 | 0 | 0 | 192.8524 | 0 | 57% | 17.9254 | 0 | 90% | 0 | 40.1524
6974 | 819 | 637 | 124 | 4.4 | 26.5 | 218.9934 | 0 | 40.2705 | 26.6016 | 42.5836 | 2.6078 | 177.7941 | 0 | 70% | 0 | 0 | 90% | 0 | 39.9819
6975 | 629 | 489 | 161 | 5 | 25.8 | 152.9779 | 0 | 26.9299 | 20.7253 | 42.5886 | 14.6929 | 112.08 | 0 | 79% | 0 | 0 | 90% | 0 | 39.7497
6976 | 252 | 236 | 130 | 4.4 | 24.5 | 0 | 51.7007 | 15.9149 | 0 | 42.589 | 14.7987 | 0 | 40.3839 | 76% | 0 | 12.101 | 70.64% | 0 | 41.2084
6977 | 12 | 68 | 66 | 3.2 | 23 | 0 | 2.3715 | 0 | 0 | 56.6175 | 20.8671 | 0 | 54.2214 | 72% | 0 | 25 | 30.64% | 0 | 43.3027
6978 | 3 | 8 | 8 | 2.2 | 20.8 | 0 | 0 | 0 | 0 | 81.2059 | 31.5417 | 0 | 82.0323 | 66% | 0 | 12.899 | 10% | 0 | 41.7801
6979 | 0 | 0 | 0 | 1.3 | 18 | 0 | 0 | 0 | 0 | 102.5834 | 41.0595 | 0 | 104.2871 | 58% | 0 | 0 | 10% | 0 | 38.5
6980 | 0 | 0 | 0 | 0.8 | 16.9 | 0 | 0 | 0 | 0 | 95.7362 | 38.2782 | 0 | 95.5992 | 51% | 0 | 0 | 10% | 0 | 35.8507
6981 | 0 | 0 | 0 | 1.1 | 16.5 | 0 | 0 | 0 | 0 | 91.3305 | 36.4488 | 0 | 90.1073 | 44% | 0 | 0 | 10% | 0 | 34.0627
6982 | 0 | 0 | 0 | 0.4 | 14.9 | 0 | 0 | 0 | 0 | 86.8518 | 34.6629 | 0 | 84.6917 | 38% | 0 | 0 | 10% | 0 | 32.2778
6983 | 0 | 0 | 0 | 0.9 | 14.7 | 0 | 0 | 0 | 0 | 83.2334 | 33.1549 | 0 | 80.5107 | 32% | 0 | 0 | 10% | 0 | 30.7428
6984 | 0 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 0 | 81.8672 | 32.5217 | 0 | 79.2156 | 26% | 0 | 0 | 10% | 0 | 30.0675
6985 | 0 | 0 | 0 | 1.1 | 15 | 0 | 0 | 0 | 0 | 80.9978 | 32.1262 | 0 | 78.4417 | 20% | 0 | 0 | 10% | 0 | 29.6352
6986 | 0 | 0 | 0 | 1.9 | 14.9 | 0 | 0 | 0 | 0 | 80.6167 | 31.9602 | 0 | 78.1428 | 14% | 0 | 0 | 10% | 0 | 29.4373
6987 | 0 | 0 | 0 | 0.8 | 14.3 | 0 | 0 | 0 | 0 | 82.0546 | 32.6551 | 0 | 79.6685 | 8% | 0 | 0 | 10% | 0 | 30.1018
6988 | 0 | 0 | 0 | 1.2 | 13.7 | 0 | 0 | 0 | 0 | 86.2332 | 34.4804 | 0 | 84.5538 | 2% | 0 | 0 | 10% | 0 | 31.8952
6989 | 0 | 0 | 0 | 1.5 | 14.2 | 0 | 0 | 0 | 0 | 22.3406 | 8.9463 | 0 | 22.1227 | 0% | 0 | 0 | 10% | 0 | 6.4334
6990 | 0 | 0 | 0 | 0.9 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4641
6991 | 154 | 22 | 10 | 0.7 | 13.4 | 0 | 6.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4386
6992 | 639 | 181 | 38 | 0.8 | 16.6 | 88.6027 | 22.0987 | 16.694 | 0 | 0 | 0 | 85.153 | 0 | 6% | 0 | 0 | 10% | 0 | 15.1545
6993 | 784 | 363 | 55 | 0.6 | 20.4 | 178.2908 | 0 | 38.1894 | 0 | 0 | 0 | 175.639 | 0 | 20% | 0 | 0 | 10% | 0 | 36.2185
6994 | 881 | 532 | 59 | 1.1 | 22.6 | 227.7459 | 2.98e-14 | 57.656 | 0 | 0 | 0 | 225.8389 | 0 | 36% | 17.3645 | 0 | 33.62% | 0 | 37.852
6995 | 926 | 651 | 63 | 2.7 | 23.9 | 252.8295 | 0 | 63.3284 | 7.785 | 42.5599 | 3.0897 | 211.0692 | 0 | 52% | 25 | 0 | 67.62% | 0 | 38.2856
6996 | 926 | 709 | 75 | 4.4 | 24.9 | 256.8596 | 0 | 40.793 | 34.307 | 42.5779 | 14.7629 | 215.1387 | 0 | 68% | 16.4591 | 0 | 90% | 0 | 36.2954
6997 | 804 | 665 | 117 | 5.2 | 25 | 219.241 | -2.98e-14 | 23.0579 | 47.3909 | 42.5852 | 14.7575 | 177.6274 | 0 | 81% | 0 | 0 | 90% | 0 | 35.3464
6998 | 330 | 436 | 225 | 5.7 | 25.6 | 75.8631 | 0 | 21.5535 | 17.1055 | 42.5895 | 14.7097 | 34.6215 | 0 | 84% | 0 | 0 | 90% | 0 | 35.1262
6999 | 355 | 372 | 189 | 6.7 | 25.1 | 76.2727 | 0 | 20.3871 | 12.1033 | 42.5881 | 14.7503 | 34.142 | 0 | 86% | 0 | 0 | 90% | 0 | 35.378
7000 | 231 | 234 | 142 | 4.3 | 25.1 | 0 | 46.2125 | 15.9028 | 0 | 42.5859 | 14.7495 | 0 | 41.1282 | 83% | 0 | 8.5682 | 76.29% | 0 | 37.1204
7001 | 150 | 122 | 90 | 4.1 | 24.2 | 0 | 29.4052 | 5.0147 | 0 | 42.5829 | 14.8205 | 0 | 41.0812 | 80% | 0 | 22.5033 | 40.29% | 0 | 39.3627
7002 | 5 | 8 | 7 | 1.8 | 21.9 | 0 | 0 | 0 | 0 | 60.5482 | 22.6469 | 0 | 60.3211 | 76% | 0 | 18.9285 | 10% | 0 | 38.6137
7003 | 0 | 0 | 0 | 3.9 | 21.2 | 0 | 0 | 0 | 0 | 97.6937 | 38.7618 | 0 | 99.6523 | 69% | 0 | 0 | 10% | 0 | 35.8725
7004 | 0 | 0 | 0 | 3 | 19.8 | 0 | 0 | 0 | 0 | 91.9334 | 36.4663 | 0 | 91.9162 | 62% | 0 | 0 | 10% | 0 | 33.7788
7005 | 0 | 0 | 0 | 2.8 | 18.9 | 0 | 0 | 0 | 0 | 86.6136 | 34.2949 | 0 | 85.1773 | 55% | 0 | 0 | 10% | 0 | 31.6781
7006 | 0 | 0 | 0 | 5 | 20 | 0 | 0 | 0 | 0 | 82.138 | 32.3137 | 0 | 80.0082 | 50% | 0 | 0 | 10% | 0 | 29.6989
7007 | 0 | 0 | 0 | 7 | 20.7 | 0 | 0 | 0 | 0 | 79.8571 | 31.2265 | 0 | 77.7683 | 44% | 0 | 0 | 10% | 0 | 28.5863
7008 | 0 | 0 | 0 | 8.7 | 20.5 | 0 | 0 | 0 | 0 | 78.0502 | 30.4282 | 0 | 75.9966 | 38% | 0 | 0 | 10% | 0 | 27.7668
7009 | 0 | 0 | 0 | 7.9 | 20.5 | 0 | 0 | 0 | 0 | 76.5297 | 29.7479 | 0 | 74.5057 | 33% | 0 | 0 | 10% | 0 | 27.0686
7010 | 0 | 0 | 0 | 5.6 | 20.1 | 0 | 0 | 0 | 0 | 76.5965 | 29.8085 | 0 | 74.6127 | 27% | 0 | 0 | 10% | 0 | 27.1121
7011 | 0 | 0 | 0 | 4.5 | 19.8 | 0 | 0 | 0 | 0 | 77.8903 | 30.4109 | 0 | 75.9556 | 21% | 0 | 0 | 10% | 0 | 27.6981
7012 | 0 | 0 | 0 | 6.1 | 19.6 | 0 | 0 | 0 | 0 | 79.9643 | 31.3616 | 0 | 78.0874 | 16% | 0 | 0 | 10% | 0 | 28.6334
7013 | 0 | 0 | 0 | 6.8 | 17.3 | 0 | 0 | 0 | 0 | 80.9897 | 31.9837 | 0 | 79.1517 | 10% | 0 | 0 | 10% | 0 | 29.2431
7014 | 0 | 0 | 0 | 3.6 | 14.8 | 0 | 0 | 0 | 0 | 84.9999 | 33.8941 | 0 | 83.6279 | 4% | 0 | 0 | 10% | 0 | 31.1372
7015 | 2 | 6 | 6 | 3.6 | 14.5 | 0 | 0.071946 | 0 | 0 | 48.6993 | 19.5023 | 0 | 48.6358 | 0% | 0 | 0 | 10% | 0 | 16.795
7016 | 0 | 30 | 30 | 3.7 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.6237
7017 | 0 | 137 | 137 | 1.6 | 13.2 | 0 | 0 | 3.0103 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.41512
7018 | 0 | 96 | 95 | 2.5 | 14.6 | 0 | 0 | 0.40407 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1628
7019 | 0 | 136 | 134 | 1.9 | 14.9 | 0 | 0 | 2.5107 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.028647
7020 | 1 | 213 | 210 | 3 | 15.6 | 0 | 0.31806 | 7.635 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 5.1227
7021 | 10 | 269 | 258 | 3.7 | 16 | 0 | 3.174 | 12.0744 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.5887
7022 | 424 | 515 | 249 | 3.8 | 17.4 | 85.162 | 21.4734 | 49.6833 | 0 | 0 | 0 | 81.2697 | 0 | 6% | 16.9615 | 0 | 33.07% | 0 | 31.2061
7023 | 282 | 404 | 252 | 5 | 18.4 | 57.3926 | 0 | 33.264 | 0.68408 | 0 | 0 | 56.3316 | 0 | 10% | 0 | 0 | 33.07% | 0 | 32.3434
7024 | 582 | 347 | 142 | 4 | 19.3 | 120.2664 | 0 | 33.4075 | 0 | 42.3531 | 0 | 77.3087 | 0 | 16% | 12.659 | 0 | 50.28% | 0 | 18.7525
7025 | 298 | 121 | 66 | 3.2 | 18.2 | 0 | 57.9515 | 7.0832 | 0 | 42.4493 | 14.7119 | 0 | 40.2858 | 13% | 0 | 17.571 | 22.17% | 0 | 37.7295
7026 | 38 | 13 | 9 | 1.5 | 16.7 | 0 | 0 | 0 | 0 | 83.0595 | 32.7696 | 0 | 83.5409 | 7% | 0 | 7.6064 | 10% | 0 | 37.7463
7027 | 0 | 0 | 0 | 2.8 | 15.4 | 0 | 0 | 0 | 0 | 95.4455 | 38.2688 | 0 | 95.8459 | 0% | 0 | 0 | 10% | 0 | 35.6587
7028 | 0 | 0 | 0 | 0.9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.453
7029 | 0 | 0 | 0 | 1.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4278
7030 | 0 | 0 | 0 | 0.9 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4031
7031 | 0 | 0 | 0 | 2.2 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3787
7032 | 0 | 0 | 0 | 2.6 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3549
7033 | 0 | 0 | 0 | 1.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3316
7034 | 0 | 0 | 0 | 2.2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3086
7035 | 0 | 0 | 0 | 2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2861
7036 | 0 | 0 | 0 | 2.1 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.264
7037 | 0 | 0 | 0 | 1.2 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2423
7038 | 0 | 0 | 0 | 0.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2211
7039 | 19 | 11 | 9 | 0.9 | 8.8 | 0 | 0.58155 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2003
7040 | 492 | 161 | 55 | 1.3 | 11.8 | 63.5645 | 16.3915 | 13.7095 | 0 | 0 | 0 | 59.8544 | 0 | 4% | 0 | 0 | 10% | 0 | 12.4156
7041 | 330 | 231 | 101 | 0.8 | 13.4 | 64.7809 | 0 | 19.3615 | 0 | 0 | 0 | 62.8884 | 0 | 9% | 0 | 0 | 10% | 0 | 18.3736
7042 | 169 | 285 | 192 | 1.2 | 14.1 | 0 | 50.0385 | 20.666 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 10% | 0 | 19.4304
7043 | 93 | 338 | 275 | 0.8 | 15.6 | 0 | 28.9946 | 23.1616 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 10% | 0 | 21.0034
7044 | 108 | 351 | 273 | 0.8 | 16.5 | 0 | 34.3153 | 26.2994 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 10% | 0 | 24.1628
7045 | 263 | 549 | 363 | 1.2 | 17.6 | 49.5865 | 12.6128 | 48.9356 | 0 | 0 | 0 | 47.5298 | 0 | 13% | 7.3079 | 0 | 19.94% | 0 | 40.465
7046 | 14 | 383 | 369 | 0.7 | 18.4 | 0 | 4.3406 | 22.7098 | 0 | 42.1785 | 0 | 0 | 39.4262 | 10% | 0 | 6.2117 | 10% | 0 | 27.2003
7047 | 4 | 254 | 250 | 1.4 | 18.3 | 0 | 1.1654 | 11.5103 | 0 | 62.7184 | 17.1815 | 0 | 59.7005 | 5% | 0 | 0 | 10% | 0 | 26.2416
7048 | 28 | 200 | 188 | 4.5 | 17.4 | 0 | 7.1163 | 8.2527 | 0 | 70.7245 | 28.2152 | 0 | 69.8424 | 0% | 0 | 0 | 10% | 0 | 34.1893
7049 | 44 | 87 | 80 | 4.3 | 16.2 | 0 | 8.4886 | 1.7275 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.45559
7050 | 16 | 9 | 8 | 3 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1629
7051 | 0 | 0 | 0 | 2.9 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1432
7052 | 0 | 0 | 0 | 2.9 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1238
7053 | 0 | 0 | 0 | 1.7 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1047
7054 | 0 | 0 | 0 | 2 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.086
7055 | 0 | 0 | 0 | 1.5 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0677
7056 | 0 | 0 | 0 | 1.2 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0497
7057 | 0 | 0 | 0 | 2.2 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.032
7058 | 0 | 0 | 0 | 1.4 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0148
7059 | 0 | 0 | 0 | 1.6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9978
7060 | 0 | 0 | 0 | 1.4 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9812
7061 | 0 | 0 | 0 | 1.7 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9648
7062 | 0 | 0 | 0 | 1.8 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9488
7063 | 0 | 1 | 2 | 1.8 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9331
7064 | 0 | 6 | 6 | 1.8 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9177
7065 | 0 | 24 | 24 | 2.7 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9026
7066 | 0 | 45 | 45 | 3.6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8877
7067 | 0 | 93 | 92 | 2.7 | 10.8 | 0 | 0 | 0.27144 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6017
7068 | 0 | 89 | 88 | 2 | 11.2 | 0 | 0 | 0.086951 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7719
7069 | 0 | 126 | 125 | 1.8 | 11.5 | 0 | 0 | 2.0197 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.17488
7070 | 0 | 71 | 71 | 1.1 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8311
7071 | 0 | 59 | 59 | 1.4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8176
7072 | 0 | 40 | 40 | 0.9 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8044
7073 | 0 | 8 | 9 | 2.9 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7914
7074 | 0 | 0 | 0 | 1.8 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7787
7075 | 0 | 0 | 0 | 1.3 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7663
7076 | 0 | 0 | 0 | 2.2 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.754
7077 | 0 | 0 | 0 | 1.7 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.742
7078 | 0 | 0 | 0 | 1.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7302
7079 | 0 | 0 | 0 | 0.7 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7187
7080 | 0 | 0 | 0 | 0.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7074
7081 | 0 | 0 | 0 | 1.4 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6963
7082 | 0 | 0 | 0 | 0.9 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6854
7083 | 0 | 0 | 0 | 0.8 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6747
7084 | 0 | 0 | 0 | 1.2 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6642
7085 | 0 | 0 | 0 | 1.3 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.654
7086 | 0 | 0 | 0 | 0.9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6439
7087 | 53 | 14 | 10 | 1.8 | 8.3 | 0 | 1.0583 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.634
7088 | 513 | 159 | 50 | 1.2 | 10.8 | 65.8249 | 17.0124 | 14.094 | 0 | 0 | 0 | 58.3489 | 0 | 5% | 0 | 0 | 10% | 0 | 12.8714
7089 | 734 | 357 | 78 | 1.9 | 13.3 | 162.4917 | 0 | 39.0785 | 0 | 0 | 0 | 153.2653 | 0 | 17% | 0 | 0 | 10% | 0 | 37.2059
7090 | 712 | 539 | 170 | 4 | 14.1 | 177.4703 | 0 | 57.9076 | 0 | 41.8385 | 0 | 134.4604 | 0 | 28% | 14.5606 | 0 | 29.8% | 0 | 40.7761
7091 | 613 | 562 | 178 | 4.6 | 14.8 | 158.9217 | 0 | 57.9597 | 1.1481 | 42.1888 | 5.2915 | 117.3584 | 0 | 37% | 20.0384 | 0 | 57.05% | 0 | 40.9751
7092 | 886 | 707 | 118 | 5.3 | 16.3 | 242.6328 | 0 | 54.9496 | 20.1504 | 42.2874 | 15.226 | 199.9598 | 0 | 52% | 24.2246 | 0 | 90% | 0 | 43.2597
7093 | 771 | 669 | 158 | 5.1 | 17.1 | 208.1848 | 0 | 29.7259 | 44.3005 | 42.39 | 15.2219 | 166.7456 | 0 | 65% | 0 | 0 | 90% | 0 | 42.5562
7094 | 199 | 360 | 233 | 3.9 | 17 | 0 | 48.1807 | 28.1213 | 0.42987 | 43.28 | 15.5911 | 0 | 40.478 | 62% | 0 | 0 | 90% | 0 | 42.49
7095 | 9 | 181 | 175 | 4.8 | 16.5 | 0 | 2.6118 | 5.8463 | 0 | 42.4341 | 15.2686 | 0 | 39.7613 | 59% | 0 | 23.4371 | 52.5% | 0 | 42.3488
7096 | 1 | 53 | 53 | 6.6 | 15.1 | 0 | 0.25203 | 0 | 0 | 58.0643 | 21.9957 | 0 | 55.0786 | 55% | 0 | 25 | 12.5% | 0 | 44.7069
7097 | 0 | 16 | 16 | 2.4 | 14.1 | 0 | 0 | 0 | 0 | 121.7356 | 49.3381 | 0 | 126.7839 | 45% | 0 | 0 | 12.5% | 0 | 46.8967
7098 | 0 | 1 | 1 | 2.6 | 13 | 0 | 0 | 0 | 0 | 117.4204 | 47.6274 | 0 | 120.6156 | 36% | 0 | 0 | 12.5% | 0 | 45.3913
7099 | 0 | 0 | 0 | 2.5 | 12.9 | 0 | 0 | 0 | 0 | 106.9559 | 43.2687 | 0 | 107.6719 | 28% | 0 | 0 | 12.5% | 0 | 41.1616
7100 | 0 | 0 | 0 | 2.1 | 12.7 | 0 | 0 | 0 | 0 | 98.6739 | 39.7982 | 0 | 97.6827 | 20% | 0 | 0 | 12.5% | 0 | 37.7393
7101 | 0 | 0 | 0 | 2.7 | 12.3 | 0 | 0 | 0 | 0 | 92.3127 | 37.1424 | 0 | 90.2004 | 14% | 0 | 0 | 12.5% | 0 | 35.0854
7102 | 0 | 0 | 0 | 4.1 | 12.7 | 0 | 0 | 0 | 0 | 87.8251 | 35.2158 | 0 | 84.8833 | 7% | 0 | 0 | 12.5% | 0 | 33.1348
7103 | 0 | 0 | 0 | 5.1 | 12.7 | 0 | 0 | 0 | 0 | 84.8687 | 33.9691 | 0 | 81.5385 | 1% | 0 | 0 | 12.5% | 0 | 31.8475
7104 | 0 | 0 | 0 | 5.4 | 12.8 | 0 | 0 | 0 | 0 | 11.2746 | 4.509 | 0 | 10.8202 | 0% | 0 | 0 | 12.5% | 0 | 2.4251
7105 | 0 | 0 | 0 | 3.3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.5% | 0 | -2.0549
7106 | 0 | 0 | 0 | 2.2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.5% | 0 | -2.0372
7107 | 0 | 0 | 0 | 3.4 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.5% | 0 | -2.0198
7108 | 0 | 0 | 0 | 4.2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.5% | 0 | -2.0027
7109 | 0 | 0 | 0 | 4.6 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.5% | 0 | -1.9859
7110 | 0 | 0 | 0 | 2.3 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.5% | 0 | -1.9695
7111 | 75 | 17 | 10 | 1.4 | 11.3 | 0 | 1.1029 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.5% | 0 | -1.9534
7112 | 595 | 169 | 46 | 1.5 | 12.4 | 78.2694 | 19.9033 | 16.4267 | 0 | 0 | 0 | 74.186 | 0 | 6% | 0 | 0 | 12.5% | 0 | 15.0475
7113 | 788 | 361 | 65 | 1 | 16 | 175.7559 | 0 | 40.0618 | 0 | 0 | 0 | 171.8081 | 0 | 19% | 0 | 0 | 12.5% | 0 | 38.0863
7114 | 888 | 517 | 60 | 1 | 17.5 | 227.4816 | 0 | 59.0587 | 0 | 42.4075 | 0 | 185.5347 | 0 | 33% | 16.836 | 0 | 35.4% | 0 | 39.2171
7115 | 933 | 633 | 62 | 2.1 | 18.5 | 253.8355 | 0 | 57.4625 | 15.0485 | 42.5068 | 13.3252 | 212.4523 | 0 | 49% | 25 | 0 | 69.4% | 0 | 42.952
7116 | 949 | 691 | 65 | 1.2 | 19.3 | 264.0645 | 0 | 44.9365 | 30.1635 | 42.5463 | 15.1521 | 222.6848 | 0 | 66% | 15.1488 | 0 | 90% | 0 | 42.0412
7117 | 943 | 682 | 67 | 2.7 | 20.1 | 260.961 | 0 | 29.4128 | 45.6872 | 42.5611 | 15.1076 | 219.5686 | 0 | 82% | 0 | 0 | 90% | 0 | 41.632
7118 | 921 | 611 | 63 | 3.9 | 20.6 | 247.8573 | 0 | 27.5752 | 41.8616 | 42.5724 | 15.0789 | 206.2243 | 0 | 98% | 0 | 0 | 90% | 0 | 41.2361
7119 | 874 | 486 | 59 | 3.6 | 20.6 | 71.8742 | 169.8766 | 25.6081 | 29.1309 | 42.5795 | 15.0814 | 30.3498 | 0 | 100% | 0 | 0 | 90% | 0 | 41.2297
7120 | 784 | 316 | 48 | 4.7 | 19.7 | 42.1527 | 146.4796 | 27.716 | 6.7411 | 42.5781 | 15.1387 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.5663
7121 | 525 | 124 | 30 | 2.3 | 19 | 42.1581 | 43.2681 | 10.1437 | 0 | 42.5762 | 15.1813 | 0 | 0 | 100% | 0 | 20.1659 | 57.73% | 0 | 46.2028
7122 | 14 | 6 | 4 | 2 | 15.9 | 0 | 0 | 0 | 0 | 58.7653 | 22.2438 | 0 | 57.2908 | 96% | 0 | 25 | 17.73% | 0 | 45.179
7123 | 0 | 0 | 0 | 1.4 | 14.4 | 0 | 0 | 0 | 0 | 98.4272 | 39.4369 | 0 | 102.0709 | 88% | 0 | 4.8341 | 10% | 0 | 41.3159
7124 | 0 | 0 | 0 | 1.6 | 13.5 | 0 | 0 | 0 | 0 | 99.7453 | 40.1922 | 0 | 100.0018 | 81% | 0 | 0 | 10% | 0 | 37.8794
7125 | 0 | 0 | 0 | 1.3 | 13 | 0 | 0 | 0 | 0 | 93.5905 | 37.6377 | 0 | 92.3111 | 74% | 0 | 0 | 10% | 0 | 35.44
7126 | 0 | 0 | 0 | 0.7 | 11.7 | 0 | 0 | 0 | 0 | 88.3679 | 35.4904 | 0 | 86.0062 | 67% | 0 | 0 | 10% | 0 | 33.2769
7127 | 0 | 0 | 0 | 1.2 | 12 | 0 | 0 | 0 | 0 | 85.3723 | 34.2101 | 0 | 82.6722 | 61% | 0 | 0 | 10% | 0 | 31.9257
7128 | 0 | 0 | 0 | 2.7 | 12.9 | 0 | 0 | 0 | 0 | 84.2465 | 33.6871 | 0 | 81.5734 | 55% | 0 | 0 | 10% | 0 | 31.328
7129 | 0 | 0 | 0 | 2.3 | 12.1 | 0 | 0 | 0 | 0 | 83.5544 | 33.44 | 0 | 80.9453 | 49% | 0 | 0 | 10% | 0 | 31.0186
7130 | 0 | 0 | 0 | 1.9 | 12.4 | 0 | 0 | 0 | 0 | 85.0557 | 34.0555 | 0 | 82.8649 | 43% | 0 | 0 | 10% | 0 | 31.5801
7131 | 0 | 0 | 0 | 0.9 | 10.8 | 0 | 0 | 0 | 0 | 92.5496 | 37.314 | 0 | 92.0605 | 36% | 0 | 0 | 10% | 0 | 34.7952
7132 | 0 | 0 | 0 | 1.1 | 10.4 | 0 | 0 | 0 | 0 | 105.5205 | 42.8065 | 0 | 107.6261 | 28% | 0 | 0 | 10% | 0 | 40.2871
7133 | 0 | 0 | 0 | 1.6 | 11 | 0 | 0 | 0 | 0 | 113.0872 | 45.9354 | 0 | 116.2665 | 19% | 0 | 0 | 10% | 0 | 43.4852
7134 | 0 | 0 | 0 | 1 | 10.3 | 0 | 0 | 0 | 0 | 114.9068 | 46.7332 | 0 | 118.0172 | 10% | 0 | 0 | 10% | 0 | 44.3739
7135 | 81 | 15 | 8 | 1.4 | 11.4 | 0 | 0.7684 | 0 | 0 | 115.5487 | 46.9446 | 0 | 118.4071 | 1% | 0 | 0 | 10% | 0 | 44.6647
7136 | 614 | 161 | 37 | 0.5 | 13.7 | 81.1344 | 20.4527 | 16.0612 | 0 | 76.254 | 30.0681 | 19.4539 | 13.7788 | 2% | 0 | 0 | 10% | 0 | 44.6167
7137 | 821 | 353 | 49 | 0.7 | 17.2 | 183.3659 | 0 | 39.9542 | 0 | 43.8106 | 15.7908 | 140.1819 | 0 | 12% | 9.0525 | 0 | 22.31% | 0 | 44.6286
7138 | 905 | 517 | 55 | 0.6 | 20.2 | 232.0607 | 0 | 56.4792 | 2.6715 | 42.6018 | 15.1155 | 190.6956 | 0 | 27% | 25 | 0 | 56.31% | 0 | 44.0804
7139 | 945 | 633 | 59 | 1.4 | 20.9 | 257.5187 | 0 | 55.1382 | 17.3872 | 42.6095 | 15.0724 | 216.2558 | 0 | 43% | 24.771 | 0 | 90% | 0 | 42.6702
7140 | 960 | 690 | 62 | 1.2 | 21.6 | 267.0977 | 0 | 29.5772 | 45.5228 | 42.6122 | 15.0255 | 225.8192 | 0 | 60% | 0 | 0 | 90% | 0 | 41.7168
7141 | 956 | 682 | 62 | 1.8 | 22.3 | 265.039 | 0 | 28.9929 | 46.1071 | 42.613 | 14.976 | 223.6429 | 0 | 76% | 0 | 0 | 90% | 0 | 41.0746
7142 | 932 | 610 | 61 | 3.1 | 22.5 | 251.4836 | 0 | 28.4496 | 41.1113 | 42.613 | 14.9612 | 209.8903 | 0 | 92% | 0 | 0 | 90% | 0 | 40.6234
7143 | 880 | 482 | 56 | 3.2 | 22.3 | 151.6716 | 79.0042 | 24.6013 | 29.8194 | 42.6122 | 14.9757 | 109.9106 | 0 | 100% | 0 | 0 | 90% | 0 | 40.4652
7144 | 780 | 311 | 48 | 3.7 | 21.5 | 42.1525 | 144.8969 | 26.6135 | 7.3728 | 42.6107 | 15.0319 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.3566
7145 | 529 | 123 | 31 | 3.3 | 20.1 | 42.158 | 42.8809 | 10.2916 | 0 | 42.6079 | 15.1242 | 0 | 0 | 100% | 0 | 18.2575 | 60.79% | 0 | 44.3849
7146 | 10 | 6 | 4 | 2.3 | 17.2 | 0 | 0 | 0 | 0 | 54.5599 | 20.3648 | 0 | 53.0335 | 96% | 0 | 25 | 20.79% | 0 | 43.3004
7147 | 0 | 0 | 0 | 0.6 | 15.4 | 0 | 0 | 0 | 0 | 90.2472 | 35.8855 | 0 | 92.838 | 89% | 0 | 6.7425 | 10% | 0 | 39.6727
7148 | 0 | 0 | 0 | 0.5 | 14.5 | 0 | 0 | 0 | 0 | 97.6997 | 39.2661 | 0 | 97.9232 | 82% | 0 | 0 | 10% | 0 | 36.8562
7149 | 0 | 0 | 0 | 0.5 | 13.5 | 0 | 0 | 0 | 0 | 92.4896 | 37.1362 | 0 | 91.2384 | 75% | 0 | 0 | 10% | 0 | 34.8525
7150 | 0 | 0 | 0 | 0.6 | 13.1 | 0 | 0 | 0 | 0 | 87.1642 | 34.9032 | 0 | 84.8165 | 69% | 0 | 0 | 10% | 0 | 32.6109
7151 | 0 | 0 | 0 | 0.9 | 12.7 | 0 | 0 | 0 | 0 | 83.0223 | 33.1807 | 0 | 80.1547 | 63% | 0 | 0 | 10% | 0 | 30.8213
7152 | 0 | 0 | 0 | 1 | 12.2 | 0 | 0 | 0 | 0 | 81.1227 | 32.3379 | 0 | 78.4789 | 57% | 0 | 0 | 10% | 0 | 29.8975
7153 | 0 | 0 | 0 | 0.8 | 11.8 | 0 | 0 | 0 | 0 | 80.6539 | 32.1452 | 0 | 78.1735 | 51% | 0 | 0 | 10% | 0 | 29.6449
7154 | 0 | 0 | 0 | 1.2 | 12.3 | 0 | 0 | 0 | 0 | 80.3806 | 31.9952 | 0 | 78.022 | 45% | 0 | 0 | 10% | 0 | 29.4493
7155 | 0 | 0 | 0 | 0.7 | 11.9 | 0 | 0 | 0 | 0 | 81.7868 | 32.6596 | 0 | 79.5409 | 39% | 0 | 0 | 10% | 0 | 30.0759
7156 | 0 | 0 | 0 | 1.1 | 11.7 | 0 | 0 | 0 | 0 | 86.2576 | 34.5986 | 0 | 84.7154 | 33% | 0 | 0 | 10% | 0 | 31.9798
7157 | 0 | 0 | 0 | 1.2 | 12.4 | 0 | 0 | 0 | 0 | 91.4426 | 36.7579 | 0 | 91.0525 | 26% | 0 | 0 | 10% | 0 | 34.1242
7158 | 0 | 0 | 0 | 2.1 | 12.9 | 0 | 0 | 0 | 0 | 97.7775 | 39.4039 | 0 | 98.6469 | 19% | 0 | 0 | 10% | 0 | 36.7819
7159 | 76 | 14 | 7 | 2.1 | 13.3 | 0 | 0.3284 | 0 | 0 | 101.8007 | 41.073 | 0 | 103.3059 | 11% | 0 | 0 | 10% | 0 | 38.4916
7160 | 628 | 161 | 35 | 1.3 | 16 | 82.5806 | 20.7197 | 16.2033 | 0 | 62.9392 | 24.0447 | 31.2263 | 11.5138 | 13% | 0 | 0 | 10% | 0 | 38.6891
7161 | 822 | 351 | 49 | 2.1 | 18.4 | 182.3459 | -2.98e-14 | 39.8363 | 0 | 43.9697 | 15.791 | 138.3584 | 0 | 23% | 15.0569 | 0 | 30.48% | 0 | 38.521
7162 | 909 | 517 | 56 | 1.4 | 21.5 | 232.457 | 2.98e-14 | 51.0588 | 8.1921 | 42.5651 | 15.0158 | 190.4217 | 0 | 37% | 25 | 0 | 64.48% | 0 | 38.5638
7163 | 948 | 632 | 60 | 1.7 | 22 | 258.1366 | 0 | 44.3026 | 28.2467 | 42.5872 | 14.9892 | 216.2796 | 0 | 53% | 18.7666 | 0 | 90% | 0 | 37.7527
7164 | 960 | 686 | 62 | 1.5 | 22.7 | 266.7878 | 0 | 23.9291 | 51.1709 | 42.5948 | 14.9399 | 224.9403 | 0 | 70% | 0 | 0 | 90% | 0 | 35.9941
7165 | 952 | 676 | 62 | 1.3 | 23.9 | 263.9566 | 0 | 23.0234 | 52.0766 | 42.5997 | 14.85 | 222.0094 | 0 | 86% | 0 | 0 | 90% | 0 | 34.9987
7166 | 927 | 604 | 61 | 2.5 | 24.1 | 230.8726 | 22.1626 | 17.3517 | 51.3607 | 42.6023 | 14.8352 | 188.7692 | 0 | 100% | 0 | 0 | 90% | 0 | 34.7943
7167 | 878 | 477 | 56 | 3.3 | 24 | 42.1522 | 204.5045 | 19.1587 | 34.7394 | 42.603 | 14.8434 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 34.7128
7168 | 777 | 306 | 47 | 3.2 | 23.2 | 42.1577 | 143.4416 | 21.2388 | 12.234 | 42.6004 | 14.9042 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 36.8539
7169 | 525 | 117 | 29 | 2.8 | 21.9 | 42.1578 | 41.3923 | 9.9039 | 0 | 42.5979 | 14.9998 | 0 | 0 | 100% | 0 | 13.3172 | 68.69% | 0 | 38.9322
7170 | 9 | 5 | 3 | 1.2 | 18.9 | 0 | 0 | 0 | 0 | 44.6473 | 16.0403 | 0 | 43.1357 | 97% | 0 | 24.6226 | 29.3% | 0 | 38.6059
7171 | 0 | 0 | 0 | 1.4 | 16.8 | 0 | 0 | 0 | 0 | 69.8875 | 27.0939 | 0 | 70.1849 | 92% | 0 | 12.0601 | 10% | 0 | 36.2258
7172 | 0 | 0 | 0 | 1.8 | 14.8 | 0 | 0 | 0 | 0 | 92.119 | 36.8966 | 0 | 92.0244 | 85% | 0 | 0 | 10% | 0 | 34.2576
7173 | 0 | 0 | 0 | 1.9 | 14.3 | 0 | 0 | 0 | 0 | 86.7866 | 34.6718 | 0 | 85.0571 | 79% | 0 | 0 | 10% | 0 | 32.1696
7174 | 0 | 0 | 0 | 1.7 | 14.3 | 0 | 0 | 0 | 0 | 81.9307 | 32.5882 | 0 | 79.5877 | 73% | 0 | 0 | 10% | 0 | 30.057
7175 | 0 | 0 | 0 | 1 | 13.2 | 0 | 0 | 0 | 0 | 78.8833 | 31.2648 | 0 | 76.6815 | 67% | 0 | 0 | 10% | 0 | 28.6726
7176 | 0 | 0 | 0 | 0.7 | 12.5 | 0 | 0 | 0 | 0 | 77.0767 | 30.4865 | 0 | 74.9707 | 61% | 0 | 0 | 10% | 0 | 27.8523
7177 | 0 | 0 | 0 | 1.2 | 12.1 | 0 | 0 | 0 | 0 | 75.4726 | 29.7869 | 0 | 73.4311 | 56% | 0 | 0 | 10% | 0 | 27.1221
7178 | 0 | 0 | 0 | 2 | 12.8 | 0 | 0 | 0 | 0 | 75.014 | 29.5452 | 0 | 73.0278 | 51% | 0 | 0 | 10% | 0 | 26.8561
7179 | 0 | 0 | 0 | 2.1 | 13.6 | 0 | 0 | 0 | 0 | 75.5986 | 29.7639 | 0 | 73.6649 | 45% | 0 | 0 | 10% | 0 | 27.0547
7180 | 0 | 0 | 0 | 1.6 | 12 | 0 | 0 | 0 | 0 | 76.8447 | 30.4109 | 0 | 74.9625 | 40% | 0 | 0 | 10% | 0 | 27.6842
7181 | 0 | 0 | 0 | 1.9 | 11.9 | 0 | 0 | 0 | 0 | 78.2635 | 31.0576 | 0 | 76.4292 | 34% | 0 | 0 | 10% | 0 | 28.3163
7182 | 0 | 0 | 0 | 2.4 | 12.7 | 0 | 0 | 0 | 0 | 81.7608 | 32.6086 | 0 | 80.0076 | 28% | 0 | 0 | 10% | 0 | 29.8524
7183 | 70 | 14 | 8 | 1.6 | 11.3 | 0 | 0 | 0 | 0 | 88.3266 | 35.4953 | 0 | 87.7005 | 22% | 0 | 0 | 10% | 0 | 32.7208
7184 | 569 | 148 | 37 | 1.8 | 14.7 | 72.9296 | 18.478 | 14.5486 | 0 | 56.0983 | 21.165 | 27.2311 | 10.5117 | 23% | 0 | 0 | 10% | 0 | 34.2016
7185 | 795 | 343 | 53 | 2.2 | 16.6 | 175.1825 | 0 | 39.0012 | 0 | 43.9302 | 15.8743 | 130.6961 | 0 | 32% | 18.2843 | 0 | 34.87% | 0 | 34.6089
7186 | 867 | 505 | 68 | 2.3 | 18.7 | 220.107 | 0 | 46.7338 | 11.3555 | 42.5483 | 15.1888 | 177.6672 | 0 | 45% | 25 | 0 | 68.87% | 0 | 34.5252
7187 | 906 | 617 | 73 | 2.2 | 19.9 | 245.5516 | 0 | 38.2248 | 32.7744 | 42.5718 | 15.1241 | 203.2739 | 0 | 60% | 15.5393 | 0 | 90% | 0 | 35.156
7188 | 930 | 672 | 71 | 1.6 | 21.2 | 257.7257 | 0 | 22.2276 | 52.8724 | 42.5806 | 15.0419 | 215.432 | 0 | 76% | 0 | 0 | 90% | 0 | 34.776
7189 | 925 | 663 | 70 | 1.4 | 22.1 | 255.7964 | 0 | 17.7595 | 57.3405 | 42.5879 | 14.982 | 213.449 | 0 | 92% | 0 | 0 | 90% | 0 | 33.2677
7190 | 808 | 567 | 96 | 2.4 | 22.7 | 154.7231 | 70.3122 | 16.2398 | 47.0797 | 42.5926 | 14.9392 | 112.8565 | 0 | 100% | 0 | 0 | 90% | 0 | 32.4605
7191 | 540 | 405 | 155 | 3.5 | 21.5 | 42.1526 | 104.0046 | 16.8406 | 25.3363 | 42.5926 | 15.0255 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 32.5773
7192 | 292 | 187 | 83 | 3.1 | 20.6 | 0 | 59.3066 | 14.2034 | 0 | 42.5895 | 15.085 | 0 | 41.0983 | 97% | 0 | 7.7101 | 77.66% | 0 | 34.9284
7193 | 340 | 99 | 45 | 2.6 | 19 | 0 | 49.4738 | 6.3084 | 0 | 42.587 | 15.1851 | 0 | 40.9941 | 94% | 0 | 18.81 | 47.57% | 0 | 37.3899
7194 | 3 | 4 | 4 | 1.7 | 17 | 0 | 0 | 0 | 0 | 48.195 | 17.6765 | 0 | 46.8232 | 91% | 0 | 23.4799 | 10% | 0 | 38.272
7195 | 0 | 0 | 0 | 1.3 | 15.8 | 0 | 0 | 0 | 0 | 101.6162 | 40.8191 | 0 | 104.3988 | 83% | 0 | 0 | 10% | 0 | 37.9455
7196 | 0 | 0 | 0 | 0.7 | 15 | 0 | 0 | 0 | 0 | 95.7769 | 38.4284 | 0 | 95.8644 | 76% | 0 | 0 | 10% | 0 | 35.9583
7197 | 0 | 0 | 0 | 0.6 | 14.3 | 0 | 0 | 0 | 0 | 88.5855 | 35.4318 | 0 | 86.7871 | 69% | 0 | 0 | 10% | 0 | 33.0583
7198 | 0 | 0 | 0 | 0.5 | 13.5 | 0 | 0 | 0 | 0 | 83.3791 | 33.2872 | 0 | 80.7099 | 63% | 0 | 0 | 10% | 0 | 30.8819
7199 | 0 | 0 | 0 | 1.2 | 13.5 | 0 | 0 | 0 | 0 | 80.6472 | 32.0511 | 0 | 78.1023 | 57% | 0 | 0 | 10% | 0 | 29.5765
7200 | 0 | 0 | 0 | 1.3 | 13.3 | 0 | 0 | 0 | 0 | 78.9091 | 31.2729 | 0 | 76.5004 | 52% | 0 | 0 | 10% | 0 | 28.745
7201 | 0 | 0 | 0 | 0.6 | 12.6 | 0 | 0 | 0 | 0 | 78.349 | 31.0582 | 0 | 76.0476 | 46% | 0 | 0 | 10% | 0 | 28.4884
7202 | 0 | 0 | 0 | 0.5 | 11.8 | 0 | 0 | 0 | 0 | 78.7597 | 31.2869 | 0 | 76.5492 | 40% | 0 | 0 | 10% | 0 | 28.683
7203 | 0 | 0 | 0 | 1.3 | 11.7 | 0 | 0 | 0 | 0 | 81.1274 | 32.3708 | 0 | 79.0155 | 34% | 0 | 0 | 10% | 0 | 29.7369
7204 | 0 | 0 | 0 | 1.4 | 12 | 0 | 0 | 0 | 0 | 90.3209 | 36.3046 | 0 | 89.8028 | 28% | 0 | 0 | 10% | 0 | 33.6353
7205 | 0 | 0 | 0 | 0.7 | 12.3 | 0 | 0 | 0 | 0 | 101.572 | 41.0376 | 0 | 103.3882 | 20% | 0 | 0 | 10% | 0 | 38.3703
7206 | 0 | 0 | 0 | 0.3 | 12 | 0 | 0 | 0 | 0 | 108.2493 | 43.8594 | 0 | 111.1552 | 12% | 0 | 0 | 10% | 0 | 41.2513
7207 | 14 | 17 | 14 | 0.8 | 12.2 | 0 | 0 | 0 | 0 | 111.0276 | 45.007 | 0 | 114.099 | 3% | 0 | 0 | 10% | 0 | 42.4783
7208 | 177 | 151 | 103 | 0.4 | 14.4 | 0 | 35.3042 | 8.0072 | 0 | 44.3115 | 17.7773 | 0 | 43.962 | 0% | 0 | 0 | 10% | 0 | 23.4341
7209 | 5 | 139 | 136 | 0.4 | 15.6 | 0 | 1.2907 | 3.277 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.99797
7210 | 2 | 195 | 193 | 1.1 | 15.8 | 0 | 0.58518 | 6.8773 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.6203
7211 | 4 | 252 | 246 | 1.8 | 16.8 | 0 | 1.2398 | 10.9342 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 8.6989
7212 | 17 | 319 | 304 | 2.2 | 17.7 | 0 | 5.3636 | 16.8251 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 14.6111
7213 | 39 | 332 | 302 | 2.9 | 18.1 | 0 | 12.2771 | 21.938 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 19.7449
7214 | 787 | 607 | 145 | 2.4 | 19.8 | 170.4922 | 41.5224 | 67.6837 | 0 | 0 | 0 | 162.9915 | 0 | 12% | 24.102 | 0 | 42.78% | 0 | 41.3834
7215 | 786 | 453 | 76 | 2.2 | 21 | 193.7681 | 0 | 50.2558 | 0 | 42.7021 | 2.0102 | 151.8681 | 0 | 24% | 22.4841 | 0 | 73.36% | 0 | 27.1686
7216 | 659 | 282 | 63 | 2.5 | 21 | 134.5633 | 0 | 29.7164 | 0 | 43.7657 | 15.5434 | 92.3766 | 0 | 31% | 0 | 0 | 73.36% | 0 | 43.6014
7217 | 332 | 94 | 36 | 2.6 | 19.2 | 0 | 47.3918 | 5.6332 | 0 | 44.6821 | 16.0419 | 0 | 42.1559 | 28% | 0 | 25 | 33.36% | 0 | 45.2334
7218 | 1 | 2 | 2 | 2.3 | 16.7 | 0 | 0 | 0 | 0 | 84.8497 | 33.372 | 0 | 85.1549 | 21% | 0 | 14.5982 | 10% | 0 | 45.5221
7219 | 0 | 0 | 0 | 0.9 | 15.3 | 0 | 0 | 0 | 0 | 114.1975 | 46.1138 | 0 | 117.5721 | 13% | 0 | 0 | 10% | 0 | 43.6622
7220 | 0 | 0 | 0 | 0.3 | 14.7 | 0 | 0 | 0 | 0 | 103.596 | 41.737 | 0 | 104.5293 | 5% | 0 | 0 | 10% | 0 | 39.3953
7221 | 0 | 0 | 0 | 0.4 | 13.9 | 0 | 0 | 0 | 0 | 62.0461 | 24.9409 | 0 | 61.5451 | 0% | 0 | 0 | 10% | 0 | 22.6938
7222 | 0 | 0 | 0 | 0.8 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1568
7223 | 0 | 0 | 0 | 0.8 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1371
7224 | 0 | 0 | 0 | 0.7 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1178
7225 | 0 | 0 | 0 | 0.3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0989
7226 | 0 | 0 | 0 | 0.3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0803
7227 | 0 | 0 | 0 | 0.6 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0621
7228 | 0 | 0 | 0 | 1.4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0441
7229 | 0 | 0 | 0 | 0.8 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0266
7230 | 0 | 0 | 0 | 0.7 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0094
7231 | 30 | 10 | 7 | 1.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9925
7232 | 531 | 142 | 38 | 1.5 | 16 | 65.8639 | 16.7733 | 13.3787 | 0 | 0 | 0 | 62.3884 | 0 | 5% | 0 | 0 | 10% | 0 | 12.1016
7233 | 760 | 328 | 56 | 0.8 | 18.2 | 165.9231 | 0 | 37.1532 | 0 | 0 | 0 | 161.6393 | 0 | 17% | 0 | 0 | 10% | 0 | 35.2714
7234 | 851 | 489 | 65 | 1.1 | 20.2 | 215.2796 | 0 | 56.2343 | 0 | 42.3839 | 0 | 173.2333 | 0 | 30% | 14.4504 | 0 | 29.65% | 0 | 38.8956
7235 | 898 | 605 | 71 | 2.2 | 21.1 | 242.4919 | 0 | 60.0294 | 9.6803 | 42.5002 | 11.2007 | 201.0245 | 0 | 46% | 24.4096 | 0 | 62.85% | 0 | 44.0308
7236 | 918 | 662 | 74 | 1.9 | 22.8 | 253.2792 | 0 | 50.5625 | 24.5375 | 42.5375 | 14.9124 | 211.8371 | 0 | 62% | 19.9636 | 0 | 90% | 0 | 42.7264
7237 | 908 | 653 | 77 | 2.5 | 23.4 | 249.5054 | 0 | 29.7573 | 44.9435 | 42.5563 | 14.8734 | 208.0854 | 0 | 77% | 0 | 0 | 90% | 0 | 41.8615
7238 | 881 | 584 | 77 | 3.1 | 23.4 | 235.0984 | 0 | 29.5137 | 37.2219 | 42.5689 | 14.8778 | 193.5175 | 0 | 92% | 0 | 0 | 90% | 0 | 41.7442
7239 | 779 | 447 | 80 | 2.3 | 23.6 | 155.6236 | 42.0464 | 26.4568 | 23.2578 | 42.5767 | 14.8651 | 113.85 | 0 | 100% | 0 | 0 | 90% | 0 | 42.1737
7240 | 589 | 269 | 76 | 2.3 | 23.2 | 45.4243 | 89.2525 | 27.1584 | 0 | 45.7967 | 16.2159 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.0788
7241 | 314 | 95 | 43 | 2.7 | 20.7 | 0 | 56.9589 | 5.8318 | 0 | 46.0299 | 16.505 | 0 | 44.5092 | 97% | 0 | 24.9859 | 50.02% | 0 | 45.2626
7242 | 2 | 3 | 3 | 1.6 | 17.5 | 0 | 0 | 0 | 0 | 61.3012 | 23.2448 | 0 | 59.7354 | 92% | 0 | 25 | 10.02% | 0 | 45.3111
7243 | 0 | 0 | 0 | 0.5 | 16.2 | 0 | 0 | 0 | 0 | 115.6634 | 46.6513 | 0 | 121.8201 | 83% | 0 | 0 | 10.02% | 0 | 43.7086
7244 | 0 | 0 | 0 | 0.2 | 15.5 | 0 | 0 | 0 | 0 | 104.2535 | 41.9524 | 0 | 104.9969 | 76% | 0 | 0 | 10.02% | 0 | 39.744
7245 | 0 | 0 | 0 | 0.9 | 15 | 0 | 0 | 0 | 0 | 95.7045 | 38.3986 | 0 | 94.3899 | 68% | 0 | 0 | 10.02% | 0 | 36.3123
7246 | 0 | 0 | 0 | 1.4 | 14.6 | 0 | 0 | 0 | 0 | 90.6781 | 36.2995 | 0 | 88.4211 | 62% | 0 | 0 | 10.02% | 0 | 34.1915
7247 | 0 | 0 | 0 | 1.9 | 15.6 | 0 | 0 | 0 | 0 | 86.9998 | 34.6805 | 0 | 84.2169 | 55% | 0 | 0 | 10.02% | 0 | 32.5115
7248 | 0 | 0 | 0 | 1.9 | 14.9 | 0 | 0 | 0 | 0 | 84.2102 | 33.5525 | 0 | 81.1617 | 49% | 0 | 0 | 10.02% | 0 | 31.3111
7249 | 0 | 0 | 0 | 0.4 | 13.7 | 0 | 0 | 0 | 0 | 83.1246 | 33.1698 | 0 | 80.1133 | 43% | 0 | 0 | 10.02% | 0 | 30.8552
7250 | 0 | 0 | 0 | 2 | 14.3 | 0 | 0 | 0 | 0 | 83.3552 | 33.2311 | 0 | 80.5675 | 37% | 0 | 0 | 10.02% | 0 | 30.8522
7251 | 0 | 0 | 0 | 2.1 | 14.4 | 0 | 0 | 0 | 0 | 85.1966 | 33.9987 | 0 | 82.8787 | 31% | 0 | 0 | 10.02% | 0 | 31.567
7252 | 0 | 0 | 0 | 2.2 | 14.7 | 0 | 0 | 0 | 0 | 93.0378 | 37.2981 | 0 | 92.502 | 24% | 0 | 0 | 10.02% | 0 | 34.8213
7253 | 0 | 0 | 0 | 2.7 | 14.7 | 0 | 0 | 0 | 0 | 104.1194 | 41.9578 | 0 | 105.7566 | 16% | 0 | 0 | 10.02% | 0 | 39.4759
7254 | 0 | 0 | 0 | 2.7 | 15.2 | 0 | 0 | 0 | 0 | 109.6406 | 44.2233 | 0 | 112.0628 | 8% | 0 | 0 | 10.02% | 0 | 41.7902
7255 | 5 | 7 | 6 | 1.9 | 14.6 | 0 | 0 | 0 | 0 | 99.9875 | 40.3983 | 0 | 102.2784 | 0% | 0 | 0 | 10.02% | 0 | 38.0506
7256 | 236 | 120 | 68 | 1.5 | 15.8 | 0 | 46.4897 | 6.9552 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.02% | 0 | 4.8027
7257 | 393 | 293 | 151 | 0.5 | 19.8 | 63.0306 | 15.775 | 26.5405 | 0 | 0 | 0 | 60.7341 | 0 | 5% | 0 | 0 | 10.02% | 0 | 25.2654
7258 | 487 | 474 | 229 | 0.6 | 22.2 | 116.1071 | 0 | 45.4961 | 1.4161 | 0 | 0 | 114.0003 | 0 | 13% | 0 | 0 | 10.02% | 0 | 44.0599
7259 | 349 | 511 | 295 | 1.2 | 23.1 | 83.8757 | -1.49e-14 | 45.2649 | 2.4165 | 0 | 0 | 82.8979 | 0 | 19% | 0 | 0 | 10.02% | 0 | 44.0991
7260 | 864 | 652 | 105 | 1.8 | 23.9 | 236.9783 | 0 | 70.5532 | 3.771 | 0 | 0 | 233.5845 | 0 | 37% | 25 | 0 | 44.02% | 0 | 43.0214
7261 | 707 | 609 | 162 | 1.5 | 24.6 | 190.5902 | 0 | 66.6329 | 0 | 0 | 0 | 189.4798 | 0 | 51% | 22.979 | 0 | 75.27% | 0 | 41.4894
7262 | 634 | 542 | 182 | 2.9 | 24.6 | 163.914 | -8.4e-15 | 49.6721 | 9.0298 | 42.5765 | 2.4798 | 122.8913 | 0 | 61% | 10.8279 | 0 | 90% | 0 | 38.947
7263 | 286 | 295 | 161 | 3.7 | 23.7 | 58.1263 | 0 | 25.395 | 0 | 42.5801 | 14.8586 | 17.6797 | 0 | 62% | 0 | 3.0232 | 85.16% | 0 | 42.298
7264 | 57 | 88 | 70 | 4 | 21.8 | 0 | 13.9722 | 2.1155 | 0 | 51.0556 | 18.5475 | 0 | 48.4821 | 58% | 0 | 25 | 45.16% | 0 | 44.1594
7265 | 306 | 107 | 58 | 3.6 | 21.5 | 0 | 55.1026 | 6.1961 | 0 | 52.2357 | 19.1211 | 0 | 50.3985 | 55% | 0 | 21.9768 | 10% | 0 | 44.8196
7266 | 1 | 2 | 2 | 3.2 | 19.5 | 0 | 0 | 0 | 0 | 118.2019 | 47.4128 | 0 | 123.0483 | 45% | 0 | 0 | 10% | 0 | 44.8434
7267 | 0 | 0 | 0 | 2.2 | 18.8 | 0 | 0 | 0 | 0 | 113.5726 | 45.5601 | 0 | 116.5192 | 37% | 0 | 0 | 10% | 0 | 43.1958
7268 | 0 | 0 | 0 | 0.9 | 17.1 | 0 | 0 | 0 | 0 | 103.8273 | 41.6524 | 0 | 104.4523 | 29% | 0 | 0 | 10% | 0 | 39.4143
7269 | 0 | 0 | 0 | 1 | 16.6 | 0 | 0 | 0 | 0 | 96.1056 | 38.4548 | 0 | 95.1077 | 22% | 0 | 0 | 10% | 0 | 36.2659
7270 | 0 | 0 | 0 | 1.7 | 16.4 | 0 | 0 | 0 | 0 | 91.5203 | 36.5381 | 0 | 89.6127 | 15% | 0 | 0 | 10% | 0 | 34.3516
7271 | 0 | 0 | 0 | 1.2 | 16.8 | 0 | 0 | 0 | 0 | 87.7678 | 34.927 | 0 | 85.1617 | 8% | 0 | 0 | 10% | 0 | 32.7223
7272 | 0 | 0 | 0 | 1 | 15.9 | 0 | 0 | 0 | 0 | 84.479 | 33.605 | 0 | 81.3921 | 2% | 0 | 0 | 10% | 0 | 31.3692
7273 | 0 | 0 | 0 | 1.3 | 15.8 | 0 | 0 | 0 | 0 | 31.1244 | 12.3762 | 0 | 29.9627 | 0% | 0 | 0 | 10% | 0 | 10.1543
7274 | 0 | 0 | 0 | 1.5 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1762
7275 | 0 | 0 | 0 | 1.6 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.156
7276 | 0 | 0 | 0 | 1.4 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1362
7277 | 0 | 0 | 0 | 1.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1169
7278 | 0 | 0 | 0 | 1.1 | 16.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.098
7279 | 17 | 8 | 6 | 1.3 | 15.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0795
7280 | 483 | 133 | 43 | 1.1 | 18.7 | 58.047 | 14.6568 | 12.1783 | 0 | 0 | 0 | 55.374 | 0 | 4% | 0 | 0 | 10% | 0 | 10.9569
7281 | 696 | 304 | 59 | 0.7 | 22.4 | 149.4512 | 0 | 33.4512 | 0 | 0 | 0 | 145.7669 | 0 | 15% | 0 | 0 | 10% | 0 | 31.7222
7282 | 827 | 476 | 73 | 2.5 | 24.5 | 207.3558 | 0 | 54.5339 | 0 | 42.4265 | 0 | 165.3198 | 0 | 28% | 24.3179 | 0 | 43.07% | 0 | 27.4104
7283 | 820 | 580 | 100 | 3 | 25.8 | 219.0685 | 0 | 57.1581 | 8.2128 | 42.5167 | 14.0692 | 177.6786 | 0 | 41% | 24.9393 | 0 | 76.99% | 0 | 43.8351
7284 | 753 | 617 | 141 | 4.9 | 26.4 | 202.1304 | 0 | 39.8663 | 28.8597 | 42.5538 | 14.6307 | 160.8128 | 0 | 53% | 9.5664 | 0 | 90% | 0 | 42.6346
7285 | 730 | 610 | 152 | 5.7 | 26.7 | 194.3379 | 0 | 29.1269 | 38.0427 | 42.5649 | 14.6091 | 152.9743 | 0 | 65% | 0 | 0 | 90% | 0 | 41.503
7286 | 638 | 598 | 228 | 5.1 | 27.6 | 163.123 | 0 | 28.4489 | 33.5275 | 42.5738 | 14.5348 | 121.7677 | 0 | 74% | 0 | 0 | 90% | 0 | 41.0331
7287 | 17 | 205 | 195 | 4.7 | 26.2 | 0 | 4.8589 | 7.7783 | 0 | 42.577 | 14.6556 | 0 | 40.5467 | 71% | 0 | 20.3217 | 57.48% | 0 | 41.043
7288 | 282 | 231 | 136 | 2.8 | 26.4 | 0 | 58.0884 | 17.6826 | 0 | 42.5729 | 14.6372 | 0 | 40.5846 | 68% | 0 | 13.068 | 36.58% | 0 | 42.7331
7289 | 84 | 67 | 51 | 1.8 | 24.6 | 0 | 15.0174 | 0.98581 | 0 | 75.1744 | 28.6296 | 0 | 75.4232 | 62% | 0 | 16.6103 | 10% | 0 | 43.5094
7290 | 0 | 2 | 2 | 5 | 24.3 | 0 | 0 | 0 | 0 | 114.4076 | 45.3834 | 0 | 118.9552 | 54% | 0 | 0 | 10% | 0 | 42.7112
7291 | 0 | 0 | 0 | 3.2 | 23.4 | 0 | 0 | 0 | 0 | 110.2903 | 43.7817 | 0 | 112.9815 | 45% | 0 | 0 | 10% | 0 | 41.3395
7292 | 0 | 0 | 0 | 2.3 | 22 | 0 | 0 | 0 | 0 | 101.6561 | 40.3432 | 0 | 102.1411 | 37% | 0 | 0 | 10% | 0 | 38.0363
7293 | 0 | 0 | 0 | 3 | 21.3 | 0 | 0 | 0 | 0 | 95.1975 | 37.7186 | 0 | 94.3189 | 30% | 0 | 0 | 10% | 0 | 35.4622
7294 | 0 | 0 | 0 | 3 | 21.5 | 0 | 0 | 0 | 0 | 91.3816 | 36.0997 | 0 | 89.6807 | 24% | 0 | 0 | 10% | 0 | 33.8493
7295 | 0 | 0 | 0 | 2.3 | 20.6 | 0 | 0 | 0 | 0 | 87.332 | 34.4717 | 0 | 84.8505 | 17% | 0 | 0 | 10% | 0 | 32.2076
7296 | 0 | 0 | 0 | 2.6 | 21.3 | 0 | 0 | 0 | 0 | 83.8298 | 32.955 | 0 | 80.8256 | 11% | 0 | 0 | 10% | 0 | 30.6611
7297 | 0 | 0 | 0 | 1.1 | 20.8 | 0 | 0 | 0 | 0 | 81.7848 | 32.1018 | 0 | 78.7447 | 5% | 0 | 0 | 10% | 0 | 29.7673
7298 | 0 | 0 | 0 | 2.4 | 20.8 | 0 | 0 | 0 | 0 | 70.4883 | 27.6339 | 0 | 67.9409 | 0% | 0 | 0 | 10% | 0 | 25.2683
7299 | 0 | 0 | 0 | 3.7 | 22.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.303
7300 | 0 | 0 | 0 | 4.8 | 22.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2804
7301 | 0 | 0 | 0 | 4.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2584
7302 | 0 | 0 | 0 | 4.7 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2368
7303 | 30 | 10 | 6 | 2.7 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2156
7304 | 536 | 146 | 47 | 2.9 | 21.1 | 64.881 | 16.2788 | 13.9784 | 0 | 0 | 0 | 62.0532 | 0 | 5% | 0 | 0 | 10% | 0 | 12.6802
7305 | 773 | 351 | 84 | 2.7 | 23.2 | 166.3105 | 0 | 40.22 | 0 | 0 | 0 | 162.7357 | 0 | 17% | 3.4545 | 0 | 14.7% | 0 | 34.894
7306 | 307 | 367 | 225 | 3.5 | 24.3 | 65.2961 | 0 | 33.6788 | 0 | 42.5131 | 1.1256 | 24.7163 | 0 | 19% | 11.546 | 0 | 30.4% | 0 | 21.7604
7307 | 12 | 286 | 275 | 3.2 | 24.6 | 0 | 3.7042 | 13.8313 | 0 | 42.4796 | 14.7527 | 0 | 39.9408 | 16% | 0 | 9.5073 | 15.19% | 0 | 36.7126
7308 | 13 | 316 | 304 | 4.1 | 24.8 | 0 | 4.0857 | 16.2878 | 0 | 52.3336 | 18.9088 | 0 | 49.618 | 12% | 0 | 3.2431 | 10% | 0 | 36.0958
7309 | 62 | 378 | 334 | 4.9 | 25.4 | 0 | 19.4422 | 26.8192 | 0 | 46.3377 | 16.2684 | 0 | 43.7589 | 9% | 6.2915 | 0 | 18.56% | 0 | 34.4343
7310 | 110 | 371 | 302 | 4.1 | 26.3 | 0 | 33.5835 | 26.8597 | 0 | 46.6724 | 16.3306 | 0 | 44.1298 | 6% | 7.3864 | 0 | 28.6% | 0 | 33.4128
7311 | 111 | 273 | 218 | 2.2 | 26.8 | 0 | 31.6696 | 17.5397 | 0 | 50.8863 | 18.0595 | 0 | 48.281 | 2% | 0 | 0 | 28.6% | 0 | 33.1751
7312 | 158 | 186 | 143 | 2.3 | 26.7 | 0 | 38.4452 | 12.2334 | 0 | 27.8827 | 9.5699 | 0 | 26.3457 | 0% | 0 | 11.6263 | 10% | 0 | 31.0012
7313 | 25 | 58 | 53 | 3.5 | 25.4 | 0 | 4.4378 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4042
7314 | 0 | 2 | 2 | 4.4 | 23.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3799
7315 | 0 | 0 | 0 | 4 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.356
7316 | 0 | 0 | 0 | 5.7 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3324
7317 | 0 | 0 | 0 | 6.6 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3094
7318 | 0 | 0 | 0 | 5.5 | 22.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2868
7319 | 0 | 0 | 0 | 6.9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2646
7320 | 0 | 0 | 0 | 6.5 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2428
7321 | 0 | 0 | 0 | 6.2 | 21.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2215
7322 | 0 | 0 | 0 | 7 | 21.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2005
7323 | 0 | 0 | 0 | 7.3 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.18
7324 | 0 | 0 | 0 | 7.3 | 21.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1598
7325 | 0 | 0 | 0 | 5.7 | 20.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.14
7326 | 0 | 0 | 0 | 7.2 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1206
7327 | 4 | 7 | 6 | 6.6 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.1016
7328 | 357 | 118 | 51 | 7.7 | 21.7 | 0 | 58.135 | 9.0497 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 6.9696
7329 | 364 | 251 | 137 | 6.4 | 22.7 | 65.3375 | 0 | 23.4816 | 0 | 0 | 0 | 61.0633 | 0 | 5% | 0 | 0 | 10% | 0 | 22.4981
7330 | 137 | 286 | 217 | 9.3 | 22.4 | 0 | 39.7424 | 20.8215 | 0 | 0 | 0 | 0 | 0 | 5% | 0 | 0 | 10% | 0 | 19.6884
7331 | 306 | 365 | 184 | 10 | 22.9 | 52.393 | 14.378 | 33.6955 | 0 | 0 | 0 | 49.8159 | 0 | 9% | 0 | 0 | 10% | 0 | 32.5268
7332 | 85 | 270 | 216 | 8.4 | 23.1 | 0 | 26.6892 | 17.0307 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 10% | 0 | 15.918
7333 | 169 | 334 | 226 | 8.9 | 23.5 | 0 | 52.946 | 26.2653 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 10% | 0 | 24.2378
7334 | 89 | 266 | 213 | 8.7 | 22.8 | 0 | 27.1199 | 16.5817 | 0 | 0 | 0 | 0 | 0 | 9% | 0 | 0 | 10% | 0 | 14.5729
7335 | 559 | 387 | 135 | 9.4 | 23.7 | 102.6602 | 26.0584 | 41.1182 | 0 | 0 | 0 | 97.9426 | 0 | 16% | 6.0338 | 0 | 18.21% | 0 | 33.4875
7336 | 182 | 161 | 113 | 7.8 | 23.1 | 0 | 44.1265 | 11.4136 | 0 | 42.1535 | 0 | 0 | 39.2191 | 13% | 0 | 5.1287 | 10% | 0 | 14.9321
7337 | 237 | 95 | 54 | 6.9 | 22.7 | 0 | 41.777 | 4.2066 | 0 | 63.819 | 16.0274 | 0 | 61.2874 | 8% | 0 | 0 | 10% | 0 | 17.848
7338 | 1 | 2 | 2 | 7.9 | 21.8 | 0 | 0 | 0 | 0 | 101.2521 | 40.2149 | 0 | 101.3433 | 1% | 0 | 0 | 10% | 0 | 38.0159
7339 | 0 | 0 | 0 | 8 | 21 | 0 | 0 | 0 | 0 | 9.774 | 3.8862 | 0 | 9.7499 | 0% | 0 | 0 | 10% | 0 | 1.8296
7340 | 0 | 0 | 0 | 5.1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0272
7341 | 0 | 0 | 0 | 5.1 | 19.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.01
7342 | 0 | 0 | 0 | 5.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9931
7343 | 0 | 0 | 0 | 5 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9765
7344 | 0 | 0 | 0 | 4.7 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9602
7345 | 0 | 0 | 0 | 4.5 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9443
7346 | 0 | 0 | 0 | 4.1 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9286
7347 | 0 | 0 | 0 | 6.9 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9132
7348 | 0 | 0 | 0 | 10.2 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8981
7349 | 0 | 0 | 0 | 12.6 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8833
7350 | 0 | 0 | 0 | 13.3 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8688
7351 | 11 | 9 | 8 | 11.7 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8546
7352 | 270 | 142 | 92 | 9.4 | 19.3 | 0 | 51.8426 | 9.6272 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 7.7865
7353 | 51 | 200 | 181 | 8.6 | 19.9 | 0 | 12.8956 | 10.9454 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.1185
7354 | 158 | 325 | 242 | 10 | 20.6 | 0 | 45.7558 | 24.9506 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 23.1372
7355 | 224 | 382 | 244 | 11.6 | 20.5 | 0 | 57.9993 | 31.9962 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 30.1979
7356 | 618 | 551 | 161 | 13.7 | 21.2 | 0 | 0 | 59.8504 | 0 | 0 | 0 | 0 | 0 | 0% | 24.043 | 0 | 42.7% | 0 | 34.0201
7357 | 893 | 715 | 166 | 14.2 | 21.8 | 0 | 0 | 59.656 | 15.444 | 0 | 0 | 0 | 0 | 0% | 25 | 0 | 76.7% | 0 | 32.8815
7358 | 865 | 557 | 76 | 13 | 22.1 | 0 | 0 | 43.3896 | 21.8253 | 0 | 0 | 0 | 0 | 0% | 9.7805 | 0 | 90% | 0 | 31.85
7359 | 855 | 443 | 59 | 11.1 | 22.2 | 165.4348 | 41.2991 | 34.0587 | 18.3252 | 0 | 0 | 152.3936 | 0 | 12% | 0 | 0 | 90% | 0 | 31.959
7360 | 711 | 268 | 49 | 10.5 | 21.8 | 136.2636 | 0 | 30.1992 | 0 | 42.0321 | 0 | 94.771 | 0 | 20% | 0 | 0 | 90% | 0 | 28.0141
7361 | 431 | 85 | 26 | 9.9 | 20.9 | 0 | 62.0631 | 7.2208 | 0 | 42.2672 | 7.2681 | 0 | 39.0973 | 17% | 0 | 20.7034 | 56.88% | 0 | 33.965
7362 | 2 | 1 | 1 | 10.1 | 20.1 | 0 | 0 | 0 | 0 | 42.256 | 14.9993 | 0 | 39.144 | 14% | 0 | 24.6837 | 17.38% | 0 | 37.7635
7363 | 0 | 0 | 0 | 11.2 | 20 | 0 | 0 | 0 | 0 | 88.8372 | 35.0417 | 0 | 87.6601 | 7% | 0 | 4.6129 | 10% | 0 | 37.6028
7364 | 0 | 0 | 0 | 5.6 | 19.3 | 0 | 0 | 0 | 0 | 95.276 | 37.9241 | 0 | 93.7698 | 0% | 0 | 0 | 10% | 0 | 35.8587
7365 | 0 | 0 | 0 | 1.7 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9542
7366 | 0 | 0 | 0 | 1.3 | 17.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9383
7367 | 0 | 0 | 0 | 4.7 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9227
7368 | 0 | 0 | 0 | 5.4 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9075
7369 | 0 | 0 | 0 | 3.1 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8926
7370 | 0 | 0 | 0 | 5.9 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8779
7371 | 0 | 0 | 0 | 3.2 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8635
7372 | 0 | 0 | 0 | 2 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8496
7373 | 0 | 0 | 0 | 2.6 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8358
7374 | 0 | 0 | 0 | 2.5 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8223
7375 | 31 | 7 | 4 | 2.6 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.809
7376 | 580 | 128 | 28 | 5.1 | 17.7 | 68.0905 | 17.643 | 13.7982 | 0 | 0 | 0 | 63.8535 | 0 | 5% | 0 | 0 | 10% | 0 | 12.533
7377 | 800 | 309 | 43 | 5.9 | 19.7 | 167.9961 | 0 | 37.4189 | 0 | 0 | 0 | 163.0536 | 0 | 17% | 0 | 0 | 10% | 0 | 35.5075
7378 | 891 | 468 | 50 | 6.7 | 21.2 | 219.4678 | 0 | 56.7147 | 0 | 42.3208 | 0 | 177.3591 | 0 | 31% | 14.6552 | 0 | 29.93% | 0 | 39.1183
7379 | 935 | 580 | 54 | 8.3 | 22.4 | 245.8263 | 0 | 60.6104 | 9.2952 | 42.4713 | 10.6722 | 204.4437 | 0 | 47% | 24.3696 | 0 | 63.07% | 0 | 44.0597
7380 | 954 | 636 | 54 | 7.9 | 23.4 | 257.3988 | 0 | 50.7438 | 24.3562 | 42.5177 | 14.8599 | 216.0739 | 0 | 63% | 19.7987 | 0 | 90% | 0 | 42.9632
7381 | 950 | 628 | 55 | 7.9 | 24.6 | 255.7119 | 0 | 30.0534 | 44.8071 | 42.5414 | 14.7742 | 214.4138 | 0 | 79% | 0 | 0 | 90% | 0 | 41.9821
7382 | 915 | 554 | 54 | 7 | 24.8 | 238.5316 | 0 | 29.3832 | 36.5776 | 42.5576 | 14.7638 | 197.0724 | 0 | 94% | 0 | 0 | 90% | 0 | 41.4521
7383 | 858 | 429 | 51 | 8 | 24.6 | 124.3394 | 96.4012 | 26.9993 | 24.1839 | 42.5681 | 14.7835 | 82.6547 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8233
7384 | 737 | 262 | 42 | 10 | 23.2 | 42.1525 | 124.8968 | 28.2463 | 2.2543 | 42.5687 | 14.8931 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 43.8502
7385 | 432 | 83 | 24 | 9.7 | 21.6 | 0 | 62.0359 | 7.0364 | 0 | 43.8949 | 15.5533 | 0 | 42.3897 | 97% | 0 | 24.4797 | 50.83% | 0 | 44.996
7386 | 0 | 1 | 1 | 9.3 | 19.7 | 0 | 0 | 0 | 0 | 61.2476 | 23.085 | 0 | 59.6709 | 93% | 0 | 25 | 10.83% | 0 | 45.1562
7387 | 0 | 0 | 0 | 8.2 | 18.6 | 0 | 0 | 0 | 0 | 115.7629 | 46.4871 | 0 | 121.9385 | 84% | 0 | 0 | 10.83% | 0 | 43.5471
7388 | 0 | 0 | 0 | 8.9 | 18.2 | 0 | 0 | 0 | 0 | 104.8895 | 42.0134 | 0 | 105.7393 | 76% | 0 | 0 | 10.83% | 0 | 39.8136
7389 | 0 | 0 | 0 | 7.4 | 17.4 | 0 | 0 | 0 | 0 | 96.4679 | 38.5477 | 0 | 95.2241 | 68% | 0 | 0 | 10.83% | 0 | 36.4768
7390 | 0 | 0 | 0 | 4.5 | 17.5 | 0 | 0 | 0 | 0 | 91.7619 | 36.5629 | 0 | 89.6777 | 62% | 0 | 0 | 10.83% | 0 | 34.4729
7391 | 0 | 0 | 0 | 4 | 17.2 | 0 | 0 | 0 | 0 | 87.6367 | 34.8432 | 0 | 84.892 | 55% | 0 | 0 | 10.83% | 0 | 32.6997
7392 | 0 | 0 | 0 | 7.1 | 17.5 | 0 | 0 | 0 | 0 | 85.0171 | 33.7238 | 0 | 82.0255 | 49% | 0 | 0 | 10.83% | 0 | 31.5084
7393 | 0 | 0 | 0 | 8.3 | 17.7 | 0 | 0 | 0 | 0 | 83.6354 | 33.1329 | 0 | 80.6253 | 43% | 0 | 0 | 10.83% | 0 | 30.8461
7394 | 0 | 0 | 0 | 8.5 | 17.5 | 0 | 0 | 0 | 0 | 83.5794 | 33.123 | 0 | 80.7479 | 37% | 0 | 0 | 10.83% | 0 | 30.7716
7395 | 0 | 0 | 0 | 5.1 | 16.2 | 0 | 0 | 0 | 0 | 85.3 | 33.9288 | 0 | 82.9235 | 31% | 0 | 0 | 10.83% | 0 | 31.5226
7396 | 0 | 0 | 0 | 2.6 | 12.6 | 0 | 0 | 0 | 0 | 93.1454 | 37.4737 | 0 | 92.5586 | 24% | 0 | 0 | 10.83% | 0 | 35.0199
7397 | 0 | 0 | 0 | 2.1 | 12.6 | 0 | 0 | 0 | 0 | 104.5551 | 42.2814 | 0 | 106.2092 | 16% | 0 | 0 | 10.83% | 0 | 39.8199
7398 | 0 | 0 | 0 | 6.8 | 15.5 | 0 | 0 | 0 | 0 | 110.6429 | 44.6177 | 0 | 113.1702 | 7% | 0 | 0 | 10.83% | 0 | 42.2038
7399 | 17 | 6 | 5 | 11.3 | 16.4 | 0 | 0 | 0 | 0 | 93.9444 | 37.8609 | 0 | 96.2937 | 0% | 0 | 0 | 10.83% | 0 | 35.5472
7400 | 532 | 123 | 32 | 12.8 | 16.1 | 0 | 0 | 12.7781 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.83% | 0 | 10.649
7401 | 805 | 312 | 48 | 9.8 | 16.4 | 134.5893 | 34.4615 | 38.6308 | 0 | 0 | 0 | 129.6449 | 0 | 10% | 0 | 0 | 10.83% | 0 | 36.7461
7402 | 905 | 477 | 57 | 8.7 | 17.2 | 221.0473 | 0 | 59.1744 | 0 | 0 | 0 | 218.9219 | 0 | 26% | 13.2066 | 0 | 28.79% | 0 | 43.5867
7403 | 956 | 596 | 62 | 9.9 | 17.6 | 249.7511 | 0 | 72.4033 | 1.1002 | 0 | 0 | 248.2054 | 0 | 45% | 25 | 0 | 62.79% | 0 | 44.7207
7404 | 963 | 649 | 66 | 7.3 | 18.8 | 260.2088 | 0 | 66.3451 | 8.7549 | 0 | 0 | 258.9085 | 0 | 65% | 20.0047 | 0 | 90% | 0 | 43.5036
7405 | 952 | 639 | 68 | 5.8 | 19.8 | 257.7851 | 0 | 45.4291 | 29.6709 | 0 | 0 | 256.5905 | 0 | 84% | 0 | 0 | 90% | 0 | 42.572
7406 | 920 | 566 | 67 | 7 | 20.1 | 213.4585 | 28.6433 | 44.497 | 24.265 | 0 | 0 | 212.4913 | 0 | 100% | 0 | 0 | 90% | 0 | 42.0112
7407 | 861 | 440 | 63 | 6.5 | 20.5 | 41.3675 | 195.2359 | 41.7886 | 11.6028 | 42.596 | 1.1186 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.1413
7408 | 735 | 270 | 54 | 6.6 | 19 | 42.1581 | 124.7981 | 28.7672 | 3.3935 | 42.5937 | 15.1875 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.6665
7409 | 330 | 82 | 32 | 6.6 | 17.1 | 0 | 57.0064 | 5.187 | 0 | 47.9867 | 17.5458 | 0 | 46.4575 | 97% | 0 | 25 | 50% | 0 | 45.6766
7410 | 0 | 1 | 1 | 5.9 | 15.4 | 0 | 0 | 0 | 0 | 62.8785 | 24.0415 | 0 | 61.3542 | 92% | 0 | 25 | 10% | 0 | 46.103
7411 | 0 | 0 | 0 | 5.7 | 14.8 | 0 | 0 | 0 | 0 | 117.044 | 47.3372 | 0 | 123.4986 | 83% | 0 | 0 | 10% | 0 | 44.3955
7412 | 0 | 0 | 0 | 6.2 | 14.8 | 0 | 0 | 0 | 0 | 106.0992 | 42.7772 | 0 | 107.124 | 75% | 0 | 0 | 10% | 0 | 40.5835
7413 | 0 | 0 | 0 | 6.8 | 14.8 | 0 | 0 | 0 | 0 | 96.9889 | 38.949 | 0 | 95.7632 | 68% | 0 | 0 | 10% | 0 | 36.8933
7414 | 0 | 0 | 0 | 7.6 | 14.9 | 0 | 0 | 0 | 0 | 92.1387 | 36.8994 | 0 | 90.0684 | 61% | 0 | 0 | 10% | 0 | 34.8252
7415 | 0 | 0 | 0 | 5.8 | 14.7 | 0 | 0 | 0 | 0 | 87.8989 | 35.1167 | 0 | 85.1382 | 54% | 0 | 0 | 10% | 0 | 32.9898
7416 | 0 | 0 | 0 | 3 | 13.8 | 0 | 0 | 0 | 0 | 84.7628 | 33.8512 | 0 | 81.6662 | 48% | 0 | 0 | 10% | 0 | 31.6526
7417 | 0 | 0 | 0 | 5.4 | 13.9 | 0 | 0 | 0 | 0 | 83.9524 | 33.505 | 0 | 80.9456 | 42% | 0 | 0 | 10% | 0 | 31.2308
7418 | 0 | 0 | 0 | 4 | 13.6 | 0 | 0 | 0 | 0 | 83.9334 | 33.5149 | 0 | 81.111 | 36% | 0 | 0 | 10% | 0 | 31.1764
7419 | 0 | 0 | 0 | 4.8 | 13.3 | 0 | 0 | 0 | 0 | 86.236 | 34.5021 | 0 | 83.9796 | 30% | 0 | 0 | 10% | 0 | 32.1083
7420 | 0 | 0 | 0 | 4.7 | 12.9 | 0 | 0 | 0 | 0 | 94.2467 | 37.9234 | 0 | 93.8414 | 23% | 0 | 0 | 10% | 0 | 35.4848
7421 | 0 | 0 | 0 | 4 | 12.9 | 0 | 0 | 0 | 0 | 105.5956 | 42.6991 | 0 | 107.3615 | 15% | 0 | 0 | 10% | 0 | 40.2566
7422 | 0 | 0 | 0 | 4.6 | 12.7 | 0 | 0 | 0 | 0 | 111.345 | 45.108 | 0 | 113.8992 | 6% | 0 | 0 | 10% | 0 | 42.7144
7423 | 26 | 5 | 4 | 3.2 | 11.5 | 0 | 0 | 0 | 0 | 80.2595 | 32.5898 | 0 | 82.207 | 0% | 0 | 0 | 10% | 0 | 30.3202
7424 | 576 | 125 | 30 | 4.2 | 13.3 | 66.8641 | 17.4332 | 14.0856 | 0 | 0 | 0 | 64.5563 | 0 | 5% | 0 | 0 | 10% | 0 | 12.7758
7425 | 812 | 312 | 48 | 3.4 | 15.5 | 171.7348 | 0 | 39.0693 | 0 | 0 | 0 | 168.9445 | 0 | 18% | 0 | 0 | 10% | 0 | 37.1445
7426 | 848 | 464 | 75 | 2.6 | 17.1 | 210.5821 | 2.98e-14 | 57.1264 | 0 | 0 | 0 | 208.9327 | 0 | 33% | 11.3882 | 0 | 25.49% | 0 | 43.4333
7427 | 950 | 589 | 61 | 1.6 | 18.8 | 254.379 | 0 | 72.1371 | 0.38504 | 0 | 0 | 252.8507 | 0 | 52% | 25 | 0 | 59.49% | 0 | 44.3954
7428 | 941 | 640 | 74 | 3.6 | 18.9 | 256.9003 | 0 | 68.232 | 6.868 | 0 | 0 | 255.6769 | 0 | 72% | 22.4354 | 0 | 90% | 0 | 42.9758
7429 | 876 | 611 | 89 | 3.1 | 18.7 | 237.6305 | 0 | 44.8383 | 28.8089 | 0 | 0 | 236.5481 | 0 | 90% | 0 | 0 | 90% | 0 | 42.1562
7430 | 777 | 537 | 115 | 3 | 18.8 | 138.8803 | 69.1286 | 43.6412 | 19.9463 | 0 | 0 | 138.2129 | 0 | 100% | 0 | 0 | 90% | 0 | 41.8552
7431 | 852 | 432 | 62 | 4.5 | 19 | 41.2477 | 192.799 | 42.0858 | 10.7813 | 42.5968 | 0.97093 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 42.2124
7432 | 734 | 261 | 48 | 5 | 18.2 | 42.1581 | 124.4446 | 28.6349 | 2.857 | 42.5945 | 15.2345 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 44.5813
7433 | 401 | 80 | 25 | 3.7 | 16.9 | 0 | 55.6597 | 6.5333 | 0 | 45.5267 | 16.5224 | 0 | 44.0091 | 97% | 0 | 24.8436 | 50.25% | 0 | 45.833
7434 | 0 | 1 | 1 | 3.8 | 14.7 | 0 | 0 | 0 | 0 | 63.8112 | 24.484 | 0 | 62.2998 | 92% | 0 | 25 | 10.25% | 0 | 46.549
7435 | 0 | 0 | 0 | 2.5 | 13.6 | 0 | 0 | 0 | 0 | 117.8512 | 47.7593 | 0 | 124.4563 | 83% | 0 | 0 | 10.25% | 0 | 44.8227
7436 | 0 | 0 | 0 | 1.9 | 12.4 | 0 | 0 | 0 | 0 | 106.6761 | 43.1771 | 0 | 107.7142 | 75% | 0 | 0 | 10.25% | 0 | 41.0029
7437 | 0 | 0 | 0 | 2.4 | 12.6 | 0 | 0 | 0 | 0 | 97.5838 | 39.3381 | 0 | 96.3861 | 68% | 0 | 0 | 10.25% | 0 | 37.3013
7438 | 0 | 0 | 0 | 1.9 | 12.5 | 0 | 0 | 0 | 0 | 92.9634 | 37.3981 | 0 | 91.0078 | 61% | 0 | 0 | 10.25% | 0 | 35.3427
7439 | 0 | 0 | 0 | 2.3 | 10.6 | 0 | 0 | 0 | 0 | 88.2637 | 35.5002 | 0 | 85.4922 | 54% | 0 | 0 | 10.25% | 0 | 33.3969
7440 | 0 | 0 | 0 | 2.2 | 10.4 | 0 | 0 | 0 | 0 | 85.3567 | 34.2806 | 0 | 82.2886 | 48% | 0 | 0 | 10.25% | 0 | 32.1042
7441 | 0 | 0 | 0 | 2.3 | 9.9 | 0 | 0 | 0 | 0 | 84.1917 | 33.8118 | 0 | 81.1509 | 42% | 0 | 0 | 10.25% | 0 | 31.5605
7442 | 0 | 0 | 0 | 1.7 | 9.4 | 0 | 0 | 0 | 0 | 84.3354 | 33.8931 | 0 | 81.513 | 36% | 0 | 0 | 10.25% | 0 | 31.5756
7443 | 0 | 0 | 0 | 1.8 | 8.7 | 0 | 0 | 0 | 0 | 86.0939 | 34.663 | 0 | 83.7417 | 30% | 0 | 0 | 10.25% | 0 | 32.2905
7444 | 0 | 0 | 0 | 1.8 | 9.3 | 0 | 0 | 0 | 0 | 94.8938 | 38.3762 | 0 | 94.5329 | 22% | 0 | 0 | 10.25% | 0 | 35.9547
7445 | 0 | 0 | 0 | 1.6 | 9.6 | 0 | 0 | 0 | 0 | 106.2571 | 43.1509 | 0 | 108.0602 | 14% | 0 | 0 | 10.25% | 0 | 40.7259
7446 | 0 | 0 | 0 | 1.3 | 9.4 | 0 | 0 | 0 | 0 | 112.0742 | 45.5896 | 0 | 114.6876 | 6% | 0 | 0 | 10.25% | 0 | 43.2132
7447 | 24 | 5 | 4 | 1.1 | 9 | 0 | 0 | 0 | 0 | 74.2959 | 30.257 | 0 | 76.1624 | 0% | 0 | 0 | 10.25% | 0 | 28.0166
7448 | 532 | 119 | 33 | 0.6 | 12.1 | 61.7176 | 15.8548 | 13.0461 | 0 | 0 | 0 | 59.5818 | 0 | 5% | 0 | 0 | 10.25% | 0 | 11.7815
7449 | 780 | 304 | 53 | 1.4 | 15 | 164.6515 | 0 | 37.8952 | 0 | 0 | 0 | 161.7833 | 0 | 17% | 0 | 0 | 10.25% | 0 | 36.0334
7450 | 878 | 455 | 54 | 1.9 | 16.9 | 218.5837 | 0 | 56.7845 | 0 | 0 | 0 | 216.7902 | 0 | 33% | 10.2358 | 0 | 24.17% | 0 | 44.173
7451 | 669 | 537 | 170 | 3 | 18.4 | 172.9646 | 0 | 61.2161 | 0 | 0 | 0 | 171.9523 | 0 | 46% | 14.6272 | 0 | 44.06% | 0 | 44.5907
7452 | 335 | 517 | 310 | 4.8 | 19.4 | 78.329 | 0 | 50.5537 | 0 | 0 | 0 | 77.7923 | 0 | 52% | 5.6849 | 0 | 51.8% | 0 | 43.7228
7453 | 254 | 427 | 271 | 5.1 | 20.2 | 40.1468 | 16.962 | 38.5095 | 0 | 42.5814 | 3.8888 | 10.0417 | 10.2758 | 52% | 9.3351 | 0 | 64.49% | 0 | 31.8681
7454 | 419 | 457 | 238 | 7.2 | 20.9 | 96.5513 | 0 | 47.2316 | 0 | 42.5784 | 15.0614 | 53.0733 | 0 | 56% | 18.09 | 0 | 89.09% | 0 | 42.8962
7455 | 51 | 201 | 175 | 7.2 | 21 | 0 | 14.4078 | 10.3632 | 0 | 42.5773 | 15.0545 | 0 | 40.1248 | 53% | 0 | 19.4218 | 58.02% | 0 | 43.4149
7456 | 634 | 248 | 74 | 7.4 | 20.8 | 97.87 | 24.7649 | 28.9837 | 0 | 42.5718 | 15.0656 | 62.097 | 7.2867 | 57% | 0 | 3.4704 | 52.47% | 0 | 45.8473
7457 | 412 | 78 | 22 | 8.7 | 19.5 | 0 | 56.9331 | 6.4444 | 0 | 47.7713 | 17.3113 | 0 | 45.3925 | 54% | 0 | 25 | 12.47% | 0 | 47.1821
7458 | 0 | 1 | 1 | 5.5 | 17.6 | 0 | 0 | 0 | 0 | 124.3747 | 50.1338 | 0 | 130.7663 | 44% | 0 | 0 | 12.47% | 0 | 47.5178
7459 | 0 | 0 | 0 | 5.6 | 15.9 | 0 | 0 | 0 | 0 | 118.8514 | 47.9977 | 0 | 122.8232 | 35% | 0 | 0 | 12.47% | 0 | 45.6336
7460 | 0 | 0 | 0 | 5.5 | 15 | 0 | 0 | 0 | 0 | 109.0364 | 43.9849 | 0 | 110.4643 | 26% | 0 | 0 | 12.47% | 0 | 41.772
7461 | 0 | 0 | 0 | 6.3 | 14.4 | 0 | 0 | 0 | 0 | 100.975 | 40.6514 | 0 | 100.6533 | 19% | 0 | 0 | 12.47% | 0 | 38.5059
7462 | 0 | 0 | 0 | 4.9 | 13.6 | 0 | 0 | 0 | 0 | 95.3313 | 38.3349 | 0 | 93.9684 | 12% | 0 | 0 | 12.47% | 0 | 36.2072
7463 | 0 | 0 | 0 | 4.9 | 13.5 | 0 | 0 | 0 | 0 | 90.6543 | 36.361 | 0 | 88.3729 | 5% | 0 | 0 | 12.47% | 0 | 34.2274
7464 | 0 | 0 | 0 | 3.6 | 13 | 0 | 0 | 0 | 0 | 67.1083 | 26.8912 | 0 | 64.9984 | 0% | 0 | 0 | 12.47% | 0 | 24.7512
7465 | 0 | 0 | 0 | 6.1 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.47% | 0 | -2.0721
7466 | 0 | 0 | 0 | 7.1 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.47% | 0 | -2.054
7467 | 0 | 0 | 0 | 6.8 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.47% | 0 | -2.0363
7468 | 0 | 0 | 0 | 4.4 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.47% | 0 | -2.0189
7469 | 0 | 0 | 0 | 4.2 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.47% | 0 | -2.0019
7470 | 0 | 0 | 0 | 3.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.47% | 0 | -1.9852
7471 | 3 | 3 | 3 | 2.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.47% | 0 | -1.9688
7472 | 129 | 65 | 37 | 4.6 | 10.8 | 0 | 23.9615 | 1.8241 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 12.47% | 0 | -0.12854
7473 | 748 | 298 | 61 | 7.1 | 12.5 | 123.5509 | 31.8821 | 37.2863 | 0 | 0 | 0 | 117.4766 | 0 | 9% | 0 | 0 | 12.47% | 0 | 35.517
7474 | 836 | 457 | 80 | 7.7 | 13.7 | 202.1125 | 0 | 57.2763 | 0 | 0 | 0 | 199.1261 | 0 | 24% | 9.5327 | 0 | 25.43% | 0 | 45.5207
7475 | 898 | 591 | 100 | 5.9 | 14.6 | 235.0554 | 0 | 73.4168 | 0 | 42.4703 | 0 | 193.5207 | 0 | 39% | 24.5834 | 0 | 58.86% | 0 | 45.7465
7476 | 920 | 632 | 87 | 2.6 | 15.8 | 250.8983 | 0 | 70.1437 | 4.9563 | 0 | 0 | 249.2339 | 0 | 58% | 22.8944 | 0 | 90% | 0 | 44.5122
7477 | 920 | 625 | 86 | 5.7 | 16.1 | 247.8145 | 0 | 46.2081 | 28.8919 | 0 | 0 | 246.4 | 0 | 77% | 0 | 0 | 90% | 0 | 43.4552
7478 | 891 | 553 | 81 | 4.8 | 16.4 | 231.4831 | 0 | 45.6861 | 22.9162 | 0 | 0 | 230.2314 | 0 | 94% | 0 | 0 | 90% | 0 | 43.0442
7479 | 830 | 426 | 72 | 2.4 | 16.9 | 120.6985 | 93.2919 | 37.7791 | 14.9796 | 42.5752 | 7.244 | 79.4882 | 0 | 100% | 0 | 0 | 90% | 0 | 43.2659
7480 | 721 | 259 | 55 | 5.3 | 16.4 | 42.1667 | 119.9853 | 29.7824 | 1.9898 | 42.5754 | 15.3246 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 45.8193
7481 | 426 | 81 | 27 | 5.2 | 14.9 | 0 | 59.0103 | 7.4446 | 0 | 45.38 | 16.5615 | 0 | 43.8633 | 97% | 0 | 24.8108 | 50.3% | 0 | 46.7532
7482 | 0 | 1 | 1 | 4.5 | 13.5 | 0 | 0 | 0 | 0 | 64.0437 | 24.648 | 0 | 62.5385 | 92% | 0 | 25 | 10.3% | 0 | 46.7129
7483 | 0 | 0 | 0 | 1.3 | 11.7 | 0 | 0 | 0 | 0 | 118.1128 | 47.991 | 0 | 124.7805 | 83% | 0 | 0 | 10.3% | 0 | 45.0548
7484 | 0 | 0 | 0 | 4.6 | 11.6 | 0 | 0 | 0 | 0 | 108.435 | 43.9571 | 0 | 109.76 | 75% | 0 | 0 | 10.3% | 0 | 41.7863
7485 | 0 | 0 | 0 | 2.8 | 10.8 | 0 | 0 | 0 | 0 | 100.8565 | 40.8154 | 0 | 100.1642 | 67% | 0 | 0 | 10.3% | 0 | 38.7978
7486 | 0 | 0 | 0 | 3.9 | 10.8 | 0 | 0 | 0 | 0 | 94.5328 | 38.1556 | 0 | 92.7424 | 60% | 0 | 0 | 10.3% | 0 | 36.1466
7487 | 0 | 0 | 0 | 6.1 | 10 | 0 | 0 | 0 | 0 | 89.3159 | 35.975 | 0 | 86.5785 | 54% | 0 | 0 | 10.3% | 0 | 33.9245
7488 | 0 | 0 | 0 | 8.3 | 10.4 | 0 | 0 | 0 | 0 | 85.453 | 34.3221 | 0 | 82.2376 | 47% | 0 | 0 | 10.3% | 0 | 32.1999
7489 | 0 | 0 | 0 | 8.8 | 10.6 | 0 | 0 | 0 | 0 | 83.4622 | 33.4745 | 0 | 80.1597 | 41% | 0 | 0 | 10.3% | 0 | 31.2726
7490 | 0 | 0 | 0 | 4.1 | 10.4 | 0 | 0 | 0 | 0 | 82.9709 | 33.2771 | 0 | 79.8072 | 35% | 0 | 0 | 10.3% | 0 | 31.0009
7491 | 0 | 0 | 0 | 4.8 | 10.8 | 0 | 0 | 0 | 0 | 82.7528 | 33.1612 | 0 | 79.7624 | 29% | 0 | 0 | 10.3% | 0 | 30.8227
7492 | 0 | 0 | 0 | 1.6 | 7.4 | 0 | 0 | 0 | 0 | 84.7056 | 34.1219 | 0 | 82.1702 | 23% | 0 | 0 | 10.3% | 0 | 31.7282
7493 | 0 | 0 | 0 | 3.3 | 6.8 | 0 | 0 | 0 | 0 | 88.4981 | 35.7462 | 0 | 86.8044 | 17% | 0 | 0 | 10.3% | 0 | 33.3101
7494 | 0 | 0 | 0 | 2.5 | 5.9 | 0 | 0 | 0 | 0 | 93.0127 | 37.6956 | 0 | 92.389 | 10% | 0 | 0 | 10.3% | 0 | 35.2368
7495 | 29 | 5 | 4 | 1.4 | 5.4 | 0 | 0 | 0 | 0 | 101.2971 | 41.2057 | 0 | 102.2544 | 2% | 0 | 0 | 10.3% | 0 | 38.7399
7496 | 565 | 117 | 30 | 1.6 | 7.6 | 64.785 | 16.9275 | 13.9572 | 0 | 71.1183 | 28.0486 | 7.6434 | 13.309 | 2% | 0 | 0 | 10.3% | 0 | 40.5956
7497 | 804 | 300 | 48 | 1.2 | 11.7 | 169.1607 | -2.98e-14 | 38.8995 | 0 | 43.1206 | 15.754 | 125.8764 | 0 | 11% | 11.7015 | 0 | 26.22% | 0 | 41.0307
7498 | 898 | 458 | 55 | 1 | 14.3 | 223.7188 | 2.98e-14 | 52.5394 | 6.0595 | 42.5895 | 15.4287 | 181.9127 | 0 | 25% | 25 | 0 | 60.22% | 0 | 40.5492
7499 | 939 | 570 | 59 | 1.1 | 15.8 | 250.1351 | 0 | 49.9512 | 21.7993 | 42.6043 | 15.3649 | 208.5282 | 0 | 40% | 21.8994 | 0 | 90% | 0 | 40.7354
7500 | 957 | 624 | 60 | 3.4 | 16.5 | 261.106 | 0 | 27.3698 | 47.7302 | 42.6086 | 15.3314 | 219.506 | 0 | 56% | 0 | 0 | 90% | 0 | 39.8957
7501 | 945 | 617 | 65 | 3.4 | 16.7 | 257.1097 | 0 | 26.0457 | 49.0543 | 42.6105 | 15.3219 | 215.4452 | 0 | 72% | 0 | 0 | 90% | 0 | 38.5715
7502 | 830 | 531 | 93 | 3.6 | 17.4 | 215.2451 | 0 | 24.8193 | 40.0063 | 42.611 | 15.2848 | 173.5552 | 0 | 85% | 0 | 0 | 90% | 0 | 37.6762
7503 | 695 | 391 | 91 | 4 | 17.4 | 164.0119 | 0 | 22.4124 | 23.6533 | 42.6103 | 15.2846 | 122.1218 | 0 | 94% | 0 | 0 | 90% | 0 | 38.0403
7504 | 53 | 135 | 116 | 3.5 | 16.3 | 0 | 12.5589 | 5.3529 | 0 | 42.6081 | 15.3414 | 0 | 41.141 | 91% | 0 | 21.8392 | 55.06% | 0 | 40.4673
7505 | 10 | 37 | 36 | 2.6 | 14.7 | 0 | 1.6849 | 0 | 0 | 52.0452 | 19.3923 | 0 | 50.453 | 87% | 0 | 25 | 15.06% | 0 | 41.4303
7506 | 0 | 0 | 0 | 1.4 | 12.9 | 0 | 0 | 0 | 0 | 102.9309 | 41.4706 | 0 | 107.1623 | 79% | 0 | 3.1608 | 10% | 0 | 41.6543
7507 | 0 | 0 | 0 | 1.5 | 12.2 | 0 | 0 | 0 | 0 | 107.5162 | 43.5386 | 0 | 110.0819 | 71% | 0 | 0 | 10% | 0 | 41.0215
7508 | 0 | 0 | 0 | 2 | 13.3 | 0 | 0 | 0 | 0 | 102.0919 | 41.1923 | 0 | 102.6461 | 64% | 0 | 0 | 10% | 0 | 38.9047
7509 | 0 | 0 | 0 | 3.7 | 14.9 | 0 | 0 | 0 | 0 | 95.6143 | 38.3665 | 0 | 94.673 | 56% | 0 | 0 | 10% | 0 | 36.1602
7510 | 0 | 0 | 0 | 5.4 | 15.9 | 0 | 0 | 0 | 0 | 89.1906 | 35.5833 | 0 | 86.8994 | 50% | 0 | 0 | 10% | 0 | 33.3836
7511 | 0 | 0 | 0 | 5.7 | 16.3 | 0 | 0 | 0 | 0 | 83.7468 | 33.2685 | 0 | 80.6073 | 44% | 0 | 0 | 10% | 0 | 31.0257
7512 | 0 | 0 | 0 | 5.2 | 15.9 | 0 | 0 | 0 | 0 | 80.4686 | 31.8255 | 0 | 77.412 | 38% | 0 | 0 | 10% | 0 | 29.5155
7513 | 0 | 0 | 0 | 7.6 | 15.6 | 0 | 0 | 0 | 0 | 78.6279 | 31.0105 | 0 | 75.7341 | 32% | 0 | 0 | 10% | 0 | 28.6423
7514 | 0 | 0 | 0 | 9.8 | 15.8 | 0 | 0 | 0 | 0 | 77.8312 | 30.64 | 0 | 75.0681 | 27% | 0 | 0 | 10% | 0 | 28.2232
7515 | 0 | 0 | 0 | 10.7 | 15.7 | 0 | 0 | 0 | 0 | 78.2183 | 30.8218 | 0 | 75.5659 | 21% | 0 | 0 | 10% | 0 | 28.3626
7516 | 0 | 0 | 0 | 9.2 | 14.8 | 0 | 0 | 0 | 0 | 79.2694 | 31.3526 | 0 | 76.7157 | 15% | 0 | 0 | 10% | 0 | 28.8562
7517 | 0 | 0 | 0 | 6 | 13.8 | 0 | 0 | 0 | 0 | 80.6778 | 32.0539 | 0 | 78.2148 | 10% | 0 | 0 | 10% | 0 | 29.5246
7518 | 0 | 0 | 0 | 3.7 | 13.5 | 0 | 0 | 0 | 0 | 82.6671 | 32.9844 | 0 | 80.2946 | 4% | 0 | 0 | 10% | 0 | 30.4254
7519 | 0 | 2 | 2 | 3.2 | 13.4 | 0 | 0 | 0 | 0 | 47.6255 | 19.0985 | 0 | 47.1625 | 0% | 0 | 0 | 10% | 0 | 16.5588
7520 | 0 | 35 | 35 | 3 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.464
7521 | 0 | 87 | 87 | 4.6 | 14.4 | 0 | 0 | 0.20088 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2375
7522 | 2 | 186 | 184 | 5.9 | 13.9 | 0 | 0.57233 | 6.5983 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.185
7523 | 121 | 319 | 247 | 6.6 | 12.9 | 0 | 36.7153 | 25.0445 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 22.6556
7524 | 263 | 439 | 279 | 5.9 | 14.3 | 45.5862 | 12.4758 | 41.1336 | 0 | 0 | 0 | 43.6781 | 0 | 3% | 2.9964 | 0 | 14.07% | 0 | 36.9679
7525 | 2 | 218 | 215 | 7.3 | 14 | 0 | 0.62214 | 8.5455 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 2.5469 | 10% | 0 | 9.6823
7526 | 1 | 152 | 151 | 6.3 | 13.7 | 0 | 0.3004 | 3.822 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | 1.4841
7527 | 0 | 116 | 115 | 7.3 | 13.3 | 0 | 0 | 1.6284 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -0.68562
7528 | 0 | 69 | 69 | 6 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.2906
7529 | 1 | 22 | 22 | 7.9 | 12.9 | 0 | 0.16751 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.2677
7530 | 0 | 0 | 0 | 4.2 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.2452
7531 | 0 | 0 | 0 | 4.9 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.2233
7532 | 0 | 0 | 0 | 4 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.2017
7533 | 0 | 0 | 0 | 4.3 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.1806
7534 | 0 | 0 | 0 | 2.6 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.1598
7535 | 0 | 0 | 0 | 4.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.1394
7536 | 0 | 0 | 0 | 7.4 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.1193
7537 | 0 | 0 | 0 | 4.6 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.0998
7538 | 0 | 0 | 0 | 6.6 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.0806
7539 | 0 | 0 | 0 | 7.6 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.0618
7540 | 0 | 0 | 0 | 8.8 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.0434
7541 | 0 | 0 | 0 | 9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.0253
7542 | 0 | 0 | 0 | 5.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -2.0076
7543 | 5 | 3 | 3 | 3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.9903
7544 | 14 | 43 | 42 | 3.3 | 10.5 | 0 | 2.548 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.9731
7545 | 0 | 116 | 116 | 5.9 | 11.3 | 0 | 0 | 2.0816 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | 0.12524
7546 | 12 | 217 | 209 | 4.6 | 12.7 | 0 | 3.4282 | 9.4234 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | 7.4835
7547 | 16 | 267 | 255 | 4.4 | 14 | 0 | 4.846 | 13.267 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | 11.3433
7548 | 1 | 223 | 221 | 7 | 14.6 | 0 | 0.31147 | 8.9468 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | 7.0388
7549 | 8 | 235 | 228 | 5.6 | 15.3 | 0 | 2.4839 | 10.039 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | 8.1464
7550 | 0 | 154 | 153 | 4.5 | 15.8 | 0 | 0 | 3.8748 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | 1.9974
7551 | 0 | 132 | 131 | 6.2 | 16.4 | 0 | 0 | 2.6232 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | 0.76075
7552 | 0 | 108 | 107 | 6.7 | 16.5 | 0 | 0 | 1.5969 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -0.25102
7553 | 0 | 35 | 35 | 5.4 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.8337
7554 | 0 | 0 | 0 | 2.4 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.8198
7555 | 0 | 0 | 0 | 2.5 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.8061
7556 | 0 | 0 | 0 | 1.3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.7928
7557 | 0 | 0 | 0 | 2.3 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.7797
7558 | 0 | 0 | 0 | 1.2 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.7668
7559 | 0 | 0 | 0 | 2.1 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.7542
7560 | 0 | 0 | 0 | 2 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.7418
7561 | 0 | 0 | 0 | 1.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.7297
7562 | 0 | 0 | 0 | 1.2 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.7179
7563 | 0 | 0 | 0 | 1.6 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.7062
7564 | 0 | 0 | 0 | 2.2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.6947
7565 | 0 | 0 | 0 | 1.6 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.6835
7566 | 0 | 0 | 0 | 1.5 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.6725
7567 | 4 | 4 | 3 | 1.2 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3% | 0 | 0 | 10% | 0 | -1.6617
7568 | 523 | 124 | 48 | 1.8 | 12 | 57.3596 | 14.9064 | 13.1202 | 0 | 0 | 0 | 52.4703 | 0 | 8% | 0 | 0 | 10% | 0 | 11.966
7569 | 788 | 321 | 83 | 2.6 | 15.1 | 162.4734 | 0 | 41.102 | 0 | 0 | 0 | 153.9 | 0 | 20% | 0 | 0 | 10% | 0 | 39.2294
7570 | 863 | 446 | 70 | 1.2 | 17.2 | 212.835 | 0 | 57.0453 | 0 | 41.8488 | 0 | 168.9003 | 0 | 33% | 23.5572 | 0 | 42.04% | 0 | 30.5916
7571 | 802 | 507 | 75 | 1.5 | 18.4 | 209.3311 | 0 | 60.8054 | 0.90919 | 42.2079 | 5.0954 | 167.1865 | 0 | 46% | 19.5741 | 0 | 68.66% | 0 | 43.6095
7572 | 941 | 603 | 60 | 3.8 | 19.4 | 255.0393 | 0 | 48.7796 | 26.3204 | 42.3315 | 15.0695 | 212.7864 | 0 | 62% | 15.6923 | 0 | 90% | 0 | 45.3252
7573 | 949 | 601 | 59 | 6.1 | 19.7 | 254.3871 | 0 | 32.465 | 42.635 | 42.3955 | 15.0738 | 212.4875 | 0 | 78% | 0 | 0 | 90% | 0 | 44.695
7574 | 913 | 529 | 59 | 6.4 | 19.9 | 234.7351 | 0 | 31.9187 | 34.8242 | 42.4453 | 15.0792 | 192.9253 | 0 | 93% | 0 | 0 | 90% | 0 | 44.3299
7575 | 850 | 403 | 53 | 5.4 | 20 | 137.0355 | 75.5205 | 30.08 | 21.1079 | 42.479 | 15.085 | 95.1943 | 0 | 100% | 0 | 0 | 90% | 0 | 44.9357
7576 | 722 | 238 | 43 | 6.5 | 19.4 | 46.9771 | 111.8857 | 30.0863 | 0 | 47.2165 | 17.0836 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 47.8678
7577 | 370 | 66 | 21 | 3 | 18.3 | 0 | 48.1518 | 5.4668 | 0 | 55.2795 | 20.6166 | 0 | 53.7616 | 96% | 0 | 25 | 50% | 0 | 49.0059
7578 | 0 | 0 | 0 | 2.5 | 15 | 0 | 0 | 0 | 0 | 70.6015 | 27.4727 | 0 | 69.2941 | 91% | 0 | 25 | 10% | 0 | 49.5276
7579 | 0 | 0 | 0 | 4.7 | 14.7 | 0 | 0 | 0 | 0 | 125.4099 | 50.8146 | 0 | 133.803 | 81% | 0 | 0 | 10% | 0 | 47.8902
7580 | 0 | 0 | 0 | 2.6 | 13.1 | 0 | 0 | 0 | 0 | 113.9986 | 46.1921 | 0 | 115.9603 | 72% | 0 | 0 | 10% | 0 | 44.1144
7581 | 0 | 0 | 0 | 1.6 | 11.2 | 0 | 0 | 0 | 0 | 103.0765 | 41.7365 | 0 | 102.3782 | 64% | 0 | 0 | 10% | 0 | 39.8361
7582 | 0 | 0 | 0 | 1.2 | 10.5 | 0 | 0 | 0 | 0 | 96.3876 | 38.9519 | 0 | 94.5061 | 57% | 0 | 0 | 10% | 0 | 37.0537
7583 | 0 | 0 | 0 | 1.3 | 11 | 0 | 0 | 0 | 0 | 91.2482 | 36.7538 | 0 | 88.579 | 51% | 0 | 0 | 10% | 0 | 34.8079
7584 | 0 | 0 | 0 | 1.5 | 11 | 0 | 0 | 0 | 0 | 87.6525 | 35.2281 | 0 | 84.5075 | 44% | 0 | 0 | 10% | 0 | 33.2127
7585 | 0 | 0 | 0 | 3.4 | 12.3 | 0 | 0 | 0 | 0 | 86.8723 | 34.8311 | 0 | 83.8296 | 38% | 0 | 0 | 10% | 0 | 32.7371
7586 | 0 | 0 | 0 | 3.8 | 12.9 | 0 | 0 | 0 | 0 | 86.8717 | 34.7981 | 0 | 84.0339 | 31% | 0 | 0 | 10% | 0 | 32.6369
7587 | 0 | 0 | 0 | 6 | 13.9 | 0 | 0 | 0 | 0 | 89.2288 | 35.7362 | 0 | 87.0206 | 25% | 0 | 0 | 10% | 0 | 33.5168
7588 | 0 | 0 | 0 | 7.1 | 14.5 | 0 | 0 | 0 | 0 | 97.9835 | 39.3928 | 0 | 97.6302 | 17% | 0 | 0 | 10% | 0 | 37.1251
7589 | 0 | 0 | 0 | 9.8 | 15 | 0 | 0 | 0 | 0 | 112.3799 | 45.3836 | 0 | 114.7102 | 9% | 0 | 0 | 10% | 0 | 43.1008
7590 | 0 | 0 | 0 | 9.9 | 14.6 | 0 | 0 | 0 | 0 | 111.2944 | 45.0504 | 0 | 114.442 | 0% | 0 | 0 | 10% | 0 | 42.8324
7591 | 1 | 2 | 2 | 10.7 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9888
7592 | 329 | 84 | 37 | 8.9 | 15.4 | 0 | 48.1001 | 6.7946 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.8249
7593 | 739 | 284 | 62 | 10.2 | 17.6 | 144.1377 | 0 | 35.9711 | 0 | 0 | 0 | 138.3514 | 0 | 11% | 0 | 0 | 10% | 0 | 34.3073
7594 | 874 | 441 | 62 | 10.1 | 18.7 | 208.2737 | 0 | 56.5189 | 0 | 0 | 0 | 205.877 | 0 | 26% | 7.3379 | 0 | 19.98% | 0 | 46.9021
7595 | 925 | 555 | 66 | 8 | 21.1 | 238.6913 | 0 | 69.7948 | 0 | 0 | 0 | 237.0002 | 0 | 44% | 21.0456 | 0 | 48.6% | 0 | 46.1546
7596 | 924 | 597 | 66 | 7.1 | 21.7 | 246.7854 | 0 | 73.5542 | 0.73193 | 0 | 0 | 245.384 | 0 | 63% | 25 | 0 | 82.6% | 0 | 45.839
7597 | 750 | 516 | 87 | 3.8 | 22.1 | 198.4334 | 0 | 52.3468 | 9.1536 | 0 | 0 | 197.2838 | 0 | 78% | 5.44 | 0 | 90% | 0 | 44.599
7598 | 864 | 511 | 68 | 0.1 | 22 | 224.898 | 0 | 46.1478 | 17.3271 | 42.5838 | 1.2395 | 183.8957 | 0 | 92% | 0 | 0 | 90% | 0 | 44.3369
7599 | 852 | 404 | 56 | 0 | 22.1 | 151.6645 | 61.2038 | 30.9181 | 20.3617 | 42.5883 | 14.9821 | 110.3233 | 0 | 100% | 0 | 0 | 90% | 0 | 44.809
7600 | 403 | 147 | 24 | 0 | 11.2 | 42.1534 | 39.0971 | 13.1996 | 0 | 42.5887 | 15.5498 | 0 | 0 | 100% | 0 | 18.5535 | 60.31% | 0 | 48.0163
7601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5011 | 26.1379 | 0 | 65.1944 | 95% | 0 | 25 | 20.31% | 0 | 49.0894
7602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.7679 | 45.9811 | 0 | 118.8889 | 87% | 0 | 6.4465 | 10% | 0 | 49.4975
7603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.9855 | 49.5658 | 0 | 124.2436 | 77% | 0 | 0 | 10% | 0 | 47.4658
7604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.5968 | 45.6381 | 0 | 111.8612 | 69% | 0 | 0 | 10% | 0 | 43.8361
7605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.9221 | 41.5692 | 0 | 100.3703 | 61% | 0 | 0 | 10% | 0 | 39.8181
7606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.9998 | 38.647 | 0 | 92.4915 | 54% | 0 | 0 | 10% | 0 | 36.8532
7607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6823 | 36.3822 | 0 | 86.385 | 47% | 0 | 0 | 10% | 0 | 34.5162
7608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9564 | 35.2241 | 0 | 83.4558 | 41% | 0 | 0 | 10% | 0 | 33.267
7609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.605 | 34.6516 | 0 | 82.1427 | 35% | 0 | 0 | 10% | 0 | 32.6076
7610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.4451 | 34.5843 | 0 | 82.1893 | 28% | 0 | 0 | 10% | 0 | 32.4628
7611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1365 | 35.7262 | 0 | 85.5688 | 22% | 0 | 0 | 10% | 0 | 33.5361
7612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.9568 | 39.4733 | 0 | 96.2985 | 15% | 0 | 0 | 10% | 0 | 37.2261
7613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.3065 | 45.0995 | 0 | 112.1347 | 6% | 0 | 0 | 10% | 0 | 42.8312
7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.0251 | 32.3609 | 0 | 81.0242 | 0% | 0 | 0 | 10% | 0 | 30.1995
7615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0104
7616 | 137 | 48 | 22 | 1.9 | 4.7 | 0 | 24.4247 | 1.1802 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.81301
7617 | 511 | 248 | 94 | 6.5 | 15.8 | 77.1216 | 20.5368 | 27.5684 | 0 | 0 | 0 | 74.1464 | 0 | 6% | 0 | 0 | 10% | 0 | 26.191
7618 | 128 | 228 | 172 | 6 | 16.4 | 0 | 36.386 | 16.4318 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | 15.4025
7619 | 72 | 296 | 256 | 8.9 | 16.4 | 0 | 21.6897 | 20.6674 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | 18.7092
7620 | 16 | 248 | 237 | 13 | 16.7 | 0 | 0 | 11.4115 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | 9.47
7621 | 64 | 292 | 254 | 11.1 | 17.1 | 0 | 19.7652 | 19.888 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | 17.9631
7622 | 170 | 301 | 210 | 12.4 | 17.1 | 0 | 0 | 24.4056 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | 22.4968
7623 | 10 | 169 | 164 | 12.2 | 14.2 | 0 | 0 | 5.6576 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | 3.7644
7624 | 45 | 137 | 123 | 9.2 | 13.2 | 0 | 10.4978 | 6.0108 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | 4.133
7625 | 3 | 34 | 33 | 10.3 | 12.2 | 0 | 0.47526 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.8626
7626 | 0 | 0 | 0 | 5.6 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.8478
7627 | 0 | 0 | 0 | 4.1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.8333
7628 | 0 | 0 | 0 | 6.1 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.819
7629 | 0 | 0 | 0 | 6.7 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.805
7630 | 0 | 0 | 0 | 5.5 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.7913
7631 | 0 | 0 | 0 | 4.3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.7779
7632 | 0 | 0 | 0 | 7.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.7648
7633 | 0 | 0 | 0 | 7.8 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.7519
7634 | 0 | 0 | 0 | 5.2 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.7393
7635 | 0 | 0 | 0 | 5.4 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.727
7636 | 0 | 0 | 0 | 7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.7149
7637 | 0 | 0 | 0 | 6.4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.703
7638 | 0 | 0 | 0 | 9.4 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.6914
7639 | 1 | 2 | 2 | 6.4 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | -1.68
7640 | 387 | 88 | 32 | 7.5 | 9 | 0 | 57.4548 | 8.3052 | 0 | 0 | 0 | 0 | 0 | 6% | 0 | 0 | 10% | 0 | 6.638
7641 | 733 | 272 | 58 | 4.7 | 10.6 | 146.2527 | 0 | 35.8529 | 0 | 0 | 0 | 138.371 | 0 | 17% | 0 | 0 | 10% | 0 | 34.1472
7642 | 848 | 433 | 72 | 6 | 12.6 | 203.8194 | 0 | 56.7356 | 0 | 0 | 0 | 199.708 | 0 | 32% | 6.0599 | 0 | 18.24% | 0 | 48.4012
7643 | 909 | 556 | 84 | 6.9 | 13 | 233.8495 | 0 | 72.1428 | 0 | 42.3243 | 0 | 192.0207 | 0 | 47% | 20.533 | 0 | 46.17% | 0 | 48.4934
7644 | 301 | 394 | 220 | 4 | 13.2 | 68.0352 | 0 | 39.7019 | 0 | 0 | 0 | 67.3947 | 0 | 52% | 0 | 8.3158 | 32.86% | 0 | 46.9568
7645 | 139 | 300 | 219 | 6.7 | 12.9 | 0 | 42.8539 | 24.2071 | 0 | 50.2237 | 9.8097 | 0 | 46.7049 | 48% | 0 | 13.2101 | 11.72% | 0 | 46.0275
7646 | 643 | 568 | 236 | 6.9 | 13.9 | 128.3038 | 32.8019 | 57.4453 | 6.6529 | 42.4288 | 15.3878 | 91.9562 | 7.2852 | 55% | 25 | 0 | 45.73% | 0 | 45.9495
7647 | 209 | 222 | 128 | 5.9 | 12.6 | 0 | 57.6563 | 18.2173 | 0 | 42.4545 | 15.4489 | 0 | 39.5494 | 52% | 0 | 14.0754 | 23.2% | 0 | 46.6363
7648 | 192 | 150 | 92 | 5.6 | 12.3 | 0 | 44.6108 | 10.6704 | 0 | 81.9803 | 32.5617 | 0 | 81.0568 | 46% | 0 | 8.2527 | 10% | 0 | 49.3146
7649 | 150 | 62 | 40 | 3.9 | 11.3 | 0 | 23.1022 | 2.2284 | 0 | 122.2171 | 49.7217 | 0 | 126.1842 | 36% | 0 | 0 | 10% | 0 | 49.7384
7650 | 0 | 0 | 0 | 2 | 9.3 | 0 | 0 | 0 | 0 | 125.7959 | 51.3139 | 0 | 129.7843 | 26% | 0 | 0 | 10% | 0 | 49.2298
7651 | 0 | 0 | 0 | 1 | 7.3 | 0 | 0 | 0 | 0 | 121.6307 | 49.6613 | 0 | 124.1947 | 17% | 0 | 0 | 10% | 0 | 47.6961
7652 | 0 | 0 | 0 | 1.6 | 5.4 | 0 | 0 | 0 | 0 | 113.1749 | 46.1945 | 0 | 113.904 | 8% | 0 | 0 | 10% | 0 | 44.309
7653 | 0 | 0 | 0 | 0.7 | 4.9 | 0 | 0 | 0 | 0 | 104.5149 | 42.5847 | 0 | 103.7207 | 0% | 0 | 0 | 10% | 0 | 40.7356
7654 | 0 | 0 | 0 | 1.4 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7128
7655 | 0 | 0 | 0 | 1.9 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7016
7656 | 0 | 0 | 0 | 0.8 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6906
7657 | 0 | 0 | 0 | 1 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6798
7658 | 0 | 0 | 0 | 2.5 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6692
7659 | 0 | 0 | 0 | 1.9 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6588
7660 | 0 | 0 | 0 | 1.7 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6487
7661 | 0 | 0 | 0 | 0.6 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6388
7662 | 0 | 0 | 0 | 1.5 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6289
7663 | 0 | 2 | 2 | 1.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6193
7664 | 387 | 105 | 51 | 0.9 | 6.3 | 0 | 56.9365 | 8.4092 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 6.8008
7665 | 699 | 267 | 64 | 3.4 | 9.9 | 139.1798 | 0 | 34.88 | 0 | 0 | 0 | 131.2597 | 0 | 10% | 0 | 0 | 10% | 0 | 33.2417
7666 | 807 | 416 | 75 | 4.8 | 11.4 | 193.4274 | 0 | 54.2905 | 0 | 42.2406 | 0 | 151.3521 | 0 | 22% | 13.9694 | 0 | 29% | 0 | 37.6159
7667 | 879 | 537 | 83 | 5.6 | 12.8 | 226.1343 | 0 | 58.3196 | 11.2234 | 42.4596 | 11.7106 | 185.0491 | 0 | 36% | 24.7776 | 0 | 62.7% | 0 | 42.6046
7668 | 899 | 592 | 86 | 4.6 | 13.7 | 240.0114 | 0 | 49.1401 | 25.9599 | 42.5177 | 15.4282 | 199.0139 | 0 | 52% | 20.0765 | 0 | 90% | 0 | 41.8164
7669 | 914 | 591 | 81 | 5.1 | 14.5 | 243.1833 | 0 | 27.666 | 47.434 | 42.5446 | 15.4035 | 202.2189 | 0 | 67% | 0 | 0 | 90% | 0 | 40.3466
7670 | 903 | 526 | 73 | 5.8 | 15.1 | 230.7541 | 0 | 26.5537 | 41.7719 | 42.5619 | 15.3828 | 189.7093 | 0 | 81% | 0 | 0 | 90% | 0 | 39.3156
7671 | 865 | 403 | 58 | 5.2 | 15 | 202.7004 | 0 | 26.7844 | 26.6723 | 42.5715 | 15.391 | 161.4411 | 0 | 93% | 0 | 0 | 90% | 0 | 39.8175
7672 | 741 | 236 | 44 | 5.4 | 14.4 | 130.438 | 12.4801 | 26.376 | 5.2603 | 42.5768 | 15.4196 | 88.8151 | 0 | 100% | 0 | 0 | 90% | 0 | 42.7912
7673 | 359 | 61 | 20 | 4.8 | 12.8 | 0 | 53.7791 | 5.2431 | 0 | 44.1273 | 16.1274 | 0 | 42.62 | 97% | 0 | 24.5013 | 50.8% | 0 | 43.8266
7674 | 0 | 0 | 0 | 4.2 | 11.2 | 0 | 0 | 0 | 0 | 58.4822 | 22.3444 | 0 | 56.8576 | 93% | 0 | 25 | 10.8% | 0 | 44.415
7675 | 0 | 0 | 0 | 2.4 | 10.8 | 0 | 0 | 0 | 0 | 115.5466 | 46.973 | 0 | 121.7009 | 84% | 0 | 0 | 10.8% | 0 | 44.0239
7676 | 0 | 0 | 0 | 2.5 | 8.8 | 0 | 0 | 0 | 0 | 107.7531 | 43.8076 | 0 | 109.1056 | 76% | 0 | 0 | 10.8% | 0 | 41.6022
7677 | 0 | 0 | 0 | 2.4 | 7.5 | 0 | 0 | 0 | 0 | 100.6247 | 40.8545 | 0 | 99.9911 | 68% | 0 | 0 | 10.8% | 0 | 38.8102
7678 | 0 | 0 | 0 | 1.5 | 5.4 | 0 | 0 | 0 | 0 | 93.5591 | 37.9379 | 0 | 91.6568 | 61% | 0 | 0 | 10.8% | 0 | 35.9076
7679 | 0 | 0 | 0 | 1.9 | 5.3 | 0 | 0 | 0 | 0 | 87.0395 | 35.1651 | 0 | 83.959 | 55% | 0 | 0 | 10.8% | 0 | 33.09
7680 | 0 | 0 | 0 | 2 | 4.7 | 0 | 0 | 0 | 0 | 82.1302 | 33.0735 | 0 | 78.6386 | 49% | 0 | 0 | 10.8% | 0 | 30.9138
7681 | 0 | 0 | 0 | 0.8 | 4.1 | 0 | 0 | 0 | 0 | 79.973 | 32.1019 | 0 | 76.7475 | 43% | 0 | 0 | 10.8% | 0 | 29.8521
7682 | 0 | 0 | 0 | 1.1 | 4.4 | 0 | 0 | 0 | 0 | 79.435 | 31.8513 | 0 | 76.4097 | 37% | 0 | 0 | 10.8% | 0 | 29.5297
7683 | 0 | 0 | 0 | 1.9 | 4.6 | 0 | 0 | 0 | 0 | 79.4026 | 31.833 | 0 | 76.5366 | 31% | 0 | 0 | 10.8% | 0 | 29.453
7684 | 0 | 0 | 0 | 2.2 | 3.9 | 0 | 0 | 0 | 0 | 81.1347 | 32.6386 | 0 | 78.4074 | 26% | 0 | 0 | 10.8% | 0 | 30.2078
7685 | 0 | 0 | 0 | 1.9 | 3.8 | 0 | 0 | 0 | 0 | 83.4926 | 33.7005 | 0 | 80.9923 | 20% | 0 | 0 | 10.8% | 0 | 31.2258
7686 | 0 | 0 | 0 | 2.3 | 5.7 | 0 | 0 | 0 | 0 | 85.8097 | 34.637 | 0 | 83.8252 | 13% | 0 | 0 | 10.8% | 0 | 32.1267
7687 | 0 | 1 | 1 | 1.7 | 4.7 | 0 | 0 | 0 | 0 | 93.3014 | 37.8492 | 0 | 93.0367 | 6% | 0 | 0 | 10.8% | 0 | 35.3067
7688 | 470 | 101 | 37 | 2 | 7.2 | 47.8443 | 12.7592 | 10.8657 | 0 | 72.902 | 28.8508 | 0 | 24.0541 | 5% | 0 | 0 | 10.8% | 0 | 38.4275
7689 | 761 | 321 | 103 | 2.6 | 11.2 | 153.4573 | 0 | 40.6338 | 0 | 42.4732 | 15.5076 | 110.0443 | 0 | 13% | 14.4458 | 0 | 30.44% | 0 | 39.9192
7690 | 707 | 490 | 191 | 5.3 | 14.2 | 166.3421 | 0 | 51.8088 | 5.9941 | 42.5566 | 15.4212 | 124.566 | 0 | 22% | 25 | 0 | 64.44% | 0 | 40.3204
7691 | 290 | 436 | 288 | 5.6 | 15 | 61.4051 | 0 | 42.9686 | 0 | 42.5796 | 15.394 | 20.4826 | 0 | 24% | 16.0559 | 0 | 86.28% | 0 | 41.3121
7692 | 1 | 195 | 192 | 4 | 13.7 | 0 | 0.30819 | 6.7743 | 0 | 42.5726 | 15.4481 | 0 | 40.5571 | 21% | 0 | 20.4677 | 53.53% | 0 | 40.9795
7693 | 0 | 176 | 174 | 3.3 | 13 | 0 | 0 | 5.3724 | 0 | 42.5619 | 15.4727 | 0 | 40.5602 | 18% | 0 | 20.919 | 20.06% | 0 | 39.1076
7694 | 0 | 144 | 143 | 4.6 | 13.6 | 0 | 0 | 3.2927 | 0 | 78.6111 | 31.1015 | 0 | 78.3163 | 12% | 0 | 6.2884 | 10% | 0 | 37.9585
7695 | 1 | 141 | 139 | 9.6 | 14.9 | 0 | 0.27445 | 3.3383 | 0 | 94.2157 | 37.7844 | 0 | 94.7621 | 5% | 0 | 0 | 10% | 0 | 38.4001
7696 | 161 | 113 | 80 | 8.7 | 15.4 | 0 | 37.1249 | 8.1694 | 0 | 63.6807 | 25.4425 | 0 | 63.2109 | 0% | 0 | 0 | 10% | 0 | 30.97
7697 | 146 | 51 | 30 | 7.3 | 15.2 | 0 | 21.2847 | 1.2847 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.2611
7698 | 0 | 0 | 0 | 4 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.5189
7699 | 0 | 0 | 0 | 3.2 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4924
7700 | 0 | 0 | 0 | 3.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4663
7701 | 0 | 0 | 0 | 4.2 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4407
7702 | 0 | 0 | 0 | 2 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.4157
7703 | 0 | 0 | 0 | 1.1 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3911
7704 | 0 | 0 | 0 | 1.1 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3669
7705 | 0 | 0 | 0 | 0.8 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3432
7706 | 0 | 0 | 0 | 1.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.3201
7707 | 0 | 0 | 0 | 4 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2972
7708 | 0 | 0 | 0 | 3.9 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2747
7709 | 0 | 0 | 0 | 4.3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2529
7710 | 0 | 0 | 0 | 3 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2315
7711 | 0 | 1 | 1 | 3.5 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.2105
7712 | 222 | 63 | 28 | 3.4 | 8 | 0 | 38.4954 | 3.4273 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 1.2375
7713 | 716 | 256 | 54 | 1.4 | 11.1 | 116.4381 | 29.4298 | 34.1703 | 0 | 0 | 0 | 109.1603 | 0 | 9% | 0 | 0 | 10% | 0 | 32.4262
7714 | 849 | 415 | 63 | 2.1 | 13.5 | 205.1425 | 0 | 55.2646 | 0 | 0 | 0 | 200.9072 | 0 | 24% | 5.3363 | 0 | 17.26% | 0 | 47.6974
7715 | 908 | 530 | 69 | 2 | 14.9 | 236.4804 | 0 | 69.5663 | 0 | 42.3691 | 0 | 194.1169 | 0 | 38% | 22.4139 | 0 | 47.74% | 0 | 44.0736
7716 | 929 | 586 | 71 | 3.6 | 15.7 | 248.9793 | 0 | 66.6667 | 8.4333 | 42.4823 | 8.4089 | 207.117 | 0 | 54% | 24.8383 | 0 | 81.52% | 0 | 47.2884
7717 | 927 | 580 | 71 | 5.4 | 15.7 | 246.0416 | 0 | 40.3065 | 34.7935 | 42.5193 | 15.339 | 204.2795 | 0 | 69% | 6.235 | 0 | 90% | 0 | 46.6926
7718 | 901 | 512 | 67 | 6.6 | 15.6 | 228.9429 | 0 | 33.5389 | 33.6962 | 42.5379 | 15.3504 | 187.2139 | 0 | 83% | 0 | 0 | 90% | 0 | 46.3166
7719 | 843 | 391 | 60 | 6.2 | 15.4 | 195.3231 | 0 | 33.3517 | 18.7378 | 42.5515 | 15.3648 | 153.4754 | 0 | 95% | 0 | 0 | 90% | 0 | 47.208
7720 | 717 | 227 | 45 | 2.3 | 15.9 | 115.6408 | 25.4304 | 30.4249 | 0 | 42.5596 | 15.344 | 73.7261 | 0 | 100% | 0 | 3.024 | 85.16% | 0 | 50.0879
7721 | 351 | 59 | 20 | 5.2 | 13.3 | 0 | 49.8296 | 5.0553 | 0 | 58.046 | 22.0594 | 0 | 56.5625 | 96% | 0 | 25 | 45.16% | 0 | 50.0548
7722 | 0 | 0 | 0 | 2.3 | 11.5 | 0 | 0 | 0 | 0 | 78.1719 | 30.8875 | 0 | 78.085 | 90% | 0 | 21.976 | 10% | 0 | 49.925
7723 | 0 | 0 | 0 | 1 | 9.5 | 0 | 0 | 0 | 0 | 127.4698 | 51.9983 | 0 | 135.4085 | 80% | 0 | 0 | 10% | 0 | 49.2399
7724 | 0 | 0 | 0 | 0.9 | 7.5 | 0 | 0 | 0 | 0 | 117.3101 | 47.8542 | 0 | 119.475 | 71% | 0 | 0 | 10% | 0 | 45.8571
7725 | 0 | 0 | 0 | 1.3 | 7.1 | 0 | 0 | 0 | 0 | 106.1798 | 43.2137 | 0 | 105.6694 | 63% | 0 | 0 | 10% | 0 | 41.3944
7726 | 0 | 0 | 0 | 2.9 | 7.8 | 0 | 0 | 0 | 0 | 98.0843 | 39.7739 | 0 | 96.116 | 56% | 0 | 0 | 10% | 0 | 37.9631
7727 | 0 | 0 | 0 | 2 | 7.4 | 0 | 0 | 0 | 0 | 92.3346 | 37.3585 | 0 | 89.5701 | 49% | 0 | 0 | 10% | 0 | 35.495
7728 | 0 | 0 | 0 | 1.9 | 5.7 | 0 | 0 | 0 | 0 | 88.8643 | 35.9304 | 0 | 85.6538 | 42% | 0 | 0 | 10% | 0 | 33.9928
7729 | 0 | 0 | 0 | 2 | 5.7 | 0 | 0 | 0 | 0 | 87.6303 | 35.4069 | 0 | 84.4467 | 36% | 0 | 0 | 10% | 0 | 33.3886
7730 | 0 | 0 | 0 | 1.3 | 5.4 | 0 | 0 | 0 | 0 | 87.7478 | 35.4647 | 0 | 84.808 | 29% | 0 | 0 | 10% | 0 | 33.3743
7731 | 0 | 0 | 0 | 1 | 4.5 | 0 | 0 | 0 | 0 | 90.2201 | 36.537 | 0 | 87.9516 | 23% | 0 | 0 | 10% | 0 | 34.3846
7732 | 0 | 0 | 0 | 1.4 | 4.6 | 0 | 0 | 0 | 0 | 99.8535 | 40.6142 | 0 | 99.5623 | 15% | 0 | 0 | 10% | 0 | 38.4091
7733 | 0 | 0 | 0 | 1.7 | 4.5 | 0 | 0 | 0 | 0 | 115.3296 | 47.1202 | 0 | 117.9105 | 6% | 0 | 0 | 10% | 0 | 44.8968
7734 | 0 | 0 | 0 | 2.3 | 4.7 | 0 | 0 | 0 | 0 | 79.5274 | 32.5363 | 0 | 82.0431 | 0% | 0 | 0 | 10% | 0 | 30.4444
7735 | 0 | 2 | 1 | 2.4 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9341
7736 | 31 | 46 | 43 | 1.9 | 5.3 | 0 | 5.3382 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9187
7737 | 147 | 203 | 158 | 1 | 8.4 | 0 | 35.1314 | 15.3292 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 13.4259
7738 | 195 | 312 | 228 | 0.6 | 11.5 | 0 | 54.5234 | 27.3349 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 25.4466
7739 | 343 | 424 | 243 | 1.7 | 12.7 | 63.4898 | 16.3322 | 43.3293 | 0 | 0 | 0 | 60.7693 | 0 | 5% | 0 | 0 | 10% | 0 | 42.0879
7740 | 732 | 544 | 137 | 1.8 | 13.8 | 192.7499 | 0 | 67.5659 | 0 | 0 | 0 | 188.6576 | 0 | 19% | 18.0923 | 0 | 34.61% | 0 | 47.3494
7741 | 698 | 546 | 160 | 1.7 | 14.5 | 182.5258 | -2.55e-14 | 65.0594 | 1.0062 | 42.495 | 2.1995 | 141.5612 | 0 | 30% | 21.3205 | 0 | 63.6% | 0 | 43.4043
7742 | 251 | 336 | 207 | 0.8 | 14.9 | 0 | 60.9649 | 31.8038 | 0 | 45.3477 | 16.5485 | 0 | 42.2414 | 27% | 0 | 0 | 63.6% | 0 | 47.2668
7743 | 157 | 276 | 208 | 2.2 | 15 | 0 | 42.8838 | 22.0581 | 0 | 42.5249 | 15.3742 | 0 | 39.6099 | 24% | 0 | 12.9376 | 42.9% | 0 | 48.3211
7744 | 95 | 161 | 139 | 3.7 | 13.5 | 0 | 21.7536 | 10.1323 | 0 | 56.6151 | 21.4719 | 0 | 54.2761 | 20% | 0 | 20.5633 | 10% | 0 | 50.0411
7745 | 52 | 48 | 41 | 3.2 | 12.3 | 0 | 7.1937 | 0.24359 | 0 | 127.2522 | 51.7536 | 0 | 132.3559 | 10% | 0 | 0 | 10% | 0 | 49.7307
7746 | 0 | 0 | 0 | 2.3 | 10.5 | 0 | 0 | 0 | 0 | 127.1893 | 51.8338 | 0 | 131.631 | 0% | 0 | 0 | 10% | 0 | 49.684
7747 | 0 | 0 | 0 | 2.1 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.868
7748 | 0 | 0 | 0 | 1.4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.854
7749 | 0 | 0 | 0 | 1.5 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8401
7750 | 0 | 0 | 0 | 1.4 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8265
7751 | 0 | 0 | 0 | 1.1 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8132
7752 | 0 | 0 | 0 | 1.3 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8002
7753 | 0 | 0 | 0 | 1.7 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7873
7754 | 0 | 0 | 0 | 0.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7748
7755 | 0 | 0 | 0 | 1.2 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7624
7756 | 0 | 0 | 0 | 0.7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7504
7757 | 0 | 0 | 0 | 0.7 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7386
7758 | 0 | 0 | 0 | 0.8 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7269
7759 | 0 | 1 | 1 | 1.3 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7155
7760 | 330 | 70 | 29 | 0.7 | 5.3 | 0 | 56.4353 | 6.3002 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.5959
7761 | 668 | 248 | 66 | 0.8 | 9.2 | 106.706 | 27.2401 | 33.0545 | 0 | 0 | 0 | 99.9893 | 0 | 8% | 0 | 0 | 10% | 0 | 31.4642
7762 | 635 | 360 | 103 | 0.7 | 12.1 | 148.539 | 0 | 45.0388 | 0 | 0 | 0 | 145.3857 | 0 | 19% | 0 | 0 | 10% | 0 | 43.2843
7763 | 629 | 472 | 154 | 2.2 | 12.8 | 157.6068 | 0 | 56.411 | 0 | 0 | 0 | 155.3941 | 0 | 31% | 4.911 | 0 | 16.68% | 0 | 49.6442
7764 | 883 | 577 | 92 | 3.2 | 13.8 | 234.7895 | 0 | 74.8928 | 0 | 42.43 | 0 | 193.0801 | 0 | 46% | 22.8912 | 0 | 47.81% | 0 | 48.8857
7765 | 707 | 546 | 157 | 3.5 | 14.4 | 183.743 | 0 | 62.8175 | 3.71 | 42.5018 | 8.9612 | 142.9269 | 0 | 57% | 22.8778 | 0 | 78.92% | 0 | 46.5306
7766 | 124 | 289 | 222 | 3.4 | 14 | 0 | 36.7106 | 22.64 | 0 | 42.5185 | 15.4163 | 0 | 39.5206 | 54% | 0 | 11.3923 | 60.7% | 0 | 48.397
7767 | 1 | 164 | 163 | 2.7 | 13.7 | 0 | 0.27253 | 5.2803 | 0 | 55.8056 | 21.089 | 0 | 52.4088 | 50% | 0 | 25 | 20.7% | 0 | 49.3022
7768 | 0 | 49 | 49 | 2.2 | 13.5 | 0 | 0 | 0 | 0 | 111.941 | 45.1496 | 0 | 114.9435 | 41% | 0 | 6.6857 | 10% | 0 | 49.5891
7769 | 45 | 23 | 20 | 2.2 | 12.8 | 0 | 6.0711 | 0 | 0 | 127.2529 | 51.721 | 0 | 131.828 | 31% | 0 | 0 | 10% | 0 | 49.5849
7770 | 0 | 0 | 0 | 1.3 | 11.4 | 0 | 0 | 0 | 0 | 127.2364 | 51.8028 | 0 | 131.0555 | 21% | 0 | 0 | 10% | 0 | 49.8028
7771 | 0 | 0 | 0 | 1.2 | 10.2 | 0 | 0 | 0 | 0 | 127.203 | 51.8551 | 0 | 130.4647 | 11% | 0 | 0 | 10% | 0 | 49.9524
7772 | 0 | 0 | 0 | 1.7 | 9.7 | 0 | 0 | 0 | 0 | 118.3244 | 48.1871 | 0 | 119.5462 | 2% | 0 | 0 | 10% | 0 | 46.3731
7773 | 0 | 0 | 0 | 1.5 | 8.8 | 0 | 0 | 0 | 0 | 21.8886 | 8.8991 | 0 | 21.7375 | 0% | 0 | 0 | 10% | 0 | 7.251
7774 | 0 | 0 | 0 | 0.5 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.6102
7775 | 0 | 0 | 0 | 1 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.601
7776 | 0 | 0 | 0 | 1.1 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5919
7777 | 0 | 0 | 0 | 1.1 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.583
7778 | 0 | 0 | 0 | 0.7 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5744
7779 | 0 | 0 | 0 | 0.5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5658
7780 | 0 | 0 | 0 | 1 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5574
7781 | 0 | 0 | 0 | 1 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5492
7782 | 0 | 0 | 0 | 1.3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5411
7783 | 0 | 0 | 0 | 1.1 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5331
7784 | 0 | 25 | 25 | 1 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.5253
7785 | 11 | 113 | 109 | 0.9 | 9.6 | 0 | 2.6107 | 2.2914 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.77383
7786 | 0 | 127 | 126 | 0.5 | 10.4 | 0 | 0 | 2.4311 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.92099
7787 | 0 | 114 | 113 | 1.1 | 11.4 | 0 | 0 | 1.4393 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.063339
7788 | 0 | 222 | 220 | 1.1 | 12.2 | 0 | 0 | 9.1276 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 7.6322
7789 | 9 | 328 | 320 | 1.9 | 13.7 | 0 | 2.7486 | 19.5173 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 18.029
7790 | 136 | 311 | 243 | 2 | 14.8 | 0 | 40.2138 | 25.7761 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 24.2948
7791 | 68 | 213 | 183 | 2.7 | 15.1 | 0 | 18.492 | 12.9821 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 11.5076
7792 | 11 | 96 | 93 | 2.6 | 14.9 | 0 | 2.5029 | 1.2079 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.25987
7793 | 14 | 35 | 33 | 2.3 | 14.4 | 0 | 1.8436 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4612
7794 | 0 | 0 | 0 | 2.5 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4548
7795 | 0 | 0 | 0 | 2.9 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4485
7796 | 0 | 0 | 0 | 2.1 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4424
7797 | 0 | 0 | 0 | 2.8 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4363
7798 | 0 | 0 | 0 | 1.7 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4303
7799 | 0 | 0 | 0 | 1.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4245
7800 | 0 | 0 | 0 | 2.1 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4188
7801 | 0 | 0 | 0 | 2.3 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4132
7802 | 0 | 0 | 0 | 2.4 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4077
7803 | 0 | 0 | 0 | 2.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.4023
7804 | 0 | 0 | 0 | 1.8 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.397
7805 | 0 | 0 | 0 | 1.9 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3918
7806 | 0 | 0 | 0 | 1 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3867
7807 | 0 | 0 | 0 | 0.8 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3817
7808 | 0 | 6 | 6 | 1.3 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3768
7809 | 0 | 23 | 23 | 2.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3719
7810 | 2 | 155 | 152 | 3.2 | 12.9 | 0 | 0.55371 | 4.4024 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.0352
7811 | 0 | 111 | 110 | 3.4 | 13.3 | 0 | 0 | 1.2517 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.11087
7812 | 2 | 201 | 197 | 5.8 | 13.9 | 0 | 0.61131 | 7.3238 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 5.9658
7813 | 2 | 156 | 154 | 6.7 | 14.1 | 0 | 0.60992 | 4.0969 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 2.7433
7814 | 20 | 231 | 219 | 8 | 14.1 | 0 | 5.9068 | 10.7131 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 9.364
7815 | 1 | 126 | 124 | 6 | 14 | 0 | 0.27138 | 2.3678 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 1.023
7816 | 2 | 88 | 88 | 6 | 14.1 | 0 | 0.45375 | 0.60414 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -0.73649
7817 | 0 | 19 | 19 | 5 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3365
7818 | 0 | 0 | 0 | 4.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3325
7819 | 0 | 0 | 0 | 3.1 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3285
7820 | 0 | 0 | 0 | 3.4 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3246
7821 | 0 | 0 | 0 | 2.6 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3208
7822 | 0 | 0 | 0 | 2.5 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.317
7823 | 0 | 0 | 0 | 4 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3133
7824 | 0 | 0 | 0 | 4.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3097
7825 | 0 | 0 | 0 | 5.7 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3061
7826 | 0 | 0 | 0 | 9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.3027
7827 | 0 | 0 | 0 | 12.4 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.2992
7828 | 0 | 0 | 0 | 14.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.2959
7829 | 0 | 0 | 0 | 13.5 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.2926
7830 | 0 | 0 | 0 | 10.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.2894
7831 | 0 | 0 | 0 | 7.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.2863
7832 | 360 | 66 | 23 | 7.2 | 11.7 | 0 | 49.3062 | 6.6053 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 5.3226
7833 | 713 | 236 | 48 | 9.7 | 13.3 | 132.4623 | 0 | 32.621 | 0 | 0 | 0 | 113.4177 | 0 | 10% | 0 | 0 | 10% | 0 | 31.0262
7834 | 843 | 396 | 61 | 10.9 | 14.6 | 192.1925 | 0 | 53.8387 | 0 | 41.0932 | 0 | 146.0029 | 0 | 22% | 13.8767 | 0 | 28.87% | 0 | 37.2456
7835 | 909 | 514 | 67 | 2.9 | 15.2 | 233.9419 | 0 | 64.4684 | 4.2767 | 42.0041 | 4.7531 | 190.8657 | 0 | 37% | 23.795 | 0 | 61.23% | 0 | 42.456
7836 | 930 | 574 | 73 | 0 | 15.7 | 248.8289 | 0 | 50.3056 | 24.7944 | 42.2394 | 15.238 | 206.7538 | 0 | 53% | 21.1518 | 0 | 90% | 0 | 41.6042
7837 | 755 | 506 | 100 | 0.3 | 16.5 | 198.3185 | 0 | 26.9729 | 36.8193 | 42.3505 | 15.2385 | 157.2886 | 0 | 65% | 0 | 0 | 90% | 0 | 39.887
7838 | 0 | 173 | 171 | 2.3 | 19.5 | 0 | 0 | 5.2585 | 0 | 42.4052 | 15.0895 | 0 | 39.2136 | 62% | 0 | 19.3537 | 59.03% | 0 | 38.7765
7839 | 0 | 110 | 109 | 6.1 | 20.9 | 0 | 0 | 1.2897 | 0 | 42.401 | 14.9987 | 0 | 39.347 | 59% | 0 | 24.6394 | 19.61% | 0 | 38.978
7840 | 278 | 170 | 110 | 7.3 | 21.4 | 0 | 52.0342 | 15.7726 | 0 | 59.0715 | 22.1375 | 0 | 55.8458 | 55% | 0 | 6.007 | 10% | 0 | 41.8271
7841 | 306 | 64 | 33 | 5.5 | 20.9 | 0 | 38.5039 | 4.1713 | 0 | 102.5595 | 40.8254 | 0 | 102.9617 | 47% | 0 | 0 | 10% | 0 | 42.7868
7842 | 0 | 0 | 0 | 2.6 | 19.4 | 0 | 0 | 0 | 0 | 113.4845 | 45.4786 | 0 | 115.7237 | 38% | 0 | 0 | 10% | 0 | 43.2954
7843 | 0 | 0 | 0 | 5.8 | 18.2 | 0 | 0 | 0 | 0 | 112.0651 | 44.9931 | 0 | 113.6164 | 30% | 0 | 0 | 10% | 0 | 42.8996
7844 | 0 | 0 | 0 | 6.3 | 18.2 | 0 | 0 | 0 | 0 | 107.4898 | 43.0973 | 0 | 107.9694 | 21% | 0 | 0 | 10% | 0 | 41.0673
7845 | 0 | 0 | 0 | 2.3 | 16.2 | 0 | 0 | 0 | 0 | 100.3655 | 40.2751 | 0 | 99.4275 | 14% | 0 | 0 | 10% | 0 | 38.2809
7846 | 0 | 0 | 0 | 2.4 | 14.4 | 0 | 0 | 0 | 0 | 92.8473 | 37.2469 | 0 | 90.6305 | 7% | 0 | 0 | 10% | 0 | 35.2567
7847 | 0 | 0 | 0 | 2.1 | 13.1 | 0 | 0 | 0 | 0 | 86.3293 | 34.564 | 0 | 82.9092 | 0% | 0 | 0 | 10% | 0 | 32.5522
7848 | 0 | 0 | 0 | 4.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9555
7849 | 0 | 0 | 0 | 5.7 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9395
7850 | 0 | 0 | 0 | 9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9239
7851 | 0 | 0 | 0 | 12.4 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9085
7852 | 0 | 0 | 0 | 14.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8935
7853 | 0 | 0 | 0 | 13.5 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8788
7854 | 0 | 0 | 0 | 10.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8644
7855 | 0 | 0 | 0 | 7.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8503
7856 | 360 | 66 | 23 | 7.2 | 11.7 | 0 | 48.8997 | 6.5952 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 4.7608
7857 | 713 | 236 | 48 | 9.7 | 13.3 | 131.8512 | 0 | 32.5317 | 0 | 0 | 0 | 124.8181 | 0 | 10% | 0 | 0 | 10% | 0 | 30.9669
7858 | 843 | 396 | 61 | 10.9 | 14.6 | 191.7495 | 0 | 53.7244 | 0 | 42.2527 | 0 | 149.3587 | 0 | 22% | 18.8563 | 0 | 35.64% | 0 | 32.1947
7859 | 909 | 514 | 67 | 2.9 | 15.2 | 233.7485 | 0 | 52.9768 | 15.6529 | 42.4598 | 13.2824 | 192.3457 | 0 | 36% | 25 | 0 | 69.64% | 0 | 38.615
7860 | 930 | 574 | 73 | 0 | 15.7 | 248.6092 | 0 | 40.8283 | 34.2717 | 42.5269 | 15.3417 | 207.341 | 0 | 52% | 14.9672 | 0 | 90% | 0 | 38.4635
7861 | 755 | 506 | 100 | 0.3 | 16.5 | 198.2032 | 0 | 23.9365 | 39.8004 | 42.5495 | 15.3101 | 157.279 | 0 | 64% | 0 | 0 | 90% | 0 | 36.9608
7862 | 0 | 173 | 171 | 2.3 | 19.5 | 0 | 0 | 5.2734 | 0 | 42.5608 | 15.1449 | 0 | 40.0039 | 61% | 0 | 17.1554 | 62.55% | 0 | 36.228
7863 | 0 | 110 | 109 | 6.1 | 20.9 | 0 | 0 | 1.2965 | 0 | 42.5568 | 15.0537 | 0 | 40.0726 | 58% | 0 | 22.7819 | 26.1% | 0 | 36.804
7864 | 278 | 170 | 110 | 7.3 | 21.4 | 0 | 51.8717 | 15.7921 | 0 | 46.6085 | 16.7592 | 0 | 44.1856 | 55% | 0 | 10.0627 | 10% | 0 | 40.2145
7865 | 306 | 64 | 33 | 5.5 | 20.9 | 0 | 37.6997 | 4.1835 | 0 | 101.6258 | 40.4271 | 0 | 102.8714 | 47% | 0 | 0 | 10% | 0 | 42.1131
7866 | 0 | 0 | 0 | 2.6 | 19.4 | 0 | 0 | 0 | 0 | 114.5938 | 45.9323 | 0 | 118.0736 | 38% | 0 | 0 | 10% | 0 | 43.4976
7867 | 0 | 0 | 0 | 5.8 | 18.2 | 0 | 0 | 0 | 0 | 113.186 | 45.4524 | 0 | 115.7653 | 29% | 0 | 0 | 10% | 0 | 43.1514
7868 | 0 | 0 | 0 | 6.3 | 18.2 | 0 | 0 | 0 | 0 | 108.6798 | 43.5843 | 0 | 110.0115 | 21% | 0 | 0 | 10% | 0 | 41.3791
7869 | 0 | 0 | 0 | 2.3 | 16.2 | 0 | 0 | 0 | 0 | 100.3815 | 40.2746 | 0 | 99.943 | 13% | 0 | 0 | 10% | 0 | 38.1312
7870 | 0 | 0 | 0 | 2.4 | 14.4 | 0 | 0 | 0 | 0 | 91.7008 | 36.7503 | 0 | 89.6153 | 7% | 0 | 0 | 10% | 0 | 34.6273
7871 | 0 | 0 | 0 | 2.1 | 13.1 | 0 | 0 | 0 | 0 | 86.2866 | 34.539 | 0 | 83.2136 | 0% | 0 | 0 | 10% | 0 | 32.3977
7872 | 0 | 0 | 0 | 2.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0764
7873 | 0 | 0 | 0 | 4.6 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0582
7874 | 0 | 0 | 0 | 5.7 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0402
7875 | 0 | 0 | 0 | 9 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0226
7876 | 0 | 0 | 0 | 12.4 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0054
7877 | 0 | 0 | 0 | 14.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9886
7878 | 0 | 0 | 0 | 13.5 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9721
7879 | 0 | 0 | 0 | 10.9 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.9559
7880 | 0 | 0 | 0 | 7.3 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.94
7881 | 360 | 66 | 23 | 7.2 | 11.7 | 45.9617 | 12.8784 | 11.7553 | 0 | 0 | 0 | 43.6677 | 0 | 4% | 0 | 0 | 10% | 0 | 10.656
7882 | 713 | 236 | 48 | 9.7 | 13.3 | 158.7197 | 0 | 43.1228 | 0 | 0 | 0 | 153.6638 | 0 | 16% | 0 | 0 | 10% | 0 | 41.3103
7883 | 843 | 396 | 61 | 10.9 | 14.6 | 207.9613 | 0 | 62.5616 | 0 | 42.3767 | 0 | 165.9774 | 0 | 28% | 16.8197 | 0 | 32.88% | 0 | 42.9185
7884 | 909 | 514 | 67 | 2.9 | 15.2 | 240.6191 | 0 | 61.3274 | 11.986 | 42.4979 | 12.4718 | 199.2288 | 0 | 43% | 24.8165 | 0 | 66.62% | 0 | 46.2435
7885 | 930 | 574 | 73 | 0 | 15.7 | 247.7708 | 0 | 50.2338 | 24.8662 | 42.5403 | 15.3466 | 206.4378 | 0 | 59% | 17.1873 | 0 | 90% | 0 | 45.6575
7886 | 0 | 173 | 171 | 2.3 | 19.5 | 0 | 0 | 5.2881 | 0 | 46.0855 | 16.6042 | 0 | 43.3714 | 56% | 0 | 25 | 50% | 0 | 45.5664
7887 | 0 | 110 | 109 | 6.1 | 20.9 | 0 | 0 | 1.3033 | 0 | 60.33 | 22.6079 | 0 | 57.4008 | 51% | 0 | 25 | 10% | 0 | 46.5866
7888 | 278 | 170 | 110 | 7.3 | 21.4 | 0 | 51.7205 | 15.8124 | 0 | 90.2434 | 35.6282 | 0 | 88.9289 | 45% | 0 | 0 | 10% | 0 | 49.0137
7889 | 306 | 64 | 33 | 5.5 | 20.9 | 0 | 36.9569 | 4.1971 | 0 | 119.2276 | 47.7059 | 0 | 123.8206 | 35% | 0 | 0 | 10% | 0 | 49.4286
7890 | 0 | 0 | 0 | 2.6 | 19.4 | 0 | 0 | 0 | 0 | 127.2812 | 51.1673 | 0 | 132.8721 | 25% | 0 | 0 | 10% | 0 | 48.8379
7891 | 0 | 0 | 0 | 5.8 | 18.2 | 0 | 0 | 0 | 0 | 124.9821 | 50.3315 | 0 | 129.2096 | 16% | 0 | 0 | 10% | 0 | 48.1623
7892 | 0 | 0 | 0 | 6.3 | 18.2 | 0 | 0 | 0 | 0 | 115.6061 | 46.4595 | 0 | 117.441 | 7% | 0 | 0 | 10% | 0 | 44.4119
7893 | 0 | 0 | 0 | 2.3 | 16.2 | 0 | 0 | 0 | 0 | 88.039 | 35.3966 | 0 | 87.8297 | 0% | 0 | 0 | 10% | 0 | 33.4382
7894 | 0 | 0 | 0 | 2.4 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8313
7895 | 0 | 0 | 0 | 2.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8179
7896 | 0 | 0 | 0 | 1.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.8047
7897 | 0 | 0 | 0 | 1.6 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7917
7898 | 0 | 0 | 0 | 1.5 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7791
7899 | 0 | 0 | 0 | 1.1 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7666
7900 | 0 | 0 | 0 | 1.5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7544
7901 | 0 | 0 | 0 | 2 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7424
7902 | 0 | 0 | 0 | 1 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7306
7903 | 0 | 1 | 1 | 1.5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -1.7191
7904 | 183 | 53 | 33 | 0.8 | 10.7 | 0 | 28.5111 | 2.6361 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.92843
7905 | 522 | 226 | 94 | 0.9 | 14.4 | 78.0279 | 19.7603 | 27.1029 | 0 | 0 | 0 | 73.7374 | 0 | 6% | 0 | 0 | 10% | 0 | 25.7645
7906 | 584 | 334 | 105 | 1 | 16.9 | 132.1273 | 0 | 40.4299 | 0 | 0 | 0 | 128.9968 | 0 | 16% | 0 | 0 | 10% | 0 | 38.8286
7907 | 884 | 517 | 88 | 3.4 | 19.6 | 225.7164 | 0 | 67.8901 | 0 | 0 | 0 | 222.4014 | 0 | 33% | 18.6847 | 0 | 35.41% | 0 | 46.7374
7908 | 847 | 568 | 118 | 3.8 | 20.6 | 221.8234 | 0 | 73.2449 | 0 | 0 | 0 | 219.9529 | 0 | 50% | 24.3004 | 0 | 68.46% | 0 | 46.4664
7909 | 206 | 361 | 248 | 3.2 | 20.6 | 0 | 49.0824 | 32.3179 | 0 | 42.5124 | 0 | 0 | 39.1553 | 47% | 0 | 14.6269 | 45.06% | 0 | 45.6061
7910 | 276 | 330 | 198 | 2.5 | 20.5 | 57.8169 | 0 | 31.4984 | 0.74795 | 42.5078 | 9.625 | 16.9367 | 0 | 48% | 0 | 5.1799 | 36.77% | 0 | 45.1496
7911 | 350 | 338 | 202 | 2.7 | 20.6 | 70.1296 | 0 | 32.3728 | 1.1455 | 42.5104 | 15.0569 | 29.285 | 0 | 50% | 0 | 0 | 36.77% | 0 | 46.3413
7912 | 41 | 94 | 82 | 2.7 | 18.9 | 0 | 9.2093 | 2.3967 | 0 | 83.212 | 32.5101 | 0 | 82.6341 | 44% | 0 | 14.791 | 13.1% | 0 | 48.4982
7913 | 15 | 19 | 18 | 2.4 | 17.2 | 0 | 1.7782 | 0 | 0 | 127.2345 | 51.3578 | 0 | 131.9882 | 34% | 0 | 0 | 13.1% | 0 | 49.1996
7914 | 0 | 0 | 0 | 2.2 | 15.6 | 0 | 0 | 0 | 0 | 126.9472 | 51.3795 | 0 | 130.8223 | 24% | 0 | 0 | 13.1% | 0 | 49.3703
7915 | 0 | 0 | 0 | 1.3 | 14 | 0 | 0 | 0 | 0 | 122.6435 | 49.7205 | 0 | 125.0704 | 15% | 0 | 0 | 13.1% | 0 | 47.8222
7916 | 0 | 0 | 0 | 1 | 12.7 | 0 | 0 | 0 | 0 | 114.1487 | 46.2807 | 0 | 114.7395 | 6% | 0 | 0 | 13.1% | 0 | 44.4558
7917 | 0 | 0 | 0 | 2.4 | 13.7 | 0 | 0 | 0 | 0 | 74.8592 | 30.2163 | 0 | 74.0165 | 0% | 0 | 0 | 13.1% | 0 | 28.463
7918 | 0 | 0 | 0 | 2.7 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.6555
7919 | 0 | 0 | 0 | 3.2 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.6453
7920 | 0 | 0 | 0 | 1.4 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.6354
7921 | 0 | 0 | 0 | 1.6 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.6257
7922 | 0 | 0 | 0 | 1.2 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.6162
7923 | 0 | 0 | 0 | 1.8 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.6067
7924 | 0 | 0 | 0 | 3.2 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.5975
7925 | 0 | 0 | 0 | 2.7 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.5884
7926 | 0 | 0 | 0 | 3.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.5795
7927 | 0 | 0 | 0 | 4.2 | 16.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | -1.5708
7928 | 306 | 57 | 22 | 3.7 | 17.3 | 0 | 45.9061 | 4.7023 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 13.1% | 0 | 3.1402
7929 | 721 | 243 | 61 | 4.3 | 18.5 | 111.125 | 27.7381 | 33.5999 | 0 | 0 | 0 | 104.8973 | 0 | 8% | 0 | 0 | 13.1% | 0 | 31.9979
7930 | 845 | 390 | 65 | 6.3 | 19.8 | 194.4078 | 0 | 53.0813 | 0 | 0 | 0 | 190.8045 | 0 | 23% | 5.0092 | 0 | 19.92% | 0 | 45.8935
7931 | 900 | 484 | 61 | 5.7 | 20.9 | 227.7131 | 0 | 65.6284 | 0 | 42.4198 | 0 | 186.5099 | 0 | 38% | 20.8379 | 0 | 48.25% | 0 | 41.7405
7932 | 925 | 548 | 64 | 6.3 | 21.6 | 241.5684 | 0 | 62.3695 | 10.2994 | 42.509 | 10.5854 | 200.7312 | 0 | 53% | 24.7879 | 0 | 81.97% | 0 | 45.3148
7933 | 928 | 544 | 58 | 5.8 | 22.1 | 242.5454 | 0 | 38.407 | 33.4359 | 42.5398 | 14.9651 | 201.7007 | 0 | 68% | 5.9067 | 0 | 90% | 0 | 44.7314
7934 | 897 | 478 | 55 | 5.2 | 22.1 | 226.4829 | 0 | 31.95 | 31.7727 | 42.5547 | 14.9703 | 185.5935 | 0 | 82% | 0 | 0 | 90% | 0 | 44.3278
7935 | 836 | 362 | 50 | 7 | 22 | 189.0544 | 0 | 32.3855 | 16.871 | 42.5654 | 14.9815 | 147.9576 | 0 | 94% | 0 | 0 | 90% | 0 | 45.1316
7936 | 692 | 203 | 39 | 7.3 | 21.2 | 123.6686 | 0 | 28.1755 | 0 | 42.5709 | 15.0384 | 82.1636 | 0 | 100% | 0 | 3.6482 | 84.16% | 0 | 47.7438
7937 | 269 | 44 | 16 | 5.4 | 19.3 | 0 | 31.3443 | 2.7688 | 0 | 59.2075 | 22.2385 | 0 | 57.7431 | 95% | 0 | 25 | 44.16% | 0 | 47.9374
7938 | 0 | 0 | 0 | 2.9 | 17.8 | 0 | 0 | 0 | 0 | 77.8541 | 30.3602 | 0 | 78.0041 | 90% | 0 | 21.3518 | 10% | 0 | 48.7745
7939 | 0 | 0 | 0 | 1.8 | 16.3 | 0 | 0 | 0 | 0 | 124.2464 | 50.1973 | 0 | 131.3461 | 80% | 0 | 0 | 10% | 0 | 47.467
7940 | 0 | 0 | 0 | 3.2 | 15 | 0 | 0 | 0 | 0 | 113.69 | 45.9241 | 0 | 115.3828 | 71% | 0 | 0 | 10% | 0 | 43.8829
7941 | 0 | 0 | 0 | 2.6 | 12.7 | 0 | 0 | 0 | 0 | 103.1762 | 41.6892 | 0 | 102.4023 | 63% | 0 | 0 | 10% | 0 | 39.8014
7942 | 0 | 0 | 0 | 1.1 | 11.5 | 0 | 0 | 0 | 0 | 96.226 | 38.8301 | 0 | 94.2545 | 56% | 0 | 0 | 10% | 0 | 36.9406
7943 | 0 | 0 | 0 | 1.5 | 10.2 | 0 | 0 | 0 | 0 | 91.0219 | 36.6907 | 0 | 88.2456 | 49% | 0 | 0 | 10% | 0 | 34.7507
7944 | 0 | 0 | 0 | 1.9 | 10.3 | 0 | 0 | 0 | 0 | 87.3155 | 35.1137 | 0 | 84.0652 | 43% | 0 | 0 | 10% | 0 | 33.1015
7945 | 0 | 0 | 0 | 1.5 | 10.5 | 0 | 0 | 0 | 0 | 86.0934 | 34.5883 | 0 | 82.8766 | 37% | 0 | 0 | 10% | 0 | 32.4957
7946 | 0 | 0 | 0 | 2.6 | 10.5 | 0 | 0 | 0 | 0 | 86.0535 | 34.5718 | 0 | 83.0454 | 31% | 0 | 0 | 10% | 0 | 32.4078
7947 | 0 | 0 | 0 | 1.6 | 9.8 | 0 | 0 | 0 | 0 | 88.5002 | 35.6388 | 0 | 86.131 | 24% | 0 | 0 | 10% | 0 | 33.4127
7948 | 0 | 0 | 0 | 3 | 10.2 | 0 | 0 | 0 | 0 | 97.1281 | 39.2763 | 0 | 96.6238 | 17% | 0 | 0 | 10% | 0 | 36.9985
7949 | 0 | 0 | 0 | 1.7 | 8.6 | 0 | 0 | 0 | 0 | 111.2443 | 45.2765 | 0 | 113.3721 | 8% | 0 | 0 | 10% | 0 | 42.9809
7950 | 0 | 0 | 0 | 2.1 | 8.9 | 0 | 0 | 0 | 0 | 105.5884 | 43.0278 | 0 | 108.3705 | 0% | 0 | 0 | 10% | 0 | 40.8017
7951 | 0 | 0 | 0 | 1.4 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.0145
7952 | 315 | 57 | 21 | 1 | 8.4 | 0 | 45.4633 | 5.0161 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.0186
7953 | 703 | 221 | 48 | 1.3 | 11.9 | 108.4128 | 27.4243 | 31.7645 | 0 | 0 | 0 | 104.2369 | 0 | 8% | 0 | 0 | 10% | 0 | 30.1179
7954 | 845 | 379 | 58 | 1.2 | 16.1 | 197.6539 | 0 | 52.7555 | 0 | 0 | 0 | 195.2396 | 0 | 23% | 4.4252 | 0 | 16.02% | 0 | 46.1544
7955 | 905 | 492 | 62 | 2.2 | 17.6 | 231.5984 | 0 | 66.7266 | 0 | 0 | 0 | 229.9038 | 0 | 40% | 18.3949 | 0 | 41.03% | 0 | 45.8129
7956 | 932 | 552 | 64 | 3.7 | 18.5 | 245.6066 | 0 | 73.2655 | 0.60928 | 0 | 0 | 244.1919 | 0 | 59% | 25 | 0 | 75.03% | 0 | 45.5739
7957 | 932 | 549 | 63 | 2.5 | 19.5 | 246.0423 | 0 | 58.8169 | 14.4796 | 0 | 0 | 244.7954 | 0 | 77% | 11.0034 | 0 | 90% | 0 | 45.0595
7958 | 879 | 485 | 72 | 2.9 | 20.1 | 223.1904 | 0 | 47.3534 | 17.3778 | 0 | 0 | 222.0921 | 0 | 94% | 0 | 0 | 90% | 0 | 44.7854
7959 | 725 | 364 | 93 | 3.2 | 19.9 | 118.1617 | 54.4841 | 47.0888 | 0.25963 | 42.5913 | 0.017407 | 77.4345 | 0 | 100% | 0 | 0 | 90% | 0 | 45.1182
7960 | 553 | 197 | 62 | 3.1 | 19.3 | 42.158 | 70.4194 | 24.0985 | 0 | 42.5908 | 15.1679 | 0 | 0 | 100% | 0 | 7.8626 | 77.42% | 0 | 47.8408
7961 | 210 | 50 | 28 | 2.6 | 17.1 | 0 | 24.0889 | 2.5837 | 0 | 60.8077 | 23.0607 | 0 | 59.3682 | 96% | 0 | 25 | 37.42% | 0 | 48.5798
7962 | 0 | 0 | 0 | 1.6 | 13.5 | 0 | 0 | 0 | 0 | 87.5131 | 34.7292 | 0 | 89.3636 | 89% | 0 | 17.1374 | 10% | 0 | 48.935
7963 | 0 | 0 | 0 | 0.7 | 12.1 | 0 | 0 | 0 | 0 | 123.2269 | 50.0899 | 0 | 129.0051 | 80% | 0 | 0 | 10% | 0 | 47.5737
7964 | 0 | 0 | 0 | 0.3 | 10.3 | 0 | 0 | 0 | 0 | 113.4951 | 46.1392 | 0 | 114.7885 | 71% | 0 | 0 | 10% | 0 | 44.1782
7965 | 0 | 0 | 0 | 0.8 | 9.9 | 0 | 0 | 0 | 0 | 103.4441 | 41.9514 | 0 | 102.5149 | 63% | 0 | 0 | 10% | 0 | 40.1135
7966 | 0 | 0 | 0 | 1.4 | 10.1 | 0 | 0 | 0 | 0 | 96.7019 | 39.0994 | 0 | 94.651 | 56% | 0 | 0 | 10% | 0 | 37.2498
7967 | 0 | 0 | 0 | 1.7 | 9.7 | 0 | 0 | 0 | 0 | 90.9903 | 36.6985 | 0 | 88.0771 | 49% | 0 | 0 | 10% | 0 | 34.7948
7968 | 0 | 0 | 0 | 2 | 9.8 | 0 | 0 | 0 | 0 | 87.9652 | 35.4102 | 0 | 84.727 | 43% | 0 | 0 | 10% | 0 | 33.4279
7969 | 0 | 0 | 0 | 1.6 | 8.7 | 0 | 0 | 0 | 0 | 86.6357 | 34.8917 | 0 | 83.4099 | 36% | 0 | 0 | 10% | 0 | 32.8291
7970 | 0 | 0 | 0 | 1.7 | 8.3 | 0 | 0 | 0 | 0 | 86.1044 | 34.6818 | 0 | 83.0028 | 30% | 0 | 0 | 10% | 0 | 32.5479
7971 | 0 | 0 | 0 | 1.3 | 8 | 0 | 0 | 0 | 0 | 88.8021 | 35.8359 | 0 | 86.3957 | 23% | 0 | 0 | 10% | 0 | 33.6365
7972 | 0 | 0 | 0 | 1.5 | 8.3 | 0 | 0 | 0 | 0 | 96.9307 | 39.2713 | 0 | 96.2887 | 16% | 0 | 0 | 10% | 0 | 37.0197
7973 | 0 | 0 | 0 | 1.8 | 8.3 | 0 | 0 | 0 | 0 | 110.672 | 45.0486 | 0 | 112.5879 | 8% | 0 | 0 | 10% | 0 | 42.7762
7974 | 0 | 0 | 0 | 1.9 | 7.9 | 0 | 0 | 0 | 0 | 98.2849 | 40.0813 | 0 | 100.7278 | 0% | 0 | 0 | 10% | 0 | 37.8854
7975 | 0 | 0 | 0 | 1.5 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | -2.004
7976 | 336 | 55 | 19 | 1.9 | 8.8 | 0 | 46.6121 | 5.3272 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 3.34
7977 | 726 | 218 | 40 | 1.5 | 13.1 | 111.7801 | 28.1962 | 31.748 | 0 | 0 | 0 | 107.5081 | 0 | 8% | 0 | 0 | 10% | 0 | 30.0746
7978 | 857 | 373 | 49 | 0.3 | 17 | 200.5017 | 0 | 52.1936 | 0 | 0 | 0 | 198.1388 | 0 | 23% | 4.3625 | 0 | 15.93% | 0 | 45.6283
7979 | 914 | 487 | 55 | 1.3 | 18.4 | 234.2228 | 0 | 66.2967 | 0 | 0 | 0 | 232.55 | 0 | 41% | 19.0107 | 0 | 41.79% | 0 | 44.7412
7980 | 929 | 542 | 58 | 1.3 | 19.2 | 245.7935 | 0 | 72.2321 | 0.42285 | 0 | 0 | 244.4054 | 0 | 59% | 25 | 0 | 75.79% | 0 | 44.536
7981 | 916 | 535 | 60 | 1.2 | 20 | 241.8315 | 0 | 56.8277 | 14.6207 | 0 | 0 | 240.6042 | 0 | 78% | 10.4504 | 0 | 90% | 0 | 43.6614
7982 | 876 | 469 | 60 | 1.5 | 20.7 | 222.8813 | 0 | 45.7169 | 17.2269 | 0 | 0 | 221.773 | 0 | 95% | 0 | 0 | 90% | 0 | 43.1504
7983 | 801 | 351 | 55 | 2.2 | 20.7 | 113.2026 | 82.2168 | 45.9608 | 1.8283 | 42.5922 | 0 | 72.4916 | 0 | 100% | 0 | 0 | 90% | 0 | 43.9786
7984 | 647 | 196 | 44 | 2.2 | 20.2 | 42.158 | 92.828 | 26.7619 | 0 | 42.5914 | 15.0621 | 0 | 0 | 100% | 0 | 3.824 | 83.88% | 0 | 46.3578
7985 | 237 | 43 | 18 | 1.9 | 17.6 | 0 | 26.807 | 2.3968 | 0 | 56.6539 | 21.2383 | 0 | 55.1501 | 96% | 0 | 25 | 43.88% | 0 | 46.5695
7986 | 0 | 0 | 0 | 0.7 | 14.6 | 0 | 0 | 0 | 0 | 72.6855 | 28.2887 | 0 | 72.5764 | 91% | 0 | 21.176 | 10% | 0 | 46.525
7987 | 0 | 0 | 0 | 1.4 | 13.5 | 0 | 0 | 0 | 0 | 118.5728 | 48.0653 | 0 | 124.4612 | 81% | 0 | 0 | 10% | 0 | 45.3174
7988 | 0 | 0 | 0 | 1.8 | 13.5 | 0 | 0 | 0 | 0 | 110.4042 | 44.6601 | 0 | 111.8342 | 73% | 0 | 0 | 10% | 0 | 42.5423
7989 | 0 | 0 | 0 | 2.1 | 12.9 | 0 | 0 | 0 | 0 | 102.5289 | 41.403 | 0 | 101.9515 | 65% | 0 | 0 | 10% | 0 | 39.4331
7990 | 0 | 0 | 0 | 1.9 | 12.3 | 0 | 0 | 0 | 0 | 96.6941 | 38.9821 | 0 | 95.0459 | 58% | 0 | 0 | 10% | 0 | 37.023
7991 | 0 | 0 | 0 | 2.6 | 13 | 0 | 0 | 0 | 0 | 90.8376 | 36.466 | 0 | 88.2037 | 51% | 0 | 0 | 10% | 0 | 34.4718
7992 | 0 | 0 | 0 | 2.3 | 13.5 | 0 | 0 | 0 | 0 | 86.8535 | 34.7498 | 0 | 83.6767 | 45% | 0 | 0 | 10% | 0 | 32.6888
7993 | 0 | 0 | 0 | 1.1 | 11.9 | 0 | 0 | 0 | 0 | 84.4226 | 33.8153 | 0 | 81.0695 | 39% | 0 | 0 | 10% | 0 | 31.6772
7994 | 0 | 0 | 0 | 0.8 | 11.4 | 0 | 0 | 0 | 0 | 82.7178 | 33.1137 | 0 | 79.3532 | 33% | 0 | 0 | 10% | 0 | 30.9021
7995 | 0 | 0 | 0 | 1.6 | 11.8 | 0 | 0 | 0 | 0 | 83.2056 | 33.3092 | 0 | 80.076 | 27% | 0 | 0 | 10% | 0 | 31.0289
7996 | 0 | 0 | 0 | 2.7 | 13.5 | 0 | 0 | 0 | 0 | 85.6414 | 34.2404 | 0 | 83.0949 | 21% | 0 | 0 | 10% | 0 | 31.901
7997 | 0 | 0 | 0 | 1.6 | 11.8 | 0 | 0 | 0 | 0 | 90.3445 | 36.3259 | 0 | 88.8571 | 14% | 0 | 0 | 10% | 0 | 33.9415
7998 | 0 | 0 | 0 | 1.6 | 11 | 0 | 0 | 0 | 0 | 94.8991 | 38.3021 | 0 | 94.4526 | 7% | 0 | 0 | 10% | 0 | 35.8982
7999 | 0 | 0 | 0 | 1.4 | 10.7 | 0 | 0 | 0 | 0 | 89.9175 | 36.4193 | 0 | 90.7359 | 0% | 0 | 0 | 10% | 0 | 34.0322
8000 | 219 | 43 | 20 | 1.4 | 11.1 | 0 | 29.1751 | 2.4764 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10% | 0 | 0.24238
8001 | 683 | 212 | 45 | 0.9 | 15.2 | 104.1809 | 26.06 | 29.8593 | 0 | 0 | 0 | 100.3947 | 0 | 8% | 0 | 0 | 10% | 0 | 28.2166
8002 | 826 | 364 | 53 | 2.1 | 16.9 | 191.19 | 0 | 50.4953 | 0 | 0 | 0 | 188.921 | 0 | 22% | 8.8826 | 0 | 22.08% | 0 | 39.5116
8003 | 887 | 475 | 57 | 1.8 | 18.4 | 226.2645 | 0 | 64.3333 | 0 | 0 | 0 | 224.6341 | 0 | 39% | 22.5944 | 0 | 52.81% | 0 | 39.2905
8004 | 916 | 534 | 58 | 1.8 | 19.4 | 241.5739 | 0 | 67.325 | 4.1234 | 0 | 0 | 240.1984 | 0 | 57% | 25 | 0 | 86.81% | 0 | 39.696
8005 | 916 | 532 | 58 | 2.5 | 19.7 | 240.9735 | 0 | 43.0192 | 28.1989 | 0 | 0 | 239.7524 | 0 | 75% | 2.3466 | 0 | 90% | 0 | 38.0011
8006 | 887 | 469 | 57 | 3.1 | 20.3 | 224.9703 | 0 | 39.5768 | 23.9059 | 0 | 0 | 223.8639 | 0 | 92% | 0 | 0 | 90% | 0 | 37.0181
8007 | 819 | 353 | 51 | 3.7 | 19.9 | 153.3954 | 39.2182 | 37.8633 | 10.7646 | 42.5942 | 1.1841 | 112.2706 | 0 | 100% | 0 | 0 | 90% | 0 | 37.3756
8008 | 657 | 195 | 42 | 4 | 19.1 | 42.158 | 94.4173 | 24.3802 | 2.7689 | 42.5943 | 15.1816 | 0 | 0 | 100% | 0 | 0 | 90% | 0 | 40.2735
8009 | 229 | 41 | 17 | 3.7 | 16.2 | 0 | 25.5816 | 2.1885 | 0 | 44.3984 | 16.0868 | 0 | 42.8889 | 97% | 0 | 24.5653 | 50.7% | 0 | 40.7877
8010 | 0 | 0 | 0 | 2.3 | 13.7 | 0 | 0 | 0 | 0 | 51.0114 | 18.994 | 0 | 49.3571 | 93% | 0 | 25 | 10.7% | 0 | 41.0691
8011 | 0 | 0 | 0 | 1 | 12 | 0 | 0 | 0 | 0 | 108.3673 | 43.9059 | 0 | 112.9275 | 85% | 0 | 0 | 10.7% | 0 | 40.9594
8012 | 0 | 0 | 0 | 0.9 | 10.7 | 0 | 0 | 0 | 0 | 102.3387 | 41.445 | 0 | 103.1086 | 77% | 0 | 0 | 10.7% | 0 | 39.1272
8013 | 0 | 0 | 0 | 0.9 | 11.2 | 0 | 0 | 0 | 0 | 95.8224 | 38.6756 | 0 | 94.8611 | 70% | 0 | 0 | 10.7% | 0 | 36.4953
8014 | 0 | 0 | 0 | 0.6 | 9.8 | 0 | 0 | 0 | 0 | 89.5229 | 36.0701 | 0 | 87.2525 | 64% | 0 | 0 | 10.7% | 0 | 33.8938
8015 | 0 | 0 | 0 | 1.3 | 9.1 | 0 | 0 | 0 | 0 | 83.7836 | 33.672 | 0 | 80.6514 | 57% | 0 | 0 | 10.7% | 0 | 31.4369
8016 | 0 | 0 | 0 | 1 | 9.8 | 0 | 0 | 0 | 0 | 80.7525 | 32.2838 | 0 | 77.7509 | 52% | 0 | 0 | 10.7% | 0 | 29.9615
8017 | 0 | 0 | 0 | 0.8 | 9.7 | 0 | 0 | 0 | 0 | 79.1242 | 31.5472 | 0 | 76.319 | 46% | 0 | 0 | 10.7% | 0 | 29.1542
8018 | 0 | 0 | 0 | 2.3 | 10 | 0 | 0 | 0 | 0 | 78.3431 | 31.1815 | 0 | 75.6875 | 40% | 0 | 0 | 10.7% | 0 | 28.7328
8019 | 0 | 0 | 0 | 1.4 | 9.4 | 0 | 0 | 0 | 0 | 78.3212 | 31.1967 | 0 | 75.7864 | 35% | 0 | 0 | 10.7% | 0 | 28.7024
8020 | 0 | 0 | 0 | 1.6 | 8.9 | 0 | 0 | 0 | 0 | 79.9406 | 31.9529 | 0 | 77.5163 | 29% | 0 | 0 | 10.7% | 0 | 29.4191
8021 | 0 | 0 | 0 | 1.4 | 9.1 | 0 | 0 | 0 | 0 | 81.8545 | 32.8208 | 0 | 79.5322 | 23% | 0 | 0 | 10.7% | 0 | 30.2532
8022 | 0 | 0 | 0 | 1.9 | 8.8 | 0 | 0 | 0 | 0 | 84.0087 | 33.7805 | 0 | 81.9652 | 17% | 0 | 0 | 10.7% | 0 | 31.1834
8023 | 0 | 0 | 0 | 2 | 8.6 | 0 | 0 | 0 | 0 | 91.0653 | 36.778 | 0 | 90.5534 | 10% | 0 | 0 | 10.7% | 0 | 34.1505
8024 | 252 | 58 | 33 | 1.6 | 10.8 | 0 | 32.2083 | 4.1035 | 0 | 88.052 | 35.4059 | 0 | 86.8089 | 4% | 0 | 0 | 10.7% | 0 | 36.9024
8025 | 248 | 112 | 41 | 0.6 | 10.3 | 0 | 56.0354 | 9.2066 | 0 | 49.2121 | 19.6104 | 0 | 47.7742 | 0% | 0 | 0 | 10.7% | 0 | 26.2568
8026 | 818 | 380 | 73 | 0.9 | 16.1 | 154.0049 | 38.1774 | 52.3419 | 0 | 0 | 0 | 148.6185 | 0 | 11% | 13.1133 | 0 | 28.53% | 0 | 37.1224
8027 | 887 | 477 | 60 | 2.2 | 18 | 225.8422 | 0 | 64.6673 | 0 | 0 | 0 | 224.0133 | 0 | 28% | 24.8133 | 0 | 62.28% | 0 | 37.457
8028 | 915 | 536 | 62 | 3.6 | 18.7 | 240.032 | 0 | 61.5969 | 10.3179 | 0 | 0 | 238.6752 | 0 | 46% | 20.3855 | 0 | 90% | 0 | 38.6409
8029 | 804 | 522 | 104 | 3.1 | 19.3 | 208.8675 | 0 | 31.6604 | 35.6311 | 42.5879 | 7.7937 | 167.3117 | 0 | 58% | 0 | 0 | 90% | 0 | 36.8657
8030 | 784 | 459 | 93 | 3 | 19.4 | 196.9588 | 0 | 22.9737 | 36.9125 | 42.5919 | 15.1622 | 155.3194 | 0 | 69% | 0 | 0 | 90% | 0 | 35.8903
8031 | 521 | 316 | 126 | 3.4 | 19 | 112.4312 | 0 | 23.1113 | 14.6172 | 42.5949 | 15.1879 | 71.0577 | 0 | 75% | 0 | 0 | 90% | 0 | 36.827
8032 | 610 | 195 | 54 | 3.3 | 18.1 | 109.1371 | 0 | 25.7319 | 0.69531 | 42.5941 | 15.2401 | 67.1865 | 0 | 80% | 0 | 0 | 90% | 0 | 39.5356
8033 | 215 | 40 | 18 | 2.8 | 15.9 | 0 | 23.7596 | 1.9776 | 0 | 44.6983 | 16.2269 | 0 | 43.1907 | 76% | 0 | 24.6395 | 50.58% | 0 | 40.7866
8034 | 0 | 0 | 0 | 1.5 | 13.4 | 0 | 0 | 0 | 0 | 53.5544 | 20.1087 | 0 | 51.9835 | 73% | 0 | 25 | 10.58% | 0 | 42.1303
8035 | 0 | 0 | 0 | 1.2 | 11.9 | 0 | 0 | 0 | 0 | 110.58 | 44.8345 | 0 | 115.8304 | 64% | 0 | 0 | 10.58% | 0 | 41.8155
8036 | 0 | 0 | 0 | 0.5 | 11 | 0 | 0 | 0 | 0 | 105.1274 | 42.6104 | 0 | 107.8483 | 56% | 0 | 0 | 10.58% | 0 | 39.936
8037 | 0 | 0 | 0 | 0.7 | 10.1 | 0 | 0 | 0 | 0 | 97.309 | 39.3544 | 0 | 97.7041 | 49% | 0 | 0 | 10.58% | 0 | 36.855
8038 | 0 | 0 | 0 | 1.1 | 10.6 | 0 | 0 | 0 | 0 | 89.6931 | 36.1063 | 0 | 88.2641 | 42% | 0 | 0 | 10.58% | 0 | 33.6727
8039 | 0 | 0 | 0 | 0.9 | 9.9 | 0 | 0 | 0 | 0 | 84.7598 | 34.051 | 0 | 82.3732 | 36% | 0 | 0 | 10.58% | 0 | 31.6143
8040 | 0 | 0 | 0 | 1.5 | 9.7 | 0 | 0 | 0 | 0 | 81.5526 | 32.6547 | 0 | 78.9476 | 30% | 0 | 0 | 10.58% | 0 | 30.1859
8041 | 0 | 0 | 0 | 1.2 | 10.7 | 0 | 0 | 0 | 0 | 81.0463 | 32.3811 | 0 | 78.5413 | 24% | 0 | 0 | 10.58% | 0 | 29.8746
8042 | 0 | 0 | 0 | 0.7 | 10.1 | 0 | 0 | 0 | 0 | 81.0634 | 32.4169 | 0 | 78.6439 | 19% | 0 | 0 | 10.58% | 0 | 29.8778
8043 | 0 | 0 | 0 | 0.7 | 9.4 | 0 | 0 | 0 | 0 | 84.0898 | 33.7909 | 0 | 81.9731 | 12% | 0 | 0 | 10.58% | 0 | 31.2192
8044 | 0 | 0 | 0 | 1.3 | 8.8 | 0 | 0 | 0 | 0 | 94.2203 | 38.1149 | 0 | 94.3816 | 5% | 0 | 0 | 10.58% | 0 | 35.5051
8045 | 0 | 0 | 0 | 1.7 | 8.3 | 0 | 0 | 0 | 0 | 70.4602 | 28.6733 | 0 | 72.4717 | 0% | 0 | 0 | 10.58% | 0 | 26.1339
8046 | 0 | 0 | 0 | 1.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.3981
8047 | 0 | 0 | 0 | 1.9 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.3738
8048 | 0 | 21 | 21 | 1.8 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.35
8049 | 0 | 67 | 66 | 2.1 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.3265
8050 | 5 | 118 | 115 | 3.3 | 10.7 | 0 | 1.3432 | 2.051 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -0.25244
8051 | 50 | 291 | 262 | 4 | 12.5 | 0 | 14.6544 | 20.9042 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | 18.6234
8052 | 5 | 226 | 222 | 4.6 | 13.3 | 0 | 1.5078 | 9.8958 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | 7.6371
8053 | 1 | 160 | 158 | 5.3 | 13.1 | 0 | 0.30139 | 4.4183 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | 2.1813
8054 | 1 | 157 | 155 | 4.6 | 12.9 | 0 | 0.29262 | 4.3563 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | 2.1405
8055 | 0 | 156 | 155 | 4.7 | 13 | 0 | 0 | 4.833 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | 2.638
8056 | 13 | 109 | 104 | 5.3 | 13.1 | 0 | 2.8919 | 2.3822 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | 0.20767
8057 | 0 | 9 | 9 | 3.7 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.1546
8058 | 0 | 0 | 0 | 3.4 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.1349
8059 | 0 | 0 | 0 | 2.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.1158
8060 | 0 | 0 | 0 | 2.9 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.0969
8061 | 0 | 0 | 0 | 3.2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.0783
8062 | 0 | 0 | 0 | 3 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.0601
8063 | 0 | 0 | 0 | 2.6 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.0422
8064 | 0 | 0 | 0 | 2.6 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.0247
8065 | 0 | 0 | 0 | 2.3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -2.0076
8066 | 0 | 0 | 0 | 4.7 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.9907
8067 | 0 | 0 | 0 | 4.7 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.9742
8068 | 0 | 0 | 0 | 5.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.958
8069 | 0 | 0 | 0 | 3.4 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.9421
8070 | 0 | 0 | 0 | 4.8 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.9265
8071 | 0 | 0 | 0 | 3.3 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.9113
8072 | 0 | 4 | 4 | 5.5 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.8962
8073 | 0 | 30 | 30 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.8815
8074 | 0 | 20 | 20 | 7.1 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.867
8075 | 0 | 8 | 7 | 7.5 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.8529
8076 | 0 | 65 | 64 | 8.7 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.839
8077 | 0 | 100 | 99 | 7.7 | 10.5 | 0 | 0 | 0.66091 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.1644
8078 | 1 | 145 | 143 | 8.7 | 10.7 | 0 | 0.29243 | 3.5286 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | 1.7166
8079 | 0 | 50 | 50 | 7.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.7989
8080 | 0 | 31 | 31 | 5.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.786
8081 | 0 | 4 | 4 | 3.3 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.7734
8082 | 0 | 0 | 0 | 3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.7611
8083 | 0 | 0 | 0 | 2.6 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.7489
8084 | 0 | 0 | 0 | 2.9 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.7369
8085 | 0 | 0 | 0 | 2 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.7253
8086 | 0 | 0 | 0 | 2.3 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.7139
8087 | 0 | 0 | 0 | 1.6 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 10.58% | 0 | -1.7027