## 0 - Overview
Title: | intercomparison_of_hybrid_CSP_PV_systems_optimization_variable_load_results
Description | This excel workbook contains that results of running the variable load found in the workbook intercomparison_of_hybrid_CSP_PV_systems_model_input_data_2019 on tab 9. All models created a pareto fronteir by solving at each of the given hybrid capacity factors and reported the resulting design parameters as well as NPV and LCOE. Additionally, for models that have an electric heater capability, an additional pareto fronteir was created with an electric heater as an additional design variable.
Sheet | Description
1.1 MoSES Variable Load Results | This sheet contains the results of running the MoSES model on a variable load both with an electric heater and without an electric heater.
1.2 - YACOP Variable Load Results | This sheet contains the results of running the YACOP model on a variable load both with an electric heater and without an electric heater.
1.3 - AESOPT Variable Load Results | This sheet contains the results of running the AESOPT model on a variable load both with an electric heater and without an electric heater.
1.4 - HOPP Variable Load Results | This sheet contains the results of running the HOPP model on a variable load without an electric heater.
2.1 - Paper Figures | This sheet contains the figures used in the associated paper from the results of this workbook. The paper figure label and figure number corresponds to the paper.

## 1.1-MoSES Variable Load Results
Variable Load with Electric Heater
CF_hyb | CF_hyb_real | NPV | LCOE | PV_AC_nom | BESS_E_nom | BESS_P_nom | ST_Q_nom | PB_P_net_nom | TES_E_nom | EH_Q_nom | Legend
% | % | MEur | Eur/MWh | MW | MWh | MW | MW | MW | MWh | MW | Symbol/Abbreviation | Description | Unit
30% | 31.73% | 34.794 | 27.7892 | 52.5718 | [6 empty] | CF_hyb | Desired hybrid capacity factor | %
35% | 34.99% | 32.0991 | 31.4176 | 65.5386 | [6 empty] | CF_hyb_real | Real hybrid capacity factor | %
40% | 40.19% | 13.267 | 43.0107 | 90.4503 | 17.5189 | 8.8569 |  |  |  |  | NPV | Net present value | Meur
45% | 44.83% | -8.4831 | 53.0828 | 97.2773 | 74.9497 | 11.1637 |  |  |  |  | LCOE | Levelized cost of energy | Eur/MWh
50% | 49.29% | -23.8844 | 58.9442 | 112.9202 | 98.9146 | 18.4482 |  |  |  |  | PV_AC_nom | PV nominal AC power | MW
55% | 54.81% | -38.5377 | 63.2604 | 103.7057 | 336.3538 | 32.8305 |  |  |  |  | BESS_E_nom | BESS nominal energy content | MWh
60% | 60% | -65.1099 | 71.524 | 127.545 | 208.1845 | 42.9429 |  |  |  |  | BESS_P_nom | BESS nominal AC power | MW
65% | 64.3% | -73.1447 | 71.2924 | 128.8123 | 471.4032 | 45.7487 |  |  |  |  | ST_Q_nom | CSP receiver nominal heat output | MW
70% | 71.12% | -94.7533 | 75.2662 | 59.2947 |  |  | 174.6251 | 27.6426 | 1407.8343 |  | PB_P_net_nom | Power cycle net AC power | MW
75% | 75.01% | -111.3443 | 77.2938 | 60.1834 |  |  | 197.7184 | 32.2713 | 1440.9339 |  | TES_E_nom | TES nominal energy content | MWh
80% | 80.32% | -128.6946 | 79.523 | 87.0913 |  |  | 194.956 | 32.0316 | 1550.6339 | 36.7153 | EH_Q_nom | EH nominal heat output | MW
85% | 84.92% | -153.7117 | 83.6205 | 83.4762 |  |  | 248.0946 | 38.9779 | 1642.6803 | 23.8806
90% | 90.65% | -194.8909 | 90.656 | 87.2688 |  |  | 308.6834 | 45.3559 | 2145.6948 | 26.6897
95% | 94.61% | -333.0262 | 116.2649 | 164.8274 | 48.2769 | 39.1146 | 355.4866 | 46.1051 | 2230.7691 | 132.5402
Variable Load without an Electric Heater
CF_hyb | CF_hyb_real | NPV | LCOE | PV_AC_nom | BESS_E_nom | BESS_P_nom | ST_Q_nom | PB_P_net_nom | TES_E_nom | EH_Q_nom
% | % | MEur | Eur/MWh | MW | MWh | MW | MW | MW | MWh | MW
30% | 31.73% | 34.794 | 27.7892 | 52.5718
35% | 34.99% | 32.0991 | 31.4176 | 65.5386
40% | 40.19% | 13.267 | 43.0107 | 90.4503 | 17.5189 | 8.8569
45% | 44.83% | -8.4831 | 53.0828 | 97.2773 | 74.9497 | 11.1637
50% | 49.29% | -23.8844 | 58.9442 | 112.9202 | 98.9146 | 18.4482
55% | 54.81% | -38.5377 | 63.2604 | 103.7057 | 336.3538 | 32.8305
60% | 60% | -65.1099 | 71.524 | 127.545 | 208.1845 | 42.9429
65% | 64.3% | -73.1447 | 71.2924 | 128.8123 | 471.4032 | 45.7487
70% | 71.12% | -94.7533 | 75.2662 | 59.2947 |  |  | 174.6251 | 27.6426 | 1407.8343
75% | 75.01% | -111.3443 | 77.2938 | 60.1834 |  |  | 197.7184 | 32.2713 | 1440.9339
80% | 80.19% | -131.7849 | 80.779 | 67.1623 | 134.6586 | 19.2748 | 206.784 | 31.1115 | 1237.3663
85% | 85.7% | -154.4192 | 84.2539 | 77.8319 | 175.8441 | 18.6521 | 238.0468 | 29.0023 | 1327.6322
90% | 90.08% | -213.9813 | 95.082 | 82.2342 | 268.4486 | 20.5988 | 292.3657 | 33.6786 | 1663.2811
95% | 96.08% | -374.6552 | 123.8989 | 150.2239 | 458.657 | 31.3444 | 354.68 | 47.797 | 2058.3303

## 1.2-YACOP Variable Load Results
Variable Load with Electric Heater
CF_hyb | NPV | LCOE | PV_AC_nom | BESS_E_nom | BESS_P_nom | ST_Q_nom | PB_P_net_nom | TES_E_nom | EH_Q_nom | Legend
% | MEur | Eur/MWh | MW | MWh | MW | MW | MW | MWh | MW | Symbol/Abbreviation | Description | Unit
30.31% | 25.9367 | 32.3449 | 58.576 | [6 empty] | CF_hyb | Desired hybrid capacity factor | %
35.1% | 9.7465 | 43.6944 | 91.6189 | [6 empty] | CF_hyb_real | Real hybrid capacity factor | %
40.18% | -11.4189 | 54.8691 | 87.1131 | 81.5352 | 12.5885 |  |  |  |  | NPV | Net present value | Meur
44.72% | -33.0649 | 63.7924 | 96.1248 | 136.3174 | 20.2855 |  |  |  |  | LCOE | Levelized cost of energy | Eur/MWh
50.1% | -58.6329 | 72.3137 | 102.1326 | 205.9079 | 33.9248 |  |  |  |  | PV_AC_nom | PV nominal AC power | MW
54.39% | -80.9503 | 78.3806 | 111.1443 | 262.5543 | 40.3145 |  |  |  |  | BESS_E_nom | BESS nominal energy content | MWh
59.61% | -101.6159 | 81.4092 | 43.5566 |  |  | 191.4444 | 22.0606 | 1103.9627 |  | BESS_P_nom | BESS nominal AC power | MW
65.75% | -114.6297 | 82.1708 | 60.078 |  |  | 177.4705 | 31.4074 | 1128.4585 |  | ST_Q_nom | CSP receiver nominal heat output | MW
70.11% | -126.2985 | 83.3479 | 54.0702 |  |  | 208.8204 | 33.8349 | 1417.6596 |  | PB_P_net_nom | Power cycle net AC power | MW
75.15% | -138.4348 | 84.1777 | 49.5643 |  |  | 254.0532 | 33.5025 | 1825.2564 |  | TES_E_nom | TES nominal energy content | MWh
80.01% | -158.056 | 86.8025 | 55.5722 |  |  | 289.3379 | 36.8516 | 1933.3469 |  | EH_Q_nom | EH nominal heat output | MW
85.11% | -190.9208 | 92.0221 | 76.5995 |  |  | 303.1948 | 41.1806 | 2388.4217 | 12.8934
90.02% | -259.0296 | 104.1138 | 118.654 |  |  | 357.6261 | 43.8864 | 2524.5437 | 52.7116
95.05% | -451.3931 | 139.8676 | 196.7554 | 191.0675 | 48.6581 | 383.2925 | 48.7855 | 2546.2455 | 56.1326
Variable Load without an Electric Heater
CF_hyb | NPV | LCOE | PV_AC_nom | BESS_E_nom | BESS_P_nom | ST_Q_nom | PB_P_net_nom | TES_E_nom | EH_Q_nom
% | MEur | Eur/MWh | MW | MWh | MW | MW | MW | MWh | MW
30.31% | 25.9367 | 32.3449 | 58.576
35.1% | 9.7465 | 43.6944 | 91.6189
40.18% | -11.4189 | 54.8691 | 87.1131 | 81.5352 | 12.5885
44.72% | -33.0649 | 63.7924 | 96.1248 | 136.3174 | 20.2855
50.1% | -58.6329 | 72.3137 | 102.1326 | 205.9079 | 33.9248
54.39% | -80.9503 | 78.3806 | 111.1443 | 262.5543 | 40.3145
59.61% | -101.6159 | 81.4092 | 43.5566 |  |  | 191.4444 | 22.0606 | 1103.9627
65.75% | -114.6297 | 82.1708 | 60.078 |  |  | 177.4705 | 31.4074 | 1128.4585
70.11% | -126.2985 | 83.3479 | 54.0702 |  |  | 208.8204 | 33.8349 | 1417.6596
75.15% | -138.4348 | 84.1777 | 49.5643 |  |  | 254.0532 | 33.5025 | 1825.2564
80.01% | -158.056 | 86.8025 | 55.5722 |  |  | 289.3379 | 36.8516 | 1933.3469
84.94% | -194.2992 | 92.8872 | 66.0858 |  |  | 334.1487 | 43.042 | 2087.1599
89.97% | -273.2233 | 107.1244 | 81.1053 |  |  | 477.1565 | 42.424 | 2550.2222
95% | -488.0935 | 147.3074 | 192.2496 | 241.0071 | 37.3929 | 452.8806 | 45.7182 | 2546.9691

## 1.3-AESOPT Variable Load Result
Variable Load with Electric Heater
CF_hyb_set | CF_hyb_real | NPV | LCOE | PV_AC_nom | BESS_E_nom | BESS_P_nom | ST_Q_nom | PB_P_net_nom | TES_E_nom | EH_Q_nom | Legend
% | % | MEur | Eur/MWh | MW | MWh | MW | MW | MW | MWh | MW | Symbol/Abbreviation | Description | Unit
30% | 30.7% | 31.6 | 29 | 53.1 | [6 empty] | CF_hyb | Desired hybrid capacity factor | %
35% | 34.4% | 29.6 | 32.5 | 66.7 | [6 empty] | CF_hyb_real | Real hybrid capacity factor | %
40% | 39.4% | 8.9 | 45 | 94.2 | 15.6 | 3.1 |  |  |  |  | NPV | Net present value | Meur
45% | 44.2% | -23.6 | 60.2 | 96.2 | 80.8 | 19.8 |  |  |  |  | LCOE | Levelized cost of energy | Eur/MWh
50% | 49% | -54.1 | 71.4 | 107.2 |  |  |  | 20.3 | 336 | 52.7 | PV_AC_nom | PV nominal AC power | MW
55% | 54% | -62.7 | 72.6 | 125.7 |  |  |  | 20.3 | 450.5 | 69.8 | BESS_E_nom | BESS nominal energy content | MWh
60% | 58.9% | -72.5 | 73.8 | 144.6 |  |  |  | 20.3 | 569.5 | 86.6 | BESS_P_nom | BESS nominal AC power | MW
65% | 64.5% | -79.8 | 73.2 | 64.9 |  |  | 138.9 | 23.1 | 968.1 | 12.2 | ST_Q_nom | CSP receiver nominal heat output | MW
70% | 69.4% | -88.1 | 74 | 74.9 |  |  | 138.9 | 27.3 | 1084.3 | 20.6 | PB_P_net_nom | Power cycle net AC power | MW
75% | 74.3% | -98.8 | 75.1 | 81.6 |  |  | 152.1 | 31.1 | 1207.8 | 25.9 | TES_E_nom | TES nominal energy content | MWh
80% | 79.3% | -115 | 77.4 | 90.7 |  |  | 180.1 | 33.4 | 1259.1 | 34 | EH_Q_nom | EH nominal heat output | MW
85% | 84.4% | -138.6 | 81 | 89.4 | 5.3 | 1.9 | 232.8 | 35.8 | 1463.7 | 31.3
90% | 89.7% | -180.1 | 87.9 | 109.6 | 4.9 | 2.1 | 274 | 39.3 | 1797.7 | 47.8
95% | 95.9% | -297.7 | 108.6 | 214.3 | 19.6 | 7 | 274.7 | 40.4 | 2472.5 | 131.3
Variable Load without an Electric Heater
CF_hyb_set | CF_hyb_real | NPV | LCOE | PV_AC_nom | BESS_E_nom | BESS_P_nom | ST_Q_nom | PB_P_net_nom | TES_E_nom | EH_Q_nom
% | % | MEur | Eur/MWh | MW | MWh | MW | MW | MW | MWh | MW
30% | 30.7% | 31.6 | 29 | 53.1
35% | 34.4% | 29.6 | 32.5 | 66.7
40% | 39.4% | 8.9 | 45 | 94.2 | 15.6 | 3.1
45% | 44.2% | -23.6 | 60.2 | 96.2 | 80.8 | 19.8
50% | 49% | -58.1 | 73.1 | 102.2 | 145.4 | 32.7
55% | 58.7% | -74.9 | 73.9 | 52.9 |  |  | 138.9 | 20.3 | 884.5
60% | 59.4% | -75 | 73.6 | 55.2 |  |  | 138.9 | 20.3 | 879.5
65% | 64.5% | -81.3 | 73.8 | 63.5 |  |  | 141.9 | 24.6 | 993.3
70% | 69.5% | -91 | 74.7 | 63.5 |  |  | 163.9 | 28.7 | 1148.7
75% | 74.8% | -101.9 | 75.7 | 64.1 |  |  | 195.4 | 31.3 | 1303.9
80% | 79.3% | -119.8 | 78.5 | 64.2 | 0.3 | 0.1 | 241.1 | 34.2 | 1371.8
85% | 84.3% | -145.3 | 82.6 | 67.7 | 14.8 | 6.3 | 277.6 | 35.5 | 1551.7
90% | 89.2% | -191.3 | 90.5 | 77.2 | 26.7 | 7.9 | 343.8 | 35.9 | 1933.1
95% | 96.1% | -385.8 | 126.1 | 158 | 67.5 | 12.9 | 528 | 41.4 | 2531.3

## 1.4-HOPP Variable Load Results
Variable Load without an Electric Heater
CF_hyb | NPV | LCOE | PV_AC_nom | BESS_E_nom | BESS_P_nom | ST_Q_nom | PB_P_net_nom | TES_E_nom | EH_Q_nom | Legend
% | MEur | Eur/MWh | MW | MWh | MW | MW | MW | MWh | MW | Symbol/Abbreviation | Description | Unit
31.66% | 33.179 | 28.716 | 54.2053 | [6 empty] | CF_hyb | Desired hybrid capacity factor | %
35.14% | 30.144 | 32.551 | 68.1969 | [6 empty] | CF_hyb_real | Real hybrid capacity factor | %
40.41% | 7.4288 | 45.914 | 92.9389 | 23.1476 | 11.4897 |  |  |  |  | NPV | Net present value | Meur
45.41% | -17.169 | 57.2149 | 99.3713 | 78.3589 | 26.2261 |  |  |  |  | LCOE | Levelized cost of energy | Eur/MWh
50.03% | -40.2808 | 65.7219 | 95.4507 | 155.4738 | 24.569 |  |  |  |  | PV_AC_nom | PV nominal AC power | MW
55.62% | -71.8941 | 75.3156 | 120.3992 | 191.157 | 46.4068 |  |  |  |  | BESS_E_nom | BESS nominal energy content | MWh
59.99% | -86.5453 | 77.0639 | 61.8799 |  |  | 176.7871 | 19.8048 | 952.2168 |  | BESS_P_nom | BESS nominal AC power | MW
65.34% | -106.5795 | 81.0921 | 61.6606 |  |  | 186.3582 | 28.7107 | 1415.2322 |  | ST_Q_nom | CSP receiver nominal heat output | MW
70.57% | -118.5873 | 81.5507 | 65.2696 |  |  | 246.5475 | 27.0098 | 1292.4538 |  | PB_P_net_nom | Power cycle net AC power | MW
74.91% | -130.675 | 83.0812 | 68.3585 |  |  | 253.0408 | 34.936 | 1370.0178 |  | TES_E_nom | TES nominal energy content | MWh
80.41% | -155.562 | 86.5583 | 60.5785 |  |  | 317.0935 | 38.0826 | 1717.0056 |  | EH_Q_nom | EH nominal heat output | MW
85.57% | -190.186 | 92.0056 | 75.8992 |  |  | 362.3084 | 40.7492 | 2092.0154
89.86% | -280.7731 | 95.5822 | 58.3745 |  |  | 536.4575 | 55.216 | 2806.9374
94.91% | -415.6702 | 133.147 | 230.7692 | 363.6223 | 84.5919 | 258.0103 | 25.0263 | 1307.8882

## 2.1-Paper figures
4.2 Case Study 2: Optimize Design | 4.2 Case Study 2: Optimize Design - Inclusion of Electric Heater | Appendix D - Design Values with Electric Heaters and Variable Demand | CF | NPV-MoSES | NPV-YACOP | NPV-AESOPT | NPV-HOPP | NPV-AVERAGE | NPV-STD
|  |  | 30% | 34.794 | 25.9367 | 31.6 | 33.179 | 31.3774 | 3.338
|  |  | 35% | 32.0991 | 9.7465 | 29.6 | 30.144 | 25.3974 | 9.0837
|  |  | 40% | 13.267 | -11.4189 | 8.9 | 7.4288 | 4.5442 | 9.4631
|  |  | 45% | -8.4831 | -33.0649 | -23.6 | -17.169 | -20.5792 | 8.9856
|  |  | 50% | -23.8844 | -58.6329 | -58.1 | -40.2808 | -45.2245 | 14.3649
|  |  | 55% | -38.5377 | -80.9503 | -74.9 | -71.8941 | -66.5705 | 16.5101
|  |  | 60% | -65.1099 | -101.6159 | -75 | -86.5453 | -82.0678 | 13.5987
|  |  | 65% | -73.1447 | -114.6297 | -81.3 | -106.5795 | -93.9135 | 17.1758
|  |  | 70% | -94.7533 | -126.2985 | -91 | -118.5873 | -107.6598 | 15.0909
|  |  | 75% | -111.3443 | -138.4348 | -101.9 | -130.675 | -120.5885 | 14.6197
|  |  | 80% | -131.7849 | -158.056 | -119.8 | -155.562 | -141.3007 | 16.1009
|  |  | 85% | -154.4192 | -194.2992 | -145.3 | -190.186 | -171.0511 | 21.4846
|  |  | 90% | -213.9813 | -273.2233 | -191.3 | -280.7731 | -239.8194 | 38.1273
|  |  | 95% | -374.6552 | -488.0935 | -385.8 | -415.6702 | -416.0547 | 44.2126
Relative Error
|  |  | CF | NPV-MoSES | NPV-YACOP | NPV-AESOPT | NPV-HOPP | NPV-AVERAGE
|  |  | 30% | 10.89% | 17.34% | 0.7094% | 5.742% | 8.67%
|  |  | 35% | 26.39% | 61.62% | 16.55% | 18.69% | 30.81%
|  |  | 40% | 192% | 351.3% | 95.85% | 63.48% | 175.6%
|  |  | 45% | 58.78% | 60.67% | 14.68% | 16.57% | 37.67%
|  |  | 50% | 47.19% | 29.65% | 28.47% | 10.93% | 29.06%
|  |  | 55% | 42.11% | 21.6% | 12.51% | 7.997% | 21.05%
|  |  | 60% | 20.66% | 23.82% | 8.612% | 5.456% | 14.64%
|  |  | 65% | 22.11% | 22.06% | 13.43% | 13.49% | 17.77%
|  |  | 70% | 11.99% | 17.31% | 15.47% | 10.15% | 13.73%
|  |  | 75% | 7.666% | 14.8% | 15.5% | 8.364% | 11.58%
|  |  | 80% | 6.734% | 11.86% | 15.22% | 10.09% | 10.98%
|  |  | 85% | 9.723% | 13.59% | 15.05% | 11.19% | 12.39%
|  |  | 90% | 10.77% | 13.93% | 20.23% | 17.08% | 15.5%
|  |  | 95% | 9.95% | 17.31% | 7.272% | 0.09243% | 8.657%
|  | Figure 37: Optimal PV nominal AC power determined by each model for each HCF. | avg. | 34.07% | 48.35% | 19.97% | 14.24% | 29.15%
Figure 21: Maximum NPV determined by each CSP-PV hybrid modeling tool for HCFs from 30% to 95% (no EHs within the design space). | Figure 29: Change in average NPV when EHs are included in the sub-system design space. | [6 empty] | 14.91%
|  |  | CF | NPV-KTH | NPV-YACOP | NPV-AESOPT | NPV-HOPP | Max Range
|  |  | 30% | 3.4165 | -5.4407 | 0.22258 | 1.8016 | 8.8573
|  |  | 35% | 6.7017 | -15.6509 | 4.2026 | 4.7466 | 22.3526
|  |  | 40% | 8.7228 | -15.9631 | 4.3558 | 2.8845 | 24.6859
|  |  | 45% | 12.0961 | -12.4856 | -3.0208 | 3.4103 | 24.5818
|  |  | 50% | 21.3401 | -13.4084 | -12.8755 | 4.9437 | 34.7485
|  |  | 55% | 28.0328 | -14.3798 | -8.3295 | -5.3235 | 42.4126
|  |  | 60% | 16.9579 | -19.5481 | 7.0678 | -4.4775 | 36.506
|  |  | 65% | 20.7688 | -20.7162 | 12.6135 | -12.6661 | 41.4851
|  |  | 70% | 12.9065 | -18.6387 | 16.6598 | -10.9276 | 35.2985
|  |  | 75% | 9.2443 | -17.8463 | 18.6885 | -10.0865 | 36.5348
|  |  | 80% | 9.5158 | -16.7553 | 21.5007 | -14.2613 | 38.256
|  |  | 85% | 16.6319 | -23.2481 | 25.7511 | -19.1349 | 48.9992
|  |  | 90% | 25.8382 | -33.4039 | 48.5194 | -40.9537 | 89.4731
|  |  | 95% | 41.3995 | -72.0388 | 30.2547 | 0.38456 | 113.4383
WO Electric Heater
|  |  | CF | NPV-MoSES | NPV-YACOP | NPV-AESOPT | NPV-HOPP | NPV-AVERAGE | NPV-STD
|  |  | 30% | 34.794 | 25.9367 | 31.6 | 33.179 | 31.3774 | 3.338
|  |  | 35% | 32.0991 | 9.7465 | 29.6 | 30.144 | 25.3974 | 9.0837
|  |  | 40% | 13.267 | -11.4189 | 8.9 | 7.4288 | 4.5442 | 9.4631
|  |  | 45% | -8.4831 | -33.0649 | -23.6 | -17.169 | -20.5792 | 8.9856
|  |  | 50% | -23.8844 | -58.6329 | -58.1 | -40.2808 | -45.2245 | 14.3649
|  |  | 55% | -38.5377 | -80.9503 | -74.9 | -71.8941 | -66.5705 | 16.5101
|  |  | 60% | -65.1099 | -101.6159 | -75 | -86.5453 | -82.0678 | 13.5987
|  |  | 65% | -73.1447 | -114.6297 | -81.3 | -106.5795 | -93.9135 | 17.1758
|  |  | 70% | -94.7533 | -126.2985 | -91 | -118.5873 | -107.6598 | 15.0909
|  | Figure 38: Optimal BESS nominal energy content determined by each model for each HCF. | 75% | -111.3443 | -138.4348 | -101.9 | -130.675 | -120.5885 | 14.6197
|  |  | 80% | -131.7849 | -158.056 | -119.8 | -155.562 | -141.3007 | 16.1009
|  |  | 85% | -154.4192 | -194.2992 | -145.3 | -190.186 | -171.0511 | 21.4846
Figure 22: Difference between predicted NPV and mean value (mean NPV of the four models). | Figure 30: Optimal EH nominal heat output determined by each model for each HCF. |  | 90% | -213.9813 | -273.2233 | -191.3 | -280.7731 | -239.8194 | 38.1273
|  |  | 95% | -374.6552 | -488.0935 | -385.8 | -415.6702 | -416.0547 | 44.2126
EH
|  |  | CF | NPV-MoSES | NPV-YACOP | NPV-AESOPT | NPV-HOPP | NPV-AVERAGE | NPV-STD | Diff
|  |  | 30% | 34.794 | 25.9367 | 31.6 |  | 30.7769 | 3.6625 | -0.60054
|  |  | 35% | 32.0991 | 9.7465 | 29.6 |  | 23.8152 | 10.0003 | -1.5822
|  |  | 40% | 13.267 | -11.4189 | 8.9 |  | 3.5827 | 10.7565 | -0.96152
|  |  | 45% | -8.4831 | -33.0649 | -23.6 |  | -21.716 | 10.1235 | -1.1368
|  |  | 50% | -23.8844 | -58.6329 | -54.1 |  | -45.5391 | 15.4236 | -0.31457
|  |  | 55% | -38.5377 | -80.9503 | -62.7 |  | -60.7294 | 17.3709 | 5.8412
|  |  | 60% | -65.1099 | -101.6159 | -72.5 |  | -79.7419 | 15.7587 | 2.3258
|  |  | 65% | -73.1447 | -114.6297 | -79.8 |  | -89.1915 | 18.1916 | 4.722
|  |  | 70% | -94.7533 | -126.2985 | -88.1 |  | -103.0506 | 16.6616 | 4.6092
|  |  | 75% | -111.3443 | -138.4348 | -98.8 |  | -116.193 | 16.5401 | 4.3955
|  |  | 80% | -128.6946 | -158.056 | -115 |  | -133.9169 | 17.9612 | 7.3838
|  |  | 85% | -153.7117 | -190.9208 | -138.6 |  | -161.0775 | 21.9857 | 9.9736
|  |  | 90% | -194.8909 | -259.0296 | -180.1 |  | -211.3402 | 34.2579 | 28.4793
|  |  | 95% | -333.0262 | -451.3931 | -297.7 |  | -360.7064 | 65.7269 | 55.3483
Diff
|  |  | CF | NPV-MoSES | NPV-YACOP | NPV-AESOPT | NPV-HOPP | NPV-AVERAGE | NPV-STD
|  |  | 30% | 0 | 0 | 0 |  | 0 | 0
|  |  | 35% | 0 | 0 | 0 |  | 0 | 0
|  |  | 40% | 0 | 0 | 0 |  | 0 | 0
|  |  | 45% | 0 | 0 | 0 |  | 0 | 0
|  |  | 50% | 0 | 0 | 4 |  | 1.3333 | 1.8856
|  | Figure 39: Optimal BESS nominal AC power determined by each model for each HCF. | 55% | 0 | 0 | 12.2 |  | 4.0667 | 5.7511
|  |  | 60% | 0 | 0 | 2.5 |  | 0.83333 | 1.1785
|  |  | 65% | 0 | 0 | 1.5 |  | 0.5 | 0.70711
Figure 23: Optimal PV nominal AC power determined by each model for each HCF. |  |  | 70% | 0 | 0 | 2.9 |  | 0.96667 | 1.3671
|  |  | 75% | 0 | 0 | 3.1 |  | 1.0333 | 1.4614
|  |  | 80% | 3.0902 | 0 | 4.8 |  | 2.6301 | 1.9864
|  |  | 85% | 0.70744 | 3.3784 | 6.7 |  | 3.5953 | 2.4513
|  |  | 90% | 19.0904 | 14.1937 | 11.2 |  | 14.828 | 3.2523
|  |  | 95% | 41.629 | 36.7004 | 88.1 |  | 55.4765 | 23.1559
Figure 40: Optimal CSP receiver nominal heat output determined by each model for each HCF.
Figure 24: Optimal BESS nominal energy content determined by each model for each HCF.
Figure 41: Optimal power cycle net AC power determined by each model for each HCF.
Figure 25: Optimal BESS nominal AC power determined by each model for each HCF.
Figure 42: Optimal TES nominal energy content determined by each model for each HCF.
Figure 26: Optimal CSP receiver nominal heat output determined by each model for each HCF.
Figure 27: Optimal power cycle net AC power determined by each model for each HCF.
Figure 28: Optimal TES nominal energy content determined by each modelfor each HCF.