## All Commercial
Technology/Measure ID | B-TB Year | Sector | End Use Category | Component | Technology/Measure | Fuel Type | Display Name | Regression Output Units | Mapping to Most Granular NREMDB Tech/Measure Name | Mapping to Most Granular EIA/Scout Tech/Measure Name | Regression metric 1 - Coefficient-Low | Regression metric 1 - Coefficient-Mid | Regression metric 1 - Coefficient-High | Regression metric 1 - Metric | Regression metric 1 - Unit | Regression metric 1 - Lower Bound | Regression metric 1 - Typical | Regression metric 1 - High | Regression metric 1 - Upper Bound | Regression metric 2 - Coefficient-Low | Regression metric 2 - Coefficient-Mid | Regression metric 2 - Coefficient-High | Regression metric 2 - Metric | Regression metric 2 - Unit | Regression metric 2 - Lower Bound | Regression metric 2 - Typical | Regression metric 2 - High | Regression metric 2 - Upper Bound | Regression Intercept - Low | Regression Intercept - Mid | Regression Intercept - High | Typical unit multiplier | Typical unit multiplier units name | Typical unit multiplier units abbreviation | Typical Retail Price ($2023) - Low | Typical Retail Price ($2023) - Mid | Typical Retail Price ($2023) - High | New Construction | Retrofit | New Construction | Retrofit | Typical New Construction Installed Cost ($2023) - Low | Typical New Construction Installed Cost ($2023) - Mid | Typical New Construction Installed Cost ($2023) - High | Typical Retrofit Installed Cost ($2023) - Low | Typical Retrofit Installed Cost ($2023) - Mid | Typical Retrofit Installed Cost ($2023) - High | Year | Scenario | Lifetime (Years) | Cost Variation Considerations | Source Diversity | Sample Size | R-squared value | Data Age | Notes
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.25 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 1 |  |  | 10950 | 12087.2971 | 13754.508 | 1.2159 | 1.2688 | 0 | 0 | 13314.1039 | 14696.9433 | 16724.1048 | 13893.1194 | 15336.097 | 17451.4175 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.4 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 1 |  |  | 11042.3077 | 12174.5943 | 13888.188 | 1.2159 | 1.2688 | 0 | 0 | 13426.3408 | 14803.088 | 16886.6464 | 14010.2374 | 15446.8577 | 17621.0278 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.85 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 1 |  |  | 11319.2308 | 12436.4858 | 14289.2281 | 1.2159 | 1.2688 | 0 | 0 | 13763.0515 | 15121.5218 | 17374.271 | 14361.5913 | 15779.14 | 18129.8587 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 15.3 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 1 |  |  | 11596.1539 | 12698.3774 | 14690.2682 | 1.2159 | 1.2688 | 0 | 0 | 14099.7623 | 15439.9557 | 17861.8956 | 14712.9452 | 16111.4222 | 18638.6896 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 15.3 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 1 |  |  | 11596.1539 | 12698.3774 | 14690.2682 | 1.2159 | 1.2688 | 0 | 0 | 14099.7623 | 15439.9557 | 17861.8956 | 14712.9452 | 16111.4222 | 18638.6896 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 15.3 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 1 |  |  | 11596.1539 | 12698.3774 | 14690.2682 | 1.2159 | 1.2688 | 0 | 0 | 14099.7623 | 15439.9557 | 17861.8956 | 14712.9452 | 16111.4222 | 18638.6896 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.175 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 1 |  |  | 10903.8462 | 12043.6485 | 13687.668 | 1.2159 | 1.2688 | 0 | 0 | 13257.9854 | 14643.871 | 16642.834 | 13834.5604 | 15280.7166 | 17366.6123 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 564.406 | 533.7697 | 817.373 | IEER | Unitless | 10.6 | 15.65 | 20.3 | 21.5 | -9397.36 | -9370.5363 | -12788.456 | 1 |  |  | 11862.5171 | 12993.9325 | 15001.8784 | 1.2159 | 1.2688 | 0 | 0 | 14423.6333 | 15799.3211 | 18240.7824 | 15050.901 | 16486.416 | 19034.0536 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 560.6638 | 530.2307 | 811.9536 | IEER | Unitless | 10.6 | 16 | 20.3 | 21.5 | -9335.0527 | -9308.4069 | -12703.6647 | 1 |  |  | 12062.4916 | 13186.2565 | 15286.0394 | 1.2159 | 1.2688 | 0 | 0 | 14666.7823 | 16033.1679 | 18586.2937 | 15304.6243 | 16730.4325 | 19394.5909 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 557.0292 | 526.7933 | 806.6899 | IEER | Unitless | 10.6 | 16.35 | 20.3 | 21.5 | -9274.5358 | -9248.0627 | -12621.3099 | 1 |  |  | 12259.8143 | 13375.9806 | 15566.5164 | 1.2159 | 1.2688 | 0 | 0 | 14906.707 | 16263.8534 | 18927.3257 | 15554.983 | 16971.1503 | 19750.454 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 553.4975 | 523.4533 | 801.5753 | IEER | Unitless | 10.6 | 16.475 | 20.3 | 21.5 | -9215.7333 | -9189.428 | -12541.2881 | 1 |  |  | 12330.061 | 13445.4382 | 15663.1117 | 1.2159 | 1.2688 | 0 | 0 | 14992.1199 | 16348.307 | 19044.7759 | 15644.1105 | 17059.2766 | 19873.0119 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 550.0645 | 520.2066 | 796.6036 | IEER | Unitless | 10.6 | 16.6 | 20.3 | 21.5 | -9158.5733 | -9132.4312 | -12463.5016 | 1 |  |  | 12399.4199 | 13513.9718 | 15758.5646 | 1.2159 | 1.2688 | 0 | 0 | 15076.4533 | 16431.6369 | 19160.837 | 15732.1115 | 17146.2304 | 19994.1205 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.1 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 1 |  |  | 10857.6923 | 12000 | 13620.8279 | 1.2159 | 1.2688 | 0 | 0 | 13201.867 | 14590.7987 | 16561.5633 | 13776.0014 | 15225.3363 | 17281.8072 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 513.4274 | 485.5583 | 743.5458 | IEER | Unitless | 10.6 | 16.9 | 20.3 | 21.5 | -8548.5662 | -8524.1653 | -11633.3697 | 1 |  |  | 12555.2799 | 13692.742 | 15931.0006 | 1.2159 | 1.2688 | 0 | 0 | 15265.9636 | 16649.0036 | 19370.502 | 15929.8633 | 17373.0502 | 20212.9035 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 505.943 | 478.4802 | 732.7069 | IEER | Unitless | 10.6 | 17.15 | 20.3 | 21.5 | -8423.9515 | -8399.9063 | -11463.787 | 1 |  |  | 12679.8946 | 13817.001 | 16100.5833 | 1.2159 | 1.2688 | 0 | 0 | 15417.4825 | 16800.09 | 19576.6975 | 16087.9716 | 17530.7072 | 20428.0663 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 498.6737 | 471.6054 | 722.1795 | IEER | Unitless | 10.6 | 17.4 | 20.3 | 21.5 | -8302.9178 | -8279.218 | -11299.0774 | 1 |  |  | 12800.9284 | 13937.6893 | 16265.2929 | 1.2159 | 1.2688 | 0 | 0 | 15564.6475 | 16946.8349 | 19776.9679 | 16241.5367 | 17683.8339 | 20637.0462 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 491.6104 | 464.9255 | 711.9503 | IEER | Unitless | 10.6 | 17.65 | 20.3 | 21.5 | -8185.3127 | -8161.9487 | -11139.0338 | 1 |  |  | 12918.5335 | 14054.9587 | 16425.3365 | 1.2159 | 1.2688 | 0 | 0 | 15707.6435 | 17089.4228 | 19971.5649 | 16390.7514 | 17832.6227 | 20840.106 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
1 | 2023 | Commercial | HVAC | RTU Heat Pump | Standard | Electricity | RTU Heat Pump Standard | 2023$ |  | Rooftop Heat Pumps | 1656.9231 | 1868.1297 | 1999.7929 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 484.7443 | 458.4321 | 702.0069 | IEER | Unitless | 10.6 | 17.9 | 20.3 | 21.5 | -8070.9927 | -8047.955 | -10983.4607 | 1 |  |  | 13032.8535 | 14168.9524 | 16580.9096 | 1.2159 | 1.2688 | 0 | 0 | 15846.6452 | 17228.0277 | 20160.7262 | 16535.7981 | 17977.2554 | 21037.4937 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 14.1 | 20.3 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 1 |  |  | 16239.0603 | 18623.5833 | 21180.3188 | 1.1167 | 1.1795 | 0 | 0 | 18133.6031 | 20796.3182 | 23651.3373 | 19154.3597 | 21966.9615 | 24982.6921 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 14.4 | 20.3 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 1 |  |  | 16239.0603 | 18623.5833 | 21180.3188 | 1.1167 | 1.1795 | 0 | 0 | 18133.6031 | 20796.3182 | 23651.3373 | 19154.3597 | 21966.9615 | 24982.6921 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 14.85 | 20.3 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 1 |  |  | 16239.0603 | 18623.5833 | 21180.3188 | 1.1167 | 1.1795 | 0 | 0 | 18133.6031 | 20796.3182 | 23651.3373 | 19154.3597 | 21966.9615 | 24982.6921 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 15.3 | 20.3 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 1 |  |  | 16239.0603 | 18623.5833 | 21180.3188 | 1.1167 | 1.1795 | 0 | 0 | 18133.6031 | 20796.3182 | 23651.3373 | 19154.3597 | 21966.9615 | 24982.6921 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 15.3 | 20.3 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 1 |  |  | 16239.0603 | 18623.5833 | 21180.3188 | 1.1167 | 1.1795 | 0 | 0 | 18133.6031 | 20796.3182 | 23651.3373 | 19154.3597 | 21966.9615 | 24982.6921 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 15.3 | 20.3 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 1 |  |  | 16239.0603 | 18623.5833 | 21180.3188 | 1.1167 | 1.1795 | 0 | 0 | 18133.6031 | 20796.3182 | 23651.3373 | 19154.3597 | 21966.9615 | 24982.6921 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 14.1 | 20.3 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 1 |  |  | 16239.0603 | 18623.5833 | 21180.3188 | 1.1167 | 1.1795 | 0 | 0 | 18133.6031 | 20796.3182 | 23651.3373 | 19154.3597 | 21966.9615 | 24982.6921 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 15.65 | 20.3 | 0 | -2209.4636 | -1699.4717 | -1966.5415 | 1 |  |  | 16438.6248 | 18777.0839 | 21357.9419 | 1.1167 | 1.1795 | 0 | 0 | 18356.4499 | 20967.7272 | 23849.6829 | 19389.7508 | 22148.0192 | 25192.2028 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 16 | 20.3 | 0 | -2194.8142 | -1688.2037 | -1953.5027 | 1 |  |  | 16453.2742 | 18788.3519 | 21370.9806 | 1.1167 | 1.1795 | 0 | 0 | 18372.8084 | 20980.3098 | 23864.2428 | 19407.0301 | 22161.3101 | 25207.5823 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 16.35 | 20.3 | 0 | -2180.5858 | -1677.2594 | -1940.8386 | 1 |  |  | 16467.5027 | 18799.2962 | 21383.6447 | 1.1167 | 1.1795 | 0 | 0 | 18388.6968 | 20992.5308 | 23878.3844 | 19423.8129 | 22174.219 | 25222.5199 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 16.475 | 20.3 | 0 | -2166.7604 | -1666.6253 | -1928.5333 | 1 |  |  | 16481.328 | 18809.9303 | 21395.95 | 1.1167 | 1.1795 | 0 | 0 | 18404.1351 | 21004.4056 | 23892.1253 | 19440.1203 | 22186.7623 | 25237.0343 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 16.6 | 20.3 | 0 | -2153.3212 | -1656.2881 | -1916.5717 | 1 |  |  | 16494.7672 | 18820.2675 | 21407.9116 | 1.1167 | 1.1795 | 0 | 0 | 18419.1422 | 21015.9487 | 23905.4825 | 19455.9721 | 22198.9552 | 25251.1433 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 14.1 | 20.3 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 1 |  |  | 16239.0603 | 18623.5833 | 21180.3188 | 1.1167 | 1.1795 | 0 | 0 | 18133.6031 | 20796.3182 | 23651.3373 | 19154.3597 | 21966.9615 | 24982.6921 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 16.9 | 20.3 | 0 | -2009.8992 | -1545.971 | -1788.9184 | 1 |  |  | 16638.1893 | 18930.5846 | 21535.565 | 1.1167 | 1.1795 | 0 | 0 | 18579.2967 | 21139.1361 | 24048.0285 | 19625.1418 | 22329.0769 | 25401.7135 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 17.15 | 20.3 | 0 | -1980.6003 | -1523.435 | -1762.8409 | 1 |  |  | 16667.4881 | 18953.1206 | 21561.6425 | 1.1167 | 1.1795 | 0 | 0 | 18612.0137 | 21164.3013 | 24077.1484 | 19659.7005 | 22355.6587 | 25432.4725 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 17.4 | 20.3 | 0 | -1952.1434 | -1501.5465 | -1737.5127 | 1 |  |  | 16695.945 | 18975.009 | 21586.9707 | 1.1167 | 1.1795 | 0 | 0 | 18643.7905 | 21188.7434 | 24105.4315 | 19693.2661 | 22381.4766 | 25462.3477 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 17.65 | 20.3 | 0 | -1924.4927 | -1480.2782 | -1712.902 | 1 |  |  | 16723.5957 | 18996.2774 | 21611.5813 | 1.1167 | 1.1795 | 0 | 0 | 18674.6672 | 21212.493 | 24132.9134 | 19725.8808 | 22406.5631 | 25491.3766 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
2 | 2023 | Commercial | HVAC | RTU Heat Pump | Cold Climate | Electricity | RTU Heat Pump Cold Climate | 2023$ |  |  | 2486.4118 | 2730.2074 | 3109.9311 | Cooling Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 17.9 | 20.3 | 0 | -1897.6143 | -1459.6039 | -1688.9788 | 1 |  |  | 16750.4741 | 19016.9517 | 21635.5045 | 1.1167 | 1.1795 | 0 | 0 | 18704.6813 | 21235.5793 | 24159.6276 | 19757.5845 | 22430.9489 | 25519.5946 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is not included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.7 | 4.3 | 4.3 | 2000 | 2250 | 2500 | 70 | Tons | ton | 140000 | 157500 | 175000 | 1.2158 | 1.2294 | 0 | 0 | 170212 | 191488.5 | 212765 | 172112.2667 | 193626.3 | 215140.3333 | 2023 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.9027 | 4.3 | 4.3 | 2150.9434 | 2419.8113 | 2688.6792 | 70 | Tons | ton | 150566.0377 | 169386.7925 | 188207.5472 | 1.2158 | 1.2294 | 0 | 0 | 183058.1887 | 205940.4623 | 228822.7358 | 185101.8717 | 208239.6057 | 231377.3396 | 2030 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.9577 | 4.3 | 4.3 | 2188.6792 | 2462.2642 | 2735.8491 | 70 | Tons | ton | 153207.5472 | 172358.4906 | 191509.434 | 1.2158 | 1.2294 | 0 | 0 | 186269.7358 | 209553.4528 | 232837.1698 | 188349.273 | 211892.9321 | 235436.5912 | 2035 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0127 | 4.3 | 4.3 | 2226.4151 | 2504.717 | 2783.0189 | 70 | Tons | ton | 155849.0566 | 175330.1887 | 194811.3208 | 1.2158 | 1.2294 | 0 | 0 | 189481.283 | 213166.4434 | 236851.6038 | 191596.6742 | 215546.2585 | 239495.8428 | 2040 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0708 | 4.3 | 4.3 | 2289.3082 | 2575.4717 | 2861.6352 | 70 | Tons | ton | 160251.5723 | 180283.0189 | 200314.4654 | 1.2158 | 1.2294 | 0 | 0 | 194833.8616 | 219188.0943 | 243542.327 | 197009.0096 | 221635.1358 | 246261.2621 | 2045 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.129 | 4.3 | 4.3 | 2352.2013 | 2646.2264 | 2940.2516 | 70 | Tons | ton | 164654.0881 | 185235.8491 | 205817.6101 | 1.2158 | 1.2294 | 0 | 0 | 200186.4403 | 225209.7453 | 250233.0503 | 202421.3451 | 227724.0132 | 253026.6813 | 2050 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.7 | 4.3 | 4.3 | 2000 | 2250 | 2500 | 70 | Tons | ton | 140000 | 157500 | 175000 | 1.2158 | 1.2294 | 0 | 0 | 170212 | 191488.5 | 212765 | 172112.2667 | 193626.3 | 215140.3333 | 2023 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.9631 | 4.3 | 4.3 | 2201.2579 | 2476.4151 | 2751.5723 | 70 | Tons | ton | 154088.0503 | 173349.0566 | 192610.0629 | 1.2158 | 1.2294 | 0 | 0 | 187340.2516 | 210757.783 | 234175.3145 | 189431.74 | 213110.7075 | 236789.6751 | 2030 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0189 | 4.3 | 4.3 | 2220.1258 | 2497.6415 | 2775.1572 | 70 | Tons | ton | 155408.805 | 174834.9057 | 194261.0063 | 1.2158 | 1.2294 | 0 | 0 | 188946.0252 | 212564.2783 | 236182.5314 | 191055.4407 | 214937.3708 | 238819.3008 | 2035 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0747 | 4.3 | 4.3 | 2238.9937 | 2518.8679 | 2798.7421 | 70 | Tons | ton | 156729.5597 | 176320.7547 | 195911.9497 | 1.2158 | 1.2294 | 0 | 0 | 190551.7987 | 214370.7736 | 238189.7484 | 192679.1413 | 216764.034 | 240848.9266 | 2040 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.1338 | 4.3 | 4.3 | 2295.5975 | 2582.5472 | 2869.4969 | 70 | Tons | ton | 160691.8239 | 180778.3019 | 200864.7799 | 1.2158 | 1.2294 | 0 | 0 | 195369.1195 | 219790.2594 | 244211.3994 | 197550.2432 | 222244.0236 | 246937.804 | 2045 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.1928 | 4.3 | 4.3 | 2352.2013 | 2646.2264 | 2940.2516 | 70 | Tons | ton | 164654.0881 | 185235.8491 | 205817.6101 | 1.2158 | 1.2294 | 0 | 0 | 200186.4403 | 225209.7453 | 250233.0503 | 202421.3451 | 227724.0132 | 253026.6813 | 2050 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.7 | 4.3 | 4.3 | 2000 | 2250 | 2500 | 70 | Tons | ton | 140000 | 157500 | 175000 | 1.2158 | 1.2294 | 0 | 0 | 170212 | 191488.5 | 212765 | 172112.2667 | 193626.3 | 215140.3333 | 2023 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0234 | 4.3 | 4.3 | 2251.5723 | 2533.0189 | 2814.4654 | 70 | Tons | ton | 157610.0629 | 177311.3208 | 197012.5786 | 1.2158 | 1.2294 | 0 | 0 | 191622.3145 | 215575.1038 | 239527.8931 | 193761.6084 | 217981.8094 | 242202.0105 | 2030 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0801 | 4.3 | 4.3 | 2251.5723 | 2533.0189 | 2814.4654 | 70 | Tons | ton | 157610.0629 | 177311.3208 | 197012.5786 | 1.2158 | 1.2294 | 0 | 0 | 191622.3145 | 215575.1038 | 239527.8931 | 193761.6084 | 217981.8094 | 242202.0105 | 2035 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.1368 | 4.3 | 4.3 | 2251.5723 | 2533.0189 | 2814.4654 | 70 | Tons | ton | 157610.0629 | 177311.3208 | 197012.5786 | 1.2158 | 1.2294 | 0 | 0 | 191622.3145 | 215575.1038 | 239527.8931 | 193761.6084 | 217981.8094 | 242202.0105 | 2040 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.1967 | 4.3 | 4.3 | 2301.8868 | 2589.6226 | 2877.3585 | 70 | Tons | ton | 161132.0755 | 181273.5849 | 201415.0943 | 1.2158 | 1.2294 | 0 | 0 | 195904.3774 | 220392.4245 | 244880.4717 | 198091.4767 | 222852.9113 | 247614.3459 | 2045 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
3 | 2023 | Commercial | HVAC | Hydronic Heat Pump |  | Electricity | Hydronic Heat Pump | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.2567 | 4.3 | 4.3 | 2352.2013 | 2646.2264 | 2940.2516 | 70 | Tons | ton | 164654.0881 | 185235.8491 | 205817.6101 | 1.2158 | 1.2294 | 0 | 0 | 200186.4403 | 225209.7453 | 250233.0503 | 202421.3451 | 227724.0132 | 253026.6813 | 2050 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | 0 | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections.
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 143 | Tons | ton | 225225 | 250250 | 275275 | 1.1075 | 1.1256 | 0 | 0 | 249427.0791 | 277141.199 | 304855.3189 | 253513.9162 | 281682.1291 | 309850.342 | 2023 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 143 | Tons | ton | 225225 | 250250 | 275275 | 1.1075 | 1.1256 | 0 | 0 | 249427.0791 | 277141.199 | 304855.3189 | 253513.9162 | 281682.1291 | 309850.342 | 2030 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 143 | Tons | ton | 225225 | 250250 | 275275 | 1.1075 | 1.1256 | 0 | 0 | 249427.0791 | 277141.199 | 304855.3189 | 253513.9162 | 281682.1291 | 309850.342 | 2035 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 143 | Tons | ton | 225225 | 250250 | 275275 | 1.1075 | 1.1256 | 0 | 0 | 249427.0791 | 277141.199 | 304855.3189 | 253513.9162 | 281682.1291 | 309850.342 | 2040 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 143 | Tons | ton | 225225 | 250250 | 275275 | 1.1075 | 1.1256 | 0 | 0 | 249427.0791 | 277141.199 | 304855.3189 | 253513.9162 | 281682.1291 | 309850.342 | 2045 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 143 | Tons | ton | 225225 | 250250 | 275275 | 1.1075 | 1.1256 | 0 | 0 | 249427.0791 | 277141.199 | 304855.3189 | 253513.9162 | 281682.1291 | 309850.342 | 2050 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 143 | Tons | ton | 225225 | 250250 | 275275 | 1.1075 | 1.1256 | 0 | 0 | 249427.0791 | 277141.199 | 304855.3189 | 253513.9162 | 281682.1291 | 309850.342 | 2023 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.69195 | 1.17 | 1.17 | 1796.1407 | 1995.7118 | 2195.283 | 143 | Tons | ton | 256848.1132 | 285386.7925 | 313925.4717 | 1.1075 | 1.1256 | 0 | 0 | 284448.3279 | 316053.6976 | 347659.0674 | 289108.9846 | 321232.2051 | 353355.4256 | 2030 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.68234 | 0.68234 | 1.17 | 1.17 | 1846.3122 | 2051.458 | 2256.6038 | 143 | Tons | ton | 264022.6415 | 293358.4906 | 322694.3396 | 1.1075 | 1.1256 | 0 | 0 | 292393.8119 | 324882.0132 | 357370.2145 | 297184.6545 | 330205.1717 | 363225.6888 | 2035 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.67273 | 0.67273 | 1.17 | 1.17 | 1896.4837 | 2107.2041 | 2317.9245 | 143 | Tons | ton | 271197.1698 | 301330.1887 | 331463.2075 | 1.1075 | 1.1256 | 0 | 0 | 300339.2959 | 333710.3288 | 367081.3617 | 305260.3245 | 339178.1383 | 373095.9521 | 2040 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.66312 | 0.66312 | 1.17 | 1.17 | 1966.4666 | 2184.9628 | 2403.4591 | 143 | Tons | ton | 281204.717 | 312449.6855 | 343694.6541 | 1.1075 | 1.1256 | 0 | 0 | 311422.2275 | 346024.6972 | 380627.1669 | 316524.8487 | 351694.2764 | 386863.704 | 2045 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.65351 | 0.65351 | 1.17 | 1.17 | 2036.4494 | 2262.7216 | 2488.9937 | 143 | Tons | ton | 291212.2642 | 323569.1824 | 355926.1006 | 1.1075 | 1.1256 | 0 | 0 | 322505.159 | 358339.0656 | 394172.9721 | 327789.373 | 364210.4144 | 400631.4559 | 2050 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 143 | Tons | ton | 225225 | 250250 | 275275 | 1.1075 | 1.1256 | 0 | 0 | 249427.0791 | 277141.199 | 304855.3189 | 253513.9162 | 281682.1291 | 309850.342 | 2023 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.68234 | 0.68234 | 1.17 | 1.17 | 1816.5952 | 2018.4391 | 2220.283 | 143 | Tons | ton | 259773.1132 | 288636.7925 | 317500.4717 | 1.1075 | 1.1256 | 0 | 0 | 287687.6406 | 319652.934 | 351618.2274 | 292401.3731 | 324890.4145 | 357379.456 | 2030 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.67273 | 0.67273 | 1.17 | 1.17 | 1866.7667 | 2074.1852 | 2281.6038 | 143 | Tons | ton | 266947.6415 | 296608.4906 | 326269.3396 | 1.1075 | 1.1256 | 0 | 0 | 295633.1246 | 328481.2496 | 361329.3745 | 300477.043 | 333863.3811 | 367249.7193 | 2035 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.66312 | 0.66312 | 1.17 | 1.17 | 1916.9383 | 2129.9314 | 2342.9245 | 143 | Tons | ton | 274122.1698 | 304580.1887 | 335038.2075 | 1.1075 | 1.1256 | 0 | 0 | 303578.6086 | 337309.5652 | 371040.5217 | 308552.713 | 342836.3478 | 377119.9825 | 2040 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.65351 | 0.65351 | 1.17 | 1.17 | 1986.9211 | 2207.6901 | 2428.4591 | 143 | Tons | ton | 284129.717 | 315699.6855 | 347269.6541 | 1.1075 | 1.1256 | 0 | 0 | 314661.5402 | 349623.9335 | 384586.3269 | 319817.2372 | 355352.4858 | 390887.7344 | 2045 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
4 | 2023 | Commercial | HVAC | Heat Recovery Chiller |  | Electricity | Heat Recovery Chiller | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.6439 | 0.6439 | 1.17 | 1.17 | 2056.9039 | 2285.4488 | 2513.9937 | 143 | Tons | ton | 294137.2642 | 326819.1824 | 359501.1006 | 1.1075 | 1.1256 | 0 | 0 | 325744.4717 | 361938.3019 | 398132.1321 | 331081.7615 | 367868.6239 | 404655.4863 | 2050 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | 0 | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years)
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 11000 | cubic feet per minute | CFM | 49500 | 55000 | 60500 | 1.03 | 1.2159 | 0 | 0 | 50985 | 56650 | 62315 | 60187.0448 | 66874.4943 | 73561.9437 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 11000 | cubic feet per minute | CFM | 49500 | 55000 | 60500 | 1.03 | 1.2159 | 0 | 0 | 50985 | 56650 | 62315 | 60187.0448 | 66874.4943 | 73561.9437 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 11000 | cubic feet per minute | CFM | 49500 | 55000 | 60500 | 1.03 | 1.2159 | 0 | 0 | 50985 | 56650 | 62315 | 60187.0448 | 66874.4943 | 73561.9437 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 11000 | cubic feet per minute | CFM | 49500 | 55000 | 60500 | 1.03 | 1.2159 | 0 | 0 | 50985 | 56650 | 62315 | 60187.0448 | 66874.4943 | 73561.9437 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 11000 | cubic feet per minute | CFM | 49500 | 55000 | 60500 | 1.03 | 1.2159 | 0 | 0 | 50985 | 56650 | 62315 | 60187.0448 | 66874.4943 | 73561.9437 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 11000 | cubic feet per minute | CFM | 49500 | 55000 | 60500 | 1.03 | 1.2159 | 0 | 0 | 50985 | 56650 | 62315 | 60187.0448 | 66874.4943 | 73561.9437 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 11000 | cubic feet per minute | CFM | 49500 | 55000 | 60500 | 1.03 | 1.2159 | 0 | 0 | 50985 | 56650 | 62315 | 60187.0448 | 66874.4943 | 73561.9437 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.79787 | 0.83 | 0.83 | 4.4736 | 4.9707 | 5.4678 | 11000 | cubic feet per minute | CFM | 49210.1263 | 54677.9181 | 60145.7099 | 1.03 | 1.2159 | 0 | 0 | 50686.4301 | 56318.2556 | 61950.0812 | 59834.5874 | 66482.8749 | 73131.1624 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.79787 | 0.83 | 0.83 | 4.4736 | 4.9707 | 5.4678 | 11000 | cubic feet per minute | CFM | 49210.1263 | 54677.9181 | 60145.7099 | 1.03 | 1.2159 | 0 | 0 | 50686.4301 | 56318.2556 | 61950.0812 | 59834.5874 | 66482.8749 | 73131.1624 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.79787 | 0.83 | 0.83 | 4.4736 | 4.9707 | 5.4678 | 11000 | cubic feet per minute | CFM | 49210.1263 | 54677.9181 | 60145.7099 | 1.03 | 1.2159 | 0 | 0 | 50686.4301 | 56318.2556 | 61950.0812 | 59834.5874 | 66482.8749 | 73131.1624 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.79948 | 0.83 | 0.83 | 4.4644 | 4.9605 | 5.4565 | 11000 | cubic feet per minute | CFM | 49108.6918 | 54565.2132 | 60021.7345 | 1.03 | 1.2159 | 0 | 0 | 50581.9526 | 56202.1696 | 61822.3865 | 59711.2533 | 66345.837 | 72980.4207 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.80109 | 0.83 | 0.83 | 4.4552 | 4.9502 | 5.4453 | 11000 | cubic feet per minute | CFM | 49007.2574 | 54452.5082 | 59897.7591 | 1.03 | 1.2159 | 0 | 0 | 50477.4751 | 56086.0835 | 61694.6918 | 59587.9192 | 66208.7991 | 72829.679 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 11000 | cubic feet per minute | CFM | 49500 | 55000 | 60500 | 1.03 | 1.2159 | 0 | 0 | 50985 | 56650 | 62315 | 60187.0448 | 66874.4943 | 73561.9437 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81074 | 0.83 | 0.83 | 4.3999 | 4.8888 | 5.3776 | 11000 | cubic feet per minute | CFM | 48398.6509 | 53776.2787 | 59153.9066 | 1.03 | 1.2159 | 0 | 0 | 49850.6104 | 55389.5671 | 60928.5238 | 58847.9145 | 65386.5717 | 71925.2289 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81074 | 0.83 | 0.83 | 4.3999 | 4.8888 | 5.3776 | 11000 | cubic feet per minute | CFM | 48398.6509 | 53776.2787 | 59153.9066 | 1.03 | 1.2159 | 0 | 0 | 49850.6104 | 55389.5671 | 60928.5238 | 58847.9145 | 65386.5717 | 71925.2289 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81074 | 0.83 | 0.83 | 4.3999 | 4.8888 | 5.3776 | 11000 | cubic feet per minute | CFM | 48398.6509 | 53776.2787 | 59153.9066 | 1.03 | 1.2159 | 0 | 0 | 49850.6104 | 55389.5671 | 60928.5238 | 58847.9145 | 65386.5717 | 71925.2289 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81395 | 0.83 | 0.83 | 4.3814 | 4.8683 | 5.3551 | 11000 | cubic feet per minute | CFM | 48195.782 | 53550.8689 | 58905.9558 | 1.03 | 1.2159 | 0 | 0 | 49641.6555 | 55157.395 | 60673.1345 | 58601.2463 | 65112.4959 | 71623.7455 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
5 | 2023 | Commercial | HVAC | Energy Recovery | Wheel | Electricity | Energy Recovery Wheel | 2023$/CFM |  |  | 0 | 0 | 0 | Airflow | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81717 | 0.83 | 0.83 | 4.363 | 4.8478 | 5.3325 | 11000 | cubic feet per minute | CFM | 47992.9132 | 53325.4591 | 58658.005 | 1.03 | 1.2159 | 0 | 0 | 49432.7006 | 54925.2228 | 60417.7451 | 58354.5781 | 64838.4201 | 71322.2621 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | 0 | 2024 | Used EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Tables from Commercial Rooftop AC to estimate projections for price and efficiency. Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites.
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0431 | 4.1411 | 6.2765 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 1 |  |  | 6245.5433 | 7527.4897 | 8590.3947 | 1.1336 | 1.1336 | 0 | 0 | 7079.8355 | 8533.0269 | 9737.9168 | 7079.8355 | 8533.0269 | 9737.9168 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0431 | 4.1411 | 12.6191 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 1 |  |  | 6245.5433 | 7527.4897 | 15097.8967 | 1.1336 | 1.1336 | 0 | 0 | 7079.8355 | 8533.0269 | 17114.7041 | 7079.8355 | 8533.0269 | 17114.7041 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0431 | 4.1411 | 6.2765 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 1 |  |  | 6245.5433 | 7527.4897 | 8590.3947 | 1.1336 | 1.1336 | 0 | 0 | 7079.8355 | 8533.0269 | 9737.9168 | 7079.8355 | 8533.0269 | 9737.9168 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0431 | 4.1411 | 6.2765 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 1 |  |  | 6245.5433 | 7527.4897 | 8590.3947 | 1.1336 | 1.1336 | 0 | 0 | 7079.8355 | 8533.0269 | 9737.9168 | 7079.8355 | 8533.0269 | 9737.9168 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0431 | 4.1411 | 6.2765 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 1 |  |  | 6245.5433 | 7527.4897 | 8590.3947 | 1.1336 | 1.1336 | 0 | 0 | 7079.8355 | 8533.0269 | 9737.9168 | 7079.8355 | 8533.0269 | 9737.9168 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0431 | 4.1411 | 6.2765 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 1 |  |  | 6245.5433 | 7527.4897 | 8590.3947 | 1.1336 | 1.1336 | 0 | 0 | 7079.8355 | 8533.0269 | 9737.9168 | 7079.8355 | 8533.0269 | 9737.9168 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0431 | 4.1411 | 6.2765 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 1 |  |  | 6245.5433 | 7527.4897 | 8590.3947 | 1.1336 | 1.1336 | 0 | 0 | 7079.8355 | 8533.0269 | 9737.9168 | 7079.8355 | 8533.0269 | 9737.9168 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0253 | 4.1168 | 6.2397 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 41.7947 | 130.1567 | -10.2219 | Sensible Efficiency | Unitless | 54 | 63.0164 | 68 | 68 | 513.72 | -4810.183 | 2771.9136 | 1 |  |  | 6251.449 | 7615.6989 | 8529.6995 | 1.1336 | 1.1336 | 0 | 0 | 7086.5302 | 8633.0192 | 9669.1139 | 7086.5302 | 8633.0192 | 9669.1139 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0253 | 4.1168 | 6.2397 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 41.7947 | 130.1567 | -10.2219 | Sensible Efficiency | Unitless | 54 | 63.0164 | 68 | 68 | 513.72 | -4810.183 | 2771.9136 | 1 |  |  | 6251.449 | 7615.6989 | 8529.6995 | 1.1336 | 1.1336 | 0 | 0 | 7086.5302 | 8633.0192 | 9669.1139 | 7086.5302 | 8633.0192 | 9669.1139 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0253 | 4.1168 | 6.2397 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 41.7947 | 130.1567 | -10.2219 | Sensible Efficiency | Unitless | 54 | 63.0164 | 68 | 68 | 513.72 | -4810.183 | 2771.9136 | 1 |  |  | 6251.449 | 7615.6989 | 8529.6995 | 1.1336 | 1.1336 | 0 | 0 | 7086.5302 | 8633.0192 | 9669.1139 | 7086.5302 | 8633.0192 | 9669.1139 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0191 | 4.1084 | 6.2268 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 41.7086 | 129.8884 | -10.2008 | Sensible Efficiency | Unitless | 54 | 63.1434 | 68 | 68 | 512.6611 | -4800.268 | 2766.2 | 1 |  |  | 6243.8623 | 7616.5032 | 8510.8217 | 1.1336 | 1.1336 | 0 | 0 | 7077.9299 | 8633.931 | 9647.7143 | 7077.9299 | 8633.931 | 9647.7143 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0128 | 4.0999 | 6.214 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 41.6224 | 129.6201 | -10.1798 | Sensible Efficiency | Unitless | 54 | 63.2705 | 68 | 68 | 511.6022 | -4790.353 | 2760.4864 | 1 |  |  | 6236.2536 | 7617.2394 | 8491.9492 | 1.1336 | 1.1336 | 0 | 0 | 7069.3049 | 8634.7656 | 9626.3208 | 7069.3049 | 8634.7656 | 9626.3208 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 3.0431 | 4.1411 | 6.2765 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 1 |  |  | 6245.5433 | 7527.4897 | 8590.3947 | 1.1336 | 1.1336 | 0 | 0 | 7079.8355 | 8533.0269 | 9737.9168 | 7079.8355 | 8533.0269 | 9737.9168 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 2.9754 | 4.049 | 6.1368 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 41.1055 | 128.0104 | -10.0534 | Sensible Efficiency | Unitless | 54 | 64.0328 | 68 | 68 | 505.2487 | -4730.8631 | 2726.2047 | 1 |  |  | 6190.142 | 7620.2249 | 8378.8266 | 1.1336 | 1.1336 | 0 | 0 | 7017.0336 | 8638.1498 | 9498.087 | 7017.0336 | 8638.1498 | 9498.087 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 2.9754 | 4.049 | 6.1368 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 41.1055 | 128.0104 | -10.0534 | Sensible Efficiency | Unitless | 54 | 64.0328 | 68 | 68 | 505.2487 | -4730.8631 | 2726.2047 | 1 |  |  | 6190.142 | 7620.2249 | 8378.8266 | 1.1336 | 1.1336 | 0 | 0 | 7017.0336 | 8638.1498 | 9498.087 | 7017.0336 | 8638.1498 | 9498.087 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 2.9754 | 4.049 | 6.1368 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 41.1055 | 128.0104 | -10.0534 | Sensible Efficiency | Unitless | 54 | 64.0328 | 68 | 68 | 505.2487 | -4730.8631 | 2726.2047 | 1 |  |  | 6190.142 | 7620.2249 | 8378.8266 | 1.1336 | 1.1336 | 0 | 0 | 7017.0336 | 8638.1498 | 9498.087 | 7017.0336 | 8638.1498 | 9498.087 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 2.963 | 4.032 | 6.1111 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 40.9332 | 127.4739 | -10.0112 | Sensible Efficiency | Unitless | 54 | 64.2869 | 68 | 68 | 503.1309 | -4711.0331 | 2714.7775 | 1 |  |  | 6174.5963 | 7620.6747 | 8341.1619 | 1.1336 | 1.1336 | 0 | 0 | 6999.4113 | 8638.6597 | 9455.391 | 6999.4113 | 8638.6597 | 9455.391 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
6 | 2023 | Residential, Commercial | HVAC | Energy Recovery | Ventilation | Electricity | Energy Recovery Ventilation | 2023$ |  |  | 2.9505 | 4.015 | 6.0854 | Airflow | CFM | 510 | 1026 | 2025 | 2025 | 40.7609 | 126.9373 | -9.9691 | Sensible Efficiency | Unitless | 54 | 64.541 | 68 | 68 | 501.0131 | -4691.2031 | 2703.3503 | 1 |  |  | 6158.9631 | 7620.8518 | 8303.5186 | 1.1336 | 1.1336 | 0 | 0 | 6981.6897 | 8638.8605 | 9412.7192 | 6981.6897 | 8638.8605 | 9412.7192 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 16000 | Square Feet | ft2 | 22119.5789 | 39810.2456 | 51221.8947 | 1 | 1 | 0 | 0 | 22119.5789 | 39810.2456 | 51221.8947 | 22119.5789 | 39810.2456 | 51221.8947 | 2023 | Reference | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 16000 | Square Feet | ft2 | 22119.5789 | 39810.2456 | 51221.8947 | 1 | 1 | 0 | 0 | 22119.5789 | 39810.2456 | 51221.8947 | 22119.5789 | 39810.2456 | 51221.8947 | 2030 | Reference | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 16000 | Square Feet | ft2 | 22119.5789 | 39810.2456 | 51221.8947 | 1 | 1 | 0 | 0 | 22119.5789 | 39810.2456 | 51221.8947 | 22119.5789 | 39810.2456 | 51221.8947 | 2035 | Reference | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 16000 | Square Feet | ft2 | 22119.5789 | 39810.2456 | 51221.8947 | 1 | 1 | 0 | 0 | 22119.5789 | 39810.2456 | 51221.8947 | 22119.5789 | 39810.2456 | 51221.8947 | 2040 | Reference | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 16000 | Square Feet | ft2 | 22119.5789 | 39810.2456 | 51221.8947 | 1 | 1 | 0 | 0 | 22119.5789 | 39810.2456 | 51221.8947 | 22119.5789 | 39810.2456 | 51221.8947 | 2045 | Reference | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 16000 | Square Feet | ft2 | 22119.5789 | 39810.2456 | 51221.8947 | 1 | 1 | 0 | 0 | 22119.5789 | 39810.2456 | 51221.8947 | 22119.5789 | 39810.2456 | 51221.8947 | 2050 | Reference | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 16000 | Square Feet | ft2 | 22119.5789 | 39810.2456 | 51221.8947 | 1 | 1 | 0 | 0 | 22119.5789 | 39810.2456 | 51221.8947 | 22119.5789 | 39810.2456 | 51221.8947 | 2023 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 16000 | Square Feet | ft2 | 22119.5789 | 39810.2456 | 51221.8947 | 1 | 1 | 0 | 0 | 22119.5789 | 39810.2456 | 51221.8947 | 22119.5789 | 39810.2456 | 51221.8947 | 2030 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.025 | 8.2 | 18.45 | 18.45 | 1.3479 | 2.4259 | 3.1213 | 16000 | Square Feet | ft2 | 21566.5895 | 38814.9895 | 49941.3474 | 1 | 1 | 0 | 0 | 21566.5895 | 38814.9895 | 49941.3474 | 21566.5895 | 38814.9895 | 49941.3474 | 2035 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.0381 | 8.305 | 18.6863 | 18.6863 | 1.3315 | 2.3964 | 3.0833 | 16000 | Square Feet | ft2 | 21303.9195 | 38342.2428 | 49333.0874 | 1 | 1 | 0 | 0 | 21303.9195 | 38342.2428 | 49333.0874 | 21303.9195 | 38342.2428 | 49333.0874 | 2040 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.0513 | 8.41 | 18.9225 | 18.9225 | 1.3151 | 2.3668 | 3.0453 | 16000 | Square Feet | ft2 | 21041.2495 | 37869.4961 | 48724.8274 | 1 | 1 | 0 | 0 | 21041.2495 | 37869.4961 | 48724.8274 | 21041.2495 | 37869.4961 | 48724.8274 | 2045 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.065 | 8.5203 | 19.1706 | 19.1706 | 1.2995 | 2.3388 | 3.0092 | 16000 | Square Feet | ft2 | 20791.713 | 37420.3868 | 48146.9804 | 1 | 1 | 0 | 0 | 20791.713 | 37420.3868 | 48146.9804 | 20791.713 | 37420.3868 | 48146.9804 | 2050 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 16000 | Square Feet | ft2 | 22119.5789 | 39810.2456 | 51221.8947 | 1 | 1 | 0 | 0 | 22119.5789 | 39810.2456 | 51221.8947 | 22119.5789 | 39810.2456 | 51221.8947 | 2023 | Advanced | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.05 | 8.4 | 18.9 | 18.9 | 1.3134 | 2.3637 | 3.0413 | 16000 | Square Feet | ft2 | 21013.6 | 37819.7333 | 48660.8 | 1 | 1 | 0 | 0 | 21013.6 | 37819.7333 | 48660.8 | 21013.6 | 37819.7333 | 48660.8 | 2030 | Advanced | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.0762 | 8.61 | 19.3725 | 19.3725 | 1.2805 | 2.3046 | 2.9653 | 16000 | Square Feet | ft2 | 20488.26 | 36874.24 | 47444.28 | 1 | 1 | 0 | 0 | 20488.26 | 36874.24 | 47444.28 | 20488.26 | 36874.24 | 47444.28 | 2035 | Advanced | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.1025 | 8.82 | 19.845 | 19.845 | 1.2477 | 2.2455 | 2.8892 | 16000 | Square Feet | ft2 | 19962.92 | 35928.7467 | 46227.76 | 1 | 1 | 0 | 0 | 19962.92 | 35928.7467 | 46227.76 | 19962.92 | 35928.7467 | 46227.76 | 2040 | Advanced | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.1301 | 9.0405 | 20.3411 | 20.3411 | 1.2165 | 2.1894 | 2.817 | 16000 | Square Feet | ft2 | 19463.847 | 35030.528 | 45072.066 | 1 | 1 | 0 | 0 | 19463.847 | 35030.528 | 45072.066 | 19463.847 | 35030.528 | 45072.066 | 2045 | Advanced | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
7 | 2023 | Commercial | HVAC | Demand Controlled Ventilation |  | Electricity | Demand Controlled Ventilation | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.1576 | 9.261 | 20.8373 | 20.8373 | 1.1853 | 2.1333 | 2.7448 | 16000 | Square Feet | ft2 | 18964.774 | 34132.3093 | 43916.372 | 1 | 1 | 0 | 0 | 18964.774 | 34132.3093 | 43916.372 | 18964.774 | 34132.3093 | 43916.372 | 2050 | Advanced | 15 | Providing a general rule to estimate DCV costs is challenging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | 0 | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an average home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 11 | Tons | ton | 121414.3333 | 165162.25 | 183656 | 1.2151 | 1.3145 | 0 | 0 | 147529.3564 | 200687.0175 | 223158.5904 | 159603.0745 | 217111.1282 | 241421.7617 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 11 | Tons | ton | 121414.3333 | 165162.25 | 183656 | 1.2151 | 1.3145 | 0 | 0 | 147529.3564 | 200687.0175 | 223158.5904 | 159603.0745 | 217111.1282 | 241421.7617 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 11 | Tons | ton | 121414.3333 | 165162.25 | 183656 | 1.2151 | 1.3145 | 0 | 0 | 147529.3564 | 200687.0175 | 223158.5904 | 159603.0745 | 217111.1282 | 241421.7617 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 11 | Tons | ton | 121414.3333 | 165162.25 | 183656 | 1.2151 | 1.3145 | 0 | 0 | 147529.3564 | 200687.0175 | 223158.5904 | 159603.0745 | 217111.1282 | 241421.7617 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 11 | Tons | ton | 121414.3333 | 165162.25 | 183656 | 1.2151 | 1.3145 | 0 | 0 | 147529.3564 | 200687.0175 | 223158.5904 | 159603.0745 | 217111.1282 | 241421.7617 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 11 | Tons | ton | 121414.3333 | 165162.25 | 183656 | 1.2151 | 1.3145 | 0 | 0 | 147529.3564 | 200687.0175 | 223158.5904 | 159603.0745 | 217111.1282 | 241421.7617 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 11 | Tons | ton | 121414.3333 | 165162.25 | 183656 | 1.2151 | 1.3145 | 0 | 0 | 147529.3564 | 200687.0175 | 223158.5904 | 159603.0745 | 217111.1282 | 241421.7617 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 10123.3037 | 13770.9246 | 15312.8994 | 11 | Tons | ton | 111356.3412 | 151480.1701 | 168441.8935 | 1.2151 | 1.3145 | 0 | 0 | 135307.9896 | 184062.0575 | 204672.0799 | 146381.518 | 199125.5909 | 221422.3258 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 10056.1832 | 13679.6192 | 15211.3703 | 11 | Tons | ton | 110618.0151 | 150475.8109 | 167325.0729 | 1.2151 | 1.3145 | 0 | 0 | 134410.8568 | 182841.6705 | 203315.0422 | 145410.9643 | 197805.3281 | 219954.2289 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9990.9914 | 13590.9375 | 15112.7586 | 11 | Tons | ton | 109900.9052 | 149500.3125 | 166240.3448 | 1.2151 | 1.3145 | 0 | 0 | 133539.5036 | 181656.3521 | 201996.9999 | 144468.3002 | 196523.0039 | 218528.3187 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9927.6464 | 13504.7681 | 15016.9405 | 11 | Tons | ton | 109204.11 | 148552.4487 | 165186.3456 | 1.2151 | 1.3145 | 0 | 0 | 132692.8347 | 180504.6121 | 200716.2959 | 143552.3403 | 195277.0062 | 217142.8026 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9866.0708 | 13421.0056 | 14923.7989 | 11 | Tons | ton | 108526.7784 | 147631.0615 | 164161.7877 | 1.2151 | 1.3145 | 0 | 0 | 131869.8158 | 179385.0436 | 199471.3657 | 142661.966 | 194065.8129 | 215795.9881 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 11 | Tons | ton | 121414.3333 | 165162.25 | 183656 | 1.2151 | 1.3145 | 0 | 0 | 147529.3564 | 200687.0175 | 223158.5904 | 159603.0745 | 217111.1282 | 241421.7617 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9208.9408 | 12527.0991 | 13929.7988 | 11 | Tons | ton | 101298.3491 | 137798.0902 | 153227.787 | 1.2151 | 1.3145 | 0 | 0 | 123086.6228 | 167437.0975 | 186185.5695 | 133159.9615 | 181140.0537 | 201422.8899 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9074.6997 | 12344.4883 | 13726.7405 | 11 | Tons | ton | 99821.6968 | 135789.3717 | 150994.1458 | 1.2151 | 1.3145 | 0 | 0 | 121292.3571 | 164996.3235 | 183471.4941 | 131218.8542 | 178499.5281 | 198486.6962 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 8944.3161 | 12167.125 | 13529.5172 | 11 | Tons | ton | 98387.477 | 133838.375 | 148824.6897 | 1.2151 | 1.3145 | 0 | 0 | 119549.6509 | 162625.6866 | 180835.4094 | 129333.5259 | 175934.8797 | 195634.8758 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 8817.6261 | 11994.7861 | 13337.881 | 11 | Tons | ton | 96993.8867 | 131942.6473 | 146716.6912 | 1.2151 | 1.3145 | 0 | 0 | 117856.313 | 160322.2066 | 178274.0014 | 127501.6062 | 173442.8843 | 192863.8436 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
8 | 2023 | Commercial | HVAC | DOAS with Mini Split Heat Pumps |  | Electricity | DOAS with Mini Split Heat Pumps | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 8694.4749 | 11827.2612 | 13151.5978 | 11 | Tons | ton | 95639.2235 | 130099.8729 | 144667.5754 | 1.2151 | 1.3145 | 0 | 0 | 116210.2751 | 158083.0697 | 175784.141 | 125720.8575 | 171020.4976 | 190170.2145 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 13409.6667 | 17953.9091 | 19738 | 11 | Tons | ton | 147506.3333 | 197493 | 217118 | 1.2151 | 1.3145 | 0 | 0 | 179233.4877 | 239971.7923 | 263817.9358 | 193901.8537 | 259610.9464 | 285408.6447 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 13409.6667 | 17953.9091 | 19738 | 11 | Tons | ton | 147506.3333 | 197493 | 217118 | 1.2151 | 1.3145 | 0 | 0 | 179233.4877 | 239971.7923 | 263817.9358 | 193901.8537 | 259610.9464 | 285408.6447 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 13409.6667 | 17953.9091 | 19738 | 11 | Tons | ton | 147506.3333 | 197493 | 217118 | 1.2151 | 1.3145 | 0 | 0 | 179233.4877 | 239971.7923 | 263817.9358 | 193901.8537 | 259610.9464 | 285408.6447 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 13409.6667 | 17953.9091 | 19738 | 11 | Tons | ton | 147506.3333 | 197493 | 217118 | 1.2151 | 1.3145 | 0 | 0 | 179233.4877 | 239971.7923 | 263817.9358 | 193901.8537 | 259610.9464 | 285408.6447 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 13409.6667 | 17953.9091 | 19738 | 11 | Tons | ton | 147506.3333 | 197493 | 217118 | 1.2151 | 1.3145 | 0 | 0 | 179233.4877 | 239971.7923 | 263817.9358 | 193901.8537 | 259610.9464 | 285408.6447 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 13409.6667 | 17953.9091 | 19738 | 11 | Tons | ton | 147506.3333 | 197493 | 217118 | 1.2151 | 1.3145 | 0 | 0 | 179233.4877 | 239971.7923 | 263817.9358 | 193901.8537 | 259610.9464 | 285408.6447 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 13409.6667 | 17953.9091 | 19738 | 11 | Tons | ton | 147506.3333 | 197493 | 217118 | 1.2151 | 1.3145 | 0 | 0 | 179233.4877 | 239971.7923 | 263817.9358 | 193901.8537 | 259610.9464 | 285408.6447 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 12298.8067 | 16466.603 | 18102.8994 | 11 | Tons | ton | 135286.8738 | 181132.6331 | 199131.8935 | 1.2151 | 1.3145 | 0 | 0 | 164385.7432 | 220092.4722 | 241963.1956 | 177838.9783 | 238104.7142 | 261765.325 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 12217.2619 | 16357.4245 | 17982.8717 | 11 | Tons | ton | 134389.881 | 179931.6691 | 197811.5889 | 1.2151 | 1.3145 | 0 | 0 | 163295.8161 | 218633.1927 | 240358.9066 | 176659.8522 | 236526.008 | 260029.7419 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 12138.0603 | 16251.3832 | 17866.2931 | 11 | Tons | ton | 133518.6638 | 178765.2155 | 196529.2241 | 1.2151 | 1.3145 | 0 | 0 | 162237.2087 | 217215.8465 | 238800.7178 | 175514.609 | 234992.667 | 258344.0318 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 12061.1025 | 16148.346 | 17753.017 | 11 | Tons | ton | 132672.127 | 177631.8059 | 195283.187 | 1.2151 | 1.3145 | 0 | 0 | 161208.5902 | 215838.6517 | 237286.6703 | 174401.809 | 233502.7634 | 256706.0756 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11986.2942 | 16048.1869 | 17642.905 | 11 | Tons | ton | 131849.2365 | 176530.0559 | 194071.9553 | 1.2151 | 1.3145 | 0 | 0 | 160208.7041 | 214499.9261 | 235814.9147 | 173320.0927 | 232054.4772 | 255113.8723 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 13409.6667 | 17953.9091 | 19738 | 11 | Tons | ton | 147506.3333 | 197493 | 217118 | 1.2151 | 1.3145 | 0 | 0 | 179233.4877 | 239971.7923 | 263817.9358 | 193901.8537 | 259610.9464 | 285408.6447 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11187.9467 | 14979.2969 | 16467.7988 | 11 | Tons | ton | 123067.4142 | 164772.2663 | 181145.787 | 1.2151 | 1.3145 | 0 | 0 | 149537.9986 | 200213.1522 | 220108.4553 | 161776.1028 | 216598.4819 | 238122.0053 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11024.8571 | 14760.9398 | 16227.7434 | 11 | Tons | ton | 121273.4286 | 162370.3382 | 178505.1778 | 1.2151 | 1.3145 | 0 | 0 | 147358.1444 | 197294.5931 | 216899.8773 | 159417.8506 | 213441.0696 | 234650.8391 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 10866.454 | 14548.8574 | 15994.5862 | 11 | Tons | ton | 119530.9943 | 160037.431 | 175940.4483 | 1.2151 | 1.3145 | 0 | 0 | 145240.9297 | 194459.9007 | 213783.4997 | 157127.3642 | 210374.3876 | 231279.419 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 10712.5382 | 14342.7829 | 15768.034 | 11 | Tons | ton | 117837.9207 | 157770.6119 | 173448.3739 | 1.2151 | 1.3145 | 0 | 0 | 143183.6927 | 191705.5111 | 210755.4048 | 154901.7642 | 207394.5804 | 228003.5065 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
9 | 2023 | Commercial | HVAC | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | Electricity | DOAS with VRF | 2023$/ton |  |  | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 10562.9218 | 14142.4647 | 15547.8101 | 11 | Tons | ton | 116192.1397 | 155567.1117 | 171025.9106 | 1.2151 | 1.3145 | 0 | 0 | 141183.9205 | 189028.0599 | 207811.8936 | 152738.3317 | 204498.0081 | 224819.1 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2023 | Reference | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2030 | Reference | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2035 | Reference | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2040 | Reference | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2045 | Reference | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2050 | Reference | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2023 | Intermediate | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2030 | Intermediate | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2035 | Intermediate | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2040 | Intermediate | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2045 | Intermediate | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2050 | Intermediate | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2023 | Advanced | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2030 | Advanced | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2035 | Advanced | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2040 | Advanced | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2045 | Advanced | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
10 | 2023 | Commercial | HVAC | Ground Source Heat Pump | Ground Source Heat Pump | Electricity | Commercial Ground Source Heat Pump | 2023$ |  | Commercial Ground Source Heat Pump | 5369.4 | 8949 | 12528.6 | Cooling Capacity | Tons | 3 | 4 | 6 | 20 | 0 | 0 | 0 | Heating COP | Unitless | 3.1 | 3.6 | 4.5 | 5 | 9482.4 | 15804 | 22125.6 | 1 |  |  | 30960 | 51600 | 72240 | 1 | 1 | 0 | 0 | 30960 | 51600 | 72240 | 30960 | 51600 | 72240 | 2050 | Advanced | 15.3 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 13 | 0.3368 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Typical retail price refers to the total installed cost due to lack of data availability. No ground heat exchanger.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.000463 | 0.002939 | 0.026427 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.04311 | -0.036938 | 0.31743 | Efficacy | lm/W | 0.045901 | 140.146 | 163.6364 | 278.5714 | -0.118 | 15.1226 | 85.2784 | 1 |  |  | 6.8127 | 15.5888 | 180.5048 | 1 | 1 | 26.4 | 26.4 | 33.2127 | 41.9888 | 206.9048 | 33.2127 | 41.9888 | 206.9048 | 2023 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.00041174 | 0.0026136 | 0.023501 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.032326 | -0.027698 | 0.23802 | Efficacy | lm/W | 0.045901 | 166.209 | 194.0679 | 278.5714 | -0.10494 | 13.4484 | 75.8374 | 1 |  |  | 6.0584 | 13.863 | 160.5215 | 1 | 1 | 26.4 | 26.4 | 32.4584 | 40.263 | 186.9215 | 32.4584 | 40.263 | 186.9215 | 2030 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.00040707 | 0.002584 | 0.023235 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.029642 | -0.025398 | 0.21826 | Efficacy | lm/W | 0.045901 | 179.2024 | 209.2392 | 278.5714 | -0.10375 | 13.2958 | 74.9769 | 1 |  |  | 5.9897 | 13.7057 | 158.7002 | 1 | 1 | 26.4 | 26.4 | 32.3897 | 40.1057 | 185.1002 | 32.3897 | 40.1057 | 185.1002 | 2035 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.0004024 | 0.0025543 | 0.022968 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.027321 | -0.023409 | 0.20117 | Efficacy | lm/W | 0.045901 | 192.1959 | 224.4105 | 278.5714 | -0.10256 | 13.1432 | 74.1165 | 1 |  |  | 5.921 | 13.5484 | 156.8788 | 1 | 1 | 26.4 | 26.4 | 32.321 | 39.9484 | 183.2788 | 32.321 | 39.9484 | 183.2788 | 2040 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.000398 | 0.0025264 | 0.022717 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.02532 | -0.021695 | 0.18644 | Efficacy | lm/W | 0.045901 | 205.1131 | 237.2052 | 278.5714 | -0.10144 | 12.9996 | 73.3066 | 1 |  |  | 5.8563 | 13.4003 | 155.1647 | 1 | 1 | 26.4 | 26.4 | 32.2563 | 39.8003 | 181.5647 | 32.2563 | 39.8003 | 181.5647 | 2045 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.00039361 | 0.0024985 | 0.022466 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.023557 | -0.020184 | 0.17346 | Efficacy | lm/W | 0.045901 | 218.0303 | 250 | 278.5714 | -0.10031 | 12.856 | 72.4968 | 1 |  |  | 5.7916 | 13.2523 | 153.4505 | 1 | 1 | 26.4 | 26.4 | 32.1916 | 39.6523 | 179.8505 | 32.1916 | 39.6523 | 179.8505 | 2050 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.000463 | 0.002939 | 0.026427 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.04311 | -0.036938 | 0.31743 | Efficacy | lm/W | 0.045901 | 140.146 | 163.6364 | 278.5714 | -0.118 | 15.1226 | 85.2784 | 1 |  |  | 6.8127 | 15.5888 | 180.5048 | 1 | 1 | 26.4 | 26.4 | 33.2127 | 41.9888 | 206.9048 | 33.2127 | 41.9888 | 206.9048 | 2023 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.00041174 | 0.0026136 | 0.023501 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.028109 | -0.024085 | 0.20698 | Efficacy | lm/W | 0.045901 | 191.1404 | 222.034 | 278.5714 | -0.10494 | 13.4484 | 75.8374 | 1 |  |  | 6.0584 | 13.863 | 160.5215 | 1 | 1 | 26.4 | 26.4 | 32.4584 | 40.263 | 186.9215 | 32.4584 | 40.263 | 186.9215 | 2030 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.00040707 | 0.002584 | 0.023235 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.025771 | -0.022081 | 0.18976 | Efficacy | lm/W | 0.045901 | 206.1192 | 229.6196 | 278.5714 | -0.10375 | 13.2958 | 74.9769 | 1 |  |  | 5.9897 | 13.7057 | 158.7002 | 1 | 1 | 26.4 | 26.4 | 32.3897 | 40.1057 | 185.1002 | 32.3897 | 40.1057 | 185.1002 | 2035 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.0004024 | 0.0025543 | 0.022968 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.023749 | -0.020349 | 0.17487 | Efficacy | lm/W | 0.045901 | 221.0979 | 237.2052 | 278.5714 | -0.10256 | 13.1432 | 74.1165 | 1 |  |  | 5.921 | 13.5484 | 156.8788 | 1 | 1 | 26.4 | 26.4 | 32.321 | 39.9484 | 183.2788 | 32.321 | 39.9484 | 183.2788 | 2040 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.000398 | 0.0025264 | 0.022717 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.022823 | -0.019556 | 0.16805 | Efficacy | lm/W | 0.045901 | 227.5565 | 243.6026 | 278.5714 | -0.10144 | 12.9996 | 73.3066 | 1 |  |  | 5.8563 | 13.4003 | 155.1647 | 1 | 1 | 26.4 | 26.4 | 32.2563 | 39.8003 | 181.5647 | 32.2563 | 39.8003 | 181.5647 | 2045 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.00039361 | 0.0024985 | 0.022466 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.021948 | -0.018806 | 0.16161 | Efficacy | lm/W | 0.045901 | 234.0151 | 250 | 278.5714 | -0.10031 | 12.856 | 72.4968 | 1 |  |  | 5.7916 | 13.2523 | 153.4505 | 1 | 1 | 26.4 | 26.4 | 32.1916 | 39.6523 | 179.8505 | 32.1916 | 39.6523 | 179.8505 | 2050 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.000463 | 0.002939 | 0.026427 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.04311 | -0.036938 | 0.31743 | Efficacy | lm/W | 0.045901 | 140.146 | 163.6364 | 278.5714 | -0.118 | 15.1226 | 85.2784 | 1 |  |  | 6.8127 | 15.5888 | 180.5048 | 1 | 1 | 26.4 | 26.4 | 33.2127 | 41.9888 | 206.9048 | 33.2127 | 41.9888 | 206.9048 | 2023 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.00041174 | 0.0026136 | 0.023501 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.024866 | -0.021306 | 0.18309 | Efficacy | lm/W | 0.045901 | 216.0717 | 250 | 278.5714 | -0.10494 | 13.4484 | 75.8374 | 1 |  |  | 6.0584 | 13.863 | 160.5215 | 1 | 1 | 26.4 | 26.4 | 32.4584 | 40.263 | 186.9215 | 32.4584 | 40.263 | 186.9215 | 2030 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.00040707 | 0.002584 | 0.023235 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.022794 | -0.019531 | 0.16784 | Efficacy | lm/W | 0.045901 | 233.0359 | 250 | 278.5714 | -0.10375 | 13.2958 | 74.9769 | 1 |  |  | 5.9897 | 13.7057 | 158.7002 | 1 | 1 | 26.4 | 26.4 | 32.3897 | 40.1057 | 185.1002 | 32.3897 | 40.1057 | 185.1002 | 2035 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.0004024 | 0.0025543 | 0.022968 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.021004 | -0.017997 | 0.15466 | Efficacy | lm/W | 0.045901 | 250 | 250 | 278.5714 | -0.10256 | 13.1432 | 74.1165 | 1 |  |  | 5.921 | 13.5484 | 156.8788 | 1 | 1 | 26.4 | 26.4 | 32.321 | 39.9484 | 183.2788 | 32.321 | 39.9484 | 183.2788 | 2040 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.000398 | 0.0025264 | 0.022717 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.020774 | -0.0178 | 0.15297 | Efficacy | lm/W | 0.045901 | 250 | 250 | 278.5714 | -0.10144 | 12.9996 | 73.3066 | 1 |  |  | 5.8563 | 13.4003 | 155.1647 | 1 | 1 | 26.4 | 26.4 | 32.2563 | 39.8003 | 181.5647 | 32.2563 | 39.8003 | 181.5647 | 2045 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
11 | 2023 | Commercial | Lighting | LED | TLED | Electricity | Commercial TLED | 2023$ |  | 4ft LED Replacement Lamp | 0.00039361 | 0.0024985 | 0.022466 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.020545 | -0.017603 | 0.15128 | Efficacy | lm/W | 0.045901 | 250 | 250 | 278.5714 | -0.10031 | 12.856 | 72.4968 | 1 |  |  | 5.7916 | 13.2523 | 153.4505 | 1 | 1 | 26.4 | 26.4 | 32.1916 | 39.6523 | 179.8505 | 32.1916 | 39.6523 | 179.8505 | 2050 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.004616 | 0.011117 | 0.007179 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.26937 | -0.40131 | -0.4759 | Efficacy | lm/W | 55.4333 | 120.5 | 137.1429 | 156.25 | 78.3972 | 137.0269 | 248.5897 | 1 |  |  | 70.4125 | 147.611 | 229.3069 | 1 | 1 | 36.2208 | 36.2208 | 106.6333 | 183.8318 | 265.5277 | 106.6333 | 183.8318 | 265.5277 | 2023 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0039951 | 0.0096218 | 0.0062134 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.18882 | -0.28131 | -0.3336 | Efficacy | lm/W | 55.4333 | 148.7806 | 169.3294 | 156.25 | 67.8528 | 118.5968 | 215.1543 | 1 |  |  | 60.942 | 127.7573 | 198.4651 | 1 | 1 | 36.2208 | 36.2208 | 97.1628 | 163.9781 | 234.6859 | 97.1628 | 163.9781 | 234.6859 | 2030 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0038805 | 0.0093457 | 0.0060351 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.16742 | -0.24942 | -0.29578 | Efficacy | lm/W | 55.4333 | 162.9892 | 185.5005 | 156.25 | 65.906 | 115.194 | 208.9812 | 1 |  |  | 59.1935 | 124.0917 | 192.7708 | 1 | 1 | 36.2208 | 36.2208 | 95.4143 | 160.3125 | 228.9916 | 95.4143 | 160.3125 | 228.9916 | 2035 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0037659 | 0.0090696 | 0.0058569 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.14944 | -0.22265 | -0.26403 | Efficacy | lm/W | 55.4333 | 177.1978 | 201.6715 | 156.25 | 63.9591 | 111.7912 | 202.808 | 1 |  |  | 57.445 | 120.4261 | 187.0764 | 1 | 1 | 36.2208 | 36.2208 | 93.6658 | 156.6469 | 223.2972 | 93.6658 | 156.6469 | 223.2972 | 2040 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0036565 | 0.0088061 | 0.0056867 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.13438 | -0.2002 | -0.23741 | Efficacy | lm/W | 55.4333 | 191.3382 | 217.7648 | 156.25 | 62.1009 | 108.5432 | 196.9155 | 1 |  |  | 55.7759 | 116.9272 | 181.6411 | 1 | 1 | 36.2208 | 36.2208 | 91.9967 | 153.148 | 217.8619 | 91.9967 | 153.148 | 217.8619 | 2045 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0035471 | 0.0085426 | 0.0055165 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.12139 | -0.18085 | -0.21446 | Efficacy | lm/W | 55.4333 | 205.4785 | 233.8581 | 156.25 | 60.2426 | 105.2952 | 191.0231 | 1 |  |  | 54.1069 | 113.4284 | 176.2057 | 1 | 1 | 36.2208 | 36.2208 | 90.3277 | 149.6492 | 212.4265 | 90.3277 | 149.6492 | 212.4265 | 2050 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.004616 | 0.011117 | 0.007179 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.26937 | -0.40131 | -0.4759 | Efficacy | lm/W | 55.4333 | 120.5 | 137.1429 | 156.25 | 78.3972 | 137.0269 | 248.5897 | 1 |  |  | 70.4125 | 147.611 | 229.3069 | 1 | 1 | 36.2208 | 36.2208 | 106.6333 | 183.8318 | 265.5277 | 106.6333 | 183.8318 | 265.5277 | 2023 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0039951 | 0.0096218 | 0.0062134 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.16419 | -0.24462 | -0.29008 | Efficacy | lm/W | 55.4333 | 171.0977 | 194.7289 | 156.25 | 67.8528 | 118.5968 | 215.1543 | 1 |  |  | 60.942 | 127.7573 | 198.4651 | 1 | 1 | 36.2208 | 36.2208 | 97.1628 | 163.9781 | 234.6859 | 97.1628 | 163.9781 | 234.6859 | 2030 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0038805 | 0.0093457 | 0.0060351 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.14558 | -0.21689 | -0.2572 | Efficacy | lm/W | 55.4333 | 187.4376 | 210.2823 | 156.25 | 65.906 | 115.194 | 208.9812 | 1 |  |  | 59.1935 | 124.0917 | 192.7708 | 1 | 1 | 36.2208 | 36.2208 | 95.4143 | 160.3125 | 228.9916 | 95.4143 | 160.3125 | 228.9916 | 2035 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0037659 | 0.0090696 | 0.0058569 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.12995 | -0.1936 | -0.22959 | Efficacy | lm/W | 55.4333 | 203.7775 | 225.8358 | 156.25 | 63.9591 | 111.7912 | 202.808 | 1 |  |  | 57.445 | 120.4261 | 187.0764 | 1 | 1 | 36.2208 | 36.2208 | 93.6658 | 156.6469 | 223.2972 | 93.6658 | 156.6469 | 223.2972 | 2040 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0036565 | 0.0088061 | 0.0056867 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.11917 | -0.17754 | -0.21054 | Efficacy | lm/W | 55.4333 | 215.7584 | 233.8824 | 156.25 | 62.1009 | 108.5432 | 196.9155 | 1 |  |  | 55.7759 | 116.9272 | 181.6411 | 1 | 1 | 36.2208 | 36.2208 | 91.9967 | 153.148 | 217.8619 | 91.9967 | 153.148 | 217.8619 | 2045 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0035471 | 0.0085426 | 0.0055165 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.10952 | -0.16317 | -0.19349 | Efficacy | lm/W | 55.4333 | 227.7392 | 241.9291 | 156.25 | 60.2426 | 105.2952 | 191.0231 | 1 |  |  | 54.1069 | 113.4284 | 176.2057 | 1 | 1 | 36.2208 | 36.2208 | 90.3277 | 149.6492 | 212.4265 | 90.3277 | 149.6492 | 212.4265 | 2050 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.004616 | 0.011117 | 0.007179 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.26937 | -0.40131 | -0.4759 | Efficacy | lm/W | 55.4333 | 120.5 | 137.1429 | 156.25 | 78.3972 | 137.0269 | 248.5897 | 1 |  |  | 70.4125 | 147.611 | 229.3069 | 1 | 1 | 36.2208 | 36.2208 | 106.6333 | 183.8318 | 265.5277 | 106.6333 | 183.8318 | 265.5277 | 2023 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0039951 | 0.0096218 | 0.0062134 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.14525 | -0.2164 | -0.25661 | Efficacy | lm/W | 55.4333 | 193.4148 | 220.1283 | 156.25 | 67.8528 | 118.5968 | 215.1543 | 1 |  |  | 60.942 | 127.7573 | 198.4651 | 1 | 1 | 36.2208 | 36.2208 | 97.1628 | 163.9781 | 234.6859 | 97.1628 | 163.9781 | 234.6859 | 2030 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0038805 | 0.0093457 | 0.0060351 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.12878 | -0.19186 | -0.22752 | Efficacy | lm/W | 55.4333 | 211.886 | 235.0641 | 156.25 | 65.906 | 115.194 | 208.9812 | 1 |  |  | 59.1935 | 124.0917 | 192.7708 | 1 | 1 | 36.2208 | 36.2208 | 95.4143 | 160.3125 | 228.9916 | 95.4143 | 160.3125 | 228.9916 | 2035 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0037659 | 0.0090696 | 0.0058569 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.11496 | -0.17127 | -0.2031 | Efficacy | lm/W | 55.4333 | 230.3572 | 250 | 156.25 | 63.9591 | 111.7912 | 202.808 | 1 |  |  | 57.445 | 120.4261 | 187.0764 | 1 | 1 | 36.2208 | 36.2208 | 93.6658 | 156.6469 | 223.2972 | 93.6658 | 156.6469 | 223.2972 | 2040 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0036565 | 0.0088061 | 0.0056867 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.10705 | -0.15949 | -0.18913 | Efficacy | lm/W | 55.4333 | 240.1786 | 250 | 156.25 | 62.1009 | 108.5432 | 196.9155 | 1 |  |  | 55.7759 | 116.9272 | 181.6411 | 1 | 1 | 36.2208 | 36.2208 | 91.9967 | 153.148 | 217.8619 | 91.9967 | 153.148 | 217.8619 | 2045 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
12 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | Commercial LED Troffer & Panel | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0.0035471 | 0.0085426 | 0.0055165 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.099769 | -0.14864 | -0.17626 | Efficacy | lm/W | 55.4333 | 250 | 250 | 156.25 | 60.2426 | 105.2952 | 191.0231 | 1 |  |  | 54.1069 | 113.4284 | 176.2057 | 1 | 1 | 36.2208 | 36.2208 | 90.3277 | 149.6492 | 212.4265 | 90.3277 | 149.6492 | 212.4265 | 2050 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.001648 | 0.003012 | 0.001264 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.021554 | 0.020291 | 0.081726 | Efficacy | lm/W | 50 | 90.0141 | 100 | 125 | -0.66465 | 1.1906 | 4.8261 | 1 |  |  | 2.5939 | 5.4267 | 13.1937 | 1 | 1 | 72.4416 | 76.0637 | 75.0355 | 77.8683 | 85.6353 | 78.6576 | 81.4904 | 89.2574 | 2023 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0013593 | 0.0024844 | 0.0010426 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.014702 | 0.013841 | 0.055746 | Efficacy | lm/W | 50 | 108.8505 | 120.9261 | 125 | -0.54824 | 0.98207 | 3.9807 | 1 |  |  | 2.1396 | 4.4762 | 10.8828 | 1 | 1 | 72.4416 | 76.0637 | 74.5812 | 76.9178 | 83.3244 | 78.2033 | 80.5399 | 86.9465 | 2030 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0012776 | 0.0023351 | 0.00097993 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.012156 | 0.011444 | 0.046093 | Efficacy | lm/W | 50 | 123.7326 | 137.4592 | 125 | -0.51528 | 0.92303 | 3.7414 | 1 |  |  | 2.011 | 4.2071 | 10.2286 | 1 | 1 | 72.4416 | 76.0637 | 74.4526 | 76.6487 | 82.6702 | 78.0746 | 80.2708 | 86.2923 | 2035 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0011959 | 0.0021857 | 0.00091725 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.010157 | 0.0095619 | 0.038513 | Efficacy | lm/W | 50 | 138.6147 | 153.9923 | 125 | -0.48232 | 0.86399 | 3.5021 | 1 |  |  | 1.8823 | 3.938 | 9.5744 | 1 | 1 | 72.4416 | 76.0637 | 74.3239 | 76.3796 | 82.016 | 77.946 | 80.0017 | 85.638 | 2040 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0011142 | 0.0020364 | 0.0008546 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.008764 | 0.0082504 | 0.03323 | Efficacy | lm/W | 50 | 149.6761 | 166.2808 | 125 | -0.44938 | 0.80498 | 3.2629 | 1 |  |  | 1.7538 | 3.669 | 8.9204 | 1 | 1 | 72.4416 | 76.0637 | 74.1954 | 76.1106 | 81.362 | 77.8174 | 79.7327 | 84.9841 | 2045 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0010325 | 0.0018871 | 0.00079194 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0075626 | 0.0071194 | 0.028675 | Efficacy | lm/W | 50 | 160.7375 | 178.5693 | 125 | -0.41643 | 0.74596 | 3.0237 | 1 |  |  | 1.6252 | 3.4 | 8.2664 | 1 | 1 | 72.4416 | 76.0637 | 74.0668 | 75.8416 | 80.708 | 77.6889 | 79.4637 | 84.3301 | 2050 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.001648 | 0.003012 | 0.001264 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.021554 | 0.020291 | 0.081726 | Efficacy | lm/W | 50 | 90.0141 | 100 | 125 | -0.66465 | 1.1906 | 4.8261 | 1 |  |  | 2.5939 | 5.4267 | 13.1937 | 1 | 1 | 72.4416 | 76.0637 | 75.0355 | 77.8683 | 85.6353 | 78.6576 | 81.4904 | 89.2574 | 2023 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0013593 | 0.0024844 | 0.0010426 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.012784 | 0.012035 | 0.048475 | Efficacy | lm/W | 50 | 125.1781 | 139.065 | 125 | -0.54824 | 0.98207 | 3.9807 | 1 |  |  | 2.1396 | 4.4762 | 10.8828 | 1 | 1 | 72.4416 | 76.0637 | 74.5812 | 76.9178 | 83.3244 | 78.2033 | 80.5399 | 86.9465 | 2030 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0012776 | 0.0023351 | 0.00097993 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.010571 | 0.0099513 | 0.040081 | Efficacy | lm/W | 50 | 142.2925 | 158.0781 | 125 | -0.51528 | 0.92303 | 3.7414 | 1 |  |  | 2.011 | 4.2071 | 10.2286 | 1 | 1 | 72.4416 | 76.0637 | 74.4526 | 76.6487 | 82.6702 | 78.0746 | 80.2708 | 86.2923 | 2035 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0011959 | 0.0021857 | 0.00091725 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0088323 | 0.0083147 | 0.033489 | Efficacy | lm/W | 50 | 159.4069 | 177.0911 | 125 | -0.48232 | 0.86399 | 3.5021 | 1 |  |  | 1.8823 | 3.938 | 9.5744 | 1 | 1 | 72.4416 | 76.0637 | 74.3239 | 76.3796 | 82.016 | 77.946 | 80.0017 | 85.638 | 2040 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0011142 | 0.0020364 | 0.0008546 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0076208 | 0.0071743 | 0.028896 | Efficacy | lm/W | 50 | 172.1275 | 191.2229 | 125 | -0.44938 | 0.80498 | 3.2629 | 1 |  |  | 1.7538 | 3.669 | 8.9204 | 1 | 1 | 72.4416 | 76.0637 | 74.1954 | 76.1106 | 81.362 | 77.8174 | 79.7327 | 84.9841 | 2045 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0010325 | 0.0018871 | 0.00079194 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0065761 | 0.0061908 | 0.024935 | Efficacy | lm/W | 50 | 184.8481 | 205.3547 | 125 | -0.41643 | 0.74596 | 3.0237 | 1 |  |  | 1.6252 | 3.4 | 8.2664 | 1 | 1 | 72.4416 | 76.0637 | 74.0668 | 75.8416 | 80.708 | 77.6889 | 79.4637 | 84.3301 | 2050 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.001648 | 0.003012 | 0.001264 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.021554 | 0.020291 | 0.081726 | Efficacy | lm/W | 50 | 90.0141 | 100 | 125 | -0.66465 | 1.1906 | 4.8261 | 1 |  |  | 2.5939 | 5.4267 | 13.1937 | 1 | 1 | 72.4416 | 76.0637 | 75.0355 | 77.8683 | 85.6353 | 78.6576 | 81.4904 | 89.2574 | 2023 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0013593 | 0.0024844 | 0.0010426 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.011309 | 0.010647 | 0.042881 | Efficacy | lm/W | 50 | 141.5056 | 157.2039 | 125 | -0.54824 | 0.98207 | 3.9807 | 1 |  |  | 2.1396 | 4.4762 | 10.8828 | 1 | 1 | 72.4416 | 76.0637 | 74.5812 | 76.9178 | 83.3244 | 78.2033 | 80.5399 | 86.9465 | 2030 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0012776 | 0.0023351 | 0.00097993 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.009351 | 0.0088031 | 0.035456 | Efficacy | lm/W | 50 | 160.8524 | 178.6969 | 125 | -0.51528 | 0.92303 | 3.7414 | 1 |  |  | 2.011 | 4.2071 | 10.2286 | 1 | 1 | 72.4416 | 76.0637 | 74.4526 | 76.6487 | 82.6702 | 78.0746 | 80.2708 | 86.2923 | 2035 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0011959 | 0.0021857 | 0.00091725 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0078132 | 0.0073553 | 0.029625 | Efficacy | lm/W | 50 | 180.1991 | 200.19 | 125 | -0.48232 | 0.86399 | 3.5021 | 1 |  |  | 1.8823 | 3.938 | 9.5744 | 1 | 1 | 72.4416 | 76.0637 | 74.3239 | 76.3796 | 82.016 | 77.946 | 80.0017 | 85.638 | 2040 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0011142 | 0.0020364 | 0.0008546 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0067415 | 0.0063465 | 0.025562 | Efficacy | lm/W | 50 | 194.5789 | 216.165 | 125 | -0.44938 | 0.80498 | 3.2629 | 1 |  |  | 1.7538 | 3.669 | 8.9204 | 1 | 1 | 72.4416 | 76.0637 | 74.1954 | 76.1106 | 81.362 | 77.8174 | 79.7327 | 84.9841 | 2045 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
13 | 2023 | Residential, Commercial | Lighting | LED | A19 | Electricity | LED A19 | 2023$ | LED A-Type | 60W Equivalent A19 LED | 0.0010325 | 0.0018871 | 0.00079194 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0058173 | 0.0054765 | 0.022058 | Efficacy | lm/W | 50 | 208.9587 | 232.1401 | 125 | -0.41643 | 0.74596 | 3.0237 | 1 |  |  | 1.6252 | 3.4 | 8.2664 | 1 | 1 | 72.4416 | 76.0637 | 74.0668 | 75.8416 | 80.708 | 77.6889 | 79.4637 | 84.3301 | 2050 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.003157 | 0.002484 | 0.000155 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.079147 | 0.27601 | 0.13452 | Efficacy | lm/W | 50 | 106.015 | 123.0769 | 160 | -8.5149 | -17.2735 | 15.24 | 1 |  |  | 4.8218 | 15.8792 | 29.7441 | 1 | 1 | 72.4416 | 76.0637 | 77.2634 | 88.3208 | 102.1857 | 80.8855 | 91.9429 | 105.8078 | 2023 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030873 | 0.0024291 | 0.00015158 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.064005 | 0.22321 | 0.10879 | Efficacy | lm/W | 50 | 128.1998 | 148.8321 | 160 | -8.3269 | -16.892 | 14.9034 | 1 |  |  | 4.7153 | 15.5285 | 29.0872 | 1 | 1 | 72.4416 | 76.0637 | 77.1569 | 87.9701 | 101.5288 | 80.779 | 91.5922 | 105.1509 | 2030 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030585 | 0.0024065 | 0.00015016 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.055782 | 0.19453 | 0.094809 | Efficacy | lm/W | 50 | 145.7274 | 169.1805 | 160 | -8.2492 | -16.7345 | 14.7645 | 1 |  |  | 4.6714 | 15.3837 | 28.816 | 1 | 1 | 72.4416 | 76.0637 | 77.113 | 87.8253 | 101.2576 | 80.735 | 91.4474 | 104.8796 | 2035 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030297 | 0.0023838 | 0.00014875 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.049324 | 0.17201 | 0.083833 | Efficacy | lm/W | 50 | 163.255 | 189.529 | 160 | -8.1716 | -16.577 | 14.6255 | 1 |  |  | 4.6274 | 15.2389 | 28.5447 | 1 | 1 | 72.4416 | 76.0637 | 77.069 | 87.6805 | 100.9863 | 80.6911 | 91.3026 | 104.6084 | 2040 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030018 | 0.0023618 | 0.00014738 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.045258 | 0.15783 | 0.076922 | Efficacy | lm/W | 50 | 176.2826 | 204.6533 | 160 | -8.0962 | -16.4241 | 14.4906 | 1 |  |  | 4.5847 | 15.0983 | 28.2814 | 1 | 1 | 72.4416 | 76.0637 | 77.0263 | 87.5399 | 100.723 | 80.6484 | 91.162 | 104.3451 | 2045 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0029738 | 0.0023399 | 0.00014601 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.041751 | 0.1456 | 0.070961 | Efficacy | lm/W | 50 | 189.3103 | 219.7776 | 160 | -8.0208 | -16.2712 | 14.3557 | 1 |  |  | 4.542 | 14.9578 | 28.0181 | 1 | 1 | 72.4416 | 76.0637 | 76.9836 | 87.3994 | 100.4597 | 80.6057 | 91.0215 | 104.0818 | 2050 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.003157 | 0.002484 | 0.000155 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.079147 | 0.27601 | 0.13452 | Efficacy | lm/W | 50 | 106.015 | 123.0769 | 160 | -8.5149 | -17.2735 | 15.24 | 1 |  |  | 4.8218 | 15.8792 | 29.7441 | 1 | 1 | 72.4416 | 76.0637 | 77.2634 | 88.3208 | 102.1857 | 80.8855 | 91.9429 | 105.8078 | 2023 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030873 | 0.0024291 | 0.00015158 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.055657 | 0.19409 | 0.094596 | Efficacy | lm/W | 50 | 147.4298 | 171.1569 | 160 | -8.3269 | -16.892 | 14.9034 | 1 |  |  | 4.7153 | 15.5285 | 29.0872 | 1 | 1 | 72.4416 | 76.0637 | 77.1569 | 87.9701 | 101.5288 | 80.779 | 91.5922 | 105.1509 | 2030 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030585 | 0.0024065 | 0.00015016 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.048506 | 0.16915 | 0.082442 | Efficacy | lm/W | 50 | 167.5865 | 194.5576 | 160 | -8.2492 | -16.7345 | 14.7645 | 1 |  |  | 4.6714 | 15.3837 | 28.816 | 1 | 1 | 72.4416 | 76.0637 | 77.113 | 87.8253 | 101.2576 | 80.735 | 91.4474 | 104.8796 | 2035 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030297 | 0.0023838 | 0.00014875 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.042891 | 0.14957 | 0.072898 | Efficacy | lm/W | 50 | 187.7432 | 217.9583 | 160 | -8.1716 | -16.577 | 14.6255 | 1 |  |  | 4.6274 | 15.2389 | 28.5447 | 1 | 1 | 72.4416 | 76.0637 | 77.069 | 87.6805 | 100.9863 | 80.6911 | 91.3026 | 104.6084 | 2040 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030018 | 0.0023618 | 0.00014738 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.039355 | 0.13724 | 0.066888 | Efficacy | lm/W | 50 | 202.725 | 226.4236 | 160 | -8.0962 | -16.4241 | 14.4906 | 1 |  |  | 4.5847 | 15.0983 | 28.2814 | 1 | 1 | 72.4416 | 76.0637 | 77.0263 | 87.5399 | 100.723 | 80.6484 | 91.162 | 104.3451 | 2045 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0029738 | 0.0023399 | 0.00014601 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.036305 | 0.12661 | 0.061705 | Efficacy | lm/W | 50 | 217.7069 | 234.8888 | 160 | -8.0208 | -16.2712 | 14.3557 | 1 |  |  | 4.542 | 14.9578 | 28.0181 | 1 | 1 | 72.4416 | 76.0637 | 76.9836 | 87.3994 | 100.4597 | 80.6057 | 91.0215 | 104.0818 | 2050 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.003157 | 0.002484 | 0.000155 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.079147 | 0.27601 | 0.13452 | Efficacy | lm/W | 50 | 106.015 | 123.0769 | 160 | -8.5149 | -17.2735 | 15.24 | 1 |  |  | 4.8218 | 15.8792 | 29.7441 | 1 | 1 | 72.4416 | 76.0637 | 77.2634 | 88.3208 | 102.1857 | 80.8855 | 91.9429 | 105.8078 | 2023 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030873 | 0.0024291 | 0.00015158 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.049235 | 0.1717 | 0.083681 | Efficacy | lm/W | 50 | 166.6598 | 193.4817 | 160 | -8.3269 | -16.892 | 14.9034 | 1 |  |  | 4.7153 | 15.5285 | 29.0872 | 1 | 1 | 72.4416 | 76.0637 | 77.1569 | 87.9701 | 101.5288 | 80.779 | 91.5922 | 105.1509 | 2030 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030585 | 0.0024065 | 0.00015016 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.042909 | 0.14964 | 0.07293 | Efficacy | lm/W | 50 | 189.4456 | 219.9347 | 160 | -8.2492 | -16.7345 | 14.7645 | 1 |  |  | 4.6714 | 15.3837 | 28.816 | 1 | 1 | 72.4416 | 76.0637 | 77.113 | 87.8253 | 101.2576 | 80.735 | 91.4474 | 104.8796 | 2035 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030297 | 0.0023838 | 0.00014875 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.037942 | 0.13231 | 0.064487 | Efficacy | lm/W | 50 | 212.2315 | 246.3877 | 160 | -8.1716 | -16.577 | 14.6255 | 1 |  |  | 4.6274 | 15.2389 | 28.5447 | 1 | 1 | 72.4416 | 76.0637 | 77.069 | 87.6805 | 100.9863 | 80.6911 | 91.3026 | 104.6084 | 2040 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0030018 | 0.0023618 | 0.00014738 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.034814 | 0.12141 | 0.05917 | Efficacy | lm/W | 50 | 229.1674 | 248.1938 | 160 | -8.0962 | -16.4241 | 14.4906 | 1 |  |  | 4.5847 | 15.0983 | 28.2814 | 1 | 1 | 72.4416 | 76.0637 | 77.0263 | 87.5399 | 100.723 | 80.6484 | 91.162 | 104.3451 | 2045 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
14 | 2023 | Residential, Commercial | Lighting | LED | A21 | Electricity | LED A21 | 2023$ | LED A-Type | 100W Equivalent LED A Lamp | 0.0029738 | 0.0023399 | 0.00014601 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.032116 | 0.112 | 0.054586 | Efficacy | lm/W | 50 | 246.1034 | 250 | 160 | -8.0208 | -16.2712 | 14.3557 | 1 |  |  | 4.542 | 14.9578 | 28.0181 | 1 | 1 | 72.4416 | 76.0637 | 76.9836 | 87.3994 | 100.4597 | 80.6057 | 91.0215 | 104.0818 | 2050 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.013782 | 0.017101 | 0.21248 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.050752 | -0.21248 | -0.19464 | Efficacy | lm/W | 50 | 82.0273 | 100 | 125 | -14.7421 | 15.9262 | 25.9484 | 1 |  |  | 7.9463 | 21.4837 | 295.5901 | 1 | 1 | 72.4416 | 76.0637 | 80.3879 | 93.9253 | 368.0317 | 84.01 | 97.5474 | 371.6538 | 2023 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.013217 | 0.0164 | 0.20377 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.041698 | -0.17457 | -0.15991 | Efficacy | lm/W | 50 | 95.7449 | 116.7232 | 125 | -14.1375 | 15.2731 | 24.8843 | 1 |  |  | 7.6204 | 20.6027 | 283.4683 | 1 | 1 | 72.4416 | 76.0637 | 80.062 | 93.0443 | 355.9099 | 83.6841 | 96.6664 | 359.532 | 2030 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.013026 | 0.016163 | 0.20082 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.038338 | -0.1605 | -0.14703 | Efficacy | lm/W | 50 | 102.6324 | 125.1197 | 125 | -13.9334 | 15.0526 | 24.525 | 1 |  |  | 7.5104 | 20.3052 | 279.3754 | 1 | 1 | 72.4416 | 76.0637 | 79.952 | 92.7468 | 351.817 | 83.5741 | 96.3689 | 355.4391 | 2035 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.012835 | 0.015926 | 0.19788 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.0354 | -0.14821 | -0.13576 | Efficacy | lm/W | 50 | 109.5199 | 133.5163 | 125 | -13.7293 | 14.8321 | 24.1657 | 1 |  |  | 7.4003 | 20.0078 | 275.2825 | 1 | 1 | 72.4416 | 76.0637 | 79.842 | 92.4494 | 347.7241 | 83.464 | 96.0714 | 351.3461 | 2040 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.012651 | 0.015698 | 0.19504 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.03284 | -0.13749 | -0.12594 | Efficacy | lm/W | 50 | 116.3654 | 141.8617 | 125 | -13.5323 | 14.6193 | 23.8191 | 1 |  |  | 7.2942 | 19.7207 | 271.3336 | 1 | 1 | 72.4416 | 76.0637 | 79.7358 | 92.1623 | 343.7752 | 83.3579 | 95.7844 | 347.3973 | 2045 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.012467 | 0.015469 | 0.1922 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.030564 | -0.12796 | -0.11721 | Efficacy | lm/W | 50 | 123.2109 | 150.2072 | 125 | -13.3354 | 14.4065 | 23.4724 | 1 |  |  | 7.188 | 19.4337 | 267.3847 | 1 | 1 | 72.4416 | 76.0637 | 79.6296 | 91.8753 | 339.8263 | 83.2517 | 95.4974 | 343.4484 | 2050 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.013782 | 0.013782 | 0.013782 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.050752 | -0.21248 | -0.19464 | Efficacy | lm/W | 50 | 82.0273 | 100 | 125 | -14.7421 | 15.9262 | 25.9484 | 1 |  |  | 7.9463 | 17.0224 | 28.5082 | 1 | 1 | 72.4416 | 76.0637 | 80.3879 | 89.464 | 100.9498 | 84.01 | 93.0861 | 104.5719 | 2023 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.013217 | 0.013217 | 0.013217 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.041698 | -0.17457 | -0.15991 | Efficacy | lm/W | 50 | 95.7449 | 134.2316 | 125 | -14.1375 | 15.2731 | 24.8843 | 1 |  |  | 7.6204 | 16.3244 | 27.3392 | 1 | 1 | 72.4416 | 76.0637 | 80.062 | 88.766 | 99.7808 | 83.6841 | 92.3881 | 103.4028 | 2030 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.013026 | 0.016163 | 0.20082 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.035497 | -0.14861 | -0.13613 | Efficacy | lm/W | 50 | 110.8464 | 143.8877 | 125 | -13.9334 | 15.0526 | 24.525 | 1 |  |  | 7.5104 | 20.3052 | 279.3754 | 1 | 1 | 72.4416 | 76.0637 | 79.952 | 92.7468 | 351.817 | 83.5741 | 96.3689 | 355.4391 | 2035 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.012835 | 0.015926 | 0.19788 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.030783 | -0.12888 | -0.11805 | Efficacy | lm/W | 50 | 125.9478 | 153.5437 | 125 | -13.7293 | 14.8321 | 24.1657 | 1 |  |  | 7.4003 | 20.0078 | 275.2825 | 1 | 1 | 72.4416 | 76.0637 | 79.842 | 92.4494 | 347.7241 | 83.464 | 96.0714 | 351.3461 | 2040 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.012651 | 0.015698 | 0.19504 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.028556 | -0.11955 | -0.10952 | Efficacy | lm/W | 50 | 133.8202 | 163.141 | 125 | -13.5323 | 14.6193 | 23.8191 | 1 |  |  | 7.2942 | 19.7207 | 271.3336 | 1 | 1 | 72.4416 | 76.0637 | 79.7358 | 92.1623 | 343.7752 | 83.3579 | 95.7844 | 347.3973 | 2045 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.012467 | 0.015469 | 0.1922 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.026577 | -0.11127 | -0.10193 | Efficacy | lm/W | 50 | 141.6926 | 172.7382 | 125 | -13.3354 | 14.4065 | 23.4724 | 1 |  |  | 7.188 | 19.4337 | 267.3847 | 1 | 1 | 72.4416 | 76.0637 | 79.6296 | 91.8753 | 339.8263 | 83.2517 | 95.4974 | 343.4484 | 2050 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.013782 | 0.013782 | 0.013782 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.050752 | -0.21248 | -0.19464 | Efficacy | lm/W | 50 | 82.0273 | 100 | 125 | -14.7421 | 15.9262 | 25.9484 | 1 |  |  | 7.9463 | 17.0224 | 28.5082 | 1 | 1 | 72.4416 | 76.0637 | 80.3879 | 89.464 | 100.9498 | 84.01 | 93.0861 | 104.5719 | 2023 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.013217 | 0.013217 | 0.013217 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.041698 | -0.17457 | -0.15991 | Efficacy | lm/W | 50 | 95.7449 | 151.7401 | 125 | -14.1375 | 15.2731 | 24.8843 | 1 |  |  | 7.6204 | 16.3244 | 27.3392 | 1 | 1 | 72.4416 | 76.0637 | 80.062 | 88.766 | 99.7808 | 83.6841 | 92.3881 | 103.4028 | 2030 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.013026 | 0.016163 | 0.20082 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.033048 | -0.13836 | -0.12674 | Efficacy | lm/W | 50 | 119.0604 | 162.6556 | 125 | -13.9334 | 15.0526 | 24.525 | 1 |  |  | 7.5104 | 20.3052 | 279.3754 | 1 | 1 | 72.4416 | 76.0637 | 79.952 | 92.7468 | 351.817 | 83.5741 | 96.3689 | 355.4391 | 2035 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.012835 | 0.015926 | 0.19788 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.027231 | -0.11401 | -0.10443 | Efficacy | lm/W | 50 | 142.3758 | 173.5712 | 125 | -13.7293 | 14.8321 | 24.1657 | 1 |  |  | 7.4003 | 20.0078 | 275.2825 | 1 | 1 | 72.4416 | 76.0637 | 79.842 | 92.4494 | 347.7241 | 83.464 | 96.0714 | 351.3461 | 2040 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.012651 | 0.015698 | 0.19504 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.025261 | -0.10576 | -0.096879 | Efficacy | lm/W | 50 | 151.275 | 184.4202 | 125 | -13.5323 | 14.6193 | 23.8191 | 1 |  |  | 7.2942 | 19.7207 | 271.3336 | 1 | 1 | 72.4416 | 76.0637 | 79.7358 | 92.1623 | 343.7752 | 83.3579 | 95.7844 | 347.3973 | 2045 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
15 | 2023 | Residential, Commercial | Lighting | LED | PAR38 | Electricity | LED PAR38 | 2023$ | LED - Reflector | LED PAR 38 | 0.012467 | 0.015469 | 0.1922 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.023511 | -0.09843 | -0.090165 | Efficacy | lm/W | 50 | 160.1742 | 195.2693 | 125 | -13.3354 | 14.4065 | 23.4724 | 1 |  |  | 7.188 | 19.4337 | 267.3847 | 1 | 1 | 72.4416 | 76.0637 | 79.6296 | 91.8753 | 339.8263 | 83.2517 | 95.4974 | 343.4484 | 2050 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit).
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.001901 | 0.001219 | 0.009184 | Light Output | Lumens | 600 | 683.0769 | 650 | 1600 | -0.014919 | 0.004457 | -0.075722 | Efficacy | lm/W | 53.8462 | 78.5538 | 90.2778 | 150 | 3.9588 | 6.0319 | 12.0849 | 1 |  |  | 4.0854 | 7.2147 | 12.41 | 1 | 1 | 0 | 0 | 4.0854 | 7.2147 | 12.41 | 4.0854 | 7.2147 | 12.41 | 2023 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0015595 | 0.001 | 0.0075341 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.010485 | 0.0031324 | -0.053218 | Efficacy | lm/W | 53.8462 | 91.6905 | 105.3751 | 150 | 3.2476 | 4.9483 | 9.9138 | 1 |  |  | 3.2999 | 5.8855 | 9.9313 | 1 | 1 | 0 | 0 | 3.2999 | 5.8855 | 9.9313 | 3.2999 | 5.8855 | 9.9313 | 2030 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0014673 | 0.0009409 | 0.0070888 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0092035 | 0.0027495 | -0.046713 | Efficacy | lm/W | 53.8462 | 98.2863 | 112.9553 | 150 | 3.0557 | 4.6558 | 9.3279 | 1 |  |  | 3.1049 | 5.5377 | 9.3444 | 1 | 1 | 0 | 0 | 3.1049 | 5.5377 | 9.3444 | 3.1049 | 5.5377 | 9.3444 | 2035 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0013752 | 0.0008818 | 0.0066436 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.008083 | 0.0024148 | -0.041026 | Efficacy | lm/W | 53.8462 | 104.8821 | 120.5355 | 150 | 2.8638 | 4.3634 | 8.742 | 1 |  |  | 2.9099 | 5.1898 | 8.7575 | 1 | 1 | 0 | 0 | 2.9099 | 5.1898 | 8.7575 | 2.9099 | 5.1898 | 8.7575 | 2040 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0012833 | 0.00082292 | 0.0061999 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0070995 | 0.002121 | -0.036034 | Efficacy | lm/W | 53.8462 | 111.4378 | 128.0696 | 150 | 2.6725 | 4.072 | 8.1583 | 1 |  |  | 2.7155 | 4.8433 | 8.1727 | 1 | 1 | 0 | 0 | 2.7155 | 4.8433 | 8.1727 | 2.7155 | 4.8433 | 8.1727 | 2045 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0011915 | 0.00076404 | 0.0057563 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0062253 | 0.0018598 | -0.031597 | Efficacy | lm/W | 53.8462 | 117.9934 | 135.6037 | 150 | 2.4813 | 3.7807 | 7.5745 | 1 |  |  | 2.5212 | 4.4967 | 7.5879 | 1 | 1 | 0 | 0 | 2.5212 | 4.4967 | 7.5879 | 2.5212 | 4.4967 | 7.5879 | 2050 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.001901 | 0.001219 | 0.009184 | Light Output | Lumens | 600 | 683.0769 | 650 | 1600 | -0.014919 | 0.004457 | -0.075722 | Efficacy | lm/W | 53.8462 | 78.5538 | 90.2778 | 150 | 3.9588 | 6.0319 | 12.0849 | 1 |  |  | 4.0854 | 7.2147 | 12.41 | 1 | 1 | 0 | 0 | 4.0854 | 7.2147 | 12.41 | 4.0854 | 7.2147 | 12.41 | 2023 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0015595 | 0.001 | 0.0075341 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0091176 | 0.0027239 | -0.046277 | Efficacy | lm/W | 53.8462 | 105.4441 | 121.1813 | 150 | 3.2476 | 4.9483 | 9.9138 | 1 |  |  | 3.2999 | 5.8855 | 9.9313 | 1 | 1 | 0 | 0 | 3.2999 | 5.8855 | 9.9313 | 3.2999 | 5.8855 | 9.9313 | 2030 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0014673 | 0.0009409 | 0.0070888 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0080031 | 0.0023909 | -0.04062 | Efficacy | lm/W | 53.8462 | 113.0292 | 129.8986 | 150 | 3.0557 | 4.6558 | 9.3279 | 1 |  |  | 3.1049 | 5.5377 | 9.3444 | 1 | 1 | 0 | 0 | 3.1049 | 5.5377 | 9.3444 | 3.1049 | 5.5377 | 9.3444 | 2035 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0013752 | 0.0008818 | 0.0066436 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0070287 | 0.0020998 | -0.035675 | Efficacy | lm/W | 53.8462 | 120.6144 | 138.6159 | 150 | 2.8638 | 4.3634 | 8.742 | 1 |  |  | 2.9099 | 5.1898 | 8.7575 | 1 | 1 | 0 | 0 | 2.9099 | 5.1898 | 8.7575 | 2.9099 | 5.1898 | 8.7575 | 2040 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0012833 | 0.00082292 | 0.0061999 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0061735 | 0.0018443 | -0.031334 | Efficacy | lm/W | 53.8462 | 128.1534 | 147.28 | 150 | 2.6725 | 4.072 | 8.1583 | 1 |  |  | 2.7155 | 4.8433 | 8.1727 | 1 | 1 | 0 | 0 | 2.7155 | 4.8433 | 8.1727 | 2.7155 | 4.8433 | 8.1727 | 2045 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0011915 | 0.00076404 | 0.0057563 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0054133 | 0.0016172 | -0.027475 | Efficacy | lm/W | 53.8462 | 135.6925 | 155.9442 | 150 | 2.4813 | 3.7807 | 7.5745 | 1 |  |  | 2.5212 | 4.4967 | 7.5879 | 1 | 1 | 0 | 0 | 2.5212 | 4.4967 | 7.5879 | 2.5212 | 4.4967 | 7.5879 | 2050 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.001901 | 0.001219 | 0.009184 | Light Output | Lumens | 600 | 683.0769 | 650 | 1600 | -0.014919 | 0.004457 | -0.075722 | Efficacy | lm/W | 53.8462 | 78.5538 | 90.2778 | 150 | 3.9588 | 6.0319 | 12.0849 | 1 |  |  | 4.0854 | 7.2147 | 12.41 | 1 | 1 | 0 | 0 | 4.0854 | 7.2147 | 12.41 | 4.0854 | 7.2147 | 12.41 | 2023 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0015595 | 0.001 | 0.0075341 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0080656 | 0.0024096 | -0.040937 | Efficacy | lm/W | 53.8462 | 119.1976 | 136.9876 | 150 | 3.2476 | 4.9483 | 9.9138 | 1 |  |  | 3.2999 | 5.8855 | 9.9313 | 1 | 1 | 0 | 0 | 3.2999 | 5.8855 | 9.9313 | 3.2999 | 5.8855 | 9.9313 | 2030 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0014673 | 0.0009409 | 0.0070888 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0070797 | 0.002115 | -0.035933 | Efficacy | lm/W | 53.8462 | 127.7722 | 146.8419 | 150 | 3.0557 | 4.6558 | 9.3279 | 1 |  |  | 3.1049 | 5.5377 | 9.3444 | 1 | 1 | 0 | 0 | 3.1049 | 5.5377 | 9.3444 | 3.1049 | 5.5377 | 9.3444 | 2035 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0013752 | 0.0008818 | 0.0066436 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0062177 | 0.0018575 | -0.031558 | Efficacy | lm/W | 53.8462 | 136.3468 | 156.6962 | 150 | 2.8638 | 4.3634 | 8.742 | 1 |  |  | 2.9099 | 5.1898 | 8.7575 | 1 | 1 | 0 | 0 | 2.9099 | 5.1898 | 8.7575 | 2.9099 | 5.1898 | 8.7575 | 2040 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0012833 | 0.00082292 | 0.0061999 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0054612 | 0.0016315 | -0.027718 | Efficacy | lm/W | 53.8462 | 144.8691 | 166.4905 | 150 | 2.6725 | 4.072 | 8.1583 | 1 |  |  | 2.7155 | 4.8433 | 8.1727 | 1 | 1 | 0 | 0 | 2.7155 | 4.8433 | 8.1727 | 2.7155 | 4.8433 | 8.1727 | 2045 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
16 | 2023 | Residential, Commercial | Lighting | LED | BR30 | Electricity | LED BR30 | 2023$ | LED - Reflector | LED BR30 | 0.0011915 | 0.00076404 | 0.0057563 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0047887 | 0.0014306 | -0.024305 | Efficacy | lm/W | 53.8462 | 153.3915 | 176.2848 | 150 | 2.4813 | 3.7807 | 7.5745 | 1 |  |  | 2.5212 | 4.4967 | 7.5879 | 1 | 1 | 0 | 0 | 2.5212 | 4.4967 | 7.5879 | 2.5212 | 4.4967 | 7.5879 | 2050 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | 0 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 350 | 600 | 900 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 1 |  |  | 175000 | 300000 | 450000 | 1.0536 | 1.0672 | 0 | 0 | 184382.7279 | 316084.6763 | 474127.0145 | 186759.8821 | 320159.7979 | 480239.6968 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 350 | 600 | 900 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 1 |  |  | 175000 | 300000 | 450000 | 1.0536 | 1.0672 | 0 | 0 | 184382.7279 | 316084.6763 | 474127.0145 | 186759.8821 | 320159.7979 | 480239.6968 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 350 | 600 | 900 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 1 |  |  | 175000 | 300000 | 450000 | 1.0536 | 1.0672 | 0 | 0 | 184382.7279 | 316084.6763 | 474127.0145 | 186759.8821 | 320159.7979 | 480239.6968 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 350 | 600 | 900 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 1 |  |  | 175000 | 300000 | 450000 | 1.0536 | 1.0672 | 0 | 0 | 184382.7279 | 316084.6763 | 474127.0145 | 186759.8821 | 320159.7979 | 480239.6968 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 350 | 600 | 900 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 1 |  |  | 175000 | 300000 | 450000 | 1.0536 | 1.0672 | 0 | 0 | 184382.7279 | 316084.6763 | 474127.0145 | 186759.8821 | 320159.7979 | 480239.6968 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 350 | 600 | 900 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 1 |  |  | 175000 | 300000 | 450000 | 1.0536 | 1.0672 | 0 | 0 | 184382.7279 | 316084.6763 | 474127.0145 | 186759.8821 | 320159.7979 | 480239.6968 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 350 | 600 | 900 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 1 |  |  | 175000 | 300000 | 450000 | 1.0536 | 1.0672 | 0 | 0 | 184382.7279 | 316084.6763 | 474127.0145 | 186759.8821 | 320159.7979 | 480239.6968 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 381.5 | 654 | 981 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 7.4796e-07 | 7.63e-06 | -2.18e-06 | 1 |  |  | 190750 | 327000 | 490500 | 1.0536 | 1.0672 | 0 | 0 | 200977.1734 | 344532.2972 | 516798.4458 | 203568.2715 | 348974.1797 | 523461.2695 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 393.75 | 675 | 1012.5 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 7.7197e-07 | 7.875e-06 | -2.25e-06 | 1 |  |  | 196875 | 337500 | 506250 | 1.0536 | 1.0672 | 0 | 0 | 207430.5688 | 355595.2609 | 533392.8913 | 210104.8674 | 360179.7726 | 540269.6589 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 406 | 696 | 1044 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 7.9599e-07 | 8.12e-06 | -2.32e-06 | 1 |  |  | 203000 | 348000 | 522000 | 1.0536 | 1.0672 | 0 | 0 | 213883.9643 | 366658.2246 | 549987.3368 | 216641.4632 | 371385.3655 | 557078.0483 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 411.25 | 705 | 1057.5 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 8.0628e-07 | 8.225e-06 | -2.35e-06 | 1 |  |  | 205625 | 352500 | 528750 | 1.0536 | 1.0672 | 0 | 0 | 216649.7052 | 371399.4947 | 557099.242 | 219442.8615 | 376187.7625 | 564281.6438 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 416.5 | 714 | 1071 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 8.1658e-07 | 8.33e-06 | -2.38e-06 | 1 |  |  | 208250 | 357000 | 535500 | 1.0536 | 1.0672 | 0 | 0 | 219415.4462 | 376140.7649 | 564211.1473 | 222244.2597 | 380990.1595 | 571485.2392 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 350 | 600 | 900 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 1 |  |  | 175000 | 300000 | 450000 | 1.0536 | 1.0672 | 0 | 0 | 184382.7279 | 316084.6763 | 474127.0145 | 186759.8821 | 320159.7979 | 480239.6968 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 413 | 708 | 1062 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 8.0971e-07 | 8.26e-06 | -2.36e-06 | 1 |  |  | 206500 | 354000 | 531000 | 1.0536 | 1.0672 | 0 | 0 | 217571.6189 | 372979.9181 | 559469.8771 | 220376.6609 | 377788.5615 | 566682.8422 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 437.5 | 750 | 1125 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 8.5775e-07 | 8.75e-06 | -2.5e-06 | 1 |  |  | 218750 | 375000 | 562500 | 1.0536 | 1.0672 | 0 | 0 | 230478.4098 | 395105.8454 | 592658.7681 | 233449.8526 | 400199.7474 | 600299.621 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 462 | 792 | 1188 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 9.0578e-07 | 9.24e-06 | -2.64e-06 | 1 |  |  | 231000 | 396000 | 594000 | 1.0536 | 1.0672 | 0 | 0 | 243385.2008 | 417231.7728 | 625847.6591 | 246523.0444 | 422610.9332 | 633916.3998 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 472.5 | 810 | 1215 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 9.2637e-07 | 9.45e-06 | -2.7e-06 | 1 |  |  | 236250 | 405000 | 607500 | 1.0536 | 1.0672 | 0 | 0 | 248916.6826 | 426714.3131 | 640071.4696 | 252125.8408 | 432215.7271 | 648323.5907 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
17 | 2023 | Commercial | HVAC | Centrifugal Chiller | Water-Cooled | Electricity | Centrifugal Chillers Water-Cooled | 2023$ |  | Commercial Centrifugal Chillers (Water-Cooled) | 483 | 828 | 1242 | Cooling Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 9.4695e-07 | 9.66e-06 | -2.76e-06 | 1 |  |  | 241500 | 414000 | 621000 | 1.0536 | 1.0672 | 0 | 0 | 254448.1645 | 436196.8534 | 654295.28 | 257728.6373 | 441820.5211 | 662730.7816 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish between oil bearing and magnetic bearing chillers.
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
18 | 2023 | Commercial | Refrigeration | Ice Machine | Standard | Electricity | Commercial Ice Machine Standard | 2023$ |  | Commercial Ice Maker | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 1 |  |  | 1898.6812 | 2171.9209 | 3097.0667 | 1.17 | 1.46 | 0 | 0 | 2221.457 | 2541.1475 | 3623.568 | 2772.0745 | 3171.0046 | 4521.7174 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2023 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2030 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2035 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2040 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2045 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2050 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2023 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2030 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2035 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2040 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2045 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2050 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2023 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2030 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2035 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2040 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2045 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
19 | 2023 | Commercial | HVAC | Furnace | Oil-Fired | Oil | Commercial Oil-Fired Furnaces | 2023$ |  | Commercial Oil-Fired Furnace | 4.2169 | 5.2711 | 6.3253 | Heating Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 1 |  |  | 4015.5283 | 5019.4103 | 6023.2924 | 1.08 | 1.12 | 0 | 0 | 4336.7705 | 5420.9632 | 6505.1558 | 4497.3917 | 5621.7396 | 6746.0875 | 2050 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2023 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2030 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2035 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2040 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 88 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2045 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 81 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2050 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2023 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2030 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2035 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2040 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 91.5 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2045 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 88 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2050 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2023 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2030 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2035 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2040 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2045 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
20 | 2023 | Commercial | HVAC | Furnace | Gas-Fired | Gas | Commercial Gas-Fired Furnaces | 2023$ |  | Commercial Gas-Fired Furnaces | 13.5765 | 16.9706 | 20.3647 | Heating Capacity | MBH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 1 |  |  | 3183.5294 | 3979.4117 | 4775.2941 | 1.16 | 1.22 | 0 | 0 | 3692.8941 | 4616.1176 | 5539.3411 | 3883.9058 | 4854.8823 | 5825.8587 | 2050 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upper bound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
21 | 2023 | Commercial | HVAC | Boiler | Electric Steam | Electricity | Boiler - Electric Steam | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.14 | 1.18 | 0 | 0 | 10269.12 | 12836.4 | 15403.68 | 10629.44 | 13286.8 | 15944.16 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
22 | 2023 | Commercial | HVAC | Boiler | Electric Hot Water | Electricity | Boiler - Electric Hot Water | 2023$ |  | Commercial Electric Boilers | 16 | 20 | 24 | Heating Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 1 |  |  | 9008 | 11260 | 13512 | 1.1 | 1.13 | 0 | 0 | 9908.8 | 12386 | 14863.2 | 10179.04 | 12723.8 | 15268.56 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upper bound value was used as the high value
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2023 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2030 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2035 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2040 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2045 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2050 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2023 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2030 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2035 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2040 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2045 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2050 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2023 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2030 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2035 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2040 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2045 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
23 | 2023 | Commercial | HVAC | Water Heater | Oil-Fired | Oil | Commercial Oil-Fired Water Heater | 2023$ |  | Commercial Oil-Fired Water Heater | 96 | 120 | 144 | Heating Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 1 |  |  | 25360 | 31700 | 38040 | 1.03 | 1.06 | 0 | 0 | 26120.8 | 32651 | 39181.2 | 26881.6 | 33602 | 40322.4 | 2050 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 14.8 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 14.8 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.55 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.675 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.8 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.05 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.3 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 14.8 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.25 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.5 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 17 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
24 | 2023 | Commercial | HVAC | Air Conditioner | Electric Rooftop Unit (RTU) | Electricity | Electric Rooftop Unit (RTU) AC | 2023$ |  | Electric Rooftop Unit (RTU) Air Conditioner | 965.21 | 1162.22 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 8.3 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 17.5 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 1 |  |  | 4847.7707 | 7605.5389 | 11709.1447 | 1.15 | 1.16 | 0 | 0 | 5574.9363 | 8746.3697 | 13465.5164 | 5623.414 | 8822.4251 | 13582.6079 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
25 | 2023 | Commercial | HVAC | Air Conditioner | Packaged Terminal | Electricity | Commercial Packaged Terminal Air Conditioner | 2023$ |  | Commercial Packaged Terminal Air Conditioner | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 828.09 | 1506.05 | 6727.5 | 1 |  |  | 828.09 | 1506.05 | 6727.5 | 1 | 1 | 877 | 1050 | 1705.09 | 2383.05 | 7604.5 | 1878.09 | 2556.05 | 7777.5 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | 0 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 137.619 | 172.0238 | 206.4286 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 214.2857 | 267.8571 | 321.4286 | 1 |  |  | 1452.8571 | 1816.0714 | 2179.2857 | 1 | 1 | 977 | 1150 | 2429.8571 | 2793.0714 | 3156.2857 | 2602.8571 | 2966.0714 | 3329.2857 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 137.619 | 172.0238 | 206.4286 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 214.2857 | 267.8571 | 321.4286 | 1 |  |  | 1452.8571 | 1816.0714 | 2179.2857 | 1 | 1 | 977 | 1150 | 2429.8571 | 2793.0714 | 3156.2857 | 2602.8571 | 2966.0714 | 3329.2857 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.625 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.75 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.85 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.95 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 137.619 | 172.0238 | 206.4286 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 214.2857 | 267.8571 | 321.4286 | 1 |  |  | 1452.8571 | 1816.0714 | 2179.2857 | 1 | 1 | 977 | 1150 | 2429.8571 | 2793.0714 | 3156.2857 | 2602.8571 | 2966.0714 | 3329.2857 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.75 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 12 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 12.2 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
26 | 2023 | Commercial | HVAC | Heat Pump | Packaged Terminal | Electricity | Heat Pump - Packaged Terminal | 2023$ |  | Packaged Terminal Heat Pumps | 138.4685 | 173.0857 | 207.7028 | Cooling Capacity | kBtu/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 12.4 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1 |  |  | 1461.8254 | 1827.2817 | 2192.7381 | 1 | 1 | 977 | 1150 | 2438.8254 | 2804.2817 | 3169.7381 | 2611.8254 | 2977.2817 | 3342.7381 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.51407 | 0.52521 | 1.7771 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 333 | 333 | 333 | 4.3e-05 | 2042.0794 | 4679.9385 | 1 |  |  | 411.2552 | 2462.2466 | 6101.5905 | 1.09 | 1.16 | 0 | 0 | 448.2682 | 2683.8488 | 6650.7336 | 477.0561 | 2856.206 | 7077.8449 | 2023 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. 3) Metric 1, airflow, refers to System Airflow. Metric 2, Annual Energy Use, refers to Annual Fan Energy Use.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 296.0093 | 296.0093 | 296.0093 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2030 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 263.1277 | 263.1277 | 263.1277 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2035 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 233.8987 | 233.8987 | 233.8987 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2040 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 207.9165 | 207.9165 | 207.9165 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2045 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 184.8205 | 184.8205 | 184.8205 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2050 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.51407 | 0.52521 | 1.7771 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 333 | 333 | 333 | 4.3e-05 | 2042.0794 | 4679.9385 | 1 |  |  | 411.2552 | 2462.2466 | 6101.5905 | 1.09 | 1.16 | 0 | 0 | 448.2682 | 2683.8488 | 6650.7336 | 477.0561 | 2856.206 | 7077.8449 | 2023 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 296.0093 | 296.0093 | 296.0093 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2030 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 263.1277 | 263.1277 | 263.1277 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2035 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 233.8987 | 233.8987 | 233.8987 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2040 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 207.9165 | 207.9165 | 207.9165 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2045 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 184.8205 | 184.8205 | 184.8205 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2050 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.51407 | 0.52521 | 1.7771 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 333 | 333 | 333 | 4.3e-05 | 2042.0794 | 4679.9385 | 1 |  |  | 411.2552 | 2462.2466 | 6101.5905 | 1.09 | 1.16 | 0 | 0 | 448.2682 | 2683.8488 | 6650.7336 | 477.0561 | 2856.206 | 7077.8449 | 2023 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 296.0093 | 296.0093 | 296.0093 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2030 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 263.1277 | 263.1277 | 263.1277 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2035 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 233.8987 | 233.8987 | 233.8987 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2040 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 207.9165 | 207.9165 | 207.9165 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2045 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
27 | 2023 | Commercial | HVAC | Fan Coil Unit | Standard | Electricity | Fan Coil Unit - Standard | 2023$ |  | Commercial Fan Coil Units | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 184.8205 | 184.8205 | 184.8205 | 4.8373e-05 | 2297.2668 | 5264.7646 | 1 |  |  | 462.6475 | 2769.94 | 6864.0727 | 1.09 | 1.16 | 0 | 0 | 504.2858 | 3019.2346 | 7481.8392 | 536.6712 | 3213.1304 | 7962.3243 | 2050 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric.
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2023 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2030 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2035 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2040 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2045 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2050 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2023 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2030 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2035 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2040 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2045 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2050 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2023 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2030 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2035 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2040 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2045 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
28 | 2023 | Commercial | HVAC | Water Heater | Electric Booster | Electricity | Water Heater - Electric Booster | 2023$ |  | Commercial Electric Booster Water Heaters | 80.4471 | 107.7997 | 167.0917 | Nominal Volume | Gallons | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 1 |  |  | -3439.9059 | 6412.1368 | 28799.6931 | 1.01 | 1.44 | 0 | 0 | -3474.3049 | 6476.2581 | 29087.6901 | -4953.4645 | 9233.4769 | 41471.5581 | 2050 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBtu/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
29 | 2023 | Commercial | HVAC | Gas-fired Chiller | Water Cooled | Gas | Gas-Fired Chillers (Water-Cooled) | 2023$ |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | 827.9137 | 865 | 823.8889 | Cooling Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 1 |  |  | 419917.2667 | 447500 | 498555.5556 | 1.0502 | 1.0664 | 0 | 0 | 440984.7428 | 469951.3167 | 523568.3571 | 447803.6103 | 477218.0891 | 531664.2002 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 12 | 0.9296 | 2023 | There is no available efficiency data.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2023 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2030 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2035 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2040 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2045 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2050 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2023 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2030 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2035 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2040 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2045 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2050 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2023 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2030 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2035 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2040 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2045 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
30 | 2023 | Commercial | Refrigeration | Beverage Merchandisers | Standard | Electricity | Beverage Merchandisers - Standard | 2023$ |  | Commercial Beverage Merchandisers | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 1 |  |  | 1697.207 | 2121.5087 | 2545.8105 | 1.2 | 1.22 | 0 | 0 | 2036.6484 | 2545.8105 | 3054.9726 | 2070.5925 | 2588.2407 | 3105.8888 | 2050 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric.
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2023 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2030 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2035 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2040 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2045 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2050 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2023 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2030 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2035 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2040 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2045 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2050 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2023 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2030 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2035 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2040 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2045 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
31 | 2023 | Commercial | Refrigeration | Refrigerated Vending Machine | Standard | Electricity | Refrigerated Vending Machine - Standard | 2023$ |  | Commercial Refrigerated Vending Machines | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 1 |  |  | 3953.4954 | 4941.8692 | 5930.243 | 1.09 | 1.11 | 0 | 0 | 4309.3099 | 5386.6374 | 6463.9649 | 4388.3798 | 5485.4748 | 6582.5698 | 2050 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Online Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3)
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
32 | 2023 | Commercial | HVAC | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | 2023$/ton |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | 0 | 0 | 0 | Cooling Capacity | Tons | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 11 | tons | ton | 31428.54 | 40641.9761 | 46359.8438 | 1.01 | 1.03 | 0 | 0 | 31742.8254 | 41048.3959 | 46823.4422 | 32371.3962 | 41861.2354 | 47750.6391 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | 0 | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric.
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
33 | 2023 | Commercial | Cooking | Induction Cooktop |  | Electricity | Induction Cooktop | 2023$ |  |  | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 1 |  |  | 777.5786 | 2015.7373 | 2822.9151 | 1.05 | 1.06 | 0 | 0 | 816.4576 | 2116.5241 | 2964.0608 | 824.2333 | 2136.6815 | 2992.29 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high".
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2023 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2030 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2035 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2040 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2045 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2050 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2023 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2030 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2035 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2040 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2045 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2050 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2023 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2030 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2035 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2040 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2045 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
34 | 2023 | Commercial | Cooking | Induction Wells |  | Electricity | Induction Wells | 2023$ |  |  | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 1 |  |  | 2547.52 | 3184.4 | 3821.28 | 1.02 | 1.02 | 0 | 0 | 2598.4704 | 3248.088 | 3897.7056 | 2598.4704 | 3248.088 | 3897.7056 | 2050 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.52 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.73 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.72 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.71 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.7 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.69 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.645 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.72 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.71 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.7 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.69 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.68 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.71 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.7 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.69 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.68 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
35 | 2023 | Commercial | HVAC | Scroll Chiller | Air-Cooled | Electricity | Scroll Chiller Air-Cooled | 2023$ |  | Commercial Scroll Chillers (Air-Cooled) | 600 | 693.9655 | 1120.1587 | Cooling Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.67 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 1 |  |  | 54000 | 73482.7586 | 105711.9047 | 1.0925 | 1.1947 | 0 | 0 | 58997.0271 | 80282.6722 | 115494.2243 | 64512.1448 | 87787.5993 | 126290.7724 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.79 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.755 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.72 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.7 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.68 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.79 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.78 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.7325 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.685 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.6655 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.646 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.81 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.71 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.65 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.631 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
36 | 2023 | Commercial | HVAC | Screw Chiller | Air-Cooled | Electricity | Screw Chiller Air-Cooled | 2023$ |  | Commercial Screw Chillers (Air-Cooled) | 610 | 650 | 504.6875 | Cooling Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.612 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 1 |  |  | 123750 | 169500 | 257453.125 | 1.0832 | 1.1136 | 0 | 0 | 134051.2225 | 183609.5533 | 278884.0901 | 137810.3424 | 188758.4084 | 286704.6733 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
37 | 2023 | Commercial | HVAC | Scroll Chiller | Water-Cooled | Electricity | Scroll Chiller Water-Cooled | 2023$ |  |  | 500 | 471.3462 | 600 | Cooling Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 1 |  |  | 27500 | 29935.5769 | 49000 | 1.2112 | 1.3216 | 0 | 0 | 33308.6955 | 36258.7279 | 59350.0393 | 36343.0747 | 39561.8512 | 64756.7512 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
38 | 2023 | Commercial | HVAC | Screw Chiller | Water-Cooled | Electricity | Screw Chiller Water-Cooled | 2023$ |  |  | 336.5385 | 410 | 456 | Cooling Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 1 |  |  | 100375.0001 | 111500 | 121600 | 1.1732 | 1.2285 | 0 | 0 | 117764.6498 | 130817.0206 | 142666.8135 | 123308.1414 | 136974.9216 | 149382.5154 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
39 | 2023 | Commercial | HVAC | Reciprocating Chiller | Air-Cooled | Electricity | Reciprocating Chiller Air-Cooled | 2023$ |  | Commercial Reciprocating Chillers (Air-Cooled Only) | 432.5 | 659.1837 | 667.1642 | Cooling Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 1 |  |  | 53525 | 70040.8163 | 78201.4925 | 1.1377 | 1.1842 | 0 | 0 | 60893.1064 | 79682.4452 | 88966.4981 | 63386.1676 | 82944.7719 | 92608.9287 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 35 | 0.7642 | 2023 | There is no available efficiency data.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2023 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2030 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2035 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2040 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2045 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2050 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2023 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22306 | 22306 | 21190.5 | 21190.5 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2030 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22034.25 | 22034.25 | 20932.5 | 20932.5 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2035 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21762.5 | 21762.5 | 20674.5 | 20674.5 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2040 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21504.5 | 21504.5 | 20429.25 | 20429.25 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2045 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21246.5 | 21246.5 | 20184 | 20184 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2050 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2023 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21734 | 21734 | 20647 | 20647 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2030 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21190.5 | 21190.5 | 20131 | 20131 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2035 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20647 | 20647 | 19615 | 19615 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2040 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20131 | 20131 | 19124.5 | 19124.5 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2045 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
40 | 2023 | Commercial | HVAC | Variable Air Volume System | Standard | Electricity | Variable Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Variable Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 19615 | 19615 | 18634 | 18634 | 6544.8 | 8181 | 9817.2 | 16.3 | thousand CFM | thousand CFM | 106680.24 | 133350.3 | 160020.36 | 1.02 | 1.13 | 0 | 0 | 108813.8448 | 136017.306 | 163220.7672 | 120548.6712 | 150685.839 | 180823.0068 | 2050 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2023 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2030 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2035 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2040 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2045 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2050 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2023 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21339 | 21339 | 20272 | 20272 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2030 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21079 | 21079 | 20025.25 | 20025.25 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2035 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20819 | 20819 | 19778.5 | 19778.5 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2040 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20572.25 | 20572.25 | 19543.75 | 19543.75 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2045 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20325.5 | 20325.5 | 19309 | 19309 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2050 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2023 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20792 | 20792 | 19752 | 19752 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2030 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20272 | 20272 | 19258.5 | 19258.5 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2035 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 19752 | 19752 | 18765 | 18765 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2040 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 19258.5 | 19258.5 | 18295.5 | 18295.5 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2045 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
41 | 2023 | Commercial | HVAC | Constant Air Volume System | Standard | Electricity | Constant Air Volume System - Standard | 2023$/thousand CFM |  | Commercial Constant Air Volume System | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 18765 | 18765 | 17826 | 17826 | 4649.736 | 5812.17 | 6974.604 | 16.3 | thousand CFM | thousand CFM | 75790.6968 | 94738.371 | 113686.0452 | 1.02 | 1.14 | 0 | 0 | 77306.5107 | 96633.1384 | 115959.7661 | 86401.3944 | 108001.7429 | 129602.0915 | 2050 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | 0 | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligible.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3942 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3766.75 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3591.5 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3451.5 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3311.5 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3504 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3153.5 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2035 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 2803 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2040 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 2523 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2045 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
42 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet - Large | Large | Electricity | Hot Food Holding Cabinet - Large | 2023$ |  | Hot Food Holding Cabinet - Large | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 2243 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 1 |  |  | 5247.8243 | 6559.7804 | 7871.7365 | 1.02 | 1.03 | 0 | 0 | 5352.7808 | 6690.976 | 8029.1712 | 5405.2591 | 6756.5738 | 8107.8886 | 2050 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1785.75 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1706.375 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1627 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1579.875 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1532.75 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1587.5 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1428.75 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2035 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1270 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2040 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1175.75 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2045 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
43 | 2023 | Commercial | Cooking | Hot Food Holding Cabinet | Small and Medium | Electricity | Hot Food Holding Cabinet - Small and Medium | 2023$ |  | Hot Food Holding Cabinet - Small and Medium | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1081.5 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 1 |  |  | 2313.2791 | 2891.5989 | 3469.9187 | 1.05 | 1.07 | 0 | 0 | 2428.9431 | 3036.1788 | 3643.4146 | 2475.2086 | 3094.0108 | 3712.813 | 2050 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost information available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2023 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2030 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2035 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2040 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2045 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2050 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2023 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1170.5 | 1102 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2030 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1142.75 | 1075.75 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2035 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1115 | 1049.5 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2040 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1090 | 1026 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2045 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1065 | 1002.5 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2050 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2023 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1109 | 1044 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2030 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1053.5 | 991.5 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2035 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 998 | 939 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2040 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 948 | 892 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2045 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
44 | 2023 | Commercial | Refrigeration | Compressor Rack Systems | Standard | Electricity | Compressor Rack Systems Standard | 2023$ |  | Compressor Rack Systems | 0 | 0 | 0 | Cooling Capacity | kBtu/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 898 | 845 | 1160 | 533618.08 | 667022.6 | 800427.12 | 1 |  |  | 533618.08 | 667022.6 | 800427.12 | 1.05 | 1.07 | 0 | 0 | 560298.984 | 700373.73 | 840448.476 | 570971.3456 | 713714.182 | 856457.0184 | 2050 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upper bounds for both metrics, respectively.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 100.5 | 100.5 | 81.5 | 81.5 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 98.25 | 98.25 | 79.75 | 79.75 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 96 | 96 | 78 | 78 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 93.75 | 93.75 | 76.25 | 76.25 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 91.5 | 91.5 | 74.5 | 74.5 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 95 | 95 | 77 | 77 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 90.5 | 90.5 | 73.5 | 73.5 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 86 | 86 | 70 | 70 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 81.5 | 81.5 | 66.5 | 66.5 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
45 | 2023 | Commercial | Refrigeration | Condensers | Standard | Electricity | Condensers Standard | 2023$ |  | Condensers | 33.0684 | 41.3355 | 49.6026 | Cooling Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy Use | MMWh/y | 77 | 77 | 63 | 63 | 2922.08 | 5130.59 | 7339.1 | 1 |  |  | 50540.6232 | 64653.769 | 78766.9148 | 1.1 | 1.16 | 0 | 0 | 55594.6856 | 71119.1459 | 86643.6063 | 58627.1229 | 74998.3721 | 91369.6212 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | 0 | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.004214 | 0.009752 | 0.012619 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.6286 | 0.18645 | -3.4594 | Efficacy | lm/W | 43.75 | 134.3013 | 145.3846 | 180.5237 | -167.033 | 73.3194 | 712.6457 | 1 |  |  | 129.6451 | 278.7716 | 481.4962 | 1 | 1 | 99 | 99 | 228.6451 | 377.7716 | 580.4962 | 228.6451 | 377.7716 | 580.4962 | 2023 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0037323 | 0.0086374 | 0.011177 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.2091 | 0.13842 | -2.5683 | Efficacy | lm/W | 43.75 | 160.2241 | 173.4467 | 180.5237 | -147.9413 | 64.9391 | 631.1911 | 1 |  |  | 114.8268 | 246.9083 | 426.4617 | 1 | 1 | 99 | 99 | 213.8268 | 345.9083 | 525.4617 | 213.8268 | 345.9083 | 525.4617 | 2030 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0036377 | 0.0084183 | 0.010893 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.0906 | 0.12486 | -2.3166 | Efficacy | lm/W | 43.75 | 173.1263 | 187.4137 | 180.5237 | -144.1898 | 63.2923 | 615.1853 | 1 |  |  | 111.9151 | 240.6472 | 415.6475 | 1 | 1 | 99 | 99 | 210.9151 | 339.6472 | 514.6475 | 210.9151 | 339.6472 | 514.6475 | 2035 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0035431 | 0.0081993 | 0.01061 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.98853 | 0.11317 | -2.0998 | Efficacy | lm/W | 43.75 | 186.0285 | 201.3807 | 180.5237 | -140.4383 | 61.6456 | 599.1796 | 1 |  |  | 109.0033 | 234.3861 | 404.8332 | 1 | 1 | 99 | 99 | 208.0033 | 333.3861 | 503.8332 | 208.0033 | 333.3861 | 503.8332 | 2040 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0034525 | 0.0079897 | 0.010339 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.90104 | 0.10316 | -1.914 | Efficacy | lm/W | 43.75 | 198.8737 | 215.286 | 180.5237 | -136.8476 | 60.0694 | 583.8597 | 1 |  |  | 106.2163 | 228.3933 | 394.4824 | 1 | 1 | 99 | 99 | 205.2163 | 327.3933 | 493.4824 | 205.2163 | 327.3933 | 493.4824 | 2045 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0033619 | 0.00778 | 0.010067 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.82416 | 0.094355 | -1.7507 | Efficacy | lm/W | 43.75 | 211.719 | 229.1913 | 180.5237 | -133.2568 | 58.4933 | 568.5398 | 1 |  |  | 103.4293 | 222.4005 | 384.1316 | 1 | 1 | 99 | 99 | 202.4293 | 321.4005 | 483.1316 | 202.4293 | 321.4005 | 483.1316 | 2050 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.004214 | 0.009752 | 0.012619 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.6286 | 0.18645 | -3.4594 | Efficacy | lm/W | 43.75 | 134.3013 | 145.3846 | 180.5237 | -167.033 | 73.3194 | 712.6457 | 1 |  |  | 129.6451 | 278.7716 | 481.4962 | 1 | 1 | 99 | 99 | 228.6451 | 377.7716 | 580.4962 | 228.6451 | 377.7716 | 580.4962 | 2023 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0037323 | 0.0086374 | 0.011177 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.0514 | 0.12036 | -2.2333 | Efficacy | lm/W | 43.75 | 184.2577 | 199.4638 | 180.5237 | -147.9413 | 64.9391 | 631.1911 | 1 |  |  | 114.8268 | 246.9083 | 426.4617 | 1 | 1 | 99 | 99 | 213.8268 | 345.9083 | 525.4617 | 213.8268 | 345.9083 | 525.4617 | 2030 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0036377 | 0.0084183 | 0.010893 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.94833 | 0.10857 | -2.0144 | Efficacy | lm/W | 43.75 | 199.0952 | 212.577 | 180.5237 | -144.1898 | 63.2923 | 615.1853 | 1 |  |  | 111.9151 | 240.6472 | 415.6475 | 1 | 1 | 99 | 99 | 210.9151 | 339.6472 | 514.6475 | 210.9151 | 339.6472 | 514.6475 | 2035 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0035431 | 0.0081993 | 0.01061 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.85959 | 0.098411 | -1.8259 | Efficacy | lm/W | 43.75 | 213.9328 | 225.6903 | 180.5237 | -140.4383 | 61.6456 | 599.1796 | 1 |  |  | 109.0033 | 234.3861 | 404.8332 | 1 | 1 | 99 | 99 | 208.0033 | 333.3861 | 503.8332 | 208.0033 | 333.3861 | 503.8332 | 2040 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0034525 | 0.0079897 | 0.010339 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.80574 | 0.092246 | -1.7115 | Efficacy | lm/W | 43.75 | 222.3961 | 232.643 | 180.5237 | -136.8476 | 60.0694 | 583.8597 | 1 |  |  | 106.2163 | 228.3933 | 394.4824 | 1 | 1 | 99 | 99 | 205.2163 | 327.3933 | 493.4824 | 205.2163 | 327.3933 | 493.4824 | 2045 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0033619 | 0.00778 | 0.010067 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.75583 | 0.086532 | -1.6055 | Efficacy | lm/W | 43.75 | 230.8595 | 239.5957 | 180.5237 | -133.2568 | 58.4933 | 568.5398 | 1 |  |  | 103.4293 | 222.4005 | 384.1316 | 1 | 1 | 99 | 99 | 202.4293 | 321.4005 | 483.1316 | 202.4293 | 321.4005 | 483.1316 | 2050 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.004214 | 0.009752 | 0.012619 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.6286 | 0.18645 | -3.4594 | Efficacy | lm/W | 43.75 | 134.3013 | 145.3846 | 180.5237 | -167.033 | 73.3194 | 712.6457 | 1 |  |  | 129.6451 | 278.7716 | 481.4962 | 1 | 1 | 99 | 99 | 228.6451 | 377.7716 | 580.4962 | 228.6451 | 377.7716 | 580.4962 | 2023 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0037323 | 0.0086374 | 0.011177 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.93004 | 0.10648 | -1.9756 | Efficacy | lm/W | 43.75 | 208.2913 | 225.4808 | 180.5237 | -147.9413 | 64.9391 | 631.1911 | 1 |  |  | 114.8268 | 246.9083 | 426.4617 | 1 | 1 | 99 | 99 | 213.8268 | 345.9083 | 525.4617 | 213.8268 | 345.9083 | 525.4617 | 2030 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0036377 | 0.0084183 | 0.010893 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.8389 | 0.096043 | -1.782 | Efficacy | lm/W | 43.75 | 225.0642 | 237.7404 | 180.5237 | -144.1898 | 63.2923 | 615.1853 | 1 |  |  | 111.9151 | 240.6472 | 415.6475 | 1 | 1 | 99 | 99 | 210.9151 | 339.6472 | 514.6475 | 210.9151 | 339.6472 | 514.6475 | 2035 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0035431 | 0.0081993 | 0.01061 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.76041 | 0.087056 | -1.6153 | Efficacy | lm/W | 43.75 | 241.837 | 250 | 180.5237 | -140.4383 | 61.6456 | 599.1796 | 1 |  |  | 109.0033 | 234.3861 | 404.8332 | 1 | 1 | 99 | 99 | 208.0033 | 333.3861 | 503.8332 | 208.0033 | 333.3861 | 503.8332 | 2040 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0034525 | 0.0079897 | 0.010339 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.72867 | 0.083422 | -1.5478 | Efficacy | lm/W | 43.75 | 245.9185 | 250 | 180.5237 | -136.8476 | 60.0694 | 583.8597 | 1 |  |  | 106.2163 | 228.3933 | 394.4824 | 1 | 1 | 99 | 99 | 205.2163 | 327.3933 | 493.4824 | 205.2163 | 327.3933 | 493.4824 | 2045 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
46 | 2023 | Commercial | Lighting | LED | High/Low-Bays | Electricity | LED High/Low-Bay | 2023$ |  | LED High-Bay Integrated Luminaire | 0.0033619 | 0.00778 | 0.010067 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.69797 | 0.079907 | -1.4826 | Efficacy | lm/W | 43.75 | 250 | 250 | 180.5237 | -133.2568 | 58.4933 | 568.5398 | 1 |  |  | 103.4293 | 222.4005 | 384.1316 | 1 | 1 | 99 | 99 | 202.4293 | 321.4005 | 483.1316 | 202.4293 | 321.4005 | 483.1316 | 2050 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | 200 | 200 | 0 | 297.4496 | 0 | 1 |  |  | 0 | 297.4496 | 0 | 1 | 1 | 45 | 45 | 45 | 342.4496 | 45 | 45 | 342.4496 | 45 | 2023 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | 200 | 200 | 0 | 297.4496 | 0 | 1 |  |  | 0 | 297.4496 | 0 | 1 | 1 | 45 | 45 | 45 | 342.4496 | 45 | 45 | 342.4496 | 45 | 2030 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | 200 | 200 | 0 | 297.4496 | 0 | 1 |  |  | 0 | 297.4496 | 0 | 1 | 1 | 45 | 45 | 45 | 342.4496 | 45 | 45 | 342.4496 | 45 | 2035 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | 200 | 200 | 0 | 297.4496 | 0 | 1 |  |  | 0 | 297.4496 | 0 | 1 | 1 | 45 | 45 | 45 | 342.4496 | 45 | 45 | 342.4496 | 45 | 2040 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | 200 | 200 | 0 | 297.4496 | 0 | 1 |  |  | 0 | 297.4496 | 0 | 1 | 1 | 45 | 45 | 45 | 342.4496 | 45 | 45 | 342.4496 | 45 | 2045 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | 200 | 200 | 0 | 297.4496 | 0 | 1 |  |  | 0 | 297.4496 | 0 | 1 | 1 | 45 | 45 | 45 | 342.4496 | 45 | 45 | 342.4496 | 45 | 2050 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | 200 | 200 | 0 | 297.4496 | 0 | 1 |  |  | 0 | 297.4496 | 0 | 1 | 1 | 45 | 45 | 45 | 342.4496 | 45 | 45 | 342.4496 | 45 | 2023 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 140.5 | 200 | 200 | 0 | 255.3109 | 0 | 1 |  |  | 0 | 255.3109 | 0 | 1 | 1 | 45 | 45 | 45 | 300.3109 | 45 | 45 | 300.3109 | 45 | 2030 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 145.5 | 200 | 200 | 0 | 252.8322 | 0 | 1 |  |  | 0 | 252.8322 | 0 | 1 | 1 | 45 | 45 | 45 | 297.8322 | 45 | 45 | 297.8322 | 45 | 2035 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 150.5 | 200 | 200 | 0 | 250.3534 | 0 | 1 |  |  | 0 | 250.3534 | 0 | 1 | 1 | 45 | 45 | 45 | 295.3534 | 45 | 45 | 295.3534 | 45 | 2040 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 158 | 200 | 200 | 0 | 247.8747 | 0 | 1 |  |  | 0 | 247.8747 | 0 | 1 | 1 | 45 | 45 | 45 | 292.8747 | 45 | 45 | 292.8747 | 45 | 2045 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 165.5 | 200 | 200 | 0 | 245.3959 | 0 | 1 |  |  | 0 | 245.3959 | 0 | 1 | 1 | 45 | 45 | 45 | 290.3959 | 45 | 45 | 290.3959 | 45 | 2050 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | 200 | 200 | 0 | 297.4496 | 0 | 1 |  |  | 0 | 297.4496 | 0 | 1 | 1 | 45 | 45 | 45 | 342.4496 | 45 | 45 | 342.4496 | 45 | 2023 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 150 | 200 | 200 | 0 | 213.1722 | 0 | 1 |  |  | 0 | 213.1722 | 0 | 1 | 1 | 45 | 45 | 45 | 258.1722 | 45 | 45 | 258.1722 | 45 | 2030 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 160 | 200 | 200 | 0 | 208.2147 | 0 | 1 |  |  | 0 | 208.2147 | 0 | 1 | 1 | 45 | 45 | 45 | 253.2147 | 45 | 45 | 253.2147 | 45 | 2035 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 170 | 200 | 200 | 0 | 203.2572 | 0 | 1 |  |  | 0 | 203.2572 | 0 | 1 | 1 | 45 | 45 | 45 | 248.2572 | 45 | 45 | 248.2572 | 45 | 2040 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 185 | 200 | 200 | 0 | 198.2997 | 0 | 1 |  |  | 0 | 198.2997 | 0 | 1 | 1 | 45 | 45 | 45 | 243.2997 | 45 | 45 | 243.2997 | 45 | 2045 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
47 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel Connected with Integrated Controls | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 200 | 200 | 200 | 0 | 193.3422 | 0 | 1 |  |  | 0 | 193.3422 | 0 | 1 | 1 | 45 | 45 | 45 | 238.3422 | 45 | 45 | 238.3422 | 45 | 2050 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | 125 | 125 | 0 | 202.2657 | 0 | 1 |  |  | 0 | 202.2657 | 0 | 1 | 1 | 20 | 20 | 20 | 222.2657 | 20 | 20 | 222.2657 | 20 | 2023 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | 125 | 125 | 0 | 202.2657 | 0 | 1 |  |  | 0 | 202.2657 | 0 | 1 | 1 | 20 | 20 | 20 | 222.2657 | 20 | 20 | 222.2657 | 20 | 2030 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | 125 | 125 | 0 | 202.2657 | 0 | 1 |  |  | 0 | 202.2657 | 0 | 1 | 1 | 20 | 20 | 20 | 222.2657 | 20 | 20 | 222.2657 | 20 | 2035 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | 125 | 125 | 0 | 202.2657 | 0 | 1 |  |  | 0 | 202.2657 | 0 | 1 | 1 | 20 | 20 | 20 | 222.2657 | 20 | 20 | 222.2657 | 20 | 2040 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | 125 | 125 | 0 | 202.2657 | 0 | 1 |  |  | 0 | 202.2657 | 0 | 1 | 1 | 20 | 20 | 20 | 222.2657 | 20 | 20 | 222.2657 | 20 | 2045 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | 125 | 125 | 0 | 202.2657 | 0 | 1 |  |  | 0 | 202.2657 | 0 | 1 | 1 | 20 | 20 | 20 | 222.2657 | 20 | 20 | 222.2657 | 20 | 2050 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | 200 | 200 | 0 | 202.2657 | 0 | 1 |  |  | 0 | 202.2657 | 0 | 1 | 1 | 20 | 20 | 20 | 222.2657 | 20 | 20 | 222.2657 | 20 | 2023 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 137.5 | 200 | 200 | 0 | 172.9904 | 0 | 1 |  |  | 0 | 172.9904 | 0 | 1 | 1 | 20 | 20 | 20 | 192.9904 | 20 | 20 | 192.9904 | 20 | 2030 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 142.5 | 200 | 200 | 0 | 171.6597 | 0 | 1 |  |  | 0 | 171.6597 | 0 | 1 | 1 | 20 | 20 | 20 | 191.6597 | 20 | 20 | 191.6597 | 20 | 2035 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 147.5 | 200 | 200 | 0 | 170.329 | 0 | 1 |  |  | 0 | 170.329 | 0 | 1 | 1 | 20 | 20 | 20 | 190.329 | 20 | 20 | 190.329 | 20 | 2040 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 155 | 200 | 200 | 0 | 168.9983 | 0 | 1 |  |  | 0 | 168.9983 | 0 | 1 | 1 | 20 | 20 | 20 | 188.9983 | 20 | 20 | 188.9983 | 20 | 2045 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 162.5 | 200 | 200 | 0 | 167.6676 | 0 | 1 |  |  | 0 | 167.6676 | 0 | 1 | 1 | 20 | 20 | 20 | 187.6676 | 20 | 20 | 187.6676 | 20 | 2050 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | 200 | 200 | 0 | 202.2657 | 0 | 1 |  |  | 0 | 202.2657 | 0 | 1 | 1 | 20 | 20 | 20 | 222.2657 | 20 | 20 | 222.2657 | 20 | 2023 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 150 | 200 | 200 | 0 | 143.7151 | 0 | 1 |  |  | 0 | 143.7151 | 0 | 1 | 1 | 20 | 20 | 20 | 163.7151 | 20 | 20 | 163.7151 | 20 | 2030 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 160 | 200 | 200 | 0 | 141.0537 | 0 | 1 |  |  | 0 | 141.0537 | 0 | 1 | 1 | 20 | 20 | 20 | 161.0537 | 20 | 20 | 161.0537 | 20 | 2035 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 170 | 200 | 200 | 0 | 138.3923 | 0 | 1 |  |  | 0 | 138.3923 | 0 | 1 | 1 | 20 | 20 | 20 | 158.3923 | 20 | 20 | 158.3923 | 20 | 2040 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 185 | 200 | 200 | 0 | 135.731 | 0 | 1 |  |  | 0 | 135.731 | 0 | 1 | 1 | 20 | 20 | 20 | 155.731 | 20 | 20 | 155.731 | 20 | 2045 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
48 | 2023 | Commercial | Lighting | LED | Troffer & Panel | Electricity | LED Troffer or Panel with Dimming | 2023$ |  | 4 ft Linear Systems LED Integrated Luminaire | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 200 | 200 | 200 | 0 | 133.0696 | 0 | 1 |  |  | 0 | 133.0696 | 0 | 1 | 1 | 20 | 20 | 20 | 153.0696 | 20 | 20 | 153.0696 | 20 | 2050 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | 0 | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 68.8618 | 70.5769 | 70.5769 | 0 | 31.7516 | 0 | 1 |  |  | 0 | 31.7516 | 0 | 1 | 1 | 66 | 69.3 | 66 | 97.7516 | 66 | 69.3 | 101.0516 | 69.3 | 2023 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 71.6649 | 73.4499 | 70.5769 | 0 | 31.3555 | 0 | 1 |  |  | 0 | 31.3555 | 0 | 1 | 1 | 66 | 69.3 | 66 | 97.3555 | 66 | 69.3 | 100.6555 | 69.3 | 2030 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 73.4974 | 75.328 | 70.5769 | 0 | 31.1189 | 0 | 1 |  |  | 0 | 31.1189 | 0 | 1 | 1 | 66 | 69.3 | 66 | 97.1189 | 66 | 69.3 | 100.4189 | 69.3 | 2035 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 75.3299 | 77.2061 | 70.5769 | 0 | 30.8822 | 0 | 1 |  |  | 0 | 30.8822 | 0 | 1 | 1 | 66 | 69.3 | 66 | 96.8822 | 66 | 69.3 | 100.1822 | 69.3 | 2040 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 77.2561 | 79.1803 | 70.5769 | 0 | 30.6571 | 0 | 1 |  |  | 0 | 30.6571 | 0 | 1 | 1 | 66 | 69.3 | 66 | 96.6571 | 66 | 69.3 | 99.9571 | 69.3 | 2045 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 79.1823 | 81.1545 | 70.5769 | 0 | 30.4321 | 0 | 1 |  |  | 0 | 30.4321 | 0 | 1 | 1 | 66 | 69.3 | 66 | 96.4321 | 66 | 69.3 | 99.7321 | 69.3 | 2050 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 68.8618 | 70.5769 | 70.5769 | 0 | 31.7516 | 0 | 1 |  |  | 0 | 31.7516 | 0 | 1 | 1 | 66 | 69.3 | 66 | 97.7516 | 66 | 69.3 | 101.0516 | 69.3 | 2023 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 71.6649 | 73.4499 | 70.5769 | 0 | 31.3555 | 0 | 1 |  |  | 0 | 31.3555 | 0 | 1 | 1 | 66 | 69.3 | 66 | 97.3555 | 66 | 69.3 | 100.6555 | 69.3 | 2030 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 73.4974 | 75.328 | 70.5769 | 0 | 31.1189 | 0 | 1 |  |  | 0 | 31.1189 | 0 | 1 | 1 | 66 | 69.3 | 66 | 97.1189 | 66 | 69.3 | 100.4189 | 69.3 | 2035 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 75.3299 | 77.2061 | 70.5769 | 0 | 30.8822 | 0 | 1 |  |  | 0 | 30.8822 | 0 | 1 | 1 | 66 | 69.3 | 66 | 96.8822 | 66 | 69.3 | 100.1822 | 69.3 | 2040 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 77.2561 | 79.1803 | 70.5769 | 0 | 30.6571 | 0 | 1 |  |  | 0 | 30.6571 | 0 | 1 | 1 | 66 | 69.3 | 66 | 96.6571 | 66 | 69.3 | 99.9571 | 69.3 | 2045 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 79.1823 | 81.1545 | 70.5769 | 0 | 30.4321 | 0 | 1 |  |  | 0 | 30.4321 | 0 | 1 | 1 | 66 | 69.3 | 66 | 96.4321 | 66 | 69.3 | 99.7321 | 69.3 | 2050 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 68.8618 | 70.5769 | 70.5769 | 0 | 31.7516 | 0 | 1 |  |  | 0 | 31.7516 | 0 | 1 | 1 | 66 | 69.3 | 66 | 97.7516 | 66 | 69.3 | 101.0516 | 69.3 | 2023 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 71.6649 | 73.4499 | 70.5769 | 0 | 31.3555 | 0 | 1 |  |  | 0 | 31.3555 | 0 | 1 | 1 | 66 | 69.3 | 66 | 97.3555 | 66 | 69.3 | 100.6555 | 69.3 | 2030 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 73.4974 | 75.328 | 70.5769 | 0 | 31.1189 | 0 | 1 |  |  | 0 | 31.1189 | 0 | 1 | 1 | 66 | 69.3 | 66 | 97.1189 | 66 | 69.3 | 100.4189 | 69.3 | 2035 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 75.3299 | 77.2061 | 70.5769 | 0 | 30.8822 | 0 | 1 |  |  | 0 | 30.8822 | 0 | 1 | 1 | 66 | 69.3 | 66 | 96.8822 | 66 | 69.3 | 100.1822 | 69.3 | 2040 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 77.2561 | 79.1803 | 70.5769 | 0 | 30.6571 | 0 | 1 |  |  | 0 | 30.6571 | 0 | 1 | 1 | 66 | 69.3 | 66 | 96.6571 | 66 | 69.3 | 99.9571 | 69.3 | 2045 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
49 | 2023 | Commercial | Lighting | CFL | Spiral | Electricity | 100W Equivalent CFL Bare Spiral | 2023$ |  | 100W Equivalent CFL Bare Spiral | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 79.1823 | 81.1545 | 70.5769 | 0 | 30.4321 | 0 | 1 |  |  | 0 | 30.4321 | 0 | 1 | 1 | 66 | 69.3 | 66 | 96.4321 | 66 | 69.3 | 99.7321 | 69.3 | 2050 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 367.1439 | 0 | 1 |  |  | 0 | 367.1439 | 0 | 1 | 1 | 132 | 164 | 132 | 499.1439 | 132 | 164 | 531.1439 | 164 | 2023 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 356.6256 | 0 | 1 |  |  | 0 | 356.6256 | 0 | 1 | 1 | 132 | 164 | 132 | 488.6256 | 132 | 164 | 520.6256 | 164 | 2030 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 350.3414 | 0 | 1 |  |  | 0 | 350.3414 | 0 | 1 | 1 | 132 | 164 | 132 | 482.3414 | 132 | 164 | 514.3414 | 164 | 2035 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 344.0572 | 0 | 1 |  |  | 0 | 344.0572 | 0 | 1 | 1 | 132 | 164 | 132 | 476.0572 | 132 | 164 | 508.0572 | 164 | 2040 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 338.0803 | 0 | 1 |  |  | 0 | 338.0803 | 0 | 1 | 1 | 132 | 164 | 132 | 470.0803 | 132 | 164 | 502.0803 | 164 | 2045 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 332.1033 | 0 | 1 |  |  | 0 | 332.1033 | 0 | 1 | 1 | 132 | 164 | 132 | 464.1033 | 132 | 164 | 496.1033 | 164 | 2050 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 367.1439 | 0 | 1 |  |  | 0 | 367.1439 | 0 | 1 | 1 | 132 | 164 | 132 | 499.1439 | 132 | 164 | 531.1439 | 164 | 2023 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 356.6256 | 0 | 1 |  |  | 0 | 356.6256 | 0 | 1 | 1 | 132 | 164 | 132 | 488.6256 | 132 | 164 | 520.6256 | 164 | 2030 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 350.3414 | 0 | 1 |  |  | 0 | 350.3414 | 0 | 1 | 1 | 132 | 164 | 132 | 482.3414 | 132 | 164 | 514.3414 | 164 | 2035 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 344.0572 | 0 | 1 |  |  | 0 | 344.0572 | 0 | 1 | 1 | 132 | 164 | 132 | 476.0572 | 132 | 164 | 508.0572 | 164 | 2040 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 338.0803 | 0 | 1 |  |  | 0 | 338.0803 | 0 | 1 | 1 | 132 | 164 | 132 | 470.0803 | 132 | 164 | 502.0803 | 164 | 2045 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 332.1033 | 0 | 1 |  |  | 0 | 332.1033 | 0 | 1 | 1 | 132 | 164 | 132 | 464.1033 | 132 | 164 | 496.1033 | 164 | 2050 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 367.1439 | 0 | 1 |  |  | 0 | 367.1439 | 0 | 1 | 1 | 132 | 164 | 132 | 499.1439 | 132 | 164 | 531.1439 | 164 | 2023 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 356.6256 | 0 | 1 |  |  | 0 | 356.6256 | 0 | 1 | 1 | 132 | 164 | 132 | 488.6256 | 132 | 164 | 520.6256 | 164 | 2030 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 350.3414 | 0 | 1 |  |  | 0 | 350.3414 | 0 | 1 | 1 | 132 | 164 | 132 | 482.3414 | 132 | 164 | 514.3414 | 164 | 2035 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 344.0572 | 0 | 1 |  |  | 0 | 344.0572 | 0 | 1 | 1 | 132 | 164 | 132 | 476.0572 | 132 | 164 | 508.0572 | 164 | 2040 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 338.0803 | 0 | 1 |  |  | 0 | 338.0803 | 0 | 1 | 1 | 132 | 164 | 132 | 470.0803 | 132 | 164 | 502.0803 | 164 | 2045 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
50 | 2023 | Commercial | Lighting | High-Bay | Metal Halide | Electricity | High-Bay Metal Halide | 2023$ |  | High-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | 42000 | 42000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 332.1033 | 0 | 1 |  |  | 0 | 332.1033 | 0 | 1 | 1 | 132 | 164 | 132 | 464.1033 | 132 | 164 | 496.1033 | 164 | 2050 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 390.5538 | 0 | 1 |  |  | 0 | 390.5538 | 0 | 1 | 1 | 132 | 164 | 132 | 522.5538 | 132 | 164 | 554.5538 | 164 | 2023 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 379.18 | 0 | 1 |  |  | 0 | 379.18 | 0 | 1 | 1 | 132 | 164 | 132 | 511.18 | 132 | 164 | 543.18 | 164 | 2030 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 372.3846 | 0 | 1 |  |  | 0 | 372.3846 | 0 | 1 | 1 | 132 | 164 | 132 | 504.3846 | 132 | 164 | 536.3846 | 164 | 2035 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 365.5893 | 0 | 1 |  |  | 0 | 365.5893 | 0 | 1 | 1 | 132 | 164 | 132 | 497.5893 | 132 | 164 | 529.5893 | 164 | 2040 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 359.1262 | 0 | 1 |  |  | 0 | 359.1262 | 0 | 1 | 1 | 132 | 164 | 132 | 491.1262 | 132 | 164 | 523.1262 | 164 | 2045 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 352.6631 | 0 | 1 |  |  | 0 | 352.6631 | 0 | 1 | 1 | 132 | 164 | 132 | 484.6631 | 132 | 164 | 516.6631 | 164 | 2050 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 390.5538 | 0 | 1 |  |  | 0 | 390.5538 | 0 | 1 | 1 | 132 | 164 | 132 | 522.5538 | 132 | 164 | 554.5538 | 164 | 2023 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 379.18 | 0 | 1 |  |  | 0 | 379.18 | 0 | 1 | 1 | 132 | 164 | 132 | 511.18 | 132 | 164 | 543.18 | 164 | 2030 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 372.3846 | 0 | 1 |  |  | 0 | 372.3846 | 0 | 1 | 1 | 132 | 164 | 132 | 504.3846 | 132 | 164 | 536.3846 | 164 | 2035 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 365.5893 | 0 | 1 |  |  | 0 | 365.5893 | 0 | 1 | 1 | 132 | 164 | 132 | 497.5893 | 132 | 164 | 529.5893 | 164 | 2040 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 359.1262 | 0 | 1 |  |  | 0 | 359.1262 | 0 | 1 | 1 | 132 | 164 | 132 | 491.1262 | 132 | 164 | 523.1262 | 164 | 2045 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 352.6631 | 0 | 1 |  |  | 0 | 352.6631 | 0 | 1 | 1 | 132 | 164 | 132 | 484.6631 | 132 | 164 | 516.6631 | 164 | 2050 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 390.5538 | 0 | 1 |  |  | 0 | 390.5538 | 0 | 1 | 1 | 132 | 164 | 132 | 522.5538 | 132 | 164 | 554.5538 | 164 | 2023 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 379.18 | 0 | 1 |  |  | 0 | 379.18 | 0 | 1 | 1 | 132 | 164 | 132 | 511.18 | 132 | 164 | 543.18 | 164 | 2030 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 372.3846 | 0 | 1 |  |  | 0 | 372.3846 | 0 | 1 | 1 | 132 | 164 | 132 | 504.3846 | 132 | 164 | 536.3846 | 164 | 2035 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 365.5893 | 0 | 1 |  |  | 0 | 365.5893 | 0 | 1 | 1 | 132 | 164 | 132 | 497.5893 | 132 | 164 | 529.5893 | 164 | 2040 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 359.1262 | 0 | 1 |  |  | 0 | 359.1262 | 0 | 1 | 1 | 132 | 164 | 132 | 491.1262 | 132 | 164 | 523.1262 | 164 | 2045 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
51 | 2023 | Commercial | Lighting | High-Bay | Sodium Vapor | Electricity | High-Bay Sodium Vapor | 2023$ |  | High-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | 29000 | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 352.6631 | 0 | 1 |  |  | 0 | 352.6631 | 0 | 1 | 1 | 132 | 164 | 132 | 484.6631 | 132 | 164 | 516.6631 | 164 | 2050 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 107.006 | 0 | 1 |  |  | 0 | 107.006 | 0 | 1 | 1 | 99 | 132 | 99 | 206.006 | 99 | 132 | 239.006 | 132 | 2023 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 104.8571 | 0 | 1 |  |  | 0 | 104.8571 | 0 | 1 | 1 | 99 | 132 | 99 | 203.8571 | 99 | 132 | 236.8571 | 132 | 2030 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 103.5732 | 0 | 1 |  |  | 0 | 103.5732 | 0 | 1 | 1 | 99 | 132 | 99 | 202.5732 | 99 | 132 | 235.5732 | 132 | 2035 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 102.2893 | 0 | 1 |  |  | 0 | 102.2893 | 0 | 1 | 1 | 99 | 132 | 99 | 201.2893 | 99 | 132 | 234.2893 | 132 | 2040 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 101.0682 | 0 | 1 |  |  | 0 | 101.0682 | 0 | 1 | 1 | 99 | 132 | 99 | 200.0682 | 99 | 132 | 233.0682 | 132 | 2045 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 99.8471 | 0 | 1 |  |  | 0 | 99.8471 | 0 | 1 | 1 | 99 | 132 | 99 | 198.8471 | 99 | 132 | 231.8471 | 132 | 2050 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 107.006 | 0 | 1 |  |  | 0 | 107.006 | 0 | 1 | 1 | 99 | 132 | 99 | 206.006 | 99 | 132 | 239.006 | 132 | 2023 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 104.8571 | 0 | 1 |  |  | 0 | 104.8571 | 0 | 1 | 1 | 99 | 132 | 99 | 203.8571 | 99 | 132 | 236.8571 | 132 | 2030 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 103.5732 | 0 | 1 |  |  | 0 | 103.5732 | 0 | 1 | 1 | 99 | 132 | 99 | 202.5732 | 99 | 132 | 235.5732 | 132 | 2035 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 102.2893 | 0 | 1 |  |  | 0 | 102.2893 | 0 | 1 | 1 | 99 | 132 | 99 | 201.2893 | 99 | 132 | 234.2893 | 132 | 2040 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 101.0682 | 0 | 1 |  |  | 0 | 101.0682 | 0 | 1 | 1 | 99 | 132 | 99 | 200.0682 | 99 | 132 | 233.0682 | 132 | 2045 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 99.8471 | 0 | 1 |  |  | 0 | 99.8471 | 0 | 1 | 1 | 99 | 132 | 99 | 198.8471 | 99 | 132 | 231.8471 | 132 | 2050 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 107.006 | 0 | 1 |  |  | 0 | 107.006 | 0 | 1 | 1 | 99 | 132 | 99 | 206.006 | 99 | 132 | 239.006 | 132 | 2023 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 104.8571 | 0 | 1 |  |  | 0 | 104.8571 | 0 | 1 | 1 | 99 | 132 | 99 | 203.8571 | 99 | 132 | 236.8571 | 132 | 2030 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 103.5732 | 0 | 1 |  |  | 0 | 103.5732 | 0 | 1 | 1 | 99 | 132 | 99 | 202.5732 | 99 | 132 | 235.5732 | 132 | 2035 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 102.2893 | 0 | 1 |  |  | 0 | 102.2893 | 0 | 1 | 1 | 99 | 132 | 99 | 201.2893 | 99 | 132 | 234.2893 | 132 | 2040 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 101.0682 | 0 | 1 |  |  | 0 | 101.0682 | 0 | 1 | 1 | 99 | 132 | 99 | 200.0682 | 99 | 132 | 233.0682 | 132 | 2045 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
52 | 2023 | Commercial | Lighting | Low-Bay | Metal Halide | Electricity | Low-Bay Metal Halide | 2023$ |  | Low-Bay Metal Halide | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | 8500 | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 99.8471 | 0 | 1 |  |  | 0 | 99.8471 | 0 | 1 | 1 | 99 | 132 | 99 | 198.8471 | 99 | 132 | 231.8471 | 132 | 2050 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 184.4703 | 0 | 1 |  |  | 0 | 184.4703 | 0 | 1 | 1 | 99 | 132 | 99 | 283.4703 | 99 | 132 | 316.4703 | 132 | 2023 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 179.8083 | 0 | 1 |  |  | 0 | 179.8083 | 0 | 1 | 1 | 99 | 132 | 99 | 278.8083 | 99 | 132 | 311.8083 | 132 | 2030 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 177.0229 | 0 | 1 |  |  | 0 | 177.0229 | 0 | 1 | 1 | 99 | 132 | 99 | 276.0229 | 99 | 132 | 309.0229 | 132 | 2035 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 174.2375 | 0 | 1 |  |  | 0 | 174.2375 | 0 | 1 | 1 | 99 | 132 | 99 | 273.2375 | 99 | 132 | 306.2375 | 132 | 2040 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 171.5883 | 0 | 1 |  |  | 0 | 171.5883 | 0 | 1 | 1 | 99 | 132 | 99 | 270.5883 | 99 | 132 | 303.5883 | 132 | 2045 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 168.9391 | 0 | 1 |  |  | 0 | 168.9391 | 0 | 1 | 1 | 99 | 132 | 99 | 267.9391 | 99 | 132 | 300.9391 | 132 | 2050 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 184.4703 | 0 | 1 |  |  | 0 | 184.4703 | 0 | 1 | 1 | 99 | 132 | 99 | 283.4703 | 99 | 132 | 316.4703 | 132 | 2023 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 179.8083 | 0 | 1 |  |  | 0 | 179.8083 | 0 | 1 | 1 | 99 | 132 | 99 | 278.8083 | 99 | 132 | 311.8083 | 132 | 2030 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 177.0229 | 0 | 1 |  |  | 0 | 177.0229 | 0 | 1 | 1 | 99 | 132 | 99 | 276.0229 | 99 | 132 | 309.0229 | 132 | 2035 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 174.2375 | 0 | 1 |  |  | 0 | 174.2375 | 0 | 1 | 1 | 99 | 132 | 99 | 273.2375 | 99 | 132 | 306.2375 | 132 | 2040 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 171.5883 | 0 | 1 |  |  | 0 | 171.5883 | 0 | 1 | 1 | 99 | 132 | 99 | 270.5883 | 99 | 132 | 303.5883 | 132 | 2045 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 168.9391 | 0 | 1 |  |  | 0 | 168.9391 | 0 | 1 | 1 | 99 | 132 | 99 | 267.9391 | 99 | 132 | 300.9391 | 132 | 2050 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 184.4703 | 0 | 1 |  |  | 0 | 184.4703 | 0 | 1 | 1 | 99 | 132 | 99 | 283.4703 | 99 | 132 | 316.4703 | 132 | 2023 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 179.8083 | 0 | 1 |  |  | 0 | 179.8083 | 0 | 1 | 1 | 99 | 132 | 99 | 278.8083 | 99 | 132 | 311.8083 | 132 | 2030 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 177.0229 | 0 | 1 |  |  | 0 | 177.0229 | 0 | 1 | 1 | 99 | 132 | 99 | 276.0229 | 99 | 132 | 309.0229 | 132 | 2035 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 174.2375 | 0 | 1 |  |  | 0 | 174.2375 | 0 | 1 | 1 | 99 | 132 | 99 | 273.2375 | 99 | 132 | 306.2375 | 132 | 2040 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 171.5883 | 0 | 1 |  |  | 0 | 171.5883 | 0 | 1 | 1 | 99 | 132 | 99 | 270.5883 | 99 | 132 | 303.5883 | 132 | 2045 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
53 | 2023 | Commercial | Lighting | Low-Bay | Sodium Vapor | Electricity | Low-Bay Sodium Vapor | 2023$ |  | Low-Bay Sodium Vapor | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | 9500 | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 168.9391 | 0 | 1 |  |  | 0 | 168.9391 | 0 | 1 | 1 | 99 | 132 | 99 | 267.9391 | 99 | 132 | 300.9391 | 132 | 2050 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | 0 | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 20.1705 | 64.3859 | 116.4921 | 12 | Square Feet | ft2 | 242.0466 | 772.6312 | 1397.9048 | 1.31 | 1.67 | 0 | 0 | 317.081 | 1012.1469 | 1831.2552 | 404.2178 | 1290.2942 | 2334.501 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 21.8905 | 69.8762 | 126.4255 | 12 | Square Feet | ft2 | 262.6862 | 838.5145 | 1517.1059 | 1.31 | 1.67 | 0 | 0 | 344.1189 | 1098.454 | 1987.4088 | 438.686 | 1400.3193 | 2533.5669 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 22.2032 | 70.8744 | 128.2316 | 12 | Square Feet | ft2 | 266.4389 | 850.4933 | 1538.7789 | 1.31 | 1.67 | 0 | 0 | 349.0349 | 1114.1462 | 2015.8003 | 444.9529 | 1420.3238 | 2569.7607 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 12 | Square Feet | ft2 | 270.1915 | 862.4721 | 1560.4518 | 1.31 | 1.67 | 0 | 0 | 353.9509 | 1129.8384 | 2044.1919 | 451.2199 | 1440.3284 | 2605.9546 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 12 | Square Feet | ft2 | 270.1915 | 862.4721 | 1560.4518 | 1.31 | 1.67 | 0 | 0 | 353.9509 | 1129.8384 | 2044.1919 | 451.2199 | 1440.3284 | 2605.9546 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 12 | Square Feet | ft2 | 270.1915 | 862.4721 | 1560.4518 | 1.31 | 1.67 | 0 | 0 | 353.9509 | 1129.8384 | 2044.1919 | 451.2199 | 1440.3284 | 2605.9546 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 20.1705 | 64.3859 | 116.4921 | 12 | Square Feet | ft2 | 242.0466 | 772.6312 | 1397.9048 | 1.31 | 1.67 | 0 | 0 | 317.081 | 1012.1469 | 1831.2552 | 404.2178 | 1290.2942 | 2334.501 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.455 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.675 | 0.65 | 0.65 | 22.8287 | 72.8709 | 131.8437 | 12 | Square Feet | ft2 | 273.9442 | 874.4509 | 1582.1248 | 1.31 | 1.67 | 0 | 0 | 358.8669 | 1145.5306 | 2072.5835 | 457.4868 | 1460.333 | 2642.1484 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.445 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.6725 | 0.65 | 0.65 | 22.6723 | 72.3718 | 130.9407 | 12 | Square Feet | ft2 | 272.0679 | 868.4615 | 1571.2883 | 1.31 | 1.67 | 0 | 0 | 356.4089 | 1137.6845 | 2058.3877 | 454.3533 | 1450.3307 | 2624.0515 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.435 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.67 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 12 | Square Feet | ft2 | 270.1915 | 862.4721 | 1560.4518 | 1.31 | 1.67 | 0 | 0 | 353.9509 | 1129.8384 | 2044.1919 | 451.2199 | 1440.3284 | 2605.9546 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.4275 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.6675 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 12 | Square Feet | ft2 | 270.1915 | 862.4721 | 1560.4518 | 1.31 | 1.67 | 0 | 0 | 353.9509 | 1129.8384 | 2044.1919 | 451.2199 | 1440.3284 | 2605.9546 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.42 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.665 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 12 | Square Feet | ft2 | 270.1915 | 862.4721 | 1560.4518 | 1.31 | 1.67 | 0 | 0 | 353.9509 | 1129.8384 | 2044.1919 | 451.2199 | 1440.3284 | 2605.9546 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 20.1705 | 64.3859 | 116.4921 | 12 | Square Feet | ft2 | 242.0466 | 772.6312 | 1397.9048 | 1.31 | 1.67 | 0 | 0 | 317.081 | 1012.1469 | 1831.2552 | 404.2178 | 1290.2942 | 2334.501 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.41 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.67 | 0.65 | 0.65 | 23.7668 | 75.8656 | 137.262 | 12 | Square Feet | ft2 | 285.2022 | 910.3872 | 1647.1436 | 1.31 | 1.67 | 0 | 0 | 373.6148 | 1192.6072 | 2157.7581 | 476.2876 | 1520.3466 | 2750.7298 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.39 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.665 | 0.65 | 0.65 | 23.1414 | 73.8691 | 133.6498 | 12 | Square Feet | ft2 | 277.6969 | 886.4297 | 1603.7977 | 1.31 | 1.67 | 0 | 0 | 363.7829 | 1161.2228 | 2100.975 | 463.7537 | 1480.3375 | 2678.3422 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.37 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.66 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 12 | Square Feet | ft2 | 270.1915 | 862.4721 | 1560.4518 | 1.31 | 1.67 | 0 | 0 | 353.9509 | 1129.8384 | 2044.1919 | 451.2199 | 1440.3284 | 2605.9546 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.355 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.655 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 12 | Square Feet | ft2 | 270.1915 | 862.4721 | 1560.4518 | 1.31 | 1.67 | 0 | 0 | 353.9509 | 1129.8384 | 2044.1919 | 451.2199 | 1440.3284 | 2605.9546 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
54 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Aluminum Frame |  | Fenestration Double-Pane, Aluminum Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.34 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.65 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 12 | Square Feet | ft2 | 270.1915 | 862.4721 | 1560.4518 | 1.31 | 1.67 | 0 | 0 | 353.9509 | 1129.8384 | 2044.1919 | 451.2199 | 1440.3284 | 2605.9546 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | 0 | 2023 | The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 12 | Square Feet | ft2 | 481.4294 | 715.335 | 1012.7312 | 1.31 | 1.67 | 0 | 0 | 630.6725 | 937.0888 | 1326.6779 | 803.9871 | 1194.6094 | 1691.2611 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 12 | Square Feet | ft2 | 481.4294 | 715.335 | 1012.7312 | 1.31 | 1.67 | 0 | 0 | 630.6725 | 937.0888 | 1326.6779 | 803.9871 | 1194.6094 | 1691.2611 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 12 | Square Feet | ft2 | 481.4294 | 715.335 | 1012.7312 | 1.31 | 1.67 | 0 | 0 | 630.6725 | 937.0888 | 1326.6779 | 803.9871 | 1194.6094 | 1691.2611 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 12 | Square Feet | ft2 | 481.4294 | 715.335 | 1012.7312 | 1.31 | 1.67 | 0 | 0 | 630.6725 | 937.0888 | 1326.6779 | 803.9871 | 1194.6094 | 1691.2611 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 12 | Square Feet | ft2 | 481.4294 | 715.335 | 1012.7312 | 1.31 | 1.67 | 0 | 0 | 630.6725 | 937.0888 | 1326.6779 | 803.9871 | 1194.6094 | 1691.2611 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 12 | Square Feet | ft2 | 481.4294 | 715.335 | 1012.7312 | 1.31 | 1.67 | 0 | 0 | 630.6725 | 937.0888 | 1326.6779 | 803.9871 | 1194.6094 | 1691.2611 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.2 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 12 | Square Feet | ft2 | 481.4294 | 715.335 | 1012.7312 | 1.31 | 1.67 | 0 | 0 | 630.6725 | 937.0888 | 1326.6779 | 803.9871 | 1194.6094 | 1691.2611 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.24917 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20417 | 0.19 | 0.19 | 41.8296 | 62.1528 | 87.9925 | 12 | Square Feet | ft2 | 501.9555 | 745.8338 | 1055.9097 | 1.31 | 1.67 | 0 | 0 | 657.5617 | 977.0423 | 1383.2417 | 838.2657 | 1245.5424 | 1763.3692 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.24417 | 0.235 | 0.235 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20167 | 0.19 | 0.19 | 41.9851 | 62.3839 | 88.3196 | 12 | Square Feet | ft2 | 503.8215 | 748.6064 | 1059.835 | 1.31 | 1.67 | 0 | 0 | 660.0062 | 980.6744 | 1388.3838 | 841.3819 | 1250.1727 | 1769.9244 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.23917 | 0.23 | 0.23 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19917 | 0.185 | 0.185 | 42.1406 | 62.6149 | 88.6467 | 12 | Square Feet | ft2 | 505.6875 | 751.379 | 1063.7603 | 1.31 | 1.67 | 0 | 0 | 662.4506 | 984.3065 | 1393.526 | 844.4981 | 1254.8029 | 1776.4797 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.23417 | 0.225 | 0.225 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19667 | 0.185 | 0.185 | 42.2961 | 62.846 | 88.9738 | 12 | Square Feet | ft2 | 507.5535 | 754.1516 | 1067.6856 | 1.31 | 1.67 | 0 | 0 | 664.8951 | 987.9386 | 1398.6682 | 847.6143 | 1259.4332 | 1783.035 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.22917 | 0.22 | 0.22 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19417 | 0.185 | 0.185 | 42.4516 | 63.077 | 89.3009 | 12 | Square Feet | ft2 | 509.4195 | 756.9242 | 1071.6109 | 1.31 | 1.67 | 0 | 0 | 667.3396 | 991.5708 | 1403.8103 | 850.7306 | 1264.0635 | 1789.5903 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 12 | Square Feet | ft2 | 481.4294 | 715.335 | 1012.7312 | 1.31 | 1.67 | 0 | 0 | 630.6725 | 937.0888 | 1326.6779 | 803.9871 | 1194.6094 | 1691.2611 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.24 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19917 | 0.19 | 0.19 | 43.5401 | 64.6944 | 91.5907 | 12 | Square Feet | ft2 | 522.4815 | 776.3326 | 1099.0881 | 1.31 | 1.67 | 0 | 0 | 684.4508 | 1016.9957 | 1439.8055 | 872.5442 | 1296.4754 | 1835.4772 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.23 | 0.23 | 0.23 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19417 | 0.19 | 0.19 | 43.8511 | 65.1565 | 92.2449 | 12 | Square Feet | ft2 | 526.2136 | 781.8778 | 1106.9388 | 1.31 | 1.67 | 0 | 0 | 689.3398 | 1024.2599 | 1450.0898 | 878.7766 | 1305.7359 | 1848.5877 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.22 | 0.22 | 0.22 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.18917 | 0.18 | 0.18 | 44.1621 | 65.6186 | 92.8991 | 12 | Square Feet | ft2 | 529.9456 | 787.423 | 1114.7894 | 1.31 | 1.67 | 0 | 0 | 694.2287 | 1031.5242 | 1460.3741 | 885.0091 | 1314.9964 | 1861.6983 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.21 | 0.21 | 0.21 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.18417 | 0.18 | 0.18 | 44.4731 | 66.0807 | 93.5533 | 12 | Square Feet | ft2 | 533.6776 | 792.9683 | 1122.64 | 1.31 | 1.67 | 0 | 0 | 699.1176 | 1038.7884 | 1470.6584 | 891.2416 | 1324.257 | 1874.8088 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
55 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Wood Frame |  | Fenestration Double-Pane, Wood Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.17917 | 0.18 | 0.18 | 44.7841 | 66.5428 | 94.2076 | 12 | Square Feet | ft2 | 537.4096 | 798.5135 | 1130.4907 | 1.31 | 1.67 | 0 | 0 | 704.0066 | 1046.0527 | 1480.9428 | 897.474 | 1333.5175 | 1887.9194 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 24.6933 | 43.0342 | 98.0426 | 12 | Square Feet | ft2 | 296.32 | 516.411 | 1176.5106 | 1.31 | 1.67 | 0 | 0 | 388.1792 | 676.4984 | 1541.2289 | 494.8544 | 862.4063 | 1964.7728 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 26.799 | 46.7038 | 106.4028 | 12 | Square Feet | ft2 | 321.5876 | 560.446 | 1276.8333 | 1.31 | 1.67 | 0 | 0 | 421.2798 | 734.1843 | 1672.6516 | 537.0513 | 935.9449 | 2132.3115 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 27.1818 | 47.371 | 107.9228 | 12 | Square Feet | ft2 | 326.1817 | 568.4524 | 1295.0737 | 1.31 | 1.67 | 0 | 0 | 427.298 | 744.6727 | 1696.5466 | 544.7234 | 949.3155 | 2162.7731 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 12 | Square Feet | ft2 | 330.7758 | 576.4588 | 1313.3142 | 1.31 | 1.67 | 0 | 0 | 433.3163 | 755.161 | 1720.4416 | 552.3956 | 962.6862 | 2193.2347 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 12 | Square Feet | ft2 | 330.7758 | 576.4588 | 1313.3142 | 1.31 | 1.67 | 0 | 0 | 433.3163 | 755.161 | 1720.4416 | 552.3956 | 962.6862 | 2193.2347 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 12 | Square Feet | ft2 | 330.7758 | 576.4588 | 1313.3142 | 1.31 | 1.67 | 0 | 0 | 433.3163 | 755.161 | 1720.4416 | 552.3956 | 962.6862 | 2193.2347 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 24.6933 | 43.0342 | 98.0426 | 12 | Square Feet | ft2 | 296.32 | 516.411 | 1176.5106 | 1.31 | 1.67 | 0 | 0 | 388.1792 | 676.4984 | 1541.2289 | 494.8544 | 862.4063 | 1964.7728 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.31075 | 0.27 | 0.27 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28282 | 0.16 | 0.16 | 27.9475 | 48.7054 | 110.9629 | 12 | Square Feet | ft2 | 335.3699 | 584.4651 | 1331.5547 | 1.31 | 1.67 | 0 | 0 | 439.3346 | 765.6493 | 1744.3366 | 560.0678 | 976.0568 | 2223.6963 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.30575 | 0.265 | 0.265 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28032 | 0.16 | 0.16 | 27.7561 | 48.3718 | 110.2029 | 12 | Square Feet | ft2 | 333.0729 | 580.462 | 1322.4344 | 1.31 | 1.67 | 0 | 0 | 436.3255 | 760.4052 | 1732.3891 | 556.2317 | 969.3715 | 2208.4655 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.30075 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27782 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 12 | Square Feet | ft2 | 330.7758 | 576.4588 | 1313.3142 | 1.31 | 1.67 | 0 | 0 | 433.3163 | 755.161 | 1720.4416 | 552.3956 | 962.6862 | 2193.2347 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.29575 | 0.255 | 0.255 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27532 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 12 | Square Feet | ft2 | 330.7758 | 576.4588 | 1313.3142 | 1.31 | 1.67 | 0 | 0 | 433.3163 | 755.161 | 1720.4416 | 552.3956 | 962.6862 | 2193.2347 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.29075 | 0.25 | 0.25 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27282 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 12 | Square Feet | ft2 | 330.7758 | 576.4588 | 1313.3142 | 1.31 | 1.67 | 0 | 0 | 433.3163 | 755.161 | 1720.4416 | 552.3956 | 962.6862 | 2193.2347 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 24.6933 | 43.0342 | 98.0426 | 12 | Square Feet | ft2 | 296.32 | 516.411 | 1176.5106 | 1.31 | 1.67 | 0 | 0 | 388.1792 | 676.4984 | 1541.2289 | 494.8544 | 862.4063 | 1964.7728 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.3 | 0.28 | 0.28 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28 | 0.16 | 0.16 | 29.096 | 50.707 | 115.523 | 12 | Square Feet | ft2 | 349.1522 | 608.4843 | 1386.2761 | 1.31 | 1.67 | 0 | 0 | 457.3894 | 797.1144 | 1816.0217 | 583.0843 | 1016.1687 | 2315.0811 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.29 | 0.27 | 0.27 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.275 | 0.16 | 0.16 | 28.3303 | 49.3726 | 112.4829 | 12 | Square Feet | ft2 | 339.964 | 592.4715 | 1349.7952 | 1.31 | 1.67 | 0 | 0 | 445.3529 | 776.1377 | 1768.2316 | 567.7399 | 989.4274 | 2254.1579 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.28 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 12 | Square Feet | ft2 | 330.7758 | 576.4588 | 1313.3142 | 1.31 | 1.67 | 0 | 0 | 433.3163 | 755.161 | 1720.4416 | 552.3956 | 962.6862 | 2193.2347 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.27 | 0.25 | 0.25 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.265 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 12 | Square Feet | ft2 | 330.7758 | 576.4588 | 1313.3142 | 1.31 | 1.67 | 0 | 0 | 433.3163 | 755.161 | 1720.4416 | 552.3956 | 962.6862 | 2193.2347 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
56 | 2023 | Commercial | Envelope | Fenestration | Double-Pane, Vinyl Frame |  | Fenestration Double-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.26 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.26 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 12 | Square Feet | ft2 | 330.7758 | 576.4588 | 1313.3142 | 1.31 | 1.67 | 0 | 0 | 433.3163 | 755.161 | 1720.4416 | 552.3956 | 962.6862 | 2193.2347 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 73.7476 | 111.3574 | 127.5566 | 12 | Square Feet | ft2 | 884.9711 | 1336.2886 | 1530.6793 | 1.31 | 1.67 | 0 | 0 | 1159.3122 | 1750.5381 | 2005.1899 | 1477.9018 | 2231.602 | 2556.2345 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 80.0361 | 120.853 | 138.4335 | 12 | Square Feet | ft2 | 960.4338 | 1450.2357 | 1661.2024 | 1.31 | 1.67 | 0 | 0 | 1258.1682 | 1899.8088 | 2176.1751 | 1603.9244 | 2421.8937 | 2774.208 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 81.1795 | 122.5794 | 140.4112 | 12 | Square Feet | ft2 | 974.1543 | 1470.9534 | 1684.9338 | 1.31 | 1.67 | 0 | 0 | 1276.1421 | 1926.9489 | 2207.2633 | 1626.8376 | 2456.4921 | 2813.8395 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 12 | Square Feet | ft2 | 987.8747 | 1491.671 | 1708.6653 | 1.31 | 1.67 | 0 | 0 | 1294.1159 | 1954.0891 | 2238.3515 | 1649.7508 | 2491.0906 | 2853.471 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 12 | Square Feet | ft2 | 987.8747 | 1491.671 | 1708.6653 | 1.31 | 1.67 | 0 | 0 | 1294.1159 | 1954.0891 | 2238.3515 | 1649.7508 | 2491.0906 | 2853.471 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 12 | Square Feet | ft2 | 987.8747 | 1491.671 | 1708.6653 | 1.31 | 1.67 | 0 | 0 | 1294.1159 | 1954.0891 | 2238.3515 | 1649.7508 | 2491.0906 | 2853.471 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 73.7476 | 111.3574 | 127.5566 | 12 | Square Feet | ft2 | 884.9711 | 1336.2886 | 1530.6793 | 1.31 | 1.67 | 0 | 0 | 1159.3122 | 1750.5381 | 2005.1899 | 1477.9018 | 2231.602 | 2556.2345 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.23 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28282 | 0.16 | 0.16 | 83.4663 | 126.0324 | 144.3664 | 12 | Square Feet | ft2 | 1001.5952 | 1512.3887 | 1732.3968 | 1.31 | 1.67 | 0 | 0 | 1312.0897 | 1981.2292 | 2269.4397 | 1672.664 | 2525.6891 | 2893.1026 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.2225 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28032 | 0.16 | 0.16 | 82.8946 | 125.1692 | 143.3776 | 12 | Square Feet | ft2 | 994.735 | 1502.0299 | 1720.531 | 1.31 | 1.67 | 0 | 0 | 1303.1028 | 1967.6591 | 2253.8956 | 1661.2074 | 2508.3899 | 2873.2868 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.215 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27782 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 12 | Square Feet | ft2 | 987.8747 | 1491.671 | 1708.6653 | 1.31 | 1.67 | 0 | 0 | 1294.1159 | 1954.0891 | 2238.3515 | 1649.7508 | 2491.0906 | 2853.471 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.2075 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27532 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 12 | Square Feet | ft2 | 987.8747 | 1491.671 | 1708.6653 | 1.31 | 1.67 | 0 | 0 | 1294.1159 | 1954.0891 | 2238.3515 | 1649.7508 | 2491.0906 | 2853.471 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.2 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27282 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 12 | Square Feet | ft2 | 987.8747 | 1491.671 | 1708.6653 | 1.31 | 1.67 | 0 | 0 | 1294.1159 | 1954.0891 | 2238.3515 | 1649.7508 | 2491.0906 | 2853.471 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 73.7476 | 111.3574 | 127.5566 | 12 | Square Feet | ft2 | 884.9711 | 1336.2886 | 1530.6793 | 1.31 | 1.67 | 0 | 0 | 1159.3122 | 1750.5381 | 2005.1899 | 1477.9018 | 2231.602 | 2556.2345 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.21 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28 | 0.16 | 0.16 | 86.8964 | 131.2118 | 150.2993 | 12 | Square Feet | ft2 | 1042.7567 | 1574.5416 | 1803.5911 | 1.31 | 1.67 | 0 | 0 | 1366.0112 | 2062.6496 | 2362.7044 | 1741.4036 | 2629.4845 | 3011.9972 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.195 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.275 | 0.16 | 0.16 | 84.6096 | 127.7589 | 146.344 | 12 | Square Feet | ft2 | 1015.3157 | 1533.1063 | 1756.1282 | 1.31 | 1.67 | 0 | 0 | 1330.0636 | 2008.3693 | 2300.528 | 1695.5772 | 2560.2876 | 2932.7341 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.18 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 12 | Square Feet | ft2 | 987.8747 | 1491.671 | 1708.6653 | 1.31 | 1.67 | 0 | 0 | 1294.1159 | 1954.0891 | 2238.3515 | 1649.7508 | 2491.0906 | 2853.471 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.165 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.265 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 12 | Square Feet | ft2 | 987.8747 | 1491.671 | 1708.6653 | 1.31 | 1.67 | 0 | 0 | 1294.1159 | 1954.0891 | 2238.3515 | 1649.7508 | 2491.0906 | 2853.471 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
57 | 2023 | Commercial | Envelope | Fenestration | Triple-Pane, Vinyl Frame |  | Fenestration Triple-Pane, Vinyl Frame | 2023$/sqft |  |  | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.15 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.26 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 12 | Square Feet | ft2 | 987.8747 | 1491.671 | 1708.6653 | 1.31 | 1.67 | 0 | 0 | 1294.1159 | 1954.0891 | 2238.3515 | 1649.7508 | 2491.0906 | 2853.471 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | 0 | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.22411 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30679 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.23411 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.31679 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.23411 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.31679 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.23911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.32179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.24411 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.32679 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.22911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.31179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.24911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.33179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.24911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.33179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.25911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.34179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
58 | 2023 | Commercial | Envelope | Fenestration | Window Film |  | Fenestration Window Film | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.26911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.35179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 12 | Square Feet | ft2 | 158.976 | 583.9611 | 640 | 1 | 1 | 1.4833 | 1.5733 | 176.776 | 601.7611 | 657.8 | 177.856 | 602.8411 | 658.88 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | 0 | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows.
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 85295.5285 | 88050.4903 | 1 | 1 | 12560 | 12560 | 33464.168 | 97855.5285 | 100610.4903 | 33464.168 | 97855.5285 | 100610.4903 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 85295.5285 | 88050.4903 | 1 | 1 | 12560 | 12560 | 33464.168 | 97855.5285 | 100610.4903 | 33464.168 | 97855.5285 | 100610.4903 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 85295.5285 | 88050.4903 | 1 | 1 | 12560 | 12560 | 33464.168 | 97855.5285 | 100610.4903 | 33464.168 | 97855.5285 | 100610.4903 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 85295.5285 | 88050.4903 | 1 | 1 | 12560 | 12560 | 33464.168 | 97855.5285 | 100610.4903 | 33464.168 | 97855.5285 | 100610.4903 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 85295.5285 | 88050.4903 | 1 | 1 | 12560 | 12560 | 33464.168 | 97855.5285 | 100610.4903 | 33464.168 | 97855.5285 | 100610.4903 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 85295.5285 | 88050.4903 | 1 | 1 | 12560 | 12560 | 33464.168 | 97855.5285 | 100610.4903 | 33464.168 | 97855.5285 | 100610.4903 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 85295.5285 | 88050.4903 | 1 | 1 | 12560 | 12560 | 33464.168 | 97855.5285 | 100610.4903 | 33464.168 | 97855.5285 | 100610.4903 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 89 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 88268.3973 | 90679.4821 | 1 | 1 | 12560 | 12560 | 33464.168 | 100828.3973 | 103239.4821 | 33464.168 | 100828.3973 | 103239.4821 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 89.5 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 88640.0059 | 91008.1061 | 1 | 1 | 12560 | 12560 | 33464.168 | 101200.0059 | 103568.1061 | 33464.168 | 101200.0059 | 103568.1061 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 90 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 89011.6145 | 91336.7301 | 1 | 1 | 12560 | 12560 | 33464.168 | 101571.6145 | 103896.7301 | 33464.168 | 101571.6145 | 103896.7301 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 90 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 89011.6145 | 91336.7301 | 1 | 1 | 12560 | 12560 | 33464.168 | 101571.6145 | 103896.7301 | 33464.168 | 101571.6145 | 103896.7301 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 90 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 89011.6145 | 91336.7301 | 1 | 1 | 12560 | 12560 | 33464.168 | 101571.6145 | 103896.7301 | 33464.168 | 101571.6145 | 103896.7301 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 85295.5285 | 88050.4903 | 1 | 1 | 12560 | 12560 | 33464.168 | 97855.5285 | 100610.4903 | 33464.168 | 97855.5285 | 100610.4903 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 93 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 91241.2661 | 93308.4739 | 1 | 1 | 12560 | 12560 | 33464.168 | 103801.2661 | 105868.4739 | 33464.168 | 103801.2661 | 105868.4739 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 94 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 91984.4833 | 93965.7219 | 1 | 1 | 12560 | 12560 | 33464.168 | 104544.4833 | 106525.7219 | 33464.168 | 104544.4833 | 106525.7219 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 95 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 92727.7005 | 94622.9698 | 1 | 1 | 12560 | 12560 | 33464.168 | 105287.7005 | 107182.9698 | 33464.168 | 105287.7005 | 107182.9698 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Gas | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 95 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 92727.7005 | 94622.9698 | 1 | 1 | 12560 | 12560 | 33464.168 | 105287.7005 | 107182.9698 | 33464.168 | 105287.7005 | 107182.9698 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
59 | 2023 | Commercial | HVAC | Boilers | Gas-Fired | Oil | Commercial Boiler Gas-Fired | 2023$ |  | Commercial Gas-Fired Boilers | 0.02613 | 0.026672 | 0.039338 | Heating Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 95 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 1 |  |  | 20904.168 | 92727.7005 | 94622.9698 | 1 | 1 | 12560 | 12560 | 33464.168 | 105287.7005 | 107182.9698 | 33464.168 | 105287.7005 | 107182.9698 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2035 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2040 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2045 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
60 | 2023 | Commercial | Water Heating | Commercial Water Heater | Electric Storage | Electricity | Commercial Water Heater Electric Storage | 2023$ |  | Commercial Electric Resistance Water Heaters | 46.28 | 76.0526 | 102.1111 | Nominal Volume | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 1 |  |  | 5737.43 | 9777.8847 | 14875.7678 | 1 | 1 | 940 | 1280 | 6677.43 | 10717.8847 | 15815.7678 | 7017.43 | 11057.8847 | 16155.7678 | 2050 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3864.6137 | 4830.7671 | 5796.9206 | 1 | 1 | 950 | 950 | 4814.6137 | 5780.7671 | 6746.9206 | 4814.6137 | 5780.7671 | 6746.9206 | 2023 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3864.6137 | 4830.7671 | 5796.9206 | 1 | 1 | 950 | 950 | 4814.6137 | 5780.7671 | 6746.9206 | 4814.6137 | 5780.7671 | 6746.9206 | 2030 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3864.6137 | 4830.7671 | 5796.9206 | 1 | 1 | 950 | 950 | 4814.6137 | 5780.7671 | 6746.9206 | 4814.6137 | 5780.7671 | 6746.9206 | 2035 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3864.6137 | 4830.7671 | 5796.9206 | 1 | 1 | 950 | 950 | 4814.6137 | 5780.7671 | 6746.9206 | 4814.6137 | 5780.7671 | 6746.9206 | 2040 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3864.6137 | 4830.7671 | 5796.9206 | 1 | 1 | 950 | 950 | 4814.6137 | 5780.7671 | 6746.9206 | 4814.6137 | 5780.7671 | 6746.9206 | 2045 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3864.6137 | 4830.7671 | 5796.9206 | 1 | 1 | 950 | 950 | 4814.6137 | 5780.7671 | 6746.9206 | 4814.6137 | 5780.7671 | 6746.9206 | 2050 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3864.6137 | 4830.7671 | 5796.9206 | 1 | 1 | 950 | 950 | 4814.6137 | 5780.7671 | 6746.9206 | 4814.6137 | 5780.7671 | 6746.9206 | 2023 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 93.9724 | 79.6837 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3939.119 | 4923.8988 | 5908.6785 | 1 | 1 | 950 | 950 | 4889.119 | 5873.8988 | 6858.6785 | 4889.119 | 5873.8988 | 6858.6785 | 2030 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 91.7468 | 77.7964 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3972.6464 | 4965.808 | 5958.9696 | 1 | 1 | 950 | 950 | 4922.6464 | 5915.808 | 6908.9696 | 4922.6464 | 5915.808 | 6908.9696 | 2035 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 89.5211 | 75.9092 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 4006.1738 | 5007.7173 | 6009.2607 | 1 | 1 | 950 | 950 | 4956.1738 | 5957.7173 | 6959.2607 | 4956.1738 | 5957.7173 | 6959.2607 | 2040 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 87.518 | 74.2107 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 4036.3485 | 5045.4356 | 6054.5227 | 1 | 1 | 950 | 950 | 4986.3485 | 5995.4356 | 7004.5227 | 4986.3485 | 5995.4356 | 7004.5227 | 2045 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 85.5149 | 72.5121 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 4066.5231 | 5083.1539 | 6099.7847 | 1 | 1 | 950 | 950 | 5016.5231 | 6033.1539 | 7049.7847 | 5016.5231 | 6033.1539 | 7049.7847 | 2050 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 3864.6137 | 4830.7671 | 5796.9206 | 1 | 1 | 950 | 950 | 4814.6137 | 5780.7671 | 6746.9206 | 4814.6137 | 5780.7671 | 6746.9206 | 2023 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 89.0265 | 75.4898 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 4013.6243 | 5017.0304 | 6020.4365 | 1 | 1 | 950 | 950 | 4963.6243 | 5967.0304 | 6970.4365 | 4963.6243 | 5967.0304 | 6970.4365 | 2030 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 84.5752 | 71.7153 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 4080.6791 | 5100.8489 | 6121.0187 | 1 | 1 | 950 | 950 | 5030.6791 | 6050.8489 | 7071.0187 | 5030.6791 | 6050.8489 | 7071.0187 | 2035 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 80.1239 | 67.9408 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 4147.7339 | 5184.6674 | 6221.6009 | 1 | 1 | 950 | 950 | 5097.7339 | 6134.6674 | 7171.6009 | 5097.7339 | 6134.6674 | 7171.6009 | 2040 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 76.1177 | 64.5438 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 4208.0832 | 5260.104 | 6312.1248 | 1 | 1 | 950 | 950 | 5158.0832 | 6210.104 | 7262.1248 | 5158.0832 | 6210.104 | 7262.1248 | 2045 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
61 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Freezer | Electricity | Commercial Reach-in Freezer | 2023$ |  | Reach-in Freezer | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 72.1115 | 61.1467 | 123 | 2192.456 | 2740.57 | 3288.684 | 1 |  |  | 4268.4325 | 5335.5406 | 6402.6488 | 1 | 1 | 950 | 950 | 5218.4325 | 6285.5406 | 7352.6488 | 5218.4325 | 6285.5406 | 7352.6488 | 2050 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3218.5094 | 4023.1367 | 4827.7641 | 1 | 1 | 863 | 863 | 4081.5094 | 4886.1367 | 5690.7641 | 4081.5094 | 4886.1367 | 5690.7641 | 2023 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3218.5094 | 4023.1367 | 4827.7641 | 1 | 1 | 863 | 863 | 4081.5094 | 4886.1367 | 5690.7641 | 4081.5094 | 4886.1367 | 5690.7641 | 2030 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3218.5094 | 4023.1367 | 4827.7641 | 1 | 1 | 863 | 863 | 4081.5094 | 4886.1367 | 5690.7641 | 4081.5094 | 4886.1367 | 5690.7641 | 2035 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3218.5094 | 4023.1367 | 4827.7641 | 1 | 1 | 863 | 863 | 4081.5094 | 4886.1367 | 5690.7641 | 4081.5094 | 4886.1367 | 5690.7641 | 2040 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3218.5094 | 4023.1367 | 4827.7641 | 1 | 1 | 863 | 863 | 4081.5094 | 4886.1367 | 5690.7641 | 4081.5094 | 4886.1367 | 5690.7641 | 2045 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3218.5094 | 4023.1367 | 4827.7641 | 1 | 1 | 863 | 863 | 4081.5094 | 4886.1367 | 5690.7641 | 4081.5094 | 4886.1367 | 5690.7641 | 2050 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3218.5094 | 4023.1367 | 4827.7641 | 1 | 1 | 863 | 863 | 4081.5094 | 4886.1367 | 5690.7641 | 4081.5094 | 4886.1367 | 5690.7641 | 2023 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3227.5597 | 4034.4496 | 4841.3395 | 1 | 1 | 863 | 863 | 4090.5597 | 4897.4496 | 5704.3395 | 4090.5597 | 4897.4496 | 5704.3395 | 2030 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3227.5597 | 4034.4496 | 4841.3395 | 1 | 1 | 863 | 863 | 4090.5597 | 4897.4496 | 5704.3395 | 4090.5597 | 4897.4496 | 5704.3395 | 2035 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3227.5597 | 4034.4496 | 4841.3395 | 1 | 1 | 863 | 863 | 4090.5597 | 4897.4496 | 5704.3395 | 4090.5597 | 4897.4496 | 5704.3395 | 2040 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3227.5597 | 4034.4496 | 4841.3395 | 1 | 1 | 863 | 863 | 4090.5597 | 4897.4496 | 5704.3395 | 4090.5597 | 4897.4496 | 5704.3395 | 2045 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3227.5597 | 4034.4496 | 4841.3395 | 1 | 1 | 863 | 863 | 4090.5597 | 4897.4496 | 5704.3395 | 4090.5597 | 4897.4496 | 5704.3395 | 2050 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3218.5094 | 4023.1367 | 4827.7641 | 1 | 1 | 863 | 863 | 4081.5094 | 4886.1367 | 5690.7641 | 4081.5094 | 4886.1367 | 5690.7641 | 2023 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3236.6099 | 4045.7624 | 4854.9149 | 1 | 1 | 863 | 863 | 4099.6099 | 4908.7624 | 5717.9149 | 4099.6099 | 4908.7624 | 5717.9149 | 2030 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3236.6099 | 4045.7624 | 4854.9149 | 1 | 1 | 863 | 863 | 4099.6099 | 4908.7624 | 5717.9149 | 4099.6099 | 4908.7624 | 5717.9149 | 2035 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3236.6099 | 4045.7624 | 4854.9149 | 1 | 1 | 863 | 863 | 4099.6099 | 4908.7624 | 5717.9149 | 4099.6099 | 4908.7624 | 5717.9149 | 2040 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3236.6099 | 4045.7624 | 4854.9149 | 1 | 1 | 863 | 863 | 4099.6099 | 4908.7624 | 5717.9149 | 4099.6099 | 4908.7624 | 5717.9149 | 2045 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
62 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Reach-in Refrigerator | Electricity | Commercial Reach-in Refrigerator | 2023$ |  | Reach-in Refrigerator | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 1 |  |  | 3236.6099 | 4045.7624 | 4854.9149 | 1 | 1 | 863 | 863 | 4099.6099 | 4908.7624 | 5717.9149 | 4099.6099 | 4908.7624 | 5717.9149 | 2050 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2023 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2030 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2035 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2040 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2045 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2050 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2023 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2030 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2035 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2040 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2045 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2050 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2023 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2030 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2035 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2040 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2045 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
63 | 2023 | Commercial | HVAC | Unit Heater | Electric | Electricity | Unit Heater Electric | 2023$ |  | Commercial Electric Resistance Heaters | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1 |  |  | 865.0075 | 1382.0102 | 2259.27 | 1.18 | 1.18 | 0 | 0 | 1020.7088 | 1630.7721 | 2665.9386 | 1020.7088 | 1630.7721 | 2665.9386 | 2050 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2023 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2030 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2035 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2040 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2045 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2050 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2023 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29637.7411 | 34633.726 | 44456.6116 | 1.285 | 1.285 | 0 | 0 | 38084.4973 | 44504.3379 | 57126.746 | 38084.4973 | 44504.3379 | 57126.746 | 2030 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29637.7411 | 34633.726 | 44456.6116 | 1.285 | 1.285 | 0 | 0 | 38084.4973 | 44504.3379 | 57126.746 | 38084.4973 | 44504.3379 | 57126.746 | 2035 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29637.7411 | 34633.726 | 44456.6116 | 1.285 | 1.285 | 0 | 0 | 38084.4973 | 44504.3379 | 57126.746 | 38084.4973 | 44504.3379 | 57126.746 | 2040 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29637.7411 | 34633.726 | 44456.6116 | 1.285 | 1.285 | 0 | 0 | 38084.4973 | 44504.3379 | 57126.746 | 38084.4973 | 44504.3379 | 57126.746 | 2045 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29637.7411 | 34633.726 | 44456.6116 | 1.285 | 1.285 | 0 | 0 | 38084.4973 | 44504.3379 | 57126.746 | 38084.4973 | 44504.3379 | 57126.746 | 2050 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2023 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2030 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2035 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2040 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2045 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
64 | 2023 | Commercial | HVAC | Boilers | Oil-Fired | Oil | Commercial Boiler Oil | 2023$ |  | Commercial Oil-Fired Boilers | 17.7308 | 22.1636 | 26.5963 | Heating Capacity | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 1 |  |  | 29627.1918 | 34620.5393 | 44440.7876 | 1.285 | 1.285 | 0 | 0 | 38070.9414 | 44487.393 | 57106.4121 | 38070.9414 | 44487.393 | 57106.4121 | 2050 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 82 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 5370.5379 | 11449.1293 | 16055.338 | 1 | 1 | 2440 | 3060 | 7810.5379 | 13889.1293 | 18495.338 | 8430.5379 | 14509.1293 | 19115.338 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 82 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 5370.5379 | 11449.1293 | 16055.338 | 1 | 1 | 2440 | 3060 | 7810.5379 | 13889.1293 | 18495.338 | 8430.5379 | 14509.1293 | 19115.338 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 82 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 5370.5379 | 11449.1293 | 16055.338 | 1 | 1 | 2440 | 3060 | 7810.5379 | 13889.1293 | 18495.338 | 8430.5379 | 14509.1293 | 19115.338 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
65 | 2023 | Commercial | Water Heating | Water Heater | Gas Storage | Gas | Commercial Water Heater Gas Storage | 2023$ |  | Commercial Gas-Fired Water Heaters | 46.2689 | 71.5502 | 33.6899 | Nominal Volume | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 1 |  |  | 6979.6563 | 12678.5361 | 18882.0914 | 1 | 1 | 2440 | 3060 | 9419.6563 | 15118.5361 | 21322.0914 | 10039.6563 | 15738.5361 | 21942.0914 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2023 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2030 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2035 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2040 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2045 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2050 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2023 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2030 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2035 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2040 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2045 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2050 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2023 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2030 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2035 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2040 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2045 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
66 | 2023 | Commercial | Water Heating | Water Heater | Gas Booster | Gas | Commercial Water Heater Gas Booster | 2023$ |  | Commercial Gas-Fired Booster Water Heaters | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 1 |  |  | 10054 | 15108.1882 | 20162.3764 | 1 | 1 | 300 | 300 | 10354 | 15408.1882 | 20462.3764 | 10354 | 15408.1882 | 20462.3764 | 2050 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | "High" and "Low" coefficients and intercepts are based on individual linear regressions of selected points which defined the upper and lower range of models identified, not quantile regressions of a single dataset. "Mid" coefficient and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.95 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.05 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.1 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.15 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.1 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.2 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.3 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
67 | 2023 | Commercial | Water Heating | Water Heater | Heat Pump | Electricity | Commercial Water Heater Heat Pump | 2023$ |  | Commercial Heat Pump Water Heaters | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.4 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 1 |  |  | 8499 | 9233.5 | 9968 | 1.08 | 1.08 | 0 | 0 | 9178.92 | 9972.18 | 10765.44 | 9178.92 | 9972.18 | 10765.44 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | 0 | 2023 | Analysis includes storage and instantaneous heaters due to limited market availability and data for both varieties
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.92 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2023 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2030 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2035 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2040 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2045 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2050 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.92 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2023 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2030 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2035 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2040 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2045 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2050 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.92 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2023 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2030 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2035 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2040 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2045 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
68 | 2023 | Commercial | Water Heating | Water Heater | Gas Instantaneous | Gas | Commercial Water Heater Gas Instantaneous | 2023$ |  | Commercial Gas-Fired Instantaneous Water Heaters | 0.011363 | 0.014204 | 0.0017045 | Heating Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 1 |  |  | 2840.868 | 3551.085 | 426.1302 | 1.5832 | 2.135 | 0 | 0 | 4497.719 | 5622.1488 | 674.6579 | 6065.2532 | 7581.5665 | 909.788 | 2050 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2023 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2030 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2035 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2040 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2045 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2050 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20930 | 20930 | 20214 | 20214 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2023 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 19860 | 19860 | 19144 | 19144 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2030 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 19378.5 | 19378.5 | 18662.5 | 18662.5 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2035 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 18897 | 18897 | 18181 | 18181 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2040 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 18463.65 | 18463.65 | 17747.65 | 17747.65 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2045 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 18030.3 | 18030.3 | 17314.3 | 17314.3 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2050 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21400 | 21400 | 21400 | 21400 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2023 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 19260 | 19260 | 19260 | 19260 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2030 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 18297 | 18297 | 18297 | 18297 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2035 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 17334 | 17334 | 17334 | 17334 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2040 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16467.3 | 16467.3 | 16467.3 | 16467.3 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2045 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
69 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Freezer | Electricity | Pre-Fabricated Walk-in Freezer | 2023$ |  | Commercial Walk-In Freezer | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 15600.6 | 15600.6 | 15600.6 | 15600.6 | 6888.96 | 8611.2 | 10333.44 | 1 |  |  | 14361.6 | 17952 | 11454.336 | 1.19 | 1.2573 | 0 | 0 | 17090.304 | 21362.88 | 13630.6598 | 18057.3719 | 22571.7149 | 14401.9611 | 2050 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regression and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 13056 | 16200 | 18528 | 1 |  |  | 13056 | 16200 | 18528 | 1.1409 | 1.1899 | 0 | 0 | 14895.1858 | 18482.078 | 21138.0211 | 15535.4225 | 19276.4893 | 22046.5922 | 2023 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2030 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2035 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2040 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2045 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2050 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 13056 | 16200 | 18528 | 1 |  |  | 13056 | 16200 | 18528 | 1.1409 | 1.1899 | 0 | 0 | 14895.1858 | 18482.078 | 21138.0211 | 15535.4225 | 19276.4893 | 22046.5922 | 2023 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 15390 | 15390 | 14060 | 14060 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2030 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 15025.5 | 15025.5 | 13727 | 13727 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2035 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 14661 | 14661 | 13394 | 13394 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2040 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 14332.95 | 14332.95 | 13094.3 | 13094.3 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2045 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 14004.9 | 14004.9 | 12794.6 | 12794.6 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2050 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 13056 | 16200 | 18528 | 1 |  |  | 13056 | 16200 | 18528 | 1.1409 | 1.1899 | 0 | 0 | 14895.1858 | 18482.078 | 21138.0211 | 15535.4225 | 19276.4893 | 22046.5922 | 2023 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 14580 | 14580 | 13320 | 13320 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2030 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 13851 | 13851 | 12654 | 12654 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2035 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 13122 | 13122 | 11988 | 11988 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2040 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 12465.9 | 12465.9 | 11388.6 | 11388.6 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2045 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
70 | 2023 | Commercial | Refrigeration | Pre-Fabricated Walk-In | Cooler | Electricity | Pre-Fabricated Walk-in Cooler | 2023$ |  | Commercial Walk-In Cooler | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 11809.8 | 11809.8 | 10789.2 | 10789.2 | 10558.2103 | 13100.7205 | 14983.3426 | 1 |  |  | 10558.2103 | 13100.7205 | 14983.3426 | 1.1409 | 1.1899 | 0 | 0 | 12045.535 | 14946.2061 | 17094.0313 | 12563.2857 | 15588.6357 | 17828.7804 | 2050 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented.
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
71 | 2023 | Commercial | Water Heating | Water Heater | Solar | Solar/Electricity | Commercial Water Heater Solar | 2023$ |  | Commercial Solar Water Heaters | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 1 |  |  | 5652.25 | 6782.7025 | 9559.68 | 1.23 | 1.3 | 0 | 0 | 6952.2675 | 8342.7241 | 11758.4064 | 7347.925 | 8817.5132 | 12427.584 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | 0 | 2023 | Limited data available so could not do a regression, a range of values is presented. Retail price includes, a collector, standard piping, and an electric backup storage water heater
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 575.7143 | 612.4204 | 702.2222 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 1 |  |  | 6970.7143 | 5175 | 8670 | 1.32 | 1.4966 | 0 | 0 | 9201.5978 | 6831.1892 | 11444.717 | 10432.3462 | 7744.8866 | 12975.4911 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 575.7143 | 612.4204 | 702.2222 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 1 |  |  | 6970.7143 | 5175 | 8670 | 1.32 | 1.4966 | 0 | 0 | 9201.5978 | 6831.1892 | 11444.717 | 10432.3462 | 7744.8866 | 12975.4911 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 575.7143 | 612.4204 | 702.2222 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 1 |  |  | 6970.7143 | 5175 | 8670 | 1.32 | 1.4966 | 0 | 0 | 9201.5978 | 6831.1892 | 11444.717 | 10432.3462 | 7744.8866 | 12975.4911 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 575.7143 | 612.4204 | 702.2222 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 1 |  |  | 6970.7143 | 5175 | 8670 | 1.32 | 1.4966 | 0 | 0 | 9201.5978 | 6831.1892 | 11444.717 | 10432.3462 | 7744.8866 | 12975.4911 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 575.7143 | 612.4204 | 702.2222 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 1 |  |  | 6970.7143 | 5175 | 8670 | 1.32 | 1.4966 | 0 | 0 | 9201.5978 | 6831.1892 | 11444.717 | 10432.3462 | 7744.8866 | 12975.4911 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 575.7143 | 612.4204 | 702.2222 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 1 |  |  | 6970.7143 | 5175 | 8670 | 1.32 | 1.4966 | 0 | 0 | 9201.5978 | 6831.1892 | 11444.717 | 10432.3462 | 7744.8866 | 12975.4911 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 575.7143 | 612.4204 | 702.2222 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 1 |  |  | 6970.7143 | 5175 | 8670 | 1.32 | 1.4966 | 0 | 0 | 9201.5978 | 6831.1892 | 11444.717 | 10432.3462 | 7744.8866 | 12975.4911 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 546.9286 | 581.7994 | 667.1111 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 1 |  |  | 6622.1786 | 4916.25 | 8236.5 | 1.32 | 1.4966 | 0 | 0 | 8741.5179 | 6489.6298 | 10872.4811 | 9910.7289 | 7357.6422 | 12326.7165 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 546.9286 | 581.7994 | 667.1111 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 1 |  |  | 6622.1786 | 4916.25 | 8236.5 | 1.32 | 1.4966 | 0 | 0 | 8741.5179 | 6489.6298 | 10872.4811 | 9910.7289 | 7357.6422 | 12326.7165 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 546.9286 | 581.7994 | 667.1111 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 1 |  |  | 6622.1786 | 4916.25 | 8236.5 | 1.32 | 1.4966 | 0 | 0 | 8741.5179 | 6489.6298 | 10872.4811 | 9910.7289 | 7357.6422 | 12326.7165 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 546.9286 | 581.7994 | 667.1111 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 1 |  |  | 6622.1786 | 4916.25 | 8236.5 | 1.32 | 1.4966 | 0 | 0 | 8741.5179 | 6489.6298 | 10872.4811 | 9910.7289 | 7357.6422 | 12326.7165 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 546.9286 | 581.7994 | 667.1111 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 1 |  |  | 6622.1786 | 4916.25 | 8236.5 | 1.32 | 1.4966 | 0 | 0 | 8741.5179 | 6489.6298 | 10872.4811 | 9910.7289 | 7357.6422 | 12326.7165 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 575.7143 | 612.4204 | 702.2222 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 1 |  |  | 6970.7143 | 5175 | 8670 | 1.32 | 1.4966 | 0 | 0 | 9201.5978 | 6831.1892 | 11444.717 | 10432.3462 | 7744.8866 | 12975.4911 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 518.1429 | 551.1783 | 632 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 1 |  |  | 6273.6428 | 4657.5 | 7803 | 1.32 | 1.4966 | 0 | 0 | 8281.438 | 6148.0703 | 10300.2453 | 9389.1116 | 6970.3979 | 11677.942 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 518.1429 | 551.1783 | 632 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 1 |  |  | 6273.6428 | 4657.5 | 7803 | 1.32 | 1.4966 | 0 | 0 | 8281.438 | 6148.0703 | 10300.2453 | 9389.1116 | 6970.3979 | 11677.942 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 518.1429 | 551.1783 | 632 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 1 |  |  | 6273.6428 | 4657.5 | 7803 | 1.32 | 1.4966 | 0 | 0 | 8281.438 | 6148.0703 | 10300.2453 | 9389.1116 | 6970.3979 | 11677.942 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 518.1429 | 551.1783 | 632 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 1 |  |  | 6273.6428 | 4657.5 | 7803 | 1.32 | 1.4966 | 0 | 0 | 8281.438 | 6148.0703 | 10300.2453 | 9389.1116 | 6970.3979 | 11677.942 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
72 | 2023 | Commercial | HVAC | Water Source Heat Pump |  | Electricity | Water Source Heat Pump | 2023$ |  |  | 518.1429 | 551.1783 | 632 | Cooling Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 1 |  |  | 6273.6428 | 4657.5 | 7803 | 1.32 | 1.4966 | 0 | 0 | 8281.438 | 6148.0703 | 10300.2453 | 9389.1116 | 6970.3979 | 11677.942 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 17 | 0.8584 | 2023 | 0
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
73 | 2023 | Commercial | HVAC | Variable Air Volume Box | Cool Only | Electricity | VAV Box Cool Only | 2023$ |  |  | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1 |  |  | 1487.6739 | 1501.3999 | 1509.7332 | 1.1215 | 1.243 | 0 | 0 | 1668.4051 | 1683.7985 | 1693.1442 | 1849.1362 | 1866.1971 | 1876.5552 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 6 | 0.8606 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
74 | 2023 | Commercial | HVAC | Variable Air Volume Box | Heating and Cooling | Electricity | Variable Air Volume Box Heating and Cooling | 2023$ |  |  | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1 |  |  | 1876.4 | 1951.4 | 2068.0663 | 1.1391 | 1.2782 | 0 | 0 | 2137.3966 | 2222.8287 | 2355.7226 | 2398.3932 | 2494.2574 | 2643.3789 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 9 | 0.7224 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2023 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2030 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2035 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2040 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2045 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2050 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2023 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2030 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2035 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2040 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2045 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2050 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2023 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2030 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2035 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2040 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2045 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
75 | 2023 | Commercial | HVAC | Variable Air Volume Box | Fan Powered | Electricity | Variable Air Volume Box Fan Powered | 2023$ |  |  | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 1 |  |  | 2823.6223 | 3283.1281 | 3630.567 | 1.1458 | 1.2896 | 0 | 0 | 3235.43 | 3761.9517 | 4160.0624 | 3641.2778 | 4233.8457 | 4681.8949 | 2050 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 1 | 16 | 0.1005 | 2023 | VAV boxes are an established technology and don't anticipate any major efficiency developments or price changes.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2023 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2030 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2035 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2040 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2045 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2050 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2023 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2030 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2035 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2040 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2045 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2050 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2023 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2030 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2035 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2040 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2045 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
76 | 2023 | Commercial | Refrigeration | Ice Machine | Energy Star Connected | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 1 |  |  | 4193.7413 | 4546.6595 | 4899.5777 | 1 | 1 | 857.1853 | 857.1853 | 5050.9266 | 5403.8448 | 5756.763 | 5050.9266 | 5403.8448 | 5756.763 | 2050 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | 0 | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products.
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2023 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2030 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2035 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2040 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2045 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2050 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2023 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2030 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2035 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2040 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2045 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2050 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2023 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2030 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2035 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2040 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Add-on Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2045 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
77 | 2023 | Commercial | Refrigeration | Ice Machine | Add-on Control | Electricity | Ice Machine Energy Star Connected | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 1 |  |  | 275.1799 | 343.9748 | 412.7698 | 1 | 1 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 275.1799 | 343.9748 | 412.7698 | 2050 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | 0 | 2020 | There are very few add-on controls available on the market
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2035 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2040 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2045 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
78 | 2023 | Commercial | Water Heating | Electric Resistance Water Heater | Add-On Control | Electricity | Electric Resistance Water Heater Add-On Control | 2023$ |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 1 |  |  | 137.5899 | 252.4775 | 367.3651 | 1 | 1 | 134.8381 | 134.8381 | 272.4281 | 387.3157 | 502.2033 | 272.4281 | 387.3157 | 502.2033 | 2050 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | 0 | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2023 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2030 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2035 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2040 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2045 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2050 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2023 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2030 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2035 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2040 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2045 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2050 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2023 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2030 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2035 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2040 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2045 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
79 | 2023 | Commercial | Envelope | Fenestration | Thermochromic Glazing |  | Fenestration Thermochromic Glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 12 | Square Feet | ft2 | 1039.5883 | 1100.383 | 1161.1776 | 1.31 | 1.67 | 0 | 0 | 1361.8607 | 1441.5017 | 1521.1427 | 1736.1125 | 1837.6396 | 1939.1666 | 2050 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 12 | Square Feet | ft2 | 1206.7736 | 1259.9689 | 1313.1642 | 1.31 | 1.67 | 0 | 0 | 1580.8734 | 1650.5593 | 1720.2451 | 2015.3119 | 2104.1481 | 2192.9842 | 2023 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 12 | Square Feet | ft2 | 1206.7736 | 1259.9689 | 1313.1642 | 1.31 | 1.67 | 0 | 0 | 1580.8734 | 1650.5593 | 1720.2451 | 2015.3119 | 2104.1481 | 2192.9842 | 2030 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 12 | Square Feet | ft2 | 1206.7736 | 1259.9689 | 1313.1642 | 1.31 | 1.67 | 0 | 0 | 1580.8734 | 1650.5593 | 1720.2451 | 2015.3119 | 2104.1481 | 2192.9842 | 2035 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 12 | Square Feet | ft2 | 1206.7736 | 1259.9689 | 1313.1642 | 1.31 | 1.67 | 0 | 0 | 1580.8734 | 1650.5593 | 1720.2451 | 2015.3119 | 2104.1481 | 2192.9842 | 2040 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 12 | Square Feet | ft2 | 1206.7736 | 1259.9689 | 1313.1642 | 1.31 | 1.67 | 0 | 0 | 1580.8734 | 1650.5593 | 1720.2451 | 2015.3119 | 2104.1481 | 2192.9842 | 2045 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 12 | Square Feet | ft2 | 1206.7736 | 1259.9689 | 1313.1642 | 1.31 | 1.67 | 0 | 0 | 1580.8734 | 1650.5593 | 1720.2451 | 2015.3119 | 2104.1481 | 2192.9842 | 2050 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 12 | Square Feet | ft2 | 1206.7736 | 1259.9689 | 1313.1642 | 1.31 | 1.67 | 0 | 0 | 1580.8734 | 1650.5593 | 1720.2451 | 2015.3119 | 2104.1481 | 2192.9842 | 2023 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.245 | 0.245 | 0.245 | 0.245 | 98.0314 | 102.7809 | 107.5305 | 12 | Square Feet | ft2 | 1176.3763 | 1233.3712 | 1290.3662 | 1.31 | 1.67 | 0 | 0 | 1541.0529 | 1615.7163 | 1690.3797 | 1964.5484 | 2059.73 | 2154.9116 | 2030 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.2375 | 0.2375 | 0.2375 | 0.2375 | 96.7648 | 101.5144 | 106.264 | 12 | Square Feet | ft2 | 1161.1776 | 1218.1726 | 1275.1676 | 1.31 | 1.67 | 0 | 0 | 1521.1427 | 1595.8061 | 1670.4695 | 1939.1666 | 2034.3482 | 2129.5298 | 2035 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.23 | 0.23 | 0.23 | 0.23 | 95.4982 | 100.2478 | 104.9974 | 12 | Square Feet | ft2 | 1145.9789 | 1202.9739 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1501.2324 | 1575.8958 | 1650.5593 | 1913.7848 | 2008.9665 | 2104.1481 | 2040 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.225 | 0.225 | 0.225 | 0.225 | 95.4982 | 100.2478 | 104.9974 | 12 | Square Feet | ft2 | 1145.9789 | 1202.9739 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1501.2324 | 1575.8958 | 1650.5593 | 1913.7848 | 2008.9665 | 2104.1481 | 2045 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.22 | 0.22 | 0.22 | 0.22 | 95.4982 | 100.2478 | 104.9974 | 12 | Square Feet | ft2 | 1145.9789 | 1202.9739 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1501.2324 | 1575.8958 | 1650.5593 | 1913.7848 | 2008.9665 | 2104.1481 | 2050 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 12 | Square Feet | ft2 | 1206.7736 | 1259.9689 | 1313.1642 | 1.31 | 1.67 | 0 | 0 | 1580.8734 | 1650.5593 | 1720.2451 | 2015.3119 | 2104.1481 | 2192.9842 | 2023 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.21 | 0.21 | 0.21 | 0.21 | 95.4982 | 100.5645 | 105.6307 | 12 | Square Feet | ft2 | 1145.9789 | 1206.7736 | 1267.5682 | 1.31 | 1.67 | 0 | 0 | 1501.2324 | 1580.8734 | 1660.5144 | 1913.7848 | 2015.3119 | 2116.8389 | 2030 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.195 | 0.195 | 0.195 | 0.195 | 92.9651 | 98.0314 | 103.0976 | 12 | Square Feet | ft2 | 1115.5816 | 1176.3763 | 1237.1709 | 1.31 | 1.67 | 0 | 0 | 1461.4119 | 1541.0529 | 1620.6939 | 1863.0213 | 1964.5484 | 2066.0754 | 2035 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.18 | 0.18 | 0.18 | 0.18 | 90.432 | 95.4982 | 100.5645 | 12 | Square Feet | ft2 | 1085.1843 | 1145.9789 | 1206.7736 | 1.31 | 1.67 | 0 | 0 | 1421.5914 | 1501.2324 | 1580.8734 | 1812.2578 | 1913.7848 | 2015.3119 | 2040 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.17 | 0.17 | 0.17 | 0.17 | 90.432 | 95.4982 | 100.5645 | 12 | Square Feet | ft2 | 1085.1843 | 1145.9789 | 1206.7736 | 1.31 | 1.67 | 0 | 0 | 1421.5914 | 1501.2324 | 1580.8734 | 1812.2578 | 1913.7848 | 2015.3119 | 2045 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
80 | 2023 | Commercial | Envelope | Fenestration | Electrochromic glazing |  | Fenestration Electrochromic glazing | 2023$/sqft |  |  | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.16 | 0.16 | 0.16 | 0.16 | 90.432 | 95.4982 | 100.5645 | 12 | Square Feet | ft2 | 1085.1843 | 1145.9789 | 1206.7736 | 1.31 | 1.67 | 0 | 0 | 1421.5914 | 1501.2324 | 1580.8734 | 1812.2578 | 1913.7848 | 2015.3119 | 2050 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | 0 | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 12 | Square Feet | ft2 | 75.1873 | 109.3001 | 143.4129 | 1 | 1 | 0 | 0 | 75.1873 | 109.3001 | 143.4129 | 75.1873 | 109.3001 | 143.4129 | 2023 | Reference | 30 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 12 | Square Feet | ft2 | 75.1873 | 109.3001 | 143.4129 | 1 | 1 | 0 | 0 | 75.1873 | 109.3001 | 143.4129 | 75.1873 | 109.3001 | 143.4129 | 2030 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 12 | Square Feet | ft2 | 75.1873 | 109.3001 | 143.4129 | 1 | 1 | 0 | 0 | 75.1873 | 109.3001 | 143.4129 | 75.1873 | 109.3001 | 143.4129 | 2035 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 12 | Square Feet | ft2 | 75.1873 | 109.3001 | 143.4129 | 1 | 1 | 0 | 0 | 75.1873 | 109.3001 | 143.4129 | 75.1873 | 109.3001 | 143.4129 | 2040 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 12 | Square Feet | ft2 | 75.1873 | 109.3001 | 143.4129 | 1 | 1 | 0 | 0 | 75.1873 | 109.3001 | 143.4129 | 75.1873 | 109.3001 | 143.4129 | 2045 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 12 | Square Feet | ft2 | 75.1873 | 109.3001 | 143.4129 | 1 | 1 | 0 | 0 | 75.1873 | 109.3001 | 143.4129 | 75.1873 | 109.3001 | 143.4129 | 2050 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 12 | Square Feet | ft2 | 75.1873 | 109.3001 | 143.4129 | 1 | 1 | 0 | 0 | 75.1873 | 109.3001 | 143.4129 | 75.1873 | 109.3001 | 143.4129 | 2023 | Intermediate | 30 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.0916 | 8.8473 | 11.603 | 12 | Square Feet | ft2 | 73.0988 | 106.1673 | 139.2358 | 1 | 1 | 0 | 0 | 73.0988 | 106.1673 | 139.2358 | 73.0988 | 106.1673 | 139.2358 | 2030 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.0045 | 8.7457 | 11.487 | 12 | Square Feet | ft2 | 72.0545 | 104.949 | 137.8435 | 1 | 1 | 0 | 0 | 72.0545 | 104.949 | 137.8435 | 72.0545 | 104.949 | 137.8435 | 2035 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.9175 | 8.6442 | 11.3709 | 12 | Square Feet | ft2 | 71.0103 | 103.7307 | 136.4511 | 1 | 1 | 0 | 0 | 71.0103 | 103.7307 | 136.4511 | 71.0103 | 103.7307 | 136.4511 | 2040 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.8595 | 8.5427 | 11.2259 | 12 | Square Feet | ft2 | 70.3141 | 102.5124 | 134.7106 | 1 | 1 | 0 | 0 | 70.3141 | 102.5124 | 134.7106 | 70.3141 | 102.5124 | 134.7106 | 2045 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.8015 | 8.4412 | 11.0808 | 12 | Square Feet | ft2 | 69.6179 | 101.2941 | 132.9702 | 1 | 1 | 0 | 0 | 69.6179 | 101.2941 | 132.9702 | 69.6179 | 101.2941 | 132.9702 | 2050 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 12 | Square Feet | ft2 | 75.1873 | 109.3001 | 143.4129 | 1 | 1 | 0 | 0 | 75.1873 | 109.3001 | 143.4129 | 75.1873 | 109.3001 | 143.4129 | 2023 | Advanced | 30 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.9175 | 8.5862 | 11.2549 | 12 | Square Feet | ft2 | 71.0103 | 103.0345 | 135.0587 | 1 | 1 | 0 | 0 | 71.0103 | 103.0345 | 135.0587 | 71.0103 | 103.0345 | 135.0587 | 2030 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.7435 | 8.3832 | 11.0228 | 12 | Square Feet | ft2 | 68.9217 | 100.5979 | 132.274 | 1 | 1 | 0 | 0 | 68.9217 | 100.5979 | 132.274 | 68.9217 | 100.5979 | 132.274 | 2035 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.5694 | 8.1801 | 10.7908 | 12 | Square Feet | ft2 | 66.8332 | 98.1612 | 129.4893 | 1 | 1 | 0 | 0 | 66.8332 | 98.1612 | 129.4893 | 66.8332 | 98.1612 | 129.4893 | 2040 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.4534 | 7.9771 | 10.5007 | 12 | Square Feet | ft2 | 65.4408 | 95.7246 | 126.0084 | 1 | 1 | 0 | 0 | 65.4408 | 95.7246 | 126.0084 | 65.4408 | 95.7246 | 126.0084 | 2045 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
81 | 2023 | Commercial | Envelope | Insulation | Inorganic PCM |  | Insulation Inorganic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.3374 | 7.774 | 10.2106 | 12 | Square Feet | ft2 | 64.0485 | 93.288 | 122.5275 | 1 | 1 | 0 | 0 | 64.0485 | 93.288 | 122.5275 | 64.0485 | 93.288 | 122.5275 | 2050 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 12 | Square Feet | ft2 | 69.6179 | 80.0606 | 90.5033 | 1 | 1 | 0 | 0 | 69.6179 | 80.0606 | 90.5033 | 69.6179 | 80.0606 | 90.5033 | 2023 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 12 | Square Feet | ft2 | 69.6179 | 80.0606 | 90.5033 | 1 | 1 | 0 | 0 | 69.6179 | 80.0606 | 90.5033 | 69.6179 | 80.0606 | 90.5033 | 2030 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 12 | Square Feet | ft2 | 69.6179 | 80.0606 | 90.5033 | 1 | 1 | 0 | 0 | 69.6179 | 80.0606 | 90.5033 | 69.6179 | 80.0606 | 90.5033 | 2035 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 12 | Square Feet | ft2 | 69.6179 | 80.0606 | 90.5033 | 1 | 1 | 0 | 0 | 69.6179 | 80.0606 | 90.5033 | 69.6179 | 80.0606 | 90.5033 | 2040 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 12 | Square Feet | ft2 | 69.6179 | 80.0606 | 90.5033 | 1 | 1 | 0 | 0 | 69.6179 | 80.0606 | 90.5033 | 69.6179 | 80.0606 | 90.5033 | 2045 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 12 | Square Feet | ft2 | 69.6179 | 80.0606 | 90.5033 | 1 | 1 | 0 | 0 | 69.6179 | 80.0606 | 90.5033 | 69.6179 | 80.0606 | 90.5033 | 2050 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 12 | Square Feet | ft2 | 69.6179 | 80.0606 | 90.5033 | 1 | 1 | 0 | 0 | 69.6179 | 80.0606 | 90.5033 | 69.6179 | 80.0606 | 90.5033 | 2023 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.6274 | 6.8748 | 6.9038 | 12 | Square Feet | ft2 | 67.5294 | 82.4972 | 82.8453 | 1 | 1 | 0 | 0 | 67.5294 | 82.4972 | 82.8453 | 67.5294 | 82.4972 | 82.8453 | 2030 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.5694 | 6.7877 | 6.8313 | 12 | Square Feet | ft2 | 66.8332 | 81.4529 | 81.9751 | 1 | 1 | 0 | 0 | 66.8332 | 81.4529 | 81.9751 | 66.8332 | 81.4529 | 81.9751 | 2035 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.5114 | 6.7007 | 6.7587 | 12 | Square Feet | ft2 | 66.137 | 80.4087 | 81.1049 | 1 | 1 | 0 | 0 | 66.137 | 80.4087 | 81.1049 | 66.137 | 80.4087 | 81.1049 | 2040 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.4244 | 6.4252 | 6.8603 | 12 | Square Feet | ft2 | 65.0927 | 77.1018 | 82.3232 | 1 | 1 | 0 | 0 | 65.0927 | 77.1018 | 82.3232 | 65.0927 | 77.1018 | 82.3232 | 2045 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.3374 | 6.1496 | 6.9618 | 12 | Square Feet | ft2 | 64.0485 | 73.795 | 83.5415 | 1 | 1 | 0 | 0 | 64.0485 | 73.795 | 83.5415 | 64.0485 | 73.795 | 83.5415 | 2050 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 12 | Square Feet | ft2 | 69.6179 | 80.0606 | 90.5033 | 1 | 1 | 0 | 0 | 69.6179 | 80.0606 | 90.5033 | 69.6179 | 80.0606 | 90.5033 | 2023 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.4534 | 7.0778 | 6.2656 | 12 | Square Feet | ft2 | 65.4408 | 84.9338 | 75.1873 | 1 | 1 | 0 | 0 | 65.4408 | 84.9338 | 75.1873 | 65.4408 | 84.9338 | 75.1873 | 2030 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.3374 | 6.9038 | 6.1206 | 12 | Square Feet | ft2 | 64.0485 | 82.8453 | 73.4469 | 1 | 1 | 0 | 0 | 64.0485 | 82.8453 | 73.4469 | 64.0485 | 82.8453 | 73.4469 | 2035 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.2213 | 6.7297 | 5.9755 | 12 | Square Feet | ft2 | 62.6561 | 80.7568 | 71.7064 | 1 | 1 | 0 | 0 | 62.6561 | 80.7568 | 71.7064 | 62.6561 | 80.7568 | 71.7064 | 2040 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.0473 | 6.1786 | 6.1786 | 12 | Square Feet | ft2 | 60.5676 | 74.1431 | 74.1431 | 1 | 1 | 0 | 0 | 60.5676 | 74.1431 | 74.1431 | 60.5676 | 74.1431 | 74.1431 | 2045 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
82 | 2023 | Commercial | Envelope | Insulation | Organic PCM |  | Insulation Organic PCM | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 4.8733 | 5.6274 | 6.3816 | 12 | Square Feet | ft2 | 58.479 | 67.5294 | 76.5797 | 1 | 1 | 0 | 0 | 58.479 | 67.5294 | 76.5797 | 58.479 | 67.5294 | 76.5797 | 2050 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | 0 | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by building needs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2023 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2030 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2035 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2040 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2045 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2050 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2023 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2030 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2035 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2040 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2045 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2050 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2023 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2030 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2035 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2040 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2045 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
83 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Modular | Electricity | Ice Storage for Commercial Chiller Modular | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 550 | ton hours | ton-hr | 121079.1447 | 211888.5031 | 302697.8616 | 1 | 1 | 0 | 0 | 121079.1447 | 211888.5031 | 302697.8616 | 121079.1447 | 211888.5031 | 302697.8616 | 2050 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | 0 | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2023 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2030 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2035 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2040 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2045 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2050 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2023 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 161.6682 | 161.6682 | 150000 | ton hours | ton-hr | 13415018.8679 | 24250226.4151 | 24250226.4151 | 1 | 1 | 0 | 0 | 13415018.8679 | 24250226.4151 | 24250226.4151 | 13415018.8679 | 24250226.4151 | 24250226.4151 | 2030 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 161.6682 | 161.6682 | 150000 | ton hours | ton-hr | 13415018.8679 | 24250226.4151 | 24250226.4151 | 1 | 1 | 0 | 0 | 13415018.8679 | 24250226.4151 | 24250226.4151 | 13415018.8679 | 24250226.4151 | 24250226.4151 | 2035 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 161.6682 | 161.6682 | 150000 | ton hours | ton-hr | 13415018.8679 | 24250226.4151 | 24250226.4151 | 1 | 1 | 0 | 0 | 13415018.8679 | 24250226.4151 | 24250226.4151 | 13415018.8679 | 24250226.4151 | 24250226.4151 | 2040 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 149.6291 | 173.7073 | 150000 | ton hours | ton-hr | 13415018.8679 | 22444358.4906 | 26056094.3396 | 1 | 1 | 0 | 0 | 13415018.8679 | 22444358.4906 | 26056094.3396 | 13415018.8679 | 22444358.4906 | 26056094.3396 | 2045 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2050 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2023 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 185.7464 | 137.5899 | 150000 | ton hours | ton-hr | 13415018.8679 | 27861962.2642 | 20638490.566 | 1 | 1 | 0 | 0 | 13415018.8679 | 27861962.2642 | 20638490.566 | 13415018.8679 | 27861962.2642 | 20638490.566 | 2030 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 185.7464 | 137.5899 | 150000 | ton hours | ton-hr | 13415018.8679 | 27861962.2642 | 20638490.566 | 1 | 1 | 0 | 0 | 13415018.8679 | 27861962.2642 | 20638490.566 | 13415018.8679 | 27861962.2642 | 20638490.566 | 2035 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 185.7464 | 137.5899 | 150000 | ton hours | ton-hr | 13415018.8679 | 27861962.2642 | 20638490.566 | 1 | 1 | 0 | 0 | 13415018.8679 | 27861962.2642 | 20638490.566 | 13415018.8679 | 27861962.2642 | 20638490.566 | 2040 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 161.6682 | 161.6682 | 150000 | ton hours | ton-hr | 13415018.8679 | 24250226.4151 | 24250226.4151 | 1 | 1 | 0 | 0 | 13415018.8679 | 24250226.4151 | 24250226.4151 | 13415018.8679 | 24250226.4151 | 24250226.4151 | 2045 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
84 | 2023 | Commercial | HVAC | Ice Storage for Commercial Chiller | Site-Built | Electricity | Ice Storage for Commercial Chiller Site-Built | 2023$/ton-hr |  |  | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 150000 | ton hours | ton-hr | 13415018.8679 | 20638490.566 | 27861962.2642 | 1 | 1 | 0 | 0 | 13415018.8679 | 20638490.566 | 27861962.2642 | 13415018.8679 | 20638490.566 | 27861962.2642 | 2050 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | 0 | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 4 | Square Feet | ft2 | 22.0144 | 24.7662 | 27.518 | 1 | 1 | 6.1915 | 6.1915 | 46.7806 | 49.5324 | 52.2842 | 46.7806 | 49.5324 | 52.2842 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 4 | Square Feet | ft2 | 22.0144 | 24.7662 | 27.518 | 1 | 1 | 6.1915 | 6.1915 | 46.7806 | 49.5324 | 52.2842 | 46.7806 | 49.5324 | 52.2842 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 4 | Square Feet | ft2 | 22.0144 | 24.7662 | 27.518 | 1 | 1 | 6.1915 | 6.1915 | 46.7806 | 49.5324 | 52.2842 | 46.7806 | 49.5324 | 52.2842 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 4 | Square Feet | ft2 | 22.0144 | 24.7662 | 27.518 | 1 | 1 | 6.1915 | 6.1915 | 46.7806 | 49.5324 | 52.2842 | 46.7806 | 49.5324 | 52.2842 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 4 | Square Feet | ft2 | 22.0144 | 24.7662 | 27.518 | 1 | 1 | 6.1915 | 6.1915 | 46.7806 | 49.5324 | 52.2842 | 46.7806 | 49.5324 | 52.2842 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 4 | Square Feet | ft2 | 22.0144 | 24.7662 | 27.518 | 1 | 1 | 6.1915 | 6.1915 | 46.7806 | 49.5324 | 52.2842 | 46.7806 | 49.5324 | 52.2842 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 4 | Square Feet | ft2 | 22.0144 | 24.7662 | 27.518 | 1 | 1 | 6.1915 | 6.1915 | 46.7806 | 49.5324 | 52.2842 | 46.7806 | 49.5324 | 52.2842 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.9532 | 5.5724 | 6.1915 | 4 | Square Feet | ft2 | 19.813 | 22.2896 | 24.7662 | 1 | 1 | 5.5724 | 5.5724 | 42.1025 | 44.5791 | 47.0558 | 42.1025 | 44.5791 | 47.0558 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.7469 | 5.6756 | 6.6043 | 4 | Square Feet | ft2 | 18.9874 | 22.7023 | 26.4173 | 1 | 1 | 5.3316 | 5.3316 | 40.3139 | 44.0288 | 47.7437 | 40.3139 | 44.0288 | 47.7437 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.5405 | 5.7788 | 7.0171 | 4 | Square Feet | ft2 | 18.1619 | 23.1151 | 28.0683 | 1 | 1 | 5.0908 | 5.0908 | 38.5252 | 43.4784 | 48.4317 | 38.5252 | 43.4784 | 48.4317 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.5405 | 5.7788 | 7.0171 | 4 | Square Feet | ft2 | 18.1619 | 23.1151 | 28.0683 | 1 | 1 | 5.0908 | 5.0908 | 38.5252 | 43.4784 | 48.4317 | 38.5252 | 43.4784 | 48.4317 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.5405 | 5.7788 | 7.0171 | 4 | Square Feet | ft2 | 18.1619 | 23.1151 | 28.0683 | 1 | 1 | 5.0908 | 5.0908 | 38.5252 | 43.4784 | 48.4317 | 38.5252 | 43.4784 | 48.4317 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 9.4655 | 4 | Square Feet | ft2 | 22.0144 | 24.7662 | 37.862 | 1 | 1 | 6.1915 | 6.1915 | 46.7806 | 49.5324 | 62.6282 | 46.7806 | 49.5324 | 62.6282 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.4029 | 4.9532 | 5.5036 | 4 | Square Feet | ft2 | 17.6115 | 19.813 | 22.0144 | 1 | 1 | 4.9532 | 4.9532 | 37.4245 | 39.6259 | 41.8273 | 37.4245 | 39.6259 | 41.8273 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 3.9901 | 5.1596 | 6.3291 | 4 | Square Feet | ft2 | 15.9604 | 20.6385 | 25.3165 | 1 | 1 | 4.4717 | 4.4717 | 33.8471 | 38.5252 | 43.2032 | 33.8471 | 38.5252 | 43.2032 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 3.5773 | 5.366 | 7.1547 | 4 | Square Feet | ft2 | 14.3094 | 21.464 | 28.6187 | 1 | 1 | 3.9901 | 3.9901 | 30.2698 | 37.4245 | 44.5791 | 30.2698 | 37.4245 | 44.5791 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 3.5773 | 5.366 | 7.1547 | 4 | Square Feet | ft2 | 14.3094 | 21.464 | 28.6187 | 1 | 1 | 3.9901 | 3.9901 | 30.2698 | 37.4245 | 44.5791 | 30.2698 | 37.4245 | 44.5791 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
85 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Thermal Energy Storage | Electricity | Commercial Refrigeration Thermal Energy Storage | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 3.5773 | 5.366 | 7.1547 | 4 | Square Feet | ft2 | 14.3094 | 21.464 | 28.6187 | 1 | 1 | 3.9901 | 3.9901 | 30.2698 | 37.4245 | 44.5791 | 30.2698 | 37.4245 | 44.5791 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | 0 | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2023 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2030 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2035 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2040 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2045 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2050 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2023 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2030 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2035 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2040 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2045 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2050 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2023 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 25 | 40.5 | 56 | 56 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2030 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 25 | 40.5 | 56 | 56 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2035 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 25 | 40.5 | 56 | 56 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2040 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 25 | 40.5 | 56 | 56 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2045 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
86 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 2 | Electricity | Advanced Power Strip Tier 2 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 25 | 40.5 | 56 | 56 | 17.8966 | 19.9615 | 22.0265 | 6 | outlets | outlet | 107.3793 | 119.7692 | 132.1592 | 1 | 1 | 0 | 0 | 107.3793 | 119.7692 | 132.1592 | 107.3793 | 119.7692 | 132.1592 | 2050 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | 0 | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2023 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2030 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2035 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2040 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2045 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2050 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2023 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2030 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2035 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2040 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2045 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2050 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2023 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2030 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2035 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2040 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2045 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
87 | 2023 | Commercial | Controls | Advanced Power Strip | Tier 1 | Electricity | Advanced Power Strip Tier 1 | 2023$/outlet |  |  | 0 | 0 | 0 | Number of Outlets | Unitless | 2 | 4 | 4 | 4 | 0 | 0 | 0 | Computer Energy Savings | % | 4 | 15 | 26 | 26 | 9.6366 | 13.0783 | 16.5199 | 4 | outlets | outlet | 38.5464 | 52.313 | 66.0796 | 1 | 1 | 0 | 0 | 38.5464 | 52.313 | 66.0796 | 38.5464 | 52.313 | 66.0796 | 2050 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 3 | 0 | 2020 | Tier 1 power strips use either programming/scheduling or current sensing. Tier 1 power strips will be obsolete by 2030 as market shifts to Tier 2.
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1098 | -2.8056 | -7.6546 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 326.0953 | 1093.37 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1098 | -2.8056 | -7.6546 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 326.0953 | 1093.37 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1098 | -2.8056 | -7.6546 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 326.0953 | 1093.37 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1098 | -2.8056 | -7.6546 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 326.0953 | 1093.37 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1098 | -2.8056 | -7.6546 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 326.0953 | 1093.37 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1098 | -2.8056 | -7.6546 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 326.0953 | 1093.37 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1098 | -2.8056 | -7.6546 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 326.0953 | 1093.37 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1389 | -2.879 | -7.855 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 317.9838 | 1066.1729 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.5723 | 15180.0451 | 19061.4648 | 1 | 1 | 2000 | 2000 | 13429.5723 | 17180.0451 | 21061.4648 | 13429.5723 | 17180.0451 | 21061.4648 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1538 | -2.9169 | -7.9582 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 314.1104 | 1053.1857 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.2803 | 15179.307 | 19059.4509 | 1 | 1 | 2000 | 2000 | 13429.2803 | 17179.307 | 21059.4509 | 13429.2803 | 17179.307 | 21059.4509 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1696 | -2.9567 | -8.067 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 310.237 | 1040.1985 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11428.8598 | 15178.244 | 19056.5509 | 1 | 1 | 2000 | 2000 | 13428.8598 | 17178.244 | 21056.5509 | 13428.8598 | 17178.244 | 21056.5509 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1853 | -2.9966 | -8.1757 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 306.5573 | 1027.8607 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11428.3319 | 15176.9094 | 19052.9095 | 1 | 1 | 2000 | 2000 | 13428.3319 | 17176.9094 | 21052.9095 | 13428.3319 | 17176.9094 | 21052.9095 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.2019 | -3.0385 | -8.2901 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 302.8776 | 1015.5229 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11427.6687 | 15175.2328 | 19048.3353 | 1 | 1 | 2000 | 2000 | 13427.6687 | 17175.2328 | 21048.3353 | 13427.6687 | 17175.2328 | 21048.3353 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1098 | -2.8056 | -7.6546 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 326.0953 | 1093.37 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1679 | -2.9525 | -8.0553 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 309.8724 | 1038.9758 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.1978 | -3.0282 | -8.2619 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 302.1256 | 1013.0015 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.2294 | -3.1079 | -8.4793 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 294.3787 | 987.0271 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.2609 | -3.1876 | -8.6967 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 287.0193 | 962.3514 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
88 | 2023 | Commercial | Refrigeration | Commercial Refrigeration | Supermarket Display Cases | Electricity | Commercial Supermarket Display Cases | 2023$ |  | Commercial Supermarket Display Cases | 157.7 | 206.1374 | 216.2592 | Total Display Area | ft2 | 12.8 | 51 | 65 | 65 | -1.2941 | -3.2714 | -8.9256 | Energy Use Per Total Display Area | (kWh/year)/ft2 | 61.7 | 279.6598 | 937.6757 | 1093.37 | 3749.0085 | 5582.5264 | 10530 | 1 |  |  | 11429.8079 | 15180.6408 | 19063.0901 | 1 | 1 | 2000 | 2000 | 13429.8079 | 17180.6408 | 21063.0901 | 13429.8079 | 17180.6408 | 21063.0901 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 91 | 0.799 | 2014
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 35 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 35 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 35 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 35 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 35 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 35 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 35 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 36.5 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 37.25 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 38 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 38.75 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 39.5 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 35 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 38 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 39.5 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2035 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 41 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2040 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 42.5 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2045 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
89 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Natural Gas | Gas | Commercial Natural Gas Range with Griddle and Oven | 2023$ |  | Commercial Natural Gas Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | BTU/h | 10350 | 10350 | 4178 | 4178 | 0 | 0 | 0 | Combined Energy Efficiency | % | 35 | 44 | 58 | 58 | 7242.4 | 9053 | 10863.6 | 1 |  |  | 7242.4 | 9053 | 10863.6 | 1 | 1 | 186 | 186 | 7428.4 | 9239 | 11049.6 | 7428.4 | 9239 | 11049.6 | 2050 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.4 | 1.4 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 71 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.4 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 71 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.4 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 71 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.4 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 71 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.4 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 71 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.4 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 71 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.2 | 1.35 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 71 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.2 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 72 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.2 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 72.75 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.2 | 1.25 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 73.5 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.2 | 1.25 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 73.75 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.2 | 1.25 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 74 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.3 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 71 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.3 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 73 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.3 | 1.3 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 74.5 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2035 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.2 | 1.2 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 76 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2040 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.2 | 1.2 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 76.5 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2045 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
90 | 2023 | Commercial | Cooking | Commercial Range with Griddle and Oven | Electric | Electricity | Commercial Electric Range with Griddle and Oven | 2023$ |  | Commercial Electric Range with Griddle and Oven | 0 | 0 | 0 | Combined Idle Energy Rate | kW | 1.2 | 1.2 | 0.8 | 0.8 | 0 | 0 | 0 | Combined Energy Efficiency | % | 71 | 77 | 88 | 88 | 9476.8 | 11846 | 14215.2 | 1 |  |  | 9476.8 | 11846 | 14215.2 | 1 | 1 | 186 | 186 | 9662.8 | 12032 | 14401.2 | 9662.8 | 12032 | 14401.2 | 2050 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 1 | 1 | 0 | 2023
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 15 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2382.995 | 5050.21 | 13756.99 | 1 | 1 | 0.73559 | 0.92559 | 6060.9555 | 8728.1705 | 17434.9505 | 7010.9555 | 9678.1705 | 18384.9505 | 2023 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 15 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2382.995 | 5050.21 | 13756.99 | 1 | 1 | 0.73559 | 0.92559 | 6060.9555 | 8728.1705 | 17434.9505 | 7010.9555 | 9678.1705 | 18384.9505 | 2030 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 15 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2382.995 | 5050.21 | 13756.99 | 1 | 1 | 0.73559 | 0.92559 | 6060.9555 | 8728.1705 | 17434.9505 | 7010.9555 | 9678.1705 | 18384.9505 | 2035 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 15 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2382.995 | 5050.21 | 13756.99 | 1 | 1 | 0.73559 | 0.92559 | 6060.9555 | 8728.1705 | 17434.9505 | 7010.9555 | 9678.1705 | 18384.9505 | 2040 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 15 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2382.995 | 5050.21 | 13756.99 | 1 | 1 | 0.73559 | 0.92559 | 6060.9555 | 8728.1705 | 17434.9505 | 7010.9555 | 9678.1705 | 18384.9505 | 2045 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 15 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2382.995 | 5050.21 | 13756.99 | 1 | 1 | 0.73559 | 0.92559 | 6060.9555 | 8728.1705 | 17434.9505 | 7010.9555 | 9678.1705 | 18384.9505 | 2050 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 15 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2382.995 | 5050.21 | 13756.99 | 1 | 1 | 0.73559 | 0.92559 | 6060.9555 | 8728.1705 | 17434.9505 | 7010.9555 | 9678.1705 | 18384.9505 | 2023 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 17.5 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2569.17 | 5388.8725 | 14255.8025 | 1 | 1 | 0.73559 | 0.92559 | 6247.1305 | 9066.833 | 17933.763 | 7197.1305 | 10016.833 | 18883.763 | 2030 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 18.6 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2651.087 | 5537.884 | 14475.28 | 1 | 1 | 0.73559 | 0.92559 | 6329.0475 | 9215.8445 | 18153.2405 | 7279.0475 | 10165.8445 | 19103.2405 | 2035 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 19.7 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2733.004 | 5686.8955 | 14694.7575 | 1 | 1 | 0.73559 | 0.92559 | 6410.9645 | 9364.856 | 18372.718 | 7360.9645 | 10314.856 | 19322.718 | 2040 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 20.9025 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2822.5542 | 5849.7922 | 14934.6863 | 1 | 1 | 0.73559 | 0.92559 | 6500.5147 | 9527.7527 | 18612.6468 | 7450.5147 | 10477.7527 | 19562.6468 | 2045 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 22.105 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2912.1044 | 6012.6888 | 15174.6151 | 1 | 1 | 0.73559 | 0.92559 | 6590.0649 | 9690.6494 | 18852.5757 | 7540.0649 | 10640.6494 | 19802.5757 | 2050 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 22.105 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2912.1044 | 6012.6888 | 15174.6151 | 1 | 1 | 0.73559 | 0.92559 | 6590.0649 | 9690.6494 | 18852.5757 | 7540.0649 | 10640.6494 | 19802.5757 | 2023 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 20 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2755.345 | 5727.535 | 14754.615 | 1 | 1 | 0.73559 | 0.92559 | 6433.3055 | 9405.4955 | 18432.5755 | 7383.3055 | 10355.4955 | 19382.5755 | 2030 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 22.2 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 2919.179 | 6025.558 | 15193.57 | 1 | 1 | 0.73559 | 0.92559 | 6597.1395 | 9703.5185 | 18871.5305 | 7547.1395 | 10653.5185 | 19821.5305 | 2035 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 24.4 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 3083.013 | 6323.581 | 15632.525 | 1 | 1 | 0.73559 | 0.92559 | 6760.9735 | 10001.5415 | 19310.4855 | 7710.9735 | 10951.5415 | 20260.4855 | 2040 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 26.805 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 3262.1134 | 6649.3743 | 16112.3826 | 1 | 1 | 0.73559 | 0.92559 | 6940.0739 | 10327.3349 | 19790.3432 | 7890.0739 | 11277.3349 | 20740.3432 | 2045 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
91 | 2023 | Commercial | Envelope | Wall Insulation | Interior |  | Wall Insulation Interior | 2023$/sqft |  |  | 0.014894 | 0.027093 | 0.039905 | R-Value | K*m/W/W | 1.39 | 29.21 | 49 | 49 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.25319 | 0.60365 | 2.1528 | 5000 | Square Feet | ft2 | 3441.2137 | 6975.1677 | 16592.2403 | 1 | 1 | 0.73559 | 0.92559 | 7119.1742 | 10653.1282 | 20270.2008 | 8069.1742 | 11603.1282 | 21220.2008 | 2050 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 152 | 0.05915 | 2023 | Includes all common interior insulation types: Rigid Foam, Blanket, Batt, Loose Fill, Blown, and Spray foam. Typical costs assume a wall area of 5000 sq ft as an example, though wall areas and insulation amounts vary greatly by building.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2023 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2030 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2035 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2040 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2045 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2050 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2023 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2030 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2035 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2040 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2045 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2050 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2023 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2030 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2035 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2040 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2045 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
92 | 2023 | Commercial | Envelope | Wall Insulation | Exterior |  | Wall Insulation Exterior | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.501 | 1.105 | 5.386 | 5000 | Square Feet | ft2 | 2505 | 5525 | 26930 | 1 | 1 | 1.1875 | 2.5975 | 8442.5 | 11462.5 | 32867.5 | 15492.5 | 18512.5 | 39917.5 | 2050 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 16 | 0 | 2023 | Data is for a polymer based exterior insulation and finish system. Typical prices assume an average wall area of 5,000 sq ft, though wall areas and insulation amounts vary greatly by building. No R-values were available for exterior wall insulation in RSMeans.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 5.56 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 3023.0574 | 7285.7146 | 12411.967 | 1 | 1 | 0.73559 | 0.92559 | 6701.0179 | 10963.6751 | 16089.9275 | 7651.0179 | 11913.6751 | 17039.9275 | 2023 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 5.56 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 3023.0574 | 7285.7146 | 12411.967 | 1 | 1 | 0.73559 | 0.92559 | 6701.0179 | 10963.6751 | 16089.9275 | 7651.0179 | 11913.6751 | 17039.9275 | 2030 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 5.56 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 3023.0574 | 7285.7146 | 12411.967 | 1 | 1 | 0.73559 | 0.92559 | 6701.0179 | 10963.6751 | 16089.9275 | 7651.0179 | 11913.6751 | 17039.9275 | 2035 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 5.56 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 3023.0574 | 7285.7146 | 12411.967 | 1 | 1 | 0.73559 | 0.92559 | 6701.0179 | 10963.6751 | 16089.9275 | 7651.0179 | 11913.6751 | 17039.9275 | 2040 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 5.56 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 3023.0574 | 7285.7146 | 12411.967 | 1 | 1 | 0.73559 | 0.92559 | 6701.0179 | 10963.6751 | 16089.9275 | 7651.0179 | 11913.6751 | 17039.9275 | 2045 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 5.56 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 3023.0574 | 7285.7146 | 12411.967 | 1 | 1 | 0.73559 | 0.92559 | 6701.0179 | 10963.6751 | 16089.9275 | 7651.0179 | 11913.6751 | 17039.9275 | 2050 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 5.56 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 3023.0574 | 7285.7146 | 12411.967 | 1 | 1 | 0.73559 | 0.92559 | 6701.0179 | 10963.6751 | 16089.9275 | 7651.0179 | 11913.6751 | 17039.9275 | 2023 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 7.49 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 3902.9734 | 8664.2846 | 14402.9068 | 1 | 1 | 0.73559 | 0.92559 | 7580.9339 | 12342.2452 | 18080.8673 | 8530.9339 | 13292.2452 | 19030.8673 | 2030 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 8.6775 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 4444.3724 | 9512.4981 | 15627.9021 | 1 | 1 | 0.73559 | 0.92559 | 8122.3329 | 13190.4586 | 19305.8626 | 9072.3329 | 14140.4586 | 20255.8626 | 2035 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 9.865 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 4985.7715 | 10360.7115 | 16852.8974 | 1 | 1 | 0.73559 | 0.92559 | 8663.732 | 14038.6721 | 20530.8579 | 9613.732 | 14988.6721 | 21480.8579 | 2040 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 11.07 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 5535.149 | 11221.4249 | 18095.9453 | 1 | 1 | 0.73559 | 0.92559 | 9213.1096 | 14899.3855 | 21773.9058 | 10163.1096 | 15849.3855 | 22723.9058 | 2045 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 12.275 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 6084.5266 | 12082.1384 | 19338.9931 | 1 | 1 | 0.73559 | 0.92559 | 9762.4872 | 15760.0989 | 23016.9537 | 10712.4872 | 16710.0989 | 23966.9537 | 2050 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 12.275 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 6084.5266 | 12082.1384 | 19338.9931 | 1 | 1 | 0.73559 | 0.92559 | 9762.4872 | 15760.0989 | 23016.9537 | 10712.4872 | 16710.0989 | 23966.9537 | 2023 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 9.42 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 4782.8893 | 10042.8547 | 16393.8465 | 1 | 1 | 0.73559 | 0.92559 | 8460.8498 | 13720.8152 | 20071.807 | 9410.8498 | 14670.8152 | 21021.807 | 2030 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 11.795 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 5865.6874 | 11739.2816 | 18843.8371 | 1 | 1 | 0.73559 | 0.92559 | 9543.648 | 15417.2421 | 22521.7977 | 10493.648 | 16367.2421 | 23471.7977 | 2035 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 14.17 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 6948.4855 | 13435.7085 | 21293.8277 | 1 | 1 | 0.73559 | 0.92559 | 10626.4461 | 17113.669 | 24971.7883 | 11576.4461 | 18063.669 | 25921.7883 | 2040 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 16.58 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 8047.2407 | 15157.1353 | 23779.9235 | 1 | 1 | 0.73559 | 0.92559 | 11725.2012 | 18835.0958 | 27457.884 | 12675.2012 | 19785.0958 | 28407.884 | 2045 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
93 | 2023 | Commercial | Envelope | Roof Insulation |  |  | Roof Insulation | 2023$/sqft |  |  | 0.091183 | 0.14286 | 0.20631 | R-Value | K*m/W/W | 1.3 | 18.99 | 23.26 | 23.26 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 5000 | 0 | 0 | 0.097634 | 0.66286 | 1.3353 | 5000 | Square Feet | ft2 | 9145.9958 | 16878.5622 | 26266.0192 | 1 | 1 | 0.73559 | 0.92559 | 12823.9564 | 20556.5227 | 29943.9798 | 13773.9564 | 21506.5227 | 30893.9798 | 2050 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Site assessment, Ceiling height | 2 | 42 | 0.2827 | 2023 | Insulation types include polystyrene, expanded polystyrene, fiberglass, perlite, asphaltic cover board, fiberboard high density, fiberboard low density, polyisocyanurate, and gypsum cover board. Typical costs assume an average roof area of 5,000 sq ft, thought roof area and insulation amounts vary greatly by building.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2023 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2030 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2035 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2040 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2045 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2050 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2023 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2030 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2035 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2040 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2045 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2050 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2023 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2030 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2035 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2040 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2045 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
94 | 2023 | Commercial | Controls | Building Automation System | Front End Upgrade | Electricity | BAS Front End Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.69 | 0.79 | 0.95 | 53625 | Square Feet | ft2 | 37001.25 | 42363.75 | 50943.75 | 1 | 1 | 0 | 0 | 37001.25 | 42363.75 | 50943.75 | 37001.25 | 42363.75 | 50943.75 | 2050 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2023 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2030 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2035 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2040 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2045 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2050 | Reference | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2023 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2030 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2035 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2040 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2045 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2050 | Intermediate | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2023 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2030 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2035 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2040 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2045 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
95 | 2023 | Commercial | Controls | Building Automation System | Existing System Upgrade | Electricity | BAS Existing System Upgrade | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 0.49 | 2.53 | 7.86 | 53625 | Square Feet | ft2 | 26276.25 | 135671.25 | 421492.5 | 1 | 1 | 0 | 0 | 26276.25 | 135671.25 | 421492.5 | 26276.25 | 135671.25 | 421492.5 | 2050 | Advanced | 7 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
96 | 2023 | Commercial | Controls | Building Automation System | Complete System | Electricity | BAS Complete System | 2023$/sqft |  |  | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Square Feet | ft2 | 0 | 53625 | 0 | 0 | 5.2 | 7.6 | 14.23 | 53625 | Square Feet | ft2 | 278850 | 407550 | 763083.75 | 1 | 1 | 0 | 0 | 278850 | 407550 | 763083.75 | 278850 | 407550 | 763083.75 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 1 | 0 | 2022 | Total installed cost. Assumes a typical commercial building is 53,625 sqft based on sources.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 14.8 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 14.8 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.55 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.675 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.8 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.05 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.3 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 14.8 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.25 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.5 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 17 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.
97 | 2023 | Commercial | HVAC | Air Conditioner w Gas Heat | Electric Rooftop Unit (RTU) w Gas Heat | Electricity/Gas | Electric Rooftop Unit (RTU) AC w/ Gas Heat | 2023$ |  |  | 965.21 | 1316.1317 | 1724.4907 | Cooling Capacity | Tons | 3 | 7.5 | 7.5 | 8.3 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 17.5 | 23.3 | 23.3 | -1891.3043 | -611.1111 | -724.5356 | 1 |  |  | 5347.7707 | 9259.8764 | 12209.1447 | 1.15 | 1.16 | 0 | 0 | 6149.9363 | 10648.8579 | 14040.5164 | 6203.414 | 10741.4567 | 14162.6079 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambient temperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficient units could be found online.

## Main Data Sources
Source # | Key Sources | Description | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links | Links
1 | Retail/Distributor Websites | Webscraped retail data from online distributors including Home Depot, Lowes, Supply House, and the Restaurant Store | https://www.homedepot.com/ | https://www.lowes.com/ | https://www.supplyhouse.com/ | https://www.therestaurantstore.com/ | https://hdsupplysolutions.com/ | https://www.topbulb.com/ | https://shop.regencysupply.com/ | https://www.beeslighting.com/ | https://www.energyavenue.com/ | https://www.platt.com/ | https://www.lbclighting.com/ | https://www.e-conolight.com/ | https://www.rexelenergy.com/ | https://www.greenelectricalsupply.com/ | https://www.1000bulbs.com/ | https://www.iesupply.com/ | https://www.bulbs.com/ | https://www.standardelectric.com/ | https://www.newtonelectric.com/ | https://www.grainger.com/
2 | RSMeans | Construction estimating software purchased from Gordian in 2023 | https://www.rsmeans.com/
3 | DOE Appliance Standard Technical Support Document | For each product covered by the DOE appliance standards, data on cost, shipments, efficiency, and capacity are available in the technical support documents. | https://www.regulations.gov/
4 | Homewyse | This website was used for some residential technologies to estimate installation costs. | https://www.homewyse.com/
6 | LBNL Cost of Decarbonization | This report summarizes a nationwide effort to gather home energy upgrade project cost data along with household energy performance data. This report was used for some residential technologies to estimate retrofit costs. | https://eta-publications.lbl.gov/sites/default/files/final_walker_-_the_cost_of_decarbonization_and_energy.pdf
7 | Energy Sage | Used to estimate residential solar PV costs. | https://www.energysage.com/
9 | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Provides a baseline and projected performance/cost characteristics for residential and commercial end-use equipment for a reference and advanced case scenario. This report was primarily used to develop the projections for newly collected data. | https://www.eia.gov/analysis/studies/buildings/equipcosts/pdf/full.pdf
10 | Home Guide | This website was used for some residential technologies to estimate installation costs. | https://homeguide.com/costs/
11 | Manufacturer/Contractor Estimates | For some commercial technologies, Guidehouse collected data directly from manufacturers and contractors who will remain annonymous. | N/A
12 | Energy Star | For each product that is EPA energy star certified, data efficiency and capacity are available to download online. | https://www.energystar.gov/productfinder/
13 | DOE CCMS Database | The DOE compliance certification management system (CCMCS) database products a full list of appliance standard covered products. For some technologies, this database was used to estimate the typical and high efficiencies and capacities on the market. | https://www.regulations.doe.gov/ccms
14 | Internal Guidehouse SMEs | To estimate projections for price and efficiency changes for some technologies, we consulted with internal Guidehouse subject matter experts | N/A
15 | Manufacturer Product Specifications | For some commercial technologies, efficiency, lifetime, and/or capacity data was collected from online manufacturer product specifications. | Links available in Specific Data Sources
16 | Case Study | For some commercial technologies, case studies were used to estimate prices, efficiency, capacity, and/or lifetime values. | Links available in Specific Data Sources
17 | Industry Article/Research Reports | For some commercial technologies, industry articles and research reports were used to estimate prices, efficiency, capacity, and/or lifetime values. | Links available in Specific Data Sources
18 | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | For all controls and energy storage technologies with grid-interactive capability, data and projections were taken from this data report and converted to 2023 dollars. | https://escholarship.org/content/qt44t4c2v6/qt44t4c2v6.pdf?t=qmeyoi
19 | External Researcher/SME Interview | To estimate projections for price and efficiency changes for some technologies, we consulted with external researchers and subject matter experts. | N/A
20 | Market Research Reports | To estimate projections for price and efficiency changes for some technologies, we used available market research reports. | Links available in Specific Data Sources

## Data Sources by Technology
ID | Technology Name | Retail Costs | Installation Costs | Projections | Performance Metric 1 | Performance Metric 2 | Lifetime | Additional Sources | Additional Link 1 | Additional Link 2 | Additional Link 3 | Additional Link 4 | Additional Link 5 | Additional Link 6 | Additional Link 7 | Additional Link 8 | Additional Link 9 | Additional Link 10 | Additional Link 11 | Additional Link 12 | Additional Link 13 | Additional Link 14 | Additional Link 15 | Additional Link 16 | Additional Link 17
1 | RTU Heat Pump (Standard) | RSMeans, Manufacturer Estimates | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications (See additional links: Johnson Control, Daikin, Trane, and Carrier) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Manufacturer Product Specifications (See additional links: Johnson Control, Daikin, Trane, and Carrier) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer Product Specifications: Johnson Control, Daikin, Trane, and Carrier | https://www.johnsoncontrols.com/hvac-equipment/rooftop-units#Products | https://www.daikinapplied.com/products/rooftop-systems | https://www.trane.com/commercial/north-america/us/en/products-systems/packaged-units-and-split-systems/rooftop-units/precedent.html | https://www.carrier.com/commercial/en/us/products/packaged-outdoor/outdoor-packaged-units/ | https://www.regulations.gov/document/EERE-2013-BT-STD-0007-0105
2 | RTU Heat Pump (Cold Climate) | Manufacturer estimates, DOE Appliance Standard Technical Support Document | RSMeans, DOE Appliance Standard Technical Support Document | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications (See additional links: Johnson Control, Daikin, Trane, and Carrier) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Manufacturer Product Specifications (See additional links: Johnson Control, Daikin, Trane, and Carrier) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Johnson Controls, Daikin, Trane, Carrier | https://www.johnsoncontrols.com/hvac-equipment/rooftop-units#Products | https://www.daikinapplied.com/products/rooftop-systems | https://www.trane.com/commercial/north-america/us/en/products-systems/packaged-units-and-split-systems/rooftop-units/precedent.html | https://www.carrier.com/commercial/en/us/products/packaged-outdoor/outdoor-packaged-units/
3 | Hydronic Heat Pump | Manufacturer estimates | RSMeans, Guidehouse SMEs | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Guidehouse SMEs | RSMeans, DOE Appliance Standard Technical Support Document | Manufacturer Product Specifications (See additional links) | Manufacturer Product Specifications (See additional links) | Manufacturer Product Specifications: Carrier, Trane, Raypak, ATH, Mitsubishi, SPACEPAK, Rheem, | https://www.carrier.com/commercial/en/eu/products/heating-air-conditioning/air-to-water-heat-pumps/30rq--30rqp/ | https://www.carrier.com/commercial/en/eu/products/heating-air-conditioning/air-to-water-heat-pumps/30rq-040r-160r/ | https://www.trane.com/commercial/north-america/us/en/products-systems/chillers/air-cooled-chillers/ascend-air-to-water-heat-pump.html | https://s3.amazonaws.com/AWSProd/sites/raypakcom/documents/1100.16.pdf | https://www.knseries.com/commercial-heat-pumps | https://www.mhi-mth.co.jp/en/products/heat-pump/commercial/ | https://skipthewarehouse.com/spacepak-hp0275-commercial-inverter-heat-pump-chiller-6-29-tons | https://www.rheem.com.au/rheem/products/Commercial/Commercial-Heat-Pumps/Rheem-Commercial-Air-To-Water-Heat-Pumps/Air-to-Water-%28A2W%29-16kW-Commercial-Heat-Pump--Non-Ducted/p/95301600
4 | Heat Recovery Chiller | Manufacturer estimates | RSMeans, Guidehouse SMEs | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Guidehouse SMEs | RSMeans, DOE Appliance Standard Technical Support Document | Manufacturer Product Specifications (See additional links) | Manufacturer Product Specifications (See additional links) | Manufacturer Product Specifications: Trane, Climacool, Carrier | Water-Cooled Helical Rotary Chiller (trane.com) | ClimaCool Water Cooled Modular Chillers (climacoolcorp.com) | 04-811-90019.pdf (shareddocs.com)
5 | Energy Recovery Wheel | Manufacturer estimates, RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Guidehouse SMEs | Manufacturer Product Specifications (See additional links: lennox), RSMeans | Manufacturer Product Specifications (See additional links: lennox) | Manufacturer Product Specifications (See additional links: Lennox) | Manufacturer Product Specifications: Lennox L-Series | ehb_erw_0896 (lennoxintl.com)
6 | Energy Recovery Ventilation | Retail/Distributor Websites (see additional links: HVACQuick, KitchenSource, Grainger, Vents-US), RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Guidehouse SMEs | Retail/Distributor Websites (See additional links: HVACQuick, KitchenSource, Grainger, Vents-US) | Retail/Distributor Websites (See additional links: HVACQuick, KitchenSource, Grainger, Vents-US) | Retail/Distributor Websites (See additional links: HVACQuick, KitchenSource, Grainger, Vents-US) | Manufacturer Product Specifications (See additional links: HVACQuick, KitchenSource, Grainger, Vents-US) | TRC Series Energy Recovery Ventilator with Single or Three HP Motor, 115V, 230V or 460V, 600 CFM to 2025 CFM by S&P ¦ KitchenSource.com | Energy- & Heat-Recovery Ventilators - Grainger Industrial Supply | Vents Airlite Series Commercial HRVs – Vents US Shop (vents-us.com) | Vents Airlite Series Commercial ERVs – Vents US Shop (vents-us.com) | HVACQuick - Lifebreath Commercial ERV Energy Recovery Ventilators | TRCV Series Model TRC800V Commercial Energy Recovery Ventilator, 115V or 230V, 970 CFM, Vertical by S&P¦ KitchenSource.com | TRCVe Series Model TRCE800V Commercial Energy Recovery Ventilator with EC Motor, Single Phase, 115V or 230V, 1100 CFM, Vertical by S&P¦ KitchenSource.com | TRCe Series Model TRCe800 Commercial Energy Recovery Ventilator with EC Motor, Single Phase, 115V or 230V, 925 CFM, Horizontal by S&P¦ KitchenSource.com
7 | Demand Controlled Ventilation | Industry Articles, Case Studies, Research Reports (See additional links) | N/A | Guidehouse SMEs | Industry Articles, Case Studies, Research Reports (See additional links) | N/A | Industry Articles, Case Studies, Research Reports (See additional links) | Taylor Engineering, LBNL, FPL, Irish Indendent, CO2 Meter, E Source, Footbot, Case study from New York Engineers, Minnesota Division of Energy Resources, Fixr, Illinois Statewide Technical Reference Manual, Oregon office of energy, U.S. Department of Energy, CEC 2003, Schulte et al (Schulte 2005), Haghighat et al (Haghighat 1992), | https://www.osti.gov/servlets/purl/983506 | https://www.fpl.com/content/dam/fplgp/us/en/business/save/programs/pdf/dcv-primer.pdf | https://www.independent.ie/life/home-garden/homes/how-to-treat-ventilation-and-damp-problems-in-your-home/35074417.html#:~:text=about%20%E2%82%AC400.-,In%20the%20longer%20term%20I%20would%20recommend%20a%20whole%20house,the%20bathrooms%20and%20utility%20rooms. | https://www.co2meter.com/collections/demand-controlled-ventilation | https://esource.bizenergyadvisor.com/article/demand-controlled-ventilation | https://foobot.io/resources/demand-control-ventilation-cost/#:~:text=DCV%20costs%20of%20%24300%20to,unique%20design%20of%20each%20building. | https://www.fixr.com/costs/ventilation-installation#:~:text=Demand%20controlled%20ventilation%20costs%20%24300,of%20people%20in%20the%20room. | https://www.icc.illinois.gov/downloads/public/edocket/399394.PDF | https://mn.gov/commerce-stat/pdfs/card-report-energy-savings-demand-control-ventilation.pdf | https://hvacrassets.net/handouts2/DCVGuide.pdf | https://www.energy.gov/sites/default/files/2018/05/f52/31696_Smith_043018-1630.pdf
8 | DOAS with Mini Split Heat Pumps | Manufacturer estimates, DOE Appliance Standard Technical Support Document | RSMeans, DOE Appliance Standard Technical Support Document | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Appliance Standards | https://www.regulations.gov/document/EERE-2013-BT-STD-0007-0105 | https://www.regulations.gov/document/EERE-2014-BT-STD-0048-0098
9 | DOAS with VRF | Manufacturer estimates, RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
10 | Commercial Ground Source Heat Pump | Geothermal Heat Pump Quote and Informational Survey. reddit.com | N/A | N/A | N/A | N/A | Based on Air Source Heat Pump |  | https://www.reddit.com/r/geothermal/comments/118glok/geothermal_heat_pump_quote_and_informational/
11 | Commercial TLED | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
12 | Commercial LED Troffer & Panel | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
13 | LED A19 | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
14 | LED A21 | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
15 | LED PAR38 | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
16 | LED BR30 | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
17 | Centrifugal Chiller | RSMeans, Manufacturer estimates | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier | https://www.johnsoncontrols.com/hvac-equipment/water-cooled-chillers | https://www.daikin.com/products/ac/lineup/water_cooled_chillers | https://www.trane.com/commercial/north-america/us/en/products-systems/chillers/water-cooled-chillers.html | https://www.carrier.com/commercial/en/us/products/chillers-components/water-cooled-chillers/
18 | Commercial Ice Machine Standard | DOE Appliance Standard Technical Support Document | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | DOE Appliance Standard Technical Support Document (see additional links) | DOE Appliance Standard Technical Support Document (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Appliance Standards | CommercialIceEquipStandard
19 | Oil-Fired Furnace | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Manufacturer websites (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer's website | LowestPossibleOilFAFUE | LowestOil&GasAFUEStandard
20 | Gas-Fired Furnace | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Manufacturer websites (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer's website | AlliedGasFurnace
21 | Electric Boiler (Steam) | RSMeans, Manufacturer estimates, Retail/Distributor Websites | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Retail/Distributor Websites, Manufacturer websites (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer's website | CleaverBrooksModelS | CleaverBrooksModelCR | CleaverBrooksModelHSB | LochinvarSteamBoiler
22 | Electric Boiler (Hot Water) | RSMeans, Manufacturer estimates, Manufacturer websites (see additional links) | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Retail/Distributor Websites, Manufacturer websites (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer's website | LochinvarBoiler | CBBoiler
23 | Oil-Fired Water Heater | RSMeans, EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans, EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans, EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
24 | Electric Rooftop Unit (RTU) Air Conditioner | RSMeans, Manufacturer websites (see additional links) | RSMeans | RSMeans, Manufacturer websites (see additional links) | RSMeans, Manufacturer websites (see additional links) | Manufacturer websites (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer's website | HVACDirectAC1 | HVACDirectAC2 | JCEfficiency
25 | Packaged Terminal AC | RSMeans, Retail/Distributor Websites (See additional links), DOE Appliance Standards Data | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | Manufacturer websites (see additional links), DOE Appliance Standards Data (see additional links) | RSMeans, Manufacturer websites (see additional links), DOE Appliance Standards Data (see additional links) | Manufacturer websites (see additional links), DOE Appliance Standards Data (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer's Websites | https://www.regulations.gov/document/EERE-2012-BT-STD-0029-0040 | https://northstock.com/ge-hotpoint-ah12h15d5b-heat-pump-ptac-w-elec-heat-r32-14-700-btuh-cool-30a-208-230v/ | https://northstock.com/ge-hotpoint-ah12h12e3b-heat-pump-ptac-w-elec-heat-12000-btuh-cool-20a-265v/ | https://northstock.com/ge-hotpoint-ah12h12e3b-heat-pump-ptac-w-elec-heat-12000-btuh-cool-20a-265v/ | https://northstock.com/ge-hotpoint-ah12h09e3b-heat-pump-ptac-w-elec-heat-9000-btuh-cool-20a-265v/ | https://northstock.com/ge-hotpoint-ah12h07d2b-heat-pump-ptac-w-elec-heat-7200-btuh-cool-15a-208-230v/ | https://northstock.com/ge-hotpoint-ah12h15d3b-heat-pump-ptac-w-elec-heat-14700-btuh-cool-20a-208-230v/ | https://northstock.com/ge-hotpoint-ah12e09d3b-ptac-w-elec-heat-9200-btuh-cool-20a-208-230v/ | https://northstock.com/ge-hotpoint-ah12e07d3b-ptac-w-elec-heat-7200-btuh-cool-20a-208-230v/ | https://northstock.com/ge-hotpoint-ah12e07d2b-ptac-w-elec-heat-7200-btuh-cool-15a-208-230v/ | PTAC/HP TSD
26 | Packaged Terminal HP | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | Retail/Distriubutor Website, DOE Appliance Standards Data (see additional links) | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Appliance Standards | PTAC/HP TSD
27 | Commercial Fan Coil Unit | RSMeans | RSMeans | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
28 | Electric Booster Water Heater | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | RSMeans, DOE Appliance Standard Technical Support Document (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Appliance Standards | WHStandard
29 | Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
30 | Beverage Merchandisers | RSMeans, Retail/Distributor Websites (see additional links), DOE Appliance Standards Data | RSMeans | RSMeans, Retail/Distributor Websites (see additional links), DOE Appliance Standards Data | Retail/Distributor Websites (see additional links), DOE Appliance Standards Data | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, Online Website, Manufacturer Data | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail Website | https://www.homedepot.com/p/Koolmore-35-in-W-7-4-cu-ft-2-Glass-Door-Counter-Height-Back-Bar-Cooler-Refrigerator-with-LED-Lighting-in-Black-CT35-2S-BK/313661564?MERCH=REC-_-sp-_-313661564-_-1-_-n/a-_-n/a-_-n/a-_-n/a-_-n/a&ITC=AUC-61539-23-12010 | https://www.homedepot.com/p/Koolmore-21-in-6-cu-ft-Commercial-Glass-Door-Display-Merchandiser-Refrigerator-in-Black-KM-MDR-1D-6C/325932767?MERCH=REC-_-sp-_-325932767-_-1-_-n/a-_-n/a-_-n/a-_-n/a-_-n/a&ITC=AUC-61366-23-12730 | https://www.homedepot.com/p/Koolmore-22-in-Glass-Door-Merchandiser-Refrigerator-in-Black-9-Cu-Ft-MDR-9CP/322414700 | https://www.homedepot.com/p/Koolmore-24-in-W-12-cu-ft-Commercial-Upright-Display-Glass-Door-Beverage-Refrigerator-in-Black-M-12-1G/319504762 | https://www.homedepot.com/p/Koolmore-45-in-W-38-cu-ft-Commercial-Upright-Display-Refrigerator-with-2-Swing-Glass-Door-Beverage-Cooler-in-Black-M45-2G/313661573 | https://www.homedepot.com/p/Koolmore-78-in-57-5-cu-ft-Commercial-Three-Glass-Swing-Door-Merchandiser-Refrigerator-in-Black-M78-3G/310692893 | https://www.homedepot.com/p/Koolmore-23-cu-ft-Commercial-Upright-Display-Refrigerator-Glass-Door-Merchandiser-with-LED-Lighting-in-Black-M29-1G/313666613 | https://www.homedepot.com/p/Cooler-Depot-11-cu-ft-Glass-Door-Counter-Height-Back-Bar-Refrigerator-with-LED-Interior-Light-in-Black-Coated-Steel-BBT350L/319812592?MERCH=REC-_-sp-_-319812592-_-5-_-n/a-_-n/a-_-n/a-_-n/a-_-n/a&ITC=AUC-265281-23-12730 | https://www.homedepot.com/p/Premium-LEVELLA-3-1-cu-ft-Commercial-Upright-Merchandiser-Display-Refrigerator-Glass-Door-Beverage-Cooler-in-Silver-PRF36DX/328548375 | https://www.homedepot.com/p/Premium-LEVELLA-15-5-cu-ft-Commercial-Upright-Display-Refrigerator-Glass-Door-Beverage-Cooler-in-Black-PRF1557DX/316469396 | https://www.homedepot.com/p/Elite-Kitchen-Supply-14-7-cu-ft-Commercial-Display-Cooler-Refrigerator-with-Glass-Door-in-Black-EKS-ESM16R/320118423 | https://www.homedepot.com/p/Koolmore-16-in-W-3-cu-Ft-Countertop-Commercial-Refrigerator-Glass-Display-Beverage-Cooler-in-Black-KT17-3B/309719205 | https://www.homedepot.com/p/Koolmore-53-in-W-11-cu-ft-3-Glass-Door-Counter-Height-Back-Bar-Cooler-Refrigerator-with-LED-Lighting-in-Black-CT53-3S-BK/313661565?MERCH=REC-_-sp-_-313661565-_-2-_-n/a-_-n/a-_-n/a-_-n/a-_-n/a&ITC=AUC-61539-23-12730 | https://www.homedepot.com/p/EdgeStar-22-Inch-Wide-10-1-Cu-Ft-Commercial-Beverage-Merchandiser-With-Temperature-Alarm-and-Reversible-Door-VBM101SS/326570898 | https://www.homedepot.com/p/EdgeStar-24-Inch-Wide-13-7-Cu-Ft-Commercial-Beverage-Merchandiser-With-Temperature-Alarm-and-Reversible-Door-VBM131SS/326570891 | https://www.homedepot.com/p/Cooler-Depot-22-in-9-cu-ft-Glass-Door-Merchandiser-Refrigerator-in-Black-DXXLSC-235W/327865243?MERCH=REC-_-sp-_-327865243-_-5-_-n/a-_-n/a-_-n/a-_-n/a-_-n/a&ITC=AUC-265281-23-12730 | https://www.homedepot.com/p/Cooler-Depot-22-in-9-cu-ft-Glass-Door-Merchandiser-Refrigerator-in-Black-DXXLSC-235W/327865243?MERCH=REC-_-sp-_-327865243-_-5-_-n/a-_-n/a-_-n/a-_-n/a-_-n/a&ITC=AUC-265281-23-12730
31 | Refrigerated Vending Machine | Retail/Distributor Websites (See additional links) | RSMeans | Retail/Distributor Websites (See additional links) | Retail/Distributor Websites (See additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Home Depot, Koolmore, Drops Vending, Sam's Club, | https://www.homedepot.com/p/Koolmore-39-in-Refrigerated-Vending-Machine-36-Slots-With-Bill-Acceptor-in-Black-35-cu-ft-HD-RSVMB-36/329268834 | https://koolmore.com/products/refrigerated-snack-vending-machine-with-60-slots-and-bill-acceptor-in-black-km-vmr-40-b?currency=USD&variant=40934838698073&utm_medium=cpc&utm_source=google&utm_campaign=Google%20Shopping&stkn=96a452cddc72&srsltid=AfmBOooLyocyirdp589gEs7HLXzTUe1vcuJ5NPPh0aj217uYQsI-NzlGrZU | https://dropsvending.com/new-g-series-g525-drink-vending-machine-cashless/ | https://dropsvending.com/new-g-series-g636-combo-machine/ | https://dropsvending.com/new-g-series-g654-combo-machine/ | https://evending.com/products/3-wide-combination-vending-machine?variant=44875074109761&currency=USD&utm_medium=product_sync&utm_source=google&utm_content=sag_organic&utm_campaign=sag_organic&srsltid=AfmBOopQfQTy0qtTPWRRbzlejJOXG1ba4vs6quQv4BWqo49yYz1F9G94pRw | https://www.homedepot.com/p/Koolmore-51-in-Refrigerated-Vending-Machine-60-Slots-With-CC-reader-Coin-and-Bill-Acceptor-in-Black-75-cu-ft-HD-TRSVMBCR-60/329279840 | https://www.homedepot.com/p/Koolmore-39-in-Refrigerated-Vending-Machine-36-Slots-With-CC-reader-and-Bill-Acceptor-in-Black-35-cu-ft-HD-RSVMBR-36/329279831 | https://www.homedepot.com/p/Koolmore-39-in-Refrigerated-Vending-Machine-36-Slots-With-CC-reader-and-Bill-Acceptor-in-Black-35-cu-ft-HD-RSVMBR-36/329279831 | https://www.samsclub.com/p/selectivend-cb500-10-selection-drink-vending-machine/prod21940086 | https://www.samsclub.com/p/seaga-envision-beverage-vending-machine-40-selections-choose-type/P03008573?xid=pdp_carousel_rich-relevance.rr0_8 | https://www.samsclub.com/p/cb500-sa-ada-gatorad-10-sel-drink-machine/prod9570434?xid=pdp_carousel_rich-relevance.rr0_11
32 | Gas Driven Heat Pump | RSMeans | RSMeans | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
33 | Induction Cooktop | Retail/Distributor Websites | RSMeans | Retail/Distributor Websites | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Chef's Deal | https://www.chefsdeal.com/vollrath-69507-29-countertop-induction-range.html | https://www.chefsdeal.com/vollrath-mpi4-1440s-13-countertop-induction-range.html | https://www.chefsdeal.com/vollrath-59300-12-countertop-induction-range.html | https://www.chefsdeal.com/media/pdfs_hashed/b43c999360480c2c91c4605c2a7c9869c0ebc433d8df30a2e8df3ac432faada7.pdf | https://www.chefsdeal.com/vollrath-59500p-14-countertop-induction-range.html | Vollrath 69522 15" Countertop Induction Range (chefsdeal.com) | Vollrath 924HIMC 24" Countertop Induction Range (chefsdeal.com) | Eurodib USA SWI3500 18" Countertop Induction Range (chefsdeal.com) | https://www.chefsdeal.com/equipex-octopus-3500-countertop-induction-range.html | Vollrath 69523 26" Countertop Induction Range (chefsdeal.com) | Tarrison TI-CI40-2LR 24" Countertop Induction Range (chefsdeal.com) | Equipex GL2-3500F Countertop Commercial Induction Cooktop (chefsdeal.com) | Equipex BRIC 3000 Panther Single Countertop Induction Cooktop (chefsdeal.com) | https://www.chefsdeal.com/equipex-bric-3600-15-countertop-induction-range.html | Equipex GL2-5000 Countertop Commercial Induction Cooktop (chefsdeal.com) | Equipex GL2-7000 Adventys Commercial Induction Cooktop (chefsdeal.com) | Equipex GL2-6000F Countertop Commercial Induction Cooktop (chefsdeal.com) | https://www.chefsdeal.com/summit-sinccom1-single-burner-portable-induction-cook-top-glass-surface.html | https://www.chefsdeal.com/summit-sinccom1-single-burner-portable-induction-cook-top-glass-surface.html
34 | Induction Wells | Retail/Distributor Websites | RSMeans | Retail/Distributor Websites | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Webstaurant Store, Restaurant Supply | https://www.webstaurantstore.com/vollrath-fc-6ih-06208-six-well-modular-induction-drop-in-hot-food-well-208-240v-4760w/9226IH06208.html?utm_source=google&utm_medium=freeclicks&utm_campaign=GoogleShopping&srsltid=AfmBOoqf-YjblI6OROTF1OZBMcfrc4sxMoobU1AYXFh5AVVixfG_PbB5KUw | https://www.webstaurantstore.com/hatco-iwelb-ful-a-24-1-8-x-16-x-9-5-16-drop-in-induction-dry-heated-food-well-208-240v-1-phase-720w/413IWELBFULM.html | https://www.webstaurantstore.com/vollrath-fc-6ih-01208-single-well-modular-induction-drop-in-hot-food-well-208-240v-800w/9226IH01208.html | https://www.webstaurantstore.com/vollrath-fc-6ih-02120-two-well-modular-induction-drop-in-hot-food-well-120v-1590w/9226IH02120.html | https://www.webstaurantstore.com/vollrath-fc-6ih-03120-three-well-modular-induction-drop-in-hot-food-well-120v-1590w/9226IH03120.html | https://www.webstaurantstore.com/vollrath-fc-6ih-04208-four-well-modular-induction-drop-in-hot-food-well-208-240v-3180w/9226IH04208.html | https://www.webstaurantstore.com/vollrath-fc-6ih-05208-five-well-modular-induction-drop-in-hot-food-well-208-240v-3980w/9226IH05208.html | https://www.restaurantsupply.com/cooktek-638201-ihw061-34-sinaqua-induction-hot-food-well-drop-in-rectangular?srsltid=AfmBOorIz2H60y7i4WifojMZwdAFxfFKXMu6FdRnLtewPUuN2P8AxU-tekk | https://www.restaurantsupply.com/vollrath-fc-6ih-01120-modular-1-well-induction-drop-in-dry-well-120v
35 | Air Cooled Scroll Chillers | RSMeans, Manufacturer estimates | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier | https://www.johnsoncontrols.com/hvac-equipment/air-cooled-chillers | https://www.daikinapplied.com/products/chiller-products/trailblazer | https://www.trane.com/commercial/north-america/us/en/products-systems/chillers/air-cooled-chillers.html | https://www.carrier.com/commercial/en/us/products/chillers-components/air-cooled-chillers/
36 | Air Cooled Screw Chillers | RSMeans, Manufacturer estimates | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier | https://www.johnsoncontrols.com/hvac-equipment/air-cooled-chillers | https://www.daikinapplied.com/products/chiller-products/pathfinder | https://www.trane.com/commercial/north-america/us/en/products-systems/chillers/air-cooled-chillers.html | https://www.carrier.com/commercial/en/us/products/chillers-components/air-cooled-chillers/
37 | Water Cooled Scroll Chillers | RSMeans, Manufacturer estimates | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Carrier (see additional links) | Johnson Controls (See additional links to the right) | Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier | https://www.johnsoncontrols.com/hvac-equipment/water-cooled-chillers | https://www.daikinapplied.com/products/chiller-products/water-cooled-scroll | https://www.carrier.com/commercial/en/us/products/chillers-components/water-cooled-chillers/ | https://www.johnsoncontrols.com/campaigns/chiller-life-cycle
38 | Water Cooled Screw Chillers | RSMeans, Manufacturer estimates | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans, Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier (see additional links) | Johnson Controls (See additional links to the right) | Manufacturer Product Specifications: Johnson Control, Daikn spec sheets, Trane, Carrier | https://www.york.com/commercial-equipment/chilled-water-systems/water-cooled-chillers/yvwa_ch/yvwa-variable-speed-screw-chiller | https://www.daikin.com/products/ac/lineup/water_cooled_chillers | https://www.trane.com/WEBCACHE/RLC-PRC063B-GB_01012019.PDF | https://www.johnsoncontrols.com/campaigns/chiller-life-cycle | https://www.carrier.com/commercial/en/us/products/chillers-components/water-cooled-chillers/
39 | Reciprocating Chiller (Air-Cooled) | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report, RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
40 | Variable Air Volume System | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
41 | Constant Air Volume System | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
42 | Hot food holding cabinets - large | Retail/Distributor Websites | RSMeans | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Webstaurant Store | https://www.webstaurantstore.com/true-sta1h-2hg-specification-series-glass-half-door-reach-in-heated-holding-cabinet/890TA1H2HG.html | https://www.webstaurantstore.com/true-sta2hrt-2s-2s-specification-series-two-section-roll-through-heated-holding-cabinet/890TA2HRT2S2.html | https://www.webstaurantstore.com/true-sta1h-1g-specification-series-glass-door-reach-in-stainless-steel-heated-holding-cabinet/890TA1H1G.html | https://www.webstaurantstore.com/true-sta1hrt89-1s-1s-specification-series-89-roll-through-heated-holding-cabinet/890TA1HRT891.html | https://www.webstaurantstore.com/true-sta1hpt-1s-1s-specification-series-solid-door-pass-through-heated-holding-cabinet/890TA1HP1S1S.html | https://www.webstaurantstore.com/true-sta1hpt-1g-1s-specification-series-glass-and-solid-door-pass-through-heated-holding-cabinet/890TA1HP1G1S.html | https://www.webstaurantstore.com/true-sta2h-2g-specification-series-two-section-glass-door-reach-in-heated-holding-cabinet/890TA2H2G.html | https://www.webstaurantstore.com/true-sta2hpt-2s-2s-specification-series-solid-door-pass-through-heated-holding-cabinet/890TA2HP2S2S.html
43 | Hot food holding cabinets - small and medium | Retail/Distributor Websites | RSMeans | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Webstaurant Store | https://www.webstaurantstore.com/cambro-upch800192-granite-green-ultra-camcart-two-compartment-heated-holding-pan-carrier-with-casters-both-compartments-heated-110v/214UPCH800GN.html | https://www.webstaurantstore.com/cambro-upch16002192-granite-green-ultra-camcart-two-compartment-heated-holding-pan-carrier-with-casters-both-compartments-heated-220v-international-use-only/214UPCH1602G.html | https://www.webstaurantstore.com/cambro-upcht16002hd191-granite-gray-ultra-camcart-two-compartment-heated-holding-pan-carrier-with-heavy-duty-casters-top-compartment-heated-only-220v-international-use-only/214UPCHT62SH.html | https://www.webstaurantstore.com/cambro-upch1600hd191-granite-gray-ultra-camcart-two-compartment-heated-holding-pan-carrier-with-heavy-duty-casters-110v/214UPCH160SH.html | https://www.webstaurantstore.com/cambro-upch8002191-granite-gray-ultra-camcart-two-compartment-heated-holding-pan-carrier-with-casters-both-compartments-heated-220v-international-use-only/214UPCH802GY.html | https://www.webstaurantstore.com/cambro-upch16002sp191-granite-gray-ultra-camcart-two-compartment-heated-holding-pan-carrier-with-security-package-220v-international-use-only/214UPCH162SS.html | https://www.webstaurantstore.com/hatco-fsdt-1-flav-r-savor-humidified-hot-food-holding-display-cabinet-with-4-tier-circle-rack/413FSDT1.html | https://www.webstaurantstore.com/hatco-fdwd-1x-flav-r-fresh-humidified-impulse-hot-food-display-cabinet-with-4-shelf-stationary-rack/413FDWD1X.html
44 | Compressor Rack Systems | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
45 | Condensers | RSMeans | RSMeans | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
46 | LED High/Low-Bay | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
47 | LED Troffer or Panel Connected with Integrated Controls | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
48 | LED Troffer or Panel with Dimming | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
49 | 100W Equivalent CFL Bare Spiral | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
50 | High-Bay Metal Halide | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
51 | High-Bay Sodium Vapor | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
52 | Low-Bay Metal Halide | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
53 | Low-Bay Sodium Vapor | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites | Retail/Distributor Websites | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
54 | Fenestration Double-Pane, Aluminum Frame | RSMeans | RSMeans, Homewyse | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Retail/Distributor Websites: Home Depot, ENERGY STAR Certified Products | Retail/Distributor Websites: Home Depot, ENERGY STAR Certified Products | NREL National Residential Energy Measure Database
55 | Fenestration Double-Pane, Wood Frame | Retail/Distributor Websites, RSMeans | RSMeans, Homewyse | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Retail/Distributor Websites: Home Depot, ENERGY STAR Certified Products | Retail/Distributor Websites: Home Depot, ENERGY STAR Certified Products | NREL National Residential Energy Measure Database
56 | Fenestration Double-Pane, Vinyl Frame | Retail/Distributor Websites, RSMeans | RSMeans, Homewyse | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Retail/Distributor Websites: Home Depot, ENERGY STAR Certified Products | Retail/Distributor Websites: Home Depot, ENERGY STAR Certified Products | NREL National Residential Energy Measure Database
57 | Fenestration Triple-Pane, Vinyl Frame | Retail/Distributor Websites, RSMeans | RSMeans, Homewyse | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Retail/Distributor Websites: Home Depot, ENERGY STAR Certified Products | Retail/Distributor Websites: Home Depot, ENERGY STAR Certified Products | NREL National Residential Energy Measure Database
58 | Fenestration Window Film | RSMeans | RSMeans | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | NFRC Window Film Ratings (3M products) | NFRC Window Film Ratings (3M products) | NREL National Residential Energy Measure Database | NFRC | https://search.nfrc.org/search/apd_film/film_search_productline.aspx?mfr=1323&mfr_nm=3M
59 | Commercial Boiler Gas | Retail/Distributor Websites (See additional links: Supply House) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites (See additional links: Supply House) | Retail/Distributor Websites (See additional links: Supply House) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Supply House | https://www.supplyhouse.com/Boilers-449000
60 | Commercial Water Heater Electric Storage | Retail/Distributor Websites (See additional links: Supply House) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites (See additional links: Supply House) | Retail/Distributor Websites (See additional links: Supply House) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Supply House | https://www.supplyhouse.com/Commercial-Water-Heaters-29960000
61 | Commercial Reach-in Freezer | DOE Appliance Standard Technical Support Document (See additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | DOE Appliance Standard Technical Support Document (See additional links) | DOE Appliance Standard Technical Support Document (See additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Appliance Standards | https://www.regulations.gov/document/EERE-2010-BT-STD-0003-0102 | https://www.regulations.gov/document/EERE-2010-BT-STD-0003-0098
62 | Commercial Reach-in Refrigerator | DOE Appliance Standard Technical Support Document (See additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | DOE Appliance Standard Technical Support Document (See additional links) | DOE Appliance Standard Technical Support Document (See additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Appliance Standards | https://www.regulations.gov/document/EERE-2010-BT-STD-0003-0102 | https://www.regulations.gov/document/EERE-2010-BT-STD-0003-0098
63 | Unit Heater Electric | Retail/Distributor Websites (See additional links: Grainger) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites (See additional links: Grainger) | N/A | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Grainger | https://www.grainger.com/category/hvac-and-refrigeration/heaters/electric-heaters/electric-wall-ceiling-heaters/suspended-electric-wall-ceiling-unit-heaters?categoryIndex=6
64 | Commercial Boiler Oil | DOE Appliance Standard Technical Support Document (See additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | DOE Appliance Standard Technical Support Document (See additional links) | DOE Appliance Standard Technical Support Document (See additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Appliance Standards | https://www.regulations.gov/document/EERE-2013-BT-STD-0030-0083
65 | Commercial Water Heater Gas Storage | Retail/Distributor Websites (See additional links: Supply House) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites (See additional links: Supply House) | Retail/Distributor Websites (See additional links: Supply House) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Supply House | https://www.supplyhouse.com/Commercial-Water-Heaters-29960000
66 | Commercial Water Heater Gas Booster | Retail/Distributor Websites (See additional links: Katom Restaurant Supply, Central Restaurant Products) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites (See additional links: Katom Restaurant Supply, Central Restaurant Products ) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Katom Restaurant Supply, Central Restaurant Products | https://www.katom.com/cat/water-booster-heaters.html?heat=Gas | https://www.centralrestaurant.com/category/dishwashing-and-janitorial/commercial-dishwashers/booster-heaters.html?power_type=Natural+Gas+or+LP+Must+Specify
67 | Commercial Water Heater Heat Pump | Retail/Distributor Websites (See additional links: AF Supply, FW Webb, Ebay) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Energy Star | Energy Star | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | AF Supply, FW Webb, Ebay | https://www.afsupply.com/ao-smith-cahp-120-119-gallons-12-kw-commercial-heat-pump-water-heater.html?srsltid=AfmBOopJIrH4pein1XoW293l3XU3sGzSxBGOJIY9YGh4eK1y10w2SRZGEVQ | https://www.fwwebb.com/product/Lochinvar/Water-Heater/CHPA120PD/1188149
68 | Commercial Water Heater Gas Instantaneous | Retail/Distributor Websites (See additional links: Supply House) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Retail/Distributor Websites (See additional links: Supply House) | Retail/Distributor Websites (See additional links: Supply House) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Supply House | https://www.supplyhouse.com/Tankless-Water-Heaters-1060000
69 | Pre-Fabricated Walk-in Freezer | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
70 | Pre-Fabricated Walk-in Cooler | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
71 | Commercial Water Heater Solar | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans, Energy Star | RSMeans, Energy Star | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
72 | Water Source Heat Pumps | RSMeans | RSMeans | RSMeans | RSMeans | RSMeans | Water Furnace Inc | Water Furnace Inc | https://www.waterfurnace.com/commercial/why-waterfurnace/technology#:~:text=Long%20Life,can%20last%20more%20than%20100.
73 | VAV Box (Cool Only) | RSMeans, Manufacturer estimates | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
74 | VAV Box (Heat and Cool) | RSMeans, Manufacturer estimates | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
75 | VAV Box (Fan Powered) | RSMeans, Manufacturer estimates | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | RSMeans | RSMeans | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
76 | Ice Machine Energy Star Connected | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
77 | Ice Machine Add-on Control | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
78 | Electric Resistance Water Heater Add-On Control | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
79 | Commercial Fenestration Thermochromic Glazing | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
80 | Commercial Fenestration Electrochromic Glazing | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
81 | Insulation Inorganic PCM | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
82 | Insulation Organic PCM | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
83 | Ice Storage for Commercial Chiller Modular | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
84 | Ice Storage for Commercial Chiller Site-Built | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
85 | Commercial Refrigeration Thermal Energy Storage | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
86 | Advanced Power Strip Tier 2 | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
87 | Advanced Power Strip Tier 1 | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
88 | Supermarket Display Cases | DOE Appliance Standard Technical Support Document (See additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | DOE Appliance Standard Technical Support Document (See additional links) | DOE Appliance Standard Technical Support Document (See additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Appliance Standards | https://www.regulations.gov/document/EERE-2010-BT-STD-0003-0102 | https://www.regulations.gov/document/EERE-2010-BT-STD-0003-0098
89 | Commercial Natural Gas Range with Griddle and Oven | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
90 | Commercial Electric Range with Griddle and Oven | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report
91 | Wall Insulation Interior | RSMeans | RSMeans | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | RSMeans | N/A | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
92 | Wall Insulation Exterior | RSMeans | RSMeans | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | N/A | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
93 | Roof Insulation | RSMeans | RSMeans | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics | RSMeans | N/A | Grid-Interactive Efficient Building Technology Cost, Performance, and Lifetime Characteristics
94 | BAS Front End Upgrade | Commercial Building Sensors and Controls Systems – Barriers, Drivers, and Costs | Commercial Building Sensors and Controls Systems – Barriers, Drivers, and Costs | Commercial Building Sensors and Controls Systems – Barriers, Drivers, and Costs | N/A | N/A | ACHR |  | https://www.nrel.gov/docs/fy22osti/82117.pdf | https://www.achrnews.com/articles/152914-age-technology-dictate-building-controls-lifespan
95 | BAS Existing System Upgrade | Commercial Building Sensors and Controls Systems – Barriers, Drivers, and Costs | Commercial Building Sensors and Controls Systems – Barriers, Drivers, and Costs | Commercial Building Sensors and Controls Systems – Barriers, Drivers, and Costs | N/A | N/A | ACHR |  | https://www.nrel.gov/docs/fy22osti/82117.pdf | https://www.achrnews.com/articles/152914-age-technology-dictate-building-controls-lifespan
96 | BAS Complete System | Commercial Building Sensors and Controls Systems – Barriers, Drivers, and Costs | Commercial Building Sensors and Controls Systems – Barriers, Drivers, and Costs | Commercial Building Sensors and Controls Systems – Barriers, Drivers, and Costs | N/A | N/A | ACHR |  | https://www.nrel.gov/docs/fy22osti/82117.pdf | https://www.achrnews.com/articles/152914-age-technology-dictate-building-controls-lifespan
97 | Electric Rooftop Unit (RTU) AC w/ Gas Heat | RSMeans, Manufacturer websites (see additional links), Manufacturer Interview | RSMeans, Manufacturer Interview | RSMeans, Manufacturer websites (see additional links) | RSMeans, Manufacturer websites (see additional links) | Manufacturer websites (see additional links) | EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Report | Manufacturer's website | HVACDirectAC1 | HVACDirectAC2 | JCEfficiency

## Tableau Tables (hidden)
Component & Class | [10 empty] | Retail Price Regression, Performance metric 1 | [8 empty] | Retail Price Regression, Performance metric 2 | [8 empty] | Retail Price Regression, Intercepts |  |  |  | Installation Multiplier |  | Installation Adder |  |  |  | Projection |  | Additional Data
Technology/Measure ID | atb_year | End Use Category | Fuel Type | Building Type | Most Granular NREMDB Tech/Measure | Most Granular EIA/Scout Tech/Measure | Component | Technology/Measure | Display Name | Output Units | Coefficient-Low | Coefficient-Mid | Coefficient-High | Metric | Unit | Lower Bound | Typical | High | Upper Bound | Coefficient-Low | Coefficient-Mid | Coefficient-High | Metric | Unit | Lower Bound | Typical | High | Upper Bound | Int-Low | Int-Mid | Int-High | Typical Retail Price ($2023) | New Construction | Retrofit | New Construction | Retrofit | Typical New Construction Installed Cost ($2023) | Typical Retrofit Installed Cost ($2023) | Year | Scenario | Lifetime (Years) | Cost Variation Considerations | Source Diversity | Sample Size | R^2 | Data Age | Notes | 2023 Typical Retail Price (2023 $/Unit) | 2023 Typical New Construction Installed Cost (2023 $/Unit) | 2023 Typical Retrofit Installed Cost (2023 $/Unit
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1656.9231 | 1868.1297 | 1999.7929 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.25 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 12087.2971 | 1.2159 | 1.2688 | 0 | 0 | 14696.9433 | 15336.097 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 12087.2971 | 14696.9433 | 15336.097
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1656.9231 | 1868.1297 | 1999.7929 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.25 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 12087.2971 | 1.2159 | 1.2688 | 0 | 0 | 14696.9433 | 15336.097 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 12087.2971 | 14696.9433 | 15336.097
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1656.9231 | 1868.1297 | 1999.7929 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.25 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 12087.2971 | 1.2159 | 1.2688 | 0 | 0 | 14696.9433 | 15336.097 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 12087.2971 | 14696.9433 | 15336.097
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1656.9231 | 1868.1297 | 1999.7929 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.25 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 12087.2971 | 1.2159 | 1.2688 | 0 | 0 | 14696.9433 | 15336.097 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 12087.2971 | 14696.9433 | 15336.097
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1656.9231 | 1868.1297 | 1999.7929 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.25 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 12087.2971 | 1.2159 | 1.2688 | 0 | 0 | 14696.9433 | 15336.097 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 12087.2971 | 14696.9433 | 15336.097
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1656.9231 | 1868.1297 | 1999.7929 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.25 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 12087.2971 | 1.2159 | 1.2688 | 0 | 0 | 14696.9433 | 15336.097 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 12087.2971 | 14696.9433 | 15336.097
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1656.9231 | 1868.1297 | 1999.7929 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.25 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 12087.2971 | 1.2159 | 1.2688 | 0 | 0 | 14696.9433 | 15336.097 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 12087.2971 | 14696.9433 | 15336.097
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1521.2577 | 1715.1712 | 1836.0541 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 564.9982 | 534.3298 | 818.2307 | IEER | Unitless | 10.6 | 14.325 | 20.3 | 21.5 | -9407.2203 | -9380.3685 | -12801.8744 | 11137.6894 | 1.2159 | 1.2688 | 0 | 0 | 15084.4694 | 15740.4762 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 11097.6147 | 13493.5885 | 14080.4096
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1492.7673 | 1683.0491 | 1801.6681 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 554.4168 | 524.3228 | 802.9067 | IEER | Unitless | 10.6 | 14.55 | 20.3 | 21.5 | -9231.0403 | -9204.6914 | -12562.1188 | 11047.0735 | 1.2159 | 1.2688 | 0 | 0 | 15112.9165 | 15770.1604 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 10889.7767 | 13240.8784 | 13816.7094
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1464.277 | 1650.9271 | 1767.2822 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 543.8355 | 514.3158 | 787.5827 | IEER | Unitless | 10.6 | 14.775 | 20.3 | 21.5 | -9054.8604 | -9029.0143 | -12322.3632 | 10951.9545 | 1.2159 | 1.2688 | 0 | 0 | 15140.5462 | 15798.9916 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 10681.9387 | 12988.1682 | 13553.0092
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1449.5879 | 1634.3657 | 1749.5535 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 538.3799 | 509.1563 | 779.682 | IEER | Unitless | 10.6 | 14.775 | 20.3 | 21.5 | -8964.0257 | -8938.4389 | -12198.7502 | 10842.0889 | 1.2159 | 1.2688 | 0 | 0 | 15167.3931 | 15827.0061 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 10574.7819 | 12857.8762 | 13417.0509
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1434.8989 | 1617.8043 | 1731.8249 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 532.9244 | 503.9969 | 771.7813 | IEER | Unitless | 10.6 | 14.775 | 20.3 | 21.5 | -8873.191 | -8847.8635 | -12075.1373 | 10732.2234 | 1.2159 | 1.2688 | 0 | 0 | 15193.4901 | 15854.2381 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 10467.625 | 12727.5841 | 13281.0925
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1656.9231 | 1868.1297 | 1999.7929 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 615.3846 | 581.9812 | 891.2003 | IEER | Unitless | 10.6 | 14.25 | 20.3 | 21.5 | -10246.1538 | -10216.9074 | -13943.5424 | 12087.2971 | 1.2159 | 1.2688 | 0 | 0 | 14696.9433 | 15336.097 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 12087.2971 | 14696.9433 | 15336.097
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1349.0895 | 1521.0568 | 1628.2588 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 501.0546 | 473.8571 | 725.6275 | IEER | Unitless | 10.6 | 14.4 | 20.3 | 21.5 | -8342.559 | -8318.7461 | -11353.0234 | 9912.7217 | 1.2159 | 1.2688 | 0 | 0 | 14890.7064 | 15538.2866 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 9841.6431 | 11966.4528 | 12486.8605
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1344.9893 | 1516.434 | 1623.3101 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 499.5318 | 472.4169 | 723.4221 | IEER | Unitless | 10.6 | 14.85 | 20.3 | 21.5 | -8317.2039 | -8293.4634 | -11318.5189 | 10095.1821 | 1.2159 | 1.2688 | 0 | 0 | 14904.9299 | 15553.1287 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 9811.732 | 11930.0839 | 12448.91
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1340.8891 | 1511.8111 | 1618.3615 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 498.0089 | 470.9767 | 721.2168 | IEER | Unitless | 10.6 | 15.3 | 20.3 | 21.5 | -8291.8489 | -8268.1808 | -11284.0143 | 10276.3464 | 1.2159 | 1.2688 | 0 | 0 | 14918.7447 | 15567.5443 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 9781.8209 | 11893.715 | 12410.9594
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1311.511 | 1478.6882 | 1582.9041 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 487.0979 | 460.6579 | 705.4153 | IEER | Unitless | 10.6 | 15.3 | 20.3 | 21.5 | -8110.1795 | -8087.0299 | -11036.7884 | 10051.1979 | 1.2159 | 1.2688 | 0 | 0 | 14932.1682 | 15581.5516 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 9567.5071 | 11633.1309 | 12139.0428
1 | 2023 | Heating, Cooling | Electricity | Commercial |  | Rooftop Heat Pumps | RTU Heat Pump | Standard | RTU Heat Pump Standard | 2023$ | 1282.1329 | 1445.5654 | 1547.4468 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 476.1868 | 450.3391 | 689.6139 | IEER | Unitless | 10.6 | 15.3 | 20.3 | 21.5 | -7928.5101 | -7905.8791 | -10789.5625 | 9826.0494 | 1.2159 | 1.2688 | 0 | 0 | 14945.2167 | 15595.1675 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 76 | 0.885 | 2017 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; Assumes reuse of existing ductwork | 9353.1933 | 11372.5468 | 11867.1262
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2486.4118 | 2730.2074 | 3109.9311 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 18623.5833 | 1.1167 | 1.1795 | 0 | 0 | 20796.3182 | 21966.9615 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18623.5833 | 20796.3182 | 21966.9615
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2486.4118 | 2730.2074 | 3109.9311 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 18623.5833 | 1.1167 | 1.1795 | 0 | 0 | 20796.3182 | 21966.9615 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18623.5833 | 20796.3182 | 21966.9615
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2486.4118 | 2730.2074 | 3109.9311 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 18623.5833 | 1.1167 | 1.1795 | 0 | 0 | 20796.3182 | 21966.9615 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18623.5833 | 20796.3182 | 21966.9615
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2486.4118 | 2730.2074 | 3109.9311 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 18623.5833 | 1.1167 | 1.1795 | 0 | 0 | 20796.3182 | 21966.9615 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18623.5833 | 20796.3182 | 21966.9615
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2486.4118 | 2730.2074 | 3109.9311 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 18623.5833 | 1.1167 | 1.1795 | 0 | 0 | 20796.3182 | 21966.9615 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18623.5833 | 20796.3182 | 21966.9615
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2486.4118 | 2730.2074 | 3109.9311 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 18623.5833 | 1.1167 | 1.1795 | 0 | 0 | 20796.3182 | 21966.9615 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18623.5833 | 20796.3182 | 21966.9615
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2486.4118 | 2730.2074 | 3109.9311 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 18623.5833 | 1.1167 | 1.1795 | 0 | 0 | 20796.3182 | 21966.9615 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18623.5833 | 20796.3182 | 21966.9615
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2453.4033 | 2693.9624 | 3068.6451 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2377.0469 | -1828.3731 | -2115.6997 | 18930.5846 | 1.1167 | 1.1795 | 0 | 0 | 21139.1361 | 22329.0769 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18376.3452 | 20520.236 | 21675.3383
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2484.9243 | 2728.5741 | 3108.0707 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2407.5869 | -1851.8638 | -2142.8819 | 18953.1206 | 1.1167 | 1.1795 | 0 | 0 | 21164.3013 | 22355.6587 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18612.4421 | 20783.8772 | 21953.8202
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2516.4453 | 2763.1858 | 3147.4962 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2438.1269 | -1875.3545 | -2170.0641 | 18975.009 | 1.1167 | 1.1795 | 0 | 0 | 21188.7434 | 22381.4766 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18848.5389 | 21047.5185 | 22232.302
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2494.4027 | 2738.9818 | 3119.9259 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2416.7703 | -1858.9275 | -2151.0556 | 18996.2774 | 1.1167 | 1.1795 | 0 | 0 | 21212.493 | 22406.5631 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18683.4362 | 20863.154 | 22037.5595
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2472.36 | 2714.7779 | 3092.3556 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2395.4136 | -1842.5004 | -2132.047 | 19016.9517 | 1.1167 | 1.1795 | 0 | 0 | 21235.5793 | 22430.9489 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18518.3335 | 20678.7895 | 21842.8169
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2486.4118 | 2730.2074 | 3109.9311 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2409.0281 | -1852.9723 | -2144.1646 | 18623.5833 | 1.1167 | 1.1795 | 0 | 0 | 20796.3182 | 21966.9615 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18623.5833 | 20796.3182 | 21966.9615
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2365.618 | 2597.5697 | 2958.8458 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2291.9937 | -1762.952 | -2039.9977 | 18777.0839 | 1.1167 | 1.1795 | 0 | 0 | 20967.7272 | 22148.0192 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 17718.8205 | 19786.0006 | 20899.7722
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2508.0136 | 2753.9273 | 3136.95 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2429.9576 | -1869.0708 | -2162.793 | 18788.3519 | 1.1167 | 1.1795 | 0 | 0 | 20980.3098 | 22161.3101 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 18785.3839 | 20976.9954 | 22157.8092
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2650.4092 | 2910.2849 | 3315.0542 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2567.9214 | -1975.1897 | -2285.5882 | 18799.2962 | 1.1167 | 1.1795 | 0 | 0 | 20992.5308 | 22174.219 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 19851.9473 | 22167.9903 | 23415.8462
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2606.3238 | 2861.877 | 3259.9136 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2525.2081 | -1942.3355 | -2247.5711 | 18809.9303 | 1.1167 | 1.1795 | 0 | 0 | 21004.4056 | 22186.7623 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 19521.7419 | 21799.2612 | 23026.361
2 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | RTU Heat Pump | Cold Climate | RTU Heat Pump Cold Climate | 2023$ | 2562.2385 | 2813.4691 | 3204.773 | Capacity | Tons | 3 | 7.5 | 30 | 30 | 0 | 0 | 0 | IEER | Unitless | 0 | 0 | 0 | 0 | -2482.4949 | -1909.4814 | -2209.554 | 18820.2675 | 1.1167 | 1.1795 | 0 | 0 | 21015.9487 | 22198.9552 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 30 | 0.8516 | 2024 | Cost of Roof curb adapters is included; Updated DOE Rulemaking will be coming sometime over the next couple of months with updated data and new efficiency metric IVEC (integrated ventilation, economizer, and cooling). IVEC takes into account factors such as outdoor air intake, economizer operation (which utilizes outdoor air for cooling when conditions allow), and ventilation rates to determine the overall efficiency of the system; THere are no typical or bounded efficiency values because CCHPs are an emerging technology without units on teh market; Assumes reuse of existing ductwork | 19191.5365 | 21430.5322 | 22636.8759
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.7 | 4.3 | 4.3 | 2000 | 2250 | 2500 | 157500 | 1.2158 | 1.2294 | 0 | 0 | 191488.5 | 193626.3 | 2023 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 157500 | 191488.5 | 193626.3
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.9027 | 4.3 | 4.3 | 2150.9434 | 2419.8113 | 2688.6792 | 169386.7925 | 1.2158 | 1.2294 | 0 | 0 | 205940.4623 | 208239.6057 | 2030 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 169386.7925 | 205940.4623 | 208239.6057
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.9577 | 4.3 | 4.3 | 2188.6792 | 2462.2642 | 2735.8491 | 172358.4906 | 1.2158 | 1.2294 | 0 | 0 | 209553.4528 | 211892.9321 | 2035 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 172358.4906 | 209553.4528 | 211892.9321
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0127 | 4.3 | 4.3 | 2226.4151 | 2504.717 | 2783.0189 | 175330.1887 | 1.2158 | 1.2294 | 0 | 0 | 213166.4434 | 215546.2585 | 2040 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 175330.1887 | 213166.4434 | 215546.2585
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0708 | 4.3 | 4.3 | 2289.3082 | 2575.4717 | 2861.6352 | 180283.0189 | 1.2158 | 1.2294 | 0 | 0 | 219188.0943 | 221635.1358 | 2045 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 180283.0189 | 219188.0943 | 221635.1358
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.129 | 4.3 | 4.3 | 2352.2013 | 2646.2264 | 2940.2516 | 185235.8491 | 1.2158 | 1.2294 | 0 | 0 | 225209.7453 | 227724.0132 | 2050 | Reference | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 185235.8491 | 225209.7453 | 227724.0132
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.7 | 4.3 | 4.3 | 2000 | 2250 | 2500 | 157500 | 1.2158 | 1.2294 | 0 | 0 | 191488.5 | 193626.3 | 2023 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 157500 | 191488.5 | 193626.3
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.9631 | 4.3 | 4.3 | 2201.2579 | 2476.4151 | 2751.5723 | 173349.0566 | 1.2158 | 1.2294 | 0 | 0 | 210757.783 | 213110.7075 | 2030 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 173349.0566 | 210757.783 | 213110.7075
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0189 | 4.3 | 4.3 | 2220.1258 | 2497.6415 | 2775.1572 | 174834.9057 | 1.2158 | 1.2294 | 0 | 0 | 212564.2783 | 214937.3708 | 2035 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 174834.9057 | 212564.2783 | 214937.3708
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0747 | 4.3 | 4.3 | 2238.9937 | 2518.8679 | 2798.7421 | 176320.7547 | 1.2158 | 1.2294 | 0 | 0 | 214370.7736 | 216764.034 | 2040 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 176320.7547 | 214370.7736 | 216764.034
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.1338 | 4.3 | 4.3 | 2295.5975 | 2582.5472 | 2869.4969 | 180778.3019 | 1.2158 | 1.2294 | 0 | 0 | 219790.2594 | 222244.0236 | 2045 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 180778.3019 | 219790.2594 | 222244.0236
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.1928 | 4.3 | 4.3 | 2352.2013 | 2646.2264 | 2940.2516 | 185235.8491 | 1.2158 | 1.2294 | 0 | 0 | 225209.7453 | 227724.0132 | 2050 | Intermediate | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 185235.8491 | 225209.7453 | 227724.0132
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 3.7 | 4.3 | 4.3 | 2000 | 2250 | 2500 | 157500 | 1.2158 | 1.2294 | 0 | 0 | 191488.5 | 193626.3 | 2023 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 157500 | 191488.5 | 193626.3
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0234 | 4.3 | 4.3 | 2251.5723 | 2533.0189 | 2814.4654 | 177311.3208 | 1.2158 | 1.2294 | 0 | 0 | 215575.1038 | 217981.8094 | 2030 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 177311.3208 | 215575.1038 | 217981.8094
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.0801 | 4.3 | 4.3 | 2251.5723 | 2533.0189 | 2814.4654 | 177311.3208 | 1.2158 | 1.2294 | 0 | 0 | 215575.1038 | 217981.8094 | 2035 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 177311.3208 | 215575.1038 | 217981.8094
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.1368 | 4.3 | 4.3 | 2251.5723 | 2533.0189 | 2814.4654 | 177311.3208 | 1.2158 | 1.2294 | 0 | 0 | 215575.1038 | 217981.8094 | 2040 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 177311.3208 | 215575.1038 | 217981.8094
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.1967 | 4.3 | 4.3 | 2301.8868 | 2589.6226 | 2877.3585 | 181273.5849 | 1.2158 | 1.2294 | 0 | 0 | 220392.4245 | 222852.9113 | 2045 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 181273.5849 | 220392.4245 | 222852.9113
3 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Hydronic Heat Pump |  | Hydronic Heat Pump | 2023$/ton | 0 | 0 | 0 | Cooling Capacity | Tons | 3 | 70 | 296 | 296 | 0 | 0 | 0 | COP | Unitless | 3.04 | 4.2567 | 4.3 | 4.3 | 2352.2013 | 2646.2264 | 2940.2516 | 185235.8491 | 1.2158 | 1.2294 | 0 | 0 | 225209.7453 | 227724.0132 | 2050 | Advanced | 22 | Freeze protection / glycol loops for outdoor components in cold weather regions, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 11 | 2 | N/A | 2024 | Installation costs include labor and deconstruction of an existing gas boiler (for retrofits). Labor costs are assumed to be similar to labor installation for scroll chillers, using the same ratio of equipment costs to installation costs. Projections for cost and efficiency are assumed to be similar to the scroll chillers using EIA data projections. | 185235.8491 | 225209.7453 | 227724.0132
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 250250 | 1.1075 | 1.1256 | 0 | 0 | 277141.199 | 281682.1291 | 2023 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 250250 | 277141.199 | 281682.1291
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 250250 | 1.1075 | 1.1256 | 0 | 0 | 277141.199 | 281682.1291 | 2030 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 250250 | 277141.199 | 281682.1291
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 250250 | 1.1075 | 1.1256 | 0 | 0 | 277141.199 | 281682.1291 | 2035 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 250250 | 277141.199 | 281682.1291
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 250250 | 1.1075 | 1.1256 | 0 | 0 | 277141.199 | 281682.1291 | 2040 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 250250 | 277141.199 | 281682.1291
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 250250 | 1.1075 | 1.1256 | 0 | 0 | 277141.199 | 281682.1291 | 2045 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 250250 | 277141.199 | 281682.1291
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 250250 | 1.1075 | 1.1256 | 0 | 0 | 277141.199 | 281682.1291 | 2050 | Reference | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 250250 | 277141.199 | 281682.1291
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 250250 | 1.1075 | 1.1256 | 0 | 0 | 277141.199 | 281682.1291 | 2023 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 250250 | 277141.199 | 281682.1291
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.69195 | 1.17 | 1.17 | 1796.1407 | 1995.7118 | 2195.283 | 285386.7925 | 1.1075 | 1.1256 | 0 | 0 | 316053.6976 | 321232.2051 | 2030 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 285386.7925 | 316053.6976 | 321232.2051
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.68234 | 0.68234 | 1.17 | 1.17 | 1846.3122 | 2051.458 | 2256.6038 | 293358.4906 | 1.1075 | 1.1256 | 0 | 0 | 324882.0132 | 330205.1717 | 2035 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 293358.4906 | 324882.0132 | 330205.1717
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.67273 | 0.67273 | 1.17 | 1.17 | 1896.4837 | 2107.2041 | 2317.9245 | 301330.1887 | 1.1075 | 1.1256 | 0 | 0 | 333710.3288 | 339178.1383 | 2040 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 301330.1887 | 333710.3288 | 339178.1383
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.66312 | 0.66312 | 1.17 | 1.17 | 1966.4666 | 2184.9628 | 2403.4591 | 312449.6855 | 1.1075 | 1.1256 | 0 | 0 | 346024.6972 | 351694.2764 | 2045 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 312449.6855 | 346024.6972 | 351694.2764
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.65351 | 0.65351 | 1.17 | 1.17 | 2036.4494 | 2262.7216 | 2488.9937 | 323569.1824 | 1.1075 | 1.1256 | 0 | 0 | 358339.0656 | 364210.4144 | 2050 | Intermediate | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 323569.1824 | 358339.0656 | 364210.4144
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.69 | 0.74 | 1.17 | 1.17 | 1575 | 1750 | 1925 | 250250 | 1.1075 | 1.1256 | 0 | 0 | 277141.199 | 281682.1291 | 2023 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 250250 | 277141.199 | 281682.1291
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.68234 | 0.68234 | 1.17 | 1.17 | 1816.5952 | 2018.4391 | 2220.283 | 288636.7925 | 1.1075 | 1.1256 | 0 | 0 | 319652.934 | 324890.4145 | 2030 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 288636.7925 | 319652.934 | 324890.4145
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.67273 | 0.67273 | 1.17 | 1.17 | 1866.7667 | 2074.1852 | 2281.6038 | 296608.4906 | 1.1075 | 1.1256 | 0 | 0 | 328481.2496 | 333863.3811 | 2035 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 296608.4906 | 328481.2496 | 333863.3811
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.66312 | 0.66312 | 1.17 | 1.17 | 1916.9383 | 2129.9314 | 2342.9245 | 304580.1887 | 1.1075 | 1.1256 | 0 | 0 | 337309.5652 | 342836.3478 | 2040 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 304580.1887 | 337309.5652 | 342836.3478
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.65351 | 0.65351 | 1.17 | 1.17 | 1986.9211 | 2207.6901 | 2428.4591 | 315699.6855 | 1.1075 | 1.1256 | 0 | 0 | 349623.9335 | 355352.4858 | 2045 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 315699.6855 | 349623.9335 | 355352.4858
4 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Heat Recovery Chiller |  | Heat Recovery Chiller | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 10 | 143 | 1100 | 1100 | 0 | 0 | 0 | Efficiency | kW/ton | 0.6439 | 0.6439 | 1.17 | 1.17 | 2056.9039 | 2285.4488 | 2513.9937 | 326819.1824 | 1.1075 | 1.1256 | 0 | 0 | 361938.3019 | 367868.6239 | 2050 | Advanced | 22.5 | Air- vs. water-cooled, Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 9 | 42 | N/A | 2023 | Assumed +/- 10% $/tonnage from Mid Intercept to High and Low Intercepts. Typical capacity is the average of the upper and lower bounds. Typical efficiency is the median of the dataset. Lifetime of chiller can depend on if its air cooled (15-20 years) or water cooled (20-30 years) | 326819.1824 | 361938.3019 | 367868.6239
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 55000 | 1.2159 | 1.034 | 0 | 0 | 66874.4943 | 56871.375 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 55000 | 66874.4943 | 56871.375
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 55000 | 1.2159 | 1.034 | 0 | 0 | 66874.4943 | 56871.375 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 55000 | 66874.4943 | 56871.375
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 55000 | 1.2159 | 1.034 | 0 | 0 | 66874.4943 | 56871.375 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 55000 | 66874.4943 | 56871.375
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 55000 | 1.2159 | 1.034 | 0 | 0 | 66874.4943 | 56871.375 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 55000 | 66874.4943 | 56871.375
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 55000 | 1.2159 | 1.034 | 0 | 0 | 66874.4943 | 56871.375 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 55000 | 66874.4943 | 56871.375
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 55000 | 1.2159 | 1.034 | 0 | 0 | 66874.4943 | 56871.375 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 55000 | 66874.4943 | 56871.375
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 55000 | 1.2159 | 1.034 | 0 | 0 | 66874.4943 | 56871.375 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 55000 | 66874.4943 | 56871.375
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.79787 | 0.83 | 0.83 | 4.4736 | 4.9707 | 5.4678 | 54677.9181 | 1.2159 | 1.034 | 0 | 0 | 66482.8749 | 56538.3342 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 54677.9181 | 66482.8749 | 56538.3342
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.79787 | 0.83 | 0.83 | 4.4736 | 4.9707 | 5.4678 | 54677.9181 | 1.2159 | 1.034 | 0 | 0 | 66482.8749 | 56538.3342 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 54677.9181 | 66482.8749 | 56538.3342
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.79787 | 0.83 | 0.83 | 4.4736 | 4.9707 | 5.4678 | 54677.9181 | 1.2159 | 1.034 | 0 | 0 | 66482.8749 | 56538.3342 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 54677.9181 | 66482.8749 | 56538.3342
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.79948 | 0.83 | 0.83 | 4.4644 | 4.9605 | 5.4565 | 54565.2132 | 1.2159 | 1.034 | 0 | 0 | 66345.837 | 56421.7945 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 54565.2132 | 66345.837 | 56421.7945
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.80109 | 0.83 | 0.83 | 4.4552 | 4.9502 | 5.4453 | 54452.5082 | 1.2159 | 1.034 | 0 | 0 | 66208.7991 | 56305.2548 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 54452.5082 | 66208.7991 | 56305.2548
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.785 | 0.83 | 0.83 | 4.5 | 5 | 5.5 | 55000 | 1.2159 | 1.034 | 0 | 0 | 66874.4943 | 56871.375 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 55000 | 66874.4943 | 56871.375
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81074 | 0.83 | 0.83 | 4.3999 | 4.8888 | 5.3776 | 53776.2787 | 1.2159 | 1.034 | 0 | 0 | 65386.5717 | 55606.0166 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 53776.2787 | 65386.5717 | 55606.0166
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81074 | 0.83 | 0.83 | 4.3999 | 4.8888 | 5.3776 | 53776.2787 | 1.2159 | 1.034 | 0 | 0 | 65386.5717 | 55606.0166 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 53776.2787 | 65386.5717 | 55606.0166
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81074 | 0.83 | 0.83 | 4.3999 | 4.8888 | 5.3776 | 53776.2787 | 1.2159 | 1.034 | 0 | 0 | 65386.5717 | 55606.0166 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 53776.2787 | 65386.5717 | 55606.0166
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81395 | 0.83 | 0.83 | 4.3814 | 4.8683 | 5.3551 | 53550.8689 | 1.2159 | 1.034 | 0 | 0 | 65112.4959 | 55372.9372 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 53550.8689 | 65112.4959 | 55372.9372
5 | 2023 | Ventilation | Electricity | Commercial |  |  | Energy Recovery | Wheel | Energy Recovery Wheel | 2023$/CFM | 0 | 0 | 0 | Capacity | CFM | 1000 | 11000 | 50000 | 50000 | 0 | 0 | 0 | Sensible Efficiency | Unitless | 0.75 | 0.81717 | 0.83 | 0.83 | 4.363 | 4.8478 | 5.3325 | 53325.4591 | 1.2159 | 1.034 | 0 | 0 | 64838.4201 | 55139.8578 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 10 | N/A | 2024 | Used EIA Updated Buildings Sector Appliance and Equipment Costs and Efficiencies Tables from Commercial Rooftop AC to estimate projections for price and efficiency. Assumed +/- 10% $/CFM from Mid intercept to High and Low Intercepts based on manufacturer estimates. Typical CFM and sensible efficiency is the average of the dataset collected from manufacturer websites. | 53325.4591 | 64838.4201 | 55139.8578
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0431 | 4.1411 | 6.2765 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 7527.4897 | 1.1336 | 1.1336 | 0 | 0 | 8533.0269 | 8533.0269 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7527.4897 | 8533.0269 | 8533.0269
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0431 | 4.1411 | 12.6191 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 7527.4897 | 1.1336 | 1.1336 | 0 | 0 | 8533.0269 | 8533.0269 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7527.4897 | 8533.0269 | 8533.0269
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0431 | 4.1411 | 6.2765 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 7527.4897 | 1.1336 | 1.1336 | 0 | 0 | 8533.0269 | 8533.0269 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7527.4897 | 8533.0269 | 8533.0269
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0431 | 4.1411 | 6.2765 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 7527.4897 | 1.1336 | 1.1336 | 0 | 0 | 8533.0269 | 8533.0269 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7527.4897 | 8533.0269 | 8533.0269
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0431 | 4.1411 | 6.2765 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 7527.4897 | 1.1336 | 1.1336 | 0 | 0 | 8533.0269 | 8533.0269 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7527.4897 | 8533.0269 | 8533.0269
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0431 | 4.1411 | 6.2765 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 7527.4897 | 1.1336 | 1.1336 | 0 | 0 | 8533.0269 | 8533.0269 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7527.4897 | 8533.0269 | 8533.0269
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0431 | 4.1411 | 6.2765 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 7660.5594 | 1.1336 | 1.1336 | 0 | 0 | 8683.8723 | 8683.8723 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7527.4897 | 8533.0269 | 8533.0269
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0253 | 4.1168 | 6.2397 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 41.7947 | 130.1567 | -10.2219 | Sensible Efficiency | Unitless | 54 | 63.0164 | 68 | 68 | 513.72 | -4810.183 | 2771.9136 | 7615.6989 | 1.1336 | 1.1336 | 0 | 0 | 8633.0192 | 8633.0192 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7483.4085 | 8483.0572 | 8483.0572
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0253 | 4.1168 | 6.2397 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 41.7947 | 130.1567 | -10.2219 | Sensible Efficiency | Unitless | 54 | 63.0164 | 68 | 68 | 513.72 | -4810.183 | 2771.9136 | 7615.6989 | 1.1336 | 1.1336 | 0 | 0 | 8633.0192 | 8633.0192 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7483.4085 | 8483.0572 | 8483.0572
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0253 | 4.1168 | 6.2397 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 41.7947 | 130.1567 | -10.2219 | Sensible Efficiency | Unitless | 54 | 63.0164 | 68 | 68 | 513.72 | -4810.183 | 2771.9136 | 7615.6989 | 1.1336 | 1.1336 | 0 | 0 | 8633.0192 | 8633.0192 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7483.4085 | 8483.0572 | 8483.0572
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0191 | 4.1084 | 6.2268 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 41.7086 | 129.8884 | -10.2008 | Sensible Efficiency | Unitless | 54 | 63.1434 | 68 | 68 | 512.6611 | -4800.268 | 2766.2 | 7616.5032 | 1.1336 | 1.1336 | 0 | 0 | 8633.931 | 8633.931 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7467.9833 | 8465.5715 | 8465.5715
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0128 | 4.0999 | 6.214 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 41.6224 | 129.6201 | -10.1798 | Sensible Efficiency | Unitless | 54 | 63.2705 | 68 | 68 | 511.6022 | -4790.353 | 2760.4864 | 7617.2394 | 1.1336 | 1.1336 | 0 | 0 | 8634.7656 | 8634.7656 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7452.5581 | 8448.0858 | 8448.0858
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 3.0431 | 4.1411 | 6.2765 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 42.0409 | 130.9234 | -10.2821 | Sensible Efficiency | Unitless | 54 | 62 | 68 | 68 | 516.746 | -4838.5176 | 2788.2416 | 7527.4897 | 1.1336 | 1.1336 | 0 | 0 | 8533.0269 | 8533.0269 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7527.4897 | 8533.0269 | 8533.0269
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 2.9754 | 4.049 | 6.1368 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 41.1055 | 128.0104 | -10.0534 | Sensible Efficiency | Unitless | 54 | 64.0328 | 68 | 68 | 505.2487 | -4730.8631 | 2726.2047 | 7620.2249 | 1.1336 | 1.1336 | 0 | 0 | 8638.1498 | 8638.1498 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7360.007 | 8343.1715 | 8343.1715
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 2.9754 | 4.049 | 6.1368 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 41.1055 | 128.0104 | -10.0534 | Sensible Efficiency | Unitless | 54 | 64.0328 | 68 | 68 | 505.2487 | -4730.8631 | 2726.2047 | 7620.2249 | 1.1336 | 1.1336 | 0 | 0 | 8638.1498 | 8638.1498 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7360.007 | 8343.1715 | 8343.1715
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 2.9754 | 4.049 | 6.1368 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 41.1055 | 128.0104 | -10.0534 | Sensible Efficiency | Unitless | 54 | 64.0328 | 68 | 68 | 505.2487 | -4730.8631 | 2726.2047 | 7620.2249 | 1.1336 | 1.1336 | 0 | 0 | 8638.1498 | 8638.1498 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7360.007 | 8343.1715 | 8343.1715
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 2.963 | 4.032 | 6.1111 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 40.9332 | 127.4739 | -10.0112 | Sensible Efficiency | Unitless | 54 | 64.2869 | 68 | 68 | 503.1309 | -4711.0331 | 2714.7775 | 7620.6747 | 1.1336 | 1.1336 | 0 | 0 | 8638.6597 | 8638.6597 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7329.1566 | 8308.2001 | 8308.2001
6 | 2023 | Ventilation | Electricity | Residential, Commercial |  |  | Energy Recovery | Ventilation | Energy Recovery Ventilation | 2023$ | 2.9505 | 4.015 | 6.0854 | Capacity | CFM | 510 | 1026 | 2025 | 2025 | 40.7609 | 126.9373 | -9.9691 | Sensible Efficiency | Unitless | 54 | 64.541 | 68 | 68 | 501.0131 | -4691.2031 | 2703.3503 | 7620.8518 | 1.1336 | 1.1336 | 0 | 0 | 8638.8605 | 8638.8605 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 6 | 21 | 0.536 | 2024 | Used EIA tables from Commercial Rooftop AC | 7298.3063 | 8273.2287 | 8273.2287
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 40805.5018 | 1 | 1 | 0 | 0 | 40805.5018 | 40805.5018 | 2023 | Reference | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 40805.5018 | 40805.5018 | 40805.5018
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 40805.5018 | 1 | 1 | 0 | 0 | 40805.5018 | 40805.5018 | 2030 | Reference | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 40805.5018 | 40805.5018 | 40805.5018
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 40805.5018 | 1 | 1 | 0 | 0 | 40805.5018 | 40805.5018 | 2035 | Reference | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 40805.5018 | 40805.5018 | 40805.5018
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 40805.5018 | 1 | 1 | 0 | 0 | 40805.5018 | 40805.5018 | 2040 | Reference | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 40805.5018 | 40805.5018 | 40805.5018
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 40805.5018 | 1 | 1 | 0 | 0 | 40805.5018 | 40805.5018 | 2045 | Reference | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 40805.5018 | 40805.5018 | 40805.5018
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 40805.5018 | 1 | 1 | 0 | 0 | 40805.5018 | 40805.5018 | 2050 | Reference | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 40805.5018 | 40805.5018 | 40805.5018
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 40805.5018 | 1 | 1 | 0 | 0 | 40805.5018 | 40805.5018 | 2023 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 40805.5018 | 40805.5018 | 40805.5018
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 40805.5018 | 1 | 1 | 0 | 0 | 40805.5018 | 40805.5018 | 2030 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 40805.5018 | 40805.5018 | 40805.5018
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.025 | 8.2 | 18.45 | 18.45 | 1.3479 | 2.4259 | 3.1213 | 39785.3642 | 1 | 1 | 0 | 0 | 39785.3642 | 39785.3642 | 2035 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 39785.3642 | 39785.3642 | 39785.3642
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.0381 | 8.305 | 18.6863 | 18.6863 | 1.3315 | 2.3964 | 3.0833 | 39300.7989 | 1 | 1 | 0 | 0 | 39275.2954 | 39300.7989 | 2040 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 39300.7989 | 39300.7989 | 39300.7989
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.0513 | 8.41 | 18.9225 | 18.9225 | 1.3151 | 2.3668 | 3.0453 | 38816.2335 | 1 | 1 | 0 | 0 | 38765.2267 | 38816.2335 | 2045 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 38816.2335 | 38816.2335 | 38816.2335
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.065 | 8.5203 | 19.1706 | 19.1706 | 1.2995 | 2.3388 | 3.0092 | 38355.8965 | 1 | 1 | 0 | 0 | 38306.1648 | 38355.8965 | 2050 | Intermediate | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 38355.8965 | 38355.8965 | 38355.8965
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1 | 8 | 18 | 18 | 1.3825 | 2.4881 | 3.2014 | 40805.5018 | 1 | 1 | 0 | 0 | 40805.5018 | 40805.5018 | 2023 | Advanced | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 40805.5018 | 40805.5018 | 40805.5018
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.05 | 8.4 | 18.9 | 18.9 | 1.3134 | 2.3637 | 3.0413 | 38765.2267 | 1 | 1 | 0 | 0 | 38765.2267 | 38765.2267 | 2030 | Advanced | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 38765.2267 | 38765.2267 | 38765.2267
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.0762 | 8.61 | 19.3725 | 19.3725 | 1.2805 | 2.3046 | 2.9653 | 37796.096 | 1 | 1 | 0 | 0 | 37745.0891 | 37796.096 | 2035 | Advanced | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 37796.096 | 37796.096 | 37796.096
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.1025 | 8.82 | 19.845 | 19.845 | 1.2477 | 2.2455 | 2.8892 | 36826.9653 | 1 | 1 | 0 | 0 | 36724.9516 | 36826.9653 | 2040 | Advanced | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 36826.9653 | 36826.9653 | 36826.9653
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.1301 | 9.0405 | 20.3411 | 20.3411 | 1.2165 | 2.1894 | 2.817 | 35906.2912 | 1 | 1 | 0 | 0 | 35806.8278 | 35906.2912 | 2045 | Advanced | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 35906.2912 | 35906.2912 | 35906.2912
7 | 2023 | Ventilation | Electricity | Commercial |  |  | Demand Controlled Ventilation |  | Demand Controlled Ventilation | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Building Energy Savings | % | 1.1576 | 9.261 | 20.8373 | 20.8373 | 1.1853 | 2.1333 | 2.7448 | 34985.6171 | 1 | 1 | 0 | 0 | 34888.704 | 34985.6171 | 2050 | Advanced | 15 | Providing a general rule to estimate DCV costs is challeging, since the design changes drastically depending on building conditions. Two similar buildings with the same area can have very different DCV costs, depending on factors like their internal layout and occupancy patterns. In addition, Weather conditions such as temperature and humidity also influence the overall HVAC design, which includes the ventilation system. In the case of retrofits, the cost of implementing a DCV also depends on whether the existing installation uses CAV (Constant Air Volume) or VAV (Variable Air Volume) boxes as parts of the ventilation system. The cost will be much lower in a building using VAV boxes. | 16 | 18 | N/A | 2017 | Retail costs include CO2 sensor cost, programming the existing energy management, DDC conversions, and airflow controls. Typical installed costs assumes a 16,000 sq ft building. The data from available case studies and online articles was converted to 2023 dollars and converted to $/sq ft assuming 1 sensor/3500 sq ft, 1cfm/1 ft, an average room size of 285 sq ft, and an averege home size of 1500 sq ft. The average cost of a CO2 sensor was found to be $329. 15 year lifetime represents the lifetime of the CO2 sensors. | 34985.6171 | 34985.6171 | 34985.6171
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 165162.25 | 1.2151 | 1.3145 | 0 | 0 | 200687.0175 | 217111.1282 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 165162.25 | 200687.0175 | 217111.1282
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 165162.25 | 1.2151 | 1.3145 | 0 | 0 | 200687.0175 | 217111.1282 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 165162.25 | 200687.0175 | 217111.1282
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 165162.25 | 1.2151 | 1.3145 | 0 | 0 | 200687.0175 | 217111.1282 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 165162.25 | 200687.0175 | 217111.1282
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 165162.25 | 1.2151 | 1.3145 | 0 | 0 | 200687.0175 | 217111.1282 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 165162.25 | 200687.0175 | 217111.1282
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 165162.25 | 1.2151 | 1.3145 | 0 | 0 | 200687.0175 | 217111.1282 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 165162.25 | 200687.0175 | 217111.1282
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 165162.25 | 1.2151 | 1.3145 | 0 | 0 | 200687.0175 | 217111.1282 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 165162.25 | 200687.0175 | 217111.1282
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 165162.25 | 1.2151 | 1.3145 | 0 | 0 | 200687.0175 | 217111.1282 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 165162.25 | 200687.0175 | 217111.1282
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 10123.3037 | 13770.9246 | 15312.8994 | 151480.1701 | 1.2151 | 1.3145 | 0 | 0 | 184062.0575 | 199125.5909 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 151480.1701 | 184062.0575 | 199125.5909
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 10056.1832 | 13679.6192 | 15211.3703 | 150475.8109 | 1.2151 | 1.3145 | 0 | 0 | 182841.6705 | 197805.3281 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 150475.8109 | 182841.6705 | 197805.3281
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9990.9914 | 13590.9375 | 15112.7586 | 149500.3125 | 1.2151 | 1.3145 | 0 | 0 | 181656.3521 | 196523.0039 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 149500.3125 | 181656.3521 | 196523.0039
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9927.6464 | 13504.7681 | 15016.9405 | 148552.4487 | 1.2151 | 1.3145 | 0 | 0 | 180504.6121 | 195277.0062 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 148552.4487 | 180504.6121 | 195277.0062
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9866.0708 | 13421.0056 | 14923.7989 | 147631.0615 | 1.2151 | 1.3145 | 0 | 0 | 179385.0436 | 194065.8129 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 147631.0615 | 179385.0436 | 194065.8129
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 11037.6667 | 15014.75 | 16696 | 165162.25 | 1.2151 | 1.3145 | 0 | 0 | 200687.0175 | 217111.1282 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 165162.25 | 200687.0175 | 217111.1282
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9208.9408 | 12527.0991 | 13929.7988 | 137798.0902 | 1.2151 | 1.3145 | 0 | 0 | 167437.0975 | 181140.0537 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 137798.0902 | 167437.0975 | 181140.0537
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 9074.6997 | 12344.4883 | 13726.7405 | 135789.3717 | 1.2151 | 1.3145 | 0 | 0 | 164996.3235 | 178499.5281 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 135789.3717 | 164996.3235 | 178499.5281
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 8944.3161 | 12167.125 | 13529.5172 | 133838.375 | 1.2151 | 1.3145 | 0 | 0 | 162625.6866 | 175934.8797 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 133838.375 | 162625.6866 | 175934.8797
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 8817.6261 | 11994.7861 | 13337.881 | 131942.6473 | 1.2151 | 1.3145 | 0 | 0 | 160322.2066 | 173442.8843 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 131942.6473 | 160322.2066 | 173442.8843
8 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | DOAS with Mini Split Heat Pumps |  | DOAS with Mini Split Heat Pumps | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 12 | 12 | 18 | 18 | 8694.4749 | 11827.2612 | 13151.5978 | 130099.8729 | 1.2151 | 1.3145 | 0 | 0 | 158083.0697 | 171020.4976 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 31 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 130099.8729 | 158083.0697 | 171020.4976
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 13409.6667 | 17953.9091 | 19738 | 197493 | 1.2027 | 1.2773 | 0 | 0 | 237529.2336 | 252253.7958 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 197493 | 237529.2336 | 252253.7958
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 13409.6667 | 17953.9091 | 19738 | 197493 | 1.2027 | 1.2773 | 0 | 0 | 237529.2336 | 252253.7958 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 197493 | 237529.2336 | 252253.7958
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 13409.6667 | 17953.9091 | 19738 | 197493 | 1.2027 | 1.2773 | 0 | 0 | 237529.2336 | 252253.7958 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 197493 | 237529.2336 | 252253.7958
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 13409.6667 | 17953.9091 | 19738 | 197493 | 1.2027 | 1.2773 | 0 | 0 | 237529.2336 | 252253.7958 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 197493 | 237529.2336 | 252253.7958
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 13409.6667 | 17953.9091 | 19738 | 197493 | 1.2027 | 1.2773 | 0 | 0 | 237529.2336 | 252253.7958 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 197493 | 237529.2336 | 252253.7958
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 13409.6667 | 17953.9091 | 19738 | 197493 | 1.2027 | 1.2773 | 0 | 0 | 237529.2336 | 252253.7958 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 197493 | 237529.2336 | 252253.7958
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 13409.6667 | 17953.9091 | 19738 | 197493 | 1.2027 | 1.2773 | 0 | 0 | 237529.2336 | 252253.7958 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 197493 | 237529.2336 | 252253.7958
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 12298.8067 | 16466.603 | 18102.8994 | 181132.6331 | 1.2027 | 1.2773 | 0 | 0 | 217852.2557 | 231357.0317 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 181132.6331 | 217852.2557 | 231357.0317
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 12217.2619 | 16357.4245 | 17982.8717 | 179931.6691 | 1.2027 | 1.2773 | 0 | 0 | 216407.8295 | 229823.0647 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 179931.6691 | 216407.8295 | 229823.0647
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 12138.0603 | 16251.3832 | 17866.2931 | 178765.2155 | 1.2027 | 1.2773 | 0 | 0 | 215004.9098 | 228333.1773 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 178765.2155 | 215004.9098 | 228333.1773
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 12061.1025 | 16148.346 | 17753.017 | 177631.8059 | 1.2027 | 1.2773 | 0 | 0 | 213641.7328 | 226885.4963 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 177631.8059 | 213641.7328 | 226885.4963
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 11986.2942 | 16048.1869 | 17642.905 | 176530.0559 | 1.2027 | 1.2773 | 0 | 0 | 212316.6334 | 225478.2533 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 176530.0559 | 212316.6334 | 225478.2533
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 13409.6667 | 17953.9091 | 19738 | 197493 | 1.2027 | 1.2773 | 0 | 0 | 237529.2336 | 252253.7958 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 197493 | 237529.2336 | 252253.7958
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 11187.9467 | 14979.2969 | 16467.7988 | 164772.2663 | 1.2027 | 1.2773 | 0 | 0 | 198175.2778 | 210460.2675 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 164772.2663 | 198175.2778 | 210460.2675
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 11024.8571 | 14760.9398 | 16227.7434 | 162370.3382 | 1.2027 | 1.2773 | 0 | 0 | 195286.4253 | 207392.3336 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 162370.3382 | 195286.4253 | 207392.3336
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 10866.454 | 14548.8574 | 15994.5862 | 160037.431 | 1.2027 | 1.2773 | 0 | 0 | 192480.5859 | 204412.5587 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 160037.431 | 192480.5859 | 204412.5587
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 10712.5382 | 14342.7829 | 15768.034 | 157770.6119 | 1.2027 | 1.2773 | 0 | 0 | 189754.232 | 201517.1967 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 157770.6119 | 189754.232 | 201517.1967
9 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Variable Refrigerant Flow with Dedicated Outdoor Air System |  | DOAS with VRF | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 3 | 11 | 55 | 55 | 0 | 0 | 0 | IEER | Unitless | 0 | 12 | 18 | 0 | 10562.9218 | 14142.4647 | 15547.8101 | 155567.1117 | 1.2027 | 1.2773 | 0 | 0 | 187104.0332 | 198702.7107 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 28 | N/A | 2023 | Assumes 1CFM/sqft, Assumes 400-600 sqft per 1 ton of cooling, Assume 20 ft piping connections per ton, Projections are mainly based on improvement of DOAS unit efficiency and pricing, Includes piping material and labor costs and wiring material and labor costs, Assumes reuse of existing ductwork. Retrofit costs include demolition of existing RTU system. Potentially large variation in installation cost of wiring and piping which is highly dependent on the layout of the building and available space. | 155567.1117 | 187104.0332 | 198702.7107
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2922.08 | 5130.59 | 7339.1 | 20522.36 | 1 | 1 | 537.13 | 621.81 | 22670.88 | 23009.6 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 20522.36 | 22670.88 | 23009.6
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2922.08 | 5130.59 | 7339.1 | 20522.36 | 1 | 1 | 537.13 | 621.81 | 22670.88 | 23009.6 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 20522.36 | 22670.88 | 23009.6
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2922.08 | 5130.59 | 7339.1 | 20522.36 | 1 | 1 | 537.13 | 621.81 | 22670.88 | 23009.6 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 20522.36 | 22670.88 | 23009.6
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2922.08 | 5130.59 | 7339.1 | 20522.36 | 1 | 1 | 537.13 | 621.81 | 22670.88 | 23009.6 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 20522.36 | 22670.88 | 23009.6
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2922.08 | 5130.59 | 7339.1 | 20522.36 | 1 | 1 | 537.13 | 621.81 | 22670.88 | 23009.6 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 20522.36 | 22670.88 | 23009.6
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2922.08 | 5130.59 | 7339.1 | 20522.36 | 1 | 1 | 537.13 | 621.81 | 22670.88 | 23009.6 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 20522.36 | 22670.88 | 23009.6
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2922.08 | 5130.59 | 7339.1 | 20522.36 | 1 | 1 | 537.13 | 621.81 | 22670.88 | 23009.6 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 20522.36 | 22670.88 | 23009.6
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2775.2985 | 4872.871 | 6970.4435 | 19491.4841 | 1 | 1 | 537.13 | 621.81 | 21640.0041 | 21978.7241 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 19491.4841 | 21640.0041 | 21978.7241
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2775.2985 | 4872.871 | 6970.4435 | 19491.4841 | 1 | 1 | 537.13 | 621.81 | 21640.0041 | 21978.7241 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 19491.4841 | 21640.0041 | 21978.7241
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2775.2985 | 4872.871 | 6970.4435 | 19491.4841 | 1 | 1 | 537.13 | 621.81 | 21640.0041 | 21978.7241 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 19491.4841 | 21640.0041 | 21978.7241
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2775.2985 | 4872.871 | 6970.4435 | 19491.4841 | 1 | 1 | 537.13 | 621.81 | 21640.0041 | 21978.7241 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 19491.4841 | 21640.0041 | 21978.7241
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2775.2985 | 4872.871 | 6970.4435 | 19491.4841 | 1 | 1 | 537.13 | 621.81 | 21640.0041 | 21978.7241 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 19491.4841 | 21640.0041 | 21978.7241
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2922.08 | 5130.59 | 7339.1 | 20522.36 | 1 | 1 | 537.13 | 621.81 | 22670.88 | 23009.6 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 20522.36 | 22670.88 | 23009.6
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2628.5171 | 4615.1521 | 6601.787 | 18460.6082 | 1 | 1 | 537.13 | 621.81 | 20609.1282 | 20947.8482 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 18460.6082 | 20609.1282 | 20947.8482
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2628.5171 | 4615.1521 | 6601.787 | 18460.6082 | 1 | 1 | 537.13 | 621.81 | 20609.1282 | 20947.8482 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 18460.6082 | 20609.1282 | 20947.8482
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2628.5171 | 4615.1521 | 6601.787 | 18460.6082 | 1 | 1 | 537.13 | 621.81 | 20609.1282 | 20947.8482 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 18460.6082 | 20609.1282 | 20947.8482
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2628.5171 | 4615.1521 | 6601.787 | 18460.6082 | 1 | 1 | 537.13 | 621.81 | 20609.1282 | 20947.8482 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 18460.6082 | 20609.1282 | 20947.8482
10 | 2023 | Heating, Cooling | Electricity | Commercial |  | Commercial Ground Source Heat Pump | Ground Source Heat Pump |  | Commercial Ground Source Heat Pump | 2023$/ton | 0 | 0 | 0 | Capacity | Tons | 1.5 | 4 | 4 | 20 | 0 | 0 | 0 | COP | Unitless | 3.1 | 3.5 | 3.6 | 3.7 | 2628.5171 | 4615.1521 | 6601.787 | 18460.6082 | 1 | 1 | 537.13 | 621.81 | 20609.1282 | 20947.8482 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 5 | 13 | N/A | 2019 | Installation cost includes HP installation and pumbling, but not additional piping costs which may be needed in some instalation scenarios. Retrofit installation costs include demolition of a boiler and chiller. The cost of a vertical geothermal field is included in the retail price range. | 18460.6082 | 20609.1282 | 20947.8482
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.000463 | 0.002939 | 0.026427 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.04311 | -0.036938 | 0.31743 | Efficacy | lm/W | 0.045901 | 140.146 | 163.6364 | 278.5714 | -0.118 | 15.1226 | 85.2784 | 15.5888 | 1 | 1 | 26.4 | 26.4 | 41.9888 | 41.9888 | 2023 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 15.5888 | 41.9888 | 41.9888
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.00041174 | 0.0026136 | 0.023501 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.032326 | -0.027698 | 0.23802 | Efficacy | lm/W | 0.045901 | 166.209 | 194.0679 | 278.5714 | -0.10494 | 13.4484 | 75.8374 | 13.863 | 1 | 1 | 26.4 | 26.4 | 40.263 | 40.263 | 2030 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.863 | 40.263 | 40.263
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.00040707 | 0.002584 | 0.023235 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.029642 | -0.025398 | 0.21826 | Efficacy | lm/W | 0.045901 | 179.2024 | 209.2392 | 278.5714 | -0.10375 | 13.2958 | 74.9769 | 13.7057 | 1 | 1 | 26.4 | 26.4 | 40.1057 | 40.1057 | 2035 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.7057 | 40.1057 | 40.1057
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.0004024 | 0.0025543 | 0.022968 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.027321 | -0.023409 | 0.20117 | Efficacy | lm/W | 0.045901 | 192.1959 | 224.4105 | 278.5714 | -0.10256 | 13.1432 | 74.1165 | 13.5484 | 1 | 1 | 26.4 | 26.4 | 39.9484 | 39.9484 | 2040 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.5484 | 39.9484 | 39.9484
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.000398 | 0.0025264 | 0.022717 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.02532 | -0.021695 | 0.18644 | Efficacy | lm/W | 0.045901 | 205.1131 | 237.2052 | 278.5714 | -0.10144 | 12.9996 | 73.3066 | 13.4003 | 1 | 1 | 26.4 | 26.4 | 39.8003 | 39.8003 | 2045 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.4003 | 39.8003 | 39.8003
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.00039361 | 0.0024985 | 0.022466 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.023557 | -0.020184 | 0.17346 | Efficacy | lm/W | 0.045901 | 218.0303 | 250 | 278.5714 | -0.10031 | 12.856 | 72.4968 | 13.2523 | 1 | 1 | 26.4 | 26.4 | 39.6523 | 39.6523 | 2050 | Reference | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.2523 | 39.6523 | 39.6523
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.000463 | 0.002939 | 0.026427 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.04311 | -0.036938 | 0.31743 | Efficacy | lm/W | 0.045901 | 140.146 | 163.6364 | 278.5714 | -0.118 | 15.1226 | 85.2784 | 15.5888 | 1 | 1 | 26.4 | 26.4 | 41.9888 | 41.9888 | 2023 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 15.5888 | 41.9888 | 41.9888
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.00041174 | 0.0026136 | 0.023501 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.028109 | -0.024085 | 0.20698 | Efficacy | lm/W | 0.045901 | 191.1404 | 222.034 | 278.5714 | -0.10494 | 13.4484 | 75.8374 | 13.863 | 1 | 1 | 26.4 | 26.4 | 40.263 | 40.263 | 2030 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.863 | 40.263 | 40.263
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.00040707 | 0.002584 | 0.023235 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.025771 | -0.022081 | 0.18976 | Efficacy | lm/W | 0.045901 | 206.1192 | 229.6196 | 278.5714 | -0.10375 | 13.2958 | 74.9769 | 13.7057 | 1 | 1 | 26.4 | 26.4 | 40.1057 | 40.1057 | 2035 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.7057 | 40.1057 | 40.1057
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.0004024 | 0.0025543 | 0.022968 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.023749 | -0.020349 | 0.17487 | Efficacy | lm/W | 0.045901 | 221.0979 | 237.2052 | 278.5714 | -0.10256 | 13.1432 | 74.1165 | 13.5484 | 1 | 1 | 26.4 | 26.4 | 39.9484 | 39.9484 | 2040 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.5484 | 39.9484 | 39.9484
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.000398 | 0.0025264 | 0.022717 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.022823 | -0.019556 | 0.16805 | Efficacy | lm/W | 0.045901 | 227.5565 | 243.6026 | 278.5714 | -0.10144 | 12.9996 | 73.3066 | 13.4003 | 1 | 1 | 26.4 | 26.4 | 39.8003 | 39.8003 | 2045 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.4003 | 39.8003 | 39.8003
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.00039361 | 0.0024985 | 0.022466 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.021948 | -0.018806 | 0.16161 | Efficacy | lm/W | 0.045901 | 234.0151 | 250 | 278.5714 | -0.10031 | 12.856 | 72.4968 | 13.2523 | 1 | 1 | 26.4 | 26.4 | 39.6523 | 39.6523 | 2050 | Intermediate | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.2523 | 39.6523 | 39.6523
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.000463 | 0.002939 | 0.026427 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.04311 | -0.036938 | 0.31743 | Efficacy | lm/W | 0.045901 | 140.146 | 163.6364 | 278.5714 | -0.118 | 15.1226 | 85.2784 | 15.5888 | 1 | 1 | 26.4 | 26.4 | 41.9888 | 41.9888 | 2023 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 15.5888 | 41.9888 | 41.9888
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.00041174 | 0.0026136 | 0.023501 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.024866 | -0.021306 | 0.18309 | Efficacy | lm/W | 0.045901 | 216.0717 | 250 | 278.5714 | -0.10494 | 13.4484 | 75.8374 | 13.863 | 1 | 1 | 26.4 | 26.4 | 40.263 | 40.263 | 2030 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.863 | 40.263 | 40.263
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.00040707 | 0.002584 | 0.023235 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.022794 | -0.019531 | 0.16784 | Efficacy | lm/W | 0.045901 | 233.0359 | 250 | 278.5714 | -0.10375 | 13.2958 | 74.9769 | 13.7057 | 1 | 1 | 26.4 | 26.4 | 40.1057 | 40.1057 | 2035 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.7057 | 40.1057 | 40.1057
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.0004024 | 0.0025543 | 0.022968 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.021004 | -0.017997 | 0.15466 | Efficacy | lm/W | 0.045901 | 250 | 250 | 278.5714 | -0.10256 | 13.1432 | 74.1165 | 13.5484 | 1 | 1 | 26.4 | 26.4 | 39.9484 | 39.9484 | 2040 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.5484 | 39.9484 | 39.9484
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.000398 | 0.0025264 | 0.022717 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.020774 | -0.0178 | 0.15297 | Efficacy | lm/W | 0.045901 | 250 | 250 | 278.5714 | -0.10144 | 12.9996 | 73.3066 | 13.4003 | 1 | 1 | 26.4 | 26.4 | 39.8003 | 39.8003 | 2045 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.4003 | 39.8003 | 39.8003
11 | 2023 | Lighting | Electricity | Commercial |  | 4ft LED Replacement Lamp | LED | TLED | Commercial TLED | 2023$ | 0.00039361 | 0.0024985 | 0.022466 | Light Output | Lumens | 270 | 1920 | 1800 | 9000 | 0.020545 | -0.017603 | 0.15128 | Efficacy | lm/W | 0.045901 | 250 | 250 | 278.5714 | -0.10031 | 12.856 | 72.4968 | 13.2523 | 1 | 1 | 26.4 | 26.4 | 39.6523 | 39.6523 | 2050 | Advanced | 6.1644 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1722 | 0.006235 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 13.2523 | 39.6523 | 39.6523
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.004616 | 0.011117 | 0.007179 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.26937 | -0.40131 | -0.4759 | Efficacy | lm/W | 55.4333 | 120.5 | 137.1429 | 156.25 | 78.3972 | 137.0269 | 248.5897 | 147.611 | 1 | 1 | 36.2208 | 36.2208 | 183.8318 | 183.8318 | 2023 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 147.611 | 183.8318 | 183.8318
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0039951 | 0.0096218 | 0.0062134 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.18882 | -0.28131 | -0.3336 | Efficacy | lm/W | 55.4333 | 148.7806 | 169.3294 | 156.25 | 67.8528 | 118.5968 | 215.1543 | 127.7573 | 1 | 1 | 36.2208 | 36.2208 | 163.9781 | 163.9781 | 2030 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 127.7573 | 163.9781 | 163.9781
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0038805 | 0.0093457 | 0.0060351 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.16742 | -0.24942 | -0.29578 | Efficacy | lm/W | 55.4333 | 162.9892 | 185.5005 | 156.25 | 65.906 | 115.194 | 208.9812 | 124.0917 | 1 | 1 | 36.2208 | 36.2208 | 160.3125 | 160.3125 | 2035 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 124.0917 | 160.3125 | 160.3125
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0037659 | 0.0090696 | 0.0058569 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.14944 | -0.22265 | -0.26403 | Efficacy | lm/W | 55.4333 | 177.1978 | 201.6715 | 156.25 | 63.9591 | 111.7912 | 202.808 | 120.4261 | 1 | 1 | 36.2208 | 36.2208 | 156.6469 | 156.6469 | 2040 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 120.4261 | 156.6469 | 156.6469
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0036565 | 0.0088061 | 0.0056867 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.13438 | -0.2002 | -0.23741 | Efficacy | lm/W | 55.4333 | 191.3382 | 217.7648 | 156.25 | 62.1009 | 108.5432 | 196.9155 | 116.9272 | 1 | 1 | 36.2208 | 36.2208 | 153.148 | 153.148 | 2045 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 116.9272 | 153.148 | 153.148
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0035471 | 0.0085426 | 0.0055165 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.12139 | -0.18085 | -0.21446 | Efficacy | lm/W | 55.4333 | 205.4785 | 233.8581 | 156.25 | 60.2426 | 105.2952 | 191.0231 | 113.4284 | 1 | 1 | 36.2208 | 36.2208 | 149.6492 | 149.6492 | 2050 | Reference | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 113.4284 | 149.6492 | 149.6492
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.004616 | 0.011117 | 0.007179 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.26937 | -0.40131 | -0.4759 | Efficacy | lm/W | 55.4333 | 120.5 | 137.1429 | 156.25 | 78.3972 | 137.0269 | 248.5897 | 147.611 | 1 | 1 | 36.2208 | 36.2208 | 183.8318 | 183.8318 | 2023 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 147.611 | 183.8318 | 183.8318
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0039951 | 0.0096218 | 0.0062134 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.16419 | -0.24462 | -0.29008 | Efficacy | lm/W | 55.4333 | 171.0977 | 194.7289 | 156.25 | 67.8528 | 118.5968 | 215.1543 | 127.7573 | 1 | 1 | 36.2208 | 36.2208 | 163.9781 | 163.9781 | 2030 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 127.7573 | 163.9781 | 163.9781
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0038805 | 0.0093457 | 0.0060351 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.14558 | -0.21689 | -0.2572 | Efficacy | lm/W | 55.4333 | 187.4376 | 210.2823 | 156.25 | 65.906 | 115.194 | 208.9812 | 124.0917 | 1 | 1 | 36.2208 | 36.2208 | 160.3125 | 160.3125 | 2035 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 124.0917 | 160.3125 | 160.3125
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0037659 | 0.0090696 | 0.0058569 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.12995 | -0.1936 | -0.22959 | Efficacy | lm/W | 55.4333 | 203.7775 | 225.8358 | 156.25 | 63.9591 | 111.7912 | 202.808 | 120.4261 | 1 | 1 | 36.2208 | 36.2208 | 156.6469 | 156.6469 | 2040 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 120.4261 | 156.6469 | 156.6469
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0036565 | 0.0088061 | 0.0056867 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.11917 | -0.17754 | -0.21054 | Efficacy | lm/W | 55.4333 | 215.7584 | 233.8824 | 156.25 | 62.1009 | 108.5432 | 196.9155 | 116.9272 | 1 | 1 | 36.2208 | 36.2208 | 153.148 | 153.148 | 2045 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 116.9272 | 153.148 | 153.148
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0035471 | 0.0085426 | 0.0055165 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.10952 | -0.16317 | -0.19349 | Efficacy | lm/W | 55.4333 | 227.7392 | 241.9291 | 156.25 | 60.2426 | 105.2952 | 191.0231 | 113.4284 | 1 | 1 | 36.2208 | 36.2208 | 149.6492 | 149.6492 | 2050 | Intermediate | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 113.4284 | 149.6492 | 149.6492
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.004616 | 0.011117 | 0.007179 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.26937 | -0.40131 | -0.4759 | Efficacy | lm/W | 55.4333 | 120.5 | 137.1429 | 156.25 | 78.3972 | 137.0269 | 248.5897 | 147.611 | 1 | 1 | 36.2208 | 36.2208 | 183.8318 | 183.8318 | 2023 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 147.611 | 183.8318 | 183.8318
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0039951 | 0.0096218 | 0.0062134 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.14525 | -0.2164 | -0.25661 | Efficacy | lm/W | 55.4333 | 193.4148 | 220.1283 | 156.25 | 67.8528 | 118.5968 | 215.1543 | 127.7573 | 1 | 1 | 36.2208 | 36.2208 | 163.9781 | 163.9781 | 2030 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 127.7573 | 163.9781 | 163.9781
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0038805 | 0.0093457 | 0.0060351 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.12878 | -0.19186 | -0.22752 | Efficacy | lm/W | 55.4333 | 211.886 | 235.0641 | 156.25 | 65.906 | 115.194 | 208.9812 | 124.0917 | 1 | 1 | 36.2208 | 36.2208 | 160.3125 | 160.3125 | 2035 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 124.0917 | 160.3125 | 160.3125
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0037659 | 0.0090696 | 0.0058569 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.11496 | -0.17127 | -0.2031 | Efficacy | lm/W | 55.4333 | 230.3572 | 250 | 156.25 | 63.9591 | 111.7912 | 202.808 | 120.4261 | 1 | 1 | 36.2208 | 36.2208 | 156.6469 | 156.6469 | 2040 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 120.4261 | 156.6469 | 156.6469
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0036565 | 0.0088061 | 0.0056867 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.10705 | -0.15949 | -0.18913 | Efficacy | lm/W | 55.4333 | 240.1786 | 250 | 156.25 | 62.1009 | 108.5432 | 196.9155 | 116.9272 | 1 | 1 | 36.2208 | 36.2208 | 153.148 | 153.148 | 2045 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 116.9272 | 153.148 | 153.148
12 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | Commercial LED Troffer & Panel | 2023$ | 0.0035471 | 0.0085426 | 0.0055165 | Light Output | Lumens | 810 | 5302 | 4800 | 7889 | -0.099769 | -0.14864 | -0.17626 | Efficacy | lm/W | 55.4333 | 250 | 250 | 156.25 | 60.2426 | 105.2952 | 191.0231 | 113.4284 | 1 | 1 | 36.2208 | 36.2208 | 149.6492 | 149.6492 | 2050 | Advanced | 6.0502 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 1847 | 0.01775 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 113.4284 | 149.6492 | 149.6492
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.001648 | 0.003012 | 0.001264 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.021554 | 0.020291 | 0.081726 | Efficacy | lm/W | 50 | 90.0141 | 100 | 125 | -0.66465 | 1.1906 | 4.8261 | 5.4267 | 1 | 1 | 72.4416 | 3.6221 | 77.8683 | 9.0488 | 2023 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 5.4267 | 77.8683 | 9.0488
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0013593 | 0.0024844 | 0.0010426 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.014702 | 0.013841 | 0.055746 | Efficacy | lm/W | 50 | 108.8505 | 120.9261 | 125 | -0.54824 | 0.98207 | 3.9807 | 4.4762 | 1 | 1 | 72.4416 | 3.6221 | 76.9178 | 8.0983 | 2030 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 4.4762 | 76.9178 | 8.0983
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0012776 | 0.0023351 | 0.00097993 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.012156 | 0.011444 | 0.046093 | Efficacy | lm/W | 50 | 123.7326 | 137.4592 | 125 | -0.51528 | 0.92303 | 3.7414 | 4.2071 | 1 | 1 | 72.4416 | 3.6221 | 76.6487 | 7.8292 | 2035 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 4.2071 | 76.6487 | 7.8292
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0011959 | 0.0021857 | 0.00091725 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.010157 | 0.0095619 | 0.038513 | Efficacy | lm/W | 50 | 138.6147 | 153.9923 | 125 | -0.48232 | 0.86399 | 3.5021 | 3.938 | 1 | 1 | 72.4416 | 3.6221 | 76.3796 | 7.5601 | 2040 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 3.938 | 76.3796 | 7.5601
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0011142 | 0.0020364 | 0.0008546 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.008764 | 0.0082504 | 0.03323 | Efficacy | lm/W | 50 | 149.6761 | 166.2808 | 125 | -0.44938 | 0.80498 | 3.2629 | 3.669 | 1 | 1 | 72.4416 | 3.6221 | 76.1106 | 7.2911 | 2045 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 3.669 | 76.1106 | 7.2911
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0010325 | 0.0018871 | 0.00079194 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0075626 | 0.0071194 | 0.028675 | Efficacy | lm/W | 50 | 160.7375 | 178.5693 | 125 | -0.41643 | 0.74596 | 3.0237 | 3.4 | 1 | 1 | 72.4416 | 3.6221 | 75.8416 | 7.0221 | 2050 | Reference | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 3.4 | 75.8416 | 7.0221
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.001648 | 0.003012 | 0.001264 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.021554 | 0.020291 | 0.081726 | Efficacy | lm/W | 50 | 90.0141 | 100 | 125 | -0.66465 | 1.1906 | 4.8261 | 5.4267 | 1 | 1 | 72.4416 | 3.6221 | 77.8683 | 9.0488 | 2023 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 5.4267 | 77.8683 | 9.0488
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0013593 | 0.0024844 | 0.0010426 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.012784 | 0.012035 | 0.048475 | Efficacy | lm/W | 50 | 125.1781 | 139.065 | 125 | -0.54824 | 0.98207 | 3.9807 | 4.4762 | 1 | 1 | 72.4416 | 3.6221 | 76.9178 | 8.0983 | 2030 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 4.4762 | 76.9178 | 8.0983
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0012776 | 0.0023351 | 0.00097993 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.010571 | 0.0099513 | 0.040081 | Efficacy | lm/W | 50 | 142.2925 | 158.0781 | 125 | -0.51528 | 0.92303 | 3.7414 | 4.2071 | 1 | 1 | 72.4416 | 3.6221 | 76.6487 | 7.8292 | 2035 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 4.2071 | 76.6487 | 7.8292
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0011959 | 0.0021857 | 0.00091725 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0088323 | 0.0083147 | 0.033489 | Efficacy | lm/W | 50 | 159.4069 | 177.0911 | 125 | -0.48232 | 0.86399 | 3.5021 | 3.938 | 1 | 1 | 72.4416 | 3.6221 | 76.3796 | 7.5601 | 2040 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 3.938 | 76.3796 | 7.5601
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0011142 | 0.0020364 | 0.0008546 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0076208 | 0.0071743 | 0.028896 | Efficacy | lm/W | 50 | 172.1275 | 191.2229 | 125 | -0.44938 | 0.80498 | 3.2629 | 3.669 | 1 | 1 | 72.4416 | 3.6221 | 76.1106 | 7.2911 | 2045 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 3.669 | 76.1106 | 7.2911
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0010325 | 0.0018871 | 0.00079194 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0065761 | 0.0061908 | 0.024935 | Efficacy | lm/W | 50 | 184.8481 | 205.3547 | 125 | -0.41643 | 0.74596 | 3.0237 | 3.4 | 1 | 1 | 72.4416 | 3.6221 | 75.8416 | 7.0221 | 2050 | Intermediate | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 3.4 | 75.8416 | 7.0221
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.001648 | 0.003012 | 0.001264 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.021554 | 0.020291 | 0.081726 | Efficacy | lm/W | 50 | 90.0141 | 100 | 125 | -0.66465 | 1.1906 | 4.8261 | 5.4267 | 1 | 1 | 72.4416 | 3.6221 | 77.8683 | 9.0488 | 2023 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 5.4267 | 77.8683 | 9.0488
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0013593 | 0.0024844 | 0.0010426 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.011309 | 0.010647 | 0.042881 | Efficacy | lm/W | 50 | 141.5056 | 157.2039 | 125 | -0.54824 | 0.98207 | 3.9807 | 4.4762 | 1 | 1 | 72.4416 | 3.6221 | 76.9178 | 8.0983 | 2030 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 4.4762 | 76.9178 | 8.0983
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0012776 | 0.0023351 | 0.00097993 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.009351 | 0.0088031 | 0.035456 | Efficacy | lm/W | 50 | 160.8524 | 178.6969 | 125 | -0.51528 | 0.92303 | 3.7414 | 4.2071 | 1 | 1 | 72.4416 | 3.6221 | 76.6487 | 7.8292 | 2035 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 4.2071 | 76.6487 | 7.8292
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0011959 | 0.0021857 | 0.00091725 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0078132 | 0.0073553 | 0.029625 | Efficacy | lm/W | 50 | 180.1991 | 200.19 | 125 | -0.48232 | 0.86399 | 3.5021 | 3.938 | 1 | 1 | 72.4416 | 3.6221 | 76.3796 | 7.5601 | 2040 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 3.938 | 76.3796 | 7.5601
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0011142 | 0.0020364 | 0.0008546 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0067415 | 0.0063465 | 0.025562 | Efficacy | lm/W | 50 | 194.5789 | 216.165 | 125 | -0.44938 | 0.80498 | 3.2629 | 3.669 | 1 | 1 | 72.4416 | 3.6221 | 76.1106 | 7.2911 | 2045 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 3.669 | 76.1106 | 7.2911
13 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 60W Equivalent A19 LED | LED | A19 | LED A19 | 2023$ | 0.0010325 | 0.0018871 | 0.00079194 | Light Output | Lumens | 100 | 800 | 800 | 3200 | 0.0058173 | 0.0054765 | 0.022058 | Efficacy | lm/W | 50 | 208.9587 | 232.1401 | 125 | -0.41643 | 0.74596 | 3.0237 | 3.4 | 1 | 1 | 72.4416 | 3.6221 | 75.8416 | 7.0221 | 2050 | Advanced | 1.6471 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 1679 | 0.06406 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 3.4 | 75.8416 | 7.0221
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.003157 | 0.002484 | 0.000155 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.079147 | 0.27601 | 0.13452 | Efficacy | lm/W | 50 | 106.015 | 123.0769 | 160 | -8.5149 | -17.2735 | 15.24 | 15.8792 | 1 | 1 | 72.4416 | 3.6221 | 88.3208 | 19.5013 | 2023 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.8792 | 88.3208 | 19.5013
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030873 | 0.0024291 | 0.00015158 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.064005 | 0.22321 | 0.10879 | Efficacy | lm/W | 50 | 128.1998 | 148.8321 | 160 | -8.3269 | -16.892 | 14.9034 | 15.5285 | 1 | 1 | 72.4416 | 3.6221 | 87.9701 | 19.1506 | 2030 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.5285 | 87.9701 | 19.1506
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030585 | 0.0024065 | 0.00015016 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.055782 | 0.19453 | 0.094809 | Efficacy | lm/W | 50 | 145.7274 | 169.1805 | 160 | -8.2492 | -16.7345 | 14.7645 | 15.3837 | 1 | 1 | 72.4416 | 3.6221 | 87.8253 | 19.0058 | 2035 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.3837 | 87.8253 | 19.0058
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030297 | 0.0023838 | 0.00014875 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.049324 | 0.17201 | 0.083833 | Efficacy | lm/W | 50 | 163.255 | 189.529 | 160 | -8.1716 | -16.577 | 14.6255 | 15.2389 | 1 | 1 | 72.4416 | 3.6221 | 87.6805 | 18.861 | 2040 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.2389 | 87.6805 | 18.861
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030018 | 0.0023618 | 0.00014738 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.045258 | 0.15783 | 0.076922 | Efficacy | lm/W | 50 | 176.2826 | 204.6533 | 160 | -8.0962 | -16.4241 | 14.4906 | 15.0983 | 1 | 1 | 72.4416 | 3.6221 | 87.5399 | 18.7204 | 2045 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.0983 | 87.5399 | 18.7204
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0029738 | 0.0023399 | 0.00014601 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.041751 | 0.1456 | 0.070961 | Efficacy | lm/W | 50 | 189.3103 | 219.7776 | 160 | -8.0208 | -16.2712 | 14.3557 | 14.9578 | 1 | 1 | 72.4416 | 3.6221 | 87.3994 | 18.5799 | 2050 | Reference | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 14.9578 | 87.3994 | 18.5799
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.003157 | 0.002484 | 0.000155 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.079147 | 0.27601 | 0.13452 | Efficacy | lm/W | 50 | 106.015 | 123.0769 | 160 | -8.5149 | -17.2735 | 15.24 | 15.8792 | 1 | 1 | 72.4416 | 3.6221 | 88.3208 | 19.5013 | 2023 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.8792 | 88.3208 | 19.5013
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030873 | 0.0024291 | 0.00015158 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.055657 | 0.19409 | 0.094596 | Efficacy | lm/W | 50 | 147.4298 | 171.1569 | 160 | -8.3269 | -16.892 | 14.9034 | 15.5285 | 1 | 1 | 72.4416 | 3.6221 | 87.9701 | 19.1506 | 2030 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.5285 | 87.9701 | 19.1506
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030585 | 0.0024065 | 0.00015016 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.048506 | 0.16915 | 0.082442 | Efficacy | lm/W | 50 | 167.5865 | 194.5576 | 160 | -8.2492 | -16.7345 | 14.7645 | 15.3837 | 1 | 1 | 72.4416 | 3.6221 | 87.8253 | 19.0058 | 2035 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.3837 | 87.8253 | 19.0058
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030297 | 0.0023838 | 0.00014875 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.042891 | 0.14957 | 0.072898 | Efficacy | lm/W | 50 | 187.7432 | 217.9583 | 160 | -8.1716 | -16.577 | 14.6255 | 15.2389 | 1 | 1 | 72.4416 | 3.6221 | 87.6805 | 18.861 | 2040 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.2389 | 87.6805 | 18.861
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030018 | 0.0023618 | 0.00014738 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.039355 | 0.13724 | 0.066888 | Efficacy | lm/W | 50 | 202.725 | 226.4236 | 160 | -8.0962 | -16.4241 | 14.4906 | 15.0983 | 1 | 1 | 72.4416 | 3.6221 | 87.5399 | 18.7204 | 2045 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.0983 | 87.5399 | 18.7204
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0029738 | 0.0023399 | 0.00014601 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.036305 | 0.12661 | 0.061705 | Efficacy | lm/W | 50 | 217.7069 | 234.8888 | 160 | -8.0208 | -16.2712 | 14.3557 | 14.9578 | 1 | 1 | 72.4416 | 3.6221 | 87.3994 | 18.5799 | 2050 | Intermediate | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 14.9578 | 87.3994 | 18.5799
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.003157 | 0.002484 | 0.000155 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.079147 | 0.27601 | 0.13452 | Efficacy | lm/W | 50 | 106.015 | 123.0769 | 160 | -8.5149 | -17.2735 | 15.24 | 15.8792 | 1 | 1 | 72.4416 | 3.6221 | 88.3208 | 19.5013 | 2023 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.8792 | 88.3208 | 19.5013
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030873 | 0.0024291 | 0.00015158 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.049235 | 0.1717 | 0.083681 | Efficacy | lm/W | 50 | 166.6598 | 193.4817 | 160 | -8.3269 | -16.892 | 14.9034 | 15.5285 | 1 | 1 | 72.4416 | 3.6221 | 87.9701 | 19.1506 | 2030 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.5285 | 87.9701 | 19.1506
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030585 | 0.0024065 | 0.00015016 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.042909 | 0.14964 | 0.07293 | Efficacy | lm/W | 50 | 189.4456 | 219.9347 | 160 | -8.2492 | -16.7345 | 14.7645 | 15.3837 | 1 | 1 | 72.4416 | 3.6221 | 87.8253 | 19.0058 | 2035 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.3837 | 87.8253 | 19.0058
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030297 | 0.0023838 | 0.00014875 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.037942 | 0.13231 | 0.064487 | Efficacy | lm/W | 50 | 212.2315 | 246.3877 | 160 | -8.1716 | -16.577 | 14.6255 | 15.2389 | 1 | 1 | 72.4416 | 3.6221 | 87.6805 | 18.861 | 2040 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.2389 | 87.6805 | 18.861
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0030018 | 0.0023618 | 0.00014738 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.034814 | 0.12141 | 0.05917 | Efficacy | lm/W | 50 | 229.1674 | 248.1938 | 160 | -8.0962 | -16.4241 | 14.4906 | 15.0983 | 1 | 1 | 72.4416 | 3.6221 | 87.5399 | 18.7204 | 2045 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 15.0983 | 87.5399 | 18.7204
14 | 2023 | Lighting | Electricity | Residential, Commercial | LED A-Type | 100W Equivalent LED A Lamp | LED | A21 | LED A21 | 2023$ | 0.0029738 | 0.0023399 | 0.00014601 | Light Output | Lumens | 320 | 1566.6667 | 1600 | 2910 | 0.032116 | 0.112 | 0.054586 | Efficacy | lm/W | 50 | 246.1034 | 250 | 160 | -8.0208 | -16.2712 | 14.3557 | 14.9578 | 1 | 1 | 72.4416 | 3.6221 | 87.3994 | 18.5799 | 2050 | Advanced | 1.928 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 458 | 0.181 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 14.9578 | 87.3994 | 18.5799
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.013782 | 0.017101 | 0.21248 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.050752 | -0.21248 | -0.19464 | Efficacy | lm/W | 50 | 82.0273 | 100 | 125 | -14.7421 | 15.9262 | 25.9484 | 21.4837 | 1 | 1 | 72.4416 | 3.6221 | 93.9253 | 25.1058 | 2023 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 21.4837 | 93.9253 | 25.1058
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.013217 | 0.0164 | 0.20377 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.041698 | -0.17457 | -0.15991 | Efficacy | lm/W | 50 | 95.7449 | 116.7232 | 125 | -14.1375 | 15.2731 | 24.8843 | 20.6027 | 1 | 1 | 72.4416 | 3.6221 | 93.0443 | 24.2248 | 2030 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 20.6027 | 93.0443 | 24.2248
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.013026 | 0.016163 | 0.20082 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.038338 | -0.1605 | -0.14703 | Efficacy | lm/W | 50 | 102.6324 | 125.1197 | 125 | -13.9334 | 15.0526 | 24.525 | 20.3052 | 1 | 1 | 72.4416 | 3.6221 | 92.7468 | 23.9273 | 2035 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 20.3052 | 92.7468 | 23.9273
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.012835 | 0.015926 | 0.19788 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.0354 | -0.14821 | -0.13576 | Efficacy | lm/W | 50 | 109.5199 | 133.5163 | 125 | -13.7293 | 14.8321 | 24.1657 | 20.0078 | 1 | 1 | 72.4416 | 3.6221 | 92.4494 | 23.6298 | 2040 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 20.0078 | 92.4494 | 23.6298
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.012651 | 0.015698 | 0.19504 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.03284 | -0.13749 | -0.12594 | Efficacy | lm/W | 50 | 116.3654 | 141.8617 | 125 | -13.5323 | 14.6193 | 23.8191 | 19.7207 | 1 | 1 | 72.4416 | 3.6221 | 92.1623 | 23.3428 | 2045 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 19.7207 | 92.1623 | 23.3428
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.012467 | 0.015469 | 0.1922 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.030564 | -0.12796 | -0.11721 | Efficacy | lm/W | 50 | 123.2109 | 150.2072 | 125 | -13.3354 | 14.4065 | 23.4724 | 19.4337 | 1 | 1 | 72.4416 | 3.6221 | 91.8753 | 23.0558 | 2050 | Reference | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 19.4337 | 91.8753 | 23.0558
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.013782 | 0.013782 | 0.013782 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.050752 | -0.21248 | -0.19464 | Efficacy | lm/W | 50 | 82.0273 | 100 | 125 | -14.7421 | 15.9262 | 25.9484 | 17.0224 | 1 | 1 | 72.4416 | 3.6221 | 89.464 | 20.6445 | 2023 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 17.0224 | 89.464 | 20.6445
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.013217 | 0.013217 | 0.013217 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.041698 | -0.17457 | -0.15991 | Efficacy | lm/W | 50 | 95.7449 | 134.2316 | 125 | -14.1375 | 15.2731 | 24.8843 | 16.3244 | 1 | 1 | 72.4416 | 3.6221 | 88.766 | 19.9464 | 2030 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 16.3244 | 88.766 | 19.9464
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.013026 | 0.016163 | 0.20082 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.035497 | -0.14861 | -0.13613 | Efficacy | lm/W | 50 | 110.8464 | 143.8877 | 125 | -13.9334 | 15.0526 | 24.525 | 20.3052 | 1 | 1 | 72.4416 | 3.6221 | 92.7468 | 23.9273 | 2035 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 20.3052 | 92.7468 | 23.9273
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.012835 | 0.015926 | 0.19788 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.030783 | -0.12888 | -0.11805 | Efficacy | lm/W | 50 | 125.9478 | 153.5437 | 125 | -13.7293 | 14.8321 | 24.1657 | 20.0078 | 1 | 1 | 72.4416 | 3.6221 | 92.4494 | 23.6298 | 2040 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 20.0078 | 92.4494 | 23.6298
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.012651 | 0.015698 | 0.19504 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.028556 | -0.11955 | -0.10952 | Efficacy | lm/W | 50 | 133.8202 | 163.141 | 125 | -13.5323 | 14.6193 | 23.8191 | 19.7207 | 1 | 1 | 72.4416 | 3.6221 | 92.1623 | 23.3428 | 2045 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 19.7207 | 92.1623 | 23.3428
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.012467 | 0.015469 | 0.1922 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.026577 | -0.11127 | -0.10193 | Efficacy | lm/W | 50 | 141.6926 | 172.7382 | 125 | -13.3354 | 14.4065 | 23.4724 | 19.4337 | 1 | 1 | 72.4416 | 3.6221 | 91.8753 | 23.0558 | 2050 | Intermediate | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 19.4337 | 91.8753 | 23.0558
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.013782 | 0.013782 | 0.013782 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.050752 | -0.21248 | -0.19464 | Efficacy | lm/W | 50 | 82.0273 | 100 | 125 | -14.7421 | 15.9262 | 25.9484 | 17.0224 | 1 | 1 | 72.4416 | 3.6221 | 89.464 | 20.6445 | 2023 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 17.0224 | 89.464 | 20.6445
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.013217 | 0.013217 | 0.013217 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.041698 | -0.17457 | -0.15991 | Efficacy | lm/W | 50 | 95.7449 | 151.7401 | 125 | -14.1375 | 15.2731 | 24.8843 | 16.3244 | 1 | 1 | 72.4416 | 3.6221 | 88.766 | 19.9464 | 2030 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 16.3244 | 88.766 | 19.9464
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.013026 | 0.016163 | 0.20082 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.033048 | -0.13836 | -0.12674 | Efficacy | lm/W | 50 | 119.0604 | 162.6556 | 125 | -13.9334 | 15.0526 | 24.525 | 20.3052 | 1 | 1 | 72.4416 | 3.6221 | 92.7468 | 23.9273 | 2035 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 20.3052 | 92.7468 | 23.9273
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.012835 | 0.015926 | 0.19788 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.027231 | -0.11401 | -0.10443 | Efficacy | lm/W | 50 | 142.3758 | 173.5712 | 125 | -13.7293 | 14.8321 | 24.1657 | 20.0078 | 1 | 1 | 72.4416 | 3.6221 | 92.4494 | 23.6298 | 2040 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 20.0078 | 92.4494 | 23.6298
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.012651 | 0.015698 | 0.19504 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.025261 | -0.10576 | -0.096879 | Efficacy | lm/W | 50 | 151.275 | 184.4202 | 125 | -13.5323 | 14.6193 | 23.8191 | 19.7207 | 1 | 1 | 72.4416 | 3.6221 | 92.1623 | 23.3428 | 2045 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 19.7207 | 92.1623 | 23.3428
15 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED PAR 38 | LED | PAR38 | LED PAR38 | 2023$ | 0.012467 | 0.015469 | 0.1922 | Light Output | Lumens | 100 | 1344.1667 | 1700 | 3200 | 0.023511 | -0.09843 | -0.090165 | Efficacy | lm/W | 50 | 160.1742 | 195.2693 | 125 | -13.3354 | 14.4065 | 23.4724 | 19.4337 | 1 | 1 | 72.4416 | 3.6221 | 91.8753 | 23.0558 | 2050 | Advanced | 3.1133 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 15 | 800 | 0.07237 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. New construction installation costs are much higher because it requires a fixture install, which takes a lot longer than simply replacing a light bulb (retrofit). | 19.4337 | 91.8753 | 23.0558
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.001901 | 0.001219 | 0.009184 | Light Output | Lumens | 600 | 683.0769 | 650 | 1600 | -0.014919 | 0.004457 | -0.075722 | Efficacy | lm/W | 53.8462 | 78.5538 | 90.2778 | 150 | 3.9588 | 6.0319 | 12.0849 | 7.2147 | 1 | 1 | 0 | 0 | 7.2147 | 7.2147 | 2023 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 7.2147 | 7.2147 | 7.2147
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0015595 | 0.001 | 0.0075341 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.010485 | 0.0031324 | -0.053218 | Efficacy | lm/W | 53.8462 | 91.6905 | 105.3751 | 150 | 3.2476 | 4.9483 | 9.9138 | 5.8855 | 1 | 1 | 0 | 0 | 5.8855 | 5.8855 | 2030 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 5.8855 | 5.8855 | 5.8855
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0014673 | 0.0009409 | 0.0070888 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0092035 | 0.0027495 | -0.046713 | Efficacy | lm/W | 53.8462 | 98.2863 | 112.9553 | 150 | 3.0557 | 4.6558 | 9.3279 | 5.5377 | 1 | 1 | 0 | 0 | 5.5377 | 5.5377 | 2035 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 5.5377 | 5.5377 | 5.5377
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0013752 | 0.0008818 | 0.0066436 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.008083 | 0.0024148 | -0.041026 | Efficacy | lm/W | 53.8462 | 104.8821 | 120.5355 | 150 | 2.8638 | 4.3634 | 8.742 | 5.1898 | 1 | 1 | 0 | 0 | 5.1898 | 5.1898 | 2040 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 5.1898 | 5.1898 | 5.1898
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0012833 | 0.00082292 | 0.0061999 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0070995 | 0.002121 | -0.036034 | Efficacy | lm/W | 53.8462 | 111.4378 | 128.0696 | 150 | 2.6725 | 4.072 | 8.1583 | 4.8433 | 1 | 1 | 0 | 0 | 4.8433 | 4.8433 | 2045 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 4.8433 | 4.8433 | 4.8433
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0011915 | 0.00076404 | 0.0057563 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0062253 | 0.0018598 | -0.031597 | Efficacy | lm/W | 53.8462 | 117.9934 | 135.6037 | 150 | 2.4813 | 3.7807 | 7.5745 | 4.4967 | 1 | 1 | 0 | 0 | 4.4967 | 4.4967 | 2050 | Reference | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 4.4967 | 4.4967 | 4.4967
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.001901 | 0.001219 | 0.009184 | Light Output | Lumens | 600 | 683.0769 | 650 | 1600 | -0.014919 | 0.004457 | -0.075722 | Efficacy | lm/W | 53.8462 | 78.5538 | 90.2778 | 150 | 3.9588 | 6.0319 | 12.0849 | 7.2147 | 1 | 1 | 0 | 0 | 7.2147 | 7.2147 | 2023 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 7.2147 | 7.2147 | 7.2147
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0015595 | 0.001 | 0.0075341 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0091176 | 0.0027239 | -0.046277 | Efficacy | lm/W | 53.8462 | 105.4441 | 121.1813 | 150 | 3.2476 | 4.9483 | 9.9138 | 5.8855 | 1 | 1 | 0 | 0 | 5.8855 | 5.8855 | 2030 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 5.8855 | 5.8855 | 5.8855
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0014673 | 0.0009409 | 0.0070888 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0080031 | 0.0023909 | -0.04062 | Efficacy | lm/W | 53.8462 | 113.0292 | 129.8986 | 150 | 3.0557 | 4.6558 | 9.3279 | 5.5377 | 1 | 1 | 0 | 0 | 5.5377 | 5.5377 | 2035 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 5.5377 | 5.5377 | 5.5377
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0013752 | 0.0008818 | 0.0066436 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0070287 | 0.0020998 | -0.035675 | Efficacy | lm/W | 53.8462 | 120.6144 | 138.6159 | 150 | 2.8638 | 4.3634 | 8.742 | 5.1898 | 1 | 1 | 0 | 0 | 5.1898 | 5.1898 | 2040 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 5.1898 | 5.1898 | 5.1898
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0012833 | 0.00082292 | 0.0061999 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0061735 | 0.0018443 | -0.031334 | Efficacy | lm/W | 53.8462 | 128.1534 | 147.28 | 150 | 2.6725 | 4.072 | 8.1583 | 4.8433 | 1 | 1 | 0 | 0 | 4.8433 | 4.8433 | 2045 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 4.8433 | 4.8433 | 4.8433
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0011915 | 0.00076404 | 0.0057563 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0054133 | 0.0016172 | -0.027475 | Efficacy | lm/W | 53.8462 | 135.6925 | 155.9442 | 150 | 2.4813 | 3.7807 | 7.5745 | 4.4967 | 1 | 1 | 0 | 0 | 4.4967 | 4.4967 | 2050 | Intermediate | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 4.4967 | 4.4967 | 4.4967
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.001901 | 0.001219 | 0.009184 | Light Output | Lumens | 600 | 683.0769 | 650 | 1600 | -0.014919 | 0.004457 | -0.075722 | Efficacy | lm/W | 53.8462 | 78.5538 | 90.2778 | 150 | 3.9588 | 6.0319 | 12.0849 | 7.2147 | 1 | 1 | 0 | 0 | 7.2147 | 7.2147 | 2023 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 7.2147 | 7.2147 | 7.2147
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0015595 | 0.001 | 0.0075341 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0080656 | 0.0024096 | -0.040937 | Efficacy | lm/W | 53.8462 | 119.1976 | 136.9876 | 150 | 3.2476 | 4.9483 | 9.9138 | 5.8855 | 1 | 1 | 0 | 0 | 5.8855 | 5.8855 | 2030 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 5.8855 | 5.8855 | 5.8855
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0014673 | 0.0009409 | 0.0070888 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0070797 | 0.002115 | -0.035933 | Efficacy | lm/W | 53.8462 | 127.7722 | 146.8419 | 150 | 3.0557 | 4.6558 | 9.3279 | 5.5377 | 1 | 1 | 0 | 0 | 5.5377 | 5.5377 | 2035 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 5.5377 | 5.5377 | 5.5377
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0013752 | 0.0008818 | 0.0066436 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0062177 | 0.0018575 | -0.031558 | Efficacy | lm/W | 53.8462 | 136.3468 | 156.6962 | 150 | 2.8638 | 4.3634 | 8.742 | 5.1898 | 1 | 1 | 0 | 0 | 5.1898 | 5.1898 | 2040 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 5.1898 | 5.1898 | 5.1898
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0012833 | 0.00082292 | 0.0061999 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0054612 | 0.0016315 | -0.027718 | Efficacy | lm/W | 53.8462 | 144.8691 | 166.4905 | 150 | 2.6725 | 4.072 | 8.1583 | 4.8433 | 1 | 1 | 0 | 0 | 4.8433 | 4.8433 | 2045 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 4.8433 | 4.8433 | 4.8433
16 | 2023 | Lighting | Electricity | Residential, Commercial | LED - Reflector | LED BR30 | LED | BR30 | LED BR30 | 2023$ | 0.0011915 | 0.00076404 | 0.0057563 | Light Output | Lumens | 600 | 650 | 650 | 1600 | -0.0047887 | 0.0014306 | -0.024305 | Efficacy | lm/W | 53.8462 | 153.3915 | 176.2848 | 150 | 2.4813 | 3.7807 | 7.5745 | 4.4967 | 1 | 1 | 0 | 0 | 4.4967 | 4.4967 | 2050 | Advanced | 2.125 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 14 | 432 | N/A | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 4.4967 | 4.4967 | 4.4967
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 350 | 600 | 900 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 300000 | 1.0536 | 1.0672 | 0 | 0 | 316084.6763 | 320159.7979 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 300000 | 316084.6763 | 320159.7979
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 350 | 600 | 900 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 300000 | 1.0536 | 1.0672 | 0 | 0 | 316084.6763 | 320159.7979 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 300000 | 316084.6763 | 320159.7979
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 350 | 600 | 900 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 300000 | 1.0536 | 1.0672 | 0 | 0 | 316084.6763 | 320159.7979 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 300000 | 316084.6763 | 320159.7979
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 350 | 600 | 900 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 300000 | 1.0536 | 1.0672 | 0 | 0 | 316084.6763 | 320159.7979 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 300000 | 316084.6763 | 320159.7979
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 350 | 600 | 900 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 300000 | 1.0536 | 1.0672 | 0 | 0 | 316084.6763 | 320159.7979 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 300000 | 316084.6763 | 320159.7979
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 350 | 600 | 900 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.3825 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 300000 | 1.0536 | 1.0672 | 0 | 0 | 316084.6763 | 320159.7979 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 300000 | 316084.6763 | 320159.7979
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 350 | 600 | 900 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 300000 | 1.0536 | 1.0672 | 0 | 0 | 316084.6763 | 320159.7979 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 300000 | 316084.6763 | 320159.7979
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 381.5 | 654 | 981 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 7.4796e-07 | 7.63e-06 | -2.18e-06 | 327000 | 1.0536 | 1.0672 | 0 | 0 | 344532.2972 | 348974.1797 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 327000 | 344532.2972 | 348974.1797
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 393.75 | 675 | 1012.5 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 7.7197e-07 | 7.875e-06 | -2.25e-06 | 337500 | 1.0536 | 1.0672 | 0 | 0 | 355595.2609 | 360179.7726 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 337500 | 355595.2609 | 360179.7726
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 406 | 696 | 1044 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 7.9599e-07 | 8.12e-06 | -2.32e-06 | 348000 | 1.0536 | 1.0672 | 0 | 0 | 366658.2246 | 371385.3655 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 348000 | 366658.2246 | 371385.3655
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 411.25 | 705 | 1057.5 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 8.0628e-07 | 8.225e-06 | -2.35e-06 | 352500 | 1.0536 | 1.0672 | 0 | 0 | 371399.4947 | 376187.7625 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 352500 | 371399.4947 | 376187.7625
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 416.5 | 714 | 1071 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.34625 | 0.3 | 0.25 | 8.1658e-07 | 8.33e-06 | -2.38e-06 | 357000 | 1.0536 | 1.0672 | 0 | 0 | 376140.7649 | 380990.1595 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 357000 | 376140.7649 | 380990.1595
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 350 | 600 | 900 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 6.862e-07 | 7e-06 | -2e-06 | 300000 | 1.0536 | 1.0672 | 0 | 0 | 316084.6763 | 320159.7979 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 300000 | 316084.6763 | 320159.7979
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 413 | 708 | 1062 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 8.0971e-07 | 8.26e-06 | -2.36e-06 | 354000 | 1.0536 | 1.0672 | 0 | 0 | 372979.9181 | 377788.5615 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 354000 | 372979.9181 | 377788.5615
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 437.5 | 750 | 1125 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 8.5775e-07 | 8.75e-06 | -2.5e-06 | 375000 | 1.0536 | 1.0672 | 0 | 0 | 395105.8454 | 400199.7474 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 375000 | 395105.8454 | 400199.7474
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 462 | 792 | 1188 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 9.0578e-07 | 9.24e-06 | -2.64e-06 | 396000 | 1.0536 | 1.0672 | 0 | 0 | 417231.7728 | 422610.9332 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 396000 | 417231.7728 | 422610.9332
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 472.5 | 810 | 1215 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 9.2637e-07 | 9.45e-06 | -2.7e-06 | 405000 | 1.0536 | 1.0672 | 0 | 0 | 426714.3131 | 432215.7271 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 405000 | 426714.3131 | 432215.7271
17 | 2023 | Cooling | Electricity | Commercial |  | Commercial Centrifugal Chillers (Water-Cooled) | Centrifugal Chiller | Water-Cooled | Centrifugal Chillers Water-Cooled | 2023$ | 483 | 828 | 1242 | Capacity | Tons | 150 | 500 | 3000 | 3000 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.55 | 0.31 | 0.3 | 0.25 | 9.4695e-07 | 9.66e-06 | -2.76e-06 | 414000 | 1.0536 | 1.0672 | 0 | 0 | 436196.8534 | 441820.5211 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 139 | 0.4291 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. Does not distinguish betewwn oil bearing and magnetic bearing chillers. | 414000 | 436196.8534 | 441820.5211
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
18 | 2023 | Refrigeration | Electricity | Commercial |  | Commerical Ice Maker | Ice Machine | Standard | Commercial Ice Machine Standard | 2023$ | 0.89766 | 1.0238 | 1.7986 | Capacity | lb. ice/day | 28 | 700 | 700 | 1508 | -167.97 | -183.5864 | -247.19 | Energy Use | kWh/100 lb. | 3.56 | 5.8 | 4.8 | 12.16 | 2244.5459 | 2520.064 | 3271.7711 | 2171.9209 | 1.17 | 1.46 | 0 | 0 | 2541.1475 | 3171.0046 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 159 | 0.61 | 2023 | DOE standards data did not distinguish between Ice Machines and Ice Makers | 2171.9209 | 2541.1475 | 3171.0046
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2023 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2030 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2035 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2040 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2045 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2050 | Reference | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2023 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2030 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2035 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2040 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2045 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2050 | Intermediate | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2023 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2030 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2035 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2040 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2045 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
19 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Furnace | Furnace | Oil-Fired | Commercial Oil-Fired Furnaces | 2023$ | 4.2169 | 5.2711 | 6.3253 | Capacity | MBH | 400 | 250 | 250 | 6525 | 0 | 0 | 0 | Efficiency | % | 81 | 82 | 85 | 85 | 2961.3115 | 3701.6393 | 4441.9672 | 5019.4103 | 1.08 | 1.12 | 0 | 0 | 5420.9632 | 5621.7396 | 2050 | Advanced | 23 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 4 | 20 | 0.56 | 2023 | 1) No commercial furnaces above 85% efficiency were found. 2) Lower bound comes from the efficiency found on manufacturer's website | 5019.4103 | 5420.9632 | 5621.7396
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2023 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2030 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2035 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2040 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 88 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2045 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 81 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2050 | Reference | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2023 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2030 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2035 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2040 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 91.5 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2045 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 88 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2050 | Intermediate | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2023 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2030 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2035 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2040 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2045 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
20 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Furnaces | Furnace | Gas-Fired | Commercial Gas-Fired Furnaces | 2023$ | 13.5765 | 16.9706 | 20.3647 | Capacity | BMH | 45 | 250 | 250 | 400 | 0 | 0 | 0 | Efficiency | % | 81 | 81 | 95 | 85 | -210.5882 | -263.2353 | -315.8823 | 3979.4117 | 1.16 | 1.22 | 0 | 0 | 4616.1176 | 4854.8823 | 2050 | Advanced | 21.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 20 | 0.79 | 2023 | 1) No data exists for High values of the EIA Reference Data. Since High values from the Reference and Advanced case were not shown to differ across all technologies, the Advanced High values were used for the Reference High Values. 2) Upperbound value for metric 2 assumed to be the high value as no commercial gas furnaces higher than 95% were found | 3979.4117 | 4616.1176 | 4854.8823
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
21 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boiler | Boiler | Electric Steam | Commercial Electric Steam Boiler | 2023$ | 16 | 20 | 24 | Capacity | MBH | 20.5 | 563 | 11516 | 11516 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 1.6e-06 | 2e-06 | 2.4e-06 | 11260 | 1.14 | 1.18 | 0 | 0 | 12836.4 | 13286.8 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 7 | 83 | 0.82 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12836.4 | 13286.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
22 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Boilers | Boiler | Electric Hot Water | Boiler - Electric Hot Water | 2023$ | 16 | 20 | 24 | Capacity | MBH | 25.6 | 563 | 12286 | 12286 | 0 | 0 | 0 | Efficiency | % | 98 | 98 | 99 | 99 | 5.6e-06 | 7e-06 | 8.4e-06 | 11260 | 1.1 | 1.13 | 0 | 0 | 12386 | 12723.8 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 5 | 123 | 0.61 | 2023 | 1) Electric Boilers operate at efficiencies close to 100%. Hot water electric boilers are theoretically SLIGHTLY more efficient than steam based electric boilers. For analysis, this difference was assumed insignificant and both types of boilers were referenced to be 98-99% efficiency as per data sources. 2) Since the High Data from the EIA did not exist, the upperbound value was used as the high value | 11260 | 12386 | 12723.8
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2023 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2030 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2035 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2040 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2045 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2050 | Reference | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2023 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2030 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2035 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2040 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2045 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2050 | Intermediate | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2023 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2030 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2035 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2040 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2045 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
23 | 2023 | Heating | Oil | Commercial |  | Commercial Oil-Fired Water Heater | Water Heater | Oil-Fired | Commercial Oil-Fired Water Heater | 2023$ | 96 | 120 | 144 | Capacity | MBH | 125 | 85 | 85 | 900 | 0 | 0 | 0 | Efficiency | % | 80 | 81 | 82 | 82 | 17200 | 21500 | 25800 | 31700 | 1.03 | 1.06 | 0 | 0 | 32651 | 33602 | 2050 | Advanced | 13 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 65 | 0.5589 | 2023 | All oil-fired water heaters have an efficiency between 80-82%. However, a one variable regression was done since sources did not give the exact efficiency value. | 31700 | 32651 | 33602
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 14.8 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.1 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 14.8 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.55 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.675 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 15.8 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.05 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.3 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 14.8 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.25 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 16.5 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 17 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
24 | 2023 | Cooling | Elecricity | Commercial |  | Commercial Rooftop Air Conditioners | Air Conditioner | Electric Rooftop | Air Conditioner - Electric Rooftop | 2023$ | 965.21 | 1162.22 | 1724.4907 | Capacity | MBH | 3 | 90 | 90 | 100 | 0 | 0 | 0 | IEER | Unitless | 13.2 | 17.5 | 23.3 | 23.3 | -2391.3043 | -1111.1111 | -1224.5356 | 103488.6889 | 1.15 | 1.16 | 0 | 0 | 119011.9922 | 120046.8791 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 93 | 0.7048 | 2023 | 1) EER is the ratio of the cooling capacity (in Btu/h) to the power input (in watts) and provides a measure of the efficiency of equipment operating at full load (i.e., 100 percent cooling capacity) in high-ambienttemperature conditions (i.e., 95 °F). IEER is a single number part-load efficiency based on weighting of EER at various load capacities. The relationship between IEER and EER is weak. 2) The high value from the EIA Report was used at the Upper Bound as no higher efficienct units could be found online. | 103488.6889 | 119011.9922 | 120046.8791
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
25 | 2023 | Cooling | Electricity | Commercial |  | Commercial Packaged Terminal Air Conditioner | Air Conditioner | Packaged Terminal | Commercial Packaged Terminal Air Conditioner | 2023$/kBtu/h | 0 | 0 | 0 | Capacity | kBTU/h | 6 | 9 | 9 | 48 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 84.4953 | 168.8672 | 293.5417 | 1519.8046 | 1.13 | 1.26 | 0 | 0 | 1717.3792 | 1914.9538 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 3 | 33 | N/A | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 1 since no higher capacity was found | 1519.8046 | 1717.3792 | 1914.9538
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 137.619 | 172.0238 | 206.4286 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 214.2857 | 267.8571 | 321.4286 | 1816.0714 | 1.15 | 1.18 | 0 | 0 | 2088.4821 | 2142.9643 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1816.0714 | 2088.4821 | 2142.9643
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 137.619 | 172.0238 | 206.4286 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 214.2857 | 267.8571 | 321.4286 | 1816.0714 | 1.15 | 1.18 | 0 | 0 | 2088.4821 | 2142.9643 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1816.0714 | 2088.4821 | 2142.9643
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.625 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.75 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.85 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.95 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 137.619 | 172.0238 | 206.4286 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.3 | 13.1 | 13.1 | 214.2857 | 267.8571 | 321.4286 | 1816.0714 | 1.15 | 1.18 | 0 | 0 | 2088.4821 | 2142.9643 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1816.0714 | 2088.4821 | 2142.9643
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.5 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 11.75 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 12 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 12.2 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
26 | 2023 | Heating | Electricity | Commercial |  | Packaged Terminal Heat Pumps | Heat Pump | Packaged Terminal | Heat Pump - Packaged Terminal | 2023$ | 138.4685 | 173.0857 | 207.7028 | Capacity | kBTU/h | 9.5 | 9 | 13.1 | 13.1 | 0 | 0 | 0 | EER | BTU/W | 6 | 12.4 | 13.1 | 13.1 | 215.6085 | 269.5106 | 323.4127 | 1827.2817 | 1.15 | 1.18 | 0 | 0 | 2101.374 | 2156.1925 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 26 | 0.5223 | 2023 | 1) High Value from EIA Report was used as the Upper Bound for Metric 2 since no higher efficiency was found. Lower value for metric 2 comes from EIA standards data. 2) According to the EIA, efficiency is higher from the advanced case than the reference case. Though the price is constant between the two cases, the changes in efficiency were not reflected within the data because a one variable regression was run without using the efficiency as a variable. | 1827.2817 | 2101.374 | 2156.1925
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.51407 | 0.52521 | 1.7771 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 333 | 333 | 333 | 4.3e-05 | 2042.0794 | 4679.9385 | 2462.2466 | 1.09 | 1.16 | 0 | 0 | 2683.8488 | 2856.206 | 2023 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. 3) Metric 1, airflow, refers to System Airflow. Metric 2, Annual Energy Use, refers to Annual Fan Energy Use. | 2462.2466 | 2683.8488 | 2856.206
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 296.0093 | 296.0093 | 296.0093 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2030 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 263.1277 | 263.1277 | 263.1277 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2035 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 233.8987 | 233.8987 | 233.8987 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2040 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 207.9165 | 207.9165 | 207.9165 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2045 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 184.8205 | 184.8205 | 184.8205 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2050 | Reference | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.51407 | 0.52521 | 1.7771 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 333 | 333 | 333 | 4.3e-05 | 2042.0794 | 4679.9385 | 2462.2466 | 1.09 | 1.16 | 0 | 0 | 2683.8488 | 2856.206 | 2023 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2462.2466 | 2683.8488 | 2856.206
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 296.0093 | 296.0093 | 296.0093 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2030 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 263.1277 | 263.1277 | 263.1277 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2035 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 233.8987 | 233.8987 | 233.8987 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2040 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 207.9165 | 207.9165 | 207.9165 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2045 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 184.8205 | 184.8205 | 184.8205 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2050 | Intermediate | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.51407 | 0.52521 | 1.7771 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 333 | 333 | 333 | 4.3e-05 | 2042.0794 | 4679.9385 | 2462.2466 | 1.09 | 1.16 | 0 | 0 | 2683.8488 | 2856.206 | 2023 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2462.2466 | 2683.8488 | 2856.206
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 296.0093 | 296.0093 | 296.0093 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2030 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 263.1277 | 263.1277 | 263.1277 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2035 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 233.8987 | 233.8987 | 233.8987 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2040 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 207.9165 | 207.9165 | 207.9165 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2045 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
27 | 2023 | Cooling | Electricity | Commercial |  | Commercial Fan Coil Units | Fan Coil Unit | Standard | Fan Coil Unit - Standard | 2023$ | 0.57831 | 0.59084 | 1.9991 | Airflow | cfm | 200 | 800 | 800 | 12000 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 333 | 184.8205 | 184.8205 | 184.8205 | 4.8373e-05 | 2297.2668 | 5264.7646 | 2769.94 | 1.09 | 1.16 | 0 | 0 | 3019.2346 | 3213.1304 | 2050 | Advanced | 37 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 129 | 0.2143 | 2023 | 1) Installed Cost from EIA report was used in place of the equipment cost since equipment cost was not found in EIA report. 2) Lower and Upper Bounds values were set to be the Typical and High values from the EIA report as online sources did not provide efficiency metric. | 2769.94 | 3019.2346 | 3213.1304
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2023 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2030 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2035 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2040 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2045 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2050 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2023 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2030 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2035 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2040 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2045 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2050 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2023 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2030 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2035 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2040 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2045 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
28 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Booster Water Heaters | Water Heater | Electric Booster | Water Heater - Electric Booster | 2023$ | 80.4471 | 107.7997 | 167.0917 | Capacity | gal | 5 | 6 | 16 | 1500 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | -3922.5882 | 5765.3385 | 27797.1429 | 6412.1368 | 1.01 | 1.44 | 0 | 0 | 6476.2581 | 9233.4769 | 2050 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades, Condition of existing electrical system, Need for additional wiring / switching | 2 | 93 | 0.5811 | 2023 | 1) EIA data thermal efficiency did not contain the standby loss (kBTU/hr) so the thermal efficiency could not be converted to UEF. Thermal Efficiency is said to be 98% for electric water heaters. 2) According to standards data, price increases were shown for units that had a higher UEF. Enough data did not exist to run a 2 var regression. 3) Commercial booster water heaters are regulated by DOE as either storage or instantaneous water heaters, depending on the ratio of input capacity to storage volume. Units with input capacity < 4,000 Btu/h per gallon of stored water are storage water heaters; all other units are instantaneous water heaters. Both water heaters were used in this regression | 6412.1368 | 6476.2581 | 9233.4769
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
29 | 2023 | Cooling | Electricity | Commercial |  | Commercial Gas-Fired Chillers (Water-Cooled, Direct-Fired Only) | Gas-fired Chiller | Water Cooled | Gas-Fired Chillers Water-Cooled | 2023$ | 827.9137 | 865 | 823.8889 | Capacity | Tons | 10 | 500 | 1000 | 1000 | 0 | 0 | 0 | Efficiency (IPLV) | COP | 1.2 | 1.2 | 1.8 | 1.8 | 5960.4317 | 15000 | 86611.1111 | 447500 | 1.0502 | 1.0664 | 0 | 0 | 469951.3167 | 477218.0891 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 12 | 0.9296 | 2023 | There is no available efficiency data. | 447500 | 469951.3167 | 477218.0891
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2023 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2030 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2035 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2040 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2045 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2050 | Reference | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2023 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2030 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2035 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2040 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2045 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2050 | Intermediate | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2023 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2030 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2035 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2040 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2045 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
30 | 2023 | Cooling | Electricity | Commercial |  | Commercial Beverage Merchandisers | Beverage Merchandisers | Standard | Beverage Merchandisers - Standard | 2023$ | 46.0981 | 57.6227 | 69.1472 | Volume | ft3 | 3 | 27 | 27 | 57.5 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1141 | 1141 | 902 | 902 | 452.5575 | 565.6968 | 678.8362 | 2121.5087 | 1.2 | 1.22 | 0 | 0 | 2545.8105 | 2588.2407 | 2050 | Advanced | 31 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 10 | 0.6397 | 2024 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. | 2121.5087 | 2545.8105 | 2588.2407
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2023 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2030 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2035 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2040 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2045 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2050 | Reference | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2023 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2030 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2035 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2040 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2045 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2050 | Intermediate | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2023 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2030 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2035 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2040 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2045 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
31 | 2023 | Cooling | Electricity | Commercial |  | Commercial Refrigerated Vending Machines | Refrigerated Vending Machine | Standard | Refrigerated Vending Machine - Standard | 2023$ | 29.9859 | 37.4824 | 44.9789 | Volume | ft3 | 35 | 35 | 35 | 84.44 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1531 | 1531 | 1443 | 1443 | 2903.9876 | 3629.9845 | 4355.9814 | 4941.8692 | 1.09 | 1.11 | 0 | 0 | 5386.6374 | 5485.4748 | 2050 | Advanced | 13.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 6 | 28 | 0.331 | 2018 | 1) Efficiency data could not be found on Oneline Retailer Websites or RSMeans, but was found on EIA Standards Data. EIA Standards Data was not used because average consumer price was unable to be calculated. 2) EIA Energy Usage Typical and High values were used as the Lower Bound and Upper Bound for the energy efficiency metric. 3) | 4941.8692 | 5386.6374 | 5485.4748
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
32 | 2023 | Heating | Electricity | Commercial |  | Gas-Fired Engine-Drive Rooftop Air Conditioners | Gas-Fired Engine-Drive Rooftop Air Conditioners | Standard | Gas-Fired Engine-Drive Rooftop Air Conditioners - Standard | $2023/ton | 0 | 0 | 0 | Capacity | ton | 8 | 11 | 11 | 15 | 0 | 0 | 0 | COP | Unitless | 1.4 | 1.4 | 1.4 | 1.4 | 2857.14 | 3694.7251 | 4214.5312 | 40641.9761 | 1.01 | 1.03 | 0 | 0 | 41048.3959 | 41861.2354 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Electrical infrastructure upgrades, Software upgrades, Site assessment, Ceiling height, Coil upgrades | 2 | 18 | N/A | 2023 | Data points from Gas Driven Heat Pump units was used to build projections and values. This decision was based on information found in the EIA document for Rooftop Air Conditioner units. EIA values were used as the lower bound and upper bound for the COP metric. | 40641.9761 | 41048.3959 | 41861.2354
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooking | Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
33 | 2023 | Cooking | Electricity | Commercial |  |  | Commercial Induction Cooktop | Induction Cooktop | Commercial Induction Cooktop | 2023$ | 1117.7825 | 1250.5125 | 1329.9072 | Volume | ft3 | 0.35 | 1.0325 | 5.68 | 5.68 | -160.7177 | 176.218 | 170.4762 | Capacity | kW | 1.4 | 2.45 | 2.45 | 5 | 17.2266 | 292.8491 | 1032.1192 | 2015.7373 | 1.05 | 1.06 | 0 | 0 | 2116.5241 | 2136.6815 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 21 | 0.3811 | 2024 | 1) Commercial EIA data did not exist. As a result, the residential data for the EIA was used. 2) Size metric (Metric 1 - Capacity) did not exist in the EIA data so the median value from the data collected was used as the "Typical" in the EIA. The max value from the data collected was used as the "high". | 2015.7373 | 2116.5241 | 2136.6815
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2023 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2030 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2035 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2040 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2045 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2050 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2023 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2030 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2035 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2040 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2045 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2050 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2023 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2030 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2035 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2040 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2045 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
34 | 2023 | Cooking | Electricity | Commercial |  |  | Induction Wells |  | Induction Wells | 2023$ | 9.0288 | 11.286 | 13.5432 | Volume | ft3 | 1.35 | 11.69 | 98.1 | 98.1 | 1383.1151 | 1728.8939 | 2074.6727 | Capacity | kW | 0.7 | 1.59 | 4.76 | 4.76 | 242.8203 | 303.5253 | 364.2304 | 3184.4 | 1.02 | 1.02 | 0 | 0 | 3248.088 | 3248.088 | 2050 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 11 | 0.8541 | 2024 | 1) EIA data did not exist. As a result, the typical value was found to be the median of the data points and the high was the max of the datapoints. Advanced case was assumed to be the same as the Reference case. 2) Higher efficient units (metric 2 - Energy) are associated with a lower capacity (metric 1 - size), which are the units with the lowest retail price. 3) EIA Lifetime from electric cooktops was used as the technology includes induction heating elements. | 3184.4 | 3248.088 | 3248.088
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 600 | 693.9655 | 1120.1587 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 73482.7586 | 1.0925 | 1.1947 | 0 | 0 | 80282.6722 | 87787.5993 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 73482.7586 | 80282.6722 | 87787.5993
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 600 | 693.9655 | 1120.1587 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 73482.7586 | 1.0925 | 1.1947 | 0 | 0 | 80282.6722 | 87787.5993 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 73482.7586 | 80282.6722 | 87787.5993
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 600 | 693.9655 | 1120.1587 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 73482.7586 | 1.0925 | 1.1947 | 0 | 0 | 80282.6722 | 87787.5993 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 73482.7586 | 80282.6722 | 87787.5993
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 600 | 693.9655 | 1120.1587 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 73482.7586 | 1.0925 | 1.1947 | 0 | 0 | 80282.6722 | 87787.5993 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 73482.7586 | 80282.6722 | 87787.5993
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 600 | 693.9655 | 1120.1587 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 73482.7586 | 1.0925 | 1.1947 | 0 | 0 | 80282.6722 | 87787.5993 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 73482.7586 | 80282.6722 | 87787.5993
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 600 | 693.9655 | 1120.1587 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 73482.7586 | 1.0925 | 1.1947 | 0 | 0 | 80282.6722 | 87787.5993 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 73482.7586 | 80282.6722 | 87787.5993
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 600 | 693.9655 | 1120.1587 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 73482.7586 | 1.0925 | 1.1947 | 0 | 0 | 80282.6722 | 87787.5993 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 73482.7586 | 80282.6722 | 87787.5993
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 622.6415 | 720.1529 | 1162.4289 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.0755e-06 | 11441.9323 | 5082.4349 | 76255.6929 | 1.0925 | 1.1947 | 0 | 0 | 83312.207 | 91100.3389 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 76255.6929 | 83312.207 | 91100.3389
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 628.3019 | 726.6997 | 1172.9964 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.0943e-06 | 11545.9499 | 5128.6388 | 76948.9265 | 1.0925 | 1.1947 | 0 | 0 | 84069.5907 | 91928.5238 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 76948.9265 | 84069.5907 | 91928.5238
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 633.9623 | 733.2466 | 1183.5639 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.1132e-06 | 11649.9675 | 5174.8428 | 77642.16 | 1.0925 | 1.1947 | 0 | 0 | 84826.9744 | 92756.7087 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 77642.16 | 84826.9744 | 92756.7087
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 643.3962 | 744.158 | 1201.1765 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.1447e-06 | 11823.3301 | 5251.8494 | 78797.5493 | 1.0925 | 1.1947 | 0 | 0 | 86089.2806 | 94137.0169 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 78797.5493 | 86089.2806 | 94137.0169
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 652.8302 | 755.0694 | 1218.7891 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.1761e-06 | 11996.6927 | 5328.8559 | 79952.9386 | 1.0925 | 1.1947 | 0 | 0 | 87351.5868 | 95517.3251 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 79952.9386 | 87351.5868 | 95517.3251
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 600 | 693.9655 | 1120.1587 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2e-06 | 11025.8621 | 4897.619 | 73482.7586 | 1.0925 | 1.1947 | 0 | 0 | 80282.6722 | 87787.5993 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 73482.7586 | 80282.6722 | 87787.5993
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 645.283 | 746.3403 | 1204.699 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.1509e-06 | 11858.0026 | 5267.2507 | 79028.6272 | 1.0925 | 1.1947 | 0 | 0 | 86341.7418 | 94413.0785 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 79028.6272 | 86341.7418 | 94413.0785
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 656.6038 | 759.434 | 1225.8341 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.1887e-06 | 12066.0377 | 5359.6586 | 80415.0943 | 1.0925 | 1.1947 | 0 | 0 | 87856.5092 | 96069.4483 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 80415.0943 | 87856.5092 | 96069.4483
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 667.9245 | 772.5277 | 1246.9692 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.2264e-06 | 12274.0729 | 5452.0665 | 81801.5615 | 1.0925 | 1.1947 | 0 | 0 | 89371.2766 | 97725.8181 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 81801.5615 | 89371.2766 | 97725.8181
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 686.7925 | 794.3505 | 1282.1943 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.2893e-06 | 12620.7981 | 5606.0797 | 84112.34 | 1.0925 | 1.1947 | 0 | 0 | 91895.889 | 100486.4345 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 84112.34 | 91895.889 | 100486.4345
35 | 2023 | Cooling | Electricity | Commercial |  | Commercial Scroll Chillers (Air-Cooled) | Scroll Chiller | Air-Cooled | Scroll Chiller Air-Cooled | 2023$ | 705.6604 | 816.1733 | 1317.4194 | Capacity | Tons | 10 | 90 | 140 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | -2.3522e-06 | 12967.5233 | 5760.0928 | 86423.1186 | 1.0925 | 1.1947 | 0 | 0 | 94420.5013 | 103247.0508 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 40 | 0.6936 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 86423.1186 | 94420.5013 | 103247.0508
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 610 | 650 | 504.6875 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 169500 | 1.0832 | 1.1136 | 0 | 0 | 183609.5533 | 188758.4084 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 169500 | 183609.5533 | 188758.4084
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 610 | 650 | 504.6875 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 169500 | 1.0832 | 1.1136 | 0 | 0 | 183609.5533 | 188758.4084 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 169500 | 183609.5533 | 188758.4084
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 610 | 650 | 504.6875 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 169500 | 1.0832 | 1.1136 | 0 | 0 | 183609.5533 | 188758.4084 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 169500 | 183609.5533 | 188758.4084
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 610 | 650 | 504.6875 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 169500 | 1.0832 | 1.1136 | 0 | 0 | 183609.5533 | 188758.4084 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 169500 | 183609.5533 | 188758.4084
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 610 | 650 | 504.6875 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 169500 | 1.0832 | 1.1136 | 0 | 0 | 183609.5533 | 188758.4084 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 169500 | 183609.5533 | 188758.4084
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 610 | 650 | 504.6875 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 169500 | 1.0832 | 1.1136 | 0 | 0 | 183609.5533 | 188758.4084 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 169500 | 183609.5533 | 188758.4084
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 610 | 650 | 504.6875 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 169500 | 1.0832 | 1.1136 | 0 | 0 | 183609.5533 | 188758.4084 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 169500 | 183609.5533 | 188758.4084
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 633.0189 | 674.5283 | 523.7323 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1816.0377 | 40990.566 | 162421.875 | 175896.2264 | 1.0832 | 1.1136 | 0 | 0 | 190538.2157 | 195881.3672 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 175896.2264 | 190538.2157 | 195881.3672
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 638.7736 | 680.6604 | 528.4935 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1832.5472 | 41363.2075 | 163898.4375 | 177495.283 | 1.0832 | 1.1136 | 0 | 0 | 192270.3812 | 197662.1069 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 177495.283 | 192270.3812 | 197662.1069
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 644.5283 | 686.7925 | 533.2547 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1849.0566 | 41735.8491 | 165375 | 179094.3396 | 1.0832 | 1.1136 | 0 | 0 | 194002.5468 | 199442.8466 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 179094.3396 | 194002.5468 | 199442.8466
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 654.1195 | 697.0126 | 541.1901 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1876.5723 | 42356.9182 | 167835.9375 | 181759.434 | 1.0832 | 1.1136 | 0 | 0 | 196889.4895 | 202410.7461 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 181759.434 | 196889.4895 | 202410.7461
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 663.7107 | 707.2327 | 549.1254 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1904.088 | 42977.9874 | 170296.875 | 184424.5283 | 1.0832 | 1.1136 | 0 | 0 | 199776.4322 | 205378.6456 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 184424.5283 | 199776.4322 | 205378.6456
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 610 | 650 | 504.6875 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1750 | 39500 | 156515.625 | 169500 | 1.0832 | 1.1136 | 0 | 0 | 183609.5533 | 188758.4084 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 169500 | 183609.5533 | 188758.4084
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 656.0377 | 699.0566 | 542.7771 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1882.0755 | 42481.1321 | 168328.125 | 182292.4528 | 1.0832 | 1.1136 | 0 | 0 | 197466.878 | 203004.326 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 182292.4528 | 197466.878 | 203004.326
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 667.5472 | 711.3208 | 552.2995 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1915.0943 | 43226.4151 | 171281.25 | 185490.566 | 1.0832 | 1.1136 | 0 | 0 | 200931.2092 | 206565.8054 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 185490.566 | 200931.2092 | 206565.8054
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 679.0566 | 723.5849 | 561.8219 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 1948.1132 | 43971.6981 | 174234.375 | 188688.6792 | 1.0832 | 1.1136 | 0 | 0 | 204395.5404 | 210127.2848 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 188688.6792 | 204395.5404 | 210127.2848
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 698.239 | 744.0252 | 577.6926 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 2003.1447 | 45213.8365 | 179156.25 | 194018.8679 | 1.0832 | 1.1136 | 0 | 0 | 210169.4257 | 216063.0839 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 194018.8679 | 210169.4257 | 216063.0839
36 | 2023 | Cooling | Electricity | Commercial |  | Commercial Screw Chillers (Air-Cooled) | Screw Chiller | Air-Cooled | Screw Chiller Air-Cooled | 2023$ | 717.4214 | 764.4654 | 593.5633 | Capacity | Tons | 10 | 200 | 440 | 440 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.88 | 0.77 | 0.7 | 0.6 | 2058.1761 | 46455.9748 | 184078.125 | 199349.0566 | 1.0832 | 1.1136 | 0 | 0 | 215943.3111 | 221998.8829 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 30 | 0.4208 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 199349.0566 | 215943.3111 | 221998.8829
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 500 | 471.3462 | 600 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 29935.5769 | 1.2112 | 1.3216 | 0 | 0 | 36258.7279 | 39561.8512 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 29935.5769 | 36258.7279 | 39561.8512
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 500 | 471.3462 | 600 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 29935.5769 | 1.2112 | 1.3216 | 0 | 0 | 36258.7279 | 39561.8512 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 29935.5769 | 36258.7279 | 39561.8512
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 500 | 471.3462 | 600 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 29935.5769 | 1.2112 | 1.3216 | 0 | 0 | 36258.7279 | 39561.8512 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 29935.5769 | 36258.7279 | 39561.8512
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 500 | 471.3462 | 600 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 29935.5769 | 1.2112 | 1.3216 | 0 | 0 | 36258.7279 | 39561.8512 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 29935.5769 | 36258.7279 | 39561.8512
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 500 | 471.3462 | 600 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 29935.5769 | 1.2112 | 1.3216 | 0 | 0 | 36258.7279 | 39561.8512 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 29935.5769 | 36258.7279 | 39561.8512
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 500 | 471.3462 | 600 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 29935.5769 | 1.2112 | 1.3216 | 0 | 0 | 36258.7279 | 39561.8512 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 29935.5769 | 36258.7279 | 39561.8512
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 500 | 471.3462 | 600 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 29935.5769 | 1.2112 | 1.3216 | 0 | 0 | 36258.7279 | 39561.8512 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 29935.5769 | 36258.7279 | 39561.8512
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 518.8679 | 489.1328 | 622.6415 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.7946e-07 | 4162.9173 | 16603.7736 | 31065.2213 | 1.2112 | 1.3216 | 0 | 0 | 37626.9818 | 41054.7512 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 31065.2213 | 37626.9818 | 41054.7512
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 523.5849 | 493.5795 | 628.3019 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.8745e-07 | 4200.762 | 16754.717 | 31347.6324 | 1.2112 | 1.3216 | 0 | 0 | 37969.0452 | 41427.9762 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 31347.6324 | 37969.0452 | 41427.9762
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 528.3019 | 498.0261 | 633.9623 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.9545e-07 | 4238.6067 | 16905.6604 | 31630.0436 | 1.2112 | 1.3216 | 0 | 0 | 38311.1087 | 41801.2013 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 31630.0436 | 38311.1087 | 41801.2013
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 536.1635 | 505.4372 | 643.3962 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 9.0877e-07 | 4301.6812 | 17157.2327 | 32100.7287 | 1.2112 | 1.3216 | 0 | 0 | 38881.2145 | 42423.2429 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 32100.7287 | 38881.2145 | 42423.2429
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 544.0252 | 512.8483 | 652.8302 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 9.221e-07 | 4364.7557 | 17408.805 | 32571.4139 | 1.2112 | 1.3216 | 0 | 0 | 39451.3203 | 43045.2846 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 32571.4139 | 39451.3203 | 43045.2846
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 500 | 471.3462 | 600 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 8.4748e-07 | 4011.5385 | 16000 | 29935.5769 | 1.2112 | 1.3216 | 0 | 0 | 36258.7279 | 39561.8512 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 29935.5769 | 36258.7279 | 39561.8512
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 537.7358 | 506.9194 | 645.283 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 9.1144e-07 | 4314.2961 | 17207.5472 | 32194.8658 | 1.2112 | 1.3216 | 0 | 0 | 38995.2356 | 42547.6513 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 32194.8658 | 38995.2356 | 42547.6513
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 547.1698 | 515.8128 | 656.6038 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 9.2743e-07 | 4389.9855 | 17509.434 | 32759.688 | 1.2112 | 1.3216 | 0 | 0 | 39679.3626 | 43294.1013 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 32759.688 | 39679.3626 | 43294.1013
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 556.6038 | 524.7061 | 667.9245 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 9.4342e-07 | 4465.6749 | 17811.3208 | 33324.5102 | 1.2112 | 1.3216 | 0 | 0 | 40363.4895 | 44040.5513 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 33324.5102 | 40363.4895 | 44040.5513
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 572.327 | 539.5283 | 686.7925 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 9.7007e-07 | 4591.8239 | 18314.4654 | 34265.8805 | 1.2112 | 1.3216 | 0 | 0 | 41503.7011 | 45284.6347 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 34265.8805 | 41503.7011 | 45284.6347
37 | 2023 | Cooling | Electricity | Commercial |  |  | Scroll Chiller | Water-Cooled | Scroll Chiller Water-Cooled | 2023$ | 588.0503 | 554.3505 | 705.6604 | Capacity | Tons | 2 | 55 | 145 | 145 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 15 | 15 | 20 | 20 | 9.9672e-07 | 4717.9729 | 18817.6101 | 35207.2509 | 1.2112 | 1.3216 | 0 | 0 | 42643.9127 | 46528.7181 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 32 | 0.6621 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 35207.2509 | 42643.9127 | 46528.7181
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 336.5385 | 410 | 456 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 111500 | 1.1732 | 1.2285 | 0 | 0 | 130817.0206 | 136974.9216 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 111500 | 130817.0206 | 136974.9216
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 336.5385 | 410 | 456 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 111500 | 1.1732 | 1.2285 | 0 | 0 | 130817.0206 | 136974.9216 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 111500 | 130817.0206 | 136974.9216
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 336.5385 | 410 | 456 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 111500 | 1.1732 | 1.2285 | 0 | 0 | 130817.0206 | 136974.9216 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 111500 | 130817.0206 | 136974.9216
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 336.5385 | 410 | 456 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 111500 | 1.1732 | 1.2285 | 0 | 0 | 130817.0206 | 136974.9216 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 111500 | 130817.0206 | 136974.9216
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 336.5385 | 410 | 456 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 111500 | 1.1732 | 1.2285 | 0 | 0 | 130817.0206 | 136974.9216 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 111500 | 130817.0206 | 136974.9216
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 336.5385 | 410 | 456 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 111500 | 1.1732 | 1.2285 | 0 | 0 | 130817.0206 | 136974.9216 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 111500 | 130817.0206 | 136974.9216
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 336.5385 | 410 | 456 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 111500 | 1.1732 | 1.2285 | 0 | 0 | 130817.0206 | 136974.9216 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 111500 | 130817.0206 | 136974.9216
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 349.238 | 425.4717 | 473.2075 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 34315.1306 | 30613.2075 | 31547.1698 | 115707.5472 | 1.1732 | 1.2285 | 0 | 0 | 135753.512 | 142143.7865 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 115707.5472 | 135753.512 | 142143.7865
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 352.4129 | 429.3396 | 477.5094 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 34627.0864 | 30891.5094 | 31833.9623 | 116759.434 | 1.1732 | 1.2285 | 0 | 0 | 136987.6348 | 143436.0028 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 116759.434 | 136987.6348 | 143436.0028
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 355.5878 | 433.2075 | 481.8113 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 34939.0421 | 31169.8113 | 32120.7547 | 117811.3207 | 1.1732 | 1.2285 | 0 | 0 | 138221.7576 | 144728.219 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 117811.3207 | 138221.7576 | 144728.219
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 360.8793 | 439.6541 | 488.9811 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 35458.9683 | 31633.6478 | 32598.7421 | 119564.4654 | 1.1732 | 1.2285 | 0 | 0 | 140278.629 | 146881.9128 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 119564.4654 | 140278.629 | 146881.9128
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 366.1708 | 446.1006 | 496.1509 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 35978.8945 | 32097.4843 | 33076.7296 | 121317.6101 | 1.1732 | 1.2285 | 0 | 0 | 142335.5004 | 149035.6065 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 121317.6101 | 142335.5004 | 149035.6065
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 336.5385 | 410 | 456 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 33067.3077 | 29500 | 30400 | 111500 | 1.1732 | 1.2285 | 0 | 0 | 130817.0206 | 136974.9216 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 111500 | 130817.0206 | 136974.9216
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 361.9376 | 440.9434 | 490.4151 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 35562.9536 | 31726.4151 | 32694.3396 | 119915.0943 | 1.1732 | 1.2285 | 0 | 0 | 140690.0033 | 147312.6515 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 119915.0943 | 140690.0033 | 147312.6515
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 368.2874 | 448.6792 | 499.0189 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 36186.865 | 32283.0189 | 33267.9245 | 122018.8679 | 1.1732 | 1.2285 | 0 | 0 | 143158.249 | 149897.084 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 122018.8679 | 143158.249 | 149897.084
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 374.6372 | 456.4151 | 507.6226 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 36810.7765 | 32839.6226 | 33841.5094 | 124122.6415 | 1.1732 | 1.2285 | 0 | 0 | 145626.4946 | 152481.5165 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 124122.6415 | 145626.4946 | 152481.5165
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 385.2201 | 469.3082 | 521.9623 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 37850.6289 | 33767.2956 | 34797.4843 | 127628.9308 | 1.1732 | 1.2285 | 0 | 0 | 149740.2374 | 156788.9039 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 127628.9308 | 149740.2374 | 156788.9039
38 | 2023 | Cooling | Electricity | Commercial |  |  | Screw Chiller | Water-Cooled | Screw Chiller Water-Cooled | 2023$ | 395.8031 | 482.2013 | 536.3019 | Capacity | Tons | 80 | 200 | 350 | 350 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 16 | 16 | 25 | 25 | 38890.4814 | 34694.9685 | 35753.4591 | 131135.2201 | 1.1732 | 1.2285 | 0 | 0 | 153853.9802 | 161096.2914 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 18 | 0.7399 | 2023 | There is no available efficiency data. The regression assumes an increase in efficiency as well as price over the coming decades for the advanced case. | 131135.2201 | 153853.9802 | 161096.2914
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
39 | 2023 | Cooling | Electricity | Commercial |  | Commercial Reciprocating Chillers (Air-Cooled Only) | Reciprocating Chiller | Air-Cooled | Reciprocating Chiller Air-Cooled | 2023$ | 432.5 | 659.1837 | 667.1642 | Capacity | Tons | 15 | 95 | 390 | 390 | 0 | 0 | 0 | Efficiency (IPLV) | kW/ton | 0.86 | 0.86 | 0.79 | 0.79 | 12437.5 | 7418.3673 | 14820.8955 | 70040.8163 | 1.1377 | 1.1842 | 0 | 0 | 79682.4452 | 82944.7719 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 35 | 0.7642 | 2023 | There is no available efficiency data. | 70040.8163 | 79682.4452 | 82944.7719
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2023 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2030 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2035 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2040 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2045 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2050 | Reference | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2023 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22306 | 22306 | 21190.5 | 21190.5 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2030 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22034.25 | 22034.25 | 20932.5 | 20932.5 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2035 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21762.5 | 21762.5 | 20674.5 | 20674.5 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2040 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21504.5 | 21504.5 | 20429.25 | 20429.25 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2045 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21246.5 | 21246.5 | 20184 | 20184 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2050 | Intermediate | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 22878 | 22878 | 21734 | 21734 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2023 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21734 | 21734 | 20647 | 20647 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2030 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21190.5 | 21190.5 | 20131 | 20131 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2035 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20647 | 20647 | 19615 | 19615 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2040 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20131 | 20131 | 19124.5 | 19124.5 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2045 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
40 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Variable Air Volume System | Variable Air Volume System | Standard | Variable Air Volume System - Standard | 2023/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 19615 | 19615 | 18634 | 18634 | 6544.8 | 8181 | 9817.2 | 133350.3 | 1.02 | 1.13 | 0 | 0 | 133350.3 | 133350.3 | 2050 | Advanced | 28 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead.Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 133350.3 | 133350.3 | 133350.3
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2023 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2030 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2035 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2040 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2045 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2050 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2023 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21339 | 21339 | 20272 | 20272 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2030 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21079 | 21079 | 20025.25 | 20025.25 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2035 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20819 | 20819 | 19778.5 | 19778.5 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2040 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20572.25 | 20572.25 | 19543.75 | 19543.75 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2045 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20325.5 | 20325.5 | 19309 | 19309 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2050 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 21886 | 21886 | 20792 | 20792 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2023 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20792 | 20792 | 19752 | 19752 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2030 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 20272 | 20272 | 19258.5 | 19258.5 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2035 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 19752 | 19752 | 18765 | 18765 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2040 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 19258.5 | 19258.5 | 18295.5 | 18295.5 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2045 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
41 | 2023 | Ventilation | Electricity | Commercial |  | Commercial Constant Air Volume System | Constant Air Volume System | Standard | Constant Air Volume System - Standard | 2023$/thousand CFM | 0 | 0 | 0 | Airflow | CFM | 16300 | 16300 | 16300 | 16300 | 0 | 0 | 0 | Energy | kWh/y | 18765 | 18765 | 17826 | 17826 | 4649.736 | 5812.17 | 6974.604 | 94738.371 | 1.02 | 1.14 | 0 | 0 | 96633.1384 | 108001.7429 | 2050 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 2 | N/A | 2023 | This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. Equipment cost did not exist on the EIA report so total installed cost was instead. Projected prices for the reference and advanced case were the same since coefficients were set to 0. Though we can expect a difference between the reference and advanced case prices, the price difference is small and therefore negligable. | 94738.371 | 96633.1384 | 108001.7429
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3942 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3766.75 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3591.5 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3451.5 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3311.5 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 4380 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3504 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 3153.5 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2035 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 2803 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2040 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 2523 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2045 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
42 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Large | Hot Food Holding Cabinet - Large | Large | Hot Food Holding Cabinet - Large | 2023$ | 34.0318 | 42.5398 | 51.0478 | Volume | ft3 | 44 | 44 | 44 | 101.04 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 4380 | 2243 | 1018 | 1018 | 3750.4231 | 4688.0289 | 5625.6347 | 6559.7804 | 1.02 | 1.03 | 0 | 0 | 6690.976 | 6756.5738 | 2050 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.5827 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 3) Metric - "Volume" refers to the Interior Volume. | 6559.7804 | 6690.976 | 6756.5738
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1785.75 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1706.375 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1627 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1579.875 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1532.75 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1984 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1587.5 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1428.75 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2035 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1270 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2040 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1175.75 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2045 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
43 | 2023 | Cooking | Electricity | Commercial |  | Hot Food Holding Cabinet - Small and Medium | Hot Food Holding Cabinet | Small and Medium | Hot Food Holding Cabinet - Small and Medium | 2023$ | 49.408 | 61.76 | 74.112 | Volume | ft3 | 6.68 | 15.1 | 22.4 | 31.41 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 1984 | 1081.5 | 979 | 979 | 1567.2183 | 1959.0229 | 2350.8275 | 2891.5989 | 1.05 | 1.07 | 0 | 0 | 3036.1788 | 3094.0108 | 2050 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Site assessment, Ceiling height, Coil upgrades | 2 | 11 | 0.4141 | 2024 | 1) Since the EIA Typical Capacity value was of a lower value than the data points collected, it was used as the lower bound for metric 1. 2) Due to the lack of cost infromation available for small cabinets, this data set combined small and medium cabinets. 3) Improvements in efficiency for the advanced case were not captured in retail price due to no coefficients for the efficiency metric. 4) Metric - "Volume" refers to the Interior Volume. | 2891.5989 | 3036.1788 | 3094.0108
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2023 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2030 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2035 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2040 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2045 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2050 | Reference | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2023 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1170.5 | 1102 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2030 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1142.75 | 1075.75 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2035 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1115 | 1049.5 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2040 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1090 | 1026 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2045 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1065 | 1002.5 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2050 | Intermediate | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1232 | 1160 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2023 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1109 | 1044 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2030 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 1053.5 | 991.5 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2035 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 998 | 939 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2040 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 948 | 892 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2045 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
44 | 2023 | Refrigerartion | Electricity | Commercial |  | Compressor Rack Systems | Compressor Rack Systems | Standard | Compressor Rack Systems Standard | 2023$ | 0 | 0 | 0 | Capacity | kBTU/h | 1190 | 1190 | 930 | 930 | 0 | 0 | 0 | Annual Energy Use (kWh/y) | kWh/y | 1305 | 898 | 845 | 1160 | 533618.08 | 667022.6 | 800427.12 | 667022.6 | 1.05 | 1.07 | 0 | 0 | 700373.73 | 713714.182 | 2050 | Advanced | 35 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. 4) EIA Typical and High values were used as the lower and upperbounds for both metrics, respectively. | 667022.6 | 700373.73 | 713714.182
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 100.5 | 100.5 | 81.5 | 81.5 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 98.25 | 98.25 | 79.75 | 79.75 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 96 | 96 | 78 | 78 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 93.75 | 93.75 | 76.25 | 76.25 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 91.5 | 91.5 | 74.5 | 74.5 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 106 | 106 | 86 | 86 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 95 | 95 | 77 | 77 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 90.5 | 90.5 | 73.5 | 73.5 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 86 | 86 | 70 | 70 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 81.5 | 81.5 | 66.5 | 66.5 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
45 | 2023 | Refrigerartion | Electricity | Commercial |  | Condensers | Condensers | Standard | Condensers Standard | 2023$ | 33.0684 | 41.3355 | 49.6026 | Capacity | Tons | 1440 | 1440 | 1440 | 1440 | 0 | 0 | 0 | Annual Energy User | MMWh/y | 77 | 77 | 63 | 63 | 2922.08 | 5130.59 | 7339.1 | 64653.769 | 1.1 | 1.16 | 0 | 0 | 71119.1459 | 74998.3721 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Need to bring in combustion air, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 1 | 2 | N/A | 2024 | 1) This technology has a high variety of models that provide a large variation in retail price between the models. As a result, a regression was not created and point values were used using EIA data. 2) Equipment cost did not exist on the EIA report so total installed cost was instead. 3) Projected prices for the reference and advanced case were the same since coefficients were set to 0. | 64653.769 | 71119.1459 | 74998.3721
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.004214 | 0.009752 | 0.012619 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.6286 | 0.18645 | -3.4594 | Efficacy | lm/W | 43.75 | 134.3013 | 145.3846 | 180.5237 | -167.033 | 73.3194 | 712.6457 | 278.7716 | 1 | 1 | 99 | 99 | 377.7716 | 377.7716 | 2023 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 278.7716 | 377.7716 | 377.7716
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0037323 | 0.0086374 | 0.011177 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.2091 | 0.13842 | -2.5683 | Efficacy | lm/W | 43.75 | 160.2241 | 173.4467 | 180.5237 | -147.9413 | 64.9391 | 631.1911 | 246.9083 | 1 | 1 | 99 | 99 | 345.9083 | 345.9083 | 2030 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 246.9083 | 345.9083 | 345.9083
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0036377 | 0.0084183 | 0.010893 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.0906 | 0.12486 | -2.3166 | Efficacy | lm/W | 43.75 | 173.1263 | 187.4137 | 180.5237 | -144.1898 | 63.2923 | 615.1853 | 240.6472 | 1 | 1 | 99 | 99 | 339.6472 | 339.6472 | 2035 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 240.6472 | 339.6472 | 339.6472
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0035431 | 0.0081993 | 0.01061 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.98853 | 0.11317 | -2.0998 | Efficacy | lm/W | 43.75 | 186.0285 | 201.3807 | 180.5237 | -140.4383 | 61.6456 | 599.1796 | 234.3861 | 1 | 1 | 99 | 99 | 333.3861 | 333.3861 | 2040 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 234.3861 | 333.3861 | 333.3861
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0034525 | 0.0079897 | 0.010339 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.90104 | 0.10316 | -1.914 | Efficacy | lm/W | 43.75 | 198.8737 | 215.286 | 180.5237 | -136.8476 | 60.0694 | 583.8597 | 228.3933 | 1 | 1 | 99 | 99 | 327.3933 | 327.3933 | 2045 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 228.3933 | 327.3933 | 327.3933
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0033619 | 0.00778 | 0.010067 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.82416 | 0.094355 | -1.7507 | Efficacy | lm/W | 43.75 | 211.719 | 229.1913 | 180.5237 | -133.2568 | 58.4933 | 568.5398 | 222.4005 | 1 | 1 | 99 | 99 | 321.4005 | 321.4005 | 2050 | Reference | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 222.4005 | 321.4005 | 321.4005
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.004214 | 0.009752 | 0.012619 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.6286 | 0.18645 | -3.4594 | Efficacy | lm/W | 43.75 | 134.3013 | 145.3846 | 180.5237 | -167.033 | 73.3194 | 712.6457 | 278.7716 | 1 | 1 | 99 | 99 | 377.7716 | 377.7716 | 2023 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 278.7716 | 377.7716 | 377.7716
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0037323 | 0.0086374 | 0.011177 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.0514 | 0.12036 | -2.2333 | Efficacy | lm/W | 43.75 | 184.2577 | 199.4638 | 180.5237 | -147.9413 | 64.9391 | 631.1911 | 246.9083 | 1 | 1 | 99 | 99 | 345.9083 | 345.9083 | 2030 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 246.9083 | 345.9083 | 345.9083
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0036377 | 0.0084183 | 0.010893 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.94833 | 0.10857 | -2.0144 | Efficacy | lm/W | 43.75 | 199.0952 | 212.577 | 180.5237 | -144.1898 | 63.2923 | 615.1853 | 240.6472 | 1 | 1 | 99 | 99 | 339.6472 | 339.6472 | 2035 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 240.6472 | 339.6472 | 339.6472
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0035431 | 0.0081993 | 0.01061 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.85959 | 0.098411 | -1.8259 | Efficacy | lm/W | 43.75 | 213.9328 | 225.6903 | 180.5237 | -140.4383 | 61.6456 | 599.1796 | 234.3861 | 1 | 1 | 99 | 99 | 333.3861 | 333.3861 | 2040 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 234.3861 | 333.3861 | 333.3861
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0034525 | 0.0079897 | 0.010339 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.80574 | 0.092246 | -1.7115 | Efficacy | lm/W | 43.75 | 222.3961 | 232.643 | 180.5237 | -136.8476 | 60.0694 | 583.8597 | 228.3933 | 1 | 1 | 99 | 99 | 327.3933 | 327.3933 | 2045 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 228.3933 | 327.3933 | 327.3933
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0033619 | 0.00778 | 0.010067 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.75583 | 0.086532 | -1.6055 | Efficacy | lm/W | 43.75 | 230.8595 | 239.5957 | 180.5237 | -133.2568 | 58.4933 | 568.5398 | 222.4005 | 1 | 1 | 99 | 99 | 321.4005 | 321.4005 | 2050 | Intermediate | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 222.4005 | 321.4005 | 321.4005
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.004214 | 0.009752 | 0.012619 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 1.6286 | 0.18645 | -3.4594 | Efficacy | lm/W | 43.75 | 134.3013 | 145.3846 | 180.5237 | -167.033 | 73.3194 | 712.6457 | 278.7716 | 1 | 1 | 99 | 99 | 377.7716 | 377.7716 | 2023 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 278.7716 | 377.7716 | 377.7716
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0037323 | 0.0086374 | 0.011177 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.93004 | 0.10648 | -1.9756 | Efficacy | lm/W | 43.75 | 208.2913 | 225.4808 | 180.5237 | -147.9413 | 64.9391 | 631.1911 | 246.9083 | 1 | 1 | 99 | 99 | 345.9083 | 345.9083 | 2030 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 246.9083 | 345.9083 | 345.9083
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0036377 | 0.0084183 | 0.010893 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.8389 | 0.096043 | -1.782 | Efficacy | lm/W | 43.75 | 225.0642 | 237.7404 | 180.5237 | -144.1898 | 63.2923 | 615.1853 | 240.6472 | 1 | 1 | 99 | 99 | 339.6472 | 339.6472 | 2035 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 240.6472 | 339.6472 | 339.6472
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0035431 | 0.0081993 | 0.01061 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.76041 | 0.087056 | -1.6153 | Efficacy | lm/W | 43.75 | 241.837 | 250 | 180.5237 | -140.4383 | 61.6456 | 599.1796 | 234.3861 | 1 | 1 | 99 | 99 | 333.3861 | 333.3861 | 2040 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 234.3861 | 333.3861 | 333.3861
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0034525 | 0.0079897 | 0.010339 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.72867 | 0.083422 | -1.5478 | Efficacy | lm/W | 43.75 | 245.9185 | 250 | 180.5237 | -136.8476 | 60.0694 | 583.8597 | 228.3933 | 1 | 1 | 99 | 99 | 327.3933 | 327.3933 | 2045 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 228.3933 | 327.3933 | 327.3933
46 | 2023 | Lighting | Electricity | Commercial |  | LED High-Bay Integrated Luminaire | LED | High/Low-Bays | LED High/Low-Bay | 2023$ | 0.0033619 | 0.00778 | 0.010067 | Light Output | Lumens | 1750 | 18500 | 18900 | 56660 | 0.69797 | 0.079907 | -1.4826 | Efficacy | lm/W | 43.75 | 250 | 250 | 180.5237 | -133.2568 | 58.4933 | 568.5398 | 222.4005 | 1 | 1 | 99 | 99 | 321.4005 | 321.4005 | 2050 | Advanced | 11.4155 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 16 | 704 | 0.1453 | 2020 | Due to the pace of innovation in the lighting industry, it is unlikely that the "2023 Typical Retail" product will exist on the market in future years. Thus, we have instead used the Typical values for future years to create the Tableau graphs. | 222.4005 | 321.4005 | 321.4005
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | N/A | 200 | 0 | 297.4496 | 0 | 297.4496 | 1 | 1 | 45 | 45 | 342.4496 | 342.4496 | 2023 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 297.4496 | 342.4496 | 342.4496
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | N/A | 200 | 0 | 297.4496 | 0 | 297.4496 | 1 | 1 | 45 | 45 | 342.4496 | 342.4496 | 2030 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 297.4496 | 342.4496 | 342.4496
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | N/A | 200 | 0 | 297.4496 | 0 | 297.4496 | 1 | 1 | 45 | 45 | 342.4496 | 342.4496 | 2035 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 297.4496 | 342.4496 | 342.4496
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | N/A | 200 | 0 | 297.4496 | 0 | 297.4496 | 1 | 1 | 45 | 45 | 342.4496 | 342.4496 | 2040 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 297.4496 | 342.4496 | 342.4496
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | N/A | 200 | 0 | 297.4496 | 0 | 297.4496 | 1 | 1 | 45 | 45 | 342.4496 | 342.4496 | 2045 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 297.4496 | 342.4496 | 342.4496
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | N/A | 200 | 0 | 297.4496 | 0 | 297.4496 | 1 | 1 | 45 | 45 | 342.4496 | 342.4496 | 2050 | Reference | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 297.4496 | 342.4496 | 342.4496
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | N/A | 200 | 0 | 297.4496 | 0 | 297.4496 | 1 | 1 | 45 | 45 | 342.4496 | 342.4496 | 2023 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 297.4496 | 342.4496 | 342.4496
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 140.5 | N/A | 200 | 0 | 255.3109 | 0 | 255.3109 | 1 | 1 | 45 | 45 | 300.3109 | 300.3109 | 2030 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 255.3109 | 300.3109 | 300.3109
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 145.5 | N/A | 200 | 0 | 252.8322 | 0 | 252.8322 | 1 | 1 | 45 | 45 | 297.8322 | 297.8322 | 2035 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 252.8322 | 297.8322 | 297.8322
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 150.5 | N/A | 200 | 0 | 250.3534 | 0 | 250.3534 | 1 | 1 | 45 | 45 | 295.3534 | 295.3534 | 2040 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 250.3534 | 295.3534 | 295.3534
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 158 | N/A | 200 | 0 | 247.8747 | 0 | 247.8747 | 1 | 1 | 45 | 45 | 292.8747 | 292.8747 | 2045 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 247.8747 | 292.8747 | 292.8747
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 165.5 | N/A | 200 | 0 | 245.3959 | 0 | 245.3959 | 1 | 1 | 45 | 45 | 290.3959 | 290.3959 | 2050 | Intermediate | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 245.3959 | 290.3959 | 290.3959
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 131 | N/A | 200 | 0 | 297.4496 | 0 | 297.4496 | 1 | 1 | 45 | 45 | 342.4496 | 342.4496 | 2023 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 297.4496 | 342.4496 | 342.4496
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 150 | N/A | 200 | 0 | 213.1722 | 0 | 213.1722 | 1 | 1 | 45 | 45 | 258.1722 | 258.1722 | 2030 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 213.1722 | 258.1722 | 258.1722
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 160 | N/A | 200 | 0 | 208.2147 | 0 | 208.2147 | 1 | 1 | 45 | 45 | 253.2147 | 253.2147 | 2035 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 208.2147 | 253.2147 | 253.2147
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 170 | N/A | 200 | 0 | 203.2572 | 0 | 203.2572 | 1 | 1 | 45 | 45 | 248.2572 | 248.2572 | 2040 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 203.2572 | 248.2572 | 248.2572
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 185 | N/A | 200 | 0 | 198.2997 | 0 | 198.2997 | 1 | 1 | 45 | 45 | 243.2997 | 243.2997 | 2045 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 198.2997 | 243.2997 | 243.2997
47 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel Connected with Integrated Controls | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 131 | 200 | N/A | 200 | 0 | 193.3422 | 0 | 193.3422 | 1 | 1 | 45 | 45 | 238.3422 | 238.3422 | 2050 | Advanced | 7.9909 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 15 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 193.3422 | 238.3422 | 238.3422
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | N/A | 125 | 0 | 202.2657 | 0 | 202.2657 | 1 | 1 | 20 | 20 | 222.2657 | 222.2657 | 2023 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 202.2657 | 222.2657 | 222.2657
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | N/A | 125 | 0 | 202.2657 | 0 | 202.2657 | 1 | 1 | 20 | 20 | 222.2657 | 222.2657 | 2030 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 202.2657 | 222.2657 | 222.2657
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | N/A | 125 | 0 | 202.2657 | 0 | 202.2657 | 1 | 1 | 20 | 20 | 222.2657 | 222.2657 | 2035 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 202.2657 | 222.2657 | 222.2657
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | N/A | 125 | 0 | 202.2657 | 0 | 202.2657 | 1 | 1 | 20 | 20 | 222.2657 | 222.2657 | 2040 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 202.2657 | 222.2657 | 222.2657
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | N/A | 125 | 0 | 202.2657 | 0 | 202.2657 | 1 | 1 | 20 | 20 | 222.2657 | 222.2657 | 2045 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 202.2657 | 222.2657 | 222.2657
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | N/A | 125 | 0 | 202.2657 | 0 | 202.2657 | 1 | 1 | 20 | 20 | 222.2657 | 222.2657 | 2050 | Reference | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 202.2657 | 222.2657 | 222.2657
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | N/A | 200 | 0 | 202.2657 | 0 | 202.2657 | 1 | 1 | 20 | 20 | 222.2657 | 222.2657 | 2023 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 202.2657 | 222.2657 | 222.2657
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 137.5 | N/A | 200 | 0 | 172.9904 | 0 | 172.9904 | 1 | 1 | 20 | 20 | 192.9904 | 192.9904 | 2030 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 172.9904 | 192.9904 | 192.9904
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 142.5 | N/A | 200 | 0 | 171.6597 | 0 | 171.6597 | 1 | 1 | 20 | 20 | 191.6597 | 191.6597 | 2035 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 171.6597 | 191.6597 | 191.6597
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 147.5 | N/A | 200 | 0 | 170.329 | 0 | 170.329 | 1 | 1 | 20 | 20 | 190.329 | 190.329 | 2040 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 170.329 | 190.329 | 190.329
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 155 | N/A | 200 | 0 | 168.9983 | 0 | 168.9983 | 1 | 1 | 20 | 20 | 188.9983 | 188.9983 | 2045 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 168.9983 | 188.9983 | 188.9983
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 162.5 | N/A | 200 | 0 | 167.6676 | 0 | 167.6676 | 1 | 1 | 20 | 20 | 187.6676 | 187.6676 | 2050 | Intermediate | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 167.6676 | 187.6676 | 187.6676
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 125 | N/A | 200 | 0 | 202.2657 | 0 | 202.2657 | 1 | 1 | 20 | 20 | 222.2657 | 222.2657 | 2023 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 202.2657 | 222.2657 | 222.2657
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 150 | N/A | 200 | 0 | 143.7151 | 0 | 143.7151 | 1 | 1 | 20 | 20 | 163.7151 | 163.7151 | 2030 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 143.7151 | 163.7151 | 163.7151
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 160 | N/A | 200 | 0 | 141.0537 | 0 | 141.0537 | 1 | 1 | 20 | 20 | 161.0537 | 161.0537 | 2035 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 141.0537 | 161.0537 | 161.0537
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 170 | N/A | 200 | 0 | 138.3923 | 0 | 138.3923 | 1 | 1 | 20 | 20 | 158.3923 | 158.3923 | 2040 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 138.3923 | 158.3923 | 158.3923
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 185 | N/A | 200 | 0 | 135.731 | 0 | 135.731 | 1 | 1 | 20 | 20 | 155.731 | 155.731 | 2045 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 135.731 | 155.731 | 155.731
48 | 2023 | Lighting | Electricity | Commercial |  | 4 ft Linear Systems LED Integrated Luminaire | LED | Troffer & Panel | LED Troffer or Panel with Dimming | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 5000 | 5000 | N/A | 5000 | 0 | 0 | 0 | Efficacy | lm/W | 125 | 200 | N/A | 200 | 0 | 133.0696 | 0 | 133.0696 | 1 | 1 | 20 | 20 | 153.0696 | 153.0696 | 2050 | Advanced | 6.8493 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 4 | 102 | N/A | 2020 | These estimates assume continued R&D effort at manufacturers to improve luminaire luminous efficacy (lm/W) and cost improvements through 2050. | 133.0696 | 153.0696 | 153.0696
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 68.8618 | 70.5769 | 70.5769 | 0 | 31.7516 | 0 | 31.7516 | 1 | 1 | 66 | 3.3 | 97.7516 | 35.0516 | 2023 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 31.7516 | 97.7516 | 35.0516
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 71.6649 | 73.4499 | 70.5769 | 0 | 31.3555 | 0 | 31.3555 | 1 | 1 | 66 | 3.3 | 97.3555 | 34.6555 | 2030 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 31.3555 | 97.3555 | 34.6555
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 73.4974 | 75.328 | 70.5769 | 0 | 31.1189 | 0 | 31.1189 | 1 | 1 | 66 | 3.3 | 97.1189 | 34.4189 | 2035 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 31.1189 | 97.1189 | 34.4189
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 75.3299 | 77.2061 | 70.5769 | 0 | 30.8822 | 0 | 30.8822 | 1 | 1 | 66 | 3.3 | 96.8822 | 34.1822 | 2040 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 30.8822 | 96.8822 | 34.1822
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 77.2561 | 79.1803 | 70.5769 | 0 | 30.6571 | 0 | 30.6571 | 1 | 1 | 66 | 3.3 | 96.6571 | 33.9571 | 2045 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 30.6571 | 96.6571 | 33.9571
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 79.1823 | 81.1545 | 70.5769 | 0 | 30.4321 | 0 | 30.4321 | 1 | 1 | 66 | 3.3 | 96.4321 | 33.7321 | 2050 | Reference | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 30.4321 | 96.4321 | 33.7321
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 68.8618 | 70.5769 | 70.5769 | 0 | 31.7516 | 0 | 31.7516 | 1 | 1 | 66 | 3.3 | 97.7516 | 35.0516 | 2023 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 31.7516 | 97.7516 | 35.0516
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 71.6649 | 73.4499 | 70.5769 | 0 | 31.3555 | 0 | 31.3555 | 1 | 1 | 66 | 3.3 | 97.3555 | 34.6555 | 2030 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 31.3555 | 97.3555 | 34.6555
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 73.4974 | 75.328 | 70.5769 | 0 | 31.1189 | 0 | 31.1189 | 1 | 1 | 66 | 3.3 | 97.1189 | 34.4189 | 2035 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 31.1189 | 97.1189 | 34.4189
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 75.3299 | 77.2061 | 70.5769 | 0 | 30.8822 | 0 | 30.8822 | 1 | 1 | 66 | 3.3 | 96.8822 | 34.1822 | 2040 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 30.8822 | 96.8822 | 34.1822
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 77.2561 | 79.1803 | 70.5769 | 0 | 30.6571 | 0 | 30.6571 | 1 | 1 | 66 | 3.3 | 96.6571 | 33.9571 | 2045 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 30.6571 | 96.6571 | 33.9571
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 79.1823 | 81.1545 | 70.5769 | 0 | 30.4321 | 0 | 30.4321 | 1 | 1 | 66 | 3.3 | 96.4321 | 33.7321 | 2050 | Intermediate | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 30.4321 | 96.4321 | 33.7321
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 68.8618 | 70.5769 | 70.5769 | 0 | 31.7516 | 0 | 31.7516 | 1 | 1 | 66 | 3.3 | 97.7516 | 35.0516 | 2023 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 31.7516 | 97.7516 | 35.0516
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 71.6649 | 73.4499 | 70.5769 | 0 | 31.3555 | 0 | 31.3555 | 1 | 1 | 66 | 3.3 | 97.3555 | 34.6555 | 2030 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 31.3555 | 97.3555 | 34.6555
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 73.4974 | 75.328 | 70.5769 | 0 | 31.1189 | 0 | 31.1189 | 1 | 1 | 66 | 3.3 | 97.1189 | 34.4189 | 2035 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 31.1189 | 97.1189 | 34.4189
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 75.3299 | 77.2061 | 70.5769 | 0 | 30.8822 | 0 | 30.8822 | 1 | 1 | 66 | 3.3 | 96.8822 | 34.1822 | 2040 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 30.8822 | 96.8822 | 34.1822
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 77.2561 | 79.1803 | 70.5769 | 0 | 30.6571 | 0 | 30.6571 | 1 | 1 | 66 | 3.3 | 96.6571 | 33.9571 | 2045 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 30.6571 | 96.6571 | 33.9571
49 | 2023 | Lighting | Electricity | Commercial |  | 100W Equivalent CFL Bare Spiral | CFL | Spiral | 100W Equivalent CFL Bare Spiral | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 1600 | 1694 | 1835 | 1835 | 0 | 0 | 0 | Efficacy | lm/W | 64 | 79.1823 | 81.1545 | 70.5769 | 0 | 30.4321 | 0 | 30.4321 | 1 | 1 | 66 | 3.3 | 96.4321 | 33.7321 | 2050 | Advanced | 1.1416 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 3 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. | 30.4321 | 96.4321 | 33.7321
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 367.1439 | 0 | 367.1439 | 1 | 1 | 132 | 33 | 499.1439 | 400.1439 | 2023 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 367.1439 | 499.1439 | 400.1439
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 356.6256 | 0 | 356.6256 | 1 | 1 | 132 | 33 | 488.6256 | 389.6256 | 2030 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 356.6256 | 488.6256 | 389.6256
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 350.3414 | 0 | 350.3414 | 1 | 1 | 132 | 33 | 482.3414 | 383.3414 | 2035 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 350.3414 | 482.3414 | 383.3414
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 344.0572 | 0 | 344.0572 | 1 | 1 | 132 | 33 | 476.0572 | 377.0572 | 2040 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 344.0572 | 476.0572 | 377.0572
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 338.0803 | 0 | 338.0803 | 1 | 1 | 132 | 33 | 470.0803 | 371.0803 | 2045 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 338.0803 | 470.0803 | 371.0803
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 332.1033 | 0 | 332.1033 | 1 | 1 | 132 | 33 | 464.1033 | 365.1033 | 2050 | Reference | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 332.1033 | 464.1033 | 365.1033
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 367.1439 | 0 | 367.1439 | 1 | 1 | 132 | 33 | 499.1439 | 400.1439 | 2023 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 367.1439 | 499.1439 | 400.1439
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 356.6256 | 0 | 356.6256 | 1 | 1 | 132 | 33 | 488.6256 | 389.6256 | 2030 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 356.6256 | 488.6256 | 389.6256
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 350.3414 | 0 | 350.3414 | 1 | 1 | 132 | 33 | 482.3414 | 383.3414 | 2035 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 350.3414 | 482.3414 | 383.3414
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 344.0572 | 0 | 344.0572 | 1 | 1 | 132 | 33 | 476.0572 | 377.0572 | 2040 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 344.0572 | 476.0572 | 377.0572
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 338.0803 | 0 | 338.0803 | 1 | 1 | 132 | 33 | 470.0803 | 371.0803 | 2045 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 338.0803 | 470.0803 | 371.0803
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 332.1033 | 0 | 332.1033 | 1 | 1 | 132 | 33 | 464.1033 | 365.1033 | 2050 | Intermediate | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 332.1033 | 464.1033 | 365.1033
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 367.1439 | 0 | 367.1439 | 1 | 1 | 132 | 33 | 499.1439 | 400.1439 | 2023 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 367.1439 | 499.1439 | 400.1439
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 356.6256 | 0 | 356.6256 | 1 | 1 | 132 | 33 | 488.6256 | 389.6256 | 2030 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 356.6256 | 488.6256 | 389.6256
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 350.3414 | 0 | 350.3414 | 1 | 1 | 132 | 33 | 482.3414 | 383.3414 | 2035 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 350.3414 | 482.3414 | 383.3414
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 344.0572 | 0 | 344.0572 | 1 | 1 | 132 | 33 | 476.0572 | 377.0572 | 2040 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 344.0572 | 476.0572 | 377.0572
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 338.0803 | 0 | 338.0803 | 1 | 1 | 132 | 33 | 470.0803 | 371.0803 | 2045 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 338.0803 | 470.0803 | 371.0803
50 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Metal Halide | High-Bay | Metal Halide | High-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 36000 | 42000 | N/A | 40000 | 0 | 0 | 0 | Efficacy | lm/W | 90 | 105 | 105 | 105 | 0 | 332.1033 | 0 | 332.1033 | 1 | 1 | 132 | 33 | 464.1033 | 365.1033 | 2050 | Advanced | 2.2831 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 4 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 332.1033 | 464.1033 | 365.1033
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 390.5538 | 0 | 390.5538 | 1 | 1 | 132 | 33 | 522.5538 | 423.5538 | 2023 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 390.5538 | 522.5538 | 423.5538
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 379.18 | 0 | 379.18 | 1 | 1 | 132 | 33 | 511.18 | 412.18 | 2030 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 379.18 | 511.18 | 412.18
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 372.3846 | 0 | 372.3846 | 1 | 1 | 132 | 33 | 504.3846 | 405.3846 | 2035 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 372.3846 | 504.3846 | 405.3846
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 365.5893 | 0 | 365.5893 | 1 | 1 | 132 | 33 | 497.5893 | 398.5893 | 2040 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 365.5893 | 497.5893 | 398.5893
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 359.1262 | 0 | 359.1262 | 1 | 1 | 132 | 33 | 491.1262 | 392.1262 | 2045 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 359.1262 | 491.1262 | 392.1262
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 352.6631 | 0 | 352.6631 | 1 | 1 | 132 | 33 | 484.6631 | 385.6631 | 2050 | Reference | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 352.6631 | 484.6631 | 385.6631
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 390.5538 | 0 | 390.5538 | 1 | 1 | 132 | 33 | 522.5538 | 423.5538 | 2023 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 390.5538 | 522.5538 | 423.5538
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 379.18 | 0 | 379.18 | 1 | 1 | 132 | 33 | 511.18 | 412.18 | 2030 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 379.18 | 511.18 | 412.18
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 372.3846 | 0 | 372.3846 | 1 | 1 | 132 | 33 | 504.3846 | 405.3846 | 2035 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 372.3846 | 504.3846 | 405.3846
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 365.5893 | 0 | 365.5893 | 1 | 1 | 132 | 33 | 497.5893 | 398.5893 | 2040 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 365.5893 | 497.5893 | 398.5893
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 359.1262 | 0 | 359.1262 | 1 | 1 | 132 | 33 | 491.1262 | 392.1262 | 2045 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 359.1262 | 491.1262 | 392.1262
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 352.6631 | 0 | 352.6631 | 1 | 1 | 132 | 33 | 484.6631 | 385.6631 | 2050 | Intermediate | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 352.6631 | 484.6631 | 385.6631
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 390.5538 | 0 | 390.5538 | 1 | 1 | 132 | 33 | 522.5538 | 423.5538 | 2023 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 390.5538 | 522.5538 | 423.5538
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 379.18 | 0 | 379.18 | 1 | 1 | 132 | 33 | 511.18 | 412.18 | 2030 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 379.18 | 511.18 | 412.18
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 372.3846 | 0 | 372.3846 | 1 | 1 | 132 | 33 | 504.3846 | 405.3846 | 2035 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 372.3846 | 504.3846 | 405.3846
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 365.5893 | 0 | 365.5893 | 1 | 1 | 132 | 33 | 497.5893 | 398.5893 | 2040 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 365.5893 | 497.5893 | 398.5893
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 359.1262 | 0 | 359.1262 | 1 | 1 | 132 | 33 | 491.1262 | 392.1262 | 2045 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 359.1262 | 491.1262 | 392.1262
51 | 2023 | Lighting | Electricity | Commercial |  | High-Bay Sodium Vapor | High-Bay | Sodium Vapor | High-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 28000 | 28500 | N/A | 29000 | 0 | 0 | 0 | Efficacy | lm/W | 112 | 114 | 116 | 116 | 0 | 352.6631 | 0 | 352.6631 | 1 | 1 | 132 | 33 | 484.6631 | 385.6631 | 2050 | Advanced | 2.5114 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 3 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 352.6631 | 484.6631 | 385.6631
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 107.006 | 0 | 107.006 | 1 | 1 | 99 | 33 | 206.006 | 140.006 | 2023 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 107.006 | 206.006 | 140.006
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 104.8571 | 0 | 104.8571 | 1 | 1 | 99 | 33 | 203.8571 | 137.8571 | 2030 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 104.8571 | 203.8571 | 137.8571
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 103.5732 | 0 | 103.5732 | 1 | 1 | 99 | 33 | 202.5732 | 136.5732 | 2035 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 103.5732 | 202.5732 | 136.5732
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 102.2893 | 0 | 102.2893 | 1 | 1 | 99 | 33 | 201.2893 | 135.2893 | 2040 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 102.2893 | 201.2893 | 135.2893
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 101.0682 | 0 | 101.0682 | 1 | 1 | 99 | 33 | 200.0682 | 134.0682 | 2045 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 101.0682 | 200.0682 | 134.0682
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 99.8471 | 0 | 99.8471 | 1 | 1 | 99 | 33 | 198.8471 | 132.8471 | 2050 | Reference | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 99.8471 | 198.8471 | 132.8471
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 107.006 | 0 | 107.006 | 1 | 1 | 99 | 33 | 206.006 | 140.006 | 2023 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 107.006 | 206.006 | 140.006
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 104.8571 | 0 | 104.8571 | 1 | 1 | 99 | 33 | 203.8571 | 137.8571 | 2030 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 104.8571 | 203.8571 | 137.8571
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 103.5732 | 0 | 103.5732 | 1 | 1 | 99 | 33 | 202.5732 | 136.5732 | 2035 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 103.5732 | 202.5732 | 136.5732
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 102.2893 | 0 | 102.2893 | 1 | 1 | 99 | 33 | 201.2893 | 135.2893 | 2040 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 102.2893 | 201.2893 | 135.2893
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 101.0682 | 0 | 101.0682 | 1 | 1 | 99 | 33 | 200.0682 | 134.0682 | 2045 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 101.0682 | 200.0682 | 134.0682
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 99.8471 | 0 | 99.8471 | 1 | 1 | 99 | 33 | 198.8471 | 132.8471 | 2050 | Intermediate | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 99.8471 | 198.8471 | 132.8471
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 107.006 | 0 | 107.006 | 1 | 1 | 99 | 33 | 206.006 | 140.006 | 2023 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 107.006 | 206.006 | 140.006
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 104.8571 | 0 | 104.8571 | 1 | 1 | 99 | 33 | 203.8571 | 137.8571 | 2030 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 104.8571 | 203.8571 | 137.8571
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 103.5732 | 0 | 103.5732 | 1 | 1 | 99 | 33 | 202.5732 | 136.5732 | 2035 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 103.5732 | 202.5732 | 136.5732
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 102.2893 | 0 | 102.2893 | 1 | 1 | 99 | 33 | 201.2893 | 135.2893 | 2040 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 102.2893 | 201.2893 | 135.2893
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 101.0682 | 0 | 101.0682 | 1 | 1 | 99 | 33 | 200.0682 | 134.0682 | 2045 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 101.0682 | 200.0682 | 134.0682
52 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Metal Halide | Low-Bay | Metal Halide | Low-Bay Metal Halide | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 8500 | N/A | 8500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 85 | 85 | 85 | 0 | 99.8471 | 0 | 99.8471 | 1 | 1 | 99 | 33 | 198.8471 | 132.8471 | 2050 | Advanced | 1.7123 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 1 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 99.8471 | 198.8471 | 132.8471
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 184.4703 | 0 | 184.4703 | 1 | 1 | 99 | 33 | 283.4703 | 217.4703 | 2023 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 184.4703 | 283.4703 | 217.4703
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 179.8083 | 0 | 179.8083 | 1 | 1 | 99 | 33 | 278.8083 | 212.8083 | 2030 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 179.8083 | 278.8083 | 212.8083
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 177.0229 | 0 | 177.0229 | 1 | 1 | 99 | 33 | 276.0229 | 210.0229 | 2035 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 177.0229 | 276.0229 | 210.0229
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 174.2375 | 0 | 174.2375 | 1 | 1 | 99 | 33 | 273.2375 | 207.2375 | 2040 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 174.2375 | 273.2375 | 207.2375
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 171.5883 | 0 | 171.5883 | 1 | 1 | 99 | 33 | 270.5883 | 204.5883 | 2045 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 171.5883 | 270.5883 | 204.5883
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 168.9391 | 0 | 168.9391 | 1 | 1 | 99 | 33 | 267.9391 | 201.9391 | 2050 | Reference | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 168.9391 | 267.9391 | 201.9391
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 184.4703 | 0 | 184.4703 | 1 | 1 | 99 | 33 | 283.4703 | 217.4703 | 2023 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 184.4703 | 283.4703 | 217.4703
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 179.8083 | 0 | 179.8083 | 1 | 1 | 99 | 33 | 278.8083 | 212.8083 | 2030 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 179.8083 | 278.8083 | 212.8083
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 177.0229 | 0 | 177.0229 | 1 | 1 | 99 | 33 | 276.0229 | 210.0229 | 2035 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 177.0229 | 276.0229 | 210.0229
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 174.2375 | 0 | 174.2375 | 1 | 1 | 99 | 33 | 273.2375 | 207.2375 | 2040 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 174.2375 | 273.2375 | 207.2375
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 171.5883 | 0 | 171.5883 | 1 | 1 | 99 | 33 | 270.5883 | 204.5883 | 2045 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 171.5883 | 270.5883 | 204.5883
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 168.9391 | 0 | 168.9391 | 1 | 1 | 99 | 33 | 267.9391 | 201.9391 | 2050 | Intermediate | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 168.9391 | 267.9391 | 201.9391
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 184.4703 | 0 | 184.4703 | 1 | 1 | 99 | 33 | 283.4703 | 217.4703 | 2023 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 184.4703 | 283.4703 | 217.4703
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 179.8083 | 0 | 179.8083 | 1 | 1 | 99 | 33 | 278.8083 | 212.8083 | 2030 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 179.8083 | 278.8083 | 212.8083
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 177.0229 | 0 | 177.0229 | 1 | 1 | 99 | 33 | 276.0229 | 210.0229 | 2035 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 177.0229 | 276.0229 | 210.0229
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 174.2375 | 0 | 174.2375 | 1 | 1 | 99 | 33 | 273.2375 | 207.2375 | 2040 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 174.2375 | 273.2375 | 207.2375
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 171.5883 | 0 | 171.5883 | 1 | 1 | 99 | 33 | 270.5883 | 204.5883 | 2045 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 171.5883 | 270.5883 | 204.5883
53 | 2023 | Lighting | Electricity | Commercial |  | Low-Bay Sodium Vapor | Low-Bay | Sodium Vapor | Low-Bay Sodium Vapor | 2023$ | 0 | 0 | 0 | Light Output | Lumens | 8500 | 9300 | N/A | 9500 | 0 | 0 | 0 | Efficacy | lm/W | 85 | 93 | 95 | 95 | 0 | 168.9391 | 0 | 168.9391 | 1 | 1 | 99 | 33 | 267.9391 | 201.9391 | 2050 | Advanced | 2.7397 | Prevailing local wages, Drive time, Access, Incentive programs, Brand recognition, Need for additional wiring / switching, Site assessment, Ceiling height | 2 | 5 | N/A | 2022 | No Advanced case was provided for this technology in the 2022 EIA - Technology Forecast Updates​ as it is a conventional lighting technology. For additional information on this decision, refer to that report. Only a typical dataset is provided because these lamps all have similar efficacies. | 168.9391 | 267.9391 | 201.9391
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 20.1705 | 64.3859 | 116.4921 | 772.6312 | 1.31 | 1.67 | 0 | 0 | 1012.1469 | 1290.2942 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 772.6312 | 1012.1469 | 1290.2942
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 21.8905 | 69.8762 | 126.4255 | 838.5145 | 1.31 | 1.67 | 0 | 0 | 1098.454 | 1400.3193 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 838.5145 | 1098.454 | 1400.3193
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 22.2032 | 70.8744 | 128.2316 | 850.4933 | 1.31 | 1.67 | 0 | 0 | 1114.1462 | 1420.3238 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 850.4933 | 1114.1462 | 1420.3238
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 862.4721 | 1.31 | 1.67 | 0 | 0 | 1129.8384 | 1440.3284 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 862.4721 | 1129.8384 | 1440.3284
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 862.4721 | 1.31 | 1.67 | 0 | 0 | 1129.8384 | 1440.3284 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 862.4721 | 1129.8384 | 1440.3284
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 862.4721 | 1.31 | 1.67 | 0 | 0 | 1129.8384 | 1440.3284 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 862.4721 | 1129.8384 | 1440.3284
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 20.1705 | 64.3859 | 116.4921 | 772.6312 | 1.31 | 1.67 | 0 | 0 | 1012.1469 | 1290.2942 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 772.6312 | 1012.1469 | 1290.2942
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.455 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.675 | 0.65 | 0.65 | 22.8287 | 72.8709 | 131.8437 | 874.4509 | 1.31 | 1.67 | 0 | 0 | 1145.5306 | 1460.333 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 874.4509 | 1145.5306 | 1460.333
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.445 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.6725 | 0.65 | 0.65 | 22.6723 | 72.3718 | 130.9407 | 868.4615 | 1.31 | 1.67 | 0 | 0 | 1137.6845 | 1450.3307 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 868.4615 | 1137.6845 | 1450.3307
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.435 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.67 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 862.4721 | 1.31 | 1.67 | 0 | 0 | 1129.8384 | 1440.3284 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 862.4721 | 1129.8384 | 1440.3284
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.4275 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.6675 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 862.4721 | 1.31 | 1.67 | 0 | 0 | 1129.8384 | 1440.3284 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 862.4721 | 1129.8384 | 1440.3284
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.42 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.665 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 862.4721 | 1.31 | 1.67 | 0 | 0 | 1129.8384 | 1440.3284 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 862.4721 | 1129.8384 | 1440.3284
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.68 | 0.65 | 0.65 | 20.1705 | 64.3859 | 116.4921 | 772.6312 | 1.31 | 1.67 | 0 | 0 | 1012.1469 | 1290.2942 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 772.6312 | 1012.1469 | 1290.2942
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.41 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.67 | 0.65 | 0.65 | 23.7668 | 75.8656 | 137.262 | 910.3872 | 1.31 | 1.67 | 0 | 0 | 1192.6072 | 1520.3466 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 910.3872 | 1192.6072 | 1520.3466
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.39 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.665 | 0.65 | 0.65 | 23.1414 | 73.8691 | 133.6498 | 886.4297 | 1.31 | 1.67 | 0 | 0 | 1161.2228 | 1480.3375 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 886.4297 | 1161.2228 | 1480.3375
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.37 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.66 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 862.4721 | 1.31 | 1.67 | 0 | 0 | 1129.8384 | 1440.3284 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 862.4721 | 1129.8384 | 1440.3284
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.355 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.655 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 862.4721 | 1.31 | 1.67 | 0 | 0 | 1129.8384 | 1440.3284 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 862.4721 | 1129.8384 | 1440.3284
54 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Aluminum Frame | Fenestration Double-Pane, Aluminum Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.7 | 0.34 | 0.3 | 0.3 | 0 | 0 | 0 | SHGC | Unitless | 0.68 | 0.65 | 0.65 | 0.65 | 22.516 | 71.8727 | 130.0377 | 862.4721 | 1.31 | 1.67 | 0 | 0 | 1129.8384 | 1440.3284 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 71 | N/A | 2023 | The typical costs assume a average window size of 12 sq ft. | 862.4721 | 1129.8384 | 1440.3284
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 715.335 | 1.31 | 1.67 | 0 | 0 | 937.0888 | 1194.6094 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 715.335 | 937.0888 | 1194.6094
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 715.335 | 1.31 | 1.67 | 0 | 0 | 937.0888 | 1194.6094 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 715.335 | 937.0888 | 1194.6094
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 715.335 | 1.31 | 1.67 | 0 | 0 | 937.0888 | 1194.6094 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 715.335 | 937.0888 | 1194.6094
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 715.335 | 1.31 | 1.67 | 0 | 0 | 937.0888 | 1194.6094 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 715.335 | 937.0888 | 1194.6094
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 715.335 | 1.31 | 1.67 | 0 | 0 | 937.0888 | 1194.6094 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 715.335 | 937.0888 | 1194.6094
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 715.335 | 1.31 | 1.67 | 0 | 0 | 937.0888 | 1194.6094 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 715.335 | 937.0888 | 1194.6094
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.2 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 715.335 | 1.31 | 1.67 | 0 | 0 | 937.0888 | 1194.6094 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 715.335 | 937.0888 | 1194.6094
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.24917 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20417 | 0.19 | 0.19 | 41.8296 | 62.1528 | 87.9925 | 745.8338 | 1.31 | 1.67 | 0 | 0 | 977.0423 | 1245.5424 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 745.8338 | 977.0423 | 1245.5424
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.24417 | 0.235 | 0.235 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20167 | 0.19 | 0.19 | 41.9851 | 62.3839 | 88.3196 | 748.6064 | 1.31 | 1.67 | 0 | 0 | 980.6744 | 1250.1727 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 748.6064 | 980.6744 | 1250.1727
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.23917 | 0.23 | 0.23 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19917 | 0.185 | 0.185 | 42.1406 | 62.6149 | 88.6467 | 751.379 | 1.31 | 1.67 | 0 | 0 | 984.3065 | 1254.8029 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 751.379 | 984.3065 | 1254.8029
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.23417 | 0.225 | 0.225 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19667 | 0.185 | 0.185 | 42.2961 | 62.846 | 88.9738 | 754.1516 | 1.31 | 1.67 | 0 | 0 | 987.9386 | 1259.4332 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 754.1516 | 987.9386 | 1259.4332
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.22917 | 0.22 | 0.22 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19417 | 0.185 | 0.185 | 42.4516 | 63.077 | 89.3009 | 756.9242 | 1.31 | 1.67 | 0 | 0 | 991.5708 | 1264.0635 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 756.9242 | 991.5708 | 1264.0635
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.25833 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.20917 | 0.19 | 0.19 | 40.1191 | 59.6112 | 84.3943 | 715.335 | 1.31 | 1.67 | 0 | 0 | 937.0888 | 1194.6094 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 715.335 | 937.0888 | 1194.6094
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.24 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19917 | 0.19 | 0.19 | 43.5401 | 64.6944 | 91.5907 | 776.3326 | 1.31 | 1.67 | 0 | 0 | 1016.9957 | 1296.4754 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 776.3326 | 1016.9957 | 1296.4754
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.23 | 0.23 | 0.23 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.19417 | 0.19 | 0.19 | 43.8511 | 65.1565 | 92.2449 | 781.8778 | 1.31 | 1.67 | 0 | 0 | 1024.2599 | 1305.7359 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 781.8778 | 1024.2599 | 1305.7359
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.22 | 0.22 | 0.22 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.18917 | 0.18 | 0.18 | 44.1621 | 65.6186 | 92.8991 | 787.423 | 1.31 | 1.67 | 0 | 0 | 1031.5242 | 1314.9964 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 787.423 | 1031.5242 | 1314.9964
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.21 | 0.21 | 0.21 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.18417 | 0.18 | 0.18 | 44.4731 | 66.0807 | 93.5533 | 792.9683 | 1.31 | 1.67 | 0 | 0 | 1038.7884 | 1324.257 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 792.9683 | 1038.7884 | 1324.257
55 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Wood Frame | Fenestration Double-Pane, Wood Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.29 | 0.2 | 0.2 | 0.2 | 0 | 0 | 0 | SHGC | Unitless | 0.29 | 0.17917 | 0.18 | 0.18 | 44.7841 | 66.5428 | 94.2076 | 798.5135 | 1.31 | 1.67 | 0 | 0 | 1046.0527 | 1333.5175 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 93 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 798.5135 | 1046.0527 | 1333.5175
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 24.6933 | 43.0342 | 98.0426 | 516.411 | 1.31 | 1.67 | 0 | 0 | 676.4984 | 862.4063 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 516.411 | 676.4984 | 862.4063
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 26.799 | 46.7038 | 106.4028 | 560.446 | 1.31 | 1.67 | 0 | 0 | 734.1843 | 935.9449 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 560.446 | 734.1843 | 935.9449
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 27.1818 | 47.371 | 107.9228 | 568.4524 | 1.31 | 1.67 | 0 | 0 | 744.6727 | 949.3155 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 568.4524 | 744.6727 | 949.3155
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 576.4588 | 1.31 | 1.67 | 0 | 0 | 755.161 | 962.6862 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 576.4588 | 755.161 | 962.6862
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 576.4588 | 1.31 | 1.67 | 0 | 0 | 755.161 | 962.6862 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 576.4588 | 755.161 | 962.6862
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 576.4588 | 1.31 | 1.67 | 0 | 0 | 755.161 | 962.6862 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 576.4588 | 755.161 | 962.6862
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 24.6933 | 43.0342 | 98.0426 | 516.411 | 1.31 | 1.67 | 0 | 0 | 676.4984 | 862.4063 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 516.411 | 676.4984 | 862.4063
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.31075 | 0.27 | 0.27 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28282 | 0.16 | 0.16 | 27.9475 | 48.7054 | 110.9629 | 584.4651 | 1.31 | 1.67 | 0 | 0 | 765.6493 | 976.0568 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 584.4651 | 765.6493 | 976.0568
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.30575 | 0.265 | 0.265 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28032 | 0.16 | 0.16 | 27.7561 | 48.3718 | 110.2029 | 580.462 | 1.31 | 1.67 | 0 | 0 | 760.4052 | 969.3715 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 580.462 | 760.4052 | 969.3715
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.30075 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27782 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 576.4588 | 1.31 | 1.67 | 0 | 0 | 755.161 | 962.6862 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 576.4588 | 755.161 | 962.6862
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.29575 | 0.255 | 0.255 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27532 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 576.4588 | 1.31 | 1.67 | 0 | 0 | 755.161 | 962.6862 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 576.4588 | 755.161 | 962.6862
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.29075 | 0.25 | 0.25 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27282 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 576.4588 | 1.31 | 1.67 | 0 | 0 | 755.161 | 962.6862 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 576.4588 | 755.161 | 962.6862
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.32149 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 24.6933 | 43.0342 | 98.0426 | 516.411 | 1.31 | 1.67 | 0 | 0 | 676.4984 | 862.4063 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 516.411 | 676.4984 | 862.4063
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.3 | 0.28 | 0.28 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28 | 0.16 | 0.16 | 29.096 | 50.707 | 115.523 | 608.4843 | 1.31 | 1.67 | 0 | 0 | 797.1144 | 1016.1687 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 608.4843 | 797.1144 | 1016.1687
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.29 | 0.27 | 0.27 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.275 | 0.16 | 0.16 | 28.3303 | 49.3726 | 112.4829 | 592.4715 | 1.31 | 1.67 | 0 | 0 | 776.1377 | 989.4274 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 592.4715 | 776.1377 | 989.4274
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.28 | 0.26 | 0.26 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 576.4588 | 1.31 | 1.67 | 0 | 0 | 755.161 | 962.6862 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 576.4588 | 755.161 | 962.6862
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.27 | 0.25 | 0.25 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.265 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 576.4588 | 1.31 | 1.67 | 0 | 0 | 755.161 | 962.6862 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 576.4588 | 755.161 | 962.6862
56 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Double-Pane, Vinyl Frame | Fenestration Double-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.75 | 0.26 | 0.24 | 0.24 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.26 | 0.16 | 0.16 | 27.5647 | 48.0382 | 109.4429 | 576.4588 | 1.31 | 1.67 | 0 | 0 | 755.161 | 962.6862 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 67 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from the NREL NREMDB was used in additional to RSMeans data. The typical costs assume a average window size of 12 sq ft. | 576.4588 | 755.161 | 962.6862
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 73.7476 | 111.3574 | 127.5566 | 1336.2886 | 1.31 | 1.67 | 0 | 0 | 1750.5381 | 2231.602 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1336.2886 | 1750.5381 | 2231.602
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 80.0361 | 120.853 | 138.4335 | 1450.2357 | 1.31 | 1.67 | 0 | 0 | 1899.8088 | 2421.8937 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1450.2357 | 1899.8088 | 2421.8937
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 81.1795 | 122.5794 | 140.4112 | 1470.9534 | 1.31 | 1.67 | 0 | 0 | 1926.9489 | 2456.4921 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1470.9534 | 1926.9489 | 2456.4921
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 1491.671 | 1.31 | 1.67 | 0 | 0 | 1954.0891 | 2491.0906 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1491.671 | 1954.0891 | 2491.0906
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 1491.671 | 1.31 | 1.67 | 0 | 0 | 1954.0891 | 2491.0906 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1491.671 | 1954.0891 | 2491.0906
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 1491.671 | 1.31 | 1.67 | 0 | 0 | 1954.0891 | 2491.0906 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1491.671 | 1954.0891 | 2491.0906
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 73.7476 | 111.3574 | 127.5566 | 1336.2886 | 1.31 | 1.67 | 0 | 0 | 1750.5381 | 2231.602 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1336.2886 | 1750.5381 | 2231.602
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.23 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28282 | 0.16 | 0.16 | 83.4663 | 126.0324 | 144.3664 | 1512.3887 | 1.31 | 1.67 | 0 | 0 | 1981.2292 | 2525.6891 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1512.3887 | 1981.2292 | 2525.6891
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.2225 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28032 | 0.16 | 0.16 | 82.8946 | 125.1692 | 143.3776 | 1502.0299 | 1.31 | 1.67 | 0 | 0 | 1967.6591 | 2508.3899 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1502.0299 | 1967.6591 | 2508.3899
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.215 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27782 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 1491.671 | 1.31 | 1.67 | 0 | 0 | 1954.0891 | 2491.0906 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1491.671 | 1954.0891 | 2491.0906
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.2075 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27532 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 1491.671 | 1.31 | 1.67 | 0 | 0 | 1954.0891 | 2491.0906 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1491.671 | 1954.0891 | 2491.0906
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.2 | 0.135 | 0.135 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27282 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 1491.671 | 1.31 | 1.67 | 0 | 0 | 1954.0891 | 2491.0906 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1491.671 | 1954.0891 | 2491.0906
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.25 | 0.15 | 0.15 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28564 | 0.16 | 0.16 | 73.7476 | 111.3574 | 127.5566 | 1336.2886 | 1.31 | 1.67 | 0 | 0 | 1750.5381 | 2231.602 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1336.2886 | 1750.5381 | 2231.602
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.21 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.28 | 0.16 | 0.16 | 86.8964 | 131.2118 | 150.2993 | 1574.5416 | 1.31 | 1.67 | 0 | 0 | 2062.6496 | 2629.4845 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1574.5416 | 2062.6496 | 2629.4845
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.195 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.275 | 0.16 | 0.16 | 84.6096 | 127.7589 | 146.344 | 1533.1063 | 1.31 | 1.67 | 0 | 0 | 2008.3693 | 2560.2876 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1533.1063 | 2008.3693 | 2560.2876
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.18 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.27 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 1491.671 | 1.31 | 1.67 | 0 | 0 | 1954.0891 | 2491.0906 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1491.671 | 1954.0891 | 2491.0906
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.165 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.265 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 1491.671 | 1.31 | 1.67 | 0 | 0 | 1954.0891 | 2491.0906 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1491.671 | 1954.0891 | 2491.0906
57 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Triple-Pane, Vinyl Frame | Fenestration Triple-Pane, Vinyl Frame | 2023$/sq ft | 0 | 0 | 0 | U-Factor | Btu/h·ft2·F | 0.32 | 0.15 | 0.12 | 0.12 | 0 | 0 | 0 | SHGC | Unitless | 0.65 | 0.26 | 0.16 | 0.16 | 82.3229 | 124.3059 | 142.3888 | 1491.671 | 1.31 | 1.67 | 0 | 0 | 1954.0891 | 2491.0906 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 2 | 15 | N/A | 2023 | This technology was found to have similar pricing to its residential counterpart. As a result, residential data from a previous project was used in additional to RSMeans data. Due to limited available data, ENERGY STAR values were used for the efficiency metrics. The typical costs assume a average window size of 12 sq ft. | 1491.671 | 1954.0891 | 2491.0906
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.22411 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30679 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.23411 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.31679 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.23411 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.31679 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.23911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.32179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.24411 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.32679 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.21911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.30179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.22911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.31179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.24911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.33179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.24911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.33179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.25911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.34179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
58 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Window Film | Fenestration Window Film | 2023$/sq ft | 0 | 0 | 0 | SHGC Decrease | Unitless | 0.02 | 0.26911 | 0.52 | 0.52 | 0 | 0 | 0 | VT Decrease | Unitless | 0.01 | 0.35179 | 0.68 | 0.68 | 13.248 | 48.6634 | 53.3333 | 583.9611 | 1 | 1 | 1.4833 | 1.5733 | 601.7611 | 602.8411 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 3 | 189 | N/A | 2023 | Window films are applied to existing windows to decrease the SHGC and VT of the window. The typical costs assume a average window size of 12 sq ft. Assumes the same lifetime as windows. | 583.9611 | 601.7611 | 602.8411
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 85295.5285 | 1 | 1 | 12560 | 12560 | 97855.5285 | 97855.5285 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 85295.5285 | 1 | 1 | 12560 | 12560 | 97855.5285 | 97855.5285 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 85295.5285 | 1 | 1 | 12560 | 12560 | 97855.5285 | 97855.5285 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 85295.5285 | 1 | 1 | 12560 | 12560 | 97855.5285 | 97855.5285 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 85295.5285 | 1 | 1 | 12560 | 12560 | 97855.5285 | 97855.5285 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 85295.5285 | 1 | 1 | 12560 | 12560 | 97855.5285 | 97855.5285 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 85295.5285 | 1 | 1 | 12560 | 12560 | 97855.5285 | 97855.5285 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 89 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 88268.3973 | 1 | 1 | 12560 | 12560 | 100828.3973 | 100828.3973 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 89.5 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 88640.0059 | 1 | 1 | 12560 | 12560 | 101200.0059 | 101200.0059 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 90 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 89011.6145 | 1 | 1 | 12560 | 12560 | 101571.6145 | 101571.6145 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 90 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 89011.6145 | 1 | 1 | 12560 | 12560 | 101571.6145 | 101571.6145 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 90 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 89011.6145 | 1 | 1 | 12560 | 12560 | 101571.6145 | 101571.6145 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 85 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 85295.5285 | 1 | 1 | 12560 | 12560 | 97855.5285 | 97855.5285 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 93 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 91241.2661 | 1 | 1 | 12560 | 12560 | 103801.2661 | 103801.2661 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 94 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 91984.4833 | 1 | 1 | 12560 | 12560 | 104544.4833 | 104544.4833 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 95 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 92727.7005 | 1 | 1 | 12560 | 12560 | 105287.7005 | 105287.7005 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 95 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 92727.7005 | 1 | 1 | 12560 | 12560 | 105287.7005 | 105287.7005 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
59 | 2023 | Heating | Gas | Commercial |  | Commercial Gas-Fired Boilers | Boilers | Gas-Fired | Commercial Boiler Gas-Fired | 2023$ | 0.02613 | 0.026672 | 0.039338 | Capacity | Btu/h | 202000 | 800000 | 800000 | 2499000 | 1.0125e-08 | 743.2172 | 657.2479 | Thermal Efficiency | % | 80 | 95 | 99 | 95 | 1.046e-08 | 784.4665 | 714.0148 | 92727.7005 | 1 | 1 | 12560 | 12560 | 105287.7005 | 105287.7005 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 35 | 0.6568 | 2023 |  | 85295.5285 | 97855.5285 | 97855.5285
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2035 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2040 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2045 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
60 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Electric Resistanec Water Heaters | Commercial Water Heater | Electric Storage | Commercial Water Heater Electric Storage | 2023$ | 46.28 | 76.0526 | 102.1111 | Capacity | Gallons | 6 | 118 | 118 | 120 | 0 | 0 | 0 | Thermal Efficiency | % | 98 | 98 | 98 | 98 | 276.39 | 803.6742 | 2826.6567 | 9777.8847 | 1 | 1 | 940 | 1280 | 10717.8847 | 11057.8847 | 2050 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 159 | 0.25 | 2023 |  | 9777.8847 | 10717.8847 | 11057.8847
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 4830.7671 | 1 | 1 | 950 | 950 | 5780.7671 | 5780.7671 | 2023 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 4830.7671 | 1 | 1 | 950 | 950 | 5780.7671 | 5780.7671 | 2030 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 4830.7671 | 1 | 1 | 950 | 950 | 5780.7671 | 5780.7671 | 2035 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 4830.7671 | 1 | 1 | 950 | 950 | 5780.7671 | 5780.7671 | 2040 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 4830.7671 | 1 | 1 | 950 | 950 | 5780.7671 | 5780.7671 | 2045 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 4830.7671 | 1 | 1 | 950 | 950 | 5780.7671 | 5780.7671 | 2050 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 4830.7671 | 1 | 1 | 950 | 950 | 5780.7671 | 5780.7671 | 2023 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 93.9724 | 79.6837 | 123 | 2192.456 | 2740.57 | 3288.684 | 4923.8988 | 1 | 1 | 950 | 950 | 5873.8988 | 5873.8988 | 2030 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 91.7468 | 77.7964 | 123 | 2192.456 | 2740.57 | 3288.684 | 4965.808 | 1 | 1 | 950 | 950 | 5915.808 | 5915.808 | 2035 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 89.5211 | 75.9092 | 123 | 2192.456 | 2740.57 | 3288.684 | 5007.7173 | 1 | 1 | 950 | 950 | 5957.7173 | 5957.7173 | 2040 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 87.518 | 74.2107 | 123 | 2192.456 | 2740.57 | 3288.684 | 5045.4356 | 1 | 1 | 950 | 950 | 5995.4356 | 5995.4356 | 2045 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 85.5149 | 72.5121 | 123 | 2192.456 | 2740.57 | 3288.684 | 5083.1539 | 1 | 1 | 950 | 950 | 6033.1539 | 6033.1539 | 2050 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 98.9184 | 83.8776 | 123 | 2192.456 | 2740.57 | 3288.684 | 4830.7671 | 1 | 1 | 950 | 950 | 5780.7671 | 5780.7671 | 2023 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 89.0265 | 75.4898 | 123 | 2192.456 | 2740.57 | 3288.684 | 5017.0304 | 1 | 1 | 950 | 950 | 5967.0304 | 5967.0304 | 2030 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 84.5752 | 71.7153 | 123 | 2192.456 | 2740.57 | 3288.684 | 5100.8489 | 1 | 1 | 950 | 950 | 6050.8489 | 6050.8489 | 2035 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 80.1239 | 67.9408 | 123 | 2192.456 | 2740.57 | 3288.684 | 5184.6674 | 1 | 1 | 950 | 950 | 6134.6674 | 6134.6674 | 2040 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 76.1177 | 64.5438 | 123 | 2192.456 | 2740.57 | 3288.684 | 5260.104 | 1 | 1 | 950 | 950 | 6210.104 | 6210.104 | 2045 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
61 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Freezer | Commercial Refrigeration | Reach-in Freezer | Commercial Reach-in Freezer | 2023$ | 64.536 | 80.67 | 96.804 | Volume | ft3 | 7.03 | 49 | 49 | 49 | -15.064 | -18.83 | -22.596 | Energy Use Per Volume | (kWh/year)/ft3 | 37 | 72.1115 | 61.1467 | 123 | 2192.456 | 2740.57 | 3288.684 | 5335.5406 | 1 | 1 | 950 | 950 | 6285.5406 | 6285.5406 | 2050 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7799 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4830.7671 | 5780.7671 | 5780.7671
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4023.1367 | 1 | 1 | 863 | 863 | 4886.1367 | 4886.1367 | 2023 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4023.1367 | 1 | 1 | 863 | 863 | 4886.1367 | 4886.1367 | 2030 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4023.1367 | 1 | 1 | 863 | 863 | 4886.1367 | 4886.1367 | 2035 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4023.1367 | 1 | 1 | 863 | 863 | 4886.1367 | 4886.1367 | 2040 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4023.1367 | 1 | 1 | 863 | 863 | 4886.1367 | 4886.1367 | 2045 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4023.1367 | 1 | 1 | 863 | 863 | 4886.1367 | 4886.1367 | 2050 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4023.1367 | 1 | 1 | 863 | 863 | 4886.1367 | 4886.1367 | 2023 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4034.4496 | 1 | 1 | 863 | 863 | 4897.4496 | 4897.4496 | 2030 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4034.4496 | 1 | 1 | 863 | 863 | 4897.4496 | 4897.4496 | 2035 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4034.4496 | 1 | 1 | 863 | 863 | 4897.4496 | 4897.4496 | 2040 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4034.4496 | 1 | 1 | 863 | 863 | 4897.4496 | 4897.4496 | 2045 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 28.6247 | 17.1748 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4034.4496 | 1 | 1 | 863 | 863 | 4897.4496 | 4897.4496 | 2050 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 29.3587 | 17.6152 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4023.1367 | 1 | 1 | 863 | 863 | 4886.1367 | 4886.1367 | 2023 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4045.7624 | 1 | 1 | 863 | 863 | 4908.7624 | 4908.7624 | 2030 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4045.7624 | 1 | 1 | 863 | 863 | 4908.7624 | 4908.7624 | 2035 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4045.7624 | 1 | 1 | 863 | 863 | 4908.7624 | 4908.7624 | 2040 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4045.7624 | 1 | 1 | 863 | 863 | 4908.7624 | 4908.7624 | 2045 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
62 | 2023 | Refrigeration | Electricity | Commercial |  | Reach-in Refrigerator | Commercial Refrigeration | Reach-in Refrigerator | Commercial Reach-in Refrigerator | 2023$ | 35.824 | 44.78 | 53.736 | Volume | ft3 | 7.03 | 46 | 46 | 49 | -12.3306 | -15.4133 | -18.496 | Energy Use Per Volume | (kWh/year)/ft3 | 22.55 | 27.8908 | 16.7345 | 77.47 | 1932.6169 | 2415.7711 | 2898.9253 | 4045.7624 | 1 | 1 | 863 | 863 | 4908.7624 | 4908.7624 | 2050 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 16 | 0.7976 | 2014 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 4023.1367 | 4886.1367 | 4886.1367
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2023 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2030 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2035 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2040 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2045 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2050 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2023 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2030 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2035 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2040 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2045 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2050 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2023 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2030 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2035 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2040 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2045 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
63 | 2023 | Heating | Electricity | Commercial |  | Commercial Electric Resistance Heaters | Unit Heater | Electric | Unit Heater Electric | 2023$ | 105.3601 | 135.0223 | 156.1863 | Heating Capacity | kW | 2.2 | 7.5 | 80 | 80 | 0 | 0 | 0 | Efficiency | % | 100 | 100 | 100 | 100 | 74.807 | 369.3432 | 1087.8724 | 1382.0102 | 1.18 | 1.18 | 0 | 0 | 1630.7721 | 1630.7721 | 2050 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 125 | 0.5485 | 2023 |  | 1382.0102 | 1630.7721 | 1630.7721
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2023 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34620.5393 | 44487.393 | 44487.393
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2030 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34620.5393 | 44487.393 | 44487.393
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2035 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34620.5393 | 44487.393 | 44487.393
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2040 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34620.5393 | 44487.393 | 44487.393
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2045 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34620.5393 | 44487.393 | 44487.393
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2050 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34620.5393 | 44487.393 | 44487.393
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2023 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34620.5393 | 44487.393 | 44487.393
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34633.726 | 1.285 | 1.285 | 0 | 0 | 44504.3379 | 44504.3379 | 2030 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34161.6432 | 43897.7115 | 43897.7115
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34633.726 | 1.285 | 1.285 | 0 | 0 | 44504.3379 | 44504.3379 | 2035 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34161.6432 | 43897.7115 | 43897.7115
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34633.726 | 1.285 | 1.285 | 0 | 0 | 44504.3379 | 44504.3379 | 2040 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34161.6432 | 43897.7115 | 43897.7115
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34633.726 | 1.285 | 1.285 | 0 | 0 | 44504.3379 | 44504.3379 | 2045 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34161.6432 | 43897.7115 | 43897.7115
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 151.0665 | 188.8331 | 226.5998 | Efficiency | % | 81 | 89.5 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34633.726 | 1.285 | 1.285 | 0 | 0 | 44504.3379 | 44504.3379 | 2050 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34161.6432 | 43897.7115 | 43897.7115
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 155.2862 | 194.1078 | 232.9294 | Efficiency | % | 81 | 87 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2023 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 34620.5393 | 44487.393 | 44487.393
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2030 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 33702.747 | 43308.0299 | 43308.0299
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2035 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 33702.747 | 43308.0299 | 43308.0299
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2040 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 33702.747 | 43308.0299 | 43308.0299
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2045 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 33702.747 | 43308.0299 | 43308.0299
64 | 2023 | Heating | Gas | Commercial |  | Commercial Oil-Fired Boilers | Boilers | Oil-Fired | Commercial Boiler Oil | 2023$ | 17.7308 | 22.1636 | 26.5963 | Input Capaicty | kBtu/h | 7.03 | 800 | 3000 | 3000 | 146.8468 | 183.5585 | 220.2702 | Efficiency | % | 81 | 92 | 97 | 97 | 1932.6169 | 2.3207 | 2898.9253 | 34620.5393 | 1.285 | 1.285 | 0 | 0 | 44487.393 | 44487.393 | 2050 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 2 | 20 | 0.5737 | 2023 | Quantile regresions intersected, median regression +/- 20% was used for low and high regressions | 33702.747 | 43308.0299 | 43308.0299
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 82 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 11449.1293 | 1 | 1 | 2440 | 3060 | 13889.1293 | 14509.1293 | 2023 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2030 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2035 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2040 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2045 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2050 | Reference | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 82 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 11449.1293 | 1 | 1 | 2440 | 3060 | 13889.1293 | 14509.1293 | 2023 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2030 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2035 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2040 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2045 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2050 | Intermediate | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 82 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 11449.1293 | 1 | 1 | 2440 | 3060 | 13889.1293 | 14509.1293 | 2023 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2030 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2035 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2040 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2045 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
65 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Water Heaters | Water Heater | Gas Storage | Commercial Water Heater Gas Storage | 2023$ | 46.2689 | 71.5502 | 33.6899 | Capacity | Gallons | 50 | 100 | 100 | 250 | 123.7783 | 94.5698 | 217.4426 | Thermal Efficiency | % | 80 | 95 | 99 | 98 | -9406.175 | -3460.61 | -5143.9391 | 12678.5361 | 1 | 1 | 2440 | 3060 | 15118.5361 | 15738.5361 | 2050 | Advanced | 10 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 69 | 0.61 | 2023 |  | 11449.1293 | 13889.1293 | 14509.1293
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2023 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2030 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2035 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2040 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2045 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2050 | Reference | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2023 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2030 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2035 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2040 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2045 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2050 | Intermediate | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2023 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2030 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2035 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2040 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2045 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
66 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Booster Water Heaters | Water Heater | Gas Booster | Commercial Water Heater Gas Booster | 2023$ | 0.02 | 0.033841 | 0.047683 | Heat Output | Btu/h | 84800 | 125200 | 160000 | 160000 | 0 | 0 | 0 | Thermal Efficiency | % | 80 | 80 | 91 | 91 | 7550 | 10871.2584 | 14192.5169 | 15108.1882 | 1 | 1 | 300 | 300 | 15408.1882 | 15408.1882 | 2050 | Advanced | 7.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Piping run lengths, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | "High" and "Low" coeficeincts and intercepts are based on individual linear regressions of selected points which defined the uper and lower range of models identified, not quantile regresions of a single dataset. "Mid" coeficeint and intercept is the average of "Low" and "High". This modification in procedure was due to limited data available for this product | 15108.1882 | 15408.1882 | 15408.1882
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2023 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2030 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2035 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2040 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2045 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 3.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2050 | Reference | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2023 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.95 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2030 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2035 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.05 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2040 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.1 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2045 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.15 | 4.4 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2050 | Intermediate | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 3.9 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2023 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2030 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.1 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2035 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.2 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2040 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.3 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2045 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
67 | 2023 | Water Heating | Electricity | Commercial |  | Commercial Heat Pump Water Heaters | Water Heater | Heat Pump | Commercial Water Heater Heat Pump | 2023$ | 0 | 0 | 0 | Heat Output | kBtu/h | 125 | 157 | 257 | 257 | 0 | 0 | 0 | COP | Unitless | 3 | 4.4 | 4.9 | 4.9 | 8499 | 9233.5 | 9968 | 9233.5 | 1.08 | 1.08 | 0 | 0 | 9972.18 | 9972.18 | 2050 | Advanced | 15 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height | 3 | 4 | N/A | 2023 | Analysis includes storage and instantaneous heaters due to limited market availablity and data for both varieties | 9233.5 | 9972.18 | 9972.18
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.92 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2023 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2030 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2035 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2040 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2045 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2050 | Reference | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.92 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2023 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2030 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2035 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2040 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2045 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2050 | Intermediate | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.92 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2023 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2030 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2035 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2040 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2045 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
68 | 2023 | Water Heating | Gas | Commercial |  | Commercial Gas-Fired Instantenous Water Heaters | Water Heater | Gas Instantaneous | Commercial Water Heater Gas Instantaneous | 2023$ | 0.011363 | 0.014204 | 0.0017045 | Capacity | Btu/h | 225000 | 250000 | 250000 | 597000 | 1.8083e-08 | 2.2603e-08 | 2.7124e-09 | Thermal Efficiency | % | 0.8 | 0.96 | 0.99 | 0.99 | 1.9035e-08 | 2.3793e-08 | 2.8552e-08 | 3551.085 | 1.5832 | 2.135 | 0 | 0 | 5622.1488 | 7581.5665 | 2050 | Advanced | 17 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Brand recognition, Engineering and design fees, Need for controls and / or zoning, Condition of existing gas line, Condition of existing flue, Need to bring in combustion air, Condition of existing plumbing, Pump upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 2 | 17 | 0.2597 | 2023 | Quantile regressions intersected, median regression +/- 20% was used for low and high regressions available for this product. Regressions indicated very little correlation between efficiency and price. | 3551.085 | 5622.1488 | 7581.5665
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2023 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2030 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2035 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2040 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2045 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20460 | 20460 | 19028 | 19028 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2050 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 20930 | 20930 | 20214 | 20214 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2023 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 19860 | 19860 | 19144 | 19144 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2030 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 19378.5 | 19378.5 | 18662.5 | 18662.5 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2035 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 18897 | 18897 | 18181 | 18181 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2040 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 18463.65 | 18463.65 | 17747.65 | 17747.65 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2045 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 18030.3 | 18030.3 | 17314.3 | 17314.3 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2050 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 21400 | 21400 | 21400 | 21400 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2023 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 19260 | 19260 | 19260 | 19260 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2030 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 18297 | 18297 | 18297 | 18297 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2035 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 17334 | 17334 | 17334 | 17334 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2040 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16467.3 | 16467.3 | 16467.3 | 16467.3 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2045 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
69 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Freezer | Pre-Fabricated Walk-In | Freezer | Pre-Fabricated Walk-in Freezer | 2023$ | 66.72 | 83.4 | 10.008 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 15600.6 | 15600.6 | 15600.6 | 15600.6 | 6888.96 | 8611.2 | 10333.44 | 17952 | 1.2573 | 1.1906 | 0 | 0 | 22571.7149 | 21373.3991 | 2050 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | 0.9393 | 2023 | Limited data available so could not do a quantile regresion and could only consider price as a function of capacity, not energy use. Low and High bounds based on +/- 20% of the median regression. | 17952 | 22571.7149 | 21373.3991
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 13056 | 16200 | 18528 | 16200 | 1.1899 | 1.1409 | 0 | 0 | 19276.4893 | 18482.078 | 2023 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 16200 | 19276.4893 | 18482.078
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2030 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2035 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2040 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2045 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2050 | Reference | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 13056 | 16200 | 18528 | 16200 | 1.1899 | 1.1409 | 0 | 0 | 19276.4893 | 18482.078 | 2023 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 16200 | 19276.4893 | 18482.078
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 15390 | 15390 | 14060 | 14060 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2030 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 15025.5 | 15025.5 | 13727 | 13727 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2035 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 14661 | 14661 | 13394 | 13394 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2040 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 14332.95 | 14332.95 | 13094.3 | 13094.3 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2045 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 14004.9 | 14004.9 | 12794.6 | 12794.6 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2050 | Intermediate | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 16200 | 16200 | 14800 | 14800 | 13056 | 16200 | 18528 | 16200 | 1.1899 | 1.1409 | 0 | 0 | 19276.4893 | 18482.078 | 2023 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 16200 | 19276.4893 | 18482.078
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 14580 | 14580 | 13320 | 13320 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2030 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 13851 | 13851 | 12654 | 12654 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2035 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 13122 | 13122 | 11988 | 11988 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2040 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 12465.9 | 12465.9 | 11388.6 | 11388.6 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2045 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
70 | 2023 | Refrigeration | Electricity | Commercial |  | Commercial Walk-In Cooler | Pre-Fabricated Walk-In | Cooler | Pre-Fabricated Walk-in Cooler | 2023$ | 0 | 0 | 0 | Refrigerated Square Footage | sq ft | 64 | 112 | 160 | 160 | 0 | 0 | 0 | Annual Energy Use | kWh/y | 11809.8 | 11809.8 | 10789.2 | 10789.2 | 10558.2103 | 13100.7205 | 14983.3426 | 13100.7205 | 1.1899 | 1.1409 | 0 | 0 | 15588.6357 | 14946.2061 | 2050 | Advanced | 11 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Electrical infrastructure upgrades, Site assessment, Ceiling height | 2 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. | 13100.7205 | 15588.6357 | 14946.2061
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
71 | 2023 | Water Heating | Solar/Electricity | Commercial |  | Commercial Solar Water Heaters | Water Heater | Solar | Commercial Water Heater Solar | 2023$ | 0 | 0 | 0 | Array Area | sq ft | 18 | 85 | 120 | 120 | 0 | 0 | 0 | Solar Uniform Energy Factor (SUEF) | Unitless | 3 | 12 | 99 | 99 | 5652.25 | 6782.7025 | 9559.68 | 6782.7025 | 1.23 | 1.3 | 0 | 0 | 8342.7241 | 8817.5132 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Presence of hazardous materials, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for controls and / or zoning, Condition of existing plumbing, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Ceiling height | 4 | 4 | N/A | 2023 | Limited data available so could not do a regresion, a range of values is presented. Retail price includes, a colector, standard piping, and an electric backup storage water heater | 6782.7025 | 8342.7241 | 8817.5132
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 575.7143 | 612.4204 | 702.2222 | Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 5175 | 1.32 | 1.4966 | 0 | 0 | 6831.1892 | 7744.8866 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 5175 | 6831.1892 | 7744.8866
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 575.7143 | 612.4204 | 702.2222 | Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 5175 | 1.32 | 1.4966 | 0 | 0 | 6831.1892 | 7744.8866 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 5175 | 6831.1892 | 7744.8866
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 575.7143 | 612.4204 | 702.2222 | Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 5175 | 1.32 | 1.4966 | 0 | 0 | 6831.1892 | 7744.8866 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 5175 | 6831.1892 | 7744.8866
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 575.7143 | 612.4204 | 702.2222 | Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 5175 | 1.32 | 1.4966 | 0 | 0 | 6831.1892 | 7744.8866 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 5175 | 6831.1892 | 7744.8866
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 575.7143 | 612.4204 | 702.2222 | Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 5175 | 1.32 | 1.4966 | 0 | 0 | 6831.1892 | 7744.8866 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 5175 | 6831.1892 | 7744.8866
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 575.7143 | 612.4204 | 702.2222 | Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 5175 | 1.32 | 1.4966 | 0 | 0 | 6831.1892 | 7744.8866 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 5175 | 6831.1892 | 7744.8866
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 575.7143 | 612.4204 | 702.2222 | Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 5175 | 1.32 | 1.4966 | 0 | 0 | 6831.1892 | 7744.8866 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 5175 | 6831.1892 | 7744.8866
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 546.9286 | 581.7994 | 667.1111 | Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 4916.25 | 1.32 | 1.4966 | 0 | 0 | 6489.6298 | 7357.6422 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4916.25 | 6489.6298 | 7357.6422
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 546.9286 | 581.7994 | 667.1111 | Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 4916.25 | 1.32 | 1.4966 | 0 | 0 | 6489.6298 | 7357.6422 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4916.25 | 6489.6298 | 7357.6422
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 546.9286 | 581.7994 | 667.1111 | Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 4916.25 | 1.32 | 1.4966 | 0 | 0 | 6489.6298 | 7357.6422 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4916.25 | 6489.6298 | 7357.6422
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 546.9286 | 581.7994 | 667.1111 | Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 4916.25 | 1.32 | 1.4966 | 0 | 0 | 6489.6298 | 7357.6422 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4916.25 | 6489.6298 | 7357.6422
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 546.9286 | 581.7994 | 667.1111 | Capacity | Tons | 1 | 4 | 50 | 50 | 84.8214 | 73.5695 | 34.8333 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1465.7143 | 14.1189 | 4348.8889 | 4916.25 | 1.32 | 1.4966 | 0 | 0 | 6489.6298 | 7357.6422 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4916.25 | 6489.6298 | 7357.6422
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 575.7143 | 612.4204 | 702.2222 | Capacity | Tons | 1 | 4 | 50 | 50 | 89.2857 | 77.4416 | 36.6667 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1542.8571 | 14.862 | 4577.7778 | 5175 | 1.32 | 1.4966 | 0 | 0 | 6831.1892 | 7744.8866 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 5175 | 6831.1892 | 7744.8866
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 518.1429 | 551.1783 | 632 | Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 4657.5 | 1.32 | 1.4966 | 0 | 0 | 6148.0703 | 6970.3979 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4657.5 | 6148.0703 | 6970.3979
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 518.1429 | 551.1783 | 632 | Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 4657.5 | 1.32 | 1.4966 | 0 | 0 | 6148.0703 | 6970.3979 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4657.5 | 6148.0703 | 6970.3979
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 518.1429 | 551.1783 | 632 | Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 4657.5 | 1.32 | 1.4966 | 0 | 0 | 6148.0703 | 6970.3979 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4657.5 | 6148.0703 | 6970.3979
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 518.1429 | 551.1783 | 632 | Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 4657.5 | 1.32 | 1.4966 | 0 | 0 | 6148.0703 | 6970.3979 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4657.5 | 6148.0703 | 6970.3979
72 | 2023 | Heating, Cooling | Electricity | Commercial |  |  | Water Source Heat Pump |  | Water Source Heat Pump | 2023$ | 518.1429 | 551.1783 | 632 | Capacity | Tons | 1 | 4 | 50 | 50 | 80.3571 | 69.6975 | 33 | Heating Capacity | MBH | 13 | 35 | 200 | 200 | 1388.5714 | 13.3758 | 4120 | 4657.5 | 1.32 | 1.4966 | 0 | 0 | 6148.0703 | 6970.3979 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Need for additional structural support, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Condition of existing plumbing, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 17 | 0.8584 | 2023 |  | 4657.5 | 6148.0703 | 6970.3979
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0.5 | 0.5 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
73 | 2023 | Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Cool Only | VAV Box Cool Only | 2023$ | 0.078431 | 0.090909 | 0.095238 | Airflow | CFM | 450 | 1550 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1366.1059 | 1360.4909 | 1362.1143 | 1501.3999 | 1.1215 | 1.243 | 0 | 0 | 1683.7985 | 1866.1971 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 6 | 0.8606 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1501.3999 | 1683.7985 | 1866.1971
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2023 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2030 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2035 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2040 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2045 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2050 | Reference | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 0.5 | 0.5 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2023 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2030 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2035 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2040 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2045 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2050 | Intermediate | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2023 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2030 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2035 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2040 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2045 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
74 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Heating and Cooling | Variable Air Volume Box Heating and Cooling | 2023$ | 0.3 | 0.3125 | 0.33333 | Airflow | CFM | 200 | 1000 | 3000 | 3000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 1576.4 | 1638.9 | 1734.7333 | 1951.4 | 1.1391 | 1.2782 | 0 | 0 | 2222.8287 | 2494.2574 | 2050 | Advanced | 21 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 9 | 0.7224 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 1951.4 | 2222.8287 | 2494.2574
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2023 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2030 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2035 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2040 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2045 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2050 | Reference | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 0.5 | 0.5 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2023 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2030 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2035 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2040 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2045 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2050 | Intermediate | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2023 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2030 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2035 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2040 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2045 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
75 | 2023 | Heating, Cooling, Ventilation | Electricity | Commercial |  |  | Variable Air Volume Box | Fan Powered | Variable Air Volume Box Fan Powered | 2023$ | 0.63889 | 0.56123 | 0.54167 | Airflow | CFM | 200 | 900 | 2000 | 2000 | 0 | 0 | 0 | N/A | N/A | 0 | 1 | 1 | 0 | 2248.6222 | 2778.022 | 3143.0667 | 3283.1281 | 1.1458 | 1.2896 | 0 | 0 | 3761.9517 | 4233.8457 | 2050 | Advanced | 18 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Moisture issues present, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Condition of existing duct system, Adequacy of existing ventilation, Need for controls and / or zoning, Distance between terminal units, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Site assessment, Ceiling height | 3 | 16 | 0.1005 | 2023 | VAV boxes are an establishe technology and don't anticipate any major efficiency developments or price changes. | 3283.1281 | 3761.9517 | 4233.8457
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2023 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2030 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2035 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2040 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2045 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2050 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2023 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2030 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2035 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2040 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2045 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2050 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2023 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2030 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2035 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2040 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2045 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
76 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Energy Star Connected | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | Capacity | lb. ice/day | 360 | 360 | 360 | 360 | 0 | 0 | 0 | Energy Use | kWh/100 lb. | 5.3 | 5.3 | 5.3 | 5.3 | 4193.7413 | 4546.6595 | 4899.5777 | 4546.6595 | 1 | 1 | 857.1853 | 857.1853 | 5403.8448 | 5403.8448 | 2050 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 8 | 21 | N/A | 2020 | There are no Energy Start Connected Ice Machines available on the market, the price here is just an estimate from similar products. | 4546.6595 | 5403.8448 | 5403.8448
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2023 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2030 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2035 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2040 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2045 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2050 | Reference | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2023 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2030 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2035 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2040 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2045 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2050 | Intermediate | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2023 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2030 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2035 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2040 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Add-on Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2045 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
77 | 2023 | Refrigeration | Electricity | Commercial |  |  | Ice Machine | Add-on Control | Ice Machine Energy Star Connected | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 275.1799 | 343.9748 | 412.7698 | 343.9748 | 1 | 1 | 0 | 0 | 343.9748 | 343.9748 | 2050 | Advanced | 8.5 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Engineering and design fees, Condition of existing electrical system, Need for additional wiring / switching, Need for condensate line / drain, Need for controls and / or zoning, Piping run lengths, Pump upgrades, Electrical infrastructure upgrades, Mechanical room expansion and ventilation, Software upgrades, Site assessment, Sound barriers, Ceiling height, Coil upgrades | 2 | 1 | N/A | 2020 | There are very few add-on controls available on the market | 343.9748 | 343.9748 | 343.9748
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2023 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2030 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2035 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2040 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2045 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2050 | Reference | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2023 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2030 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2035 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2040 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2045 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2050 | Intermediate | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2023 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2030 | Advanced | 12 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition | 3 | 3 | N/A | 2020 | There are no performance metrics for add on controls because they provide only load shifting/DR capability and no additional energy savings. | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2035 | Advanced | [7 empty] | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2040 | Advanced | [7 empty] | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2045 | Advanced | [7 empty] | 252.4775 | 387.3157 | 387.3157
78 | 2023 | Water Heating | Electricity | Commercial |  |  | Electric Resistance Water Heater | Add-On Control | Electric Resistance Water Heater Add-On Control | 2023$ | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 137.5899 | 252.4775 | 367.3651 | 252.4775 | 1 | 1 | 134.8381 | 134.8381 | 387.3157 | 387.3157 | 2050 | Advanced | [7 empty] | 252.4775 | 387.3157 | 387.3157
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2023 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2030 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2035 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2040 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2045 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2050 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2023 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2030 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2035 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2040 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2045 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2050 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2023 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2030 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2035 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2040 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2045 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
79 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Thermochromic Glazing | Fenestration Thermochromic Glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.37 | 0.27 | 0.17 | 0.17 | 0 | 0 | 0 | U-factor | Unitless | 0.24 | 0.24 | 0.24 | 0.24 | 86.6324 | 91.6986 | 96.7648 | 1100.383 | 1.31 | 1.67 | 0 | 0 | 1441.5017 | 1837.6396 | 2050 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Assumes Thermochromic glazing with double low-e, insulated glass, with 90% Argon filled gap. Assumes an average window size of 12 sq ft. | 1100.383 | 1441.5017 | 1837.6396
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1650.5593 | 2104.1481 | 2023 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1259.9689 | 1650.5593 | 2104.1481
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1650.5593 | 2104.1481 | 2030 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1259.9689 | 1650.5593 | 2104.1481
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1650.5593 | 2104.1481 | 2035 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1259.9689 | 1650.5593 | 2104.1481
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1650.5593 | 2104.1481 | 2040 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1259.9689 | 1650.5593 | 2104.1481
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1650.5593 | 2104.1481 | 2045 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1259.9689 | 1650.5593 | 2104.1481
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1650.5593 | 2104.1481 | 2050 | Reference | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1259.9689 | 1650.5593 | 2104.1481
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1650.5593 | 2104.1481 | 2023 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1259.9689 | 1650.5593 | 2104.1481
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.245 | 0.245 | 0.245 | 0.245 | 98.0314 | 102.7809 | 107.5305 | 1233.3712 | 1.31 | 1.67 | 0 | 0 | 1615.7163 | 2059.73 | 2030 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1233.3712 | 1615.7163 | 2059.73
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.2375 | 0.2375 | 0.2375 | 0.2375 | 96.7648 | 101.5144 | 106.264 | 1218.1726 | 1.31 | 1.67 | 0 | 0 | 1595.8061 | 2034.3482 | 2035 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1218.1726 | 1595.8061 | 2034.3482
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.23 | 0.23 | 0.23 | 0.23 | 95.4982 | 100.2478 | 104.9974 | 1202.9739 | 1.31 | 1.67 | 0 | 0 | 1575.8958 | 2008.9665 | 2040 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1202.9739 | 1575.8958 | 2008.9665
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.225 | 0.225 | 0.225 | 0.225 | 95.4982 | 100.2478 | 104.9974 | 1202.9739 | 1.31 | 1.67 | 0 | 0 | 1575.8958 | 2008.9665 | 2045 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1202.9739 | 1575.8958 | 2008.9665
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.22 | 0.22 | 0.22 | 0.22 | 95.4982 | 100.2478 | 104.9974 | 1202.9739 | 1.31 | 1.67 | 0 | 0 | 1575.8958 | 2008.9665 | 2050 | Intermediate | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1202.9739 | 1575.8958 | 2008.9665
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.28 | 0.28 | 0.28 | 0.28 | 100.5645 | 104.9974 | 109.4304 | 1259.9689 | 1.31 | 1.67 | 0 | 0 | 1650.5593 | 2104.1481 | 2023 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1259.9689 | 1650.5593 | 2104.1481
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.21 | 0.21 | 0.21 | 0.21 | 95.4982 | 100.5645 | 105.6307 | 1206.7736 | 1.31 | 1.67 | 0 | 0 | 1580.8734 | 2015.3119 | 2030 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1206.7736 | 1580.8734 | 2015.3119
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.195 | 0.195 | 0.195 | 0.195 | 92.9651 | 98.0314 | 103.0976 | 1176.3763 | 1.31 | 1.67 | 0 | 0 | 1541.0529 | 1964.5484 | 2035 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1176.3763 | 1541.0529 | 1964.5484
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.18 | 0.18 | 0.18 | 0.18 | 90.432 | 95.4982 | 100.5645 | 1145.9789 | 1.31 | 1.67 | 0 | 0 | 1501.2324 | 1913.7848 | 2040 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1145.9789 | 1501.2324 | 1913.7848
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.17 | 0.17 | 0.17 | 0.17 | 90.432 | 95.4982 | 100.5645 | 1145.9789 | 1.31 | 1.67 | 0 | 0 | 1501.2324 | 1913.7848 | 2045 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1145.9789 | 1501.2324 | 1913.7848
80 | 2023 | Fenestration | All | Commercial |  |  | Fenestration | Electrochromic glazing | Fenestration Electrochromic glazing | 2023$/sq ft | 0 | 0 | 0 | SHGC | Unitless | 0.49 | 0.29 | 0.09 | 0.09 | 0 | 0 | 0 | U-factor | Unitless | 0.16 | 0.16 | 0.16 | 0.16 | 90.432 | 95.4982 | 100.5645 | 1145.9789 | 1.31 | 1.67 | 0 | 0 | 1501.2324 | 1913.7848 | 2050 | Advanced | 25 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 3 | N/A | 2020 | Electrochromic glazing with insulated glass unit with 90% Argon filled gap, low-iron pane. Assumes an average window size of 12 sq ft. | 1145.9789 | 1501.2324 | 1913.7848
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 109.3001 | 1 | 1 | 0 | 0 | 109.3001 | 109.3001 | 2023 | Reference | 30 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 109.3001 | 109.3001 | 109.3001
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 109.3001 | 1 | 1 | 0 | 0 | 109.3001 | 109.3001 | 2030 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 109.3001 | 109.3001 | 109.3001
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 109.3001 | 1 | 1 | 0 | 0 | 109.3001 | 109.3001 | 2035 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 109.3001 | 109.3001 | 109.3001
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 109.3001 | 1 | 1 | 0 | 0 | 109.3001 | 109.3001 | 2040 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 109.3001 | 109.3001 | 109.3001
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 109.3001 | 1 | 1 | 0 | 0 | 109.3001 | 109.3001 | 2045 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 109.3001 | 109.3001 | 109.3001
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 109.3001 | 1 | 1 | 0 | 0 | 109.3001 | 109.3001 | 2050 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 109.3001 | 109.3001 | 109.3001
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 109.3001 | 1 | 1 | 0 | 0 | 109.3001 | 109.3001 | 2023 | Intermediate | 30 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 109.3001 | 109.3001 | 109.3001
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.0916 | 8.8473 | 11.603 | 106.1673 | 1 | 1 | 0 | 0 | 106.1673 | 106.1673 | 2030 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 106.1673 | 106.1673 | 106.1673
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.0045 | 8.7457 | 11.487 | 104.949 | 1 | 1 | 0 | 0 | 104.949 | 104.949 | 2035 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 104.949 | 104.949 | 104.949
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.9175 | 8.6442 | 11.3709 | 103.7307 | 1 | 1 | 0 | 0 | 103.7307 | 103.7307 | 2040 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 103.7307 | 103.7307 | 103.7307
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.8595 | 8.5427 | 11.2259 | 102.5124 | 1 | 1 | 0 | 0 | 102.5124 | 102.5124 | 2045 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 102.5124 | 102.5124 | 102.5124
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.8015 | 8.4412 | 11.0808 | 101.2941 | 1 | 1 | 0 | 0 | 101.2941 | 101.2941 | 2050 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 101.2941 | 101.2941 | 101.2941
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 6.2656 | 9.1083 | 11.9511 | 109.3001 | 1 | 1 | 0 | 0 | 109.3001 | 109.3001 | 2023 | Advanced | 30 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 109.3001 | 109.3001 | 109.3001
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.9175 | 8.5862 | 11.2549 | 103.0345 | 1 | 1 | 0 | 0 | 103.0345 | 103.0345 | 2030 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 103.0345 | 103.0345 | 103.0345
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.7435 | 8.3832 | 11.0228 | 100.5979 | 1 | 1 | 0 | 0 | 100.5979 | 100.5979 | 2035 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 100.5979 | 100.5979 | 100.5979
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.5694 | 8.1801 | 10.7908 | 98.1612 | 1 | 1 | 0 | 0 | 98.1612 | 98.1612 | 2040 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 98.1612 | 98.1612 | 98.1612
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.4534 | 7.9771 | 10.5007 | 95.7246 | 1 | 1 | 0 | 0 | 95.7246 | 95.7246 | 2045 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 95.7246 | 95.7246 | 95.7246
81 | 2023 | Envelope | All | Commercial |  |  | Insulation | Inorganic PCM | Insulation Inorganic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 32 | 37 | 37 | 5.3374 | 7.774 | 10.2106 | 93.288 | 1 | 1 | 0 | 0 | 93.288 | 93.288 | 2050 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 93.288 | 93.288 | 93.288
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 80.0606 | 1 | 1 | 0 | 0 | 80.0606 | 80.0606 | 2023 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.0606 | 80.0606 | 80.0606
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 80.0606 | 1 | 1 | 0 | 0 | 80.0606 | 80.0606 | 2030 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.0606 | 80.0606 | 80.0606
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 80.0606 | 1 | 1 | 0 | 0 | 80.0606 | 80.0606 | 2035 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.0606 | 80.0606 | 80.0606
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 80.0606 | 1 | 1 | 0 | 0 | 80.0606 | 80.0606 | 2040 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.0606 | 80.0606 | 80.0606
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 80.0606 | 1 | 1 | 0 | 0 | 80.0606 | 80.0606 | 2045 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.0606 | 80.0606 | 80.0606
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 80.0606 | 1 | 1 | 0 | 0 | 80.0606 | 80.0606 | 2050 | Reference | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.0606 | 80.0606 | 80.0606
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 80.0606 | 1 | 1 | 0 | 0 | 80.0606 | 80.0606 | 2023 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.0606 | 80.0606 | 80.0606
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.6274 | 6.8748 | 6.9038 | 82.4972 | 1 | 1 | 0 | 0 | 82.4972 | 82.4972 | 2030 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 82.4972 | 82.4972 | 82.4972
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.5694 | 6.7877 | 6.8313 | 81.4529 | 1 | 1 | 0 | 0 | 81.4529 | 81.4529 | 2035 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 81.4529 | 81.4529 | 81.4529
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.5114 | 6.7007 | 6.7587 | 80.4087 | 1 | 1 | 0 | 0 | 80.4087 | 80.4087 | 2040 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.4087 | 80.4087 | 80.4087
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.4244 | 6.4252 | 6.8603 | 77.1018 | 1 | 1 | 0 | 0 | 77.1018 | 77.1018 | 2045 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 77.1018 | 77.1018 | 77.1018
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.3374 | 6.1496 | 6.9618 | 73.795 | 1 | 1 | 0 | 0 | 73.795 | 73.795 | 2050 | Intermediate | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 73.795 | 73.795 | 73.795
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.8015 | 6.6717 | 7.5419 | 80.0606 | 1 | 1 | 0 | 0 | 80.0606 | 80.0606 | 2023 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.0606 | 80.0606 | 80.0606
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.4534 | 7.0778 | 6.2656 | 84.9338 | 1 | 1 | 0 | 0 | 84.9338 | 84.9338 | 2030 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 84.9338 | 84.9338 | 84.9338
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.3374 | 6.9038 | 6.1206 | 82.8453 | 1 | 1 | 0 | 0 | 82.8453 | 82.8453 | 2035 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 82.8453 | 82.8453 | 82.8453
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.2213 | 6.7297 | 5.9755 | 80.7568 | 1 | 1 | 0 | 0 | 80.7568 | 80.7568 | 2040 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 80.7568 | 80.7568 | 80.7568
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 5.0473 | 6.1786 | 6.1786 | 74.1431 | 1 | 1 | 0 | 0 | 74.1431 | 74.1431 | 2045 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 74.1431 | 74.1431 | 74.1431
82 | 2023 | Envelope | All | Commercial |  |  | Insulation | Organic PCM | Insulation Organic PCM | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M-Value | Btu/sq ft | 27 | 41 | 55 | 55 | 4.8733 | 5.6274 | 6.3816 | 67.5294 | 1 | 1 | 0 | 0 | 67.5294 | 67.5294 | 2050 | Advanced | 100 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 5 | 2 | N/A | 2020 | The PCM add-on is applied to existing interior walls or to replace existing insulation in walls or ceilings. Organic PCMs refer to bio-PCMs and inorganic PCMs refer to salt hydrates (gypsum). PCM envelope add-ons provide only passive flexibility (HVAC energy/peak savings) through storing and releasing thermal energy in response to temperature changes. Typical prices assume a PCM size of 12 sq ft though sizes vary greatly by buildign needs. | 67.5294 | 67.5294 | 67.5294
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2023 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2030 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2035 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2040 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2045 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2050 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2023 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2030 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2035 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2040 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2045 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2050 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2023 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2030 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2035 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2040 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2045 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
83 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Modular | Ice Storage for Commercial Chiller Modular | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 100 | 550 | 1000 | 1000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 220.1439 | 385.2518 | 550.3597 | 211888.5031 | 1 | 1 | 0 | 0 | 211888.5031 | 211888.5031 | 2050 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 4 | N/A | 2020 | Modular units represent both the heat transfer coils and the insulated tank. Modular units are generally used incrementally (adding more tanks) to fit the thermal energy storage needs of the project. Typical storage capacities are generally 1,000 ton-hours of cooling or lower, per modular unit. Projects often include multiple modular tanks. Installation costs are included in retail costs. | 211888.5031 | 211888.5031 | 211888.5031
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2023 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2030 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2035 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2040 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2045 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2050 | Reference | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2023 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 161.6682 | 161.6682 | 24250226.4151 | 1 | 1 | 0 | 0 | 24250226.4151 | 24250226.4151 | 2030 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 24250226.4151 | 24250226.4151 | 24250226.4151
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 161.6682 | 161.6682 | 24250226.4151 | 1 | 1 | 0 | 0 | 24250226.4151 | 24250226.4151 | 2035 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 24250226.4151 | 24250226.4151 | 24250226.4151
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 161.6682 | 161.6682 | 24250226.4151 | 1 | 1 | 0 | 0 | 24250226.4151 | 24250226.4151 | 2040 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 24250226.4151 | 24250226.4151 | 24250226.4151
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 149.6291 | 173.7073 | 22444358.4906 | 1 | 1 | 0 | 0 | 22444358.4906 | 22444358.4906 | 2045 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 22444358.4906 | 22444358.4906 | 22444358.4906
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2050 | Intermediate | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2023 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 185.7464 | 137.5899 | 27861962.2642 | 1 | 1 | 0 | 0 | 27861962.2642 | 27861962.2642 | 2030 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 27861962.2642 | 27861962.2642 | 27861962.2642
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 185.7464 | 137.5899 | 27861962.2642 | 1 | 1 | 0 | 0 | 27861962.2642 | 27861962.2642 | 2035 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 27861962.2642 | 27861962.2642 | 27861962.2642
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 185.7464 | 137.5899 | 27861962.2642 | 1 | 1 | 0 | 0 | 27861962.2642 | 27861962.2642 | 2040 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 27861962.2642 | 27861962.2642 | 27861962.2642
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 161.6682 | 161.6682 | 24250226.4151 | 1 | 1 | 0 | 0 | 24250226.4151 | 24250226.4151 | 2045 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 24250226.4151 | 24250226.4151 | 24250226.4151
84 | 2023 | Cooling | Electricity | Commercial |  |  | Ice Storage for Commercial Chiller | Site-Built | Ice Storage for Commercial Chiller Site-Built | 2023$/ton | 0 | 0 | 0 | Capacity | ton-hr | 50000 | 150000 | 250000 | 250000 | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 89.4335 | 137.5899 | 185.7464 | 20638490.566 | 1 | 1 | 0 | 0 | 20638490.566 | 20638490.566 | 2050 | Advanced | 40 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, Site assessment, Ceiling height | 4 | 3 | N/A | 2020 | Site-built coil only figures represent the costs and characteristics of coils used in site-built thermal energy storage, and does not include the cost of tank construction, which can vary widely depending on numerous construction conditions. Site-built projects generally have very large TES capacities and are usually reserved for district cooling applications. Installation costs are included in retail costs. | 20638490.566 | 20638490.566 | 20638490.566
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 24.7662 | 0 | 0 | 6.1915 | 6.1915 | 49.5324 | 49.5324 | 2023 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 24.7662 | 49.5324 | 49.5324
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 24.7662 | 0 | 0 | 6.1915 | 6.1915 | 49.5324 | 49.5324 | 2030 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 24.7662 | 49.5324 | 49.5324
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 24.7662 | 0 | 0 | 6.1915 | 6.1915 | 49.5324 | 49.5324 | 2035 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 24.7662 | 49.5324 | 49.5324
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 24.7662 | 0 | 0 | 6.1915 | 6.1915 | 49.5324 | 49.5324 | 2040 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 24.7662 | 49.5324 | 49.5324
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 24.7662 | 0 | 0 | 6.1915 | 6.1915 | 49.5324 | 49.5324 | 2045 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 24.7662 | 49.5324 | 49.5324
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 24.7662 | 0 | 0 | 6.1915 | 6.1915 | 49.5324 | 49.5324 | 2050 | Reference | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 24.7662 | 49.5324 | 49.5324
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 6.8795 | 24.7662 | 0 | 0 | 6.1915 | 6.1915 | 49.5324 | 49.5324 | 2023 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 24.7662 | 49.5324 | 49.5324
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.9532 | 5.5724 | 6.1915 | 22.2896 | 0 | 0 | 5.5724 | 5.5724 | 44.5791 | 44.5791 | 2030 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 22.2896 | 44.5791 | 44.5791
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.7469 | 5.6756 | 6.6043 | 22.7023 | 0 | 0 | 5.3316 | 5.3316 | 44.0288 | 44.0288 | 2035 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 22.7023 | 44.0288 | 44.0288
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.5405 | 5.7788 | 7.0171 | 23.1151 | 0 | 0 | 5.0908 | 5.0908 | 43.4784 | 43.4784 | 2040 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 23.1151 | 43.4784 | 43.4784
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.5405 | 5.7788 | 7.0171 | 23.1151 | 0 | 0 | 5.0908 | 5.0908 | 43.4784 | 43.4784 | 2045 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 23.1151 | 43.4784 | 43.4784
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.5405 | 5.7788 | 7.0171 | 23.1151 | 0 | 0 | 5.0908 | 5.0908 | 43.4784 | 43.4784 | 2050 | Intermediate | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 23.1151 | 43.4784 | 43.4784
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 5.5036 | 6.1915 | 9.4655 | 24.7662 | 0 | 0 | 6.1915 | 6.1915 | 49.5324 | 49.5324 | 2023 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 24.7662 | 49.5324 | 49.5324
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 4.4029 | 4.9532 | 5.5036 | 19.813 | 0 | 0 | 4.9532 | 4.9532 | 39.6259 | 39.6259 | 2030 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 19.813 | 39.6259 | 39.6259
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 3.9901 | 5.1596 | 6.3291 | 20.6385 | 0 | 0 | 4.4717 | 4.4717 | 38.5252 | 38.5252 | 2035 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 20.6385 | 38.5252 | 38.5252
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 3.5773 | 5.366 | 7.1547 | 21.464 | 0 | 0 | 3.9901 | 3.9901 | 37.4245 | 37.4245 | 2040 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 21.464 | 37.4245 | 37.4245
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 3.5773 | 5.366 | 7.1547 | 21.464 | 0 | 0 | 3.9901 | 3.9901 | 37.4245 | 37.4245 | 2045 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 21.464 | 37.4245 | 37.4245
85 | 2023 | Refrigeration | Electricity | Commercial |  |  | Commercial Refrigeration | Thermal Energy Storage | Commercial Refrigeration Thermal Energy Storage | 2023$/sq ft | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Energy Savings | % | 20 | 20 | 20 | 20 | 3.5773 | 5.366 | 7.1547 | 21.464 | 0 | 0 | 3.9901 | 3.9901 | 37.4245 | 37.4245 | 2050 | Advanced | 20 | Prevailing local wages, Drive time, Local code requirements, Access, Incentive programs, Existing construction and materials, Brand recognition, commercial refrigeration size and efficiency | 4 | 2 | N/A | 2020 | The TES System case refers to only the characteristics of a TES system made up of individual PCM cells stacked on shelving within a cold storage area. These TES systems are applied to walk-in coolers. The typical price assumes a size of 4 sq ft thought size varies greatly based on refrigerator size and energy storage needs. | 21.464 | 37.4245 | 37.4245
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2023 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2030 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2035 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2040 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2045 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2050 | Reference | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2023 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2030 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2035 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2040 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2045 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 20 | 40.25 | 60.5 | 60.5 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2050 | Intermediate | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 15 | 40 | 65 | 65 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2023 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 25 | 40.5 | 56 | 56 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2030 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692
86 | 2023 | Plug Loads | Electricity | Commercial |  |  | Advanced Power Strip | Tier 2 | Advanced Power Strip Tier 2 | 2023$/outlet | 0 | 0 | 0 | Capacity | Outlets | 5 | 6 | 6 | 6 | 0 | 0 | 0 | Computer Energy Savings | % | 25 | 40.5 | 56 | 56 | 17.8966 | 19.9615 | 22.0265 | 119.7692 | 0 | 0 | 0 | 0 | 119.7692 | 119.7692 | 2035 | Advanced | 9 | Prevailing local wages, Drive time, Access, Incentive programs, Existing construction and materials, Brand recognition | 10 | 6 | N/A | 2020 | Tier 2 power strips use additional sensors, software, and algorithms to sense real time power use; tier 2 power strips reduce standby and wasteful active loads. They provide flexibility by shifting plug loads (i.e., PC workstations). Load sensing detects energy use of the equipment, occupancy sensors detect motion, and infrared sensors detect heat. | 119.7692 | 119.7692 | 119.7692